## Sheet2
AR_NUMBER | AR_TYPE | ORIGINATION_DATE | AR_PRIORITY | AR_SEVERITY | AR_SUBJECT | TSSSC | NON_TSSSC | COMP_MEASURE | QUALITY | EQUIP_REL | DESCRIPTION_NOTES | AR_EPN
383472 | CR | 20180815 | CAQ | C | RCIC and HPCS Low CST level Swap-over. | Y | Y |  | N | YES | <D> **** Detailed Description **** During fill and vent of the suction piping the of RCIC keepfil pump per WO# 02129438 and SOP-RCIC-FILL step 5.1.4.c, RCIC and HPCS suctions swapped over to the SP (alarms 4.601.A4 3-4 and 4.601.A1 5-6). Venting through RCIC-V-759 was producing slugs of air while receiving the alarms. It is suspected a perturbation from vent and fill activities caused the pressure switches to actuate. Actual level in the CSTs stayed at 17feet throughout the evolution. <I> **** Actions Taken **** Investigated cause. WR written. <N> **** Equipment Description **** RB 448. | 02-00-HPCS-LS-1A,02-00-RCIC-LS-15A
383473 | CR | 20180815 | CAQ | D | RCIC-P-3 will not start in RUN | Y | Y |  | N | YES | <C> Item is a CRBB for Maintenance to gather additional information on starter coil / NLI buckets. <D> **** Detailed Description **** SOP-RCIC-FILL directs the starting of RCIC-P-3 by going to run. RCIC-P-3 will not start. <I> **** Actions Taken **** Reset thermal overloads and attempted to start again, still will not start in RUN. This is a condition that was created as a result of the maintenance performed during this outage. RCIC-P-3 was working normally prior to the outage. <N> Found that starter coil was removed and replaced with a new one, nothing was removed for any wiring for this task. The wire was loose and came off while performing this task of replacing the starter coil. No further action required. | 02-00-RCIC-P-3
383474 | CR | 20180815 | CAQ | D | H13-P601 A1 drop 5-6 HPCS-SUCTION SWITCHOVER alarm. | Y | Y |  | N | YES | <D> **** Detailed Description **** H13-P601 A1 drop 5-6 HPCS-SUCTION SWITCHOVER alarm is in and HPCS suction automatically from CST to Suppression Pool, HPCS-V-15 open and HPCS-V-1 closed. This alarm came in during SOP-RCIC-FILL 5.1.4.c.2 and will not clear. HPCS suction cannot be swapped to normal CST supply until alarm is clear. | 02-00-HPCS-LS-1A
383476 | CR | 20180815 |  | 4 | BRE 36 & 37 | N | N |  | N | YES | <D> **** Detailed Description **** Both Bre's need to have their windows evaluated. <N> **** Equipment Description **** BRE 36 & 37
383477 | CR | 20180815 | CAQ | D | Received the ROD DRIVE CONTROL SYS INOP alarm | Y | Y |  | N | YES | <D> **** Detailed Description **** Received the ROD DRIVE CONTROL SYS INOP alarm (H13-P603.A7 2-8) and RPIS OR DMM INOP (H13-P603.A7 1-7) alarm. No rod movement was in progress. <I> **** Actions Taken **** Reset per ARP and alarms stayed clear <N> This was a soft lockup of RDCS due to â€œ7 test errorsâ€ that was reset without reoccurrence. These lockups are trended and are subject to MRule condition monitoring limits. If 12 soft lockups occur in a 2 year period then actions to improve system performance are taken. Actions were taken in April 2018 (WO 02125410) which have reduced the occurrence of these lockups (this is the first one since the maintenance was completed). Any additional soft lockups will be trended as part of the MRule program to determine if further actions are warranted. Recommend trend.
383478 | CR | 20180815 | CAQ | D | HPCS SUCTION SWITCHOVER ALARM LOCKED IN | Y | N |  | N | YES | <D> **** Detailed Description **** During fill and vent of the suction piping the of RCIC keepfil pump per WO# 02129438 and SOP-RCIC-FILL step 5.1.4.c, RCIC and HPCS suctions swapped over to the SP (alarms 4.601.A4 3-4 and 4.601.A1 5-6). See CR 383472 The HPCS Suction Switchover alarm is still locked in after the perturbation. <I> **** Actions Taken **** Referenced TS and LCS. <N> **** Equipment Description **** RB 448 | 02-00-HPCS-LS-1A,02-00-HPCS-LS-1B,02-00-HPCS-PS-3A,02-00-HPCS-PS-3B
383479 | CR | 20180815 |  | 3 | CW-CT-1A Approx 1" from overflow | N | N |  | N | NO | <D> **** Detailed Description **** During operator rounds it was noted that due to maintaining the CW basin inlet plenum higher than 3 rungs down, CW-CT -1A was approximately 1" from overflowing the lower tower basin to the environment. The inlet plenum at this time was slightly higher than 2.5 rungs down. Will need to be closely monitored to keep CW-CT-1A from overflowing while we maintain CW basins higher than 3 rungs down. <I> **** Actions Taken **** Informed CRS
383490 | CR | 20180815 | CAQ | D | Security CCTV33 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security CCTV33/T33 are not operating by design and need maintenance. <I> **** Actions Taken **** Security supervision notified. CR/WR initiated. Compensatory measures initiated. | 02-00-SEC-CCTV-33
383491 | CR | 20180815 | CAQ | C | SW-V-16A and 22A changed to LO without 50.59 screen | Y | N |  | N | YES | <C> Reviewed ANON CR for content per SWP-CAP-01, moved to CR-SRO for Ops review. <D> **** ANONYMOUS CR - Detailed Description **** In response to AR CR 379796, SW-V-16A and SW-V-22A were changed to locked open (LO) valves via PPM 1.3.29 revision 79. As such, the physical configuration of the plant was altered for these valves (i.e., to include a physical locking device on them). PPM 1.3.29 revision 79 did not have a supporting 10 CFR 50.59 Screening. ADDITIONALLY: Portal J / MEL indicates that EPNs SW-V-16A and SW-V-22A have a Normal Position of O (Open) - it now needs to be changed to indicate LO (Locked Open) for these EPNs. Top Tier flow diagrams AED MEC M524-1 and AED MEC M524-2 (FSAR Figures) show SW-V-16A and SW-V-22A as open valves - they now need to be updated to add the LO (Locked Open) configuration designation for these EPNs per AED MEC M501. | 02-00-SW-V-16A,02-00-SW-V-22A
383497 | CR | 20180815 |  | 3 | EP Copiers unable to Scan to Email |  |  |  | N | NO | <D> **** Detailed Description **** New Canon Copiers installed in EP are unable to scan to email. New Copiers where configured with a different port to better secure scan to email function whoever firewall changes where not taken into consideration to allow that port. <I> **** Actions Taken **** IS Medium risk CCB process initiated to make the change to the EP firewall to allow that traffic through RFC-000227. Infrastructure and Cyber team are working through the resolution.
383501 | CR | 20180815 |  | 3 | Updates needed for AED S877, AED S875, AED S873 |  |  |  | N | YES | <D> **** Detailed Description **** Structural drawing AED STL S877 (Zone 1-6 / E-K and NOTE 4) currently includes vague details for a "CAISSON OPTION" that could have (but does not appear to have) been used to support original construction of the TMU pumphouse and the initial installation of TMU system pumps TMU-P-1A(B,C). This AED S877 information is historial in nature and should be removed from the drawing. AED STL S875 should also be updated to remove its existing reference to NOTE 2 (Zone F/4) for PARTIAL FLOOR PLAN- EL. 365'-6" and to elimiate NOTE 2 and NOTE 3 from the drawing. Finally, AED S873 (Zone F/9) SECTION 1-1 should be updated to remove its reference to AED S875 NOTE 2. Mark-ups are attached to the EDMS of this AR CR 383501. . This is entirely administrative in nature - there is no associated physical impact or effect upon the operating plant or the continued function/qualification/operation of any station SSCs. <N> Recommend NonCAQ assignment to Mechanical Design & Drafting for resolution (drawing updates). | 02-00-M-BLDG-MISC
383502 | CR | 20180815 |  | 3 | Non acceptance of administrative license amendment request |  |  |  | N | NO | <D> **** Detailed Description **** EN submitted a LAR via GO2-18-057 to do administrative cleanup changes in the Technical Specifications. Included with the LAR was a change to delete a license condition associated with having to install shield walls. NRC determined that inadequate information had been provided to justify the shield wall license condition removal as administrative and issued a non-acceptance with opportunity to supplement. A supplement has been submitted via GO2 -18-102 and accepted by the NRC with the shield wall license condition removal deleted from the scope of the LAR. The possible risk of non-acceptance was raised prior to filing, no pre-submittal discussion was conducted with the NRC and the LAR was internally approved to be sent with a possible risk of non-acceptance. <I> **** Actions Taken **** Recommend non-CAQ 3 to licensing to document lessons learned and initiate any further actions to reduce likelihood of non-acceptance in the future. Supplement was made removing shield wall portion of the LAR was resubmitted and accepted by the NRC.
383503 | CR | 20180815 |  | 4 | RRC-TRS-601 data storage card full | N | N |  | N | YES | <D> **** Detailed Description **** RRC-TRS-601 compact flash data card is full. Recommend changing card and evaluating periodicity of PM to ensure data is not lost between normal intervals. <I> **** Actions Taken **** Notified CRS. Submitted CR & Work Request. | 02-00-RRC-TRS-601
383504 | CR | 20180815 |  | 4 | GBP-ASU-03 steps not followed |  |  |  | N | NO | <D> **** Detailed Description **** Contrary to GBP-ASU-03, assignments stemming from a snapshot benchmark were created as ASGN-type assignments instead of SARC-type assignments. <I> **** Actions Taken **** The issue was discussed with Reg Affairs management and the individual was coached. The assignments not yet completed were changed to SARC-type assignments. No additional actions are needed.
383505 | CR | 20180815 | CAQ | C | FCP-2 Ground Fault | N | N |  | N | I DONT KNOW | <C> Per SWP-CAP-01, removed proper name from immediate action notes. <D> **** Detailed Description **** During the installation of FCP2 annunciation panel replacement W/O 02089258-02, electricians discovered a ground fault alarm in phase 4 of the implementation in the new CP-35. The locked in ground fault on the old CP-31 had been a known condition before replacing the control panels in the control room. Phase 4 consisted of FM modules 19-26. The plant had hoped that by replacing the panels it would correct the degraded conditions but it appears it has not. According to Fire Protection Engineer, a locked in ground fault indication would not prevent CP-35 from functioning as designed thereby providing all of the required supervision and alarm indications for Fire Detection and Alarm components downstream of CP-35 FCPâ€™s in the control room. <I> **** Actions Taken **** Contacted Fire Protection, regarding the known issue <N> **** Equipment Description **** P851 Board S FCP-2 (Functional Alarm) Cabinent CP-35 | 02-00-FP-CP-FCP2
383510 | CR | 20180815 |  | 4 | Back pain reported |  |  |  | N | NO | <D> **** Detailed Description **** Individual reported to the Manager experiencing slight back pain upon standing up from his chair. Individual was immediately escorted to Occupational health who evaluated the condition and released him back to work. <I> **** Actions Taken **** Escorted indivisual to occupational health, an incident was filled,
383511 | CR | 20180815 |  | 4 | BUS 21 GROUND alarm twice within about 15 minutes. | N | N |  | N | YES | <D> **** Detailed Description **** Received BUS 21 GROUND alarm twice within about 15 minutes. Both times, the affected MC was MC-2B. Each time, OPS3 was able to reset the alarm upon arrival at the ground panel. MT-CRA-1 was being moved at about the same time per WR 29143623. No other abnormalities were noted. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-E-MC-2B
383512 | CR | 20180815 |  | 4 | Repair MT-ELEV-3 prior to taking MT-ELEV-4 out of service. |  |  |  | N | YES | <D> **** Detailed Description **** Currently, MT-ELEV-3, the turbine building elevator, is out of service. MT-ELEV-4, the RW elevator, isscheduled to be taken out of service for five months beginning next week. If MT-ELEV-3 is not working prior to this, all loads will be placed upon the two Rx Bldg elevators, making them likelier to fail. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB | 02-00-MT-ELEV-3
383516 | CR | 20180815 |  | 4 | HWC alarm HS PAL124-PRES STAT LOW recieved | N | N |  | N | YES | <D> **** Detailed Description **** Recieved HS PAL124-PRES STAT LOW (Hyrdogen Tube Pressure Low) alarm on HSSF-CAB-CHEM/LAB pannel. <I> **** Actions Taken **** Performed actions listed in CI-14.4 <N> **** Equipment Description **** 487' RW Chem Lab | 02-00-HSSF-CAB-CHEM/LAB
383517 | CR | 20180815 |  | 3 | (QA) Lack of attention to detail in work order planning |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Lack of attention to detail in work order planning- Quality reviewed a mixed sample of 47 Refueling Outage (R -24) planned work orders (WOs) and identified 16 examples in 12 work orders a lack of attention to detail in work order planning. The potential impact is that errors in planned work orders not corrected by the walkdown could cause errors in task performance, delays in completing work and/or inaccurate schedules. See EDMS for additional details. This problem is considered a Deficiency identified during R-24 Outage Work Order Quality Surveillance, SR-18-15. Quality recommends that this CR be routed to Maintenance Planning department AR-MNTPLAN. <I> **** Actions Taken **** Discussed these issues with the Maintenance Planning Supervisor and most have been corrected and the others will be corrected as time permits.
383518 | CR | 20180815 |  | 3 | (QA) Parts not ordered for R-24 work order tasks |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Parts not ordered for R-24 work order tasks. Quality reviewed a mixed sample of 47 Refueling Outage (R-24) planned work orders (WOs) and the required parts were NOT ordered on four tasks in four different WOs. Quality also identified an additional two similar planned WOs with none of the required parts ordered. If not identified during the walkdown or staging for work the parts/materials may not be available to support implementation of the task or cause delays in completing scheduled work. See EDMS for additional details This problem is considered a Deficiency identified during R-24 Outage Work Order Quality Surveillance, SR-18-15. Quality recommends that this CR be routed to Maintenance Planning department AR-MNTPLAN. <I> **** Actions Taken **** Discussed these issues with the Maintenance Planning Supervisor and most have been corrected and the others will be corrected as time permits.
383519 | CR | 20180815 |  | 4 | TEA-FN-52 HEPA FIlter DP above set point | N | N |  | N | YES | <D> **** Detailed Description **** TEA-FN-52 HEPA FIlter dPIS-53 DP above set point <I> **** Actions Taken **** Wrote CR <N> **** Equipment Description **** dPIS-53 | 02-00-TEA-FN-52
383520 | CR | 20180815 |  | 3 | Drawing updates associated with TMU-V-730 branch line needed |  |  |  | N | YES | <D> **** Detailed Description **** The small bore branch line piping configuration associated with TMU-V-730 existing in the field (TMU pump house 365 ft 6 in elevation overhead) is not as depicted on CVI ISO 317-00,4382 and the branch line to TMU-V-730 is not depcited on parent small bore 1"TMU(2)-1 isometric drawings CVI DWG 225-02,32 or CVI DWG 225-04,10. Additionally, the U-bolt hanger on the parent small bore 1"TMU(2)-1 piping in close proximity to the TMU-V-730 branch line is not depicted on CVI DWG 225-02,32 or CVI DWG 225-04,10. See the photos attached to the EDMS of this AR CR 383520. . All the subject small bore TMU piping is adequately supported for the applicable QC 2 SC 2 conditions (Engineering walkdown completed 08/15/18). . The subject piping needs to be as-built and the associated drawings need to be updated as necessary. Field changes associated with BDC 90-0187-0A may be responsible for the discrepancies noted here. Suggest resolution assignment to Mechanical Design & Drafting. <N> This condition was noted in passing while performing field walkdowns associated with AR EVAL 320976. | 02-00-TMU-V-730
383521 | CR | 20180815 |  | 4 | Computer points found out of tolerance | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of 16.2.3 WO# 02105831-01 step 7.2.21 Computer points L108 & X198 zero point found out of tolerance. All other data points with in tolerance. <I> **** Actions Taken **** Informed supervision and operations and wrote CR to document and WR continued with surveillance These computer points are for reference only adn are not procedulaly required per PPM 13.14.11 or PPM 16.2.3. <N> **** Equipment Description **** RW525
383525 | CR | 20180815 | CAQ | D | APRM-CHS-1 input status current found out of tolerance | Y | Y |  | N | YES | <D> **** Detailed Description **** During the performance of ISP-APRM/RRC-B301 under WO 02132156-08 the input status current for "Flow B' was found out of tolerance at the top end of range (20.13mA with a tolerance of 19.90 to 20.10) Step 7.5.16 and 17 <I> **** Actions Taken **** Calibrated into tolerance per procedure, informed supervision and CRS, noted on cover and writing this CR to document <N> **** Equipment Description **** 501 MCR | 02-00-APRM-CHS-1
383526 | CR | 20180815 | CAQ | D | The dialup phone to Benton County is not working | N | Y |  | N | NO | <C> reiopened and rescreened to CAQ by CAP Supervisor <D> **** Detailed Description **** While conducting monthly maintenance the Benton County dialup phone was found inoperable. The CRASH, PIO and FAX phones are operational if communication is needed with the county. <I> **** Actions Taken **** Notified EP and the MCR. Recommend closing to WR. <N> **** Equipment Description **** JIC, A-EOF
383527 | CR | 20180815 | CAQ | D | RCIC-V-103 Leakby | Y | N |  | N | YES | <D> **** Detailed Description **** RCIC-V-103 (RCIC-V-30 Downsteam Drain) was observed to be leaking from its pipecap downstream the valve. <I> **** Actions Taken **** CRS informed. RCIC-V-30 was checked fully shut, valve was able to be shut approx. an additional half turn. Leakage from the pipecap has decreased to approx. a drop every 1-2 minutes with the valve verified fuly shut. | 02-00-RCIC-V-103
383530 | CR | 20180815 |  | 3 | RCIC 2018 LL: STRAIN GAUGE INSTALLATION |  |  |  | N | NO | <D> **** Detailed Description **** Due to the vagaries of installing a strain gauge on the stem of a valve to support motor operator diagnostic testing, there have been several instances of faulted installations noted during the testing of RCIC-MO-46. This is submitted as a lessons learned to determine if there are opportunities for improving the strain gauge installation process, such as additional training, alternative adhesive products, or even alternative strain gauge mounting methods. This is a test equipment issue only, not an equipment issue. Recommend assignment to Engineering Technical Services. <I> **** Actions Taken **** Discussed with valve motor operator program manager. Submitted lessons learned AR-CR.
383531 | CR | 20180815 |  | 4 | D448 communications line indicating intermittent faults. | N | Y |  | N | YES | <D> **** Detailed Description **** The D448 line connects DOE (Hanford) Patrol radio console in the EOF to the TEC from which location a radio signal is then transmitted. The D448 line also connects DOE Safety Console radio system (in EOF MUDAC Area) to the TEC from which location a radio signal is then transmitted. The DOE (Hanford) Patrol radio console & DOE Safety Console radio system are both listed in PPM 13.14.11, EP Equipment, as category â€œBâ€ equipment. The Crash and Commercial phone lines are functional & available to connect & maintain the function of communications from the EOF to the Hanford Patrol Operations Center (POC) and the Hanford Emergency Operations Center (EOC). <I> **** Actions Taken **** Notified EP. The Telecom techs determined through troubleshooting at the TEC that the D448 had a bad power supply. The supply was changed out and the system now checks out good. NCAQ 4. <N> **** Equipment Description **** TEC
383532 | CR | 20180815 | CAQ | D | Received DG3 alarm drop 2-1 GEN RTD HI TEMP. | N | N |  | N | YES | <D> **** Detailed Description **** Received DG3 alarm drop 2-1 GENERATOR RTD HIGH TEMPERATURE. This was a spurious alarm and immediatly reset. "B" phase alarmed and was at 50Â°C. "A" phase was at 56Â°C and "C" phase at 61Â°C. Alarm setpoint is 130Â°C. Room temperature is 87Â°F. <I> **** Actions Taken **** Reset alarm. | 02-00-HPCS-TE-DG3/B1
383533 | CR | 20180815 | CAQ | D | DG3 GEN RTD HIGH TEMP alarm in & cleared | N | N |  | N | YES | <C> duplicate CR 383532 <D> **** Detailed Description **** The DG3 Generator â€˜Bâ€™ channel RTD High Temperature alarm came in for no apparent reason tonight. DG3 had not been started and has been in normal standby lineup all day. The temperatures on HPCS-TIS-DG3 for the three channels were as follows: â€˜Aâ€™ Channel â€“ 56 degrees C, â€˜Bâ€™ Channel â€“ 50 degrees C, â€˜Câ€™ Channelâ€“ 61 degrees C. The alarm set-point for all three channels is GE130 degrees C. The DG3 Electrical Room temperature was around 91 degrees F, and the ventilation systems were in normal line-up and running normally as expected. <I> **** Actions Taken **** informed RO of alarm clearing; wrote AR to document abnormally recieved alarm This is same issues as AR 383532. | 02-00-HPCS-TIS-DG3
383534 | CR | 20180816 |  | 4 | Damaged lock at TMU | N | N |  | N | YES | <D> **** Detailed Description **** Lock on entry gate to TMU was found damaged <I> **** Actions Taken **** Informed MCR, replaced lock with new lock and chain <N> **** Equipment Description **** TMU access gate lock
383535 | CR | 20180816 | CAQ | C | RCIC-MO-46, inconclusive as-left diagnostic data | Y | N |  | N | YES | <D> **** Detailed Description **** During As-Left Diagnostic test of RCIC-MO-46 per WOT 02066077-03, anomalous readings were encountered. Data was reviewed by MOV Component Engineer. There were no issues noted with the as-found data. <I> **** Actions Taken **** Discussed in OCC. | 02-00-RCIC-MO-46
383536 | CR | 20180816 | CAQ | C | Procedure enhancement to OSP-RCIC/IST-Q703 |  |  |  | N | NO | <D> **** Detailed Description **** RCIC-V-76 is a PCIV that has a required closing time (see attachment 9.1 of OSP-RCIC-Q703) however there is # for stroking the valve that is associated with the opening time (step 7.1.7). This # should be associated with the tech spec required closing time (step 7.1.10). This needs to be evaluated for change. <I> **** Actions Taken **** Recommend making an Engineering assignment to ensure this change is correct. Then an assignment to Operations Procedure writers to facilitate the change.
383539 | CR | 20180816 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0068189 RAD Dig. Battery Torque Wrench- model DB -RAD 3000-2 found OOT & adjusted within specs. Not used during Calibraiton cycle. DEF #6725A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
383540 | CR | 20180816 |  | 4 | Worsening B RFT Steam Leak | N | N |  | N | YES | <D> **** Detailed Description **** I was informed to write this CR to pass on the information that the B RFT Steam Leak is worsening. Reference CR#379878 WR#380701. <I> **** Actions Taken **** Doing as I was asked. <N> **** Equipment Description **** Worsening B RFT Steam Leak | 02-00-MS-V-172B
383545 | CR | 20180816 |  | 4 | Override FY18 Performance Appraisal |  |  |  | N | NO | <D> **** Detailed Description **** During the FY18 Performance Appraisal process, 2 supervisors in Operations used the override button to bypass the employeeâ€™s acknowledgement of the document due to the employee(s) being on PT. HR contacted the supervisors and explained an employee being on PT was an unacceptable reason to override the acknowledgement due to procedure (GBP-HR-20). The appraisals were re-opened and the supervisors were instructed the employee would need to acknowledge the appraisal before it would be marked as complete. The supervisor spoke to their management and was given the â€œokâ€ to override the appraisal despite the previous instructions from HR <I> **** Actions Taken **** Upper Management was contacted and it was deemed the appraisal would be marked deficient per procedure and sent back to the supervisors to have the employees acknowledge their appraisals upon return from PT.
383547 | CR | 20180816 | CAQ | C | Potential Trend with Faulted QC Inspections |  |  |  | Y | NO | <D> **** Detailed Description **** An evaluation is warranted to determine if a trend exists, in accordance with TM-01, with faulted QC inspections. A faulted inspection is defined as a condition when a QC inspector incorrectly accepts/signs off a QC hold point regardless of any resulting impact to the station. In other words, an inspection can be faulted regardless if the condition is later accepted or approved as is by engineering or other authority. <I> **** Actions Taken **** Discussed issue with the Quality Manager, CAP Supervisor and Trend Coordinator. Recommend assignment to QA for trend evaluation per Trend Manual 01.
383550 | CR | 20180816 |  | 4 | EPN's on Plant Firewalls inconsistent and confusing |  |  |  | N | YES | <D> **** Detailed Description **** DEH and RFT each have 2 EPN's. 1 for ASA Operating System and 1 for Firepower Intrusion Protection System. NET3 and MET only have 1 EPN that includes both ASA Operating System and Firepower Intrusion Protection System. This causes problems as the ASA Operating System can be upgraded separately from the Firepower Intrusion Protection System. <I> **** Actions Taken **** This CR documents the issue. EC 17309 will correct the issue by creating separate EPN's for the ASA Operating System and the Firepower Intrusion Protection System. No further action required for this CR. | 02-00-MET-SOFT-FW/01,02-00-MET-SOFT-FW/04,02-00-NET3-SOFT-LEFM/FW/01
383558 | CR | 20180816 |  | 4 | TMU North Fish Basket Insert Stuck | N | Y |  | N | YES | <D> **** Detailed Description **** During routine fish entrainment sampling in the TMU Vault, the north basket was not able to be raised the morning of August 16th due to the insert within the cage being stuck. The basket cannot be raised safely with the insert extended. Multiple attempts from Mechanical Maintenance personnel were not able to retract the insert by its designed method. The stuck insert needs to be evaluated and corrected so the study can continue. The Fish Entrainment Study is required under the CGS NPDES Permit which is administered by EFSEC. <I> **** Actions Taken **** Left cage in a safe position and notified E&RP management, Mechanical Maintenance management, and Systems Engineering. Contacted Non-Destructive Examination to schedule time for camera observation. Wrote this CR. <N> **** Equipment Description **** North Fish Basket in the TMU Pumphouse Vault.
383563 | CR | 20180816 |  | 4 | EDR-PROG-1 failed to reset per SOP-RW/EDR-ops | N | N |  | N | YES | <D> **** Detailed Description **** EDR-PROG-1 failed to reset per SOP-RW/EDR-ops. Demis had tripped on spurious hi d/p (wr 29140974). <I> **** Actions Taken **** discussed with FIN and wrote WR. | 02-00-EDR-PROG-1
383564 | CR | 20180816 |  | 3 | HSSF Pumps did not start when required. | N | N |  | N | YES | <D> **** Detailed Description **** On 8/15/2018 Hydrogen Storage Tube pressure lowered to the setpoint (650 psi) to start the HSSF liquid Hydrogen pumps, but neither pump started. Inspection of the facility and the HMI in the control room showed no alarms. <I> **** Actions Taken **** Investigated the PLC and found the "INITIAL START" was not energized. Pressed â€œRESETâ€ and â€œStartâ€ buttons on the Pump Control panel. The â€œSTARTâ€ button is in the "INITIAL START" rung of the logic, when pressed energized the pump start logic and the pump started. | 02-00-HSSF-P-1A,02-00-HSSF-P-1B,02-00-HSSF-PLC-P1
383565 | CR | 20180816 |  | 4 | SMA-FL-1 filter mesh gone | N | N |  | N | YES | <D> **** Detailed Description **** The rolled filters in SMA-FL-1 are no longer in place, fallen down. The filter mesh is past end of roll and the ends are hanging down. Over half of the surface area has no mesh filter in place. CR#381580 WR#29143306 adressed the filter not advancing. Don't know if that has been taken care of. <I> **** Actions Taken **** CR written. | 02-00-SMA-FL-1
383566 | CR | 20180816 |  | 4 | birds nest on top of east side of spare transformer E-TR-N1 | N | N |  | N | YES | <D> **** Detailed Description **** birds nest on top of spare transformer E-TR-N1 that has pulled static ground off terminations for windings. <I> **** Actions Taken **** notified superviser and wrote CR and work request. <N> **** Equipment Description **** down by wharehouse by cable cutting area. | 02-00-E-TR-N1
383567 | CR | 20180816 |  | 3 | As-built & drawing/doc updates needed for PWC-P-5 piping |  |  |  | N | YES | <D> **** Detailed Description **** The mix of small bore carbon steel (CS), copper (CU), and PVC piping physically existing at the TMU pump house in the vicinity of PWC-P-5 does not match that depicted on CVI DWG 225-02,19 or that depicted on CVI DWG 225-02,32. Additionally, the piping configuration depicted on CVI DWG 225-02,32 does not match the common area of piping also depicted on CVI DWG 225-02,19. CVI DWG 225-02,19 and CVI DWG 225-02,32 and AED M507-1 (which points to AED M784 for this piping) all indicate the subject piping is Quality Class 2. However, the MAT'L SPEC (material specification) block on CVI DWG 225-02,19 points to AED SPC 15B.1 page 15B.1-330 which is for Quality Class G (not QC 2) PWC piping. Note 4 on CVI DWG 225-02,19 points to AED SPC 15B.1 page 15B.1-58 for CBD and to AED SPC 15B.1 page 15B.1-153 for TMU material specification information but these pages of the design specification provide design and operating pressure and temperature information, not material specification information. Potentially applicable material specification information for CBD and TMU piping are provided by AED SPC 15B.1 pages 15B.1-200 & 15B.1-201 for CBD and pages 15B.1-380 & 15B.1-381 for TMU. These CBD and TMU material specification pages provide information for carbon steel (CS) and PVC piping but not for copper (CU) piping. CVI DWG 225-02,19 currently indicates the PVC branch line piping above TMU-V-4 is CBD piping but AED MEC M507-1 indicates this piping is TMU(2)-1P (TMU PVC) piping. AED MEC M784 DETAIL H points to CVI 225-02,19 but also should point to CVI 225-02,32. AED MEC M784 DETAIL H does not depict piping material changes ( .g., from CS to PVC or from CS to CU, etc.). Functionality of the subject piping is not in question - Engineering walkdowns already completed. This is a legacy CM issue. Recommend resolution assignment to Design Engineering for as-built, documentation reviews, and drawing/documentation updates as necessary. <I> **** Actions Taken **** This condition was noted in passing while performing walkdown associated with AR EVAL 320976. | 02-00-PWC-P-5,02-00-PWC-V-470,02-00-PWC-V-472,02-00-PWC-V-473,02-00-PWC-V-508,02-00-TMU-V-4
383568 | CR | 20180816 | CAQ | D | TSC Public address not heard in the Deschutes or the MCR | N | Y |  | N | YES | <D> **** Detailed Description **** While testing the TSC public address and alerting tones per WO 02095754 the PA was not heard in Deschutes or the Main Control Room. The alerting tones sounded in all locations. The Control room PA and alerting tone remain fully functional. <I> **** Actions Taken **** Notified: EP and the MCR. Post testing found no problems with the announcements in Deschutes or the MCR. The nature of the problem is unknown. A full test of the area wide PA will need to be rescheduled. Recommend closing to the WR for further testing. <N> **** Equipment Description **** TSC
383569 | CR | 20180816 |  | 4 | Need at least one more Chemical feed pump for tank 41 or42 | N | N |  | N | YES | <D> **** Detailed Description **** CF-P-42A, or CF-P-41A/41B needs repair. Currently the corrosion inhibitor and descaler for CW is running on one pump. The other pumps are not working. If CF-P-42B stops working Operations will have to do batch adds from tank 42 of 50-55 gallons per shift at given an 8 cycle blow down rate (~2000 GPM). One of the other Chemical Feed pumps needs to be repaired so that it can be available in the event the CF-P-42B fails. <I> **** Actions Taken **** Notified shift manager, chemistry management, and chemistry supervision. <N> **** Equipment Description **** CW water pump house | 02-00-CF-P-41A,02-00-CF-P-41B,02-00-CF-P-42A
383570 | CR | 20180816 |  | 4 | Loose or missing tube clips at TMU pump house | N | N |  | N | YES | <D> **** Detailed Description **** See the photos attached to the EDMS of this AR CR 383570. Def Tags hung at/near each Unistrut support with loose or missing tube clips for ~1/2", ~3/8", and ~1/4" tubing. Def Tag 41833 - 3 loose tubing support clips below grating. 1 for 1/2" SS tube from TMU-V-713A. 2 for ~1/4" CU tube to E-IR-29. Def Tag 41834- 2 loose tubing support clips above grating. 1 for ~1/4" CU tube above TMU-FS-7 and 1 for the same ~1/4" CU tube below TMU-SQRT-7B on the east side of E-IR-29. Def Tag 41835 - 1 loose tubing support clip below grating for ~1/2" CU tube downstream of PWC-V-473. Def Tag 41836 - 1 loose tubing support clip below grating for ~1/2" CU tube downstream of PWC-V-473 (different support than Def Tag 41835). Def Tag 41837 - 1 loose ~1/4" CU tubing support clip under grating. Def Tag 41838 - 1 loose ~1/4" CU tubing support clip under grating. Def Tag 41839 - 1 loose ~1/4" CU tubing support clip and 1 loose ~1/2" CU tubing support clip below grating. Def Tag 41840 - Loose ~1/4" CU (two) and ~1/2" CU (one) tubing support clips below grating. Def Tag 41841 - Missing ~1/4" CU (two) and ~1/2" CU (one) tubing support clips for two Unistrut supports (one support on either side of the Deficiency Tag) below grating. Def Tag 41843 - Partially missing ~1/2" CU tubing tube clip and loose ~1/4" CU tubing tube clip below grating. Def Tag 41844 - Loose ~1/4" CU tubing tube clip adjaceent to MWHV-2 above grating. Def Tag 41845 - Loose ~3/8" CU tubing tube clip next to PMA-DPS-81B low side valve above grating. . Each of these deficiencies should be corrected but they are not presently posing any threat to continued functionality of the associated QC 2 SAC 2 tubing. Loose support clips are still providing deadweight restraint and locations with missing support clips are not presently experiencing excessive sag (vertical deflection). <N> This issue was noted in passing while performing field walkdowns associated with AR EVAL 320976. | 02-00-M-BLDG-MISC
383572 | CR | 20180816 |  | 4 | TMU-V-713B 3/4" CS piping and 1/2" SS tubing support clip | N | N |  | N | YES | <D> **** Detailed Description **** The 3/4" carbon steel (CS) inlet pipe nipple to TMU-V-713B is visibly bent upward ~1.5 inches and the tube clip for the closest Unistrut support for the 1/2" OD stainless steel (SS) tubing downstream of TMU-V-713B is missing (and cannot be installed due to the deformed nature of the 3/4" inlet pipe nipple to TMU-V-713B). See the photos attached to the EDMS of this AR CR 383572. Def Tag 41842 hung in the field at TMU-V-713B (below the 375' elevation grating on the west side of TMU-P-1B). . From its appearance, this condition is old damage (possibily from original installation of TMU-P-1B during plant construction) and has not caused any functionality problems for associated SSCs. <I> **** Actions Taken **** This condition was noted in passing while performing field walkdowns associated with AR EVAL 320976. | 02-00-TMU-V-713B
383573 | CR | 20180816 | CAQ | D | Lightning protection RX building roof. Rod #2 | N | N |  | N | NO | <D> **** Detailed Description **** During work under work order # 02105750-01 craft discovered that rod #2 was laying on roof. Appeared to have been over tightened during the install. Craft repaired per work instructions. During the replacement craft snug tightened the new brass adapter and it also broke. Craft was able to utilize the broken reducing coupling as a reducing bushing. And was able to fully ingage all threads of rod for a tight connection. <I> **** Actions Taken **** Notified supervision and Control room. Wrote this CR <N> **** Equipment Description **** Reactor Building 606' roof lightning protection.
383574 | CR | 20180816 |  | 3 | G-101 does not address Environmentally Qualified equipment |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** While preparing to replace a switch in the plant, we noticed it had an orange EQ tag on it. Reviewing â€œUse of Itemsâ€ G-101, we could not see where it addressed Environmentally Qualified equipment. Shouldnâ€™t there be a section for this? <I> **** Actions Taken **** stopped and contacted supervisor. Procurement assisted us in verifying EQ status
383575 | CR | 20180816 |  | 3 | ESP-EPS3E3F-S901 NEEDS REVISION |  |  |  | N | NO | <D> **** Detailed Description **** ESP-EPS3E3F-S901 NEEDS REVISION to comply with plant status control. See EDMS for additional details. <N> Procedure has been uploaded to the Maintenance Procedure Database and will be worked at the next major revision. Procedure link located in the EDMS of this AR.
383576 | CR | 20180816 | CAQ | C | EWD-46E-239 has an error on circuit 42. |  |  |  | N | NO | <D> **** Detailed Description **** EWD-46E-239 is a Top Tier drawing and incorrectly lists the service of E-DISC-PP7AE/42 as CMS-SR-20 Inlet Line Standby Heat Trace. This service is actually the Normal heat trace per the MEL D030 panel and AED ELC E939. Please verify and then correct EWD-46E-239. See drawing markup in EDMS. <I> **** Actions Taken **** Informed supervisor and wrote this AR/CR. <N> Approved for Closure by Acting Supervisor, Jim Hysjulien.
383577 | CR | 20180816 |  | 4 | Poorly supported 1/2" PVC piping TMU-V-109 to TMU-SR-1 | N | N |  | N | YES | <D> **** Detailed Description **** The QC 2 SC 2 nonsafety-related 1/2" PVC piping associated with TMU-V-109 to TMU-SR-1 (TMU pump house elevation 365 ft 6 in) is poorly supported. See the video and photos attached to the EDMS of this AR CR 383577. No detail documentation tied to these EPNs in Portal J for this PVC piping could be identified but it is expected that CVI documentation should exist for it in Portal J. It appears that a N-S lateral restraint for the PVC piping above TMU-SR-1 should be installed. The subject PVC piping was walked down by Engineering and though poorly supported remains functional in its existing configuration. For resolution, a lateral support for the piping as described above should be installed. <I> Def Tag 41846 hung at TMU-V-109. <N> This condition was noted in passing while performing field walkdowns associated with AR EVAL 320976. | 02-00-TMU-SR-1
383578 | CR | 20180816 | CAQ | C | FPC-LIS-2B not replaced after C/O was hung |  |  |  | N | NO | <D> **** Detailed Description **** D-FPC-LIS-2B-001 C/O was hung to support replacement of FPC-LIS-2B. Currently installed LIS was found with an EQ tag hanging on it, but the work package was not planned with EQ replacement requirements. FPC-LIS-2B was not was not disturbed and C/O was released to OPS to lift with no work performed. <I> **** Actions Taken **** Stopped and contacted OPS, Engineering, planning and supervision.
383579 | CR | 20180816 | CAQ | D | FP-PI-7 reading high/erratic | N | Y |  | N | YES | <D> **** Detailed Description **** During FP-P-110 run, FP-PI-7 indicated 240# at 15min logs. While informing supervision it returned to band at 30#. CRS approved to finish the run. Band is 10-60#. <I> **** Actions Taken **** Informed CRS | 02-00-FP-PI-7
383580 | CR | 20180816 |  | 4 | TMU pump house degraded cabinet - 356'-6" platform | N | N |  | N | YES | <D> **** Detailed Description **** During field walkdown associated with AR EVAL 320976, an apparently permanent but visibly degraded cabinet in the northeast corner of the elevation 356 ft 6 in platform grating (below the TMU pump pedestals on elevation 365 ft 6 in) was noted to exist. The doors to the cabinet are not closed and the cabinet contains both electrical and pneumatic components including a nitrogen bottle - electrical components appear to be 'off'. This elevation of the TMU pump house can be under water when the Columbia River is flooding. The subject cabinet and its contents have not been provided with field labeling and Portal J searches have failed to identify CVI or AED documentation describing it. The 1/2" tubing to the subject cabinet penetrates into the TMU pump house east of TMU-P-1C on elevation 365 ft 6 in and also apparently also routes to tubing associated with TMU-LT-7. See the photos attached to the EDMS of this AR CR 383580. | 02-00-M-BLDG-MISC
383581 | CR | 20180816 |  | 4 | ASD glycol resistivity low | N | N |  | N | YES | <D> **** Detailed Description **** GY-CI-10A1, 10B1, 10B2; are below resistivity spec of 5 ohm GY-CI-10A2 was written up 6 days ago is now below resistivity of 4 ohms. These filiters need to be changed. <I> **** Actions Taken **** Informed CRS | 02-00-GY-CI-10A1,02-00-GY-CI-10B1,02-00-GY-CI-10B2
383582 | CR | 20180816 |  | 4 | Broken brace end bracket for TMU pump house fence | N | N |  | N | YES | <D> **** Detailed Description **** A broken central brace end bracket for the TMU pump house fence (location is the panel immediately west of the access gate) was noted to exist. See the photos attached to the EDMS of this AR CR 383582. Please replace this broken end bracket for the TMU pump house fence brace. <N> This condition was noted in passing while performing field walkdown associated with AR EVAL 320976. | 02-00-M-BLDG-MISC
383584 | CR | 20180816 | CAQ | C | (QA) eWP WOTs Missing 10CFR73.58 Security Actions |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Electronic Work Package (eWP) Work Order Tasks (WOTs) do not contain the required compensatory or mitigative actions resulting from the 10CFR73.58 reviews by Security. This information is required by SWP-SEC-14 â€œSafety/Security Interface Programâ€ and is located within PassPort on panel TIMM105 for each WOT. These compensatory or mitigative actions print out on the old paper WOT under the â€œTask Special Requirementsâ€ section, but do not transfer over into the new eWP WOT. The craft worker or his supervisor cannot tell from looking at the eWP WOT to notify security to perform their compensatory or mitigating actions prior to the performance of the work as required by 10 CFR 73.58. There are no known examples where work began before security performed their required compensatory or mitigating actions. Factual Basis: see details in EDMS Insights: â€¢ The Condition Report (CR) 380569 (initiated on 5/25/18) identified this 10CFR73.58 security issue among several other eWP problems; however, the assignment list still does not contain a corrective action to address this 10CFR73.58 issue, and this CR has a low Priority of non-CAQ (Severity 3). â€¢ The concern is that there is currently no known documented bridging strategy to ensure a craft worker or his supervisor will notify security to perform their compensatory or mitigating actions prior to the performance of the WOT, in order to fully comply with SWP-SEC-14. â€¢ An IS Analyst explained that these â€œRequirementsâ€ fields in PassPort were planned be transferred over to the eWP WOTs by the end of 2018 as a part of the eWP Phase II project, but the completion date is to be moved up a couple months based on the concerns above recently expressed by Quality to IS. <I> **** Actions Taken **** Discusssed with Assistant Information Services Manager. Recommend assignment to Information Services. . This deficiency was identified in Quality audit AU-SE-18. <N> **** Equipment Description **** N/A | FW-00-SOFT-COTS-DG/DOCPLUS
383586 | CR | 20180816 |  | 4 | ILC Training lost time due to a thor abort |  |  |  | N | NO | <D> **** Detailed Description **** Scenario LO000016B was loaded and could not be run due to a THOR cell problem (160) <I> **** Actions Taken **** Stopped training, informed Sim supervisor and initiates SR 2783. Scenario will be performed at a later date.
383587 | CR | 20180817 |  | 3 | IPM-9 TRAFFIC LAMPS | N | N |  | N | YES | <D> **** Detailed Description **** WHILE PERFORMING W/O # 02107533-02 PPM 10.24.218 STEP 7.6.2. THE RED LAMP IS BURNT OUT COULD NOT LOCATE A REPLACEMENT.THIS UNIT IS NOT THE SAME AS THE IPM-8 AND USES A DIFFERENT BULB.THIS IPM-9 STILL FUNCTIONS PROPERLY WITH ONE OF THE TWO TRAFFIC LIGHTS BURNT OUT. <I> **** Actions Taken **** E-MAILED MIKE KINMARK TO GET REPLACEMENT BULBS TOLD MY SUPPERVISOR AND WROTE THIS CR <N> **** Equipment Description **** BLDG 13 | 02-00-HP-EQ-42714
383588 | CR | 20180817 |  | 2 | Potential Clearance and Tagging violation |  |  |  | N | YES | <D> **** Detailed Description **** While performing packing consolodation on RCIC-V-46 under WO 02034759-07 the work group decided we needed to remove the packing gland follower and then remove a carbon bushing. Upon doing so, RCIC keep fill pressure (approx. 80 psi) displaced the valve packing and approximately 2 gallons of water to the RCIC room. The water and room were verified to be free of contamination. <I> **** Actions Taken **** Backseated valve manually to stop leak. Stopped work, informed OCC and MCR. Performed initial investigations and took statements. Held stand down with all onsite maintenance personel, engineering personel, and OCC staff. ***General Notes*** All written statements have been loaded into the EDMS of this AR. Risk Level Medium due to potential injury to craft. Cause is clear an event investigation was conducted and the following cause was identified. Craft, and supervisor did not use HU tools when the plan changed in the field. <N> **** Equipment Description **** RX. 422 | 02-00-RCIC-V-46
383589 | CR | 20180817 |  | 4 | SEC-XD-05 | N | N |  | N | YES | <D> **** Detailed Description **** SEC-XD-05 is not functioning as designed. Contact security at EXT. 2185 for further details. <I> **** Actions Taken **** Unit taken out of service, security notification made and WR generated. This item is not reportable. | 02-00-SEC-XD-5
383593 | CR | 20180817 | CAQ | D | IRE needs maintenance | N | N |  | Y | YES | <D> **** Detailed Description **** contact security prior to work <I> **** Actions Taken **** CR/WR security supervision notified/compensatory in place | 02-00-SEC-IDS-PAAP/IR/E/M
383595 | CR | 20180817 | CAQ | D | PAAP IR E and JBT Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** The PAAP IR East and JBT requires maintenance. Contact 2185 for more information <I> **** Actions Taken **** Security Supervision notified. Initiate CR/WR. | 02-00-SEC-IDS-PAAP/IR/E/M
383596 | CR | 20180817 | CAQ | D | CCH-CR-1a has a small oil leak. | Y | Y |  | N | YES | <C> CR reopened to cross reference additional W0 02124707, marked completion required box, then taken back to complete <D> **** Detailed Description **** Found a small pool of oil under CCH-CR-1A, traced the oil back to what appears to be a oil cooling pipe flange to the chiller. It is right under the heater with "oil heater #3" tag on it. please see attached pictures. will wipe up oil later in shift (friday). This is not a large oil leak and I dont think it will affect operability. <I> **** Actions Taken **** informed MCR | 02-00-CCH-CR-1A,02-00-W-BLDG-MISC
383597 | CR | 20180817 |  | 4 | SA-C-1 had a trail of oil coming away from it | N | N |  | N | YES | <D> **** Detailed Description **** SA-C-1 had a trail of oil coming away from it. further investigation showed that it was leaking down from the track on the right hand door which had standing oil in it. please see pictures attached. the same leak or trail of oil had previously been identified under CR 373947/WR 29139928 with the deficiency tag still hanging. <I> **** Actions Taken **** ?????? | 02-00-SA-C-1,02-00-W-BLDG-MISC
383598 | CR | 20180817 |  | 4 | Duct tape and masking tape is worn and coming up batt. rm 2 | Y | N |  | N | YES | <D> **** Detailed Description **** Duct tape and masking tape is worn and coming up in battery room 2. Tape has been there a long time. Almost as if it isnt needed any more and wasnt removed at the end of a job. request it either be replaced, removed or made permanant <I> **** Actions Taken **** wrote cr Looking at the photo attached to the EDMS of this AR CR, these floor markings are associated with a past rebar scan activity (e.g., to identify embedded rebar locations to support installation of concrete anchors per PPM 10.2.23). <N> **** Equipment Description **** battery room two RW 467, vital island | 02-00-W-BLDG-MISC
383599 | CR | 20180817 |  | 4 | SA-TI-3 reading hoos. | N | N |  | N | YES | <D> **** Detailed Description **** SA-TI-3 reading hoos. this was documented under CR 362043 and WR 29133825 which are both closed. Please adjusted TCV again and watch. <I> **** Actions Taken **** ? | 02-00-SA-C-1
383600 | CR | 20180817 |  | 4 | E-TR-N2 Cooling Fan High Vibration - Bearing Issue | N | N |  | N | YES | <D> **** Detailed Description **** Cooling fan for E-TR-N2 has a bearing issue causing increased noise and vibration. With the amount of vibration, the bearing is likely very damaged. Fan is on bottom left of North set of fans. See CR for another fan which failed and had issues with finding adequate replacements (CR 357878 from 11/16/2016). See attached photo for exact fan location. <I> **** Actions Taken **** Notified CRS and initiated CR/WR <N> **** Equipment Description **** North set of fans (bottom left fan) | 02-00-E-TR-N2
383601 | CR | 20180817 | CAQ | D | SFS-STORM-25/3 reading low while performing ICP-SFS-A301 | Y | N |  | N | I DONT KNOW | <C> CR reopened to cross reference AR 00391862 and additional WP 02135153 and marked completion required box, then taken back to complete <D> **** Detailed Description **** While performing ICP-SFS-A301 (WOT 0212027901) the reading on SFS-STORM-25/3 was reading apporx 25 deg F. average temerature for the cask RTD's is about 100 deg F. Believe the RTD is going bad or a bad connection. This will not negate ICP-SFS-A301. <I> **** Actions Taken **** notified supervisor and created CR/WR to investigate the problem. <N> **** Equipment Description **** SFS-STORM-25/3 SFS-STORM-25/3 is not an EPN in Portal J and does not exist in ICP-SFS-A301.
383602 | CR | 20180817 | CAQ | C | E-IR-67 has a second closure bracket thats not functioning | Y | N | N | N | YES | <D> **** Detailed Description **** E-IR-67 has a second closure bracket that is not functioning. Previously the upper left closure bracket on the HELB Barrier was identified as broken WR, 29117770, CR 318887. Today the lower right corner bracket was unable to be tightened. It appears the backing nut is missing from the assembly. Recommend adding this repair to the work order (02067478) that is being planned to repair the upper left bracket. | 02-00-E-IR-67
383603 | CR | 20180817 |  | 3 | Medical Isotope |  |  |  | N | NO | <D> **** Detailed Description **** A qualified RAD worker received a medical isotope on 8/15/18 at approximately 0930. The individual showed up to work on night shift, and wore their DLR for the duration of the shift. The individual and their supervisor recognized that they had not informed Health Physics of the medical procedure. They proceeded to contact HP the following shift on 8/17/18, and HP informed the individual that they would be restricted from the RCA until the medical isotope fully decayed. The individual and supervisor were coached on the proper process to follow when receiving a medical isotope. <I> **** Actions Taken **** Informed HP supervision of the incident, and followed all steps necessary in HPI-12.96.
383605 | CR | 20180818 |  | 3 | RW507 Resin barrel handling area needs better identification |  |  |  | N | YES | <D> **** Detailed Description **** The area at CF-TK-34 (on RW507) where deep-bed resin barrels are handled during a deep-bed recharge needs better identification for keeping that area clear of any item that prevents Operators from performing this tasks. The floor needs to be painted and labeled in such a way as to keep this area clear. The piping currently in this area needs to be re-located. | 02-00-CF-TK-34,02-00-W-BLDG-MISC
383606 | CR | 20180818 | CAQ | D | RCIC-V-50 will not open | Y | N |  | N | YES | <D> **** Detailed Description **** While lifting tags for D-RCIC-V-46-001, RCIC-V-50 would not OPEN. Closing RCIC-42-S21A8A, it was noted that light for valve position indicated closed for RCIC-V-50. Using RCIC-RMS-V/50, going to OPEN position; there was no relay clicking or contact closing. Switch provided no resistance to movement, after approximately 10 seconds there was no change in indications. With CRS direction, attempted to reset thermal overloads; no resistance felt and no relay or contact noise was heard. A second attempt at RCIC-RMS-V/50 was made with no relay or contact noise, and no change in valve indication. <I> **** Actions Taken **** MCR staff and OCC informed. | 02-00-RCIC-V-50
383607 | CR | 20180818 |  | 3 | RCIC system outage lessons learned |  |  |  | N | YES | <D> **** Detailed Description **** During RCIC system outage in August 2018 there are some examples where rework was needed to be performed. RCIC-V -46 was repacked 3 times. During diagnostic testing strain gauges were installed and removed at least 4 times. The purpose of this CR is to develop actions to prevent reoccurrence in future maintenance window. <I> **** Actions Taken **** Documented items in CR and provided feedback to CMPM for safety system window critique. . This CR is being tracked under the rework program in maintenance. No additional actions are required. Per Maintenance Support Supervisor/Maintenace Support Specialist . <N> **** Equipment Description **** RX 422 | 02-00-RCIC-V-46
383610 | CR | 20180818 | CAQ | C | RCIC-42-8A2B (RCIC-V-50) missing control wire jumpers | Y | N |  | N | NO | <D> **** Detailed Description **** An investigation was performed to determine why RCIC-V-50 would not operate from the control switch (reference CR# 383606). Found two missing wire jumpers in the control circuit at the MCC bucket (RCIC-42-8A2B). This bucket was replaced earlier this week with a new NLI bucket per WO# 02035897; cycling RCIC-V-50 was part of the PMT for this task. A review of both the bench test (02) and the installation task (01) indicated a discrepancy between the two work packages regarding direction to install the jumpers; each indicating that the jumpers would be installed in the other. <I> **** Actions Taken **** Wrote CR - Notified OPS Created Task 14 to install the missing wire jumpers. | 02-00-RCIC-42-8A2B,02-00-RCIC-V-50
383611 | CR | 20180818 |  | 4 | 4.COND.DM 1-10 system outlet high conductivity alarm | N | N |  | N | YES | <D> **** Detailed Description **** At about 0540 4.COND.DM 1-10 system outlet high conductivity alarm was received. THere were several spikes over a 3-5 minute period. S-CIT-201 was also referenced and it confirmed the spike. After the time period conductivity went back to the original steady state value. <I> **** Actions Taken **** Informed CRS and Chemistry. | 02-00-S-CR-24
383612 | CR | 20180818 | CAQ | D | P601.A4.6-8 alarm (RCIC MOV NETWORK PWR LOSS/OL) | Y | N |  | N | YES | <D> **** Detailed Description **** RCIC MOV NETWORK PWR LOSS/OL BISI and RCIC DIV 1 OUT OF SERVICE alarm in with all applicable disconnects closed and overloads verified reset. <I> **** Actions Taken **** Reverified disconnect positions and overloads by the ARP, the control power fuses may need to be checked. | 02-00-RCIC-DT-1
383613 | CR | 20180818 |  | 4 | Hydrogen Leakage over 7 days >500 ft3 | N | N |  | N | NO | <D> **** Detailed Description **** Hydrogen leakage average over the last 7 days is 642.86 ft3, with a max of <500 ft3 per the OPS 3 logs. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** TG 441 W Hydrogen skid | 02-00-E-GEN-1
383614 | CR | 20180818 | CAQ | D | Leakage at RPS-PS-5A | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02110798 and WR 29145493, then taken back to complete CR reopened to cross reference AR 368629 then taken back to Complete <D> **** Detailed Description **** The cabinet that contains RPS-PS-5A and MS-PS-3A has a slow leak. This buildup has been noticed, and an included picture shows how much leakage has accumulated. This is a slow buildup, as the general amount of oil has increased slowly over a year-long period. This CR is being written for trending purposes, or for an investigation to be performed whenever conditions are met to go into this cabinet. <I> **** Actions Taken **** CR written. <N> **** Equipment Description **** TB 471 E | 02-00-MS-PS-3A,02-00-RPS-PS-5A
383615 | CR | 20180818 |  | 3 | Procedural Enhancement SOP-RCIC-TRANSFER-QC |  |  |  | N | NO | <D> **** Detailed Description **** Recommend a NOTE be added to SOP-RCIC-TRANSFER-QC to say, "This procedure section assumes that RCIC is operating. Nowhere in that procedure does it mention that RCIC should be in operation.
383616 | CR | 20180818 | CAQ | D | SEC-IDS-2 3 Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** CAS recieved a malfunction alarm on on IDS 2 3. <I> **** Actions Taken **** Compensatory measure was posted. Walk down of the area was conducted. Shift manager, OCC, and electricians notified. CR/WR generated. | 02-00-SEC-IDS-E/S/2/3
383617 | CR | 20180818 |  | 4 | Operations vehicle has a failed Passenger side High Beam |  |  |  | N | NO | <D> **** Detailed Description **** The Operations Vehicle (F350) has a failed Passenger side High Beam light. All other flashers and lights were verified to be working. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** Operations F350 pickup, normally parked in front of PAAP
383618 | CR | 20180818 |  | 3 | Procedure enhancement OSP-RCIC/IST-Q701 |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** on step 7.1.1 C it states remove 1/2" NPT from RCIC-V-705 on step 7.1.1 D it states install a quck connect fitting on RCIC-705 (3/4" pipe) Both C,D should have 3/4 inch NPT <I> **** Actions Taken **** Notified supervisor and SSS | 02-00-RCIC-V-705
383619 | CR | 20180818 |  | 3 | AR CR for tracking formal work package closure - INFO ONLY |  |  |  | N | NO | <D> **** Detailed Description **** WOT 02066077-01 for RCIC-V-46 Refurb/ was at working status with two superseded copies of the work instructions. Upon review of DataGlance, it was noted that the original checked in task 01 had all the signatures besides the "Sign Off Clearance". The new active electronic package was blank. This issue was being tracked in the OCC for proper package closure. It was verified that indeed the local clearance and the danger clearance for the work had been lifted. Per discussion with OCC to avoid losing any signed off copies, the work was statused to Field Work Complete, to allow for the task to be closed but still opened in the future to address formally closing out in DataGlance. Prior to taking to "Field Work Complete", the three versions in DataGlance were reviewed and all work steps were the same with no outstanding signatures besides signing off Clearance Order. <I> **** Actions Taken **** Statused work task and generated CR as directed for documentation. <N> There is no issue with the functionality of DataGlance. Upon discussion with Maintenance, it was found this CR was written to notate that work was not showing done in DataGlance. | 02-00-RCIC-V-46
383620 | CR | 20180818 |  | 3 | Procedure enhancement OSP-RCIC/IST-Q701 |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** while retuning to service noticed on step 7.2.120 C it states to remove 1/2 swedgelock. also step D says install 1/2 plug. Back on step 7.1.1 D it said to install a quick connect on a 3/4" pipe? Maybe remove the size from step 7.2.120 C, D? <I> **** Actions Taken **** Notified supervisor | 02-00-RCIC-V-705,02-00-RCIC-V-706
383621 | CR | 20180819 | CAQ | D | RCIC-PI-16 root isolation valve leaks by its seat | Y | N |  | N | YES | <D> **** Detailed Description **** During the 2018 RCIC system maintenance window, it was identified that the root isolation valve for RCIC-PI-16 leaks by its seat. This deficiency was evaluated in CR 383456 to not result in a condition which would make RCIC inoperable, but was not corrected during the maintenance window. This CR is written to track the OBDN condition. <I> **** Actions Taken **** Wrote this CR | 02-00-RCIC-PI-16,02-00-RCIC-PIS-1,02-00-RCIC-PIS-34,02-00-RCIC-V-758
383622 | CR | 20180819 |  | 4 | TG Sump pillows require changing per WO# 02123246-01 |  |  |  | N | YES | <D> **** Detailed Description **** T1: Has pieces of the foam pillow floating on top of the water. Water and pillow are both clean though. T2: Both pillows are clean, however, the water surface is dirty and oily. May need to add a third pillow to clean this water. T3: Both pillows require changing. T4: Both pillows are clean, but they are hanging by their ropes 5 or 6 feet above the water, so they are not performing their intended function. T5: Both pillows are oily around their outer edges and may require changing. T6: One pillow is hanging several feet above the water by its rope, the other pillow has no rope securing it and is floating on top the water and it requires changing. T7: Both pillows are very rusty and oily and require changing. <I> **** Actions Taken **** wrote AR / WR; informed Shift Supervisor <N> **** Equipment Description **** TG Building Sumps T1, T2, T3, T4, T5, T6, T7 | 02-00-EDR-SUMP-T6,02-00-FD-SUMP-T1,02-00-FD-SUMP-T2,02-00-FD-SUMP-T3,02-00-FDR-SUMP-T4,02-00-FDR-SUMP-T5
383623 | CR | 20180819 |  | 3 | Fire alarm panel changes not in surveillance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Fire alarm panel changes not in surveillance WO 02100595-01 when the alarm was to be flagged it was noticed the alarm was in a new location on the panel it was H13-FCP3.23.2 and it is now H13-FCP3.16.5 procedure needs to be updated in the precautions and limitations and prerequsites. <I> **** Actions Taken **** notified supervisor
383624 | CR | 20180819 |  | 3 | Need to add T1, T3, T6 sump pillow checks to existing WO. |  |  |  | N | NO | <D> Need to add the T1, T3, T6 sump pillow checks to the existing Work Order, so all TG Building sump pillows will get checked monthly and at the same time. Currently, the sumps that are checked are T2, T4, T5, T7. The others mentioned need included. <N> CR found at INPROG, moved to Approved status. | 02-00-EDR-SUMP-T6,02-00-FD-SUMP-T1,02-00-FD-SUMP-T3
383626 | CR | 20180819 |  | 4 | RWCU-FT-89B making pulsating noise | N | N |  | N | YES | <D> **** Detailed Description **** RWCU-FT-89B making pulsating cyclic noise, may be connected with leakby on HP drain that is written up previously AR 357863 & WR# 29131985. Noise has gotten significantly worse since this other AR was written. <I> **** Actions Taken **** Informed MCR and Supervision. Initiated AR. | 02-00-RWCU-FT-89B
383627 | CR | 20180819 | CAQ | D | FP-B0-110A cover handle (east) cracked and screw sheered | N | Y |  | N | YES | <D> **** Detailed Description **** FP-B0-110A cover handle (east) cracked and screw sheered. Cover is still intact and does not effect covering the battery. Found while performing WO 02123252-01. | 02-00-FP-B0-110A
383628 | CR | 20180819 | CAQ | D | Reactor Building Stack Critical Failure due to plugging | N | Y |  | N | YES | <D> **** Detailed Description **** At 1527 on 8/19/18 the MCR received the Reactor Building Stack Critical Failure alarm (H13-P851.S2.2-4). Investigation revealed that PRM-FU-4A had high D/P (likely due to the heavy concentration of wildfire smoke in the air) which resulted in PRM-SR-2 low flow. The Shift Chemist shifted to PRM-FU-4B per WR 29144033, flow was restored to normal and the Reactor Building Stack Critical Failure alarm is clear. | 02-00-PRM-FU-4A
383629 | CR | 20180819 | CAQ | D | REA-FU-2A Moisture Separator REA-MS-2A Diff High Alarm | N | Y |  | N | YES | <D> **** Detailed Description **** Reactor building HVAC A trouble alarm was received upon investigation Moisture separator REA-MS-2A Differential High alarm was in at the local panel. REA-DPIS-2A1 was reading 1.275â€ H2O the alarm setpoint is 1.25â€ H2O however the alarm cleared. The high setpoint on REA-DPIS-2A1 (orange needle) appeared to be set at 1.3â€ H2O. This issue was previously reported in WR 29138581 and scheduled to be worked 10-30-18 per WO 02119701. Swapped to REA-FN-2B per ARP 4.RBHV.A. Recommend verifying high setpoint on REA -DPIS-2A1 <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RX 572' | 02-00-REA-DPIS-2A1
383630 | CR | 20180819 | CAQ | D | RCIC-V-50 did not operate from E-MC-8A | Y | N |  | N | NO | <D> **** Detailed Description **** This CR is being written to ensure an IOD is performed on the RCIC system due to RCIC-V-50 inoperability. This deficiency is tracked via CR 383606 and 383610. RCIC-V-50 bucket is missing jumpers that allow operation from E-MC -8A. RCIC-V-50 was operated manually to support surveillance testing. <I> **** Actions Taken **** CR written | 02-00-E-MC-8A,02-00-RCIC-V-50
383631 | CR | 20180819 |  | 3 | MCR CRO2 computer will not print tags | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** PC -- 1053v12 ESOMS will not print tags to any tag printer location tagout sheets print fine <I> **** Actions Taken **** restarted and shut down / restarted the PC and no change was noted in performance <N> 8/20/18-Contacted MCR to have them re-boot the computer. It was confirmed that after the re-boot issue was resolved. Printing to tag printers was re-established.
383632 | CR | 20180819 |  | 3 | MCR equip tag printer broken still (GT 2 months) | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Zebra ZT510 equipment tag printer in main control room from previous discussions it appears this may be a network card issue - remains unresolved after several months
383633 | CR | 20180819 |  | 3 | SLOP drum has excessive oil | N | N |  | N | YES | <D> **** Detailed Description **** common SLOP drum outside COND-HX-9 bay has more oil in it than normal as reported by Laborer. OPS 3 reports the TO-DPIS-10 at 0.8"H2O Did not enter at this time to see which bearing(s) might be source. <N> **** Equipment Description **** SLOP common gathering barrel by CST valves on TG 441' west | 02-00-MS-DT-1A,02-00-MS-DT-1B,02-00-MS-DT-1C,02-00-T-BLDG-MISC
383634 | CR | 20180819 |  |  | Security Camera Cleaning |  |  |  | N | YES | <D> **** Detailed Description **** Security Cameras needing cleaning. <I> **** Actions Taken **** CAS generated list, notified supervision, WR/CR generated <N> **** Equipment Description **** Cameras located inside the PA. | 02-00-SEC-CCTV-1,02-00-SEC-CCTV-10,02-00-SEC-CCTV-11,02-00-SEC-CCTV-12,02-00-SEC-CCTV-13,02-00-SEC-CCTV-28,02-00-SEC-CCTV-32,02-00-SEC-CCTV-4,02-00-SEC-CCTV-7,02-00-SEC-CCTV-8,02-00-SEC-CCTV-9
383635 | CR | 20180820 |  | 4 | Security Cameras needing cleaning | N | N |  | N | YES | <D> **** Detailed Description **** The following Security cameras needing cleaning: 12/12T, 11/11T, 10/10T, 9/9T, 8/8T, 7/7T, 4/4T, 32/32T, 12/12T, 13/13T, 1/1T <I> **** Actions Taken **** CAS generated list, notified supervisor, CR/WR generated <N> **** Equipment Description **** varias cameras inside the PA
383636 | CR | 20180820 |  | 4 | ROA-HV-1 base of unit rusted out with water leaking out. | N | N |  | N | YES | <D> **** Detailed Description **** ROA-HV-1 the bottom base has signs of rust on all sides with water leaking out onto floor. Large puddles forming, but water is draining into the floor drains. <I> **** Actions Taken **** Informed HP of water on floor. Informed CRS. | 02-00-ROA-HV-1
383637 | CR | 20180820 | CAQ | D | M&TE Rejected | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0065276 CSI Accelerometer- model A0760GP found OOT & Rejected- Unable to adjust. EFIN Eval: Data used for performance monitoring only. No operability data taken. DEF #6722A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
383640 | CR | 20180820 |  | 3 | Configuration Details Provided by Vendor Were Not Accurate |  |  |  | N | NO | <D> **** Detailed Description **** Design Configuration Information provided by the new Radwaste chiller vendor was not accurate. The configuration of the chiller feet included in the vendor supplied information does not agree with the as-built configuration observed during Factory Acceptance Testing (FAT). . This issue is associated with the new, not yet installed, replacement chiller (WCH-CR-51A) to be installed under EC 17099. It does not affect any equipment currently installed in the plant. . The configuration differences include the chiller feet being mounted on a 1â€ thick plate with different anchor bolt locations than depicted in the vendor information. This will most likely result in a Field Change Request (FCR) to EC 17099. The replacement chiller pedestal design as issued under EC 17099 is not acceptable because of these differences. . This issue was identified by the Project Manager during the Factory Acceptance Testing for the replacement chiller WCH-CH-51A (EC 17099). Recommend this CR be routed to AR -CMC for resolution. . This issue was discussed with the Project Manager and Mechanical Civil Stress Design supervisor. <I> **** Actions Taken **** This issue was discussed with the Project Manager and Mechanical Civil Stress Design supervisor. Initiated this CR | 02-00-WCH-CR-51A
383647 | CR | 20180820 | CAQ | D | CRD-F-2B (cuno filter) T handle leaking oil. | N | N |  | N | YES | <D> **** Detailed Description **** Found CRD-F-2B T handle used for rotating cuno filter is slowly seeping oil out of its packing. <I> **** Actions Taken **** Informed MCR, initiated AR/WR. | 02-00-CRD-F-2B
383650 | CR | 20180820 | CAQ | C | Incorrect wording - FSAR 3.6.1.20.3.6 |  |  |  | N | YES | <D> **** ANONYMOUS CR - Detailed Description **** FSAR 3.6.1.20.3.6 indicates that the turbine building has a basement. The turbine generator building at Columbia does not have a basement. The TMU transformers are on the ground floor elevation of the turbine building. <N> ANON CR moved to CR-SRO group for OPS. | 02-00-T-BLDG-MISC
383652 | CR | 20180820 |  | 3 | RCIC Operability run for RCIC Outage had no HRA ALARA Task |  |  |  | N | NO | <D> **** Detailed Description **** WOT 02129438 06 was entitled â€˜(XX) OPS RCIC OPERABILITY, OSP-RCIC/IST-Q701â€™. The WOT had not had the RWP Required Hold placed on it and did not have an associated ALARA Task resulting in 0 mrem in August dose budget for the activity and no HRA ALARA Task for those performing the work to sign in on. An ALARA Task was created for this work, but when the activity occurred, ALARA Task 02101599 01 01 was used instead. WO 02101599 was/is scheduled for 09/10/18 for the Quarterly RCIC Operability run. There was 34 p-mrem expended by various craft on ALARA Task 02101599 01 01 that was not in August budget. <I> **** Actions Taken **** Created ALARA Task on WOT 02129438 06 and removed the (XX) from WOT title so that when and if this WO is backgrounded the ALARA Task will get planned and dose included in budget. Made duplicate ALARA Task for WOT 02101599 01 so that the dose for the Quarterly RCIC Surveillance (OSP-RCIC/IST -Q701) will be included in September dose budget and those performing the work will have an ALARA Task to use. Suggest that Ops create a Model Work Order from WO 02129438 to prevent future problems of this type.
383653 | CR | 20180820 | CAQ | C | Railroad Bay Door R106 South Door Stop (Jersey Barrier) Eval | N | Y |  | N | NO | <D> **** Detailed Description **** An evaluation of the resistant forces on the jersey barrier and chain outside door R-DOOR-R106 cannot be found. Per Design Spec. 8J for door R-DOOR-R106, doors shall be equipped with adjustable shock absorbing devices to cushion against impact during opening and closing, and hold open devices shall be designed to resist forces. The jersey barrier and chain is used to hold open door R-DOOR-R106 which replaces the function of the original door stop that was not reinstalled for the south leaf. See picture in EDMS of jersey barrier. This issue was identified during the accept-as-is AR 370667 review for not reinstalling the south door stop stanchion. . Procedure SOP-DOOR/HATCH-OPS provides detailed instructions for operation of Reactor Building Equipment Access Area Doors and Hatches. Currently, the north leaf of R-DOOR-R106 has an adjustable shock absorbing door stop stanchion at 90 degrees to the door. The original south door shock absorbing door stop was also installed 90 degrees to the door, but because the south door stop interfered with transferring fuel boxes it was never reinstalled. A jersey barrier and chain is installed to stop the south leaf door from opening too far and to hold the door in the open position. The jersey barrier does not interfere with the design function of R-DOOR-R106 which is to provide secondary containment and missile protection, and to withstand the effects of the design basis wind and design basis tornado when closed. . Recommend severity 3 assignment to AR-DMC for an accept -as-is evaluation of the jersey barrier and chain. <I> **** Actions Taken **** Discussed with reactor maintenance, mechanical design authority and my supervisor. | 02-00-R-DOOR-R106
383654 | CR | 20180820 |  | 4 | Form 26108 Not Located for FW-SOFT-CAPPL- PROTO HX |  |  |  | N | NO | <D> **** Detailed Description **** This CR is initiated to document and trend an incomplete/non-retrievable software classification form 26108 for software FW-SOFT-CAPPL PROTO HX. This issue was identified during resolution of CR 373375. <I> **** Actions Taken **** Completed form 26108 and provided to software owner for review and approval to submit to RIM.
383659 | CR | 20180820 | CAQ | D | SW-V-684 boundary leakage GT 5 GPM when closed | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02113018-20. marked completion required box, then taken back to complete <D> **** Detailed Description **** When attempting to hang clearance D-SW-V-845 -001 for work on SW-V-845 per WO 02113018 leakage through drain valve SW-V-858 was in excess of 5 GPM. During this time SW-SYS-A AND B were both running. Craft support is requested to assist in closure and isolation of SW-V-684. Note that 5 GPM leakage from the SW system is unacceptable and places the station in a SW INOP LCO (4 GPM is the limit). Also note that vents and drains were installed on SW A loop to the PASS system which assist greatly in setting the system up for work on these check valves, while no vents or drains have been installed on SW loop B to the PASS system. (SW-V-880, 881, 878, 877, 879) <I> **** Actions Taken **** Crew hanging clearance closed and capped SW-V-858 to stop the leakage. Clearance is being lifted with two revisions being written to allow craft to assist in closure of SW-V -684 and subsequent hanging of boundary clearance if craft assisted closure of SW-V-684 is successful in stopping (main seat) boundary leakage. | 02-00-SW-V-684
383662 | CR | 20180820 | CAQ | C | Revision to Design Spec. 8J |  |  |  | N | NO | <D> **** Detailed Description **** Design Spec. 8J needs be revised to reflect the tornado wind loads that are in FSAR section 3.3.2 and provide an overall review of the entire spec. to ensure the spec. is up-to-date with other plant documents. These wind loads are less than the original winds loads. See EDMS for Design Spec. 8J markups. This is a documentation issue only. . Recommend severity 3 assignment to AR-DMC for Design Spec. revision. <I> **** Actions Taken **** Provided markup pages in EDMS.
383664 | CR | 20180820 |  | 4 | Gland seal steam pressure low alarm | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Recieved Gland seal steam pressure low alarm (4.820.B2.7-6) followed ARP to verify header and bearing pressures were correct. nothing looks out of the ordinary. <I> **** Actions Taken **** ARP followed.
383667 | CR | 20180820 |  | 3 | The New FCP 2 is functional except for ARP |  |  |  | N | NO | <D> **** Detailed Description **** The New Fire Control Panel #2 is working and seems to be completely functional. The only problem is that we are stuck with the old ARP, which has no relation to the new panel. For example, the new FCP2 alarm tile 11-1 is for Wet Pipe Sys 17 Water Filter Bldg", but the ARP for FCP2 drop 11-1 is for "PGCC Sect U840 Halon Discharge." <N> Annunciator response procedure 4.FCP.2 is ready for issue and Data and Document Services has been requested to issue the procedure. The Control Room had been given a transition document at the beginning of the panel upgrade that provided guidance on answering the new annunciator windows with the old annunciator response procedure and had been provided training with how to use the document. The Control Room Supervisor has been contacted and has no issue with continuing to use the transition document until 4.FCP.2 is issued. | 02-00-FP-CP-FCP2
383668 | CR | 20180820 | CAQ | C | ABN-RRC-LOSS not revised for EC 14942 (MUR) |  |  |  | N | NO | <D> **** Detailed Description **** ABN-RRC-LOSS was not updated by EC 14942 for Measurement Uncertainty Recapture(MUR) power uprate. Attachment 7.1, Single Loop Power/Flow Map, and Attachment 7.2, Single Loop Core Flow/Drive Flow Correlation, are not current. Recommend referring to SOP-RRC-SINGLELOOP, Attachments 6.1 and 6.2 for the correct operating restrictions for single loop. <I> **** Actions Taken **** Reviewed ABN-RRC-LOSS against SOP-RRC-SINGLELOOP. No other errors in power or flow identified.
383669 | CR | 20180820 | CAQ | D | RHR-M-P/2C REPLACE LUBE | Y | N |  | N | NO | <D> **** Detailed Description **** when changing oil in both upper and lower oil resevoirs of RHR-M-P/2C the drain plugs were inspected. The upper resevoir oil drain plug had some imperfections in the threads. Although this does not impact the seal surface, action was taken to replace the oil drain plug with a new one per WO 02126638-01 instructions 4.1 and 4.2. instructions 4.13 states initiate CR if drain plug was found dammaged or needed to be replaced. <I> **** Actions Taken **** replaced oil resevoir plug per wo 02126638-01 instruction 4.2 and created CR per instruction 4.13 | 02-00-RHR-M-P/2C
383670 | CR | 20180820 | CAQ | C | 2 spare APRM ODA's found non functional |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of 02095082 01 two out of three spare APRM ODA's that were energized for a functionality test did not power up and display properly. <I> **** Actions Taken **** Stopped, informed supervision and system engineering. System engineering contacted vendor and the defective units are being returned for repair. <N> THis AR and Assignement 1 of this AR are being extended by R.Shaff acting SCS MAnager in accordance with Section 4.11.2 section 3) as a CAQ C.
383671 | CR | 20180820 | CAQ | D | Sound power phone kit missing tamper tag and extension cord | N | Y |  | N | YES | <D> **** Detailed Description **** The FLEX program owner noticed a tamper tag missing on Kit #5 in building 600. Upon further investigation, it was found one of two 25 foot extension cords is missing. <I> **** Actions Taken **** Replaced the tamper tag, notified the program owner, and wrote this CR and WR to have the extension cord replaced. <N> **** Equipment Description **** B-600
383672 | CR | 20180820 |  | 4 | EDR-TK-5 Has Spurious High Level Alarm. | N | N |  | N | YES | <D> **** Detailed Description **** EDR-TK-5 has a High Level Alarm. It initially came in Audio Only, then after Doing an Annunciator check and Reset, the EDR-TK-5 High Level Alarm just Flashes and will not reset. (Flashing indicates the alarm is clear and it is awaiting Reset). The Reset/Acknowledge/Test buttons are Common buttons that function for the whole front panels. EDR-TK-5 is at 31% level. No water has been transferred to it today. Appears to be a failed card in the annunciator panel. <I> **** Actions Taken **** contacted CRS | 02-00-EDR-TK-5
383673 | CR | 20180820 | CAQ | D | RCIC-DT-1 oil level below 'Low standby' level | Y | N |  | N | YES | <D> **** Detailed Description **** RCIC-DT-1 oil level below 'Low standby' level <I> **** Actions Taken **** Informed MCR/ CRS <N> **** Equipment Description **** RCIC-DT-1 RX 422 | 02-00-RCIC-DT-1
383674 | CR | 20180820 |  | 4 | Simulator THOR aborts and lost training time |  |  |  | N | NO | <D> **** Detailed Description **** Between 21:00 and 22:00 the simulator experienced 3 THOR aborts resulting in approximately 60 minutes of lost training time. <I> **** Actions Taken **** Backtracked the scenario and saved to trouble IC 167. Initiated SR #2786. Informed Simulator Supervisor, Operations Mentor, and Training Manager.
383675 | CR | 20180820 |  | 3 | ABN-INSTRUMENTATION enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Revise ABN-INSTRUMENTATION attachment 7.7 to include LCS 1.3.5.3 as a referenced spec for MS-PS-48A, MS-PS-48B, MS -PS-48C, and MS-PS-48D. This table can be found on page 27 of the ABN. <I> **** Actions Taken **** Wrote this CR.
383676 | CR | 20180820 | CAQ | D | Missed fire tour for TCP 18-0053 |  |  |  | N | NO | <D> **** Detailed Description **** The TCP 18-0053 was not added to the Fire Tour Log when it was opened at 0757 on 20 August 2018. The error was not found until the Fire Tour Log for 21 August was printed. The fire tour was missed from 0800-2359 on 20 August. RHR-C was already INOP during this time. <I> **** Actions Taken **** CR written and SM notified.
383677 | CR | 20180821 | CAQ | D | Cable insulation on RCV71C-3 coming from CRA-42-8B4D damage | Y | Y |  | N | YES | <D> **** Detailed Description **** During pre-inspection of cubical and wire for 0211844001 RRA-42-8B4A: REPLACE STARTER COIL RRA-FN-1, craft noticed a cable in the wire way that appears has been smashed in the door over time and the insulation is damaged ( see attached photoâ€™s in emds) this cable is RCV71C-3 and is coming from CRA-42-8B4D. We took photos, called the MCR and I (craft supervisor) instructed the crew to tape the damaged areas until we receive a resolution for repair. This damage appears to be old or accured over time. <I> **** Actions Taken **** We took photos, called the MCR and I (craft supervisor) instructed the crew to tape the damaged areas until we receive a resolution for repair. | 02-00-CRA-42-8B4D,02-00-CRA-FN-1C2
383678 | CR | 20180821 | CAQ | D | RRA-42-8B4A overload heater temperature not consistent | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing thermography it was notice that A Phase and B Phase on the overload heaters are 15 degrees warmer than C Phase while runnung RRA-FN-1 . <I> **** Actions Taken **** Notified supervision and the control room. <N> **** Equipment Description **** . | 02-00-RRA-42-8B4A,02-00-RRA-FN-1
383691 | CR | 20180821 |  | 4 | ASD1A/1 GTO driver red light FLT4 on. | N | N |  | N | YES | <D> **** Detailed Description **** -ASD1A/1 GTO driver red light FLT4 on. This is the daughter GTO Card to XDCD. No alarms in the MCR. <I> **** Actions Taken **** Attempting to contact system engineer. CRS informed. | 02-00-RRC-IMD-ASD1A/1
383694 | CR | 20180821 |  | 3 | Revise EL000566 EL1 JFG to include eWP |  |  |  | N | NO | <D> **** Detailed Description **** Revise EL000566 EL1 JFG to include eWP. Need to add a sign off for familiarity with the use and applications of eWP (Data Glance and work station). Should also include this for IC and Mech.
383695 | CR | 20180821 | CAQ | C | SOP-SLC-SPARGE/LEVEL | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** In SOP-SLC-SPARGE/LEVEL section 5.1.2 which states â€œTHROTTLE OPEN SLC-V-12 approximately 1/2 turn to air sparge SLC-TK-1 (SA Supply to SLC Storage Tank Sparger).â€ SLC-V-12 is not being opened enough for a representative chemistry sample. The valve needs to be opened 2 turns and then backed down to between 1- 1 Â½ turns to get enough mixing to get a representative sample. The check valve wonâ€™t open sufficiently if it isnâ€™t opened at least 2 turns and then backed down. Evidence of this is the last SLC sample on 8/14/18 the concentration lowered from 14.35 (average over last 2 years) to 13.83 which is barely in spec. There would have to be a significant leak on the SLC tank for that value to be real.SOP-SLC -SPARGE/LEVEL section 5.1.2 needs to say â€œOPEN SLC-V-12 approximately 2 turns THEN THROTTLE back to 1 turn to air sparge SLC-TK-1 (SA Supply to SLC Storage Tank Sparger).â€ <I> **** Actions Taken **** Notified MCR, Chemistry Supervision and specialist and System Engineer <N> **** Equipment Description **** RX 548' SLC tank. The Chemistry Technician who sampled said he could barely feel flow in the sparge pipe for SLC-V-12 Our more experienced technicians always ask operations to open it more when they check it. Another hour passes before we can sample it which keeps the tank sparging for another hour that day. | 02-00-SLC-TK-1,02-00-SLC-V-11
383697 | CR | 20180821 |  | 4 | RECORDS SENT TO RECORDS CONTROL WITH BARCODE ERRORS |  |  |  | N | NO | <D> **** Detailed Description **** SEVERAL CONFIDENTIAL DOCUMENTS WERE SENT TO RECORDS CONTROL WITH BARCODE ISSUES. <I> **** Actions Taken **** VOIDED TRANSMITTALS SUBMITTED,NOTIFIED MY SUPERVISOR OF ISSUE AND SENDING RECORDS BACK TO RADIATION PROTECTION FOR V&V/ CORRECTIONS & RE-SUBMITTAL. RESUBMITTED ON A NEW TRANSMITTAL.
383699 | CR | 20180821 | CAQ | D | Received system overview alarm on TDAS AST MON | Y | N |  | N | YES | <D> **** Detailed Description **** Receive system overview alarm on TDAS AST MON. On TDAS -CRT-AST indicates SINGLE ROD SCRAM DETECTED & SCRAM SINGLE 0221095628. Reset AST MON Command F for Enter Scram Detect Mode and the alarm is clear. This were happen at least twice in two days. Need to investigate and repair the issue. <I> **** Actions Taken **** Reset AST MON Command F for Enter Scram Detect Mode. SM/CRS infoemed. | 02-00-TDAS-CPU-AST
383700 | CR | 20180821 |  | 3 | EN vehicle damaged |  |  |  | N | NO | <D> **** Detailed Description **** At 0720 an EN vehicle was damaged when it contacted an ecology block. Driver was distracted at the time and hit an ecology block that was marking the edge of the road. Driver was not injured. Liquids were released to the ground. Contacted E&RP and cleaned up per there direction. <I> **** Actions Taken **** Reviewed ISPM-1 and GBP-IRB-02. Notifications of the accident were made to: Department Manager, Industrial safety, E&RP and shift Manager. <N> E&RP observed spill cleanup. Waste was moved to 180-day area for proper disposal. This spill is not reportable.
383701 | CR | 20180821 |  | 4 | TG-ID-1 roll paper not advancing. | N | N |  | N | YES | <D> **** Detailed Description **** TG-ID-1 roll paper not advancing. <I> **** Actions Taken **** Informed MCR, initiated AR. | 02-00-TG-ID-1
383702 | CR | 20180821 | CAQ | D | (QA) Loose door handle on door L-110 | N | N |  | N | YES | <D> **** Detailed Description **** Maintenance required for door L-110 due to loose handle. <I> **** Actions Taken **** CR/WR generated <N> Identified during AU-SE-18 audit. | 02-00-GH-DOOR-L110
383704 | CR | 20180821 |  | 3 | TRAINING RECORDS SUBMITTED WITHOUT SUPPORTING DOCUMENTATION |  |  |  | N | NO | <D> **** Detailed Description **** MULTIPLE TRAINING RECORDS WERE SUBMITTED TO RECORDS CONTROL WITHOUT SUPPORTING DOCUMENTATION. <I> **** Actions Taken **** NOTIFIED MY SUPERVISOR. SENDING RECORDS BACK TO MAINTENANCE DEPARTMENT FOR CORRECTIONS AND RE-SUBMITTAL.
383705 | CR | 20180821 |  | 4 | COND-TE-512C Has one of the two elements failed open | N | N |  | N | YES | <D> **** Detailed Description **** While investigating the failure of Computer point W047 per WR#29115234 it was discovered that the element that the leads from W047 were landed on had failed open. The second element which is spared was verified to be OK and was indicating correctly locally at the element. There is no labeling differintiating between the two elements. <I> **** Actions Taken **** After discussion with Supervision and Engineering it was decided to land the computer point leads on the working temperature element and verify correct indication on Comp. Pt W047. The field leads that are spared are too short to terminate on the element that indicates open due to the blue wire (copper) breaking several times during prior investigations have been taped off and secured inside the COND-TE-512C inclosure. This CR has been initiated to document the condition and facilitate a future repair <N> **** Equipment Description **** COND-P-2C | 02-00-COND-TE-512C
383707 | CR | 20180821 |  | 4 | RWP box not selected, ref; WO 0212634401 |  |  |  | N | NO | <D> **** Detailed Description **** By not selecting the RWP box, WO 02126344 was not routed through HP Planning for a proper ALARA evaluation, which drove the work group to sign in on the < 5 mRem/task RWP to perform their task. After being in the area (RW 437 L2/13.2) for about 15 minutes they checked their Electronic Dosimeters and noted they were reading 0.3 mRem (dose) and would not be able to finish the task without having to leave the RCA or possibly getting a â€œDose Alarmâ€ This caused a "stop work" and added delays to not only I&C, but, HP Planning as well. . HP Planning had to â€œADD SCOPEâ€ and assign dose that was not budgeted for. <I> **** Actions Taken **** Workers exited they area, notified supervision. HP Planning was notified, ALARA task/dose was added to the work order. Rad Support Supervisor notified as well.
383708 | CR | 20180821 |  | 4 | Loss of position indication RCC-V-71C | N | N |  | N | YES | <D> **** Detailed Description **** RCC-V-71C red light is out with the valve open. <I> **** Actions Taken **** Verfied no change in DW temperatures, replaced the bulb two times, and an operator verified disconnect is closed. | 02-00-RCC-V-71C
383709 | CR | 20180821 |  | 4 | OG-RF-20B oil level low, in standby | N | N |  | N | YES | <D> **** Detailed Description **** OG-RF-20B oil level is low. PPM 3.1.10 requires that the standby oil level be 1/3 of sightglass. Oil level is currently just barely visible (~ 1/8 of sightglass). No apparent/significant oil leakage was found; however, this is the second time oil has been identified as low out of spec in the last 2 months (reference WR# 29143642). Please investigate/repair and restore oil level. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RW 452 | 02-00-OG-RF-20B
383710 | CR | 20180821 |  | 4 | 455â€™ Light Out in DG-3 Stairway to Door D-208 | N | N |  | N | YES | <D> **** Detailed Description **** The stairway to DG-3 455â€™ elevation, Door D-208, lighting out. There are 2 lights in the area and both are out <I> **** Actions Taken **** Initiated CR/WR and informed supervision. <N> **** Equipment Description **** The stairway to DG-3 455â€™ elevation, Door D-208 | 02-00-D-BLDG-MISC
383711 | CR | 20180821 |  | 4 | While performing WO# 02090621-01 found ROA-AD-4 not working | N | N |  | N | YES | <D> **** Detailed Description **** ROA-AD-4 was signal and air supply to it and only had a 1/4" of stroke. suspect damper is stuck or positioner is bad. Further investigation is needed to determine the issue. may need to disconnect acuator from damper arm. <I> **** Actions Taken **** Notified supervisor and generated CR, WR after it is repaired then WO# 02090621-01 can be completed. <N> **** Equipment Description **** ROA-AD-4 R596 | 02-00-ROA-AD-4
383712 | CR | 20180821 |  | 4 | SA-DPI-4 is at the High spec of 20" H2O | N | N |  | N | YES | <D> **** Detailed Description **** SA-DPI-4 (SA compressor inlet filter D/P) is at the High Spec of 20" of Water column. Filter D/P trended up quickly the last 48 hrs (this can be attributed to the hazardously smoky, outside conditions). Note: When above 20" Water column, SA-DPI-4 is in the RED. It may be prudent to elevate the priority of this filter replacement. <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** RW 467 | 02-00-SA-DPI-4
383713 | CR | 20180821 |  | 4 | Discarded Halon Cylinders | N | N |  | N | YES | <D> **** Detailed Description **** Two Ansul brand cylinders of Halon 1301 were observed in the Kootenai Building Room 157B (Standards Lab) spared in place. They are not plumbed to a discharge header and are not electrically connected. Both cylinders indicate full. The last inspection date on the cylinders was 2008. The appropriate group needs to move these units to an unoccupied storage area outside the Standards Laboratory. Caution: These units appear have explosive halon discharge devices mounted on both cylinders that should be rendered safe prior to movement. <I> **** Actions Taken **** Notified the Standards Lab supervisor and Facilities and Commercial Engineering Manager of issue. <N> **** Equipment Description **** No EPN
383714 | CR | 20180821 |  | 3 | Issue â€“ Model of Vendor Crane to Support HCV Platform Instal | N | N |  | N | NO | <D> **** Detailed Description **** A vendor crane brought into the CGS Protected Area to support the installation of the Hardened Containment Vent work platform was specified in the High Risk Work Plan and other planning documents to be a Manitowoc Grove GMK 5225 Tier III crane. The crane that was brought into the protected area on August 21, 2018 to perform the work was a Manitowoc Grove GMK 5170 crane. The field project manager and then Responsible Department Manager were advised of the concern and advised not to perform any planned lifts until this issue is resolved in accordance with PPM 1.3.76 â€œIntegrated Risk Managementâ€. <I> **** Actions Taken **** The manager who chaired the High Risk Challenge meeting on July 2, 2018 was advised of this issue. | 02-00-HCV-EQ-1
383716 | CR | 20180821 |  | 4 | Excessive Fan Vibration CW-FN-12 | N | N |  | N | YES | <D> **** Detailed Description **** Audible vibration can be heard from CW-FN-12. The noise is particularly loud from the North side of the Fan shroud. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** CW-CT-1B | 02-00-CW-FN-12
383717 | CR | 20180821 |  | 4 | RRC-IMD-ASD1A/1 Alarm Printer Low on Ink | N | N |  | N | YES | <D> **** Detailed Description **** RRC-IMD-ASD1A/1 Alarm Printer Low on Ink, making it very difficult to read drive status and alarm/fault print outs. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** ASD Building | 02-00-RRC-IMD-ASD1A/1
383718 | CR | 20180821 |  | 4 | WRA-RIS-2 Recorder out of cal | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of 10.27.51 step 7.2.29 the as left recorder value on PRM-RR-3 Ch-8 is out of tolerance. Per step 7.2.31b. a CR and WR is being initiated to repair/calibrate ch-8 on the recorder. <I> **** Actions Taken **** Notified Supervision and initiated CR/WR <N> **** Equipment Description **** PRM-RR-3 CH-8 WRA-RIS-2 MCR | 02-00-PRM-RR-3
383719 | CR | 20180821 |  | 4 | Audible Hydrogen leak from HSSF-EFC-FXV146 | N | N |  | N | YES | <D> **** Detailed Description **** Audible Hydrogen leak from HSSF-EFC-FXV146 this leak will slowly bleed down the H2 Tube Trailer #1. Investigate and repair. See EDMS for video of Snoop check. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** HSSF near Tube Trailer | 02-00-HSSF-EFC-FXV146
383721 | CR | 20180821 |  | 4 | WRA-RIS-2 Flow Rate | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** WRA-RIS-2 flow rate is not controlling at setpoint <I> **** Actions Taken **** Notified supervision and initiated a CR/WR <N> **** Equipment Description **** WRA-RIS-2 RW 487
383722 | CR | 20180821 |  | 3 | Editorial correction to ISPM-21 |  |  |  | N | NO | <D> **** Detailed Description **** ISPM-21 page 9 of 9 lists the Inspection Responsibility as Operations for the "Thermal Make-up (TMU)/river pump house). It should read as "Tower Make-up (TMU)/river pump house). <I> **** Actions Taken **** CR written <N> **** Equipment Description **** ISPM-21
383724 | CR | 20180821 | CAQ | C | RWM appears to have locked-up | Y | N |  | N | YES | <D> **** Detailed Description **** Found a SYSTEM ERROR message on the RWM on H13-P603 and 'red ice cubes' on TDAS. Investigation found the COMPUTER OPER LED extiguished on H13-P616. <I> **** Actions Taken **** Attempted to reinitialize the RWM per ABN-RWM and the RWM locked-up at step 5.2.6 of SOP-RWM-START. | 02-00-PPC-CRT-RWM,02-00-RWM-SOFT-RWM
383726 | CR | 20180821 |  | 4 | CW-CT-1A is being operated 1.5 inches from overflow. | N | N |  | N | YES | <D> **** Detailed Description **** Cooling tower levels are directly linked to the CW Basin return level. This in turn is linked to the individual CW bay levels plus the Screen D/P. We are currently maintaining bay levels high to aid in the CW-P-1C as it doesnt seem to have normal pumping amps when CW basin is lower. By maintaining the Level high we are precariously close to overflowing the CW-CT-1A. It has been logged as high as 0.5 inches from overflowing. in the event we had a transient that tripped a CW pump it would most likely overflow the tower. <I> **** Actions Taken **** wrote CR to elevate concern and possibley re-evaluate putting CW-P-1C on the plant concerns list. | 02-00-CW-CT-1A
383727 | CR | 20180821 |  | 4 | All three TMU pumps have excessive packing leakage | N | N |  | N | YES | <D> **** Detailed Description **** All three TMU pumps have excessive packing leakage. The leakage is leaking past the spray shields. Please see attached video it goes from TMU-P-1B to 1C then 1A. <I> **** Actions Taken **** wrote WR and CR | 02-00-TMU-P-1A,02-00-TMU-P-1B,02-00-TMU-P-1C
383728 | CR | 20180821 |  | 4 | 3 out of 8 lights out in SWPH A |  |  |  | N | YES | <D> **** Detailed Description **** 3 out of 8 lights out in SWPH A. Room appeared darker than normal. please replace/repair. <I> **** Actions Taken **** wrote CR/WR <N> **** Equipment Description **** swph A | 02-00-A-BLDG-MISC
383729 | CR | 20180821 |  | 4 | Scaffolding is a trip hazard in SWPH A |  |  |  | N | NO | <D> **** Detailed Description **** Scaffolding installed for TMU-LCV-2A is still in placed. WO 02105644 has this task (09) as complete. The path to E -PP-7A-G and other log readings requires multiply pipes and scaffold poles to step over. Please remove the scaffolding. please see picture attached. <I> **** Actions Taken **** wrote cr to identify the hazard <N> Will be removed after baseline testing is done under a Mundane task assignment 01158000 | 02-00-A-BLDG-MISC
383730 | CR | 20180822 | CAQ | D | BRE 36 BRE/AVSS Switch Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** The switch in BRE 36 for the BRE/AVSS transmitter is broken and needs to be replaced. <I> **** Actions Taken **** Security supervision notified. Intiiate CR/WR. <N> **** Equipment Description **** BRE/AVSS Switch located on the transmitter box inside BRE36
383731 | CR | 20180822 |  | 4 | Oscillograph Started Alarm | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm at 02:57 on 08/22/2018. Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 239KV B: 240KV C: 240KV E-TR-B A: 120KV B: 120KV C: 118KV The following sensor was tripped and is reset: J7 Sensor - 500KV Neutral Ground. BPA reports the cause was a momentary fault on the Vantage - Schultz #1 500KV line. Relaying involved a single pole with automatic re-closure and no known equipment damage. 500KV voltage at Ashe is 543KV. The 230kv and 115kv near grid was not involved. <I> **** Actions Taken **** Notified the CRS. Submitted CR as directed by Annunciator Response Procedure 4.800.C4 4-3.
383734 | CR | 20180822 |  | 3 | NRC approval of Addendum 5 to NEI 08-09 REV 6 |  |  |  | N | NO | <D> **** Detailed Description **** The NRC has endorsed Addendum 5 (Cyber Security Vulnerability and Risk Managment) to NEI 08-09, Cyber Security Plan for Nuclear Power Reactors, Rev 6. An evaluation needs to be performed to determine the impact to the site and the Cyber Security Plan (CSP-01). <I> **** Actions Taken **** Notified Cyber Security Program Manager
383736 | CR | 20180822 | CAQ | D | Emergency Light E-BU-ASD/1 Battery Fault | N | N |  | N | YES | <D> **** Detailed Description **** While performing Fire Protection walkdown of various buildings, Non-Essential E-BU-ASD/1 was observed to be blinking 2 red LED blinks. This indicates a bettery fault per PPM 10.25.175. <I> **** Actions Taken **** Initiated FPSI 18-0262 for non-functional light and wrote CR for WR. <N> **** Equipment Description **** ASD Bldg. | 02-00-E-BU-ASD/1
383740 | CR | 20180822 | CAQ | D | TEA-SR-26 indicates "No isok. control". | N | Y |  | N | YES | <D> **** Detailed Description **** During performance of CSP-INST-D201, TEA-SR-26 was indicating "No isok control". The sample flow rate is 1.92 scfm which is lower than normal. The smoke from area wildfires has loaded up on the sample filters, however the filters were changed out yesterday and sample flow is not improved. Investigation is needed to determine the cause for the decrease in sample flow. <I> **** Actions Taken **** Notified specialist, supervision and OPS. Wrote CR/WR | 02-00-TEA-SR-26
383741 | CR | 20180822 | CAQ | C | R-24 PPM 10.25.100 Instructions Differ from the Valve Manual | Y | N |  | N | NO | <D> **** Detailed Description **** Open and closed indication of the Target Rock model 96T-001solenoid valve is provided by reed switches that are actuated by a magnet attached to the valve stem. These switches are calibrated under procedure 10.25.100 Section 7.6. To adjust the reed switches, the valve is placed in the desired position and the appropriate reed switch adjusting screw is turned clock wise until the reed switch closes. The adjusting screw is then turned an additional amount to compensate for thermal growth. This additional amount is referred to as enrichment by Target Rock, the valve manufacturer. . The current revision of 10.25.100 (Rev. 12) calls for an enrichment of 1 turn for both the open and closed reed switches. This, however, is different than that specified by the valve technical manual (CVI OMM 899-00,3 Section 3.12). This manual specifies an enrichment of Â¾ turn for the open reed switch and Â¼ turn for the closed reed switch. . A search of previous revisions of 10.25.100 showed that revision 10 contained the same enrichments as the technical manual. Revision 11 changed the open switch enrichment to Â¼ turn, but no explanation or justification for this change could be found. Revision 12, the current revision, changed the enrichments for both switches to 1 turn. This was based on AR 00257142. This AR also added a note to the procedure which states: Target Rock recommends: For short stroke less than 0.200 in. enrichment setting is in the range of 1/2 to 1 turn. For longer stroke greater than 0.25 in. enrichment setting is in the range of 1 to 2 turns. This statement appears to have come from a training presentation that was given in 2012 (See the file â€œAR257142 Target Rock supplied SWITCH ADJUSTMENT PRESENTATION1.pptâ€ in the AR 00257142 EDMS folder). Inserting this requirement into 10.25.100, however, is in conflict with the letter from Target Rock that is also in the EDMS folder (AR257142-01 Target Rock recomendations.pdf) which states: The amount of enrichment is different for different valve models and is provided in the applicable Technical Manual. It appears that the generic instructions from the training power point were inserted in 10.25.100 when the instructions from the technical manual should have applied. This procedure should be revised to reflect the instructions in the technical manual. <I> **** Actions Taken **** Placed recommended changes to PPM 10.25.100 in the EDMS folder <N> Put into the Maintenance Procedure data base, no further action required.
383743 | CR | 20180822 |  | 3 | DES-4-2 process discrepancy with DSVR Form 26332 |  |  |  | N | NO | <D> **** Detailed Description **** While preparing Certified Design Specification updates for EC DEC 10671, the following Standard Design Process (SDP) discrepancy in our associated Utility-specific process procedures was discovered: For this activity, SDP procedure IP-ENG-001 3.3.4.b sends the user to the applicable Utility-specific procedure and Columbia SDP interface procedure ENG-DES-50 directs the user to EC Table of Contents Form 27162 and DES-4-2 (Preparation and Revision of Columbia Design Specifications). EC TOC Form 27162 and DES-4-2 both indicate that Form 26332 (Design Specification Verification Record) is required for EC product types tied to a plant modification (e.g., EC DEC 10671). However, DES-4-2 4.2.14.a. indicates DSVR Form 26332 is not needed if the EC product tied to a plant modification includes Form 25298 (Design Verification Record). Unfortunately, DVR Form 25298 has been eliminated from the Columbia SDP process (i.e., has been superseded by the SDP Design Verification questions per IP-ENG-001 3.3.9). DVR Form 25298 Note A states that the form is not required for the Columbia SDP and EC TOC Form 27162 does not include/list DVR Form 25298 as potentially required. As such, DSVR Form 26332 is required per Form 27162 and DES-4-2 for all SDP EC product types tied to a modification that include Design Specification changes. Discrepantly, DSVR Form 26332 itself currently includes a Note stating that it is not required for the Columbia SDP. Options for Resolution: 1) Eliminate DSVR Form 26332 from DES-4-2 4.2.14 for SDP ECs tied to plant modifications that have been subjected to the SDP Design Verification questions per IP-ENG-001 3.3.9 (i.e., just like DVR Form 25298 was eliminated for SDP ECs). DSVR Form 26332 would then only be required for SDP ECs tied to modifications that include Design Specification updates but do not require Design Verification. As such, the existing Note on DSVR Form 26332 would need similar clarification. 2) Remove the existing Note from DSVR Form 26332 that states it is not required for the Columbia SDP. The initiator of this AR CR 383743 would prefer Option 1 be taken for resolution of this issue. DSVR Form 26332 questions are covered by the IP-ENG-01 3.3.9 Design Verification questions just like the DVR Form 25298 questions were. Recommend assignment to Design Engineering for resolution. This is an administrative issue only - there is no associated issue with the physical plant or the continued function, operation, or qualification of any station SSC. <I> **** Actions Taken **** Prepared the Option 1 resolution mark-ups of DES-4-2 4.2.14 and Form 26332 included as pdfs in the EDMS of this AR CR 383743.
383745 | CR | 20180822 |  | 3 | Revision of PPM 10.2.13 & EWP Effected Procedures |  |  |  | N | NO | <D> **** Detailed Description **** Step 7.8.3 of PPM 10.2.13 does not currently align with station standards. The implementation of EWP eliminated the input of history into Asset Suite, and all history is captured in Data Glance when performing Work Orders electronically. Revise procedure accordingly <I> **** Actions Taken **** Initiated this CR <N> The following procedure revision has been entered into the Maint. Procedure revision data base. a link to the data base assignment has been added to the EDMS of this AR.
383748 | CR | 20180822 |  | 4 | Hanford Radio Fire Alarm Repeater 5020 TROUBLE signal | N | N |  | N | YES | <D> **** Detailed Description **** At approx. 1300 hrs on 8/21/2018 the Radio Fire Alarm Repeater (RFAR) 5020 transmitted a TROUBLE signal to Hanford Fire Department (HFD) Dispatch. RFAR 5020 is located on the East side of Building 62. HFD responded by sending a maintenance team to investigate and repair. When this happens, the repair team must be Red Badged and escorted to the RFAR box. HFD responded to this non-emergency call. EN Security processed the Red Badge forms and provided escort to RFAR 5020. The TROUBLE signal did not affect the HFD call button located in the Main Control Room. This notification method would still work dispite the Trouble signal. The RFAR was checked for causes and none were found. Box was reset and HFD left without really fixing anything. <I> **** Actions Taken **** EN Security provided escort to HFD to investigate RFAR 5020. No cause found. Contacted HFD Radio Maintenance at 376-0051 and they indicated no need for a return visit, no need to schedule an inspect/repair visit. <N> **** Equipment Description **** Hanford Radio Fire Alarm Repeater 5020
383750 | CR | 20180822 |  | 4 | FP- NEIL not notified upon closure of permit |  |  |  | N | NO | <D> **** Detailed Description **** FPSI did not show a notification to NEIL upon closure of the impairment. A NEIL notification was established and documented on the approval portion of the permit. This appears to be a gap as the permit can be closed without NEIL notification being established. An email to the fire marshal email to request a NEIL notification of closure would be suffiecient. <I> **** Actions Taken **** CR for trending purposes.
383751 | CR | 20180822 | CAQ | D | Essential fire door R-217 latch stays retracted | N | Y |  | N | YES | <D> **** Detailed Description **** Plant tour identified the latch of door R-DOOR-D217 stays fully retracted when fully twisted open. This deviates from our FSAR commitment to NFPA 80-1974. The door latch needs lubrication (FIN Team work). This type of problem should be caught by the PPM 15.1.2 weekly fire door inspections. <I> **** Actions Taken **** Wrote BIP 18-0359 and place on fire tour. <N> **** Equipment Description **** RB 471 SW | 02-00-R-DOOR-R217
383752 | CR | 20180822 |  | 3 | Inconsistencies in employment status between SSIS and A/S |  |  |  | N | NO | <D> **** Detailed Description **** More than 200 individuals show active in either SSIS or A/S but inactive in the other. An interface from SSIS to A/S is used to terminated persons in A/S who have been flagged for termination in SSIS, but this is not working perfectly. Other causes may also be contributing. <I> **** Actions Taken **** None, pending complete investigation of possible causes. | FW-00-SOFT-INTFAC-PQD TERM
383754 | CR | 20180822 |  | 4 | 3 Pieces of M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** 3 Pieces of M&TE found OOT & adjusted within specs. NONE were used during Calibration cycles. Calcode #0066431 Hytorc Hyd. Torque Wrench- model Avanti P7. DEF #6726A written. Calcode #0066434 Hytorc Hyd. Torque Wrench- model Avanti P7. DEF #6727A written. Calcode #C003954 Shopmade ARM Power Supply. DEF #6728A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
383756 | CR | 20180822 |  | 4 | SLC-V-11 check valve may be sticking | Y | N |  | N | YES | <D> **** Detailed Description **** Operations opens SLC-V-12 1/2 turn per SOP-SLC-SPARGE to initiate the sparge for chemistry to sample the SLC tank during the monthly Tech Spec sample. The check valve sounds like it either isn't opening fully or it is getting stuck with only a 1/2 turn. When opened a full turn you can hear the valve lift. little or no sparge creates non -representative chemistry sample (poor mixing) and will cause low in accurate results. Either the check valve needs to be fixed or the valve needs to be opened more for the sparge. <I> **** Actions Taken **** Notified MCR, chemistry supervision and system engineer. <N> **** Equipment Description **** RX 548 top of SLC tank | 02-00-SLC-V-12
383758 | CR | 20180822 | CAQ | C | Combustibles in RB 616â€™ refuel floor observation room |  |  |  | N | NO | <D> **** Detailed Description **** Amount of exposed combustibles in RB 616â€™ refuel floor observation room R804 is becoming excessive. The room is slowly turning into a storage area for miscellaneous materials. When this room was added, sprinklers were not specified because it was going to be a viewing room and temp office during outages, not a storage area. Fire Protection requests that only the combustible materials that are truly needed be present. If the materials currently present are needed, then obtain a SWP-MAI-02 authorized storage permit, place the combustible materials inside enclosed steel cabinets/boxes, and remove the open steel shelf. Note that there is already authorized storage permit locations just outside the RB 606â€™ Room R708. <I> **** Actions Taken **** Discussed with Fire Marshal and wrote this CR. | 02-00-R-BLDG-MISC
383761 | CR | 20180822 |  | 4 | INSULATION on CO-HX-1 east head needs to be replaced | N | N |  | N | YES | <D> **** Detailed Description **** The insulation on CO-HX-1 east head needs to be replaced, there is significant water damage to the calsil insulation causing it to be brittle and crumble. The wire mesh installed over the block insulation as a weight bearing/strengthening device is rusted and crumbling. There have been numerous repairs already performed on the head insulation, a fresh start with new material is recommended. Recommend replacing while the aux steam system is not in service, as this task will have significant personal safety risk while the aux steam system is running. <I> **** Actions Taken **** Notified supervision and Ops of the condition of the insulation. Initiated CR, WR took pictures. See EDMS <N> **** Equipment Description **** AUX BOILER ROOM | 02-00-CO-HX-1
383762 | CR | 20180822 |  | 4 | Loose split bolt on main grounding jumper | N | N |  | N | NO | <D> **** Detailed Description **** While supporting conduit seal off task under WR #29144249 craft noticed that the main ground for SEC-DISC-ISFSI/DB in the lower left hand corner of disconnect appeared loose and verified it to be loose. This ground is the jumper from the main ground to the OKINITE cable grounds of the line side of disconnect. bThis connection at the split bolt needs to be tight. <I> **** Actions Taken **** Notified supervison and wrote this CR. <N> **** Equipment Description **** SEC-DISC-ISFSI/DB | 02-00-SEC-DISC-ISFSI/DB
383772 | CR | 20180822 |  | 3 | Sec Checkpoint Entry Tab not populating in PQD Viewer |  |  |  | N | NO | <D> **** Detailed Description **** The Security Checkpoint Entry tab in PQD Viewer was not displaying data. <I> **** Actions Taken **** IS reviewed the issue and determined that an invalid SSN entry caused the data transfer process to fail. The SSN was corrected and the PQD Viewer data display issue was resolved. <N> Recommend NCAQ 3 - ITMGMT
383773 | CR | 20180822 | CAQ | D | B-DOOR-G200 broken hinge bolt/loose bolts on jack screw actu | Y | N |  | N | YES | <D> **** Detailed Description **** During walkdown of B-DOOR-G200 I discovered a broken hinge bolt on lower hinge of the active leaf. The bolt head appears to have been broken for some time (end of bolt is painted). Each door hinge has 8 1â€ bolts (32 total) and each door has two large locking bars holding it in place. The doorâ€™s integrity does not appear to be in question based on the number and size of bolts and locking bars. . In addition, for bolting design, tension is limited to ~60% of yield. For operability, higher allowable bolting stress is allowed up to 90% of yield to ensure that the bolting does not yield/fail. The operability allowable stress (still below yield) is 50% higher than the Design allowable loading for the bolting. By comparison to 8 bolts using design allowable stress of 60% yield, 7 bolts limiting stress to 90% of yield will ensure the door is operable but degraded. (7 x 0.9) > (8 x 0.6), 6.3 > 4.8. This evaluation does not even consider the two large shear pins that are unaffected by the condition. . Reference CR 323505 for similar occurrence on A SWPH door. . Also on the active leaf the bolts for the upper â€œmachine (jack) screw actuatorâ€ appear loose. The bolts are holding the actuator in place and the latching pin is in the up â€œclosedâ€ position. This does not appear to affect the ability of the mechanism to operate the door locking pins. The linkage is in alignment and the bolts are not excessively loose. Ref. CVI DWG 210-23,2. . See EDMS for pics of both. <I> **** Actions Taken **** Notified supervisor and SM. <N> **** Equipment Description **** B SWPH | 02-00-B-DOOR-G200
383774 | CR | 20180822 |  | 3 | Weather protection/barrier for smoking areas |  |  |  | N | I DONT KNOW | <D> **** ANONYMOUS CR - Detailed Description **** Is it possible to have some form of protection or barrier for the smoking areas? While it is appreciated that these areas have been provided, it would be unfortunate if the wind caught and caused a fire even though the most attentive person is careful. It would also be appreciated if individuals had coverage from rain or other unpleasant elements. It certainly would help with morale knowing that even those who have vices / faults are given some consideration. <N> Anonymous CR generated, moved to CR-SRO for review.
383781 | CR | 20180822 |  | 4 | WHCO-LS-1 mounting stud broken |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of 02126344-01 installation of the new level switch WHCO-LS-1, one of the mounting studs broke while tightening down the nut. <I> **** Actions Taken **** Notified supervision and engineering. It was determined that the level switch could still be installed with 3 of the studs left. Wrote CR and WR for further repair. <N> **** Equipment Description **** RW437 WHCO-CU-1 condensate tank | 02-00-WHCO-CU-1,02-00-WHCO-LS-1
383783 | CR | 20180822 |  | 4 | SEC-TN-06 | N | N |  | N | YES | <D> **** Detailed Description **** SEC-TN-06 has failed to allow exiting personal off-site on multiple occasions. <I> **** Actions Taken **** Taken out of Service, contacted electricians and generated CR/WR. | 02-00-SEC-TN-6
383784 | CR | 20180822 | CAQ | D | Public address in building-104 (ISFSI) is degraded | N | Y |  | N | YES | <D> **** Detailed Description **** The PA inside B-104 located in the back of the ISFSI area is degraded. Note: Announcements and alerting tones can be heard outside the building from other locations. <I> **** Actions Taken **** Telecom Techs checked the building PA amp and traced the problem back to I&C equipment. Notified: EP, SCC and I&C techs. <N> **** Equipment Description **** B-104
383785 | CR | 20180822 |  | 3 | PPC-CPU-VMS/WS found powered down. | N | N |  | N | YES | <D> **** Detailed Description **** While trying to perform weekly disk space checks, Computer Engineer found computer power off. Tried booting with no response. Suggest trend only. No impact on Operations. <I> **** Actions Taken **** Pushed power cord firmly into computer. It did not appear to be loose. System booted normally. | 02-00-PPC-CPU-VMS/WS
383788 | CR | 20180822 | CAQ | D | FDR Flow rate elevated. | Y | Y |  | N | YES | <D> **** Detailed Description **** FDR Flow rate is elevated. EDR-FRS-623 point 1, red pen had a prompt jump followed by a slow decline. TDAS point X167 reflects the same behavior. E-SM-3 was transferred to E-TR-S at 1919 22 AUG 18. The change in FDR flowrate has been noted to start at the same time. Current flowrate at about 0.18 gpm. <I> **** Actions Taken **** Notified the CRS, STA and SM. Reference TS 3.4.5 and 3.4.7. | 02-00-EDR-FRS-623,02-00-FDR-FT-38
383789 | CR | 20180822 |  | 3 | Unable to take WO 02100974-01 to WORKING status in DataGlanc |  |  |  | N | NO | <D> **** Detailed Description **** WOT 02100974-01 for performance of PPM 8.4.62 could not be taken to WORKING status to perform DCW-HX-1B1/1B2 Thermal Performance due to 01 task being checked out. Worked with CRS to resolve issue but was still unable to take the task to working. Engineering was given permission from Ops to continue performing the 01 task from the signed in paper copy of the procedure. WOT 02100974-01 field work was complete. <I> **** Actions Taken **** Discussed with CRS Notified Engineer working on the WO that the prior WO needs to be closed before you can work the current. <N> The reason that the users are unable to take WO 02100974-01 to WORKING status in DataGlance is because the previous occurrence of the PM WO has not been closed out. The tasks on the previous PM occurrence work order 02102685 have all been set to FINISHED in Asset Suite, but the completion processing has not been performed (Execute on M300) to set that work order to COMPLETE status. Once 02102685 is set to complete, 02100974 will be able to proceed.
383790 | CR | 20180822 |  | 4 | SEC-MDET-5 is not functioning as designed | N | N |  | N | YES | <D> **** Detailed Description **** SEC-MDET-5 is generating ghost alarms, request support to investigate | 02-00-SEC-MDET-5
383791 | CR | 20180823 |  | 3 | Received RFT A/B TROUBLE, H13-P840.A1.3-4, alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received RFT A/B TROUBLE, H13-P840.A1.3-4, alarm concurrent with transferring SM-3 from TR-S to TR-N1. Both feed pump continue to operate normally. There are 7 alarms indicated on the alarm screen (see EDMS). The RFW-P-1B Power Supply 2 fail seems to be the biggest cause for concern. Nothing else appears abnormal. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-RFT-COMP-2
383792 | CR | 20180823 |  | 4 | Turbine building elevator out of service | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-3 was observed not responding to calls. Looking down through the grating in the machinery room, it appears to be at the 501' elevation. Cycling power did not restore it to service. Recommend investigate and repair. <I> **** Actions Taken **** Informed MCR, generated AR/WR. | 02-00-MT-ELEV-3
383793 | CR | 20180823 |  | 4 | CPR-LIS-97B gave late high level alarm | N | N |  | N | YES | <D> **** Detailed Description **** When adding to tank CPR-92B, CPR-LIS-97B did not alarm (and trip the backwash transfer pump) as designed. The pump was manually secured. About two hours later, the alarm was received in the RWCR (tank contents had not changed). Please investigate and repair to avoid overfilling this tank. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RWCR | 02-00-CPR-LIS-97B
383794 | CR | 20180823 | CAQ | D | Attempting to process MWR using EDR doesn't work | N | N |  | N | YES | <D> **** Detailed Description **** Attempted to process MWR through the EDR system using SOP -RW/MWR-OPS section 5.2. This section is to process MWR -TK-23B using MWR-P-26B. Although all steps in procedure were followed, MWR-P-26B would not start when the waste collector filter START pushbutton was engaged. Please investigate and repair. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RWCR | 02-00-MWR-P-26B
383798 | CR | 20180823 |  | 4 | 15.2.45 needs a procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** 15.2.45 needs to be enhanced. <I> **** Actions Taken **** Provided markup to procedure writers. Informed Supervision. <N> **** Equipment Description **** Effected equipment is E-B0-PBX Put procedrue in Maintenance data base, no further action required. | 02-00-E-B0-PBX
383799 | CR | 20180823 | CAQ | D | Received "DC MCC RM COOLER FLOW LOW" alarm | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02113373, then taken back to complete <D> **** Detailed Description **** Received "DC MCC RM COOLER FLOW LOW" (H13-P812.R1 drop 10-2) alarm: SW-FI-41 indicates 17.5 gpm. Per OSP-SW-M101, the RRA-CC-12 recommended flow is 20-25 gpm and the minimum flow for operability is 12 gpm. No further action is required. | 02-00-SW-FI-41
383800 | CR | 20180823 | CAQ | D | Door D-207 knob needs replaced repaired | N | Y |  | N | YES | <D> **** Detailed Description **** Door knob is very hard to open. requires two hands to turn. This should be corrected as it is a potential for a wrist injury or for someone to be stuck inside the diesel exhaust room. <I> **** Actions Taken **** wrote CR | 02-00-D-DOOR-D207
383801 | CR | 20180823 | CAQ | D | DSA-DY Blowdown Pipe degraded | Y | N |  | N | YES | <D> **** Detailed Description **** system engineer identified during walkdown of DG2 that the dryer blowdown pipe is showing signs of degradation. No leaks detected at this time. Recommendation is to clean the floor/area to allow better monitoring immediately and plan for repair or replace. If replaced work can be performed online, pipe, valve should be replaced up to the union. This section of pipe is in scope for license renewal. If replaced the removed pipe and valve should be provided to engineering for inspection. <I> **** Actions Taken **** wrote CR | 02-00-DSA-DY-1B,02-00-DSA-V-77B
383802 | CR | 20180823 | CAQ | D | Vault Humidity Above Acceptable Range |  |  |  | N | NO | <C> Per MRT feedback received on August 28, 2018 - this CR was priotized to CAQ / D as the CR documents conditions that challenged quality record storage. <D> **** Detailed Description **** The humidity in the Vault (Bldg. 47) has been oscillating between 41% and 54% which is above the acceptable range of 20% to 40%. This increase in humidity occurs when the outside temperature is above normal for any length of time. The oscillation started on 6/19/18 and continues today. <I> **** Actions Taken **** The dehumidifiers were charged and placed into the vault to assist with controlling the humidity. The highest humidity reading was 54% on 8/16/18. During the week of 8/20/18, the average humidity reading was 50%. It is anticipated that the humidity will go back into range as the outside temperature decreases. This CR was initiated for trending purposes only. On 8/27/18 at 0600 the humidity was 50%.
383803 | CR | 20180823 |  | 3 | lost asset suite functionality when employee added |  |  |  | N | NO | <D> **** Detailed Description **** This week an employee was added to my org 54220 and in the process I was removed from the group. Payroll fixed the permissions allowing 5 people to 6 people to report to the supervisor, now my time card can be approved again but I have lost other functions. I cannot edit anything in asset suite, even self ARs that I created. System is acting as if I don't exist in the system. Unfortunately other organizations wish me to make changes (INPROG to ACTIVE, for example, and change due dates) that are not possible when I don't exist. Please restore functionality. Something similar happened last year when we had a substitute manager. Recommend HR for disposition. <N> HR evaluated the PeopleSoft job data record and determined to be updated to the correct supervisor after the issue was identified that the ERC wasnâ€™t processed in time for timesheet approvals. ERCs are processed as early as possible, but it is inevitable that some occur after the time approval deadlines. HR was able to fix Lindaâ€™s timesheet needs. Regarding Asset Suite â€“ that is managed by IS. IS clarified that the issue seemed to be a rare case of Linda connecting to Asset Suite on another userâ€™s session. It is possible, but rare that someone is disconnected and another user can be connected to their disconnected session when logging in. Tim had Linda log out and back in to clear the problem. Linda has confirmed that the situation has been resolved. No further actions are needed. -JHF
383805 | CR | 20180823 | CAQ | C | Identified Radiological hazard not routinely characterized |  |  |  | N | NO | <D> **** Detailed Description **** During resolution of AR-381458, documented surveys near and at the boundary of neutron monitoring areas did not include neutron dose rates to characterize/verify the hazard. There are multiple neutron monitoring areas around the plant, some are routinely accessible and others are not. Recommend assigning to Rad Ops to determine an appropriate frequency for characterizing the radiological hazard in the various locations. <I> **** Actions Taken **** Notified RP supervision. <N> This AR-CR is being addressed under AR-CR 381458. Per SWP -CAP-01, assignments 03 and 04 under resolving AR-CR has been created to address the issue documented in this AR-CR. Appropriate cross references have been added. Radiological Support Supervisor approved closure of this parent AR-CR.
383807 | CR | 20180823 |  | 3 | Training for chemical handling is inadequate to non-existent |  |  |  | N | NO | <C> Per MRT feedback received on August 28, 2018 this CR was dispositioned to AR-MMGR to review WAC code compliance for HAZMAT refresher training. <D> **** Detailed Description **** During HAZMAT Refresher training it came to light that our training for handling chemicals from large tanks or tanker trucks is inadequate to non-existent. We have procedures for performing gravity drains / batch adds of chemicals to systems and for flushing pumps and piping, but we are not trained for it. Our training per the WAC for HAZMAT response does not provide for handling chemicals. We have all of the craft who handle chemicals to varying degrees, but the laborers are the only group that are trained for handling in a HAZWOPPER situation only. We are not trained for periodic / routine handling of chemicals outside of pumps / piping. It was pointed out that the level of handling that we are expected to perform requires annual training that takes up to four days to perform. We have mechanics replacing chemical pumps operators performing batch adds from tanks using hoses from acid, chlorine, calgon tanks, etc. Please check with the state to ensure or find out what level of training is required. <I> **** Actions Taken **** Wrote this AR/CR to raise this issue to the proper level for resolution. <N> TREQ 18-0104 initiated to evaluate for potential training of Operations and Maintenance staff.
383808 | CR | 20180823 | CAQ | D | EDR-P-12 Running indications do not match | N | N |  | N | YES | <D> **** Detailed Description **** EDR-P-12 Running indications do not match between G11-P003 and G11-P001-1. When going into a HOLD condition for EDR -DM-9, the hold pump (EDR-P-12) starts as it should. The Control Panel in the RWCR (G11-P001-1) indicates that EDR -P-12 is running, however, the indications on G11-P003 in the hallway indicate that the EDR-P-12 is stopped. <I> **** Actions Taken **** Informed MCR and FIN, wrote CR | 02-00-EDR-P-12
383813 | CR | 20180823 |  | 4 | Snubber Instrumentation Pelican Case Damaged | N | N |  | N | NO | <D> **** Detailed Description **** Upon return of the Snubber Test Bench load cells from calibration at Exelon, the Pelican Case used for transportation was heavily damaged. The pelican case wall was cracked, a handle was broken off and the internal foam material was in major disarray. Pictures in EDMS. The damage was created by the load cell inside by possible drop of the case. All companies involved with the calibration and transportation were contacted resulting in no admittal of known damages. A concern of the validiaty of calibration exists and so the load cell will be sent out for calibration confirmation at Morehouse and a new case will need to be purchased. Recommend trend only. <I> **** Actions Taken **** Documented damage and arranged calibration confirmation by Morehouse.
383814 | CR | 20180823 |  | 3 | ESP-RLY8TDR-X301 NEEDS TO BE REVISED |  |  |  | N | NO | <D> **** Detailed Description **** ESP-RLY8TDR-X301 NEEDS TO BE REVISED Page 22 SN 06210712 change to 06210720 Page 24 SN 06210720 change to 06210712
383815 | CR | 20180823 |  | 4 | Deficiency Tags Containing Outdated/Incorrect Information |  |  |  | N | YES | <D> **** Detailed Description **** Two deficiency tags on the RB 471' elevation were identified with incorrect or outdated information. Tag # 41250 (from 3/27/17) on RWCU-V-34 indicates a leakage rate of 1-2 dpm, but the actual leak rate is closer to 60 dpm. Tag # 42332 (from 9/27/14) on HTP-PTM-29 states that indicator lights 10 and 11A are flashing. Currently, indicator lights 10 and B10-1 are flashing. 11A is not. <N> **** Equipment Description **** RWCU-V-34 HTP-PTM-29 | 02-00-HT-HTP-PTM/29,02-00-RWCU-V-34
383816 | CR | 20180823 |  | 3 | ABN-FIRE needs a correction. |  |  |  | N | NO | <D> **** Detailed Description **** The first note in ABN-FIRE section 5.0 explains the meaning of a star preceding a step. This note comes after step 4.2.1 which has a star preceding it. This explanatory note needs to be before the first use of a star. Please correct this. <I> **** Actions Taken **** Informed fire brigade instructor and wrote this AR/ PCR.
383823 | CR | 20180823 |  | 4 | RWCU-FCV-266B is not responding to RWCU-FC-89B. | N | N |  | N | YES | <D> **** Detailed Description **** RWCU-FCV-266B is not responding to RWCU-FC-89B. While bringing RWCU-DM-1A back online, I was not able to increase flow through RWCU-DM-1B past ~113gpm. While performing SOP-RWCU-DEMIN step 5.7.15, the B demin started at ~155gpm, and A demin had no flow. I started slowly increasing flow through the A demin using RWCU-FC-89A. At ~ 50gpm on the A demin, the B demin drastically reduced flow below 100gpm and the B hold pump started. I stopped raising flow on the A demin, and incresed flow on the B demin. Flow returned to ~120gpm and the B hold pump stopped. RWCU-FC-89B output was 54% at this point. Continuing on with step 5.7.15, I slowly adjusted flow through both demins to ~115gpm, where the A demin hold pump turned off. RWCU-FC-89B output was 69% at this point. Moving onto step 5.7.18, while trying to increse flow through both demins to 135gpm, I was not able to increase flow through the B demin. <I> **** Actions Taken **** RWCU-FC-89B output was taken upto 85% with no change in flow through the B demin. Currently, both demin flows are balanced at ~113gpm. MCR was informed and CR has been written. | 02-00-RWCU-FC-89B,02-00-RWCU-FCV-266B
383824 | CR | 20180823 |  | 3 | ABN-CAS references wrong EPN. |  |  |  | N | NO | <D> **** Detailed Description **** ABN-CAS references wrong EPN. Page 13 has CPR-V-364B as phase separator tank inlet. EPN should be CPR-V-346B. CPR-V-346A and CPR-V-346B are the phase separator tank inlet valves for CPR-TK-92A/B. CPR-V-346B currently does not appear in ABN-CAS.
383826 | CR | 20180823 |  | 4 | First aid injury |  |  |  | N | NO | <D> **** Detailed Description **** While installing a new Functional Area Scorecard report on a bulletin board an employee stuck his finger with a pin. <I> **** Actions Taken **** Employee sent to occupational health Occupational safety and RPM informed. Incident report started
383827 | CR | 20180823 |  |  | AED SPC 308 Table 19 not removed with closure of open issues |  |  |  | N | NO | <C> CR Canceled at the request of the initiator. <D> **** Detailed Description **** High Pressure Core Spray (HPCS) system Design Basis Document (DBD) AED SPC 308 was originally issued in 2006 with five Open Issues specifically listed/described via Table 19 of the DBD and tracked via listed assignments under AR EVAL 12683 (Open issues identified during development of HPCS DBD) - AS 12683-01 through 12683-05. Between 2006 and 2009, nine additional assignments related to potential or necessary AED SPC 308 updates were added to AR EVAL 12683 for tracking - AS 12683-06 through 12683-14. Currently, AR EVAL 12683 has no open assignments (and this parent AR was advanced to COMPLETE staus in 2017). However, AED SPC 308 Table 19 still exists in the DBD - it was never updated or ultimately removed as the listed Open Issue AR assignments were completed. As all these Open Issue tracking assignments are COMPLETE, it appears that AED SPC 308 should be updated to remove Table 19 entirely. <N> Please CANCEL this AR CR 383827 - this issue was recently addressed via issuance of AED SPC 308 revision 14.
383831 | CR | 20180823 |  | 3 | (QA) EGM-1-9 Purpose not consistent with SPV definition |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The Purpose to procedure EGM-1-9. revision 4 states, â€œThis document describes the process for performing a SCRAM Single Point Vulnerability (SPV) review process . . .â€ This purpose is not consistent with the Single Point Vulnerability (SPV) definition. Factual Basis: The revision 4 language is based on revision 0 in which the SPV definition only pertained to preventing plant scrams. The revision 4 SPV definition states â€œa subset of critical components that will directly result in a Turbine TRIP and/or REACTOR SCRAM.â€ Hence, the procedure purpose should be updated to reflect turbine trips. Insights: The purpose of the procedure should be aligned with the SPV definition to ensure that the scoping is clear and not subject to interpretation. When revising procedure language, the entire procedure should be reviewed to ensure consistency and alignment. <I> **** Actions Taken **** Recommend assignment to System Engineering
383836 | CR | 20180823 |  | 3 | ABN-POWER: OPRM Enabled APRM STP |  |  |  | N | NO | <D> **** Detailed Description **** ABN-POWER Step 4.1.4 and its bases refer to the OPRM enabling at APRM STP GE 25% as specified in the COLR. The COLR specifies 24.6%. It would be clearer if the procedure did not round the COLR specified value but used it unchanged. <I> **** Actions Taken **** Recommend changing ABN-POWER Step 4.1.4 to use APRM STP GE 24.6%.
383839 | CR | 20180824 |  | 3 | SOP-ELEC-BKR-OPS section 5.23 |  |  |  | N | NO | <D> **** Detailed Description **** The section 5.23 is for a Ground 'truck' that does not require control power fuses. The ground 'devise' used has Kirk keys that require 125VDC to operate the devise. This prevented the removal of the devise per volume 10.25.141A. <I> **** Actions Taken **** Stop the evolution, place equipment in safe condition and expanded team.
383840 | CR | 20180824 |  | 4 | RWCR Vacuum HEPA has no suction |  |  |  | N | YES | <D> **** Detailed Description **** While attempting to clean the Area around the Resin add tank the vacuum had no suction. <I> **** Actions Taken **** Wrote CR and Wr <N> **** Equipment Description **** RW 467 behind RWCR | 02-00-W-BLDG-MISC
383841 | CR | 20180824 | CAQ | D | RB Door R108 does not latch | Y | Y |  | N | YES | <D> **** Detailed Description **** RB Door R108, the inner airlock door on RB 441, does not latch via the doorknob. The electrical interlock still works. Please repair. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RB 441 off TB corridor | 02-00-R-DOOR-R108
383842 | CR | 20180824 |  | 4 | Work tools blocking access to WCH-CR-51B and deep bed tank. |  |  |  | N | NO | <D> **** Detailed Description **** A work area has been set up next to WCH-CR-51B that is restricting access to both the chiller itself and the tank used for adding deep bed resins. This area requires constant access for operations; consequently, the work area needs to be relocated, perhaps to the basketball court. Please relocate the work area. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 507 by chillers. | 02-00-W-BLDG-MISC
383843 | CR | 20180824 |  | 4 | Battery Charger Room #2 Lights out | N | N |  | N | YES | <D> **** Detailed Description **** Battery Charger Room #2 has half the lights in the room out, including a blue dot light. Please re-lamp. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 467 Vital Island
383847 | CR | 20180824 | CAQ | D | CRD-FCV-2B is indicating closed | N | N |  | N | YES | <D> **** Detailed Description **** CRD-FCV-2B is indicating closed, should be indicating dual postion. Light bulbs were checked and replaced. OPS 2 reports that CRD-FCV-2B is touching the lower limit switch. CRD-FCV-2A is also degraded ( ref. WR 29139118 ). CRS informed. | 02-00-CRD-FCV-2B
383852 | CR | 20180824 | CAQ | D | Sec IDS 20 21 | N | N |  | N | YES | <D> **** Detailed Description **** Sec-IDS 20 21 recieved a malfunction alarm. <I> **** Actions Taken **** Security walked down the zones and found an insolater out on pole 204 in zone 21. Contacted plant electricians, comped the zones, started event log and generated CR/WR | 02-00-SEC-IDS-E/S/20/21
383853 | CR | 20180824 |  | 3 | ABN-LEVEL procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Please add the capability to throttle RFW-V-65A(B) to the low level section step 4.1.9 in between steps b and c.
383854 | CR | 20180824 |  | 3 | 3.3.1 procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Please add the capability to insert control rods when the SCRAM cannot be immediately reset by adding a third bullet to step 5.2.7.b. This bullet should allow the restoration of drive pressure using CRD-FC-600 and CRD-V-3, bypass the RWM, and insert control as necessary by CRS direction.
383855 | CR | 20180824 |  | 4 | CF-TS-40 adjustment | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While Calibrating CF-TS-40 per WO#02082987-01 the as found trip point was out of cal at 61 degrees F, with a desired setpoint of 65+4 and -0. <I> **** Actions Taken **** Adjusted switch to 66 degrees F. and a reset of 72 degrees. As left values are sat.
383856 | CR | 20180824 |  | 4 | CF-TS-41 out of calibration |  |  |  | N | YES | <D> **** Detailed Description **** While calibrating CF-TS-41 the as found trip was out of tolerance at 35 degrees F. with a desired of 60 plus or minus 2 degrees F. <I> **** Actions Taken **** After attempting to calibrate the switch it was unrepeatable and unable to calibrate. The switch also appears to be damaged by the weather. A Work Request will be generated to replace CF-TS-41 <N> **** Equipment Description **** CF-TS-41 | 02-00-CF-TS-41
383857 | CR | 20180824 |  | 3 | SOP-CW-CHEM enhancement |  |  |  | N | NO | <D> **** Detailed Description **** the procedure is missing attachment 6.5 (sodium hypochlorite weight/volume chart) from the table of contents. The attachment is in the back, just need an editorial to place it back on the TOC <I> **** Actions Taken **** initiated CR/WR <N> **** Equipment Description **** sop-cw-chem
383858 | CR | 20180824 | CAQ | D | SEC-IDS-11 12 Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** CAS received a malfunction alarm on IDS 11 12. <I> **** Actions Taken **** Compensatory measures were posted. A walkdown of the area was conducted and nothing was found that could be causing the malfunciton alarms. Shift manager,work week manager, and electical maintenance were notified. CR/WR generated. | 02-00-SEC-IDS-EVAL/11/12
383859 | CR | 20180824 |  | 4 | LPCS Pump Room lights are all dim |  |  |  | N | YES | <D> **** Detailed Description **** LPCS Pump Room lights are all dim. this results in a poor lighting in the Pumproom. Please replace or repair lighting as necessary. <I> **** Actions Taken **** wr/cr <N> **** Equipment Description **** LPCS-PumpRoom rx 422 | 02-00-R-BLDG-MISC
383860 | CR | 20180824 | CAQ | D | lights out above BC-C1-7 charger (local EPN on charger) | N | N |  | N | YES | <D> **** Detailed Description **** lights out above BC-C1-7 charger (local EPN on charger). Blue dot light, second light fixer next to it is also out each ficture is a 2 by 4 foote fixture. <I> **** Actions Taken **** cr <N> **** Equipment Description **** Battery charger room 2, rw467 | 02-00-E-C1-7,02-00-W-BLDG-MISC
383861 | CR | 20180825 | CAQ | C | Drawing M515-3 requires updating |  |  |  | N | NO | <D> **** Detailed Description **** Drawing has references to alarm drops on the FCP-1, -2, and -3. The specific alarm location changed with the latest EC to these panels. | 02-00-FP-CP-FCP1,02-00-FP-CP-FCP2,02-00-FP-CP-FCP3
383862 | CR | 20180825 | CAQ | D | IDS 2 |  |  |  | N | YES | <D> **** Detailed Description **** High alarm rate. 12/24 <I> **** Actions Taken **** Comp measures posted. Walkdown of the area, no known cause found. <N> **** Equipment Description **** IDS 2
383867 | CR | 20180825 |  | 4 | Poor Lighting Conditions Exist | N | N |  | N | YES | <D> **** Detailed Description **** Specifically in the the MC-8B / 8BA Room. <I> **** Actions Taken **** Performed Take 2 Informed MCR <N> **** Equipment Description **** R 522 | 02-00-R-BLDG-MISC
383868 | CR | 20180825 |  | 4 | E-TR-N2 north cooler group fan has a knock | N | N |  | N | YES | <D> **** Detailed Description **** while performing rounds it was noted that the north cooler group bottom left fan was making a knocking sound. <I> **** Actions Taken **** inform CRS and initiate CR/WR. | 02-00-E-TR-N2
383869 | CR | 20180825 |  | 4 | Ops Agg tracking for Buckholz relay oos | N | N |  | N | NO | <D> **** Detailed Description **** Temporary log required per ACMP for Buckholz relay oos. CR/WR written to track when log can be removed after repair. <N> **** Equipment Description **** transformer yard
383870 | CR | 20180825 |  | 4 | Computer point F537 alarming spuriously (MD-TK-2) | N | N |  | N | NO | <D> **** Detailed Description **** Computer point F537 for MD-TK-2 high level alarm is spuriously alarming and causing the alarm typer in the MCR to print out alarms for upwards of 3-5 minutes. This can mask other alarms that may appear on the alarm typer. This CR is to state that the frequency and duration of this alarm is trending up. During the last 4 hours there have been over 1500 entries made on the alarm typer in the MCR for the MD-TK-2 high level alarm F537. <I> **** Actions Taken **** Wrote CR to imform station of degrading trend on this computer point.
383871 | CR | 20180825 |  | 4 | RHR-V-622B Staged Hose Doesn't Drain | N | N |  | N | YES | <D> **** Detailed Description **** For OSP-RHR-M102, the RHR B fill verification, there is a staged hose routed to a drain for step 7.2. For whatever reason, this hose is very resistant to draining, even when the hose is disconnected and the end elevated several feet above the drain. The drain is connected to a short, custom-made section of elevated pipe that may be causing the issue. The original purpose and necessity of this special hose connection should be evaluated to determine whether the device can be removed. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RHR B Heat Exchanger Room 572'
383872 | CR | 20180825 |  | 4 | ROA-FL-1 End of Roll | N | N |  | N | YES | <D> **** Detailed Description **** ROA-FL-1 End of Roll alarm is locked in. <I> **** Actions Taken **** Informed MCR . ROA-FL-1A & ROA-FL-1B filter roll media was just replaced 6/20/18 under WO 02128787. <N> **** Equipment Description **** ROA-FL-1, R572 | 02-00-ROA-FL-1A,02-00-ROA-FL-1B
383873 | CR | 20180826 | CAQ | D | oscillograph start | N | N |  | N | NO | <D> **** Detailed Description **** H13-P800.C4.4-3, alarm. Plant controllers and equipment response was normal. The following sensors were tripped and are reset: J7 500kv neutral ground overcurrent J11 SM-7 undervoltage J12 SM-8 undervoltage J15 230kv undervoltage J16 Main Generator negative sequence. Cause ground fault on 500kv <I> **** Actions Taken **** followed ARP
383874 | CR | 20180826 |  | 4 | Radwaste Elevator getting stuck on 441. | N | N |  | N | YES | <D> **** Detailed Description **** Elevator getting stuck on 441' and not opening doors. This caused an HP to become locked in elevator. Manually opened doors and released HP from his elevator holding cell. <I> **** Actions Taken **** Attempted to fix door by manually opening doors several times. Released HP from elevator. Initated AR and removed elevator from service. . There was no injury as a result of this incident. Elevator outer fire doors are closed. | 02-00-MT-ELEV-4
383875 | CR | 20180826 | CAQ | D | Received P800.C4.3-5 Transformer TR-B reverse power relay al | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** at 8/26 0525 MCR recieved TR-B reverse power relay alarm. In and clear. no abnormal indication on the electric plant. <I> **** Actions Taken **** Followed ARP
383876 | CR | 20180826 |  | 3 | Missing HP Instruments |  |  |  | N | NO | <D> **** Detailed Description **** 2 instruments were unable to be found while performing HP Portable Instrument Inventory WO #02123520-01. Instruments include Model 3096 ID#AD015 and Amp100 ID#RM-50. A search was conducted for these instruments but was unsuccesful. <I> **** Actions Taken **** Initiated this CR, Notified HPS and put a note in HP turnover log to keep an eye out for these instruments.
383877 | CR | 20180826 |  | 4 | TO-DMS-1 Oil Level High | N | N |  | N | YES | <D> **** Detailed Description **** Oil level for the TO-TK-2 line separator is, and has for years been, above the maximum indication. This was only noticed when an operator discovered that a max oil level marking existed, but was facing the wall. After an evaluation is made as to whether or not operation at this level is acceptable and a correction made if not, a new max level mark should be mounted where a person may accidentally see it or a sign installed reading something to the effect of â€œMax level not applicable per [evaluation].â€ Additionally, the tubing where oil level is read is becoming difficult to read near the top. Recommend replacing the tubing at a convenient time. <I> **** Actions Taken **** Informed MCR | 02-00-TO-DMS-1
383878 | CR | 20180826 | CAQ | D | FP-CP-UV/11 Power On Lamp Not Illuminated | N | N |  | N | YES | <D> **** Detailed Description **** The power lamp for FP-CP-UVD/11 is not illuminated. The bulb is not burned out. Keywords: ultraviolet, fire eye <I> **** Actions Taken **** Replaced Bulb Anyway Informed MCR | 02-00-FP-CP-UVD/11
383879 | CR | 20180826 |  | 4 | TR-1-11 Pressure Slightly Negative | N | N |  | N | YES | <D> **** Detailed Description **** The blanket pressure for E-TR-1/11 is very slightly negative. When gas is added, it would be wise to also press up E-TR-6/63, which is at exactly 0psig. <I> **** Actions Taken **** Informed MCR | 02-00-E-TR-1/11
383880 | CR | 20180826 |  | 4 | Condensate on Oil Return Sightglass on COND-P-2C | N | N |  | N | YES | <D> **** Detailed Description **** There is a small amount of condensation forming inside the oil sightglass downstream of COND-TI-12C. This may be an early indication of the same issue found previously in COND-P-2A. Recommend taking an oil sample for water intrusion. <I> **** Actions Taken **** Informed MCR | 02-00-COND-P-2C
383881 | CR | 20180826 |  | 3 | Leak From COND-V-156B Worsening | N | N |  | N | YES | <C> Reopened at request of system engineer to add additional data. <D> **** Detailed Description **** The leak documented in AR 370555 is getting worse. <I> **** Actions Taken **** Informed MCR | 02-00-COND-V-156B
383882 | CR | 20180826 |  | 4 | Battery Charger in Aux Boiler Room | N | N |  | N | YES | <D> **** Detailed Description **** There is a battery charger in the aux boiler room near TSW-PCV-20. It's not connected to anything and there is no WIP sign. It's been there for days, without an apparant reason. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** Aux Boiler Room | 02-00-T-BLDG-MISC
383883 | CR | 20180826 |  | 4 | Lighting Still Abysmal In Turbine Building | N | N |  | N | YES | <D> **** Detailed Description **** The turbing building light situation is still very bad, particularly on the 471 West, where ALL of the overhead lighting around the IBD fan unit is out. These persistant lighting deficiencies should be corrected as soon as possible, because we are probably not in compliance with WAC 296-79-070 at this time. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** Turbine Building | 02-00-T-BLDG-MISC
383884 | CR | 20180826 |  | 3 | E-TR-M3 - Cooler Group 2 Fan Contactor Trip | N | N |  | N | YES | <D> **** Detailed Description **** During response to E-TR-M3 Trouble alarm, discovered contactor for cooling group 2 fan tripped. ABN-TRANSFORMER response successfully reset tripped condition and fan restarted. Trend only <I> **** Actions Taken **** ABN-TRANSFORMER actions to reset tripped contactor | 02-00-E-TR-M3
383885 | CR | 20180826 | CAQ | D | SP-8 Cond >10% From Meter/Recorder Reading | N | Y |  | N | YES | <D> **** Detailed Description **** SP-8 meter and recorder cond readings are >10% from the grab sample but withing 20%. Request meter and recorder be adjusted to match grab sample. <I> **** Actions Taken **** CR and WR written. MCR/SM/CRS and chemistry supervision informed. | 02-00-S-CE-8
383886 | CR | 20180826 |  | 3 | Schedule Directed Tasks That Were Removed from Workweek |  |  |  | N | NO | <D> **** Detailed Description **** Line Item 287 on the Daily Shop and Crew schedule printed 8/23/18 at 1:34 PM is WOT 0207417210 OS: OPS REMOVE RWCU-DM -1B TO/FROM SERVICE. Line item 288 on this same schedule is WOT 0210497807 OS: OPS REMOVE RWCU-DM-1B TO/FROM SERVICE. Line item 288 included a subsequent WOT 0208885202 HC D-RWCU-DM-1B-001 27-AUG-18 04:00. At our beginning of shift meeting we questioned why there wasn't a separate line item to hang D-RWCU-DM-1B-001. Furhter investigation by the crew revealed that every OTHER task associated with WO's 02074172 and 02104978 were crewed to WWM4 (DO NOT WORK-TO BE RESCHEDULED-CONTACT WWM). We determined the two scheduled line items were incorrect. There is no mechanism in place to ensure that a failure to recode all affected tasks to WWM will be detected - we are vulnerable to a recurrence of this. Only a questioning attitide and communication can prevent any shop from performing a task that is incorrectly scheduled. <I> **** Actions Taken **** Contacted WWM to confirm that removing RWCU-DM-1B from service was NOT supposed to be on the schedule for 04:00 8/27/18.
383887 | CR | 20180827 |  | 3 | Procedural enhancement ARP 4.826.P1.3-4 |  |  |  | N | NO | <D> **** Detailed Description **** The ARP for loss of WEA-FN-53A is incorrect. In step 2 is says â€œto prevent hydrogen accumulation in the battery room within 40 hours per ABN-FIRE, Attachment 13.1.â€ The problem is that ABN-FIRE, Attachment 13.1 does not give any guidance at all on what to do about hydrogen accumulation. SOP-HVAC/CR-SHUTDOWN step 5.4.5 says â€œIF a battery room exhaust fan is required to be removed from service, THEN USE portable fans for room ventilation.â€ Recommend the ARP be changed to read the same as the SOP. Also, recommend deleting step 3 of the ARP because it is obvious. Recommend adding as references LCS 1.8.6.1.I and 1.8.6.2.D.
383888 | CR | 20180827 |  | 3 | Procedural enhancement ARP 4.826.P2.3-4 |  |  |  | N | NO | <D> **** Detailed Description **** The ARP for loss of WEA-FN-53B is incorrect. In step 2 it says â€œto prevent hydrogen accumulation in the battery room within 40 hours per ABN-FIRE, Attachment 13.1.â€ The problem is that ABN-FIRE, Attachment 13.1 does not give any guidance at all on what to do about hydrogen accumulation. SOP-HVAC/CR-SHUTDOWN step 5.4.5 says â€œIF a battery room exhaust fan is required to be removed from service, THEN USE portable fans for room ventilation.â€ Recommend the ARP be changed to read the same as the SOP. Also, recommend deleting step 3 of the ARP because it is obvious. Recommend adding as references LCS 1.8.6.1.I and 1.8.6.2.D.
383889 | CR | 20180827 | CAQ | D | TEA-DPIS-53 High Diff Press Alarm | N | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02117220, then taken back to complete <D> **** Detailed Description **** TEA-DPIS-53 High Diff Press Alarm is in on TGHV-3 panel which indicates a high Differential Pressure Across HEPA Filter TEA-HF-52, Recommend replacing the HEPA filter <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TB 441' in Sample room near RFT | 02-00-TEA-DPIS-53,02-00-TEA-HF-52
383894 | CR | 20180827 |  | 4 | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065618 Industrial Scientific Gas Monitor iTX found OOT and Rejected- Parts no longer available. Not used during Calibration cycle. DEF #6729A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
383896 | CR | 20180827 | CAQ | D | SEC-IDS-11 12 not functioning as designed | N | N |  | N | YES | <D> **** Detailed Description **** CAS received a malfunction on SEC-IDS-11 12 for unknown reasons. Request electrical maintenance to investigate. Contact Security for more information at 2185 <I> **** Actions Taken **** Compensatory measures initiated; CR/WR generated | 02-00-SEC-IDS-E/S/11/12
383897 | CR | 20180827 | CAQ | D | SEC-IDS-16 17 not functioning as designed | N | N |  | N | YES | <D> **** Detailed Description **** CAS received a malfunction on SEC-IDS-16 17 for unknown reasons. Request electrical maintenance to investigate. Contact Security for more information at 2185 <I> **** Actions Taken **** Compensatory measures initiated; CR/WR generated | 02-00-SEC-IDS-E/S/16/17
383899 | CR | 20180827 | CAQ | D | SFS-STORM-022 Status Yellow | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of OSP-SFS-D101 SFS-STORM-022 indicates yellow per step 7.1.1. <I> **** Actions Taken **** Per step 7.4 wrote CR. | 02-00-SFS-STORM-022
383901 | CR | 20180827 |  | 3 | Oil Leak on Manitowoc Grove GMK 5225 crane spilled oil. | N | N |  | N | NO | <D> **** Detailed Description **** Manitowoc Grove GMK 5225 Crane (Serial Number 5170-3049) located in front of the GSB developed a small oil leak and spilled about Â½ a Cup of hydraulic oil on the asphalt under the crane. This in not plant equipment. <I> **** Actions Taken **** 1. Oil absorbent material was placed over the oil spot to stoke up the oil. 2. The source of the oil leak was found to be coming from the drum hoist. That drum hoist was taken out of service and the second drum hoist was put into services. SCR was informed and Concurred with actions. 3. The load line on the crane was change over to the second drum hoist and the line was recertified. 4. The Oil absorbent material will be removed in a day or two. 5. The oiler will verify the leak was completely stop by the above actions.
383908 | CR | 20180827 | CAQ | D | PR Form Discrepancy |  |  |  | N | NO | <D> **** Detailed Description **** Incorrect name and SSN was entered into PR form for individual. The previous time they were on site they had an incorrect SSN. This caused access to create a new profile for an individual. <I> **** Actions Taken **** Worked with Access Authorization and Vendor to verify information is correct so individuals could be processed. Recommend CAT D for trending.
383911 | CR | 20180827 |  | 3 | Install a Temporary Power 200 amp fused disconnect, E-MC-3D |  |  |  | N | NO | <D> **** Detailed Description **** To support future temporary power for MT-ELEV-4 a 200 amp fused disconnect will need to be installed in E-MC-3D. During E-SH-6, E-SL-63 or E-MC-6B outages MT-ELEV-4 will require temporary power and with the elevator upgrade SOP -ELEC-BOP-TEMPPOWER will require a different power source . (EC 12277) <I> **** Actions Taken **** Added tasks to 02084844 to configure and install temp power bucket to E-MC-3D. | 02-00-E-MC-3D,02-00-MT-ELEV-4
383912 | CR | 20180827 |  | 4 | TSW-F-2A Leaking Into TSW-M-F/2B | N | N |  | N | YES | <D> **** Detailed Description **** TSW-F-2A is leaking directly into the motor for the below-mounted TSW-F-2B. This is significant and should be adressed in a timely manner. <I> **** Actions Taken **** Informed MCR Took TSW-F-2B RMS to OFF | 02-00-TSW-F-2A,02-00-TSW-F-2B,02-00-TSW-M-F/2B
383915 | CR | 20180827 |  | 4 | PWC-V-591 failed relief valve test | N | N |  | N | YES | <D> **** Detailed Description **** While performing backflow testing on PWC-V-591, relief valve failed to open within tolerance. Reilief valve needs to be rebuilt <I> **** Actions Taken **** Notified supervisor, intiated work request <N> **** Equipment Description **** Southwest corner of CWPH V.5/5.0 | 02-00-PWC-V-591
383923 | CR | 20180827 | CAQ | C | 15.3.7 vacuum breakers | N | Y |  | N | NO | <D> **** Detailed Description **** Working 15.3.7 Vacuum breaker replacement on standpipes, found 1 vacuum breaker of the 2 at each standpipe to be corroded , so the ball inside was seized,and would not move, the other was corroded with ball still moving. frequency should be adjusted , 5 years may be to long. <I> **** Actions Taken **** all replaced with new vacuum breakers. <N> **** Equipment Description **** standpipe vacuum breakers
383924 | CR | 20180827 |  | 3 | Add new EPN to Portal J |  |  |  | N | NO | <D> **** Detailed Description **** CPR-RMS-V/346AB was created in esoms for a first time clearance and needs to be updated in PORTAL J. CPR-RMS-V/346AB is the Selector Switch for TANK A or TANK B Condensate Phase Separator Tank (CPR-TK-92A/B). Located in the RW467 at G11-P001-3. Ref 02G11-05,14,5 02G11 -05,14,50 and 02G11-05,14,32 and SOP-RW/CPR-OPS | 02-00-CPR-TK-92A,02-00-CPR-TK-92B,02-00-CPR-V-346A,02-00-CPR-V-346B
383925 | CR | 20180827 |  | 4 | SEC-TN-6 is not functioning as designed | N | N |  | N | YES | <D> **** Detailed Description **** SEC-TN-6 Locked up and is making a buzzing noise. Request maintenance to investigate <I> **** Actions Taken **** Unit has been removed from service; CR/WR Generated | 02-00-SEC-TN-6
383927 | CR | 20180827 |  | 3 | CATID 54407143 for PWC-RV-105 replacement set pressure |  |  |  | N | YES | <D> **** Detailed Description **** While performing task preview/pre-job for PWC-RV-105 shop task (WOT 02085633-05) it was identified the valve supplied was marked as set at 150 psig. The CATID references 115 psig set pressure. Review of CATID 54407143 description identified the valve as a range of 50-150 psig with set pressure at 115 psig. <I> **** Actions Taken **** Generated CR. Will follow up with supply chain for last PO and trace of UTC 549482. No impact to plant. Work task states to contact supervisor for further instructions if the setpoint does not match datasheet. Reviewed inventory usage and the only three valid "confirmed" usages in plant in the past were on PWC -RV-105 (Q level G, NSR, Seismic Cat II). Last PM performance under WO 01193358-05 performed a vacuum check prior to installation and verification of stated nameplate matched the datasheet. Craft verified current valve in installed in field for EPN PWC-V-105 was verified shown set at 115 psig. CATID inventory usage shows one usage from 2/12/04 under MR 61748 for Cost Center 0219400, this was issued under Issue Ticket 83130000 however is appears this was never plant equipment as it was not tied to an active WO. <N> **** Equipment Description **** Relief valve for PWC-P-103 min flow in Well Pumphouse #2 | 02-00-PWC-RV-105
383928 | CR | 20180827 |  | 3 | RWCU Quick Disconnect EPNs not included on MEL |  |  |  | N | NO | <D> **** Detailed Description **** RWCU-QDC-1A, RWCU-QDC-1B, RWCU-QDC-2A, and RWCU-QDC-2B are not included in the Master Equipment List (asset suite D030 panel). The components are include on the following drawings: M523-2 (all); M719-1 (RWCU-QDC-1A & 2A); M719-2 (RWCU-V-1A & 2A); 215-00,14704,1 (RWCU-QDC-1A); 215 -00,14705 (RWCU-QDC-1B); 215-00,3209 (RWCU-QDC-2A); 215 -00,3210 (RWCU-QDC-2B). The components need to be added to the master equipment list. <I> **** Actions Taken **** Discussed with supervisor and initiated CR
383929 | CR | 20180827 |  | 3 | Annual TTHM at IDC exceeded MCL |  |  |  | N | NO | <D> **** Detailed Description **** Annual sampling of the Industrial Development Complex Water System (92023F) exceeded the maximum contaminant level (MCL) for Total Trihalomethane. The MCL is 80 ug/L. The result from the August 8, 2018 sampling was 90.3 ug/L. <I> **** Actions Taken **** The Regional Office of the WA State Department of Drinking Water was notified by two Environmental Scientists (org. 23000). A repeat sample will be collected this week. <N> CR Edited in â€œImmediate Actionsâ€ to remove names and replaced with titles. Coaching provided.
383931 | CR | 20180827 | CAQ | D | Broken hose clamp,antifreeze leak found during take2 | N | Y |  | N | YES | <D> **** Detailed Description **** Broken hose clamp and antifreeze leak found during prestart take 2, crew found coolant on the floor and traced it back to a broken hose clamp and also found where the coolant line hoses are leaking. The crew was preparing to start DG4 to support Annual maintenance 02101035-01 when they discovered the issue. <I> **** Actions Taken **** Stopped, contacted their supervisor, took photoâ€™s and wrote this CR | 02-00-E-GEN-DG4
383949 | CR | 20180828 |  | 3 | Maint. eWp Closure not being completed in a timely manner |  |  |  | N | NO | <D> **** Detailed Description **** Since transitioning to eWp Maintenance has not closed work packages in a timely manner which has a downstream effect on future work implementation. Current department expectation is to have packages to complete status within 14 days. <I> **** Actions Taken **** Maintenance Management informed Future Actions: 1. Benchmark other stations and then set eWp package closure expectation. 2. Revise MIâ€”3.6.4 to align with eWp closure process. Include package closure timeliness. 3. (Assignment to each component manager and SSC) Develop and implement recovery plan to maintain eWp package closure to 14 days until expectation is set from benchmarking activity.
383951 | CR | 20180828 | CAQ | C | [NRC] Lack of 50.59 screen |  |  |  | N | NO | <C> CR requested to be moved to Approved Status. <D> The NRC identified a concern with the lack of a 50.59 screen for an evaluation performed in EC-17325 (DES-2-11) that described the security lock on B-Door-G200. Recommend CAQ-C/AR-LIC. <I> Per DES-2-11 "This EC EVAL process provides a standardized method for documenting Engineering Evaluations, which are NOT related to plant modifications." <N> There was no change to the plant as a result of the associated EC 17325 (therefore no 50.59 was performed). The EC was performed four months after the orginal CR 379120 condition, which was already corrected when the EC was generated . The EC was to provide a reasonable input that the door would have remained functional due to an installed security lock. The EC did not install the security lock. This EC was for PAST Operability and did not make any changes to the plant. | 02-00-B-DOOR-G200
383952 | CR | 20180828 |  | 3 | TMU-FIS-5C IMDS needs correction | N | N |  | N | NO | <D> **** Detailed Description **** Found TMU-FIS-5C IMDS does not include the use of second switch (S2). Reference drawing AED ELC E1011 (F-4). <I> **** Actions Taken **** Submitted marked up IMDS to engineering. Discussed with supervision. | 02-00-TMU-FIS-5C
383954 | CR | 20180828 |  | 4 | MT-HOI-40 Main Line Swtich | N | N |  | N | YES | <D> **** Detailed Description **** MT-HOI-40 Main Line Swtich need to be replaced. The swtich handle is rotating 360 degs but the swtich remains on. The cord cap is disconnected no power is present at the crane. Also labeling is need to verify off and on status of the main line swtich. <I> **** Actions Taken **** Supervisor notified. CR WR created. <N> **** Equipment Description **** MT-HOI-40 | 02-00-MT-HOI-40
383957 | CR | 20180828 |  | 3 | CVI DWG 21A-00,26,1 rev A is not the current vendor drawing |  |  |  | N | YES | <D> **** Detailed Description **** Currently, Portal J indicates that the current revision of CVI DWG 21A-00,26,1 (Vendor Document RX-164440) is revision A and the currently uploaded Portal J image for CVI DWG 21A-00,26,1 is revision A of the vendor document. However, CVI OMM 21A-00,107 also includes Vendor Document RX-164440 and the revision of this document in the O&M manual is revision B (issued 3-18-77). This drawing is information for RCC-P-1A(B,C) and RCC-M-P/1A(B,C). CVI DWG 21A-00,26,1 should revised to revision B using Vendor Document RX-164440 revision B from CVI OMM 21A-00,107 (exists as pgs 20/85 and 55/85 of the currently uploaded pdf image for CVI OMM 21A-00,107 revision 4 in Portal J). This is a legacy issue. The change for revision B of Vendor Document RX-164440 was essentailly an editorial clarification (changed TAG NOs RBCC-P-1A, B, C on the drawing to RCC-P-1A, 1B & 1C). | 02-00-RCC-M-P/1A,02-00-RCC-M-P/1B,02-00-RCC-M-P/1C,02-00-RCC-P-1A,02-00-RCC-P-1B,02-00-RCC-P-1C
383958 | CR | 20180828 |  | 4 | poor lighting on RB 501 steam tunnel | N | N |  | N | YES | <D> **** Detailed Description **** lights need changed out. could be a safety issue. <I> **** Actions Taken **** cr written.MCR notified <N> **** Equipment Description **** RB 501 area before steam tunnel | 02-00-R-BLDG-MISC
383959 | CR | 20180828 |  | 4 | LPCS pump room lighting needs changed out | N | N |  | N | YES | <D> **** Detailed Description **** lighting in LPCS pump room needs changed ot. This could be a safety issue. <I> **** Actions Taken **** MCR notified <N> **** Equipment Description **** RB 422 in LPCS pump room | 02-00-R-BLDG-MISC
383960 | CR | 20180828 |  | 3 | DLR issue period extended beyond DPW date. |  |  |  | N | NO | <D> **** Detailed Description **** While performing low dose margin and DPW review it was noted that one DPW was issued a DLR during the period of declaration and maintained and entered the RCA after the declaration was withdrawn with the same DLR. If significant exposure to the DLR, that exposure could have been attributed to the period of declaration. The total exposure to the DLR was less than the monthly and gestation period administrative limits. All RCA entries were made after the withdrawal as a DPW. Whole Body Count where preformed as required. <I> **** Actions Taken **** Recommend brief to individuals who routinely issuing DLRs why issuing period for DPW DLRs is important. Notified RP supervision
383961 | CR | 20180828 |  | 4 | DG-3 end of hallway stairway needs light replacment | N | N |  | N | YES | <D> **** Detailed Description **** stairway at end of hallway going up into DG-3 room needs light replaced. Could be a safety issue. <I> **** Actions Taken **** MCR notified <N> **** Equipment Description **** 441 DG hallway | 02-00-D-BLDG-MISC
383964 | CR | 20180828 |  | 3 | ISPM-17 Revision Request |  |  |  | N | NO | <D> **** Detailed Description **** During the next revision to ISPM-17, please clarify that the use of air-filtering facepieces (dust masks) does not require completion of attachment 7.2. Currently, the guidance leads personnel to complete the attachment (nonradiological respirator authorization) for dust masks used in the Radiologically Controlled Area . Dust masks are not controlled by the respiratory protection program, and there are no prerequisites related to donning one (such as training, medical evaluations, or fit tests). Therefore, approval of issuance is unnecessary. Also, dust masks are specifically prohibited in Regulatory Guide 8.7 for protection from radiological hazards. It may be beneficial to clarify this in the ISPM. <N> ISPM-17 was revised and issued 8/29/18.
383965 | CR | 20180828 | CAQ | D | IDS 11/12 | N | N |  | N | YES | <D> **** Detailed Description **** IDS 11/12 are not functioning as designed. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Comp measures posted, CR/WR generated | 02-00-SEC-IDS-E/S/11/12
383966 | CR | 20180828 | CAQ | C | NRC Question â€“ SWPH building doors are classified Crit R |  |  |  | N | NO | <D> **** Detailed Description **** NRC Question â€“ Currently SWPH building doors are classified as Critically R. The NRC wants to know where the Maintenance Rule Run-To-Maintenance Justification exists. Currently no approved justification exists in the Maintenance Rule program. . PPM 1.5.13 requires that components that support Maintenance Rule in-scope function and are classified as Crit. R (run-to-maintenance) get approval from the Maintenance Rule Expert Panel. . CR 00280168 (from 3/8/2013) documented that some of the requirements in PPM 1.5.13 had not been completed in the past when Crit R was assigned some components. Specifically, the CR identified that components in the past did not get the Maintenance Rule Expert Panel approval for items being assigned Crit R. . The corrective action was to review Crit. R classifications of components that cause a Maintenance Rule failure, as we discover them, and present the criticality assignment to the MRule Expert Panel for approval. . Engineering Instruction SYS-4-22, Section 7.3.9.m requires that Condition Report (CR) be written if a Maintenance Rule failure is identified and the failed component is classified as Crit. R. . SW building door (B-DOOR-G200) has not had a Maintenance Rule failure since CR 00280168 was generated. <I> **** Actions Taken **** Reviewed this issue with Licensing personnel. | 02-00-A-DOOR-G100,02-00-B-DOOR-G200,02-00-R-DOOR-R106
383967 | CR | 20180828 | CAQ | C | WO 021263798-01Returned, instructions did not match componen |  |  |  | N | NO | <D> **** Detailed Description **** WO 021263798-01Returned, instructions did not match component in the field. This was not noted to just prior to performing work. The style/model in the field has only one lock down. EHO's (HPCS-EHO-1C) for all DG's will need to be labeled for Plant status control. Work instructions will need to be checked/revised for all DG's. <I> **** Actions Taken **** Provided pictures to planning and Engineer sent vendor info to planning. Need to walkdown other DG's and verify style/model that is installed. Other DG WO's will be listed in cross referrence.
383970 | CR | 20180828 |  | 3 | Quarterly CORC Danger & Local Tag Audit (WO 02122671) |  |  |  | N | NO | <D> **** Detailed Description **** Quarterly CORC Danger & Local Clearance Audit 10CFR50.59 The Quarterly CORC Danger & Local Tag Audit (WO 02122671) has documented the danger & local clearances that have been hanging for GE 30 days. 3 new clearances added to this total since the last audit; L-E-BU-DG441/1X-001, L-SCH-CR -51 -001, D-WRA-FN-52 -002. Request Technical Services/Systems Engineering Manager (or designee) to determine whether a 50.59 review is required. <I> **** Actions Taken **** CR Written
383971 | CR | 20180828 |  | 3 | Quarterly CORC Caution Tag Audit (WO 02122674) |  |  |  | N | NO | <D> **** Detailed Description **** Quarterly CORC Caution Clearance Audit 10CFR50.59 The Quarterly CORC Caution Tag Audit (WO 02122674) has documented the caution clearances that have been hanging for GE 30 days. There are 19 new Caution clearances added to this total since the last audit: C-ANN-P800/C3 -002, C -E-DISC-7A2E -001A, C-E-TR-N1 -001, C-HD-V-18D -001, C-HV -V-30D -001, C-IRM-RMS-S6 -001, C-OG-DY-30A -001, C-OG-RF -20C -002, C-REA-FU-3 -001, C-RFW-TR-1 -001, C-RPS-RLY-K10F -001, C-RPS-RLY-K10F -002, C-RRC-VMP-1 -003, C-SS-V-41 -001, C-TMU-V-104 -001, C-TO-EX-1A -001, C-TO-P-BLP -003, C-TOA-AW-1A -002, C-TOA-DPIC-2A -001.
383973 | CR | 20180828 |  | 3 | eWP Comment on Returning H/OPS WOs |  |  |  | N | NO | <D> **** Detailed Description **** When a WO is taken to field work complete and it has a â€œhold for operationsâ€ there is no method to return the WO to working if steps are missed or additional data needs to be entered. The WO is unable to be edited by the workers while in H/OPS, only SROs can edit the WO. The only options to fix an error are to â€œreturn to supervisorâ€ which sends the WO back to the planning stage or have the workers access the WO on the SROs tablet which is burdensome. Please add an option to set the WO back to working so errors can be easily corrected. <I> **** Actions Taken **** Discussed with PSRO, wrote CR to request fix . Same issue is reported in CR 00384040. <N> Same issue was reported under CRs 00384061 & 00384040. . Work will be performed under CR 00384061, Closing CR 00383973. Cross Reference panel has been updated.
383976 | CR | 20180828 | CAQ | C | CVI drawing inaccurate |  |  |  | N | NO | <D> **** Detailed Description **** During the clearance hang for D-E-DP-S1/2F-001 the annunciator power for COND-DP-DM/1 was transferred from E -DP-S1/2F to COND-PP-DM/1 which is AC powered. The expected system response was that the Lundell inverter for the annunciator panel would convert the AC power to DC power to maintain power to the annunciator panel and alarm horn. An annunciator panel test revealed that the annunciator windows were energized but the alarm horn did not function. <I> **** Actions Taken **** The clearance hang was stopped and the planner, Engineering, and Main Control Room were notified. A voltage check was performed that confirmed that DC voltage was not available to the alarm horn as expected. The Shift Manager determined that there were adequate controls in place to allow the clearance hang to continue and for the work to be performed. The initial Engineering assessment was that the CVI drawings were not reflective of the internal wiring of the inverter or the associated controls. This discrepancy did not impact the clearance boundary of the associated work. Pictures of the inverter and termianal strips were uploaded to EDMS. <N> The drawing referenced is E546-8VB-2 at F/7. Contact D .Tonthat for information. . Approved for Closure by Acting Supervisor, Jim Hysjulien.
383977 | CR | 20180828 |  | 3 | (Planning)Electronic WO revisions instead of paper rev sheet |  |  |  | N | NO | <D> **** Detailed Description **** We are still using paper WO rev sheets for eWP. Need to change our procedures to allow route lists to approve revised WO instructions. Should be routed just like the iinitial approvals, can be routed to just the required groups/individuals. <I> **** Actions Taken **** Paper copies are a waste of time going to individuals for signatures and then scanning the hard copy into eWP.
383978 | CR | 20180828 |  | 4 | Placard came off of BS-PIC-18A | N | N |  | N | YES | <D> **** Detailed Description **** A placard describing valve movement relative to controller output pressure has fallen off of the front of BS-PIC-18A and is lying on at the foot of instrument rack E-IR-32. This is an Operations aid. Please re-affix the placard. [The placard was transferred when a new controller when installed under WO 02128896 in June2018, but has fallen off.] <I> **** Actions Taken **** Selected to generate WR to correct the condition. Informed supervisor <N> **** Equipment Description **** TG 471E | 02-00-BS-PIC-18A
383979 | CR | 20180828 |  | 4 | Current readings not obtained at E-DISC-DPS12F/3 | N | N |  | N | NO | <D> **** Detailed Description **** Electricians tried to obtain current readings at E-DISC -DPS12F/3 to satisfy PMT for new QMB disconnect switches, however, the work instructions define current readings on the positive cable which does not have enough clearance from the top of the enclosure to adequately allow for the jaws of the amp clamp to fit around. The load wire on Circuit #3 appears to be #4awg and is firmly installed. Electricians felt that repositioning the load wire may be too intrusive and felt that a CR and WR be generated that would allow for the removal of the panel side covers. Per discussion with supervision, CRS and SM, WO#02116243-03 will be taken to finished status and the remaining PMT data be collected via WR. <I> **** Actions Taken **** Notified Supervisor, CRS and SM. Generate CR and WR pictures available in Dataglance media folder for reference. wo#02116243-03 . What is the WR number? No WR is Xref'ed to AR CR 383979 as of 06:30 hrs 08/29/18. . <N> **** Equipment Description **** RW control Room E-DISC-DPS12F/3 | 02-00-E-DISC-DPS12F/3
383980 | CR | 20180828 | CAQ | D | Unable to start DG4 to perform Annual maintenance | N | Y |  | N | YES | <D> **** Detailed Description **** Unable to start DG4 to perform Annual maintenance WO 02101035-01. Craft followed 10.20.15 and got to step 10.2.3 to depress manual run/stop button and DG4 didnâ€™t start. Craft stopped and contacted supervisor. The crew received instruction to use SOP-DG4-START to perform start (used SOP to line up heater breakers) while performing SOP-DG4-START craft notated that there are 20 Fault codes, Craft was unable to get DG4 started with SOP-DG4-START as well. It appears there is a computer issue with DG4 and requires trouble shooting to start. <I> **** Actions Taken **** Stop, contacted MCR and supervision wrote this CR | 02-00-DG-CP-DG4,02-00-E-DG-4,02-00-E-GEN-DG4
383981 | CR | 20180829 | CAQ | C | Unable to perform/complete ISP-APRM-B303 Step 7.11.4 | Y | N |  | N | NO | <D> **** Detailed Description **** Unable to perform/complete ISP-APRM-B303 Step 7.11.4 in support of WO 02100568-01 due to as found data reflect growth rate factor setpoints and amplitude threshold setpoints in revised Instrument Master Data Sheet from EC 17304 and AR 377683 these changes should have been to IMDS and to the/their related surveillances. ISP-APRM-B303 Parameter needs to a revision to reflect the changes made in AR 377683 IMDS setpoints <I> **** Actions Taken **** Stopped contacted supervision and SM need a PCN for ISP -APRM-B303 table 7.11b to continue calibration <N> **** Equipment Description **** MCR, APRM-CHS-3
383982 | CR | 20180829 | CAQ | C | CTP calculation not available on TDAS or PPC | Y | N |  | N | YES | <D> **** Detailed Description **** At 02:28 on 29 Aug 2018, CTP calculation data stopped updating on TDAS which is the primary computer system. Reset CTP inputs per SOP-COMPUTER-OPS and data returned for approximately 1 minute then went away again. Subsequent resets of CTP inputs were unsuccessful. All process on the U1 screen indicate green. Considered shifting to PPC but could not comply with step 5.7.2.d since all average power fields are also blank on PPC. There are PPC error messages n the CRT and a red error light on the computer itself. Request TDAS or PPC be restored to service. <I> **** Actions Taken **** Entered ABN-COMPUTER. Contacted Computer Engineering and IS Duty officer. Continued to attempt to restart processes. <N> **** Equipment Description **** MCR LEFM status and mass flows did not display any abnormal variations before, during, or after the loss of CTP in the control room. This issue therefore does not appear to have been caused by LEFM. | 02-00-PPC-COMP-8715,02-00-TDAS-COMP-8715
383988 | CR | 20180829 | CAQ | C | SOP-ELEC-SM8-MAINT needs RCC-V-48 instructions corrected |  |  |  | N | NO | <D> **** Detailed Description **** SOP-ELEC-SM8-MAINT steps for gagging and ungagging RCC-V-48 need to be corrected. The pages affected are pg 18,49,78,96. IE step 5.1.7.g.2 "HOLD OPEN RCC-V-48..." does not work. Maintenance has work instructions to uncouple air line and manually lift stem off its seat to place gagging device into position. Holding valve open with RMS does not work (See WOT 02115615-21 for work instructions ). <I> **** Actions Taken **** wrote CR | 02-00-RCC-V-48
383996 | CR | 20180829 |  | 3 | PPM 3.3.1 QC needs procedure step correction |  |  |  | N | NO | <D> **** Detailed Description **** PPM 3.3.1 QC Quick Card Rev 1 minor Rev 1 step 3.1.4 directs continuing with PPM 3.3.1 step 5.2.3. Should say step 5.2.4 due to revision in May 2018 renumbering steps.
384004 | CR | 20180829 |  | 4 | Received RFT A/B TROUBLE, H13-P840.A1.3-4, alarm. | N | N |  | N | YES | <D> **** Detailed Description **** Received RFT A/B TROUBLE, H13-P840.A1.3-4, alarm concurrent with transferring SM-2 from TR-S to TR-N1. Both feed pump continue to operate normally. There are 7 alarms indicated on the alarm screen. The RFW-P-1B Power Supply 2 fail seems to be the biggest cause for concern. Nothing else appears abnormal. Reference previously written CR 383791 and WR 29144269 from 23 AUG 18 where RFT-UPS-2B and RFT-E/S-3B/PS2 were found deenergized. <I> **** Actions Taken **** Took a photograph of the alarm screen at SM request. | 02-00-RFT-UPS-2B
384005 | CR | 20180829 |  | 3 | (QA) Poor Radiological Behaviors observed during Fire Drill |  |  |  | Y | NO | <D> **** Detailed Description **** Poor radiological behaviors were observed during the Training Crew Fire Brigade drill on August 23, 2018. 1. When laying out a firehose, one of the Fire Brigade members inadvertantly allowed the hose to cross a contaminated drain and knock over the radiological information sign. The sign indicated "Contamination on Top of Drain". Peer to peer coaching was observed when another team member coached the individual to leave the hose and use a different one to avoid the spread of contamination. 2. To address the potentially contaminated hose, another member contacted HP to survey the hose but then subsequently moved the hose off of the drain with their feet. This had the potential to spread contamination to a larger area. The follow up HP survey did not identify contamination and the hose was cleared for use. <I> **** Actions Taken **** Coaching provided at debrief.
384006 | CR | 20180829 |  | 4 | FDR-FU-19 reduced runtimes | N | N |  | N | YES | <D> **** Detailed Description **** While processing water with a fresh precoat on FDR-FU-19 the precoat only lasted for 1.75 hours before being exhausted on high DP. The cause of the reduced runtimes could be filter/septa problems or high iron or something else. FDR-TK-22 waste water was part of the water being processed at the time. The total resin capacity for FDR-TK -22 at the time of processing was 105 ft out of 180 ft. An expedited resin transfer out of FDR-TK-22 probably would lengthen the runtimes for FDR-FU-19. <I> **** Actions Taken **** Informed CRS and wrote CR <N> FDR-TK-22 is scheduled for a full resin transfer on 8/30/18 per WR 29144206. Degradation in performance was previously identified and communicated to ensure a FDR-TK-22 can be scheduled as soon as possible. | 02-00-FDR-FU-19
384014 | CR | 20180829 |  | 4 | Editorial Enhancements for ISP-APRM-B301 to B304 |  |  |  | N | NO | <D> **** Detailed Description **** The IMDS for APRM in support of Channel Calibrations goes through updates pending Rx Eng input or EC changes. Those values need to be removed from the APRM calibration procedures and the IMDS needs to be referenced for usage in applicable sections. ISP-APRM-B301, section 7.12, tables 7.12a and 7.12b ISP-APRM-B302, section 7.11, tables 7.11a and 7.11b ISP-APRM-B303, sectoin 7.11, tables 7.11a and 7.11b ISP-APRM-B304, section 7.11, tables 7.11a and 7.11b Red-lined mark up attached to EDMS. This CR documents and administrative procedural enhancement recommendation to support future surveillances with accurate information without the adminstrative burden of conflicts between procedure IMDS values and current rev of IMDS. Current rev of IMDS needs to be used at all times. Recommend this CR CAQ C to Maint Procedure Writters. <I> **** Actions Taken **** Notified Procedure Writter and Systems Supervisor <N> ***General notes*** This issue has been added to the Maint. procedure revision data base. A link to the procedure revision data base has been added to the EDMS of this AR. No further actions are needed.
384015 | CR | 20180829 |  | 3 | PPM 16.11.6 needs revision |  |  |  | N | NO | <D> **** Detailed Description **** PPM 16.11.6 section 7.2.17 step #4 - â€œCOUNT the second iodine cartridge with the inlet side facing down using the Iodine.lib library.â€ Since the new Stack monitor does not have a second filter this step needs to be changed. We still do have filter stations on the RX 606â€™, that theoretically could still be used with a temporary sample cart, it might be feasible to keep the ability to count a second filter in the procedure. The procedure could say â€œIF a second iodine cartridge was collected THEN count the second iodine cartridge with the inlet side facing down using the Iodine.Lib library.â€ Until the procedure is changed the chemistry technician will have to reference this CR on the weekly surveillance and get MCR permission to N/A the step. It will add work to this already labor intensive surveillance. <I> **** Actions Taken **** Notified PSRO, Chemistry supervision, Chemistry specialist / proceedure sponsor.
384016 | CR | 20180829 |  | 3 | SOP-DG4-START needs some enhancements for better compliance. |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** SOP-DG4-START step 5.1.3b directs determination of corrective actions for fault codes per attachment 6.2. This attachment only tells what a fault code means. Attachment 6.3 tells how to clear a fault code even though the beginning of attachment 6.2 does direct going to attachment 6.3 for category D faults. A step directly following step 5.1.3b stating â€œAddress fault codes per Attachment 6.3 â€œ would help operators find the actual solution to the problem rather than just identifying the problem. Please add this to the procedure. A similar step needs to be added to SOP-DG4-PM following step 5.1.12b that directs to attachment 7.3. <I> **** Actions Taken **** Discussed with supervisors and EFIN and wrote this AR/PCR.
384017 | CR | 20180829 | CAQ | C | WO tasks performed but cancelled.Records are not being saved |  |  |  | N | NO | <D> **** Detailed Description **** Previous CR 00382392 documents this same issue, but was closed out without addressing the entire issue. If a PM type WO task gets cancelled by Asset Suite due to completing the PM's out of sequence, there is a potential for the record copy of the procedure to be "lost" and not sent to records by data glance. This can happen when there are multiple WO tasks for the same PM going through the process (such as a weekly PM) and the PM's are not closed out in sequence based upon their due date. If "last week's PM" WO task is closed out before the current PM task, then the current PM task is cancelled by the system even though it was performed. When a task is cancelled dataglance "dumps" all the associated documents, and there are no hard copies (typically) so the Record is lost. This aspect of the problem was not addressed by the earlier CR. <I> **** Actions Taken **** Initiated CR Communicated to the WM module lead Recommend investigation/resolution and corrective actions to address the Records aspects.
384019 | CR | 20180829 |  | 3 | EC MALT 9605 did not address all changes for RCC-M-P/1A | N | N |  | N | YES | <D> **** Detailed Description **** Minor Alteration design change EC MALT 9605 was prepared in 2010 under AR EVAL 181852 to authorize replacement of RCC-M-P/1A with CID 20018 (and was plant implemented via PM WO 01155945 in 2012). In addition to differences in full load current, bearings, and KVA code (which were fully evaluated under EC MALT 9605), there were also differences in motor weight and conduit box size/location which were not addressed by the issued EC MALT 9605 package. The issued EC MALT 9605 package failed to update CVI DWG 21A-00,26,1 and CVI OMM 21A-00,107 with new information that was supplied by the vendor under PO 00329718 in 2009 for the replacement CID 20018 motor. Additionally, the weight change for the motor (from ~1250 lbs per CVI DWG 21A-00,26,1 and CVI OMM 21A-00,107 to 1620 lbs per the vendor documentation in PO 00329718) was not addressed by the issued EC MALT 9605 package. According to Portal J MEL, RCC-M-P/1A is nonsafety-related (NSR), Quality Class 2, and Seismic Category 2 -- installed in the Reactor Building on 548' elevation. There are no QC 2/1 concerns associated with this AR CR 384019 condition as there are no safety-related targets in the vicinity of RCC-M-P/1A on R548' below the motor. This issue was identified while reviewing documentation associated with proposed similar replacement of RCC-M-P/1B under AR EVAL 283724 (also proposed similar replacement of RCC-M-P/1C under AR EVAL 301348). . | 02-00-RCC-M-P/1A
384020 | CR | 20180829 |  | 3 | Investigate seemingly short report time in PPM 16.12.2 |  |  |  | N | NO | <D> **** Detailed Description **** This does not affect plant operation. Procedure PPM 16.12.2 states in the conditional portion of step 6.7 â€œIF the gaseous effluents are being discharged without treatment and in excess of the above limits, in lieu of a Licensee Event Report (LER) THEN PREPARE and submit to the Commission within 10 days, a special report as outlined in ODCM 6.2.2.5.â€ However, the ODCM requirement in 6.2.2.5 states that under these conditions the special report must be submitted to the NRC within 30 days. The reporting time requirement in 16.12.2 should be investigated and changed to match the reporting time requirement in the ODCM if appropriate. Reccomend assigning to chemistry. <I> **** Actions Taken **** Reviewed ODCM and ODCM bases.
384021 | CR | 20180829 |  | 4 | SQA Form sent to Records Control without Transmittal |  |  |  | N | NO | <D> **** Detailed Description **** A record was sent to Records Control without a transmittal attached. Please refer to SWP-REC-02 Section 4.3.2 for the submittal process. <I> **** Actions Taken **** Notified my supervisor. Sending Record back to Information Services for correction/resubmittal.
384023 | CR | 20180829 |  | 3 | Industrial safety concern with 30/60Amp disconnects | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** It appears that Energy Northwest has purchased multiple 30 or 60 amp safety switches from Platt Electric that may not deenergize even when the handle is in the off position. In discussions with procurement engineering it does NOT appear that any of these are being used in the plant but instead by facilities. See EDMS for the safety bulletin. <I> **** Actions Taken **** Discussed with procurement engineering.
384024 | CR | 20180829 |  | 3 | EC FCR 7825 not cancelled with EC MPDC 6826 |  |  |  | N | NO | <D> **** Detailed Description **** Noted in passing that EXPIRED status EC FCR 7825 is currently listed in Portal J as an outstanding modification against AED MEC M525-1 (this FCR is also outstanding against CVI ISO 317-00,4189 and CVI ISO 317-00,4869,1). However, EC FCR 7825 was issued in 2009 against/for EC MPDC 6826 which was advanced to CANCELED status on 06/20/18. EC FCR 7826 should have had its ADL listing cleared and been advanced to CANCELED status when EC MPDC 6826 was advanced to CANCELED status. Recommend assignment to Electrical Design Engineering for resolution. This is an administrative issue only.
384025 | CR | 20180829 |  | 4 | COND-V-119C 20" C booster pump check valve oscillating posit | N | N |  | N | YES | <D> **** Detailed Description **** The C booster pump discharge check valve, COND-V-119C, has shown unexpected movement for more than 2 years. While at 100% power it would normally be expected to be full open as evidenced by a stationary (once opened from flow) check valve weighted arm position. This is not the case, at any point in time movement can be seen. The exact cause of this movement is not known, may be due to valve internals or improperly positioned counter weights. The movement has not changed substantially but has been constantly present over 2+ years. <I> **** Actions Taken **** Informed SM. | 02-00-COND-V-119C
384026 | CR | 20180829 |  | 4 | TMU-V-18B leaks by | N | N |  | N | YES | <D> **** Detailed Description **** During PMT (WO 02131108-05) of replacement of TMU-FIS-5C it was observed that with TMU-V-18B closed that TMU-FIS-5C indicated 3 gpm flow. this is evidence that TMU-V-18B is leaking by. Recommend replaceing TMU-V-18B <I> **** Actions Taken **** Wrote CR. | 02-00-TMU-V-18B
384027 | CR | 20180829 |  | 4 | E-TR-M3 Gas Analyzer Yellow Caution Light Lit | N | N |  | N | YES | <D> **** Detailed Description **** Yellow Caution light lit on E-TR-M3 Gas Analyzer (E-AY -TR/M3) <I> **** Actions Taken **** Notified CRS | 02-00-E-AY-TR/M3
384028 | CR | 20180829 |  | 3 | DCW Therm. Perf. Data collection delayed. |  |  |  | N | NO | <D> **** Detailed Description **** During data collection for DCW-HX-1C thermal performance, data collection was delayed by ~30minutes due to SW flow indication on the Fluke not recording properly. I/C was notified and was able to restore flow indication on the Fluke Test equipment and 30 minutes of data collection was restarted. Data was verified collected successfully. Going through the procedure for setting up the test equipment and collecting the data it was found that the procedure could be enhanced for the test equipment setup and data collection . Recommend update ppm 8.4.63. <I> **** Actions Taken **** Discussed with SM and Supervisor
384029 | CR | 20180829 | CAQ | C | (QA) ISCR and LBID not performed for APRM setpoint changes | Y | Y |  | Y | NO | <D> **** Detailed Description **** (QA) APRM-CHS-3 setpoints are being changed per WO 02100568-01 and Instrument Master Data Sheet (IMDS) APRM -CHS-3 revision 3 (safety related APRM/OPRM chassis). Factual Basis: There is no instrument setpoint change request (ISCR) associated with these setpoint changes. Procedure 1.4.3, â€œInstrument Setpointsâ€ (ISCR) is the governing process for changing instrument setpoints that are not associated with a design change. In addition, PPM 1.4.3 revision 25 section 3.4.2 states, â€œSince an ISCR is part of the design change process and LBID screening is required to be completed.â€ Hence, no LBID screening was performed for these setpoint changes. The setpoints to be changed do not perform a safety related design function. The setpoint changes are being performed in conjunction with EC 8076 revision 7 which authorizes the replacement of a APRM computer module. 5059SCREEN-16-0119 associated with the module replacement EC does not authorize the setpoint changes. Insights: Ensure that plant changes including setpoint changes being made per an engineering change are all covered within the scope of that engineering change to ensure compliance with the applicable procedures and regulatory requirements. <I> **** Actions Taken **** Discussed with the Design Engineering Manager | 02-00-APRM-CHS-3
384030 | CR | 20180829 |  | 4 | Work Delay - Inadequate Coordination with Data Glance |  |  |  | N | NO | <D> **** Detailed Description **** Fire Protection VESDA Work Order Task 02116227-20 had been taken to Finished in Data Glance. Later it was decided to return the task to Ready to replace VESDA panel ISD/3. The task status was returned to Ready in Portal J but was not restatused in Data Glance. When planning was complete and the craft was ready to take the task to Working, it was not present in Data Glance. IS had to be involved to re-align Data Glance with Portal J. This delayed work approximately a half shift. No SSC operability issues were identified. <I> **** Actions Taken **** 1) Worked with the PSRO and IS to correct Data Glance 2) Notified CPM management of delay
384031 | CR | 20180829 |  | 3 | AED CAL 8.42.6032 does not list oustanding CMRs in Portal J | N | N |  | N | NO | <D> **** Detailed Description **** In Portal J, RCC large bore pipe stress calculation AED CAL 8.42.6032 revision 1 lists CLOSED status BDCs 90-0363-0A and 91-0137-0A as outstanding changes instead of the actual existing CMR-91-0051 and CMR-97-0194. At this time, the existing CMRs do not exist in Portal J. The CMRs need to be added in Portal J as outstanding against the calculations and advanced to MODIFIED status. The BDCs need to be removed in Portal J as outstanding against the calculations. This is a legacy artifact of how CMRs against calculations associated with BDCs used to be tracked - this is a legacy administrative issue only. Suggest resolution assignment to Mechanical Design Engineering. pdfs of CMR-91-0051 and CMR-97-0194 are attached to the EDMS of this AR CR 384031.
384032 | CR | 20180829 |  | 3 | AED CAL 8.42.0135 does not list oustanding CMRs in Portal J | N | N |  | N | NO | <D> **** Detailed Description **** In Portal J, RCC large bore pipe stress calculation AED CAL 8.42.0135 revision 2 lists CLOSED status BDC 91-0137-0A as an outstanding change instead of the actual existing CMR (CMR-97-0193). At this time, the existing CMR does not exist in Portal J. The CMR needs to be added in Portal J as outstanding against the calculation and advanced to MODIFIED status. The BDC needs to be removed in Portal J as outstanding against the calculation. As discussed in AR CR 384031, this is a legacy administrative issue only. Suggest resolution assignment to Mechanical Design Engineering. A pdf of CMR-97-0193 is attached to the EDMS of this AR CR 384032.
384033 | CR | 20180829 |  | 3 | Vehicles Observed Parked Off Road Violates ISPM-10 |  |  |  | N | NO | <D> **** Detailed Description **** Inspection today of the work being conducted for the Service Water Spray Pond cleanout found three trucks parked in an area defined as Off Road per ISPM-10. Discussions with the Project Manager revealed that ISPM-10 requirements for clearing the spray pond sludge holding area with a bulldozer last week also did not comply with ISPM-10 in that Hanford Fire Department was not notified of the work, and the attending vehicles were not properly equipped with fire extinguishers and wildland shovels. The access road to this area also travels to Building 72. This road is kept clear and free of vegetation. However, where the project site cleared vegetation for the spray pond sludge, this was off-road. Any equipment in this area during the current EXTREME fire danger could spark a wildfire and endanger the Columbia site and the Hanford Site. The utmost precautions are required at this time. <I> **** Actions Taken **** Fire Marshal inspection of the project area finds that the majority of the danger is past. A small area for vehicle parking and turn around needs to be cleared of vegetation. This was discussed with the Project Manager and should be completed by close of business today. Notice of the current fire danger and clarifications on the ISPM-10 requirements were sent to the Project Manager and the Williams Plant Services Supervisor.
384034 | CR | 20180829 |  | 4 | License Operator missed LORQ simulator training |  |  |  | N | NO | <D> **** Detailed Description **** A License Operator Org code 52220 assigned to Staff crew missed LORQ simulator training (LR001624 â€“ Task Training). The student mistakenly believed classes were completed for the day. Per TDI-08, the student has been assigned an AR assignment (AR377701-04) to complete the missed training. <N> This CR was initiated IAW GBP-TQS-01 rev. 002, sections 3.3 and 3.4.
384035 | CR | 20180829 |  | 3 | AED CAL 8.42.0218 does not list 1 oustanding CMR in Portal J | N | N |  | N | NO | <D> **** Detailed Description **** In Portal J, RCC large bore pipe stress calculation AED CAL 8.42.0218 revision 3 lists CLOSED status BDC 90-0363-0A as an outstanding change instead of the actual existing CMR (CMR-91-0050). At this time, the existing CMR does not exist in Portal J. The CMR needs to be added in Portal J as outstanding against the calculation and advanced to MODIFIED status. The BDC needs to be removed in Portal Jas outstanding against the calculation. As discussed in AR CR 384031, this is a legacy administrative issue only. Suggest resolution assignment to Mechanical Design Engineering. A pdf of CMR-91-0050 is attached to the EDMS of this AR CR 384035.
384036 | CR | 20180829 | CAQ | D | OG Analyzer N2 bottle low | N | N |  | N | NO | <D> **** Detailed Description **** The right side OG Analyzer N2 bottle is low @ 275# on the TB 441 west side. <N> **** Equipment Description **** The right OG Analyzer N2 bottle on TB 441 west near door
384037 | CR | 20180829 |  | 3 | ENS Text Notification System Not Transmitting Messages | N | N |  | N | NO | <D> **** Detailed Description **** Received reports of messages attempted to be sent that were not transmitted to users. <I> **** Actions Taken **** CR generated. Notified supervision. Will contact service provide ASAP to to create trouble ticket for resolution.
384039 | CR | 20180830 | CAQ | C | Fire Protection Modification EC 13537 | N | Y |  | N | NO | <D> **** Detailed Description **** During the implementation and Post Modification Testing of PDC 13537 (Fire Protection System Upgrade), an issue was discovered with respect to design feature associated the newly installed Siemens Control Module CP-35 and the associated power supply PS-35. Unlike the existing CP-31, once the reset switch has been activated, a momentarily loss of power will occur at the output of PS-35 power supply. The output of this power supply is currently used to power the Main Control Room (MCR) kitchen fire detection, associated door holder, and UV fire detector module for Turbine Building Elevation 501â€™ West. Turbine Building Elevation 501â€™ West detector module was found to be without power on August 26 2018. Work Request 291443115 was initiated to investigate the cause of loss of power to the detector. FPSI I#18-0264 is currently open for the out of service detectors in this area. <I> **** Actions Taken **** 1. Notified Design Engineering Supervisor 2. Will Initiate AWA to revise EC 13537 and power the MCR Kitchen and Turbine Building UV fire detector module from an alternate source. Preliminary review concluded the external 24 VDC power supply currently used in FP-CP-FCP1 can be utilized to power these two loads.
384040 | CR | 20180830 |  | 3 | Return To Supervisor option not working in Data Glance |  |  |  | N | NO | <D> **** Detailed Description **** When a surveillance is at H/OPS and errors are found in the review it should be able to be returned the the supervisor using the Return To Supervisor option. The past several times I have tried to use this function I have received the following message: "Cannot Perform the Status Update. Status Flow not defined in the table from 4000 to 9100". This is a recurring issue and the EWP help desk has been informed. <N> The following two work orders are at H/OPS in DataGlance for surveillance reviews; 02123759-01 and 02123760-01. Both work orders are for 15.2.39, one for attachment 9.1 and the other for attachment 9.4. Both need to be returned to the craft to get the data pages reviewed by their supervisor prior to a SRO review. Another work order was found at H/OPS that needs to be returned to the craft. It is WO #02100975-01 and it is missing several pages of data required from Engineering. . Same issue was reported under CRs 00384061 & 00383973. . Work will be performed under CR 00384061, Closing CR 00384040. Cross Reference panel has been updated.
384045 | CR | 20180830 |  | 4 | Portal J MEL indicates RCC-M-P/1A draws 221A FLC |  |  |  | N | YES | <D> **** Detailed Description **** EC MALT 9605 authorized replacement of the original motor at RCC-M-P/1A with a replacement motor having a different full load current (FLC) - FLC for RCC-M-P/1A increased from 221A to 228A. The controlled Portal J MEL 'Name' field for RCC-M-P/1A (200HP/221A MOTOR FOR RCC-P-1A) was not updated as part of EC MALT 9605 and is currently errant as a result. For resolution, it is suggested that the Portal J 'Name' field for RCC-M-P/1A be changed from '200HP/221A MOTOR FOR RCC-P-1A' to '200HP MOTOR FOR RCC-P-1A'. The FLC information for motors like RCC-M-P/1A is tracked elsewhere and need not be tracked via the 'Name' field in Portal J . As such, similar Portal J MEL 'Name' field updates should be made for RCC-M-P/1B and RRC-M-P/1C. The Portal J 'Name' field for RCC-M-P/1B should be changed from '200HP/221A MOTOR FOR RCC-P-1B' to '200HP MOTOR FOR RCC-P-1B'. The Portal J 'Name' field for RCC-M-P/1C should be changed from '200HP/221A MOTOR FOR RCC-P-1C' to '200HP MOTOR FOR RCC-P-1C'. Today, these recommended/necessary Portal J MEL 'Name' field updates for RCC-M-P/1A, RCC-M-P/1B, and RCC-M-P/1C should be relatively simple administrative updates. <I> This discrepancy issue has been addressed administratively by Design Engineering (see e-mail in the AR CR 384045 EDMS). The Portal J / MEL 'Name' fields for RCC-M-P/1A, RCC-M-P/1B, and RCC-M-P/1C have been updated as necessary. Recommend TREND resolution (no further action required). | 02-00-RCC-M-P/1A,02-00-RCC-M-P/1B,02-00-RCC-M-P/1C
384046 | CR | 20180830 |  | 4 | M&TE Rejected | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0062654 Mitutoyo Mic. Standard- model 167-171 31" found OOT & Rejected- No adjustment possible. Not used during Calibration cycle. DEF #6731A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
384048 | CR | 20180830 |  | 4 | Frequent TDAS point X480-12, RPS A2 TRIP alarms. | N | N |  | N | YES | <D> **** Detailed Description **** Alarm typer denoting frequent TDAS point X480-12, RPS A2 TRIP alarms. Alarms Trip and Normal very short duration. <I> **** Actions Taken **** Notified the CRS. Please investigate and repair. <N> **** Equipment Description **** TDAS point X480-12 RPS A2
384053 | CR | 20180830 |  | 4 | TOA-P-1B pump seal leak | N | N |  | N | YES | <D> **** Detailed Description **** The air wash pump TOA-P-1B has a pump seal leak at the rate of about 1 drop per minute. Recommend repairing during winter months. | 02-00-TOA-P-2B1
384054 | CR | 20180830 | CAQ | C | Incorrect list of adjusted isotopes in the 3DM User Manual |  |  |  | N | YES | <D> **** Detailed Description **** No impact on 3D MONICORE system operation or software. This is a documentation issue only. 3D Monicore Problem Number 2018-036 (attached to EDMS) identified error in the Users' Manual (CVI 981-01,31,9). The corrected information is included in the attached problem report. <I> **** Actions Taken **** Software Error Notice form 26146 attached to EDMS. Notified Users (e-mail attached). Recommend assignment to AR-RXFUEL to track revision of CVI 981-01,31,9. | 02-00-PPC-SOFT-3DM
384057 | CR | 20180830 | CAQ | D | IDS 7, 8, 9, and 10 need maintenance | N | N |  | N | YES | <D> **** Detailed Description **** IDS 7,8,9, and 10 are not functioning as designed. Contact security at ext. 2185 for further details. <N> **** Equipment Description **** IDS 7, 8, 9, and 10 are located on trhe north side of the PA
384060 | CR | 20180830 | CAQ | D | M&TE OOT | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0063677 Proto Torque Wrench- model 6062C 200in/lb found OOT & adjusted within specs. Per PPM 1.5.4 section 4.4.3 (a-c) Torque Wrench had acceptable post use verifications @ +/- .06%. DEF #6732A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
384061 | CR | 20180830 |  | 3 | Return to Supervisor is not working in DG OPS Closeout |  |  |  | N | NO | <D> **** Detailed Description **** THe Return to Supervisor is not working in the DataGlance OPS Closeout Panel. When trying to return package 02123760-01 back to the Supervisor, it was discovered that that option does not work, but it shows as a valid option on the Actiions drop down. <I> **** Actions Taken **** Have contacted vendor concerning the software bug and waiting on a solution. <N> Recomend Non-CAQ 3 . Same issue was reported under CRs 00384061 & 00384040. . Work will be performed under this CR, 00384061, Closing CRs 00384061 & 00384040. Cross Reference panel has been updated. | FW-00-SOFT-COTS-DG/DOCPLUS
384063 | CR | 20180830 |  | 4 | IA/STA weekly written exam failure |  |  |  | N | NO | <D> **** Detailed Description **** An IA/STA did not pass the weekly wriiten exam. <I> **** Actions Taken **** IA/STA qualifications removed. Remediation package started. Notified Ops and Training management <N> Remediation for exam failure IAW TDI-02.
384066 | CR | 20180830 |  | 3 | unauthorized storage in flammable storage locker |  |  |  | N | NO | <D> **** Detailed Description **** 1 aerosol can of aerokroil penetrating oil found in DG3 flammible storage locker during monthly chem storage inspection. The DG3 locker is authorized for storage of dessicant only. Due to potential incompatibility, no other chemical is authorized. Note - issue and use authority belongs to Mechanical Maintenance. <I> **** Actions Taken **** removed the oil can and returned it to the tool crib for proper storage. <N> Provided coaching on issue identified in this CR | 02-00-D-BLDG-MISC
384067 | CR | 20180830 |  | 3 | ISPM 6 Violation Portable Heater to Power Tap |  |  |  | Y | NO | <D> **** Detailed Description **** During a quarterly safety inspection, a portable heater was found plugged into, (not turned on) a power tap contrary to ISPM 6, Electrical Tools, Appliances and Extension Cord Use, section 3.7.3.e. These requirements state in part that portable heaters Shall not be plugged into power taps. <I> **** Actions Taken **** All workers in the common office area were coached on the requirements. Heater was unplugged and stored properly for future use. Notified department manager.
384072 | CR | 20180830 |  | 3 | Computer point B009 reads in lbm/hr vice gpm |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of ISP-RWCU-B301 WOT 02128594-04 computer point B009 reads in pound mass per hour, readings are needed in gpm. Determine when units were changed on computer point and if needed to stay in lbm/hr then add note in procedure that enry needs to the "B009gpm", if not change back to gpm. <I> **** Actions Taken **** Discussed with computer tech to figure out problem wrote cr
384073 | CR | 20180830 |  | 4 | Moisture Carryover Increase |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The latest moisture carryover (MCO) result increased three -fold over the last sample. This trend up was previously identified in AR382920 and is now near the BWRVIP-190 alert level of 0.1% MCO. The latest result occurred during the RWCU outage. RWCU leakage into the hotwell would bias the MCO result high, especially during a demineralizer outage. No specific action is required if the 0.1% MCO limit is exceeded. This limit is established to alert the station to possible steam quality issues and potential elevated dose rates in steam affected areas. <I> **** Actions Taken **** Informed supervision, the Shift Manager, Radiation Protection, and Reactor Fuels. Increased the MCO calculation frequency to identify a trend.
384076 | CR | 20180830 |  | 3 | SOP-COND-OPS procedure change required |  |  |  | N | NO | <D> **** Detailed Description **** sop-cond-ops sections that disable the condensate booster pump low lube oil pressure trips when transferring lube oil coolers need to be revised to use electrical tape to cover termination points 1, 2, and 8 prior to determing the white wire at termination point 7 and to maintain positive control over the white wire at termination point 7 during determing and reterming. <I> **** Actions Taken **** Discussed revision when Operations procedure group supervisor.
384077 | CR | 20180830 | CAQ | D | ISP-IRM-X302 | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of ISP-IRM-X302 (WO 0210061501) as found ZERO 2 voltage found OOT at 0.007 VDC at step 7.3.9. Adjusted ZERO 2 voltage to 0.000 VDC per step 7.3.10 within tolerance of -0.005 to 0.005 VDC. <I> **** Actions Taken **** Informed OPS, supervision, and wrote CR <N> **** Equipment Description **** IRM-EMSQ-601B
384078 | CR | 20180830 |  | 4 | SOP-COND-OPS walk down | N | N |  | N | NO | <D> **** Detailed Description **** SOP-COND-OPS section 5.3.4 will be used to disable the COND-P-2C low lube oil trip when transferring from TSW-HX -6F to TSW-HX-6E per WO 02119556-19 during the 9/22 down power. This trip logic was installed in R23 per EC 6766 and is disabled by determing a single wire at COND-PS-4C/1, COND-PS-4C/2, and COND-PS-4C/3. A walk down was performed per WR 29144376 with a FIN instrument technician to determine if there is any potential for an error to occur when performing this procedure since it has not been performed before. The following issues were noted. The pressure switch termination points are covered by a red plastic dust cover which has a label on the cover showing the layout of the termination points. Termination points are not in the same orientation as shown on AED ELC E538 -54. The electrical drawing shows termination points 5, 6, 7, and 8 are oriented sequentially with point 5 on the bottom and point 8 on top. The label shows the orientation as 6, 5, 7, and 8 from bottom to top. This does not have any impact as points 5 and 6 are not used. Point 5 on COND-PS-4C/1 does not have a screw. The other two pressure switches have screws installed at their point 5. This has no impact since termination point 5 is not used. Points 1, 2, 7, and 8 are in close proximity with points 2 and 8 being the closest to point 7 where the determination will be performed. If the wire at point 7 comes in contact with point 8 a half-trip is enabled for the low lube oil pressure trip of COND-P-2C which has a 2 out 3 logic of the lube oil pressures switches. Points 1 and 2 are used in the start permissive for COND -P-2C to ensure lube oil pressure is adequate for pump start. If the wire being determend from point 7 comes in contact with points 1 or 2, control power fuse F31-1 or F31-2 could clear. If this occurs the low suction pressure trip and low lube oil pressure trip for COND-P-2C would not be available. This would not have any impact on COND -P-2C since it is running. The close and trip fuses for COND-P-2C are in parallel with fuses F31-1 and F31-2 and would not be impacted. <I> **** Actions Taken **** This walk down was documented on WR 29144376 with recommended mitigating actions to prevent a half trip of the logic and to prevent a ground short. The actions are to use electrical tape to cover termination points 1, 2, and 8 and to maintain positive control of the wire at termination point 7 during the determ. Discussed the missing screw and dust cover label with the Responsible Engineer for EC 6766. The RE agreed that the missing screw has no impact and that the dust cover cap label is incorrect since the pressure switches and logic for the trip was tested during EC 6766. The only potential impact would be an error likely situation would exist if wires were terminated to points 5 and 6 for some other purpose in the future. Discussed the close proximity of termination points 1, 2, 7, and 8 with Operations Work Control management. It was agreed that the use of the mitigation strategies noted in this CR and on WR 29144376 would prevent any problems from occurring during SOP-COND-OPS sect 5.3.4. This mitigating actions were written on the TM102 panel for the IC support task 02119556 task 19 and will be included in the High Risk plan for task 19. Additionally, the High Risk plan will have an IC supervisor in the field when the wires at the pressures switches are determed and retermed. The High Risk plan will also include actions to verify that the low lube oil pressure logic does not indicate being enabled at COND-CP-1 prior to determing and reterming each pressure switch. In summary, Wr 29144395, 29144396, and 29144397 were written to re-label the dust covers. WR 29144398 was written to replace the missing screw. CR 384076 was written to revise SOP-COND-OPS to include the mitigation actions in the procedure and that the procedure revision was required before the 9/22 down power.
384079 | CR | 20180830 |  | 3 | TSP-APRM-C302 enhancements identified |  |  |  | N | NO | <D> **** Detailed Description **** During performance of SOP-APRM/LPRM-OPS to return an LPRM to service, it refers the user to TSP-APRM-C302 to complete the adjustments necessary to return an LPRM to service. TSP-APRM-C302 has a section for making LPRM adjustments on ALL the detectors, however, it could be modified to allow adjustments of just a single or few detectors to accommodate this type of situation. <I> **** Actions Taken **** Notifiied Supervisor, and initiated this CR to identify this recommended ehnancement to TSP-APRM-C302. Recommend a 3 to AR-RxEng to revise TSP-APRM-C302.
384080 | CR | 20180830 |  | 4 | 'Lost' 200HP motor removed from RCC-M-P/1A found on W507' |  |  |  | N | YES | <D> **** Detailed Description **** The 'lost' 200HP motor removed from RCC-M-P/1A per WO 01155945 in 2012 has been found - it is in the W507' basket ball court area. See the photos attached to the EDMS of this AR CR 384080. Arrangements should be made to send this motor off site for rewind/rebuild for future installation at RCC-M-P/1B or RCC-M-P/1C. This would avoid the need for a design change to replace these motors with CID 20018 (AR EVAL 283724 or AR EVAL 301348). <N> W507' basketball court = W507' room C405 (ref. AED A508). | 02-00-RCC-M-P/1A,02-00-RCC-M-P/1B,02-00-RCC-M-P/1C
384082 | CR | 20180830 | CAQ | D | E-GEN-DG4 W Ground Fault alarm in | N | Y |  | N | YES | <C> CR reopened to cross reference additional WR 29146245 then taken back to complete <D> **** Detailed Description **** Over the past several years there have been many occurrences of a W GROUND FAULT alarm occurring on DG4 when running. It came in again today while running E-GEN-DG4 on the DG5 load bank. The control room was informed and task continued. | 02-00-E-GEN-DG4
384083 | CR | 20180830 |  | 4 | CF-P-41B still not pumping. | N | N |  | N | YES | <D> **** Detailed Description **** Following work on CF-P-41B per WO 02110623, the fill and vent per SOP-CW-CHEM-MAINT went perfect. After the fill and vent, CF-P-41B was placed in service per SOP-CW-CHEM with less than satisfactory results. Initially, there were flow pulses observed through the discharge sightglass, but the wheel in the brand new sightglass was not spinning. This indicates reduced flow. After running for 15 to 20 minutes the flow pulses changed to periodic surges, about every two to three minutes without any pulses. The pump was secured per the SOP. Further investigation is needed to resolve this issue. <I> **** Actions Taken **** Informed supervisor and shift manager. <N> **** Equipment Description **** CWPH | 02-00-CF-P-41B
384084 | CR | 20180830 | CAQ | D | Camera 46 needs maintenance |  |  |  | Y | YES | <D> **** Detailed Description **** Camera 46 at the SW tower at the ISFSI needs maintenance. Contact security prior to work. <I> **** Actions Taken **** notified supervision, CR/WR generated <N> **** Equipment Description **** SW tower at the ISFSI | 02-00-SEC-CCTV-ISFSI/46
384085 | CR | 20180830 |  | 3 | SOP-CW-CHEM-MAINT not IAW SWP-CM-02 |  |  |  | N | NO | <D> **** Detailed Description **** Section 5.13 of SOP-CW-CHEM-MAINT provides instruction for implementing a Procedurally Controlled Temporary Change (PCTC) for Temporary Sulfuric Acid Truck Operation, and references SWP-CM-02; however, several of the requirements from Section 5.6.6 of SWP-CM-02 are missing. For example, SOP-CW-CHEM-MAINT does not contain requirements to perform Simultaneous Verification or functional test to ensure operability when the TCC is installed and design configuration is restored or requirements to notify affected work groups such as Operations, Maintenance, Engineering, Chemistry, and/or Radiation Protection as needed when the TCC is installed and removed. Recommend revision to SOP-CW-CHEM-MAINT to bring PCTC into alignment with SWP-CM-02 requirements.
384087 | CR | 20180830 |  | 3 | Revise 4.603.A7 and 4.603.A8 |  |  |  | N | NO | <D> **** Detailed Description **** The procedure steps for both of these procedures for drop 1-3 are identical. Step 3 in this section erroneously lists Technical Specifications 3.3.6.1, 3.3.6.2 and 3.3.7.1. There is no correlation between SDIV level detection and these specs. I recommend removing them from these procedures. Also, the notes after the steps 2.a erroneously lists the trip setpoints as 529â€™2â€. Per LCS table 1.3.1.1-2 function 7 a and b the trip setpoints are 529â€™7â€. I recommend updating the ARP to align with the LCS.
384088 | CR | 20180830 |  | 3 | PeopleSoft unavailable 8/30 |  |  |  | N | NO | <D> **** Detailed Description **** During the planned upgrade of PeopleSoft, an error occured during go live testing. Troubleshooting took place to try and resolve but was unsuccessful. Decision was made to revert back to pre-upgrade state. The application will be restored on 8/31/18. <I> **** Actions Taken **** IS and HR Management notified. Recommend NCAQ 3
384091 | CR | 20180830 |  | 4 | PTZ 35 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** PTZ 35 is not functioning as designed and requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security supervision notified. Initiated CR/WR. | 02-00-SEC-CCTV-35
384092 | CR | 20180830 |  | 4 | OG-V-53B green closed light out on H13-P672. | N | N |  | N | YES | <D> **** Detailed Description **** OG-V-53B is throttled per SOP-OG-START to 80% and should indicate dual position. Green closed light is extinguished on H13-P672 and it should be lit. Checked twice with known good bulbs. Suspect bad socket. | 02-00-OG-V-53B
384093 | CR | 20180831 | CAQ | D | Burned out essential fluorescent lighting in MCR | N | Y |  | N | YES | <C> CR reopened to cross reference additional WR 29146327 then taken back to complete <D> **** Detailed Description **** During performance of 15.2.39, six essential fluorescent lighting fixtured were found to have a bulb burned out. <I> **** Actions Taken **** Per 15.2.39 step 7.1.10.b.1, a WR is to be initiated to have tubes replaced as necessary. <N> **** Equipment Description **** 8FDA/2G, 8FDA/2C, 7FDA/2D, 7FDA/2C, 8FDA/2B, 7FDA/1E. All fixtures located in the Main Control Room | 02-00-W-BLDG-MISC
384094 | CR | 20180831 |  | 4 | TN-05 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** TN-05 is not functioning as designed and requires maintenance. Contact 2185 for more details <I> **** Actions Taken **** Security supervision notified. TN-05 taken out of serice. Initiate CR/WR. Notify SM. | 02-00-SEC-TN-5
384095 | CR | 20180831 | CAQ | C | FP-CP-FCP1 new control modules (ZU-35DS) failed testing | N | Y |  | N | NO | <D> **** Detailed Description **** During replacement of components in FP-CP-FCP1 per WO# 02088112-07, three new ZU-35DS control modules (CID# 9597) were found to be defective. The installed modules did not pass initial testing; Trouble alarm (yellow LED) was locked in at the modules when first energized. Investigation of the first two modules found broken solder connections for a transistor on the circuit board. Failure cause for the third module is unknown. <I> **** Actions Taken **** The work package was revised to replace the defective control modules. The new modules were carefully inspected and installed - testing was re-performed with no further issues. | 02-00-FP-CP-FCP1
384096 | CR | 20180831 |  | 4 | Wooden Ramp Requires Maintenance |  |  |  | N | YES | <D> **** Detailed Description **** The wooden ramp located in the south side of the PA that is used for vehicle traffic over hoses requires maintenance. The wooden supports are not functioning as designed and this poses a risk to any vehicle traffic in the area. Requesting a review/analysis of the affected area and functionality of ramp. <I> **** Actions Taken **** Security has been briefed to use a different route. Operations was notified and information will be included in turnover. <N> **** Equipment Description **** Wooden ramp in south PA area.
384110 | CR | 20180831 |  | 4 | Sewer manhole near 600 area |  |  |  | Y | YES | <D> **** Detailed Description **** Sewer manhole needs maintenance and appears a portion of the manhole support is degraded resulting in a hole. <I> **** Actions Taken **** supervisor notified. CR/WR generated <N> **** Equipment Description **** Located in the 600 area near the stairs over the barrier wall
384111 | CR | 20180831 |  | 3 | EDR-DM-9 extremely short run time. | N | N |  | N | YES | <D> **** Detailed Description **** EDR-DM-9 was double B/W and precoated on night shift at 0240. Water was flown through it on day shift, consisting of normal EDR-TK-2 water and decant water from CPR-TK-92A/B (CFD). The D/P steadily rose through out this processing resulting reaching high D/P 8 hours into its first shift of use. Historicaly this would be considered extremely fast as a filter should last days not hours. All water processed passed chemistry analysis. <I> **** Actions Taken **** B/W and Precoated EDR-DM-9 per precoat criteria sheet. | 02-00-EDR-DM-9
384112 | CR | 20180831 |  | 4 | XD 3 placed out of service |  |  |  | Y | YES | <D> **** Detailed Description **** XD 3 placed out of service. contact security prior to work <I> **** Actions Taken **** Placed out of service, notified supervision, CR/WR generated <N> **** Equipment Description **** Search area | 02-00-SEC-XD-3
384113 | CR | 20180831 |  | 4 | Door C-238 handle requires maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Door C-238 handle is loose and was hard to get door open, handle may require maintenance. <I> **** Actions Taken **** CR/WR initiated, Notified supervision and Notified Shift manager . | 02-00-W-DOOR-C238
384114 | CR | 20180901 | CAQ | D | D-Door-D208 not functioning as designed | N | N |  | N | YES | <D> **** Detailed Description **** D-Door-D208 is not functioning as designed request maintenance to investigate. Call 2185 for more information. <I> **** Actions Taken **** Door Key locked; CR/WR Generated This is a security related issue - all other functions of the door are working normally. | 02-00-D-DOOR-D208
384147 | CR | 20180901 |  | 4 | E-TR-M3 - Oil Pump contactor trip and reset | N | N |  | N | YES | <D> **** Detailed Description **** During response to E-TR-M3 Trouble annunciator, discovered Cooler Group 2 Failure local alarm in with oil pump not running. Contactor 52P--2 was tripped and was reset per ABN-TRANSFORMER. This CR is for trending. <I> **** Actions Taken **** Reset contactor per ABN-TRANSFORMER | 02-00-E-TR-M3
384148 | CR | 20180901 |  | 3 | Recommended change to 3.2.1 |  |  |  | N | NO | <D> **** Detailed Description **** In 2005 the note for section 5.1 was changed to give additional flexibility in performing steps out of order. Revision 77 severely restricted the scope of this note in apparent compliance with INPO 11-003 section 9.2, but the INPO recommendation applied to performing steps out of order only for a "procedure ... (that) does not allow it". It is appropriate and necessary to perform shutdown steps out of order depending on plant conditions, resources, and the desired end-state. An attempt was made to undo this restriction in the very next revision but the wording selected was the pre-2005 wording. Change this not to match that of Revision 51 (through Revision 76). <I> **** Actions Taken **** None.
384149 | CR | 20180901 |  | 4 | ROA-HV-1 appears to have a hole in it from corrosion | N | N |  | N | YES | <D> **** Detailed Description **** There appears to be a through-wall hole roughly 1-1/2 inch across near an area that was previously patched, located on the south side of the unit about eight feet from the floor. See photo #0558 and #0556 on EDMS screen. There are several locations on the outside of the unit where water is leaking out and causing corrosion. See photos on EDMS screen. <I> **** Actions Taken **** informed Shift Mgr and Shift Supervisor This has no impact to secondary containment. | 02-00-ROA-HV-1
384150 | CR | 20180901 |  | 4 | Chemical Feed Hose at CWPH | N | N |  | N | YES | <D> **** Detailed Description **** Chemical Feed Hose at CWPH used for gravity feed chemical addition has black sleeving that is brittle and decomposing. The concern is that pieces of the sleeving will fall off the hose and end up in the Circ Water Basin. Unable to remove hose from from CWPH due to lack of plan to flush it out and cap the ends. <I> **** Actions Taken **** CR/WR written. Supervision notified. <N> **** Equipment Description **** Chemical Feed Hose at CWPH | 02-00-P-BLDG-MISC
384151 | CR | 20180901 |  | 4 | Wautoma-Knight 500KV line relayed to lockout at 1312 | N | N |  | N | NO | <D> **** Detailed Description **** 1312 Received Oscillograph Started (H13-P800.C4.4-3) alarm. The alarm was due to the J7 sensor (500KV Neutral Ground). The J7 sensor has been reset. E-TR-S and E-TR-B voltages as indicated on H13-P800 are 239/240/240 kV and 119/119/118 kV respectively. BPA Dittmer reports the 500 KV Wautoma -Knight line relayed to lockout and was reclosed by Operator. No RAS initiated. All plant controllers and equipment exhibited normal operation <I> **** Actions Taken **** informed CRS/SM
384152 | CR | 20180901 |  | 3 | Several safety harnesses at RW507 are out of date |  |  |  | N | NO | <D> **** Detailed Description **** There are several safety harnesses at the scaffold storage area on RW507 that are out of date, per the current color of the tag attached to the harness. The inventory there needs gone through and the out of date equipment should be returned to the Tool Crib for proper care. <I> **** Actions Taken **** informed Shift Supervisor
384153 | CR | 20180901 |  | 4 | CW-P-1C Abnormal Vibration Observed | N | N |  | N | YES | <D> **** Detailed Description **** CW-P-1C Abnormal Vibration Observed. While taking Ops 4 rounds at CW, I observed the Lube water piping for CW-P-1C shaking and rattling. I compared the vibrations of the piping and CW-P-1C shaft to those of the other two CW Pumps and noticed that is was significantly worse on CW-P-1C. I immediately notified the Control Room and the SSS was sent out to verify. <I> **** Actions Taken **** CR/WR initiated. Supervision Notified. Notified vibrations engineer - vibrations were verified to be normal and steady (consistent with last several weeks). Additionally, mechanics and the maintenance supervisor looked at the about of shaft movement and determined this was not abnormal. We will continue to monitor the pump using the normal logtaking frequency. | 02-00-CW-M-P/1C,02-00-CW-P-1C,02-00-TSW-FI-P/1C,02-00-TSW-FIS-33C
384154 | CR | 20180902 |  | 3 | Unknown change in FPC-DM-1A D/P | N | N |  | N | YES | <D> **** Detailed Description **** While preparing to remove FPC-DM-1A from suppression pool cleanup it was noted that the D/P had dropped for no apparent reason. When FPC-DM-1A reached a D/P of 22.5 psid , FPC-DM-1B was precoated and placed in hold (around 2330) so that it could be placed in service on the fuel pool after FPC-DM-1A was exhausted. At 0010 RHR-P-1B was started for a 30 min run and then secured. At 0300 FPC -DM-1A should have been close to reaching its high D/P alarm setpoint (25 psid). Prior to removing it from service the D/P was checked and it had dropped to 20.75 psid. Looking back at the history it was noted that at 2350 the D/P went from 23.77 down to 17.85 psid for no apparent reason. Request engineering evaluate. <I> **** Actions Taken **** infrom the control room and initate CR <N> Changed CR Title and Description fields to correct component (from FPD to FPC) | 02-00-FPC-DM-1A
384161 | CR | 20180902 |  | 4 | Operations shift staffing below PPM 1.3.1 requirements |  |  |  | N | NO | <D> **** Detailed Description **** Due to illness the on-shift field supervisor/notifier was combined with the STA/IA position. This left the crew below the minimum staffing requirements of PPM 1.3.1. The crew compliment remained above the Unit Staff requirements of TS 5.2.2. <I> **** Actions Taken **** Held the off going STA/IA for an extra 2 hours to ensure minimum manning was maintained. Made a control room log entry Continued callouts until a notifier / STA / IA qualified person was available (arrived by 11:30 am).
384162 | CR | 20180902 |  | 3 | (PCR) Procedure enhancement on RCIC quick cards. |  |  |  | N | NO | <D> **** Detailed Description **** Procedure enhancement needed for SOP-RCIC-TRANSFER-QC: Remove note for RCIC-V-19, this note is not needed for the quick card and there is no mention of this in PPM 5.6.2. Move step 2.1.7 prior to step 2.1.6, this will minimize the time on minimum flow valve. Procedure enhancement needed for SOP-RCIC-INJECTION-QC: Use EPN ( RCIC-RMS-S18 ) for step 2.2.4.a
384163 | CR | 20180902 |  | 4 | PWC-P-8 signal cable connection is degraded | N | N |  | N | YES | <D> **** Detailed Description **** PWC-P-8 was found running with the free residual chlorine concentration (FRC) in PWC-TK-100 at 1.52 ppm. PWC-P-8 should cycle to conrtol FRC to 1.3 ppm and should not have been running. The signal cable that controls the cycling of PWC-P-8 was moved at the pump and PWC-P-8 stopped pumping as it should. Further movement of the cable connection did not cause the pump to restart. The cable connection does not feel snug and should be replaced. This issue was written up 4/5/18 CR 378261 WR 29141917. PWC-P-8 is currently in service and potable water chlorine concentration is in acceptable range. SWP-CHE-02 states action level at LT 0.2 ppm or GT 4.0 ppm. The admin guideline is GE1.0 ppm and the GT 4.0 ppm is for an annual average limit. <I> **** Actions Taken **** Notified OPS and supervision. Wrote CR/WR | 02-00-PWC-P-8
384164 | CR | 20180902 | CAQ | C | ISP-IRM-X304 power supply failure during survelance. | Y | Y |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02100616-01 on step7.9.9 page 28 it was discovered that the AS-Found High voltage was grossly out of tolerance. It Read -5.485 which is an unrealistic number, indicating a bad high voltage power supply. Before this equipment can be returned to service the high voltage power supply will have to be replaced. Cory H, Steve M, Richard T. 9/2/18 <I> **** Actions Taken **** CRS and I&C supervision were notified of the issues while performing x304. Equipment is bypassed, and left in a safe condition. The power supply replacement will have to be planned and scheduled for replacement, as well as the PMT. <N> **** Equipment Description **** 501 control room | 02-00-IRM-EMSQ-601D
384165 | CR | 20180902 |  | 3 | Dataglance WO Issues with Procedure Revisions |  |  |  | N | NO | <D> **** Detailed Description **** Recently Work Orders in Dataglance have been auto generating with old procedure revisions. When the WO is ready to be worked the WO package will not validate and the supervisors have to update the procedures. The procedures that have to be revised are not recently changed but months or multiple revisions behind. It was our understanding that Dataglance would be communicating with Asset Suite to have the current procedures in the WO package until the work was started. <N> **** Equipment Description **** Dataglance . This issue was previously reported and is being worked under CR00383365. This CR can be closed.
384166 | CR | 20180902 |  | 4 | ASD Building Temp 82F @ 2115 | N | N |  | N | YES | <D> **** Detailed Description **** ASD building temperature was 82F at 2115. Spec is less than 80. ASD HVAC controllers showed no errors. Please investigate and repair if necessary. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** ASD Building HVAC units. | 02-00-VRMA-AC-1,02-00-VRMA-AC-2
384167 | CR | 20180902 |  | 4 | XD-03 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** XD-03 not functioning as designed and requires maintenance. Contact security for more information. <I> **** Actions Taken **** Security supervision notified. XD-03 placed out of service. | 02-00-SEC-XD-3
384168 | CR | 20180903 | CAQ | D | Nice Video Recorder 2 not functioning as design | N | N |  | N | YES | <D> **** Detailed Description **** CAS Nice Video Recorder 2 is not functioning as design. Request engineering support. Call x2185 for more information due to safeguards <I> **** Actions Taken **** CR/WR Generated <N> **** Equipment Description **** Nice Video Recorder 2 is located inside the Central Alarm Station Building 62
384177 | CR | 20180903 |  | 3 | Procedure enhancements for OSP-RHR-A701 |  |  |  | N | NO | <D> **** Detailed Description **** A step to vent down RHR-A discharge pressure should be placed before step 7.4 in OSP-RHR-A701. See EDMS files for recommended wording. Precaution 3.3 should be removed so not to delay I&C from installing gauges. The same step is verified in the body of the procedure. The other Keep Fill verification OSPs should be checked to see if these changes are needed within them. RHR-B may need a note about entering a LHRA.
384178 | CR | 20180903 | CAQ | C | LEFM Status Error | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** On the TDAS LEFM screen (P15), LEFM Meter 2 plane status page shows the Plane A Status Data for Meter State as â€œUNKNOWN.â€ This causes a â€œMINOR ALERT â€“ CHECK +â€ indication on the LEFM Status Summary System Data screen. Switching to Receiver 1 as primary clears the â€œMinor Alert,â€ however Meter 2 still shows meter state as â€œUNKNOWN.â€ At no point were either Meter 1 or Meter 2 indicating other than â€œNormal â€“ Check +,â€ on the LEFM Status Summary screen under â€œMeter 1 Dataâ€ and â€œMeter 2 Data,â€ therefore there is currently no requirement to reduce core thermal power. <I> **** Actions Taken **** Swapped to Receiver 1 as primary, and sent an email to Station Nuclear Engineers. <N> **** Equipment Description **** LEFM System on TDAS Computer
384179 | CR | 20180903 |  | 4 | Battery fault on EBU | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-T501/1 located on the north wall of 501TG. Has a battery fault. <I> **** Actions Taken **** Initiated a CR for tracking, WR to repair, FSIP and staged lamp This is non-essential lighting. <N> **** Equipment Description **** 501 TG west side north wall | 02-00-E-BU-T501/1
384180 | CR | 20180903 |  | 3 | Recommend Procedure Change SOP-LPCS-SP |  |  |  | N | NO | <D> **** Detailed Description **** Upon start of LPCS-P-1, the Main Control Room received Annunciator 601.A3 drop 5-3, LPCS Discharge Pressure High/Low. This was not called out as an expected alarm upon starting LPCS-P-1. Due to initial discharge pressure spike upon starting the pump and sustained discharge pressure near the set-point, it is expected this annunciator will be brought in on every LPCS-P-1 start. Recommend adding A3 drop 5-3, LPCS Discharge Pressure High/Low as an expected alarm in the note above the step to start LPCS-P-1. <I> **** Actions Taken **** Informed CRS of the alarm, initiated this CR requesting a procedure change to SOP-LPCS-SP. This condition is not a DNC, but normal system response. A note should be added to the SOP to be consistent with the note in OSP-LPCS/IST-Q702 (expected alarm in the quarterly surveillance test). | 02-00-LPCS-P-1
384181 | CR | 20180903 | CAQ | D | High Effluent Conductivity Alarm RWCU-DM-1B | N | Y |  | N | YES | <D> **** Detailed Description **** The control room received annunciator P602.A5 drop 2-7, Filter Demin Effluent Conductivity High alarm several times. Indicated RWCU-DM-1B effluent spiked at approximately 0.255 umho/cm and the influent spiked at 0.78 umho/cm. In addition, the RWCR operator reported conductivity spikes on COND-DM-1B,D and F. Investigation by the crew determined these sample points are all common to S-CIT-202, High Purity Water Conductivity Analyzer. When dispatched to S-CIT-202, an operator noticed the LED screen was fading in and out, indications of a possible power supply failure. Effected sample points are as followed: SP-8, SP-27B, SP-71, SP-14B, SP-14D, SP-14F. S-CIT-201 appears to be operating normally. <I> **** Actions Taken **** Informed CRS and SM, control room entered ABN-CHEM. Chemistry samples indicate no abnormal chemistry condition, and all indications point toward instrument failure related to S-CIT-202. Informed operations management. Investigating LCS impact. | 02-00-RWCU-DM-1B,02-00-S-CIT-202
384182 | CR | 20180903 |  | 4 | Lost Simulator Time due to I/O Failure |  |  |  | N | NO | <D> **** Detailed Description **** On 8/27/18, 60 minutes of ILC simulator training time was lost due to an I/O failure that occurred in late the afternoon. An I/O power supply failed and two analog cards failed as well. Following replacement of the failed components with spares, the simulator was turned back over to ILC for training. SR 2789 was written to document simulator repairs. This CR was written to document lost time. <I> **** Actions Taken **** I/O failures repaired. Performance indicators updated with lost simulator time.
384183 | CR | 20180903 |  | 4 | WMA-FN-6 Belts failed | N | N |  | N | YES | <D> **** Detailed Description **** WMA-FN-6 Belts have failed. RWCR AC was not working, verified that the associated TCV, CCH valves were open, WMA-FN-6 running and everything looked normal. However, when looking inside the fan unit to check the Fan Belts, they were not attached to the fan. Need fan belts replaced to restore AC in RWCR. <I> **** Actions Taken **** CR/WR written. Supervision Notified. Secured and tagged out fan. Added to weekend issues list. | 02-00-WMA-FN-6
384184 | CR | 20180903 | CAQ | D | RHR-DPIS-12A Found out of tolerance | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of WO#02104486-01, ISP-RHR-Q901, RHR -DPIS-12A was found out of tolerance low. As found trip was 158 "H2O, reset was 138 "H2O. As left trip was 168"H2O, reset was 148"H2O. <I> **** Actions Taken **** Adjusted RHR-DPIS-12A per surveillance direction, notified CRS, wrote this CR. | 02-00-RHR-DPIS-12A
384190 | CR | 20180904 | CAQ | D | CRD-HCU-2211 has had 3 N2 alarms in LT 30 days | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-2211 has experienced low N2 pressure alarms on July 11 and 29, 2018, and August 11 and 23, 2018 which exceeds the criteria in PPM 1.3.79, Reactivity Management Administration, ie 3 alarms for same condition in a 30 day period, and thus requires initiation of a condition report to identify degraded equipment. This is not an operability concern. <I> **** Actions Taken **** Notified System Engineer. See individual CRs for immediate operability determinations. <N> **** Equipment Description **** R 522 L5/8.4 | 02-00-CRD-HCU-2211
384199 | CR | 20180904 |  | 4 | MCR toilet flushing valve broken | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The MCR toilet flushing valve is broken. First it continuously flushed. After isolating then unisolating the valve only flushes while the handle is held down. <I> **** Actions Taken **** Sign posted. WR written. <N> **** Equipment Description **** MCR restroom. | 02-00-W-BLDG-MISC
384200 | CR | 20180904 |  | 3 | RCC demineralizer showing signs of exhaustion | N | N |  | N | NO | <D> **** Detailed Description **** RCC weekly samples are showing a steady trend up in conductivity and PH. Per SWP-CHE-02 we are currently in a CCW action level 1 for PH as it is above the limit of 8. This is not a Tech Spec limit or an LCO issue. <I> **** Actions Taken **** Notified MCR, Chemistry supervision, system specialist and requested the demin change out work order be moved up within the required action limit 90 day window. | 02-00-RCC-DM-1
384206 | CR | 20180904 |  | 3 | Recorder Chart sent to records Control without Transmittal |  |  |  | N | NO | <D> **** Detailed Description **** A Record was sent to Records Control without a transmittal attached. Please refer to SWP-REC-02 Section 4.3.2 for the submittal process. <I> **** Actions Taken **** Notified my supervisor. Sending Record back to I&C Maintenance shop for correction/resubmittal.
384210 | CR | 20180904 |  | 3 | RWCU components not included on MEL |  |  |  | N | NO | <D> **** Detailed Description **** The following components are not included on the Master Equipment List (MEL): RWCU-SP-8, RWCU-SP-27A, RWCU-SP-27B, RWCU-SP-44, RWCU-PX-3, RWCU-PX-4, RWCU-PX-5, RWCU-ST-2. The components are found on the following drawings: RWCU-SP-8: M523-3 and 215-00,2790 RWCU-SP-27A: M523-3 and 215-00,2791 RWCU-SP-27B: M523-3 and 215-00,2792 RWCU-SP-44: M523-3 and 317-00,4875 RWCU-PX-3: M523-3 and 215-00,3144 RWCU-PX-4: M523-3 and 215-00,3144 RWCU-PX-5: M523-3 and 215-00,3334 RWCU-ST-2: M523-3, 215-00,3334, and 317-00,5169 The components need to be added to the Master Equipment List. <I> **** Actions Taken **** wrote CR <N> Per M501 note 13 these do not get EPN # See EDMS RWCU-ST-2 needs to be added into MEL
384211 | CR | 20180904 | CAQ | D | Invalid & Suspect ISFSI Cask RTD Temperature Indications | Y | N |  | N | YES | <C> AR reopened to add cross references for WO and WR, date extended and closed. <D> **** Detailed Description **** During final installation and calibration of the new ISFSI Temperature Monitoring System (TMS) via EC 15554, several temperature indications were identified as either invalid or marginal to the threshold of being considered invalid, i.e., suspect. They include the following: RTD #2 on SFS-STORM-003 RTD #3 on SFS-STORM-025 RTD #1 on SFS-STORM-033 RTD #2 & #3 on SFS-STORM-037 The ISFSI TMS has not yet been turned over to Ops, and therefore, is not yet being relied on to determine operability of cask cooling systems. Although the TMS project does not include changes to the temperature elements, correction of these deficiencies would be beneficial to Operations prior to turnover. The TMS is available to identify and troubleshoot these deficiencies. <I> **** Actions Taken **** Discussions with ISFSI Program Manager, CPM and Maintenance This equipemnt is not yet being used to determine compliance with ISFSI technical specifications and has not been turned over for operability. | 02-00-SFS-STORM-003,02-00-SFS-STORM-025,02-00-SFS-STORM-033,02-00-SFS-STORM-037
384217 | CR | 20180904 | CAQ | D | DSA-PCV-2A | Y | N |  | N | YES | <D> **** Detailed Description **** DSA-PCV-2A has a small air leak on the inlet side threads going into the body of the valve. <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-DSA-PCV-2A
384218 | CR | 20180904 | CAQ | D | CMS-SR-20 Particulate Filter Green Color | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02123982-01, Step 7.10.10c, upon removing Particulate Filter, it was noted that it had a slight green color. <I> **** Actions Taken **** Replaced filter. Turned removed filter over to Chemistry. As with previous discussions with Supervisor, wrote CR to document and continued with surveillance. <N> **** Equipment Description **** 548RX | 02-00-CMS-SR-20
384219 | CR | 20180904 | CAQ | D | DSA-PCV-1A | Y | N |  | N | YES | <D> **** Detailed Description **** DSA-PCV-1A has a small air leak coming from the bottom of the valve body <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-DSA-PCV-1A
384223 | CR | 20180904 |  | 3 | Maintenance R24 Outage Walkdown PI Yellow |  |  |  | N | NO | <D> **** Detailed Description **** This CR is to document that the R24 PI for outage walkdowns is yellow as of 9/3/18. Actions from this CR should be to develop and document recovery plan within 1 week.
384224 | CR | 20180904 | CAQ | C | Recurring DG-4 ground alarms with no resolution. | N | Y |  | N | YES | <D> **** Detailed Description **** E-GEN-DG4 has experienced frequent ground alarms. A quick search revealed at least 16 times over the last 5 years that the alarm was received during test runs. The following CRâ€™s identify the ground alarm in the subject line: 282128, 283903, 292613, 304866, 355601, 356444, 356774, 357021, 363415, 368227, 368496, 371446, 372549, 374615, 380584, 384082. The purpose of this CR is to identify actions to correct the degraded condition or to determine if this is a nuisance alarm that can be eliminated (disabled). <I> **** Actions Taken **** initiated CR for further evaluation. <N> The ground fault relay was calibrated, did not resolve issue. The ground fault relay was replaced, did not resolve issue. Cummins inspected generator terminals and load bank terminals and identified several deficiencies but did not resolve the issue. Recommend contracting Cummins to investigate the ground fault alarms and determine the cause and necessary actions to eliminate the alarm. | 02-00-E-GEN-DG4
384225 | CR | 20180904 |  | 4 | Finger injury- First aid (bandaid needed) |  |  |  | N | NO | <D> **** Detailed Description **** On 9/4/18, an individual reported they received a minor cut on a finger while operating the door of the restroom stall of Deschutes 2-297, menâ€™s restroom. Individual visisted Occupational Health, was provided a bandaid and returned back to work. The individual did not initially notice the injury but it likely occurred because the lock handle area had a chipped outter coating, which creates an abberasive surface. Coaching was provided to the individual to slow down and pay additional attention when performing everyday tasks. Contacted Facilities to repair the stall door. Based on discussions with Facilities, temporarily placed tape on the lock handle area until permanent repairs can be made. <I> **** Actions Taken **** Completed supervisor evalaution of the incident. Completed forms 26135, 321 and 322. Completed entry in Plant Tracking Log. Discussed with Occupational health, Industrial Safety, Department Manager, and VP Engineering.
384226 | CR | 20180904 |  | 3 | Dataglance validation problem |  |  |  | N | NO | <D> **** Detailed Description **** When validating WO 02124060 dataglance says that there is a new revision but there is no option to apply the revision. <I> **** Actions Taken **** wrote cr <N> The requirements data was recently brought into the DataGlance package and so the validate button recognizes that there was a change to the package. If data on the requirements panel has changed, since the original package was built, it will show that the package can be replaced, but if information didnâ€™t change on the requirements panel it doesnâ€™t recognize what information changed. This CR will be closed and CR 384226-02 will drive a Datamod to correct the issue.
384227 | CR | 20180904 |  | 4 | No stops in TO-EX-1 switch | N | N |  | N | YES | <D> **** Detailed Description **** TO-EX-1 switch on H13-P820 does not have stops to prevent rotation past the TO-EX-1A position as a minimum and most likely the TO-EX-1B position as well. When swapping exhausters TO-EX-1A started and stopped as the switch went slightly past the 1A position (not normal for stop to be missing) then started when firmly in the detent in the 1A position. Request the normal stops be incorporated in this switch. <I> **** Actions Taken **** informed electricians doing start checks - they verified normal start and run current to motor. | 02-00-TO-RMS-EX/1
384228 | CR | 20180904 |  | 4 | S-Door-S110 does not fully close | N | N |  | N | YES | <D> **** Detailed Description **** (FP) S-Door-S110 does not fully close under normal operation. Door is a non-essential 3 hour rated fire door <I> **** Actions Taken **** Wrote CR and opened BI 18-0373 <N> **** Equipment Description **** Service building | 02-00-S-DOOR-S110
384229 | CR | 20180904 | CAQ | D | MS-LIS-37C Swtch 1A out of Cal. Limits. | Y | N |  | N | YES | <D> **** Detailed Description **** MS-LIS-37C Swtch 1A out of Cal. Limits. WO#02098555-01. As found = 195.1, as left = 199.6. <I> **** Actions Taken **** adjusted switch. | 02-00-MS-LIS-37A
384230 | CR | 20180904 |  | 4 | HID Fixture need repair on 606â€™ RxBldg | N | N |  | N | YES | <D> **** Detailed Description **** After performing 0212139101 EERBR60601, QTRLY. TEST per 10.25.64, we found Fixture #3 on ELP-8BA-5, #5 on ELP-8BA -6, #8 on ELP-8BA-7 and #4 on ELP-8BA-8 not working. This issues has been documented before in the previous quarterly inspection CR380967. The electricians will need the support or/from the mechanics to operate MT-CRA-2 to repair the lamp issues. This may need to be made into a WO with a support task and be scheduled appropriately in order to be resolved. <I> **** Actions Taken **** Close quarterly, write this CR to document issue <N> **** Equipment Description **** HID fixtures on 606' see WO 02121391-01's 10.25.64 | 02-00-E-ELP-8BA,02-00-R-BLDG-MISC
384231 | CR | 20180904 |  | 3 | Ops surveillance not on proper screen DATAGLANCE |  |  |  | N | NO | <D> **** Detailed Description **** WO 02124089 is an ops surveillance that did not show up on the operations screen to authorize work in dataglance. It should have had to been authorized on the ops screen. <I> **** Actions Taken **** Wrote CR <N> The task in question has been completed. A check was made of the rest of the occurrences of this same PM and they all show up on the correct Ops Authorization panel for future authorization. The Ops Review flag is set on the tasks in question so they all should be on the Ops Authorization screen for initial authorization. If this one was on the Supervisor Authorization panel instead, then the Ops Review flag just have not been set at the time. However, It was checked and it is set. The PM Task is finished now.
384232 | CR | 20180905 |  | 4 | TO-F-2 strainer basket needs replaced. | N | N |  | N | YES | <D> **** Detailed Description **** Large oil leaking, indication of TO-F-2 needing replacement. <I> **** Actions Taken **** Informed MCR. | 02-00-TO-F-2
384241 | CR | 20180905 | CAQ | C | SNMtrac does not decay Pu-238 correctly. |  |  |  | N | NO | <C> Per MRT feedback received on Monday 9/10/2018, this has been re prioritzed to a CAQ - C. <D> **** Detailed Description **** In SNMtrac, Plutonium classified as Material Type 83 (Pu -238 greater than 10% of total Plutonium) does not decay a reportable amount during a single report period. However, over an extended period of time, the aggregate decay of Pu-238 is reportable. SNMtrac does not handle this situation and this could lead to inaccurate annual reports of special nuclear material quantities. A manual calculation is necessary to determine when Pu-238 decay should be reported. PPM 9.2.3 should be revised to require this manual calculation for Pu-238 until the software is updated to addresses this problem. See EDMS for error notice. <I> **** Actions Taken **** Verified that previous annual reports of Pu-238 quantities were correct. While Pu-238 decay did occur, the decay was not sufficient to change the reportable quanity. <N> **** Equipment Description **** FW-SOFT-TECH-SNMTRAC Version 6.0 BUILD 19 | FW-00-SOFT-TECH-SNMTRAC
384242 | CR | 20180905 |  | 3 | Lenel controller(s) reporting alarms | N | N |  | N | YES | <D> **** Detailed Description **** Lenel controllers are reporting alarms indicating the area served is having issues. In investigating the alarms, no issues are found. <I> **** Actions Taken **** The areas were walked down to verify the alarms were in error. The Lenel controller boards were visually inspected. <N> **** Equipment Description **** Paap building, building 64
384243 | CR | 20180905 | CAQ | D | Undeclared items at the Security Checkpoint |  |  |  | N | NO | <D> **** Detailed Description **** Undeclared prohibited items were discovered during a vehicle search at the security checkpoint. The individual was coached prior to arriving on site. <I> **** Actions Taken **** Individual was turned around at the gate and will not return for the completion of this work. Notified Supervision.
384244 | CR | 20180905 |  | 4 | E-CB-3/31 closed & open light sockets missing bulbs. | N | N |  | N | YES | <D> **** Detailed Description **** Discovered both lamps/bulbs missing from closed & open light sockets, thus new ones were not put in due to unknown bulb type of 24E or 24E3 and putting wrong lamp in would break the sockets. <I> **** Actions Taken **** Informed SSS & MCR, initiated AR. | 02-00-E-CB-3/31
384245 | CR | 20180905 |  | 4 | HP department over the Aug. dose goal |  |  |  | N | NO | <D> **** Detailed Description **** The HP department received 415mrem against a goal of 347mremin the month of Aug. The reasons for this overage was dose carried over from last month due to work sliding during the week of 7/30/18, RWCU system outage overrun and some emergent dose in RW processing. <I> **** Actions Taken **** WRote CR.
384248 | CR | 20180905 | CAQ | D | DSA-DY-1B drain line is clogging | Y | N |  | N | YES | <D> **** Detailed Description **** DSA-DY-1B blow down line appears to be clogging, as evidence by abnormally timid audible and visual indications during shiftly dryer blowdown. DSA-DY-1B was verified to be ~ 150 PSIG, and should have had enough pressure to create normal audible blow down indications. DSA-V-77B (blow down isolation) operated normally. The drain line is not completely clogged, and the shiftly blow down, to remove moisture from the Dryer, was completed satisfactorily. Please investigate/repair prior to complete clogging. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** DG2 room | 02-00-DSA-DY-1B,02-00-DSA-V-77B
384249 | CR | 20180905 |  | 4 | COND-V-208A indicates intermediate when open. | N | N |  | N | YES | <D> **** Detailed Description **** During the Backwash of COND-DM-1A IAW SOP-CFD-BW/PC section 5.1, COND-V-208A (fast drain valve) indicated intermediate when open. All other indications such as flow and CPR-TK-14 level increase suggest a limit switch problem. COND-V-208A also indicated full open on step dd of the Backwash. Please T/S repair as necessary. <I> **** Actions Taken **** Notified supervisor. Verified normal Backwash. <N> **** Equipment Description **** RW 467 | 02-00-COND-V-208A
384250 | CR | 20180905 | CAQ | C | (QA) Safety/Security Interface Inconsistently Implemented |  |  |  | Y | NO | <C> CAP Supervisor recommends this CR to be C/NUCSEC and completed, referenced to CR 384253 to do as a roll-up. <D> **** Detailed Description **** (QA) Review of potential security impacts from planned and emergent work are not consistently documented or managed in accordance with SWP-SEC-14, â€œSafety/Security Interface Programâ€ and SFI-23 â€œSafety/Security Interface Instructionsâ€. SWP-SEC-14 uses Form 26803 to implement regulatory requirements in 10 CFR 73.58 â€œSafety/security interface requirements for nuclear power reactorsâ€. Actual consequences are three Work Requests (WRs) contain no evidence of 10 CFR 73.58 assessments completed per SWP -SEC-14 prior to performing the work. Factual Basis: see EDMS for details Insights: Security personnel completed impact screening (form 26803) for the 3 WRs implemented prior to assessment. No impacts were identified. See EDMS for additional insights. <I> **** Actions Taken **** This deficiency was identified in Quality Audit AU-SE -PADS-MRO-SAE-18. Recommend assignment to Security. <N> **** Equipment Description **** N/A
384251 | CR | 20180905 | CAQ | C | (QA) SWP-SEC-14 is Not Well-Integrated into Site Processes |  |  |  | Y | NO | <C> CAP Supervisor recommends this CR to be C/NUCSEC and completed, referenced to CR 384253 to do as a roll-up. <D> **** Detailed Description **** (QA) Security has not ensured requirements in SWP-SEC-14 â€œSafety/Security Interface Programâ€ were effectively integrated into site processes. SWP-SEC-14 implements 10 CFR 73.58 requirements, and it specifically requires the originator of listed processes to complete Form 26803 â€œIdentifying Potential Security Impactsâ€ prior to performing work covered under 10 CFR 73.58. Sampling revealed procedures for some listed processes are not aligned with SWP-SEC-14 requirements, and SWP-SEC-14 does not list some site processes that result in activities requiring the assessment of potential safety/security impacts. The stationâ€™s adherence to requirements within 10 CFR 73.58 is error-likely when site processes are not aligned with safety/security interface requirements within SWP-SEC-14. Six examples show Form 26803 was not completed for maintenance activities and physical modifications covered under the 10 CFR 73.58 regulation. Actual consequences are no evidence of a 10 CFR 73.58 assessment on Form 26803 prior to performing the work, contrary to SWP-SEC-14, for three WO Tasks (WOTs), two Permanent Modifications, and several Preventative Maintenance activities. Factual Basis: See EDMS for details. Insights: SWP-SEC-14 lists processes for WRs, WOs, and Permanent Modifications to receive safety/security potential impact screening; however, this procedure does not list any process to similarly screen any design/build, installation, or PM work performed under contracts not associated with a WR or an EC. See EDMS for additional insights. <I> **** Actions Taken **** This deficiency was identified in Quality Audit AU-SE -PADS-MRO-SAE-18. Recommend assignment to Security. <N> **** Equipment Description **** N/A
384253 | CR | 20180905 | CAQ | C | (QA) ARMA - Multiple gaps in Safety/Security Interface Prog |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Multiple gaps exist in the Safety/Security Interface Program, including inconsistent implementation of the program by Security and other work groups, and program requirements not well-integrated into other site processes. SWP-SEC-14 â€œSafety/Security Interface Programâ€ implements 10 CFR 73.58 â€œSafety/security interface requirements for nuclear power reactorsâ€. Sampling revealed multiple examples of maintenance activities and physical modifications covered under the 10 CFR 73.58 regulation that were not assessed for potential adverse impacts on safety and security prior to performing work. These examples indicate insufficient Safety/Security Interface Program oversight by Security. Ineffective implementation of 10 CFR 73.58 requirements could lead to inadequate mitigation of adverse safety and security impacts and/or a reduction in regulatory margin. Factual Basis: See EDMS for details. Insights: No formal/informal assessments focused on the program were performed since the Safety/Security Interface Program was first formalized as SWP-SEC-14 in 2010, due in part to favorable feedback from external agencies. This ARMA provides an opportunity to review the scope and implementation of the program to ensure it is designed to drive the behaviors and results expected across the station. See EDMS for additional insights. <I> **** Actions Taken **** This issue was identified in Quality Audit AU-SE-PADS-MRO -SAE-18 Recommend assignment to Security. <N> **** Equipment Description **** N/A
384254 | CR | 20180905 |  | 3 | (QA) Data Not Entered PADS within one day |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Potentially disqualifying information (PDI) was not entered into the Personnel Access Data System (PADS) within one business day contrary to NEI 03-05 â€œPersonnel Access Data System Operating Manualâ€. If PDI is used to deny the Unauthorized Access Authorization/Unauthorized Access (UAA/UA) application or unfavorably terminate UAA/UA, the appropriate basis for action (BFA) entry should be entered in PADS within one business day. An individual that applied for UAA/UA was subsequently denied based on PDI. PADS records indicated the Pre-Access Additional Information BFA was not entered until the second business day after the decision to deny UAA/UA was made. The omission or late entry of the BFA has the potential to allow an individual to enter the protected area of a nuclear power plant or be granted UAA/UA as an individual maintaining UAA/UA under another licensee program. The individual did not enter the Protected Area of another licensee as a result of this issue. Factual Basis: See EDMS for details. Insights: There is no guidance to verify and validate that PADS data entry was made in the time required. See EDMS for additional insights. <I> **** Actions Taken **** This deficiency was identified in Quality Audit AU-SE -PADS-MRO-SAE-18. Recommend assignment to Security. <N> **** Equipment Description **** N/A Data entry for PADS was fixed at the time of discovery. The current process adequately addresses the process and the individuals and group have been briefed and management has reinforced the expectations regarding the entry of PADS data. No further actions are required as this time.
384256 | CR | 20180905 |  | 3 | (QA) Unclear Distinction for Contraband and Prohibited Items |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Security procedures SWP-SEC-03, SPIP-SEC-06, SPIP -SEC-22 use the terms â€œprohibited itemsâ€ and â€œprohibited articlesâ€ interchangeably to mean the same thing (contraband). However, the NRC considers contraband and prohibited items to be two separate terms that are used for reportability purposes. Contraband could be a 1-hour reportable event, while prohibited items are loggable events. Factual Basis: See EDMS for details. Insights: Contraband is a specific category of items for NRC reporting purposes. Including contraband items with the larger population of prohibited articles could lead to missed reports or reports submitted when not required. Columbia Generating Station did not submit any NRC reports under this requirement in the last two years. <I> **** Actions Taken **** This deficiency was identified in Quality Audit AU-SE -PADS-MRO-SAE-18 See EDMS for additional insights. <N> **** Equipment Description **** N/A
384257 | CR | 20180905 |  | 3 | Typo on FSAR page 3.2-24 |  |  |  | N | NO | <C> CR 384257 Re-screened at OFM today (10.15.2018) from CAQ/C to AR-DMC to Non-CAQ/3 to AR-DMC. <D> **** ANONYMOUS CR - Detailed Description **** A typographical error (typo) exists on FSAR page 3.2-24. In the existing FSAR Table 3.2-1 g discussion associated with Seismic Category regarding 1M (and Seismic II+), 'hangars' should be 'hangers'. <N> Anonymous CR, moved to CR-SRO for review.
384258 | CR | 20180905 |  | 3 | BPA request 3 weeks notice prior to transferring ASHE power |  |  |  | N | NO | <D> **** Detailed Description **** Due to BPA outage planning changes, BPA request 3 weeks notice prior to transferring ASHE power. SOP-ELEC-4160V-OPS notes need revised and any model WOs that reference prior notice. <I> **** Actions Taken **** Initiated CR.
384260 | CR | 20180905 | CAQ | C | MEL and FSAR updates for Seismic II+ should be considered |  |  |  | N | NO | <D> **** Detailed Description **** FSAR Section 3.2.6 provides a rosetta stone type comparison of various classification information indicated on the Flow Diagrams (which are generally also FSAR Figures), FSAR Table 3.2-1, and the MEL (i.e., Portal J / Asset Suite). Seismic Category II+ (+ = hangers to be designed to Seismic Category I loads) is a classification indicated on the Flow Diagrams for portions of many systems (e.g., the nonsafety- related parts routed in or through safety-related Seismic Category I areas of the plant) but is not currently included in the FSAR Section 3.2.6 comparisons. This should be considered for addition to FSAR Section 3.2.6. Currently, FSAR Table 3.2-1 appears to call out FSAR Figure Seismic Category II+ SSCs as Seismic Category II with the clarification of existing FSAR Table 3.2-1 Note h 4 which states "Supports for Quality Class II (nonessential) piping systems, HVAC, cable trays, and system components in the reactor building, primary containment, the control building, diesel generator building, the standby service water (SW) pump houses, and the radwaste building corridor are designed and constructed to withstand an SSE per position C.2 of Regulatory Guide 1.29. These supports are constructed to Quality Class II requirements, as a minimum." In the MEL (Portal J / Asset Suite), it appears that SSC EPNs the Flow Diagrams indicate are Seismic Category II+ are currently only called out as Seismic [Category] 2 -- the MEL is currently silent for these SSCs with respect to the FSAR requirement for their associated hangers (i.e., that their hangers are to be designed to Seismic Category I loads). MEL updates for these SSC EPNs to indicate this associated applicable FSAR requirement should be considered. FSAR Table 3.2-1 g discussion associated with Seismic Category 1M currently states "1M - non-safety-related components required to be seismically supported/mounted. This was alternatively called Seismic II+ which is Seismic II piping supported on hangars designed to Seismic I loads." Per FSAR Section 3.2.1, "Seismic Category 1M classification denotes systems, structures, or components that are designed and constructed to comply with position C.2 of Regulatory Guide 1.29." FSAR Section 3.2.4 b. 2. currently states "Structures, systems, and components that do not perform a safety-related function but must be seismically supported/mounted (seismic 2-over-1) per Regulatory Guide 1.29" should be classified as Quality Class II+ (Augmented Quality). If Seismic Category II+ is equivalent to Seismic Category 1M as the existing FSAR Table 3.2-1 g discussion for 1M indicates, this appears to create a discrepancy in FSAR and MEL Quality Class for FSAR Figure Seismic Category II+ SSCs/EPNs. To eliminate this discrepancy, an update for the FSAR Table 3.2-1 g 1M Seismic II+ discussion (e.g., to add "(hanger construction to Quality Class II requirements as a minimum)" or to eliminate the existing sentence containing Seismic II+ all together) should be considered. . Resolution assignment to Design Engineering is suggested. This is an administrative legacy issue only.
384264 | CR | 20180905 |  | 3 | SOP-CW-CHEM-MAINT needs change to reflect new pump. |  |  |  | N | NO | <D> **** Detailed Description **** CF-P-41B was replaced per WO 02110623 with a newer model of pump. The oil reservoir has a screw on cap without a dipstick, but has a bullseye on the opposite end of the pump from the oil fill hole. SOP-CW-CHEM-MAINT step 5.10.2p has the operator check that oil level indicates on the dipstick. This step needs to be changed to check that oil level indicates in the bullseye. The other three chemical feedpumps are still the older style with dipsticks and no bullseye. As they are replaced, the procedure steps will need to be changed to reflect this. <I> **** Actions Taken **** Informed supervisor and wrote this procedure change AR. <N> Should this be tracked as an assignment under AR OBS 349142? | 02-00-CF-P-41B
384265 | CR | 20180905 |  | 3 | (QA) Wrong Security Interface Doc Listed in ENG-DES-50 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) ENG-DES-50 â€œInterface Procedure for IP-ENG-001 Standard Design Processâ€ incorrectly cites PSP-01 â€œPhysical Security Planâ€ as the interface for 10 CFR Part 37 â€œProtection of Category 1 and Category 2 Quantities of Radioactive Materialâ€. Factual Basis: PSP-01 addresses 10 CFR 73 requirements, but does not address 10 CFR 37 requirements. PART37-01 â€œPart 37 Security Planâ€ is the document that addresses 10 CFR 37 requirements. â€¢ ENG-DES-50 Attachment 7.2 â€œIP-ENG-001 EC Product Type Interfacing Instructions/Procedures Matrixâ€ incorrectly cites â€œPSP-01â€ as the â€œCGS interfacingâ€ document instead of â€œPART37-01â€. Insights: ENG-DES-50 was created on 4/27/17, but the PART37-01 document has existed since 3/18/14.The individual that created ENG-DES-50 had never heard of the PART37-01 document. <I> **** Actions Taken **** This deficiency was identified in Quality audit AU-SE -PADS-MRO-SAE-18 Recommend assignment to Design Engineering. <N> **** Equipment Description **** N/A
384266 | CR | 20180905 | CAQ | C | (QA) SWP-SEC-02 Missing Regulatory Information |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) SWP-SEC-02 â€œProtection of Safeguards Informationâ€ Section 3.8 is missing two requirements from 10 CFR 73.59 â€œRelief from fingerprinting, identification and criminal history records checks and other elements of background checks for designated categories of individualsâ€. 10 CFR 73.59 contains requirements for relief from fingerprinting identification and criminal history records checks and other elements of background checks for designated categories of individuals. SWP-SEC-02 step 3.8.2 incorporates the requirements in 10 CFR 73.59, but does not contain two requirements contained in this regulation. Failure to adequately incorporate 10 CFR 73.59 requirements can lead to denial of access to Safeguards information to persons authorized for access by the regulation. Factual Basis: See EDMS for details. Insights: No visitors fitting the descriptions of requirements (d) or (k) were denied access to safeguards information in the last 2 years. See EDMS for additional insights. <I> **** Actions Taken **** This deficiency was identified in Quality audit AU-SE -PADS-MRO-SAE-18 Recommend assignment to Security. <N> **** Equipment Description **** N/A
384267 | CR | 20180905 |  | 3 | (QA) Licensing Instructions Reference Canceled Instruction |  |  |  | Y | NO | <A> Both of these conditions are minor and editorial in nature inside of department instructions. Revisions are in progress to address. No consequences can be attributed to the editorial oversight. No further actions are needed. <D> **** Detailed Description **** (QA) RPI-5.0, "Preparation and Submittal of Regulatory Correspondence", and RPI-17.0, "Requesting Withholding From Public Disclosure of Information in Submittals", have references to RPI-11.0, Processing Safeguards Information in Documents & Correspondence. RPI-11.0, "Processing Safeguards Information in Documents & Correspondence", was cancelled in 2011 as redundant to SWP-SEC-02. Quality recommends removing the references to RPI-11.0. Factual Basis: RPI-5.0, "Preparation and Submittal of Regulatory Correspondence", Revision 016-000, Step 3.5.1a.3) states, in part "The correspondence is appropriately marked in accordance with â€¦ RPI-11.0, Processing Safeguards Information in Documents & Correspondence". RPI-17.0, "Requesting Withholding From Public Disclosure of Information in Submittals", Revision 000-001, step 9.6 references RPI-11.0, "Processing Safeguards Information in Documents and Correspondence". â€¢ RPI-11.0, "Processing Safeguards Information in Documents & Correspondence", was canceled in 2011 as being redundant to SWP-SEC-02. <I> **** Actions Taken **** This deficiency was identified in Quality audit AU-SE -PADS-MRO-SAE-18 Recommend assignment to Licensing. <N> **** Equipment Description **** N/A
384268 | CR | 20180905 |  | 3 | (QA) Contract Requirements for Backup MRO not Met |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The technical requirements for the Medical Review Officer (MRO) service contract were not met. Specifically, the service provider (Lourdes Occupational Health) does not provide a back-up MRO, contrary to the Appendix A â€œStatement of Workâ€ within Contract 327300. Back-up MRO services were not requested by Energy Northwest within the last 2 years; therefore, there were no consequences of the vendorâ€™s non-compliance with this contract. Factual Basis: See EDMS for details. Insights: 10 CFR 26.183 does not require licensees to have a back -up MRO under contract. See EDMS for additional insights. <I> **** Actions Taken **** This deficiency was identified in Quality audit AU-SE -PADS-MRO-SAE-18 Recommend assignment to Security. <N> **** Equipment Description **** N/A
384269 | CR | 20180905 |  | 3 | four work orders removed from 9-24-18 work week |  |  |  | N | NO | <D> **** Detailed Description **** Four work orders were rescheduled out of the 9/24/18 work week due to scope change and resource limitations. This did not meet work management expectations of scope freeze at T-7. Recommend assigning AR action to the appropriate work group to determine the appropriate work scope. <I> **** Actions Taken **** Operations and craft notified of the removal from the schedule. All work order tasks taken to returned with reference to this CR.
384270 | CR | 20180905 |  | 3 | (QA) Annual PADS Data Validation Analysis Not Completed |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Annual analyses of Personnel Access Data System (PADS) data validation results were not conducted. There are no known consequences as a result of missing these analyses. Factual Basis: NEI 03-05, â€œPersonnel Access Data System Operating Manualâ€ requires the PADS Site System Administrator to conduct monthly and annual analysis of the data validation results. SWP-SEC-06, â€œPersonnel Access Data Systemâ€, revision 008/001, step 2.4 states â€œVERIFY PADS is operated in accordance with the provisions of NEI 03-05, PADS Operating Manualâ€. Insights: SWP-SEC-06, â€œPersonnel Access Data Systemâ€ does not require this annual analysis. Analysis of data validation is conducted monthly. No issues were identified as a result of these monthly analyses in 2016 or 2017. The annual analyses for 2016 and 2017 were completed during the audit and did not identify any issues with data validation. <I> **** Actions Taken **** This deficiency was identified in Quality audit AU-SE -PADS-MRO-SAE-18 Recommend assignment to Security. <N> **** Equipment Description **** N/A SWP-SEC-06, "Personnel Access Data System" does not require this annual analysis as the validation is conducted on a monthly basis. However, upon identification of this annual review not being conducted a thourough review of the 2016 and 2017 were conducted with no issues identified. No further actions required at this time.
384271 | CR | 20180905 |  | 3 | (QA) Errors in Security Procedures/Instructions |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Several Security procedures and instructions include errors including incorrect revision dates, references to canceled documents, and providing direction for equipment no longer in-use. Factual Basis: See EDMS for details. Insights: SFI-11 is a department instruction that relies on SWP -LIC-03 for license changes, therefor there is no conflicting guidance. Incorrectly citing a reference creates an error likely situation for accurate review and understanding of procedure requirements. Instructions to use communication equipment no longer in service could cause confusion or delay in communicating important information. . <I> **** Actions Taken **** This deficiency was identified in Quality audit AU-SE -PADS-MRO-SAE-18 Recommend assignment to Security. <N> **** Equipment Description **** N/A
384272 | CR | 20180905 |  | 3 | (QA) GBP-HR-23 Incomplete Procedure Update |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) GBP-HR-23 â€“ â€œDeath of an Employeeâ€ has an incorrect title in the Table of Contents. Factual Basis: GBP-HR-23 â€“ DEATH OF AN EMPLOYEE procedure version Major 000 Minor 004 has an incorrect position title listed in the Table of Contents. The section header in the Table of Contents reads; â€˜Manager, Nuclear Securityâ€™ and should be â€˜Manager, Security Operationsâ€™. Insights: The procedure was initially updated under CR 354235 to address a title change. The title change was completed in the body of the procedure, however, the change was not applied to the Table of Contents. The section header in the Table of Contents reads; â€˜Manager, Nuclear Securityâ€™ and should be â€˜Manager, Security Operationsâ€™. <I> **** Actions Taken **** This deficiency was identified in Quality audit AU-SE -PADS-MRO-SAE-18 The required procedure changes are complete, no further action is required. Recommend assignment to Human Resources. <N> **** Equipment Description **** N/A GBP-HR-23 has been updated.
384273 | CR | 20180905 | CAQ | D | (QA) AR-EVAL not Documented per DES-2-9 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Forms 26867 and 26868 were not uploaded into AR-EVAL 373534's EDMS per DES-2-9. Assignment 01 states that evaluation was perform per DES -2-9 "Technical Evaluations". Neither form 26867 or 26868 were uploaded into the EDMS for AR-EVAL 373534 Factual Basis: See EDMS for details. Insights: EC 4791 was used to deactivate SEC-MON-XD1, XD2, XD3. See EDMS for additional insights. <I> **** Actions Taken **** This deficiency was identified in Quality audit AU-SE -PADS-MRO-SAE-18 Recommend assignment to Security. <N> There was no deficiency in the process, it was a human error and the employee was coached, the work is complete and no adverse consequences came of it. | 02-00-SEC-MON-XD1,02-00-SEC-MON-XD2,02-00-SEC-MON-XD3
384275 | CR | 20180905 |  | 3 | PRNM Service on PDIS-CPU-DATA1 will not run | N | N |  | N | YES | <D> **** Detailed Description **** The UnvSrv64.exe program that recieves PRNM data from the local PRNMRCVR.exe program will not function correcctly. This CR should go to Computer Engineering to investigate. This data is engineering trend data and does not affect operations. PRNM Data is still working on PDIS-CPU-DATA2. <I> **** Actions Taken **** Tried restarting process which did not work. Rebooted Server which did not work. | 02-00-PDIS-CPU-DATA1
384277 | CR | 20180905 |  | 3 | RRC-E/S-S01A failure | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During attemoted burn in of replacement power supply RRC-E/S-S01A, it was noted once the AC power was applied, with no load on the DC side there was a very strong burnt smell coming form the E/S. <I> **** Actions Taken **** Notified Supervisor and Engineering, Engineering agreed that something is wrong/failing on the E/S. It is not noticable due to the frame of the E/S. Short of taking the E/S completely apart, Engineering agreed to not use these E/S and send it back for repair. | 02-00-RRC-E/S-S01A
384280 | CR | 20180905 | CAQ | D | SL-71 GND Fault Relay lights burned out | Y | N |  | N | YES | <D> **** Detailed Description **** When D-E-MC-7C/GND-001 clearance was lifted, the lights on SL-71 GND Fault Relay was reenergized but only 5 out of 22 came on, the other 17 were burned out due to loss or restoration of power. All 22 lights were on before removing power. We expect some lights might blow but 17 seemed excessive. So this AR is written for trend purposes. <I> **** Actions Taken **** Informed SSS, Replaced all the burned out bulbs, FIN elec supported, as 10 of the light sockets were extremely hard to insert bulbs into. | 02-00-E-SL-71
384282 | CR | 20180905 |  | 3 | SOP-CW-CHEM-MAINT needs a section to allow FLUSHING OF THE S |  |  |  | N | NO | <D> **** Detailed Description **** SOP-CW-CHEM-MAINT needs a section to allow FLUSHING OF THE SULFURIC ACID SYSTEM WITHOUT FLUSHING SAT-TK-2. There is work that is scheduled that requires all of the SAT system to be flushed with the exception of SAT-TK-2. Chemistry and ENGINEERING do not want to flush SAT-TK-2 every time we need to drain THE TANK OR FLUSH THE REST OF THE SYSTEM over concerns of damaging the liner inside of SAT-TK-2 caused by the violent exothermic reaction that occurs when water and sulfuric acid mix. There are currently independent sections to flush 3 separate lines, (A/B/BYPASS) HOWEVER, THEY DO NOT WORK WELL FOR THIS WORK, IT REQUIRES OPERATORS TO CONNECT/DISCONNECT HOSES 3 SEPARATE TIMES IN A CONFINED SPACE UNNESECARILY, AND IT WOULD ALSO REQUIRE SEVERAL STEPS TO BE N/Aâ€™D THAT ARE NOT CONDITIONAL. I have put together what a new section would look like referencing several steps from SOP-CW-CHEM-MAINT. THIS WORK IS SCHEDULE D FOR 10/29/2018. REF EDMS
384283 | CR | 20180905 | CAQ | C | FCP1 Ground Fault | N | Y |  | N | YES | <D> **** Detailed Description **** After installing a wiring harness per work step 4.25.11 between SM3 and SM11 a ground fault occured. Craft stopped work and contacted their supervisor. This ground fault was illuminated when the old annunciator panel was functioning and the system engineer was hoping that after installing the new annunciator panels that it would take care of this issue. <I> **** Actions Taken **** Per the note below NOTE: If at any time during the module verification testing process the Ground Fault indication is locked in at the CP-35 and can not be reset, Then initiate a CR and reference what set of modules was being introduced to the CP-35. Document the CR# in the trouble found work performed section of this WO Task and the remaining ground fault verification steps of this task can be N/A. <N> **** Equipment Description **** FCP1 | 02-00-FP-CP-FCP1
384284 | CR | 20180905 | CAQ | C | Elevated corrosion rates in open cooling systems | Y | N |  | N | NO | <D> **** Detailed Description **** Short-term and long-term corrosion coupons were removed from TSW, CW, and SSW systems on 6/13/2018. Corrosion rates of individual metal samples were calculated by mass loss and expressed relative to the exposure time as mils per year (mpy). A synopsis of results follows. The following carbon steel and cast steel materials exceeded the EN criteria of 2.0 mpy after 91-days of exposure: TSW1-cold leg GCCL30 (2.11 mpy) TSW2-hot leg C1010 (6.45 mpy), A106GrB (8.30 mpy) CW C1010 (2.74 mpy), A36 (4.04 mpy) SSW C1010 (3.02 mpy) and A36 (3.37 mpy). The corrosion rates for the following copper alloys exceeded the EN criteria of 0.2 mpy after 91 days of exposure: TSW2-hot leg CDA706 copper-nickel alloy (0.21 mpy); SSW CDA122 (0.28 mpy) and CDA443 admiralty brass (0.20 mpy). The following carbon steel and cast steel materials exceeded the EN criteria of 2.0 mpy after 182-days of exposure: TSW1-cold leg GCCL-30 cast steel (2.01mpy) and A106GrB carbon steel (2.25 mpy); TSW2-hot leg C1010 (4.20 mpy) and A106GrB (3.57 mpy); CW A36 (2.04 mpy) SSW C1010 (2.28 mpy) and A36 (2.46 mpy). These values have exceeded the EN criteria in the past. <I> **** Actions Taken **** Notified chemistry specialist. Recommend assignment to chemistry. Full corrosion coupon report is provided in EDMS docs. | 02-00-CW-PIPE-MISC,02-00-SW-PIPE-MISC,02-00-TSW-PIPE-MISC
384285 | CR | 20180905 |  | 4 | Sump W-1 high oil content | N | N |  | N | YES | <D> **** Detailed Description **** Sump W-1 high oil content. Very milky white coating on top of sump. Oil pillows saturated and submerged. Normal culprit for oil in this sump historically has been SA-C-1 drains. Recommend CT's for pump in PTL, laborers pump sump contents to barrels, replace oil pillows, investigate source of oil. <I> **** Actions Taken **** Informed MCR, RWCR <N> **** Equipment Description **** Siump W-1 RW 437 | 02-00-FDR-SUMP-W1
384286 | CR | 20180905 |  | 4 | SA-C-1 thick foamy layer on top of oil level | N | N |  | N | YES | <D> **** Detailed Description **** SA-C-1's oil sight glass shows a normal level but the top 1/8-1/4 inch is a thick white-ish foam. This is not normal and the immediate reason is not known. This may be connected to the recently found issue of the milky-white consistency of sump W-1 which receives SA-C-1 and SA-DY-1 drains. On 467 there is a oily presence within the drain scupper and liquid is actively going in it. Currently there are significant TOC issues with multiple tanks failing, which is leading to backing up radwaste processing. This may not be the absolute cause, but it is certainely contributing. See CR 00384285. | 02-00-SA-C-1
384287 | CR | 20180906 |  | 4 | Flocculator level does not appear to be tracking. | N | N |  | N | YES | <D> **** Detailed Description **** During OPS4 night shift logs flocculator level was 21.7 feet (2000). Flocculator was started. Level at 0030 was still 21.7 feet with flocculator still running. Make up was 240 to 310 gpm, PW usage was 35 to 70 gpm (was a period for 1.5 hours were it was about 150 gpm). No water was exiting the dump valve and operation appeared to be normal. <I> **** Actions Taken **** Informed CRS. | 02-00-PWC-FU-1,02-00-PWC-LI-100
384288 | CR | 20180906 | CAQ | D | FP-V-5 handwheel broke while operating. | N | Y |  | N | YES | <D> **** Detailed Description **** FP-V-5 handwheel sheared from yoke arm spinning freely (could remove hand wheel if desired). The break occured while closing the valve. No valvle operator used and normal amount of force was used. Valve was only slightly difficult, easier to operate than expected. <I> **** Actions Taken **** Stopped and informed CRS. <N> broken stem bushing is more accurate failure description | 02-00-FP-V-5
384294 | CR | 20180906 | CAQ | D | M&TE Suspended/ Lost | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0066426 Starrett Dial Caliper- model 120A-6 6in can't be located & Out of Calibraiton. EFIN EVAL: Suspended/ Lost. The M&TE being lost has no bearing on the maintenance performed. The first two items had post maintenance testing performed to ensure the associated equipment functions properly. The last item was a surveillance that passed without issue or changes required. These PMTS and SAT surveillance are evidence that the M&TE worked prior to being lost. DEF #6730A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
384295 | CR | 20180906 |  | 4 | I&C exceeded August dose |  |  |  | N | NO | <D> **** Detailed Description **** I&C was estimnated to recieve 230 mrem for August, actual dose recieved was 262 mrem. The overage of 32 mrem for the month was due to work moving from July to August during the backlog reduction week. FDR-SUMP-W2 was origianlly scheduled for 7/31/18 and moved to 8/1 and 8/2 resulting in an increase of 40 mrem being moved into August. <I> **** Actions Taken **** Wrote CR | 02-00-FDR-SUMP-W2
384305 | CR | 20180906 |  | 4 | Manway Cover Damage | N | N |  | N | NO | <D> **** Detailed Description **** There is damage to the square manway cover located outside building 88 north side (see pictures in the EDMS file). It appears something very heavy drove over the cover which caused it to cave in. This cover does not have an EPN or any indication it supports essential systems. <I> **** Actions Taken **** Discussed with the Maintenance Manager. Requested WPS place a road cone over the cover. Initiated a work request. Initial Engineering review: With 100% certainty, this is not a safety-related manhole (reference AED ELC E823-1). Additional Information: This bent cover damage was previously identified via AR CR 273174 / WR 29101224 and AR CR 331775 / WR 29122233 but WR 29101224 appears to have been cancelled to WR 29122233 which was advanced to complete without completing repair (referencing 'Telecom and Communications Group Change Gear Ticket 7554'). This appears to be the telecommunications manhole in the PA yard area roadway just northeast of Building 88 depicted on AED ELC E833 at N11525.42 / W1051.58.
384311 | CR | 20180906 |  | 3 | AED IMDS ROA-TS-2 requires revision |  |  |  | N | NO | <D> **** Detailed Description **** This CR does not affect the proper function of in service plant equipment. The instrument master data sheet for ROA-TS-2 (AED IMDS ROA-TS-2) requires revision to reflect actual component operation. Temperature switch ROA-TS-2 opens when the discharge air temperature of the associated Reactor Building HVAC Unit drops below switch setpoint triggering an RX BLDG INLET AIR TEMP LOW alarm only on annunciator ANN-ANN-R/R2 at E-CP-H13/P812 (Board R in the Main Control Room). The subject IMDS does not reflect this non control function with discrepancies found on the following IMDS information reference fields: Equipment Service field, Output To field, setpoint basis document references, and referenced EWD drawing (correct drawing is EWD-80E-014). . This is a configuration issue only. Historical calibration records for ROA-TS-2 show that the existing switch to be properly calibrated to the ~45 deg F decreasing alarm setpoint. Recommend assign to Engineering to correct the subject ROA-TS-2 IMDS reference information fields to reflect actual component function. <I> **** Actions Taken **** discussed with system engineer, design engineering, and performed drawing/wo review to confirm document only error.
384315 | CR | 20180906 |  | 4 | Demin trailer door needs to be removed | N | N |  | N | YES | <D> **** Detailed Description **** The rear loading door to the demin trailer is falling off the hinges and is currently held on by a strap. The vendor who owns this trailer cannot repair it timely. The inability to use the rear door is inhibiting the servicing of the trailer. As an interim solution, the door needs to be removed and plastic sheeting be put in place so that the trailer can be accessed and serviced. <I> **** Actions Taken **** Called and left message with facilities for help removing the door. This work can be performed by facilities. <N> **** Equipment Description **** Demin trailer outside of the floculator bldg.
384321 | CR | 20180906 |  | 3 | RFW-VMP-1 Rack A appears to not be working properly | N | N |  | N | YES | <D> **** Detailed Description **** It was reported by Electricians that RFW-VMP-1 Rack A is not working properly. During an engineering walk down it was confirmed that several cards are showing zero as a value with no indication lights on. The only cards showing values, with no indication lights on, are turbine and pump thrust cards (approximately 10 and 5 mils, respectively). The power supply is showing three green indication lights on. It was observed that the indication lights at the cards flash approximately every 10 seconds. All other RFW parameters are normal at this time. Recommendation: Have knowledgeable I & C technicians in Bently Nevada 7200 systems troubleshoot and diagnose the issue. <I> **** Actions Taken **** Vibration Engineer performed walkdown of RFW-VMP-1 Rack A and recorded observations in spreadsheet uploaded to EDMS. Discussed the need for I&C tech resources with I&C FIN Supervisor and I&C Shop Manager. Discussed issue with System Engineer. Notified Main Control Room. | 02-00-RFW-VMP-1
384322 | CR | 20180906 | CAQ | C | Design margin not accurate depicted in FSAR | Y | N |  | N | NO | <D> **** Detailed Description **** FSAR Section 6.1.2 states that â€œ4000 sqft of Dimetcote 6 coating does not meet ANSI N101.4 requirements because of damage, but that this damage will not result in the failure of the coating to adhere to its substrate. Regardless, the design of the ECCS strainers assumes the complete failure of the coating system.â€ This is not a correct statement as the amount of Dimetcote 6 coating, in pounds, used in the vendor sizing analysis for the ECCS strainers, was based on wet density instead of dry density. When dry density is used, the amount of Dimetcote 6 increases from 156 lbs to 300 lbs. This indicates that the design of the strainers was based on ~2000 sq ft (156 lbs), not 4000 sq ft (300 lbs) of coating. This is not an operability issue, as the FSAR states that no failure to adhere to the substrate occurs, and as such none of the coating will reach the strainers. The assumption in the sizing analysis that complete failure occurs is a conservatism utilized to maximize the size of the strainers, so as to provide extra margin in strainer size. As such, this is an issue with the FSAR not accurately depicting the design margin embedded in the strainers, and is not an issue with the operability of the strainers. <I> **** Actions Taken **** Reviewed analysis and design basis for design.
384325 | CR | 20180906 |  | 4 | E-CB-3/31 CLOSED light socket is broken | N | N |  | N | YES | <D> **** Detailed Description **** E-CB-3/31 CLOSED light socket is broken. See attached EDMS doc for pic of backside of lightsocket. There was no bulb located in the light socket, upon investigation. Typically, these sockets take 24E bulbs. Alternate means of breaker position verification are available. <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** TG 471W | 02-00-E-CB-3/31
384326 | CR | 20180906 | CAQ | C | [NRC] LCS Table 1.10.6-1 Observation |  |  |  | N | NO | <D> **** Detailed Description **** The NRC Residents noted that the HPCS Pump room R11 is not listed in table 1.10.6-1 (Area and Equipment Protected by Essential Fire Detection).
384328 | CR | 20180906 |  | 3 | (Engineering/OPs) SOP-ELEC-115KV-OPS needs revision |  |  |  | N | NO | <D> **** Detailed Description **** SOP-ELEC-115KV-OPS needs revision, steps 7.1.5 and 7.2.15 are to generic. Steps should be nore detailed and not have an if statement. Steps should have ensure or place selector switch is a position. Need steps to meet plant configuration control and allow touch read read. This will also be required for the E-TR-S proceedure. Assignments should be to Engineering to determine how to remove from service and OPs to rev procedure. TR-B change is needed for TRB work in Oct.
384329 | CR | 20180906 |  | 3 | Procedure ehancement for PPM 8.4.63 |  |  |  | N | NO | <D> **** Detailed Description **** PPM 8.4.63 needs an enhancement to change step 8.4.7 to just record calculated HX margin as opposed to delineating between licensing and T.S. margin. For DCW-HX-1C, the Licensing and T.S. margins would only be calculated if the Design margin was LE 0%. <I> **** Actions Taken **** discussed with supervisor
384331 | CR | 20180906 |  | 3 | eDNA bearing/winding temperature 2 hr drift | N | N |  | N | YES | <D> **** Detailed Description **** During monitoring and trending it was discovered that on the morning of 9/4/18 all motor bearing, windings, and turbine bearing temperatures that were reviewed decreased 5-6 degF during a two hour window and remained at this new lower temperature. Items reviewed are cooled by TSW or SW and some items reviewed were pumps not in-service that experienced the temperature decrease. Concluding this is not a plant system or component issue but rather an issue with the monitoring data or computer. This CR is for information to those using edna for component/system status. <I> **** Actions Taken **** Some computer point examples: F, W136, W131, F030 DATE: 9/4/18 ~0400-0700 . No edna manipulations were made on this morning that would correlate to the signal changes. . This is a trending and monitoring issue and not any plant component functionality concern. Recommend this be reviewed by computer engineering. <N> **** Equipment Description **** Possible plant computer or edna issue
384333 | CR | 20180906 |  | 4 | EDR-TK-4A released to CST with high TOC | N | N |  | N | NO | <D> **** Detailed Description **** EDR-TK-4A was authorized to be released to the CST with high TOC. The limit for TOC is 200 ppb. TOC result was 228 ppb and 217 ppb on resample. All other analysis were within specification. The tank was released due to a shortage of storage space in radwaste. <I> **** Actions Taken **** Authorized release to CST with RWCR operator.
384334 | CR | 20180906 |  | 3 | Daily Dose Report Not Accurate |  |  |  | N | NO | <D> **** ANONYMOUS CR - Detailed Description **** There have been many instances over the years where inaccurate daily dose reports have been sent out by broadcast email. These reports are used daily by all departments and in official daily meetings, and are also used for department D15â€™s. Submitting these dose reports for daily official use should be done with the same high standards for error checking that is required of all other daily company information and reports. There have been way too many instances over the years of incorrect daily dose reports being issued with no prior review for errors. See attached one from 8/27/2018. <I> **** Actions Taken **** This ANONYMOUS CR was generated using the paper process on FORM 26276. <N> CR Moved from ANON to CR-SRO for review.
384337 | CR | 20180906 |  | 4 | Crack in liner found during inspection at sanitary waste TF | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** When performing a liner inspection on the south stabilization pond at the sanitary waste treatment facility a crack in the liner was found. To inspect the 20 mil PVC liner, test holes are dug at random locations. One test hole was located at a suspect area where a slight sink hole had been observed during the drying season. We extended the hole about 3 feet long but crack continued and liner was brittle. Images in EDMS show an edge of the sink hole and the crack in the liner. This location was covered by approximately 20 inches of wet sand. The full liner inspection report is pending and more test holes will be dug to determine extent of liner condition (36 yrs old). Recommend investigating a means to seal pond liner faults and other considerations to extend SWTF useful life. <I> **** Actions Taken **** Patched and refilled the hole. The pond has been isolated and out of service since 4/25/18 in preparation for inspection and will remain out of service to address this issue. Discussed with chemistry supervisor, E&RP and F&CE engineer. <N> **** Equipment Description **** SWTF pond liner
384338 | CR | 20180906 | CAQ | B | Station Personnel Failed to Implement Compensatory Measure | Y | Y |  | N | NO | <C> This is a CR Bring Back for Security to obtain additional information for appropriate disposition. Risk: Medium (A condition that could lead to a Green finding using criteria found in the NRC Significance Determination Process) Cause Uncertainty: Partial Dispostion: B - Nucsec Recommend Investigation template. <D> **** Detailed Description **** On 9-6-18 at approximately 1300 hrs, the NRC Resident Inspector asked the Shift Manager how Fire Tours were being applied to all rooms on the reactor 441â€™ elevation and the 441 truck bay as a requirement to meet Fire Protection System Impairment (FPSI) 17-0367, License Controlled Specification (LCS) 1.10.6. Essential Fire Detection, and the associated compensatory measures for an hourly fire tour of fire detection zone 13 including all locations prescribed in LCS Table 1.10.6-1. . Review of FPSI 17-0367 indicates the system was removed from service on 9-04-18 at 07:26. This requires the station to process a fire protection system impairment immediately, which was completed, AND establish an hourly fire tour per LCS 1.10.6. which was correctly established. Review of Fire Tour Log performed by security 9-5-18 indicates the appropriate compensatory measures were implemented per the LCS. All signatures for the associated required hourly fire tours are in order and no discrepancies with documentation on the fire tour log could be identified. . Upon subsequent interviews with operations, security, and fire protection personnel it was identified that required fire tours were not conducted specifically in the RHR-B room located in the Reactor Building 441â€™ elevation due to the area being posted as a high radiation area. Through interviews, and evaluation of Security Force Instruction (SFI) 26, there may have been a misinterpretation of personnel conducting the hourly fire tours in accordance with SFI 26 section 4.3.8.b as meeting the required hourly fire tour for the RHR-B room by approaching the door to verify no smoke was actively observed around the door. . This may have been a misinterpretation because 4.3.8.b provides guidance on how to appropriately apply compensatory measures when a passive fire protection feature (ex. fire area boundary) is out-of-service. FPSI 17-0367 removed fire detection zone 13 from service, an active fire protection feature. SFI 26 section 4.3.8.b is not applicable to active fire protection features, such as smoke detection, removed from service. . Station personnel failed to implement the appropriate hourly fire tour required by LCS 1.10.6 specifically for the RHR-B pump room due to the area being a locked high radiation area. . FPSI 17-0367 has now been closed upon completion of associated work. <I> **** Actions Taken **** Reviewed applicable documents, conducted investigation and interviewed appropriate personnel. <N> When referencing a high radiation area during writing the CR the first reference was correct, the RHR-B room on 9-6-18 was a high radiation area. The second reference in the CR was incorrect, on 9-6-18 the RHR-B room was NOT a locked high radiation area. Verification and notification by HP attached to EDMS folder of parent AR. RB 9-10-18 Risk: Medium Cause Uncertainty: Partial Known direct cause: SFI 26 4.3.8b is not applicable to active fire protection features, such as smoke detection being removed from service. As such, station personnel failed to implelent the appropriate hourly fire tour specifically for the RHR-B pump room due to the area being a posted high-radation area. Assignment 04: has been reviewed and approved by parent owed to group manager and is being closed by CIC. Actions have been reviewed owed to group manager and has approved closure of parent AR as all actions have been completed.
384339 | CR | 20180906 |  | 3 | (QA) RCIC unavailable work not bundled |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Work order (WO) 02101569 ESP-RCIC-X301 RCIC TURBINE SPEED MONITOR â€“ CC is scheduled with no other work that makes RCIC unavailable. This work order is scheduled in the 9/10/18 week and four weeks after a large RCIC system outage window. Plant risk with RCIC unavailable is elevated and in a yellow condition. Refer to EDMS for additional details. <I> **** Actions Taken **** Discussed with the Work Week Manager & Work Control Manager. Initiated this CR.
384340 | CR | 20180906 |  | 4 | (QA) ESP-RCIC-X301 adds unnecessary unavailable hours |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) ESP-RCIC-X301 adds unnecessary unavailable hours due to hanging and lifting a clearance order. Prerequisite step 3.1 states to tag out the RCIC turbine. Preventing the RCIC turbine from operating does not require a tagout. Simply closing RCIC-V-1 with a procedure step prevents turbine operation and is performed in multiple operations procedures. Hanging, signing on & off and lifting the clearance order adds approximately two hours of unavailable time to this surveillance. Plant risk with RCIC unavailable is elevated and in a yellow condition. This issue is considered a Deficiency identified during Quality SR-18-03 Continuous Monitoring Roll-Up Surveillance. <I> **** Actions Taken **** Initiated this CR to revise the procedure. <N> ***General Notes*** An assignment has been created within the Maint. procedure revision data base. a link to the Maint. procedure revision data base has been added to the EDMS of this AR. No further actions are required.
384342 | CR | 20180906 |  | 3 | Operations Clearance Second Check PI is yellow R24 |  |  |  | N | NO | <D> **** Detailed Description **** This CR is to document that the R24 PI for clearance order second checks as of 9/1/18. Actions from this CR should be to develop and document recovery plan within 1 week. Assign to AR-OPSWM. <I> **** Actions Taken **** Initiated CR. Commenced actions for a recovery plan.
384343 | CR | 20180906 |  | 3 | HCU Mock up need refurbished |  |  |  | N | NO | <D> **** Detailed Description **** TREQ 18-0089 was created by an NLO to evaluate the funding available to update the HCU Mock-up in building 12 (rattlesnake). This would reduce the need to provide training on the 522' rx bldg and significanly reduce dose for Operations and possible Maintenance. recommend assignment to operations training to evaluate. <I> **** Actions Taken **** wrote this action.
384344 | CR | 20180906 |  | 3 | Evaluate SOP-COND-OPS for improved methods |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate SOP-COND-OPS for the method in which the low lube oil pressure trips are defeated on the condensate booster pumps. The current method determs wires on the lube oil pressure switches prior to shifting coolers. An alternate (lower risk) method would be to remove 2 fuses. Example: EWD-69E-011 â€“ Fuses F31-1 and F31-2 could be removed defeating all 3 low lube oil pressure trips and all 3 low suction pressure trips (adverse impact of this method) while the cooler is being swapped. Pulling fuses for the short period of time that the cooler is being swapped represents a lower risk compared to determing wires hot and the potential impacts of an error while determing. It also wouldnâ€™t require I&C resources to coordinate with Operations. <I> **** Actions Taken **** A walkdown of the fuses should be completed prior to making this change. This change is not required prior to the scheduled lube oil cooler swap on 9/22.
384345 | CR | 20180906 | CAQ | C | FLEX Equipment Found in Wrong Location | N | Y |  | N | YES | <C> This is a CR Bring Back for Engineering to obtain additional information for appropriate disposition. <D> **** Detailed Description **** While performing a walk down of Building 600 the FLEX Program Manager identified equipment that should have been returned to its assigned storage location in Building 82. SOP-FLEX-EQUIPMENT-STORAGE â€œFLEX Equipment Storageâ€ Storage Rack C, Shelf C1 FLEX-CONN-E/1A, 5-ft cable Duraline to TPC for E-GEN-DG4 (brown), FLEX-CONN-E/1B, 5-ft cable Duraline to TPC for E -GEN-DG4 (orange) and FLEX-CONN-E/1C, 5-ft cable Duraline to TPC for E-GEN-DG4 (yellow) were found on top of load bank. These components are only called out in procedures ABN-FSG-003 â€œDG4 CROSSTIE TO E-MC-7A AND E-MC-8Aâ€, ABN -FSG-004 â€œDG5 CROSSTIE TO E-MC-7A AND E-MC-8Aâ€, 1.5.18 â€œMANAGING B.5.B AND FLEX EQUIPMENT UNAVAILABILITYâ€ and SOP-FLEX-EQUIPMENT-STORAGE â€œFLEX Equipment Storageâ€. SOP-FLEX-EQUIPMENT-STORAGE states that these components should be stored on Storage Rack C, Shelf C1. AR-CR-384082 identified that E-GEN-DG4 had been run on 8/30/18 using the DG5 load bank. It cannot be readily determined what instructed the use of these cables and why they were not returned to the normal storage location. There have been seven Condition Reports written since 2015 on missing or misplaced FLEX equipment. <I> **** Actions Taken **** Notified Supervisor. Returned cables to their normal storage location. . Bridging actions: Bldgs 82 and 600 keylocks will be changed by EOS 9/12/18; keys will be provided to the MCR, TSC and FLEX Program Manager for postive building control until long term corrective actions are identified 9/21/18. Expectations for handling FLEX equipment was reinforced by PGM and Shift Manager at MSM 9/11/18 and via a D15 message to all station personnel on 9/12/18. <N> **** Equipment Description **** Building 600 | 02-CM-FLEX-CONN-E/1A,02-CM-FLEX-CONN-E/1B,02-CM-FLEX-CONN-E/1C
384346 | CR | 20180906 | CAQ | D | Spare Battery for FLEX Radios Needs Replaced | N | Y |  | N | YES | <D> **** Detailed Description **** A spare battery in the Radio Storage cabinet of Building 82 has failed. The battery charger is showing a blinking Red light for the associated battery. <I> **** Actions Taken **** Reviewed charger troubleshooting manual. Removed and reseated battery. Observed light on charger return to blinking Red condition. Notified Supervisor. <N> **** Equipment Description **** Building 82 Hose Trailer Room
384347 | CR | 20180906 |  | 4 | ASD 1B/2 coolant resistivity is low | N | N |  | N | YES | <D> **** Detailed Description **** While on operator rounds it was observed that GY-CI-10B2 was reading 4.329 MOHM's. The minimum coolant resistivity is greater than 5 MOHM's. <I> **** Actions Taken **** Wrote CR and informed CRS | 02-00-GY-CI-10B2
384348 | CR | 20180907 | CAQ | D | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 238 B: 240 C: 239 E-TR-B A: 118 B: 118 C: 118. sensors were J7, J11, and J15 are reset, Cause was Low Mo-ASHE about 14,9 miles away. single pole cycled off and on 3 times No damage equipment reported, No RAS initiated No emergent outage needed, No 230kv or 115kv involved. No line equipment outage needed, No Grid frequency change.
384352 | CR | 20180907 |  | 4 | R-5 Sump Fill Timer caused High Leakage Alarm for R-5 | N | N |  | N | YES | <D> **** Detailed Description **** At 0625 the MCR received "Leak Det Reactor Bldg Equip Sump Leakage High" alarm (H13-P601.A3.5-8). Investigation revealed the cause to be the R-5 Fill Timer (EDR-TM-603). The timer is set so that if the R-5 pump starts within 50 minutes of last having run, the alarm is received. Investigation revealed that the R-5 Fill Timer (EDR-TM-603) had not completed timing out and was indicating 40 minutes. This means the timer either mechanically stuck at 40 as it was timing down or the R-5 sump somehow filled up again within 10 minutes. Since no abnormal Drywell equipment leakage was indicated on EDR-FRS-623 over the previous several hours and that subsequently the timer did operate properly and time down to zero, it is likely the timer mechanically stuck at the 40 minutes mark. Recommend trending for re-occurrence. | 02-00-EDR-SUMP-R5,02-00-EDR-TM-603
384353 | CR | 20180907 |  | 4 | Ceiling tile out of place in Kootenai Rm 110 |  |  |  | N | NO | <D> **** Detailed Description **** A 2ft x 4ft ceiling tile is ajar in Kootenai Rm 110. The resulting gap is approximately one-half of the tile area. The tile still appears to be intact in the rafters. <I> **** Actions Taken **** Initiated W/R, notified Facilities at x8484. <N> **** Equipment Description **** Kootenai Rm 110 (Materials & Welding Metallurgical Lab) ceiling tile
384354 | CR | 20180907 |  | 4 | Control Room entered ABN-HVAC | N | N |  | N | YES | <D> **** Detailed Description **** At 11:50 the MCR entered ABN-HVAC due to MCR ambient temperature exceeding 78F. The likely primary culprit is WMA-TCV-12A and/or its control loop. Contributing cause is a weak WCH-CR-51B . Details: MCR temperature has been 75F or 76F the last 4 days. At 0748 we shifted to WMA-FN -51A thereby causing WMA-TCV-12A become the controlling throttle valve for MCR temperature. MCR temperature started to slowly increase. At 1150 temperature was noted to be 78.1F and ABN-HVAC was entered. At 1155 we shifted back to WMA-FN-51B (engaging WMA-TCV-12B) and temperature immediately dropped to about 77F and stabilized. WCH-CR -51B is presently maximized for cooling, according to Ops 2. | 02-00-WCH-CR-51B,02-00-WMA-TCV-12A
384355 | CR | 20180907 |  | 3 | SOP-PW-OPS Procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Lesson learned from crosstie potable water to Site 1 yesterday. Chlorine analyzer did not get seucred when PW -P-8 was secured. Recommend modify step 5.2.9 to read "Coordinate with Chemistry to secure the Chlorine Analyzer and CLOSE PWC-V-503 (Chlorine Analyzer line isolation) to isolate the back pressure regulating valves." <I> **** Actions Taken **** Discussed with Chem Tech and CRS.
384356 | CR | 20180908 |  | 4 | PWC-V-414 internal damage | N | N |  | N | YES | <D> **** Detailed Description **** PWC-V-414 has obtained internal damage during operation. It needs to be repaired/replaced as the current valve position cannot be verified. The handwheel now spins with low resistance in both directions. Its current position should be open but due to the stem/handwheel disconnect, position cannot be known for certain. <I> **** Actions Taken **** Informed CRS. | 02-00-PWC-V-414
384357 | CR | 20180908 |  | 4 | HSSF-CAB-CHEM/LAB alarm | N | N |  | N | YES | <D> **** Detailed Description **** At 01:10 9/8/18 recieved PC SYS STAT TROUBLE alarm on the HSSF-CAB-CHEM/LAB panel. Alarm description is PCP TROUBLE ALARM. . <I> **** Actions Taken **** Acknowledged alarm and contacted CRS and wrote this CR per direction in CI-14.4 | 02-00-HSSF-CAB-CHEM/LAB
384358 | CR | 20180908 | CAQ | D | MET-TE-10A reading high | N | Y |  | N | YES | <D> **** Detailed Description **** MET-TE-10A is reading 130.1F. Its counterpart on the B side is reading 71F, a more believable reading. <I> **** Actions Taken **** LCS is being referenced. WR written. <N> **** Equipment Description **** MET Tower | 02-00-MET-TE-10A
384361 | CR | 20180908 | CAQ | D | MET tower B signals failed. | N | Y |  | N | YES | <D> **** Detailed Description **** All MET tower B signals have failed. They all started flat-lining shortly after midnight on September 8, 2018. <I> **** Actions Taken **** Informed CRS/SM, wrote this CR and WR. | 02-00-MET-TE-10B
384362 | CR | 20180908 |  | 4 | WCH-PCV-50 is failed open | N | N |  | N | YES | <D> **** Detailed Description **** ON 9/2/18, a clearance was hung for WCH-CR-51A replacement. This clearance included the CAS valve which supplies air to the 51A control panel. Unfortunately, this also removed air from WCH-DPIC-50, which is the controller for WCH chilled water header pressure. This DPIC controls WCH -PCV-50, which, when open, bypasses WCH chilled water pump discharge back to the suction of the pump. Without air, this valve fails open. As a result, much or most of the chilled water is not flowing to the cooling coils. The clearance needs to be modified to isolate air only to the 51A controller, leaving WCH-DPIC-50 still with air, or one of the manual valves in the bypass line can be throttled (this would be WCH-V-703 or -704). Reference CR 384354, which was written for MCR high temperature. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 507 | 02-00-WCH-PCV-50
384363 | CR | 20180908 | CAQ | C | RHR-V-155A has leak by on seat. | Y | N |  | N | YES | <C> At the request of the Engineering Supervisor, this CR has been reopened and assigned to SENSSS for resolution. CR reopened to cross reference additional WO 02129443, marked completion required box, then taken back to complete <D> **** Detailed Description **** While performing WO 02123775 task 17, the portion to flush from RHR-V-155A was not able to be completed due to the pre-staged hose having a pressure lock on the quick disconnect due to RHR-V-155A seat leakage. Multiple attempts were made to relieve pressure from the hose to connect it to the hose going down to the RHR flush manifold. Due to time constraints other efforts to relieve pressure were not performed such as removing hose from camloc connection at RHR-V-155A. This would be a reasonable approach moving forward when more time is available to complete the task. Procedure steps not performed were N/Aâ€™d in the work instructions. Shift manager / CRS concur with changes. <I> **** Actions Taken **** Informed CRS/SSS and backed out of procedure. | 02-00-RHR-V-155A
384364 | CR | 20180908 |  | 4 | SA-C-1 Sump pressure high | N | N |  | N | YES | <D> **** Detailed Description **** SA-C-1 sump pressure was 137 PSIG on rounds. Please investigate. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 467 | 02-00-SA-C-1
384365 | CR | 20180908 |  | 4 | SA-DPI-4 indicating 22 PSID | N | N |  | N | YES | <D> **** Detailed Description **** SA-DPI-4 indicates 22 PSID on rounds. Please investigate and replace filter if necessary. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 467, SA-C-1 | 02-00-SA-DPI-4
384366 | CR | 20180908 | CAQ | D | Valve 37 on IR P027 has a small leak | Y | N |  | N | YES | <D> **** Detailed Description **** Valve 37 on P027 has a small leak. A drop of water was seen at this valve, and some rust on floor, but could not quantize drip rate. This valve serves MS-LIS-38B. Please repair. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RB 522 @ P027. | 02-00-E-IR-P027,02-00-MS-LIS-37B
384367 | CR | 20180908 |  | 4 | FDR-DPIS-39 red needle knob disconnected | N | N |  | N | YES | <D> **** Detailed Description **** The red needle became disconnected internally on FDR-DPIS -39 while starting FDR-TK-6 water transfer. The knob will turn but the red needle remains at a higher setting of 47 psid than the desired normal setting of 30 psid. The needle is adjusted in accordance with SOP-RW/FDR-OPS, Step 5.1.10 and 5.1.14d. Red needle mechanism needs repaired. <I> **** Actions Taken **** wrote AR / WR | 02-00-FDR-DPIS-39
384368 | CR | 20180908 |  | 3 | Work Order Task References Superseded Document |  |  |  | N | NO | <D> **** Detailed Description **** WO# 0212397103, Night Order Audit, instructions state to perform an audit of all night orders per OI-71. OI-71 is a superseded document with no replacement document. This is a periodic work order. <I> **** Actions Taken **** Initiated this CR to request a change to the model work order. Performing night order audit via work order instructions to review relevance of active night orders.
384369 | CR | 20180908 | CAQ | D | FDR-V-607 lost indication in MCR | N | Y |  | N | YES | <D> **** Detailed Description **** While stroking FDR-V-607 per WO# 02098330, FDR-V-607 lost indication. The close stroking was satisfactory, but when opening, the green light extinguished but the red light failed to illuminate. Reference WR# 29141545 and WO# 02126426 for action to restore open indication. <I> **** Actions Taken **** WR written <N> **** Equipment Description **** RB 422 | 02-00-FDR-V-607
384370 | CR | 20180908 |  | 3 | HSSF-TK-1 has a low level preventing proper operation of HWC | N | N |  | N | NO | <D> HSSF-TK-1 has a low liquid hydrogen level. As of 2100/9-8 -18, parameters are: tank level 20" H2, tank pressure 58psig, tubes are at 600psig, and the backup trailer is at 2500psig. The system attempts to run both A and B pumps and they trip on "LOPD Shutdown" which means loss of prime. The tank at this low level does not supply enough suction head to the pumps to keep the casing temperature below the -250 Â°F setpoint of the cavitation TIC. We need to contact the vendor and ensure they keep our tank full(er). Shortly, we will be using the much more expensive gaseous H2 in the backup trailer. Current status is the local alarm reset button(s) have been pressed, but not the start button because it would only attempt to restart and give the same alarm <I> Wrote this CR and notified the Main Control Room | 02-00-HSSF-TK-1
384371 | CR | 20180908 |  | 3 | Recommended change to PPM 3.2.1 |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.6.2 of revision 88-01 refers to steps 5.3.15 through 5.3.26. This step was added in revision 65 but the corresponding step numbers are now 5.3.11 through 5.3.21. <I> **** Actions Taken **** None.
384372 | CR | 20180909 |  | 4 | HSSF-CAB-CHEM/LAB alarm recieved | N | N |  | N | YES | <D> **** Detailed Description **** At 00:28 9/9/2018 recieved HS PAL124-PRES STAT LOW alarm. Alarm message is HYDROGEN TUBE PRESSURE LOW. <I> **** Actions Taken **** Contacted CRS and wrote this CR and WR per direction in CI-14.4. | 02-00-HSSF-CAB-CHEM/LAB
384373 | CR | 20180909 |  | 4 | offgas recombiner heater not working | N | N |  | N | YES | <D> **** Detailed Description **** OG-TC-2B is reading 292 degrees and continues to drop. The setpoint is 350 degrees. Fault has also caused the â€œRECOMBINER A/B LOW TEMPERATUREâ€ alarm at H-13-672.A9 drop 3-2 to lock in due to temperature under 330 degrees. OG -RC-5B is not currently in service for offgas flow | 02-00-OG-TC-2B
384374 | CR | 20180909 |  | 3 | BRE 36 Dedicated Camera | N | N |  | N | NO | <D> **** Detailed Description **** BRE 36 Dedicated Camera Needs Maintenance <I> **** Actions Taken **** Security Supervision Notifiied, CR/WR Initiated, Detailed Information communicated to Security Equipment Coordinators <N> **** Equipment Description **** BRE 36
384375 | CR | 20180909 | CAQ | D | SFS-STORM-025 Status Yellow | Y | N |  | N | YES | <D> **** Detailed Description **** SFS-STORM-025 (Cask 25) Cask Status is yellow as indicated on SFS-CP-ISFSI/TMS at step 7.1.1 of OSP-SFS-D101. The new ISFSI temperature monitoring system has not been turned over to Operations yet - CR initiated to document equipment status. <I> **** Actions Taken **** Submitted CR and WR. Notified the CRS and SM. | 02-00-SFS-STORM-025
384376 | CR | 20180909 |  | 3 | No Offgas Refrigeration machines operating per design. | N | N |  | N | YES | <D> **** Detailed Description **** No Offgas Refrigeration machines operating per design. OG-RF-20A is running. OG-RF-20B will not run as it frequently cycles Off. Reference WR 29141410 and CR 377420. OG-RF-20C is INOP and Caution Tagged in STOP. The Glycol Pump Suction Temperature High, H13-P672.A9,1-10, alarm is locked in. The Glycol Pump Suction Temperature as denoted on OG-TRS-630 is 39Â°F. No Offgas Dryer regeneration is in progress. <I> **** Actions Taken **** There are many Offgas System problems this cycle and little progress in resolution. Please assign available resources to rectify the various deficiencies. | 02-00-OG-RF-20A,02-00-OG-RF-20B,02-00-OG-RF-20C
384377 | CR | 20180909 |  | 4 | PWC-P-7 discharge line seperated from discharge piping. | N | N |  | N | YES | <D> **** Detailed Description **** The plastic/nylon discharge line from PWC-P-7 has seperated from the PVC discharge piping at the fitting. PWC-P-7 supplies Sodium Hypochlorite to the site potable water. system when the flocculatoor is processing water. PWC-P-7 is out of service until repairs can be made. PWC -P-8 remains in service to maintain Potable Water Free Residual Chlorine( FRC) at 1.3 ppm. FRC is currently 1.25 ppm and the flocculator is running. <I> **** Actions Taken **** Un plugged PWC-P-7 to prevent Sodium Hypochlorite from discharging into the bermed area. Closed PWC-V-370 (PWC-P-7 Discharge) to prevent any backflow from discharge line. Informed CRS and initiated CR and WR. | 02-00-PWC-P-7
384378 | CR | 20180910 |  | 4 | Security Camera Cleaning | N | N |  | N | NO | <D> **** Detailed Description **** CCTV9, 10, 11, 12, 13 and PTZ 28 <I> **** Actions Taken **** Notified Security Maintenance Supervisors and generated CR/WR <N> **** Equipment Description **** Security CCTV Cameras around the perimeter.
384382 | CR | 20180910 |  | 3 | Procedure enhancement to SOP-MT-AOP/TEST |  |  |  | N | YES | <D> **** Detailed Description **** In response to the 2 year procedure review. The wording of several steps in SOP-MT-AOP/TEST need to be fixed. In every case the step is not clear as to if the step requests the performer document the time period of which the pump ran at full pressure or the time at which it reached full pressure. 6 locations in the procedure need to be fixed. See the EDMS file attached. <N> **** Equipment Description **** Procedure change.
384383 | CR | 20180910 |  | 4 | Misc Drains 55 gal drum filling one each shift | N | N |  | N | NO | <D> **** Detailed Description **** The miscellaneous Turbine Lube Oil drain 55 gallon drum located TG441 west side, near the Condensate system normal makeup valves, is filling up once every shift. The 55 gallon drums for the sloop-oil drains are shown on M516. The one near the Cond make-up valves is filling up more rapidly than normal and Laborers are having to change it out with an empty barrel each shift. <N> **** Equipment Description **** Misc Drains 55 gal drum filling one each shift | 02-00-MS-DT-1A,02-00-MS-DT-1B,02-00-MS-DT-1C,02-00-T-BLDG-MISC
384386 | CR | 20180910 |  | 3 | E-TR-M2 in and out of alarm for CO and CO2 on Kellman | N | N |  | N | YES | <D> **** Detailed Description **** The purpose of this CR is to document the needed change to the alarms for the CO and CO2 limits for E-TR-M2 being seen by its online gas analyzer. Currently the settings for the Kellman are conservative for E-TR-M3 for CO and CO2. All of the alarms will still be set within the IEEE C57.104 condition 2 limits. The purpose of this CR is to document the need to change the setting for the Kellman for CO and CO2 limits. This condition has no impact on operation of the transformer and this CR is to just document the need to make changes to the Kellman settings for CO and CO2 alarms. | 02-00-E-TR-M2
384387 | CR | 20180910 |  | 3 | Hydrogen vendor having delivery difficulties | N | N |  | N | NO | <D> **** Detailed Description **** The hydrogen delivery vendor for the HSSF facility is having difficulty finding and scheduling delivery drivers to service our area. Currently, the HSSF facility inventory is near low level trip in the storage tank. The vendor confirmed a delivery today at 12:00. However, it will be a 1/2 tanker delivery. They are working on an additional delivery but have not found a driver at this time. <I> **** Actions Taken **** Notified contracts of this vendor performance deficiency.
384389 | CR | 20180910 |  | 3 | SWP-TQS-01 Instruction Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** SWP-TQS-01, Training, Qualification and Simulators, Sections 3.10 and 3.11 need instructional enhancement that will clarify qualifications for supplemental craft personnel. A management observation conducted on 9/5/18 challenged why the Ironworkers working on the Hardened Containment Vent platform installation do not have the same qualifications as a Site Support Contractor (SSC) Ironworker (SSCF). These craft are performing Ironworker trained / skilled construction activities for Construction Project Management (CPM) and are from the same Building Trade Union Hall so why would the qualification be different? According to project oversight the Ironworkers were qualified using SWP-TQS-01, Section 3.11 (Acceptable). Suggested procedure enhancements to consider have been uploaded into the EDMS file. Insight: A potential contributing factor to this challenge is at one time nearly all of the CPM project work was assigned to the SSC, however since Energy Northwest now requires the bidding of nearly all construction / modification type work, there are times when a project will be awarded to another company and they will hire building trade craft to perform the same work as the SSC would perform. When this change was implemented a revision to this procedure was not performed that would provide clearer guidance for the end users. Facts: â€¢ SWP-TQS-01 Section 3.10 is titled Qualifications Specific to Site Support Contractor Supplemental Maintenance Workers. o Sub-Section 3.10.1 states; this section apples to those individuals who are working for the designated Site Support Contractor (SSC). â€¢ SWP-TQS-01, Section 3.11 is titled Qualification Specific to Non-Site Support Contractor Supplemental Workers. o Sub-Section 3.11.1 states; this section applies to those contractors who are not working for the designated Site Support Contractor (SSC). â€¢ Craft that work for the SSC and CPM typically are form the same Building Trade Union Halls (Pipefitter, Electrician etc.). â€¢ Both SSC and CPM conduct construction type activities. <I> **** Actions Taken **** Verified all craft Ironworkers and Sheeet Metal Worker were qualified in accordance with SWP-TQS-01. Discussed condition with the Maintenance Manager and Reactor and Major Maintenance Manager.
384391 | CR | 20180910 |  | 3 | Main Condenser Waterbox coating | N | N |  | N | YES | <D> **** Detailed Description **** Coating of the Condenser Waterboxes was never completed after the condenser was installed in R20. Large chunks of the coating materials are being dislodged from the waterboxes and into the CW system. Engineering evaluation needed to determine wear rates and wear patterns, minimum wall limits and estimate time to minimum wall thickness, if waterbox coating and repairs are necessary, and develop a path forward to re-coat the waterboxes to include a project timeline, budget, and documentation required to present to PRC for approval. <N> **** Equipment Description **** T471 D3/13.0 | 02-00-COND-HX-9
384395 | CR | 20180910 |  | 3 | Categorization of AR 384257 - Typo on FSAR pg. 3.2-24 |  |  |  | N | NO | <D> **** Detailed Description **** This is an administrative issue only and does not affect any SSCs. AR 384257 identified a typo in FSAR table 3.2-1. The typo is on the word â€œhangarâ€. This word should be spelled â€œhangerâ€ with an â€œeâ€. This AR was given a CAQ by CRG which does not meet the definition of Condition Adverse to Quality in SWP-CAP-06 nor do any of the examples discuss a typo as CAQ. Realize the examples are not all inclusive, however, in reading the CAQ definition, this CR does not meet the CAQ criteria. This typo does not change the meaning of a â€œhangerâ€ in the FSAR regardless of the spelling nor does it affect any of the items listed in the CAQ definition. Seems like regardless of what the issue is, if it affects any design basis document, it automatically becomes a CAQ. Because this AR was assigned a CAQ CA to Design Engineering, it will now take priority over other more important non-CAQ work that should be done instead. Note: the resolution for this AR was an e-mail to Licensing to revise the identified typo in the next administrative LDCN for the FSAR. Another similar example is AR 383395 for separating a calculation into 4 different calculations as an enhancement. Nothing is wrong with the calculation. Recommend revising SWP-CAP-01 and SWP-CAP-06 CAQ Definition to exclude the following: typos that do not change the meaning of the word, recommendations, or enhancements to licensing basis documents for the CAQ definition. . See EDMS for backup information. Recommend assignment to AR-PERFIMP. <I> **** Actions Taken **** Discussed with Design Supervisor and engineering Design Authority.
384396 | CR | 20180910 |  | 3 | Private information found in records |  |  |  | N | NO | <D> **** Detailed Description **** Private information found in records that had not been previously identified as confidential. Technical Base Document 03-03 produced in 2003 contained confidential information. Specifically employee social security numbers. The record has had restricted retrieval ability since 1/2018 and will remain so. The information was identified during a TBD review and update. <I> **** Actions Taken **** RP supervision has been notified, records has been notified and placed DIC 1571 on the list of confidential records. It is recommended that HPI-0.13 RP TECHNICAL BASIS DOCUMENTS be revised to recommend that future TBD updates and new TBDs do not contain confidential information.
384399 | CR | 20180910 |  | 3 | Evaluate PA Patrol Vital Area Checks |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate PA Patrol Vital Area Checks. The recommendation was made during an observation to consider not scheduling vital area checks during the hour in which PA patrol rotates to another post. <I> **** Actions Taken **** Security Supervision Notified. CR generated to evaluate against 10 CFR 73.55 Requirements.
384400 | CR | 20180910 |  | 4 | Member missed scheduled meeting |  |  |  | N | NO | <D> **** Detailed Description **** Maintenance Mechanical shop craft member missed the scheduled PCSC Committee meeting on 9/10/2018. Neither the primary nor alternate member attended the meeting. <I> **** Actions Taken **** Shop called, no attendee reported. CR written. <N> ***General Notes*** All individuals involved in this event have been coached, no further action requred.
384401 | CR | 20180910 |  | 3 | Update Security's policy of after hours notifications |  |  |  | N | NO | <D> **** Detailed Description **** At ~0400 this morning, a WWM received a notification from Security that there was a fire alarm in a Fire Auxiliary Relay House. Security had already contacted Operations and they were sending an EO to silence the alarm and look for any issues. The officer was merely making a notification to the implementing WWM. They did not require any action from the WWM, just providing information as required by their procedure/checklist. This is not the first time that WWMs have been contacted for information only notifications where no action is needed from the WWM. I recommend that Security procedures/checklists be updated to have an e-mail notification be performed where no action from the WWM needs to take place. A follow up action, if necessary, could be to contact the WWM by phone during normal business/waking hours. <I> **** Actions Taken **** I discussed this issue with Security management. They recommended that I write this CR to drive a change to procedures/checklists as needed. This is a quality of life issue.
384405 | CR | 20180910 |  | 4 | AS-PI-1C requires benchtop rebuild | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of 02090667 01 a calibration of AS -PI-1C was attempted. It was found to be sticking and out of tolerance throughout the range. The sticking was remedied and the indicator was brought in tolerance at the top and bottom of scale but the mid scale values were out of tolerance. The CVI shows a linearity adjustment but it is not accessable while mounted in the control panel. The values are also not repeatable which indicates other potential problems. <I> **** Actions Taken **** Stopped, contacted supervision and system engineering where it was agreed that it should be put on the bench to determine the extent of repairs required to bring back into tolerance. A revision of the work order package will be required. It is a dual indicator so the other EPN would have to be included in the WO task. <N> **** Equipment Description **** T441 Aux Boiler Room | 02-00-AS-PI-1C
384406 | CR | 20180910 |  | 4 | E-AT-TR/M3 caution light is lit | N | N |  | N | YES | <D> **** Detailed Description **** E-AT-TR/M3 caution light is lit <I> **** Actions Taken **** cr | 02-00-E-AY-TR/M3
384407 | CR | 20180910 |  | 4 | E-AY-TR/M2 caution light was lit | N | N |  | N | YES | <D> **** Detailed Description **** E-AY-TR/M2 caution light was lit <I> **** Actions Taken **** cr | 02-00-E-AY-TR/M2
384410 | CR | 20180910 |  | 4 | PO 352041 Vendor Claims they Shipped but we never received |  |  |  | N | NO | <D> **** Detailed Description **** For PO 352041 vendor claims to have shipped us the materials/Gaskets. Signed for by "John". Warehouse shows no record of receiving the package and no one named John works in the warehouse. Vendor is Thermal Engineering. For trending only. Recommend Non CAQ 4 trend.
384411 | CR | 20180910 |  | 3 | Main turbine thrust bearing wear trip B signal spiking | N | N |  | N | YES | <D> **** Detailed Description **** On 7/16/2018 thrust bearing position from proximity sensor TG-DET-TP/B (eDNA T2 1209A) was noted to spike low to a value of -20 mil (normal thrust bearing position for this cycle has been ~7 mil). Since then, on 9/4/2018, there were two more occurrences of the signal spiking low to -16 and -18 mil. There were also three occurrences of the signal spiking high to -1 or 0 mil on 8/28, 8/31, and 9/4/2018. The signals from TG-DET-TP/A and TG-DET-TP/C did not show any anomalies. These signals are inputs to DEH for main turbine trip at 40 mil or -40 mil. Two of the proximity sensors would have to detect thrust bearing position exceeding setpoint concurrently for a turbine trip to occur (2 out of 3 trip logic). As only one of three is exhibiting spurious behavior there is no immediate threat to unit operation. Note the magnitude of the spikes may have been greater than those recorded in eDNA (but not detectable due to the low eDNA sampling rates) but at no time did they exceed the trip setpoint (if the trip setpoint were to have been spuriously exceeded, the DEH WARNING annunciator would have flashed). If the frequency of spiking increases or the DEH WARNING were to flash due to Thrust Bearing Low/High B Trip, consideration should be given to bypassing the Thrust Bearing B trip via DEH-MON-2/3 and effectively converting the trip logic to 2 out of 2. Recommend investigating the instrument loop (ref. IMDS and EWD-48-013) at the next opportunity (outage). <I> Discussed with CRS | 02-00-TG-DET-TP/B
384413 | CR | 20180910 |  | 4 | AS-MO-8 signs of packing leak and degraded grease | N | N |  | N | YES | <D> **** Detailed Description **** External PM identified AS-MO-8 had signs of a packing leak and degraded actuator / stem grease. - See attached pictures - WR is to refur actuator and replace the packing <I> **** Actions Taken **** The stem grease was replaced. The actuator grease grade was a 2 which requires a refurbishment in the near future. Generated WR to Refurb actuator and replace packing | 02-00-AS-MO-8
384414 | CR | 20180910 | CAQ | C | ARM-RIS-1 IMDS Needs Update |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02114906-03, it was discovered that the IMDS for ARM-RIS-1 incorrectly states that a Beacon Light should illuminate for Hi Alarm. <I> **** Actions Taken **** Discussed with Supervision and Engineering and confirmed that it is only Local Lamp, not Beacon that illumuniates. Wrote CR to document and to get IMDS revised.
384415 | CR | 20180910 |  | 4 | Broken screws on heat trace control knob cover | N | N |  | N | YES | <D> **** Detailed Description **** While performing WO 02092604-01 4 yr heat trace Calibrate and Adjust: The low temp alarm thermostat on FP/6 circuit 23 at the East circ water eye wash station, the screws holding the control knob Cover, broke while attempting to loosen them. Condition does not affect operability. <I> **** Actions Taken **** Taped cover into place for FME Notified supervision Initiated CR/WR <N> **** Equipment Description **** Circuit 23 is located on the east side of the circ water pump house on the eye wash station | 02-00-HT-HTP-FP/6
384416 | CR | 20180910 |  | 4 | Unidentified burried black cable |  |  |  | N | NO | <D> **** Detailed Description **** While digging a hole to install a new security camera tower under WO# 02128612-10, a coiled up unidentified black cable was discovered that was not shown in drawings prior to digging. An Electrical Engineer was called to look at the cable and an Electrician was called to come and verify that the cable was dead. The cable was found to be dead and did not pose any hazard to the workers. This did not allow the task to be completed this week due to vendor resources not being available. This will also change the scope of the work if cable removal is necessary. <I> **** Actions Taken **** Stopped work immediately and contacted the supervisor. Electrical Engineer was also contacted along with an Electrician to verify no power.
384417 | CR | 20180910 | CAQ | D | Auto scram timer system time incorrect | Y | N |  | N | YES | <D> **** Detailed Description **** The auto scram timer time is one hour later than actual time. <I> **** Actions Taken **** Searched for a procedure or work instructions on how to reset the system clock, nothing found. | 02-00-TDAS-SOFT-AST
384421 | CR | 20180911 |  | 4 | RCA Visitor Forms Submitted in Incorrect Format |  |  |  | N | NO | <D> **** Detailed Description **** On 9/10/2018, 16 of 17 RCA visitor forms (Form 25458) were submitted as PDF files instead of Microsoft Word files (as required by the form instructions). These forms were submitted to support a FEMA tour scheduled for 9/12/2018. The offsite personnel generated and submitted the files in PDF; therefore, the correct file types were unable to be obtained. This is being generated for documentation and trending purposes only. <I> **** Actions Taken **** Coordinating personnel were informed that files should be submitted in Microsoft Word format as required by step 10 of the instructions. When it became apparent that the correct file types could not be submitted, the PDF files were printed and signed for approval.
384427 | CR | 20180911 |  | 3 | Web Filter Authenication issue with Chrome Browser |  |  |  | N | NO | <D> **** Detailed Description **** The Google chrome browser is a dyanamically updating application, and after the latest updates to chrome, it is having issues with authentication with our WSA webfilters. This does not impact the plant directly, but has impacted a number of corporate services, where external sites require chrome to access their services. <I> **** Actions Taken **** Reviewed the Web filters and there are no updates or patches currently available. Open a TAC cas with Cisco. Also reviewing Web Filter replacement options we have already been evaluating.
384429 | CR | 20180911 |  | 4 | Potable water turbidimeter locall/recorder mismatch | N | N |  | N | YES | <D> **** Detailed Description **** The potable water inlet turbidimeter (PWC-TBIT-1) does not match the recorder reading on PWC-XR-1. Local is 0.398 NTU, recorder 0.014 NTU. Request I&C to check the settings. <I> **** Actions Taken **** Contacted FIN team | 02-00-PWC-TBIT-1,02-00-PWC-XR-1
384430 | CR | 20180911 | CAQ | D | CRD-FI-4A low out of spec | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-FI-4A low out of spec. Recommend adjust flow. <I> **** Actions Taken **** Informed MCR, generated AR/WR. | 02-00-CRD-FI-4A
384431 | CR | 20180911 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0068449 Shopmade ARM Power Supply found OOT & adjusted within specs. Not used during Calibration cycle. DEF #6733A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
384432 | CR | 20180911 |  | 4 | M&TE Suspended |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0053442 Teledyne Brown MOV Testing system- model FieldPro 5000 was not used during Calibration cycle and is now Suspended until needed. DEF #6734A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
384433 | CR | 20180911 |  | 4 | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calocode #0067933 Chatillon Force Gauge- model DFX2-010 was found OOT & Rejected- Unable to adjust or repair. Not used during Calibration cycle. DEF #6735A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
384434 | CR | 20180911 |  | 3 | PCR: DES-6-3 SQA document approvals |  |  |  | N | NO | <D> **** Detailed Description **** DES-6-3 specifies Design Engineering supervisor and Design Engineering Manager as required approvals for SQA documents. This conflicts with Computer Engineering and Reactor Fuels responsibility for many digital SSC's. Recommend changing DES-6-3 to specify responsible supervisor, rather than Design Engineering specifically. Also in alignment with the Supervisor Led Initiative, manager approval should be eliminated in favor of supervisor approval. <I> **** Actions Taken **** Discussed with Design Engineering Manager and procedure owner.
384438 | CR | 20180911 |  | 4 | SEC-HK-05 is not functioning as designed |  |  |  | N | YES | <D> **** Detailed Description **** SEC-HK-05 not functioning as designed, request maintenance to investigate, call 2185 for more information <I> **** Actions Taken **** Unit was removed from service; CR/WR Generated | 02-00-SEC-HK-5
384440 | CR | 20180911 |  | 4 | TSW-FIS-33C metal housing loose due to CW-P-1C vibration. | N | N |  | N | YES | <D> **** Detailed Description **** While doing Ops4 rounds a rattling noise was heard near CW-P-1C. Upon closer investigation it was noted that the metal support housing for TSW-FIS-33C lube water supply flow indicator switch is becoming loose at the base due to vibration from CW-P-1C. It appears that the size of the opening from the metal hammering together is increasing the size of the hole. See video attached. <I> **** Actions Taken **** SSS notified, CR written. . Although CW-P-1C is not a TS or Non-TS SSC, this is a serious issue that needs to be addressed. This topic was discussed at today's PHC. | 02-00-CW-P-1C,02-00-TSW-FIS-33C
384441 | CR | 20180911 | CAQ | D | MS-V-120B is continuously open. | N | N |  | N | YES | <D> **** Detailed Description **** MS-V-120B, which is the bypass valve for MS-T-1B, is continuously open with Hi Level indicated. One potential cause for this is failure of MS-LS-24B. <I> **** Actions Taken **** Informed CRS/SM, wrote this CR and WR. | 02-00-MS-LS-24B,02-00-MS-SPV-120B,02-00-MS-T-1B,02-00-MS-V-120B
384442 | CR | 20180911 |  | 3 | PRM-DPT-2 â€œEqualizerâ€ tag change |  |  |  | N | YES | <D> **** Detailed Description **** In PRM-CAB-2 on R-606â€™ the equalizer valve tag for PRM -DPT-2 does not read correctly per the work instructions in PPM 16.1.7. Step 7.1.3 instructs you to OPEN equalizer valve (16). The current Tag reads â€œINST BYPASS VALVEâ€. <I> **** Actions Taken **** Stopped and notified supervision. Initiated a CR and a WR to create a new label. <N> **** Equipment Description **** PRM-CAB-2/V16 "Inst Equalizer Valve" 16. RX606 ***General Notes*** A procedure change assignment has been added to the Maint procedure revision data base. a link to the data base has been added to the EDMS of this AR. No further actions required. | 02-00-PRM-CAB-2,02-00-PRM-DPT-2
384443 | CR | 20180911 | CAQ | D | NSSE-EQ-8E Refuel Bridge Main Hoist Motor Brake malfunction | Y | Y |  | N | YES | <D> **** Detailed Description **** NSSE-EQ-8E Refuel Bridge Main Hoist Motor Brake is malfunctioning and emitting a a scraping sound when the main hoist motor is operated. Indications are that the disc brakes are partially engaged and not totally in the reset position. This could be due to the RELEASE/RESET knob or linkage out of adjustment. <I> **** Actions Taken **** Left refuel bridge and mast in a safe condition. Informed EFIN/Elec and Rx Maintenance Supervisors. | 02-00-NSSE-EQ-8E
384444 | CR | 20180911 |  | 4 | Issued badge photos not appearing at the checkpoint |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** IT Analyst discovered the corporate badging table was not populating from the host computer to the Lenel and SSIS databases through the automatic transfer process. This caused several photos not to appear on the checkpoint readers. <I> **** Actions Taken **** Computer engineering is currently investigating the cause, contact Access Authorization for further information
384447 | CR | 20180911 |  |  | FP-V-607 is clogged. | N | N |  | N | YES | <C> Based on comments that the initator incorporated into CR 384455, this CR will be canceled at their request. <D> **** Detailed Description **** When hanging clearance D-FP-V-5-001 no flow was observed from FP-V-607. When work was commenced there was still system pressure on FP-V-5 such that water sprayed for about 10 minutes before tightening flange bolts. FP-V-607 was the only vent / drain used on the clearance. Please investigate and unclogged FP-V-607 and associated piping. <I> **** Actions Taken **** Informed shift manager and wrote this AR/WR. | 02-00-FP-V-607
384448 | CR | 20180911 |  | 3 | (QA) Sulfuric Acid Pump Area Caution Taped w/out Signs |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The area around the sulfuric acid pumps has stanchions and caution tape but no signs indicating what the hazard is which not in accordance with ISPM-18. Having barriers in place with no signs could delay work in the area and/or result in personnel injury if the area is entered without the proper PPE or compensatory actions. Refer to details in EDMS <I> **** Actions Taken **** Discussed with the Industrial Safety Program Manager & Chemistry Operations Supervisor. Initiated this CR.
384449 | CR | 20180911 | CAQ | D | B43 Fire Panel TROUBLE Signal | N | N |  | N | YES | <D> **** Detailed Description **** A fire alarm panel TROUBLE signal was transmitted at approx 0400 hrs on September 10. Security Communications Center (SCC) checked with Control Room. An operator was dispatched to look at the panel. No other report was made to Fire Protection Engineer. This is a long standing, repeat problem on a relatively new fire alarm panel. <N> **** Equipment Description **** B43 Fire Alarm Control Panel
384450 | CR | 20180911 |  | 4 | Monthly chemical storage area inspection discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** The following items were found and resolved during monthly inspections: Tube of expired Loctite 508 found in RV test shop FLSC# 13-0002, taken to W 437' for disposal. North lite of Bldg. 114 buned out, contacted facilities for replacement. <I> **** Actions Taken **** Notified appropriate personnel to resolve. All discrepancies resolved, no further action is required.
384451 | CR | 20180911 | CAQ | D | DG4 Coolant Leak, Rework required for mRule MPFF CA | N | Y |  | N | YES | <D> **** Detailed Description **** The DG4 generator has experienced a coolant leak at the heater connection as far back as 2010. The heater is installed with standard hose clamps which are not vender approved per the OMM manual. The coolant connections are under stress as they are high heat and pressure durring operation. The engine needs to be reworked to prevent another failure as we recently declared the engine inoperable due to a loss of 2-3 gallons of coolant. OMM 999-00, 194.1 has instructions for installation of constant torque clamps. They shall be double clamped. CID 36903 was made available in July 2017 as an option for repair but was not utilized. There are no current leaks, the engine recently passed the PMT and is expected to opperate if required. However as made obvious by the CR history the long term reliability is in question and rework shall be given priority. <I> **** Actions Taken **** Wrote CR, Contacted SM | 02-00-E-GEN-DG4
384454 | CR | 20180911 |  | 3 | EN maintenance person injured back. |  |  |  | N | NO | <D> **** Detailed Description **** An Energy Northwest Maintenance person injured his back while at work. After discussion with employee the injury was determined to be mild in nature. <I> **** Actions Taken **** Employee sent to Ocupational Health per the guildlines of ISPM-1. Industrial Safety was notified. Employees Manager and Maintenance Manager Notified. Shift Manager also notified. <N> WR #29146813 was written
384455 | CR | 20180911 | CAQ | D | FP-V-607 was found to have a solid pipe nipple. | N | N |  | N | YES | <D> **** Detailed Description **** While trying to depressurize FP-V-5 for replacement, FP-V -607 was found to have a solid core pipe nipple. This is in effect a pipe plug. M515-1 shows that this valve does not have a pipe cap or plug. However, CVI 215-00,841 shows that there should be a 3000# carbon steel pipe cap. M501 note 12 shows that where a threaded cap is used, quick disconnect style fittings (camlock, Chicago quick disconnect, etc) may be used on a one for one basis. This would make this pipe plug a conforming fitting, but it was misleading / confusing when it appeared to be a pipe nipple. Even if this fitting had been a pipe nipple, system pressure would not have been able to be depressurized due to leakage past FP-V-6A and FP-V-6B as evidenced by the amount of leakage from the FP-V-5 bonnet flange when the bolts were loosened. There was a Â½ gallon per minute flow from the flange with pressure on FP-PI-2 only dropping from 158 psig to 154 psig over a five minute period and then building right back to 158 psig when the flange was tightened to no leakage. Please investigate and build a plan to depressurize and replace FP-V-5. With this additional information, AR 384447 and WR 29144540 can be canceled. <I> **** Actions Taken **** Informed shift manager and CRS. Wrote this AR/CR/WR. <N> This AR/CR has two parts to it â€“ 1) a drawing discrepancy between flow diagram M515-1 and CVI 215-00,841 and 2) to investigate and plan to depressurize and replace FP-V-5. This write-up addresses Item 1) only. Item 1) M515-1 will be revised to add the pipe cap under AR 341749. No further actions are required under this AR/CR. | 02-00-FP-V-607,02-00-FP-V-6A,02-00-FP-V-6B
384456 | CR | 20180911 |  | 3 | Work orders did not have Walkdown Holds installed |  |  |  | N | NO | <D> **** Detailed Description **** Work orders continue to show up in Williams Plant Services schedules that have not been walked down by the Craft and Foreman. Current examples include work orders 02121315-10 and 02132549-09. If we do not have the ability to walk the task down we cannot add the correct resources, durations and identify material that may need to be ordered to perform the work. This also can cause a resources issue. In some cases, these tasks require us to hire additional resources to perform the work. Walk Down Holds (WD) need to be installed on all of the Williams Plant Services tasks. <I> **** Actions Taken **** Contacted Supervision.
384457 | CR | 20180911 | CAQ | D | E-B0-1A annual test | Y | Y |  | N | YES | <D> **** Detailed Description **** While performing the prerequisites for ESP-B01A-F101 the specific gravities were found to be not with in the acceptance criteria of 1.205 avg. The average was 1.2036 <I> **** Actions Taken **** Informed supervision, CRS, inistiated CR and WR <N> **** Equipment Description **** E-B0-1A battery room 1 | 02-00-E-B0-1A
384460 | CR | 20180911 |  | 3 | (QA)Housekeeping issues in Warehouse 75 during SNM Inventory |  |  |  | N | NO | <D> **** Detailed Description **** (QA) During the special nuclear material inventory of items in warehouse 75, the following housekeeping issues were identified: â€¢ A box containing LPRMs with an SNM label as required by PPM 9.2.1 also has a Radioactive Material Data Label which incorrectly notes that the box contains IRMs. This issue was previously identified in Quality audit AU-EN-1. â€¢ An SNM label visible on a box containing no SNM. Elsewhere on the box a label indicated that the box was empty. â€¢ A paper on the side of an LPRM box listing contents from 2010. â€¢ Some SNM labels were found on boxes with contact information for individuals who no longer work on site or work in different roles â€¢ A large amount of dirt/dust has also accumulated on the floor and on the boxes in warehouse 75. â€¢ Two RM Data Labels on the blue LPRM box that include the statement â€œAt one time this box had detectable contaminationâ€ dated 8-20-13. This comment is confusing to the worker and potentially contrary to the radiological information on the same label. Recommend resolution is to remove the labels with out of date and incorrect information and to create replacement labels as appropriate. It is also recommend to schedule cleaning of the SNM area prior to testing of these SNM detectors for installation during R24. <N> These issues were identified during Quality Continuous Monitoring activities. . The detailed description was modified to add the (QA) identifier to the first line.
384461 | CR | 20180911 |  | 4 | Noise on sound power phone to circulating water pump house | N | N |  | N | YES | <D> **** Detailed Description **** While preforming maintenance checks on the sound power phone system, the CWPH was found to have a noise on the line. CB-6001. This has degraded the communication but it is operable. <I> **** Actions Taken **** Notified EP. Recommend closing to IS Telecom WR for repair. <N> **** Equipment Description **** Sound power circuit to CWPH CB-6001 | 02-00-P-BLDG-MISC
384462 | CR | 20180911 |  | 3 | GT 5 CMRs against Civil Eng. Calculation 6.15.01-SII-6 |  |  |  | N | NO | <D> **** Detailed Description **** In accordance with the CMR policy detailed in Design Engineering Procedure DES-4-1, the intent of this CR is to document greater than 5 Modified status CMRs against Civil Engineering Calculation 6.15.01-SII-6 (Transformer Yard Structures Design). A revision to the subject calculation reflecting the outstandin CMRs is to be completed within 180 days. <I> **** Actions Taken **** CR written <N> Looking in Portal J at the outstanding ECs against this calculation, there is one CLOSED status CMR (EC CMR 10695 â€“ closed 07/16/18), five MODIFIED status CMRs, and one APPROVED status CMR (EC CMR 12533 for CLOSED status EC PDC 12243). It appears that EC PDC 12243 was cancelled 06/14/18 (and most likely so should EC CMR 12533 have been cancelled). It appears that AR CR 384462 can be addressed by removing CLOSED status EC CMR 10695 and by cancelling & removing APPROVED status EC CMR 12533 from the outstanding modifications list for AED CAL 6.15.01-SII-6. . Calculation 6.15.01-SII-6 has been revised to revision 1 and all the CMRs have been incorporated into this revision. No further actions required. This CR is now closed. .
384465 | CR | 20180911 | CAQ | D | Rod High Temperatures | Y | N |  | N | YES | <D> **** Detailed Description **** The NRC resident identified rod 30-31 in alarm at 288 F and rod 38-39 in alarm at 266 F on the CRD temperature recorder alarm panel, MS-TR-6. <I> **** Actions Taken **** Contacted the SM. <N> These rods are at or near center and tend to run warmer than 250 degF simple due to the physical layout of the reactor (i.e. reactor vessel bottom curvature means center CRDMs physically have more drive exposed to reactor temperature) and low insert stall flows (i.e. other drives steal their cooling water). As long as this is the cause (i.e. there is no leaking scram valve or loss of flow) there is no worry or impact with operating up to 350degF indefinitely. 250 degF could be the sign of a problem, or it may be the sign of just normal system operation. Seals are not affected by temperature and scram times are not effected below 350 degF. These rods have some history of running warm (200 to 260 degF), so I am not concerned. The industry just put out a position paper on this (see BWROG TP18-1-231). | 02-00-CRD-DRVE-3031,02-00-CRD-DRVE-3839,02-00-CRD-ROD-3031,02-00-CRD-ROD-3839
384466 | CR | 20180911 |  | 3 | Documenting measured AVG sediment in SW Pond from Divers | Y | Y |  | N | NO | <D> **** Detailed Description **** During Service Water Spray Pond A initial dive inspections prior to dredging the pond, sediment was measured in 40 x40 ft quadrants (48 total points) similar to the same area covered by the Sonar Boat used in spray pond sediment depth surveillances (OSP-SW-Q101). Prior to Spray Pond A cleaning, the average sediment measured across the whole Spray Pond A by the divers was ~1 2/3in with some areas measuring as much as 1 foot of sediment accumulation. The last surveillance (OSP-SW-Q101) using the Sonar Boat measured sediment at ~3 2/3in including uncertainties. This CR is being initiated to document the discrepancy between measured sediment from the divers and the Sonar boat and to evaluate potential enhancements to how sediment is measured in the spray ponds. Currently, the sediment measured by the sonar boat is more conservative in margin than what the divers in the spray pond have measured. <I> **** Actions Taken **** Discussed with supervisor and Shift Manager <N> Engineeringâ€™s position is that the purpose of this CR is to enhance the measurement methodology only and is not a Condition Adverse to Quality. | 02-00-A-BLDG-MISC,02-00-CGS-BLDG-MISC
384467 | CR | 20180911 |  | 3 | RWCU-DM-1B service air isolations are leaking by | N | N |  | N | YES | <D> **** Detailed Description **** Audible noise coming from the service air pipe associated with RWCU-DM-1B is an indication of isolation valve leak -by. There is condensation draining from SA-V-23, the service air filter drain valve. The service air pipe is warmer to the touch than it normally is. RWCU-V-213B (air-operated isolation) and RWCU-V-230B (manual isolation) on the service air piping to the demineralizer, were identified on 04/17/2013 as leaking by. The leak-by increased following RWCU-DM-1B removal from service for a backwash and precoat. See video of leak-by on EDMS screen; the audible noise can be heard in background. <I> **** Actions Taken **** informed Shift Supervisor | 02-00-RWCU-DM-1B,02-00-RWCU-V-213B,02-00-RWCU-V-230B,02-00-SA-V-23
384468 | CR | 20180912 | CAQ | D | RCIC-V-2 indicates closed while running. | Y | N |  | N | YES | <D> **** Detailed Description **** RCIC-V-2 indicates closed while running at 620 gpm. RCIC -FIC-600 output is at 98% and turbine speed is 4500 rpm. This has been written up many times and not fixed. <I> **** Actions Taken **** WR written <N> **** Equipment Description **** RB422 | 02-00-RCIC-V-2
384469 | CR | 20180912 |  | 3 | Procedure enhancements for OSP-RCIC/IST-Q701 |  |  |  | N | NO | <D> **** Detailed Description **** Step 7.2.8 should have the words "and record SAT in the measured value space for pump lubrication on attachment 9.2..." See Step 7.2.7 for an example. Step 7.2.7 has the word "valve" that should be "value". Step 7.2.57.b.4 should be a conditional step tied to 7.2.57.b.5. Step 7.2.132.f.6: RHR-V-628 should be RCIC-V-628. <I> **** Actions Taken **** This AR. <N> **** Equipment Description **** It's a procedure.
384470 | CR | 20180912 |  | 4 | SA-C-1 Oil Level Low | N | N |  | N | YES | <D> **** Detailed Description **** SA-C-1 Oil level is near the bottom of the sightglass and oil should be added before oil level goes out of sight low. Per the OPS Logs "Compressor is operable until oil level is out of sight low" <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RW 467' | 02-00-SA-C-1
384474 | CR | 20180912 |  | 4 | Student Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** HP technician failed HP continuing training exam. Remediation is scheduled and will consist of objective review followed by retaking exam. <I> **** Actions Taken **** Training Supervisor and RP Supervision notified. Failure documented in eTAR. This is for trending only. eTAR Class ID # 237374. <S> Reviewed objectives with student and individual passed remediation (Class ID 238521). CR for trending only. Request closing this CR.
384475 | CR | 20180912 |  | 3 | ISPM-6 definitions need refinement |  |  |  | N | NO | <D> **** Detailed Description **** ISPM-6 does not define heaters in the definition section. The intent of section 3.2 below is to provide requirements specific to heaters with high temperature heating coils which could ignite a fire. This should not be applicable to a compressor style heat pump (portable AC) unit. The Yakima Building has approximately 20 portable AC units which were temporarily installed due to the buildings loss of cooling system this summer. These AC units are evaporative cycle/ convective heat pumps which cool and heat depending on the mode of operation. Basically the heating/cooling cycle is reversed. These units have no additional conductive or radiative heating coils which increase the risk of fire. Both modes (heating and cooling) produce the same amount of heat produced by the units internal compressor. <I> **** Actions Taken **** Contacted Safety, initiated CR for action. <N> ISPM-6 does not apply to these types of units, therefore does not need to be revised . See EDMS for Industrial Safety investigation and resolution of this concern (the units will not be used for heating purposes). Recommend 4 - trend. . As previously stated ISPM-6 does not need to be revised. ISPM's are reviewed annually by a team of personnel, anyone is welcome to attend and provide feedback.
384479 | CR | 20180912 |  | 4 | PAAP Door 9 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** The lock on PAAP Door 9 requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervisio notified. Initiate CR/WR. <N> **** Equipment Description **** PAAP Door 9
384480 | CR | 20180912 |  | 3 | (QA) Inconsistencies in Digital Instructions/SQA Procedures |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Inconsistencies identified within digital design instructions and Software Quality Assurance (SQA) procedures. There are no known consequences resulting from these inconsistencies. Potential consequences of these inconsistencies include confusion that could result in lost productivity and misunderstandings that could result in not meeting the intent of one or more of the instructions/procedures. Factual Basis: (details in EDMS) - Inconsistencies in instruction/procedure steps for System, Structure, or Component (SSC) or plant software: (see EDMS for 18 examples regarding DES-6-1 and DES-6-3) - Inconsistencies in procedure steps applicable to both SSC (plant) software and non-SSC (non-plant) software: (see EDMS for 2 examples regarding SWP-CSW-01) - Inconsistencies in procedure steps applicable to non-SSC (non-plant) software: (see EDMS for 4 examples regarding SWP-CSW-01 and SWP-CSW-11) Insights: â€¢ At this time, SWP-CSW-01 Attachment 9.1 appears to only pertain to SSC (plant) software; however, if this is correct, it is not currently stated within SWP-CSW-01. â€¢ Some of the misalignments noted above appear to be due to gaps within change management with respect to the changes made to other instructions and procedures. â€¢ The issues identified above resulted from a sampling of steps reviewed in instructions and procedures, and may not be all inclusive of procedural conflicts, inconsistencies, and inaccuracies within these documents. . <I> **** Actions Taken **** Contacted the Design Engineering Manager and Assistant Information Services Manager. . This Deficiency was identified during follow-up activities related to the last Quality audit of the SQA program. . Quality recommends this CR be routed to Design Engineering.
384481 | CR | 20180912 | CAQ | D | Piping upstream DSA-V-77B leaking/ corroded | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02134304, then taken back to complete <D> **** Detailed Description **** Piping upstream DSA-V-77B leaking/ corroded This could also be the cause of a recent CR for blockage of this blowdown line (Ref AR #384248 and W/R #29144453) See EDMS for pics <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** DSA-V-77B DG2 Rm DG 441' | 02-00-DSA-DY-1B,02-00-DSA-V-77B
384482 | CR | 20180912 | CAQ | B | (QA) Elevation â€“ Continued Misalignments in SQA Documents |  |  |  | Y | NO | <C> THIS CR WILL BE BROUGHT BACK TO ALLOW TIME FOR ENGINEERING TO DEVELOP/ARTICULATE CAUSES AND CORRECTIVE ACTIONS. Risk = Medium (B) Cause Uncertainty = Cause is Clear Document Known Cause <D> **** Detailed Description **** (QA) Misalignments still exist in Software Quality Assurance (SQA) instructions and procedures related to plant software after resolution of a Condition Adverse to Quality in Condition Report (CR) 382405 â€œMisalignment in Latest SQA Guidance Documentsâ€. CR 382405 identified an Area Requiring Management Attention (ARMA) regarding a failure to properly implement corrective actions for a Quality Finding (CR 373378) issued during the last SQA audit. ARMA CR 382405 was issued with an Interoffice Memo (IOM) from the Quality Manager regarding a failure of engineering management (supervisor oversight) to coordinate efforts on process changes to the SQA program, which were found to be incomplete upon review of completed actions. There are no known consequences resulting from these misalignments. Potential consequences of misalignments include confusion that could result in lost productivity and misunderstandings that could result in not meeting the intent of one or more of the SQA guidance documents. Factual Basis: (see details in EDMS) - Misalignments in SQA-related instructions/procedures pertaining to System, Structure, or Component (SSC) or plant software: (see EDMS for 3 examples regarding DES-6-3) - Misalignments in SQA-related procedure steps applicable to both SSC (plant) software and non-SSC (non-plant) software: (see EDMS for 2 examples regarding SWP-CSW-01) - Misalignment in SQA-related procedure steps applicable to non-SSC (non-plant) software: (see EDMS for 1 example regarding SWP-CSW-01) Insights: â€¢ Some of the misalignments noted above appear to be due to gaps within change management with respect to the changes made to other instructions and procedures. â€¢ The issues identified above resulted from a sampling of steps reviewed in instructions and procedures, and may not be all inclusive of conflicts, misalignments, and inaccuracies within these documents. <I> **** Actions Taken **** Contacted the Design Engineering Manager and Assistant Information Services Manager. Acting Quality Manager issued Quality Elevation memo to Design Engineering Manager and notified VP Engineering. . This Elevation resulted from follow-up activities related to the last Quality audit (AU-CSQ-17) of the SQA program. . Quality recommends this CR be routed to Design Engineering. <N> Engineering and Information services met and agreed on a corrective action plan. The plan did not include the list of exemptions, the SWP recognizing the graded approach or a full revision review. Both parties felt that a full revision review was not necessary. This lead to a QA Elevation due to the following misalignments that were not a part of the previous revision review. The cause is known and the CAs have been placed into Passpor Corrective actions are delineated in the assignments in this CR.
384484 | CR | 20180912 |  | 3 | eDNA service ENWBU.CWFM changed unexpectedly |  |  |  | N | NO | <D> **** Detailed Description **** eDNA service for the CW flow meter signal (ENWBU.CWFM) was changed without warning, causing all historical data from the CW flow meters to be lost or unreachable, most importantly the CW volumetric flow and temperature signals. These are vital thermal performance monitoring signals. Though the signals were restored on 8/25 through ENWBU.CIRCH2O, previous historical data is not available on eDNA. <I> **** Actions Taken **** Discussed with Computer Engineering. Initiated CR.
384485 | CR | 20180912 | CAQ | D | FP-P-1 Battery No. 2 Light Out | N | Y |  | N | YES | <D> **** Detailed Description **** During performance of SOP-FP-STBY after restoration of FP -P-1, the battery number 2 light did not illuminate as expected after taking E-CB-FPCP1/CB2 to ON. Bulb was tested and electricians measured 26.3 V on both batteries. <I> **** Actions Taken **** CRS notified and electrical troubleshooted potential causes. None found. <N> **** Equipment Description **** CWPH | 02-00-FP-ENG-1,02-00-FP-P-1
384487 | CR | 20180912 | CAQ | D | Cooling water line to FP-FG-4 is partially plugged | N | Y |  | N | YES | <C> CR reopened to cross reference additional WR 29144751, then taken back to complete <D> **** Detailed Description **** While working WO#02127808-01 it was observed that there was some blockage in the upstream piping, attempted to rod out the pipe and we were successful on getting minimal flow through the piping, there is restriction in the pipe down stream of FP-V-12 to the oil cooler and FP-FG-2 on the fire pump. This piping will need to be replaced. This does not affect operability. This should be bundled in with the next diesel window <I> **** Actions Taken **** Notified my supervisor and the main control room and wrote this condition report | 02-00-FP-ENG-1,02-00-FP-FG-4,02-00-FP-RV-2,02-00-FP-V-12
384488 | CR | 20180912 |  | 4 | TOA-P-2B1 pump casing leak | N | N |  | N | YES | <D> **** Detailed Description **** Leak noticed on rounds. Leak is about 1 drop/sec and appears to be coming out of the pump back plate and possibly the drain plug. See attached pictures. <I> **** Actions Taken **** Notified CRS. | 02-00-TOA-P-2B1
384490 | CR | 20180912 |  | 4 | RWCU-DPIS-88B HP drain valve leaking by. | N | N |  | N | YES | <D> **** Detailed Description **** RWCU-DPIS-88B HP drain valve is leaking by as indicated by elevated tubing/piping temperature. Recommend valve replacement at the same time as WO 02104978, currently scheduled for December 2018. Please expedite planning of this work. <I> **** Actions Taken **** Informed supervisor and system engineer. <N> **** Equipment Description **** RW 467 | 02-00-RWCU-DPIS-88B
384491 | CR | 20180912 |  | 4 | RWCU-V-230A leaking past its seat. | N | N |  | N | YES | <D> **** Detailed Description **** Investigation of WR 29143930 revealed that RWCU-V-230A is leaking by, in addition to RWCU-V-213A and SA-V-259. Infrared temperature monitoring showed what should be a stagnant line reading 120F, indicating flow from RWCU-DM -1A. <N> **** Equipment Description **** RW 477, RWCU A hold pump room | 02-00-RWCU-V-213A,02-00-RWCU-V-230A,02-00-SA-V-259
384492 | CR | 20180912 |  | 4 | Legacy portable hd found plugged int non-corp/non-plant comp |  |  |  | N | NO | <D> **** Detailed Description **** During a walk down activity a Cyber analyst identified a legacy portable hard drive plugged into a non -corporate/non-plant computer. The cyber analyst confiscated the drive and notified Cyber Program Manager. <I> **** Actions Taken **** The investigation identified that this was a legacy portable hard drive that was not part of the plant media identified in SWP-CSW-15. The drive owner has been contacted and validated that it is no longer needed. No further action is needed.
384493 | CR | 20180912 | CAQ | D | RCIC DT-1 oil levels low out of spec. | Y | N |  | N | YES | <D> **** Detailed Description **** RCIC-DT-1 IB and OB bearing oil levels are out of spec. low IAW SOP-RCIC-STBY. Spec is "at or just above" the low level mark and below the high level mark. Current levels are: OB approximately 1/8 " below low stdby, IB miniscus just below low stdby. Please adjust levels to normal band. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** RX 422. | 02-00-RCIC-DT-1
384494 | CR | 20180912 |  | 3 | Dose Savings Suggestion. OPS 2 door checks RB 422. |  |  |  | N | NO | <D> **** Detailed Description **** A recent change to the OPS 2 logs has been implented to save dose by moving the ECCS oil checks to a weekly check. While this is intended to save dose, we are still required to verify all the doors on the RB 422 are closed, including the doors between RHR A and B pump rooms. Please evaluate if the door checks can also be changed to a weekly or allow doors located in High Rad/C-zones to be not required. This change would allow the oil checks to actually save dose. | 02-00-R-BLDG-MISC,02-00-R-DOOR-R004,02-00-R-DOOR-R005,02-00-R-DOOR-R006,02-00-R-DOOR-R006A,02-00-R-DOOR-R007,02-00-R-DOOR-R007A,02-00-R-DOOR-R008,02-00-R-DOOR-R009,02-00-R-DOOR-R009A,02-00-R-DOOR-R010,02-00-R-DOOR-R010A,02-00-R-DOOR-R011,02-00-R-DOOR-R011A,02-00-R-DOOR-R012,02-00-R-DOOR-R013
384495 | CR | 20180912 | CAQ | C | LCS 1.3.6.3 issued without notifying Operations | N | Y |  | N | NO | <D> **** Detailed Description **** LCS 1.3.6.3 issued without notifying Operations. Revision 103 of the LCS added LCS 1.3.6.3 requiring all MS radiation monitors be in service. MS-RIS-610D was non-functional at the time and tracked on sheet TS-18-MS-RIS-610D -001. This required entering LCS 1.3.6.3.A and C with an one hour action to isolate RRC-V-19 or 20. <I> **** Actions Taken **** placed MS-RIS-610D in trip within one hour, updated sheet TS-18-MS-RIS-610D -001 <N> Operations notification consisted of a single person who was on vacation at the time and not a licensed SRO. This placed Columbia outside of compliance with LCS 1.3.6.3 and beyond required LCS action times when it was discovered. . This AR will be resolved under AR 00384508. AR 00384508 is a CAQ B severity, it will address all the issues associated with this AR and itself. This AR is a level C severity so it is appropriate to resolve using the B severity. <R> CR 384508 has been initiated to address the LCS not being met. This CR was addressed by CR 384508 and is cross referenced | 02-00-MS-RIS-610D
384496 | CR | 20180912 |  | 3 | Procedure change request. SOP-CW-OPS for CW Blowdown |  |  |  | N | NO | <D> **** Detailed Description **** Per SOP-CW-OPS, section 5.8, request the actions to be performed at TMU be changed to conditional steps based on blowdown being secured for greater than 24 hrs. This would be more inline with SOP-CW-OPS section 5.9 (Securing CW B/D). Additionally, OPS 4 is required to perform a manual sample every night on rounds so this change can save time and money by eliminating additional trips to TMU.
384502 | CR | 20180912 |  | 3 | Student Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** Trainee failed an exam. Line supervisor and training supervisor have been notified. Recommend to trend in order to document remediation actions <I> **** Actions Taken **** Generated the CR in accordance with TDI-02. Informed trainee's supervisor and informed training supervision. <N> Exam failure occured in EL000307
384503 | CR | 20180912 | CAQ | D | Door C-221 needs door knob | N | Y |  | N | YES | <D> **** Detailed Description **** Working 15.3.17 found Door C-221 door knob will not latch door on it own, the strike plunger stays retracted unless helped to work .free all was no help, time for a new knob. | 02-00-W-DOOR-C221
384504 | CR | 20180912 |  | 4 | Procedure Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Reviewing 10.25.35 Testing & Setting GE CEH Relays. Enhancements are needed to make the procedure flow along & some step clarifications. <I> **** Actions Taken **** Notified supervisor, Marked up procedure attached to EDMS, Procedure needs revised before the calibrations of following relays HPCS-RLY-40, E-RLY-40G/ASHE, DG-RLY-40/DG1, DG-RLY-40/DG2 <N> ***GENERAL NOTES*** the following assignment has been created within the Maint. Procedure Revision data base. a mark up of the procedure has been placed within the EDMS of this AR. no further actions are required under this AR. see the EDMS of this AR for a link to the Maint. procedure revision data base assignment.
384505 | CR | 20180912 | CAQ | D | Door C-216 bottom bolt no working | N | Y |  | N | YES | <D> **** Detailed Description **** performing 15.3.17 found Door C-216 bottom bolt on inactive leaf to no be working, bottom plate is loose and causing interferance so bolt will not extend. | 02-00-W-DOOR-C216
384506 | CR | 20180912 | CAQ | D | Door -408 Metal on door is ripped near strike plate | N | Y |  | N | YES | <D> **** Detailed Description **** Performing 15.3.17 found door R408 to have the metal ripped near the strike plate top and bottom | 02-00-R-DOOR-R408
384507 | CR | 20180912 | CAQ | D | Door R-407 hole near bottom hinge, need door knob | N | Y |  | N | YES | <D> **** Detailed Description **** performing 15.3.17 found Door R-407 to have a dent and hole near bottom hinge, and door knob needs to be replace, tried lubrication ,no help | 02-00-R-DOOR-R407
384508 | CR | 20180912 | CAQ | B | LCS 1.3.6.3 not met due to out of service equipment | N | Y |  | N | NO | <C> RISK: MEDIUM CAUSE: PARTIAL <D> **** Detailed Description **** MS-RIS-610D has been out of service since mid-May and has been tracked on sheet TS-18-MS-RIS-610D. On August 29, 2018, Revision 103 to LCS added LCS 1.3.6.3, which requires placing the channel in trip within 24 hours if one or more channels are inoperable. Since the channel was not placed in trip when the LCS revision was implemented, the station has not met the LCS since August 29, 2018. <I> **** Actions Taken **** This issue was discussed with the Shift Manager and Reg Affairs management, and the station was placed back into compliance with the LCS. | 02-00-MS-RIS-610D
384509 | CR | 20180912 |  | 4 | (QA) SW-V-171B Planning & Scheduling Deficiencies |  |  |  | Y | YES | <D> **** Detailed Description **** (QA) SW-V-171B is inappropriately scheduled for work in the R24 outage. In addition, this valve has been repaired and the work order can be cancelled. The impact is that resources have been used to plan work that is not required and unnecessarily scoped into R24. During Quality review of Work Order (WO) 02076390, SW-V -171B stuck open, it was identified that this valve is currently closed, the work order can be cancelled and if work was required it can be worked on-line. See additional details in EDMS. <I> **** Actions Taken **** Discussed with the Ops Outage Work Control Manger, Planning Supervisor and Planner. Initiated this CR. | 02-00-SW-V-171B
384512 | CR | 20180913 | CAQ | D | FPC HX Room (RRA-CC-20) SW low flow | N | Y |  | N | YES | <D> **** Detailed Description **** Following start of SW-P-1A the â€œFPC Rm Cooler Flow Low/Temp Hiâ€ alarm (H13-P812.R1.4-2) was received. CRS issued a partial OSP-SW-M101to clear the alarm. During the performance of the partial OSP-SW-M101 the equipment operators noted that the as-found initial flow indicated on SW-FI-71A was 35.5 gpm, which less than the minimum required value of 38.5 gpm. Per note 11 of Attachment 9.1 of the surveillance, the FPC room contains no Tech Spec associated equipment and therefore no equipment was rendered Inoperable by the low flow. The flow was then successfully raised to the desired band per the partial surveillance. | 02-00-RRA-CC-20,02-00-SW-FE-71A,02-00-SW-FI-71A
384513 | CR | 20180913 |  | 4 | FPC-FIC-15B requires calibration/venting | N | N |  | N | YES | <D> **** Detailed Description **** FPC-FIC-15B is controlling FPC-DM-1B flow at approximately 140gpm less than the desired AUTO setpoint. FPC-FIC-15B was used to remove and restore FPC-DM-1B from service to support Suppression pool clean up. During this evolution FPC-FIC-15B responded appropriately in AUTO. The only issue is that the setpoint needle is required to be placed ~140 gpm greater than the flow actually desired. FPC-DM-1B is in service at this time and will very likely be removed from service by 9/17/18. Please investigate/repair. Suspect a recalibration or instrument fill and vent may address this issue. <I> **** Actions Taken **** Informed MCR. Verified proper response in the lower and raise direction. <N> **** Equipment Description **** RWCR | 02-00-FPC-FIC-15B
384517 | CR | 20180913 |  | 4 | TR-M3 Cooler Group #2 Trouble | N | N |  | N | YES | <D> **** Detailed Description **** TR-M3 Cooler Group #2 Trouble has come in on consecutive days at around 5 am on 9/12/18 and on 9/13/18. On 9/12, one fan was found not running; on 9/13, the demand for the fans had already cleared, and therefore a specific fan/pump could not be determined to be the cause. Trouble alarm reset with no issues per ABN-TRANSFORMER step 7.4.11 on both instances. This CR is being written for trending purposes. Further instances of alarm on consecutive days or similar frequency should spur an investigation into cause of trouble. <I> **** Actions Taken **** Informed MCR. Write CR. <N> **** Equipment Description **** TR-M3, Xfmr yard | 02-00-E-TR-M3
384519 | CR | 20180913 |  | 4 | 2 Pieces of M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0068471 Heise Gauge- model CM 30inhgvac was new & never used. Rejected- wouldn't pass Calibration. Sent back to Ashcroft for replacement. DEF #6737A written. Calcode #0063715 Clemco Carbon Monoxide Alarm- model CMS-2 was not used during Calibration cycle. Rejected- Beyond repair. DEF #6738A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
384521 | CR | 20180913 |  |  | Acceptance of Asset Suite Crashes |  |  |  | N | NO | <D> **** Detailed Description **** Frequent Asset Suite crashes are continuing to negatively impact computer-based productivity and frequently results in re-work. See full text document posted to EDMS. <I> **** Actions Taken **** Initiated CR.
384523 | CR | 20180913 |  | 4 | ROA-HV-01 Possible Water Leak | N | N |  | N | YES | <D> **** Detailed Description **** During a vital area check, discolored water was observed leaking from ROA-HV-01. <I> **** Actions Taken **** Security supervision notified. SSS notified. CR/WR generated | 02-00-ROA-HV-1
384524 | CR | 20180913 |  | 3 | ESOMS not updated after overtime assignment |  |  |  | N | NO | <D> **** Detailed Description **** Overtime was called for a Maintenance Supervisor to cover Monday the 9/3 holiday (Labor day), Maintenance Supervisor was called on his day off to cover the holiday, Maintenance Supervisor accepted the overtime assignment but failed to update ESOMS when he returned to work. <I> **** Actions Taken **** Informed management and updated ESOMS Discussed with CAP (L.Walker) on 10/11/18, will close CR no actions needed, this has been trended to Maint. - JSW
384525 | CR | 20180913 |  | 4 | AS-PI-1C | N | N |  | N | YES | <D> **** Detailed Description **** AS-PI-1C could not be calibrated within tolerance per IMDS and was found to be not repeatable during performance of WO# 0209066701. Recommend replacement <I> **** Actions Taken **** Notified Supervisor | 02-00-AS-PI-1C
384527 | CR | 20180913 | CAQ | C | ISP-CMS-B306 & ISP-CMS-B307 procedure changes needed |  |  |  | N | YES | <D> **** Detailed Description **** These two procedures affect TDAS points X354 and X363. The calibration of the TDAS points needs to be performed in the body of the procedure, since they must be performed with the field input. The are only performed during outages with the wetwell open. If they are not performed within the procedure an ERDS point could be out of tolerance for two years until the next outage. <I> **** Actions Taken **** Discussed with supervisor and procedure writer. Wrote this CR. <N> **** Equipment Description **** rx 471' wetwell az 35 rx 471' wetwell az 270 | 02-00-CMS-LE-6A,02-00-CMS-LE-6B
384528 | CR | 20180913 |  | 3 | Minor Spill of 12% NaClO at Bldg 33 (Flocculater) |  |  |  | N | NO | <D> **** Detailed Description **** Chemistry report a minor spill <1 gallon of 12% NaClO (bleach) in the Flocculater Building (Building 33) to Environmental and Regulatory Programs (E&RP). Spill was to impermeable surface and mostly captured in a secondary containment berm. Facilities has been given clean-up direction; spill material will be delivered to the 180-day Hazardous Waste Storage Area per E&RPâ€™s direction. This spill is not reportable; WR is not required. <I> **** Actions Taken **** Evaluated spill, notified E&RP supervision, contacted Facilities for clean-up, notified Operations that no further action is required initiated CR. <N> **** Equipment Description **** Bldg 33 Flocculater Spill Cleaned up and waste delivered to E&RP. CR can be closed
384530 | CR | 20180913 |  | 3 | Acceptance of Asset Suite Crashes |  |  |  | N | NO | <D> **** Detailed Description **** Frequent Asset Suite crashes are continuing to negatively impact computer-based productivity and frequently results in re-work. The organization appears to be willing to accept this situation. Please see full text document posted to EDMS. <I> **** Actions Taken **** Initiated CR. <N> The Asset Suite application continues to have these sporadic abends when dealing with JAVA and Microsoft Office. The answer we receive from the vendor (Asset Suite Application - ABB) is that we are using software that is no longer supported (outdated). We are currently in the middle of the Asset Suite upgrade project which will bring the software up to the latest revisions. We are hoping this will resolve these issues but if not, we will be able to address the issue with the vendor (ABB). Sent an email to CR writer and his supervisors with this information. . Recommend NCAQ-4 to ITMGMT
384533 | CR | 20180913 |  | 3 | Procedure correction ARP 4.820.B2 |  |  |  | N | NO | <D> **** Detailed Description **** 4.820.B2 Drop 5-1 TG ECCENTRICITY HI has the wrong drawing reference at the bottom. Drawing E537-7 has been superceded by EWD-49E-059 <I> **** Actions Taken **** Initiated CR
384534 | CR | 20180913 |  | 3 | DRAWING CONFIGURATION FOR FP-V-607 |  |  |  | N | NO | <D> **** Detailed Description **** This is a documentation issue only. AR/CR 384455 identified a discrepancy on CVI 215-00,841 and what is installed in the CWPH for valve FP-V-607. CVI 215-00,841 calls out a piece of pipe & pipe cap coming off of the valve, but a pipe plug is installed directly on the valve instead. Per design specification 15B.1 a plug is acceptable to interchange with a pipe cap.Therefore, CVI 215-00,841 needs to be revised to identify the pipe plug installed instead of the pipe & pipe cap. Also, the contract break currently shown on CVI 215-00,841 between contract 220 and contract 215 is incorrectly labeled and should be removed from the drawing. MEC DWG M515-1 also does not show the installed pipe plug and needs to be updated to concur with CVI 215-00,841. Recommend assignment to AR-DESDFTM to revise CVI 215-00,841 & M515-1. <I> **** Actions Taken **** WROTE CR. DISCUSSED WITH DESIGN LEAD | 02-00-FP-V-607
384536 | CR | 20180913 |  | 3 | AS-RV-1 & 5 not tested per requirements of PPM 10.2.8 | N | N |  | N | YES | <D> **** Detailed Description **** During week of implementation it was discovered that the replacement valves for AS-RV-1 and AS-RV-5 had not been set point tested within the 6 mo. per step 4.24 of PPM 10.2.8. These are steam valves and must be tested off -site. The intent of this CR is to ensure the valves are tested within the 6 mo. period for the next auxillary boiler outage in Fall of 2019. This CR should also prompt the determination of other valves in this situation. The MWO's for these valves should include a task that prompts the testing of the valves prior to installation within the 6mo.window. <I> **** Actions Taken **** Notified Supervisor. Wrote CR <N> **** Equipment Description **** T457 F3/4.4 (ON TOP OF AUX BOILER AT NORTH END). AS-RV-1 T457 F3/4.4 (ON TOP OF AUX BOILER AT NORTH END). AS-RV-5 | 02-00-AS-RV-1,02-00-AS-RV-5
384540 | CR | 20180913 | CAQ | D | TDAS MUX 9 has failed | N | Y |  | N | YES | <D> **** Detailed Description **** TDAS-MUX-9 has failed as indicated by a red box next to mux 9 on the TDAS system status screen. <I> **** Actions Taken **** Generated WR | 02-00-TDAS-MUX-9
384541 | CR | 20180913 |  | 3 | Late identification of vendor support WO 02118127-01 |  |  |  | N | NO | <D> **** Detailed Description **** The week before implementation of the 6yr maintenance of FP-ENG-1 it was identified that there was a need for vendor support for technical assistance and rebuild of specific parts of FP-ENG-1. This was caught while reviewing past WOâ€™s performed. The opportunity to catch this was missed on multiple levels within the Mechanic shop. Coaching was provided on the necessity of validating that we are prepared to perform work as scheduled. <I> **** Actions Taken **** CR generated for tracking, recommend a SP task be created by planning to â€œSchedule Vendor Supportâ€ and placed in schedule 3-4 weeks prior to the work. | 02-00-FP-ENG-1
384543 | CR | 20180913 |  | 3 | PPM 12.9.10 revision |  |  |  | N | NO | <D> In PPM 12.9.10 The section 8.5 Coupon Replacement in PS CPST TSW/2 comes first but for a better drain of the system and to reduce potential for the technician to be sprayed during the removal of these coupons it would be better if section 8.6 Replacing PS WHKB 1 (Bio fouling Unit) on Coupon Station PS CPST TSW/2 came first. I have taken the native document and made the changes that we thought would work. It is attached to EDMS doc on this AR. Please review and revise as is applicable or necessary. <I> Notified chemistry supervision and procedure sponsor <N> Taken from INPROG to APPROVED at request of initiator. Was at INPROG due to the system kicking her out.
384546 | CR | 20180913 |  | 3 | Gap Analysis not proceduralized |  |  |  | N | NO | <D> **** Detailed Description **** There is no proceduralized process for performing a Gap Analysis. A Gap Analysis can be requested to evaluate gaps in procedures, processes, new/existing requirements or other concerns. A lack of procedural guidance can result in analyses that may not be complete, have various formats, and are not as cost effective since each evaluator develops their own product/process. Recommend benchmarking with industry peers and developing either a new procedure or a section in an existing procedure for Gap Analysis. <I> **** Actions Taken **** Discussed with Corrective Action Personnel
384547 | CR | 20180913 |  | 4 | CO-42-1B2E | N | N |  | N | YES | <D> **** Detailed Description **** Duirng lift of clearance D-AS-BLR-1-002 CO-42-1B2E will not stay closed in. Reccomend electricians investigate, and lubricate if necessary. | 02-00-CO-42-1B2E
384549 | CR | 20180913 |  | 3 | PMID 26345 requires scope clarification |  |  |  | N | NO | <D> **** Detailed Description **** PMID 26345 / Work Item NUMACBATTREPLACEMENT needs scope clarified. Instruction provided on M102 screen does not provide an EPN and there is no iformation in the GEK 113815 Volume Ten for the part battery/part which requires replacement. EPN believed to be APRM-COMP-NIC. If battery replacement is required per the GEK there is both a Master and Slave CPU Card. New PM indicates only one replacement. Lack of scope detail and parts info is preventing planning of first time PM per WO 02101747. New PMID 26345-01 is an 8 year PM. <I> **** Actions Taken **** GE has been contacted via email and has been provided with info to help GE assist CGS. However no answers have been provided from GE. Cat ID 38216 created. Created this CR.
384551 | CR | 20180913 |  | 4 | During HCV platform work a workerâ€™s ED fell to the DG roof |  |  |  | N | NO | <D> **** Detailed Description **** During the installation of the HCV platform on Reactor Roof, one of the Contractorâ€™s personnel engaged in the installation knock his Electronic Dosimetry (ED) from his lanyard and if fell to the DG Roof. <I> **** Actions Taken **** 1. The individual was removed from the roof and taken to HP. 2. The ED was recovered from the DG roof. 3. The individual had recently check his ED and his reading along with other members of the crewâ€™s reading at the time the ED was lost was given to HP. 4. Under HPâ€™s direction the individual exited the plant through the IPM-8 <N> Intermech
384552 | CR | 20180913 |  | 4 | TSW leak from upstream valve TSW-V-H777 | N | N |  | N | YES | <D> **** Detailed Description **** Leak isolated with TSW-V-55 and TSW-V-56. TSW to WCH-CU-51A and WCH-CU-51B Isolated. WMA-FN-51A verified running to maintain controlroom habitability. <I> **** Actions Taken **** leak isolated. verified MCR habitability maintained. <N> **** Equipment Description **** RW 507' | 02-00-TSW-V-H777
384553 | CR | 20180913 | CAQ | D | D301 Needs Maintenance |  |  |  | N | YES | <D> **** Detailed Description **** D301 Needs Maintenance - Contact Security x2185 for details <I> **** Actions Taken **** CR/WR, Security Supervision Notified, Compensatory Measures Initiated. | 02-00-D-DOOR-D301
384554 | CR | 20180913 |  | 4 | TSW-V-H777 broke off due to corrosion. | N | N |  | N | YES | <D> **** Detailed Description **** At 1750, during implementation of WOT 02125913-26 REWORK INTERFERENCE TUBING TO (WCH-PS-53) the craft was tightening a 3/8â€ compression fitting to the copper tubing about 5 feet away from the connected threaded isolation valve TSW -V-H777. The valve suddenly broke at the male threads and blew off. No stress was placed on the valve during the activity. The male threaded portion of the nipple was extremely degraded by corrosion. See attached pictures. No personnel was injured. Ops was notified immediately and the TSW leak was isolated. <I> **** Actions Taken **** Notified OPS. TSW leak isolated. Worked stopped. <N> Williams Plant Services | 02-00-TSW-V-H777
384555 | CR | 20180913 |  | 4 | Brushes on Main Generator wearing unevenly. | N | N |  | N | YES | <D> **** Detailed Description **** Brushes on Main Generator wearing unevenly with 1 indicating new, the other halfway to refill, although halfway to refill it looks very worn down. <I> **** Actions Taken **** Informed MCR, SSS. Initated AR. | 02-00-E-GEN-1
384556 | CR | 20180913 | CAQ | D | E-CB-S/2 open light stuck in socket. | Y | N |  | N | YES | <D> **** Detailed Description **** Found light burned out, tried to replace light but bulb is stuck in socket. Could not change out without extra risk of damaging components. <I> **** Actions Taken **** Initiated AR, informed SSS. | 02-00-E-CB-S/2
384557 | CR | 20180914 |  | 4 | RW 487 Chemistry IPM Out of Service | N | N |  | N | NO | <D> **** Detailed Description **** The IPM outside the chemistry breakroom on RW 487' was placed out of service After TSW water from the RW 507 leak was running down onto the IPM. After IPM was cleaned up it was displaying Low Beta counts on the display. <I> **** Actions Taken **** IPM was placed out of service. Defiency tag was hung on IPM and Frisking SOP was set up to enter clean area. <N> **** Equipment Description **** HP-EQ-C015122 | 02-00-HP-EQ-C015122
384558 | CR | 20180914 |  | 4 | Nuisance Alarms: TR-M1 and TR-M3 Cooler Group #2 Trouble | N | N |  | N | YES | <D> **** Detailed Description **** TR-M1 Cooler Group #2 trouble alarm was received the pump and fans were all off, there were no overload trips or failed motor contactors. TR-M3 Cooler Group #2 trouble alarm was received at about 0200 the pump and fans were all off, there were no overload trips or failed motor contactors. Ambient Temperature was 54 degF, E-TIS-M3/26Q (Top Oil Temp) was 55 degC, E-TIS-M3/49W1 (H1 Winding Temp) was 52.5 degC, and E-TIS-M3/49W2 (X1 Winding Temp) was 50 degC. This is the third morning in a row that this alarm has come in on main 3, see CR 384517. It is suspected that the alarm is falsely coming in when cooler group 2 is automatically secured due to lowering temperatures. Please investigate and correct, Main 2 should be investigated for common cause issue. <I> **** Actions Taken **** Informed MCR, Cleared both alarms <N> **** Equipment Description **** Transformer Yard | 02-00-E-TR-M1,02-00-E-TR-M3
384559 | CR | 20180914 | CAQ | D | DO-FLX-1A2 insulation has a tear | Y | N |  | N | YES | <D> **** Detailed Description **** DO-FLX-1A2 insulation has a large tear (~ 3 to 4 inches long). The integrity of the hose is NOT in question. The hose underneath the insulation has no signs of damage. Please repair/replace as appropriate. See EDMS doc for Pic. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** DG1 room | 02-00-DO-FLX-1A2
384560 | CR | 20180914 |  | 4 | High Turbidity Indicated on PWC-XR-1 doesnt match PWC-TBIT-2 | N | N |  | N | YES | <D> **** Detailed Description **** The indicated turbidity on PWC-TBIT-2 while the flocculator was started was 0.074 NTU and the indicated turbidity on PWC-XR-1 was -0.004 NTU. Per drawing EWD-62E-058 and the IMDS PWC-XR-1 is used for the High turbidity shutdown and alarm for the flocculator to ensure water quality meets WA state requirements. See EDMS for photos. Please investigate and repair. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** Flocculator Building | 02-00-PWC-TBIT-2,02-00-PWC-XR-1
384561 | CR | 20180914 |  | 4 | Inability to raise flow on RWCU-DM-1B | N | N |  | N | YES | <D> **** Detailed Description **** During turnover on 9/13/18 for night shift in RWCR, it was turned over that there was an attempt to raise flow in the RWCU demineralizers, and RWCU-DM-1A responded normally, but RWCU-DM-1B did not respond and there was no increase in flow. This could be related to the current issue with the leaking air isolation valves noted in CR 384467. Cause of RWCU-DM-1B non-responsive flow control valve should be investigated, especially if related to the other issues listed in the CR above. <I> **** Actions Taken **** Informed MCR. Initiated CR. | 02-00-RWCU-DM-1B
384566 | CR | 20180914 | CAQ | D | CBD-FR-10 (circ water flow blowdown flow) reads high | N | Y |  | N | YES | <D> **** Detailed Description **** CBD-FR-10 (circ water flow blowdown flow) reads app. 600 gpm with blowdown secured. <N> WR was cancelled. Repair and calibrated per 16.9.1. See notes in WR 29144604. | 02-00-CBD-FR-10
384567 | CR | 20180914 | CAQ | D | SW Pump House B Large Double Doors stuck | Y | Y |  | N | NO | <D> **** Detailed Description **** Was unable to open the large double doors to the Service Water B Pump House in support of 02111469-02 Stage Equipment for SW-M-P/1B work to stage oil. This had happend in the past due to the seal sticking and some slight pressure applied via a come along was sufficient to unstick the door. <N> **** Equipment Description **** SW Pump House B | 02-00-B-DOOR-G200
384568 | CR | 20180914 |  | 4 | replace tag on MS-V-906C |  |  |  | N | NO | <D> **** Detailed Description **** Found identification tag broken during our surveillance and unable to read it. It needs to be replaced so we can quickly identify the test isolation valve in the locked Hi-rad area. <I> **** Actions Taken **** wrote this AR/WR per form 26989 <N> **** Equipment Description **** T 506â€™, C8/12.9, In labyrinth behind locked hi-rad door | 02-00-MS-V-906C
384569 | CR | 20180914 | CAQ | D | Refuel bridge not operating as expected | Y | N |  | N | YES | <D> **** Detailed Description **** While working on the Refuel Bridge performing spent fuel inventory activities the bridge reverse motion stopped functioning. The bridge functions as expected in the forward motion. <I> **** Actions Taken **** Parked the bridge in B5B. Verified that the bridge moved with manual controls. Contacted the vendor (PAR) to discuss the issues. Par recommended the following: I&C or Fin someone proficient using LM90 will have to hook a laptop up to the bridge PLC to actually see what's going on. I&C needs to investigate the Subroutine BR TR (bridge and trolley operation). Rung 23 is the Bridge reverse interlock. Sounds like it may be related to REDIBR (red zone vio inhibit bridge rev) since you said you used the KS ZBB (zone boundary bypass key sw) and the bridge moved reverse. Everything that has to do with bridge and trolley motion is in this subroutine on LM90. They will need to trouble shoot using the laptop hooked up to the bridge. They need to make sure they are in monitor mode so no changes get accidentally changed. ALT + M. | 02-00-NSSE-EQ-8
384571 | CR | 20180914 | CAQ | D | IDS 14 15 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** IDS 14 15 are not functioning as designed and require maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervision notified. Initiate CR/WR. Compensatory measures were initiated. | 02-00-SEC-IDS-E/S/14/15
384572 | CR | 20180914 |  | 4 | LP1EA ckt & tripped and will not reset. | N | N |  | N | YES | <D> **** Detailed Description **** During OPS3 rounds noted LP1EA ckt 7 was in tripped condition. Notified CRS and got permission to reset. Attempted to reset, but ckt 7 immediately returned to tripped condition. <I> **** Actions Taken **** CR & WR written, MCR staff informed. | 02-00-E-LP-1EA
384573 | CR | 20180914 |  | 4 | Aux Steam Boiler damage from leaking manway covers | N | N |  | N | YES | <D> **** Detailed Description **** During annual inspection run with State Boiler Inspector, I pointed out what appeared to be leaking underneath both norht and south manway covers. We confirmed that leakage was not a pressure boundary leak. Due to manway cover leaks previously identified, leaking manway cover created major rust and degredation underneath manway cover which will need repairs for both the north and south manway covers. <I> **** Actions Taken **** CR & WR written. | 02-00-AS-BLR-1
384574 | CR | 20180914 |  | 3 | Procedure enhancement to SOP-AS-OPS |  |  |  | N | NO | <D> **** Detailed Description **** SOP-AS-OPS section 5.1.7 does not work. Attempting to lower drum level using BD-V-3 and BD-V11 is very slow, approximately 2 inches every 30 minutes. Low level cutout requires that Aux Boiler is "Firng" mode. During Aux Boiler operations for our annual inspection even with heating steam loads, Aux Boiler is in "Firing" mode only for about 3 minutes and in Standby for about 25 minutes. When Aux Boiler does go in "Firing" mode, steam drum level rises approx 1.5 inches. Due to all these dynamics, the Aux boiler low level cutout can not occur using 5.1.7. Section 5.1.6 works very well for this situation. I recommend deleting section 5.1.7 in it's entirety. Keeping verbage in () which states" (When requested by Autorized Inapector during Annual External Inspection)", place that verbage into section 5.1.6 <I> **** Actions Taken **** CR & WR written <N> **** Equipment Description **** SOP-AS-OPS
384575 | CR | 20180914 |  | 4 | HWC/HSSF Alarms for loss of Nitrogen Purge Pump | N | N |  | N | YES | <D> **** Detailed Description **** @1323 recieved alarms on HSSF-CAB-Chem/Lab for the HSSF (Hydrogen Storage Supply Facility) for Hydrogen water Chemistry. Alarms HS PSL119-STAT LOSS (Loss of Nitrogen Purge Pump A) & PC-SYS-STAT TROUBLE. <I> **** Actions Taken **** Per CI-14.4 contacted MCR and wrote CR & WR. Verified Plant Injection System for HWC and flows were normal. These two alarms automatically notify the HSSF gas/maintenance contractor. No further action is required. <N> **** Equipment Description **** HSSF Facility (Hydrogen Storage Supply facility) | 02-00-HSSF-CAB-CHEM/LAB
384576 | CR | 20180914 |  | 3 | Elevator Replacement â€“ Sheave Beam Legacy Issue Discovered | N | N |  | N | NO | <D> **** Detailed Description **** During the demolition of the RW Elevator No. 4 sheaves, abandon holes were revealed on the sheave beams (I-beams). This will require additional engineering, work order planning, QC, plasma torch cutting, and weld back with like kind material in sixteen locations. <I> **** Actions Taken **** Took pictures, made a template of existing holes, contacted design engineering and received fix. Worked with the elevator vendor to fine-tune schedule to avoid any schedule impact. <N> **** Equipment Description **** N/A | 02-00-MT-ELEV-4
384577 | CR | 20180914 |  | 4 | RW G11/P001/1 A15 2-1 spurious alarms | N | N |  | N | YES | <D> **** Detailed Description **** RW G11/P001/1 A15 2-1 Demin Waste Diff Press High alarming and clearing frequently in RWCR. This is the EDR-DM-29 dp, and the alarm setpoint is controlled by the red needle on EDR-DPIS-30, normally set at 10psid. This alarm is actuating at about 0psid, and typically clearing immediately. EDR-DM-29 does not even currently have flow. This appears to be an issue with the DPIS or electronic noise. Recommend investigate and repair. <I> **** Actions Taken **** Informed MCR, generated AR/WR. | 02-00-E-CP-G11/P001/1,02-00-EDR-DM-29,02-00-EDR-DPIS-30
384578 | CR | 20180915 |  | 3 | Increase in dose rates at ARM-RIS-29 | N | N |  | N | NO | <D> **** Detailed Description **** ARM-RIS-29 has increased 100 percent since 08/30/2018 On 08/29/2018 dose rates were documented at 20mRhr general area. On 08/30/2018 documented dose rates jumped to 40mR/hr general area. Review of the RWCR log showed that 3 cubic feet of RWCU resin and 76 cubic feet of Tank 22 resin were tranferred on 08/30/2018 . The Area Radiation Monitor in question located on RW 437 behind shield wall across from RWCU Resin pump and FDR Tank 22 Resin transfer pump. Suggest recirculaton of of both tank to move residual resin through transfer line. <I> **** Actions Taken **** Informed Shift Manager. informed HP Supervision | 02-00-ARM-RIS-29
384589 | CR | 20180916 |  | 4 | House keeping issue |  |  |  | N | NO | <D> **** Detailed Description **** Turbine building 441 between E-SM-75 and E-SM-85 there is a rope hanging from a cable tray. No work in-progress or reason for the rope to still be there. There isnâ€™t any scaffolding there and a man lift would not reach the upper cable tray due to obstructions. <I> **** Actions Taken **** Informed supervision <N> **** Equipment Description **** T441 G/17 rope hanging from cable tray near E-SM-75 | 02-00-T-BLDG-MISC
384590 | CR | 20180916 |  | 4 | AS-BLR-1 south mud drum manway cover leaking | N | N |  | N | YES | <D> **** Detailed Description **** South mud drum manway cover is leaking now that the boiler is cooling down post run for the state inspection. The leakage is small amount weeping from the top of the south mud drum manway cover. <I> **** Actions Taken **** Informed supervision and the weekend craft supervisor. | 02-00-AS-BLR-1
384591 | CR | 20180916 | CAQ | D | B5b-P-1 fuel oil level low. | N | Y |  | N | YES | <D> **** Detailed Description **** OPS-4 Sunday logs give the low spec. for B5b-P-1 ( Fire Truck ) fuel oil as " full ". The acutal level is 13/16. <I> **** Actions Taken **** E-mailed the fire marshal and FP trainer to inform them of the low level and notiify them that the truck needs to be filled on a weekday dayshift when resources support performing this task. Also included OPs supervisors on E -mail. <N> **** Equipment Description **** Bldg. 600. | 02-00-B5B-P-1
384592 | CR | 20180916 |  | 3 | Re-evaulate MS-RIS-610D impact to the Ops aggregate index |  |  |  | N | NO | <D> **** Detailed Description **** When MS-LIS-610D was placed in trip in response to the issuance of LCS 1.3.6.3 this changed from a back panel (BP) issue in the MCR to a front panel alarm (CA). This in on both P602 A-5 drop 2-2 and P 820 B-2 drop 10-1. Recommend changning the coding on this item (WR 29142536). This would be appropiate until MS-RIS-610D can be repaired or replaced. <I> **** Actions Taken **** Wrote this CR. Informed supervision. <N> This will not be changed from a BP designation. It fits the definition of a CA and now based on LCS, it will recieve the appropriate priority if broke. | 02-00-MS-RIS-610D
384593 | CR | 20180916 | CAQ | D | Flex buildings 82 and 600 have new locks |  |  |  | N | NO | <D> **** Detailed Description **** Flex building 82 and 600 have had new locks installed, both buildings contain large amounts of flammable liquid, should a small fire occur in one of these buildings the fire brigade leader would be delayed in both assessing the fire scene and combating the fire as no keys are assigned to any fire brigade personnel. Additionally the new locks have only 3 keys one of which is assigned to the control room, however PPM 1.3.23 the administrative control for plant keys does not reflect this additional key. This poor planning has created a situation in which a very unique key is not being audited for control. Recommend updating PPM 1.3.23 and assign keys to building 82 and 600 to fire brigade members. <I> **** Actions Taken **** Informed MCR <N> Duplicate of CR 384345 action already taken to address this.
384594 | CR | 20180916 | CAQ | D | SEC-IDS-16 17 Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** CAS recieved a malfunction alarm on IDS 16 &17. <I> **** Actions Taken **** Comp measures were posted. A walkdown was performed. Pole 153 has a broken insulator. Contact security for more information ext. 2185 | 02-00-SEC-IDS-E/S/16/17
384595 | CR | 20180917 |  | 4 | Right ground brush on the generator shaft need replacing | N | N |  | N | YES | <D> **** Detailed Description **** Right ground brush on the generator shaft need replacing. brush is worn down to the metal base. please see pictures attached. <I> **** Actions Taken **** wr/cr <N> **** Equipment Description **** Right ground brush on the generator shaft | 02-00-E-GEN-1
384596 | CR | 20180917 |  | 4 | Camera Cleaning | N | N |  | Y | YES | <D> **** Detailed Description **** Securtity cameras needing cleaning inside PA and around ISFSI <I> **** Actions Taken **** List generated from CAS, notified supervision, CR/WR generated <N> **** Equipment Description **** Cameras needed to be cleaned: CCTV 01, CCTV 13, CCTV 12, CCTV 10, CCTV 08, CCTV07, CCTV 12, CCTV 21 CCTV 20T, CCTV 33T, CCTV 42,CCTV 43, CCTV 45, CCTV46 CCTV48
384601 | CR | 20180917 |  | 4 | Records submitted without signed transmittal |  |  |  | N | NO | <D> **** Detailed Description **** A Large stack of records was sent to Records Control without a signed transmittal by Chemistry. Please follow swp-rec-02 Section 4.3.2 for the submittal process. <I> **** Actions Taken **** Notified my supervisor. Sending records back to Chemistry Department for correction/resubmittal.
384602 | CR | 20180917 | CAQ | D | SW-V-634 could not be opened to support clearance. | Y | N |  | N | YES | <D> **** Detailed Description **** SW-V-634 could not be opened to support a clearance. <I> **** Actions Taken **** Wrote CR to document issue. | 02-00-SW-V-634
384603 | CR | 20180917 |  | 4 | OG-TR-640B PT1 failed upscale at 0330 9/17/18 | N | N |  | N | YES | <D> **** Detailed Description **** OG-TR-640B PT1 has failed upscale. This now means that of the 4 OG dryer outlet temperatures 1 has indication. Verified that E-PP-5DA/6 was closed. This could be a problem with the TE or the common power suppily, or the mV converter for the indication. This indication is used to verify that OG has achieved a proper temperature during regeneration and cooldown. <I> **** Actions Taken **** Informed Supervision, Wrote this CR. | 02-00-OG-E/S-B2,02-00-OG-MV/I-20D,02-00-OG-TE-50B,02-00-OG-TR-640B
384610 | CR | 20180917 |  | 3 | OI-41 revision needed due to LCS change |  |  |  | N | NO | <D> **** Detailed Description **** The LCS has been revised to add 1.3.6.3 for the Main Steam Line Radiation Isolation Instrumentation. OI-41 currently shows no TS/LCS or ODCM applies for MS-RIS-610A - D in att. 7.4. The LCS attachment needs to be updated to reflect the new LCS requirements for the instrumentation. <I> **** Actions Taken **** Initiated CR | 02-00-MS-RIS-610A,02-00-MS-RIS-610B,02-00-MS-RIS-610C,02-00-MS-RIS-610D
384611 | CR | 20180917 | CAQ | D | FP-V-40 has a .5 gal/min packing leak | N | Y |  | N | YES | <D> **** Detailed Description **** Discovered FP-V-40 had an approx 0.5 gal/min packing leak. <I> **** Actions Taken **** Informed MCR and laborers. Adjusted packing 5 flats to stop the leak. <N> **** Equipment Description **** TG 441 A1 stairwell | 02-00-FP-V-40
384613 | CR | 20180917 |  | 4 | Almost parked in a walkway - poorly marked lines |  |  |  | N | NO | <D> **** ANONYMOUS CR - Detailed Description **** Dang near parked in a walkway in the main parking lot...the paint lines are worn and hard to see the locations were the walkways are marked. Consider repainting the walkways at a minimum. <I> **** Actions Taken **** Realized the error prior to completion of the parking activity and parked elsewhere. <N> ANON CR written, moved to SRO.
384614 | CR | 20180917 |  | 3 | Procedure change needed - ISP-APRM/RRC-B304 |  |  |  | N | NO | <D> **** Detailed Description **** Procedure change needed - ISP-APRM/RRC-B304. During the performance of ISP-APRM/RRC-B304 an error on multiple pages was found; message: Error! Reference source not found. Error message occured in pages 10, 12, 20, 22, and 23. <I> **** Actions Taken **** Supervision contatcted, SM concurrence on editorials in the PPM, CR generated and PPM wirter contacted for support.
384615 | CR | 20180917 |  | 4 | Door S103 has a broken Door Handle (Fire Door) | N | N |  | N | NO | <D> **** Detailed Description **** -Door S103 (located in the GSB Yakima BLDG) has a broken Door Handle. This is a Fire Door. (See Attached EDMS) <I> **** Actions Taken **** -Initated Condition Report & Work Request. <N> **** Equipment Description **** Yakima Building (GSB) Door S103 | 02-00-S-DOOR-S103
384616 | CR | 20180917 |  | 3 | *ALARA suggestion* R24 shield N6A with Magnetic shielding |  |  |  | N | NO | <D> **** Detailed Description **** ALARA should perform a cost/dose savings benefit of purchasing pre- cut tungsten magnetic shielding for the N6A Nozzle for use during R24. There is an extensive amount of work on and around this nozzle during R24. The area around this nozzle is cramped, if the first layer of shielding was substituted for pre-cut magnetic style it would save installation / removal time and dose. The per-cut magnetic shielding should be more effective at reducing the contact and general area dose rates in the area.due to a better fit and the shielding properties of this type of shielding. If this proves to be cost effective precut magnetic shielding for addition nozzles should be in ALARAs budget for future outages ALARA and the laborers can mock up installation on our nozzle mock- up to determine the time savings vs hanging and tie-wrapping lead blankets on an unshielded nozzle. <I> **** Actions Taken **** notified ALARA dept.
384617 | CR | 20180917 | CAQ | C | APRM-CHS-4 test current display found out of tolerance | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of ISP-APRM/RRC-B304 under WO 02100569 01 the test current displayed was out of tolerance per step 7.5.16 <I> **** Actions Taken **** Stopped, contacted CRS, made note on the cover sheet, calibrated into tolerance per procedure, and initiating this CR to document. <N> **** Equipment Description **** 501 RW CR <R> REP/REGE assignments were cancelled with Compliance Concurrence. | 02-00-APRM-CHS-4
384618 | CR | 20180917 | CAQ | D | SW-V-4B packing gland extremely difficult to move. | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02106765 it was discovered that the packing gland was extremely difficult to remove. Once the gland was removed from the box it was noted that some of the inconel packing wires were caught/ embedded on the inside diameter of the gland making movement of the gland very difficult. The valve needs to be disassembled to replace the packing gland. The valve is being restored to as found condition until it can be fully disassembled to correct this problem. Due to the packing gland being so tight on the stem and the prospect of the lantern ring being in the same condition as the gland, it is not recommended repacking as there was no sign of leakage from the packing area and the packing components cannot be replaced or fixed until disassembly. When the valve does get disassembled, the stuffing box will need to be machined or bonnet replaced and the stem needs to be replaced. <I> **** Actions Taken **** Informed Supervisor and OCC / WWM. <N> **** Equipment Description **** D443 R9/8.0 (DG2) | 02-00-SW-V-4B
384619 | CR | 20180917 | CAQ | D | DG-4 Needs painting | N | Y |  | N | YES | <D> **** Detailed Description **** The outside of DG-4 s showing some rust threw the paint. Shuold be painted befor this fall so that it is protected from the cooling tower mist. <I> **** Actions Taken **** Contacted my supervisor. Initated this CR <N> **** Equipment Description **** outside south of dg's | 02-00-E-GEN-DG4
384620 | CR | 20180917 | CAQ | D | SW-RLY-V/2B4 as found out of tolerance | Y | N |  | N | YES | <D> **** Detailed Description **** While performing WO#02114330-01 SW-RLY-V/2B4 as found was out of data sheet tolerance. The as found time of 12.86 didnâ€™t meet data sheet tolerance of 13.25-14.75. Three subsequent tests met the data sheet tolerance, with no adjustment needed. Relay function as intended, just the as found data did not meet data sheet tolerance. <I> **** Actions Taken **** Notified supervision and operations | 02-00-SW-RLY-V/2B4
384621 | CR | 20180917 | CAQ | C | SW-V-730 up stream sockolet as found condition | Y | N |  | N | YES | <C> Re-assigned to SENSSS at the request of ENG. <D> **** Detailed Description **** the sockolet up stream of SW-V-730 only has a 1/4" of insertion. The welding PPM requires 3/8" insertion of the 3/4" pipe. This is item 12 on drawing SW-1036-1 <I> **** Actions Taken **** Contacted engineering and OCC | 02-00-SW-V-730
384625 | CR | 20180917 |  | 4 | R24 HIT Lead Mtg Attendance Inadequate |  |  |  | N | NO | <D> **** Detailed Description **** The R24 HIT Lead meeting held on 9/17/18 had inadequate attendance from several key groups (Rx Maint, CPM, and RP). Attendance by the key stakeholders is mandatory. Should a representative be unable to attend, it is their responsibility to verify an alternate will attend in their place and communicate effectively with the Outage organization. <I> **** Actions Taken **** Coaching provided by the Outage Manager.
384626 | CR | 20180917 | CAQ | D | SW Peroxide treatment skipped | Y | N |  | N | NO | <D> **** Detailed Description **** Due to the SW-B safety system window, the service water pumps were not started for a peroxide addition on 9/17/2018. No peroxide treatment of the SSW system was performed. Treatment is planned to resume on 9/20/2018. <I> **** Actions Taken **** Discussed with Chemistry. Recommend for trending | 02-00-SW-PIPE-MISC
384627 | CR | 20180917 |  | 3 | (NRC-2018RP) Question regarding SCBA hydrostatic inspections |  |  |  | N | NO | <D> **** Detailed Description **** During the 2018 Radiation Safety Inspection, an inspector was conducting a walkdown of the TG Building and Main Control Room and noted three of the staged SCBA bottles had stamped hydrostatic inspection dates past the 5-year OSHA requirement. These bottles are numbered OK374018 (location Main Control Room, put into service on 04/2010 and inspected on 03/2016), OK158999 (location TG 501â€™, put into service on 01/2006, inspected 01/2011 and last inspected 03/2017) and OK170704 (location TG 501â€™, put into service on 05/2006, inspected 06/2011 and last inspected 03/2017). All bottles currently meet requirements, this is a legacy issue. <I> **** Actions Taken **** Discussed question with Radiological Support Supervisor, Radiation Protection Manager, Licensing and Control Room. Recommend a Priority NCAQ Severity 3 to AR-RPSPT to conduct extent of condition and establish a process to document out of service time for SCBA bottles while they await inspection.
384628 | CR | 20180917 | CAQ | C | Clams found in the Service Water Spray Pond B | Y | N |  | N | NO | <D> **** Detailed Description **** While dredging the Service Water Spray Pond B, the divers discovered clams on the bottom of the spray pond. Clams were found, on average, approximately 1 clam every 16 sq ft (4x4). Clams are average about 0.5 in in height. Upon discovery, clams are removed along with the rest of the sediment in the spray ponds during the dredging process. One of the clams pulled from the pond was transported to chemistry for further evaluation and characterization. <I> **** Actions Taken **** Contacted SM and discussed with Supervisor.
384629 | CR | 20180917 |  | 3 | Exam Failure - ES000508 - ESP Orientation |  |  |  | N | NO | <D> **** Detailed Description **** One student failed the ES000508 - ESP Orientation exam conducted on 9/17/18. This CR is being writter per direction of TDI-02, Rev 35, section 4.4.10.p.3 <I> **** Actions Taken **** Notified appropriate line and training supervisors.
384630 | CR | 20180917 |  | 3 | ENG-DES-50 update to remove remaining references to DES-2-16 |  |  |  | N | NO | <D> **** Detailed Description **** Despite a previous minor revision (major rev 001 minor rev 001) intended to delete references to DES-2-16, ENG-DES-50 Attachment 7.1 (pg 30 and pg 31 of ENG-DES-50 major rev 001 minor rev 002) continues to reference DES-2-16 as a CGS interfacing instruction associated with PPM 1.3.9 Temporary Modifications. DES-2-16 is status HISTORY in Asset Suite Portal J and no longer used. An update for ENG-DES-50 should be processed to remove its remaining references to the DES-2-16 instruction.
384631 | CR | 20180917 | CAQ | D | Door C223 door stop bracket bolt broken. | N | Y |  | N | YES | <D> **** Detailed Description **** Found bracket with broken bolt and bolt stuck inside threaded hole. Rest of bolt was on the ground, this does not impair the door functioning. <I> **** Actions Taken **** Informed CRS & SSS. Initiated AR. Notified Security (x2185). <N> From the photo attached to the EDMS, the broken bolt is associated with the latch guard for the door. | 02-00-W-DOOR-C223
384632 | CR | 20180917 |  | 4 | Stairwell emergency light has a lamp fault. | N | N |  | N | YES | <D> **** Detailed Description **** Discovered Northwest 522 Emergency light with a error of 5 blinks meaning a lamp fault. <I> **** Actions Taken **** Initiated AR, informed SSS. | 02-00-E-BU-SWS3/5
384633 | CR | 20180917 |  | 3 | DES-4-11 Procedure needs to be updated |  |  |  | N | NO | <D> **** Detailed Description **** During preparation of a revision for Electrical Engineering Calculation 2.06.20 (Calculation for Cable Ampacity Verification for Scheduled Power Cables), it was noted that section 7.1 includes two calculations that are no longer treated as Working Copy calculations (E/I-02-92-14 and ME -02-92-43). The intent of this CR is to document this discrepancy and to drive changes to DES-4-11 to only include calculations 2.06.20 and E/I-02-90-01 as Working Copy calculations. In addition, as part of the update to DES-4-11, this CR will support a verification of the CMR policy presented in DES-4-1 and reflected in DES-4-11. For completion, please assign this CR to Electrical and I&C Design (AR-DEI). <I> **** Actions Taken **** Wrote CR Confirmed that E/I-02-92-14 and ME-02-92-43 have no GT 5 Modified status CMRs, in accordance with DES-4-1 CMR Policy.
384634 | CR | 20180918 |  | 4 | Add quick disconnects to SW-V-702B for Testing | Y | N |  | N | NO | <D> **** Detailed Description **** This WR is for configuration control of quick disconnects installed to support OSP-SW/IST-Q702 and to remove the disconnects after the completion of OSP-SWIST-Q702. <I> **** Actions Taken **** Wrote this CR <N> **** Equipment Description **** SW-V-702B | 02-00-SW-V-702B
384635 | CR | 20180918 | CAQ | D | SW-V-197 appears clogged; no water came out during tagout | Y | N |  | N | YES | <D> **** Detailed Description **** SW-V-197 was clogged and no water came out during tagout D-SW-V-4B-001 | 02-00-SW-V-197
384636 | CR | 20180918 | CAQ | D | SW-V-196 was clogged and no water came out during tagout | Y | N |  | N | YES | <D> **** Detailed Description **** SW-V-196 was clogged and no water came out during tagout D-SW-V-4B-001 | 02-00-SW-V-196
384637 | CR | 20180918 | CAQ | D | SW-V-611 was difficult to operate | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02080115, then taken back to complete <D> **** Detailed Description **** SW-V-611 was difficult to operate. Valve was opened during D-SW-V-4B-001 tagout and only went open 2.5 turns begrudgingly the sound of air sucking told us we had accomplished out goal of opening it but didnt feel full open. <I> **** Actions Taken **** wrote CR WR | 02-00-SW-V-611
384638 | CR | 20180918 | CAQ | D | SW-V-634 was unable to be opened for tagout | Y | N |  | N | YES | <D> **** Detailed Description **** SW-V-634 was unable to be opened for tagout D-SW-V-155T -001. Valve opened 1/2 of a turn and then would not go further. More torque was deemed as not appropriate due to the implications of damage to valve and system operability. <I> **** Actions Taken **** team enlarged, valve reshut that 1/2 a turn | 02-00-SW-V-634
384639 | CR | 20180918 | CAQ | D | FPC-P-1A seal leakage degrading | N | Y |  | N | YES | <D> **** Detailed Description **** FPC-P-1A outboard mechanical seal leakage is sufficiently bad now that water droplets are flung at least 5' high at the personnel access to the remainder of the room, this will become a personnel contamination risk. Recommend repair to prevent personnel contamination. <I> **** Actions Taken **** Informed MCR. Generated AR/WR. | 02-00-FPC-P-1A,02-00-R-BLDG-MISC
384640 | CR | 20180918 |  | 3 | (procedures) SOP-RW/FDR-OPS index page is wrong |  |  |  | N | NO | <D> **** Detailed Description **** SOP-RW/FDR-OPS index page is wrong. index page list attachment 6.1 as page 48 but it is actually page 49. Since most procedures sectios are printed from the index page this waste paper when it is discovered that its wrong. Please verify last rev did not affect other poertions as well. <I> **** Actions Taken **** cr
384643 | CR | 20180918 |  | 3 | Amend SOP-OG-OPS due to degraded temperature monitoring |  |  |  | N | YES | <D> **** Detailed Description **** Please consider amending SOP-OG-OPS due to degraded temperature monitoring. Currently, three of the four Offgas Dryer regeneration temperatures denote off scale high. OG-TR-640A Pt 1, OG-TR-640B Pt 1 & Pt 2 are failed high. OG-TR-640A Pt 2 is the only point that denotes actual temperature. SOP-OG-OPS should be amended to regenerate a dryer based on time rather than temperature. Suggest at least a twelve hour regeneration time. Years ago, we used time to support regeneration when temperature monitoring became unavailable. <I> **** Actions Taken **** Notified the SM. The next outlet moisture high alarms may be received in 3 â€“ 5 days, so amendment should be completed before the alarms are received. Engineering consultation may be required to ensure an adequate regeneration is achieved. | 02-00-OG-TR-640A,02-00-OG-TR-640B
384644 | CR | 20180918 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0067684 Mitutoyo OD Mic- model 103-260 0-1" found OOT & adjusted within specs. Not used during Calibration cycle. DEF #6739A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
384648 | CR | 20180918 |  | 4 | Security rifle aimpoint not operating as designed |  |  |  | N | YES | <D> **** Detailed Description **** Security aimpoint optics on rifle #370 is not operating by design and needs maintenance. Contact Paul Herod at #1032. <N> **** Equipment Description **** Security rifle aimpoint on Rifle 370 in Building 88. #1032
384649 | CR | 20180918 | CAQ | D | Recieved H13-P601-A1 Drop 5-8 HPCS suction pressure High/Low | Y | N |  | N | YES | <D> **** Detailed Description **** Received H13-P601-A1.5-8 HPCS suction pressure high/low alarm which immediately cleared. No operations are in progress that should have produced this alarm (HPCS is protected). Dispatched Ops-2 to investigate. Reviewed HPCS pump discharge pressure trend on TDAS (there are suction pressure points), there was a small rise in HPCS system pressure coincident with the suction pressure alarm but the variation was well within the normal daily variation based on historical TDAS data. Ops-3 reported that HPCS-PIS-3 reads 18 psig which is a normal reading and well within the 5 psig and 80 psig low and high pressure setpoints. HPCS keep fill pump was checked and is operating normally. A check valve separates the keep fill pump and the monitored discharge pressure from the suction pressure PIS so these indications are of limited value in evaluating the cause of the momentary alarm. Recommend this be investigated and corrected as needed. <I> **** Actions Taken **** Dispatched operator. Verified that HPCS sution pressure normal. Wrote this CR. | 02-00-HPCS-PIS-3
384655 | CR | 20180918 |  | 4 | Security XD 9 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security XD 9 computer screen is inoperable and needs maintenance. Contact 2185 for details. <I> **** Actions Taken **** Security supervision notified. CR/WR initiated. Equipment taken out of service. | 02-00-SEC-XD-9
384656 | CR | 20180918 |  | 4 | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0060879 Biddle Megger- model BM11D Passed Calibraiton- but now Rejected due to battery not holding charge (was replaced & still not holding charge). DEF #6740A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
384657 | CR | 20180918 |  | 3 | HU Improvement for Operations Phone Contact |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate the value in changing the contact phone numbers for the important operations phone numbers to make them sequential and easy to remember. x1231,x1232, x1233, x1234 This will allow quick access to dial the shift manager, CRS RWCR, ect... without having a quick access card. this will allow faster response for individuals to place a call in situations that don't require the x2222 number. I previously discussed this with Operation Manager. IS and Operations should review if this is possible to impliment before the outage and determine if there is value from a HU standpoint of a improvement in plant safety. A good example as presented in the D15 was the TSW leak last week. Individual in the field did not have a quick reference card and had to pause to think which number to call or to use x2222. <I> **** Actions Taken **** generated CR to track resolution/evaluation
384658 | CR | 20180918 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0063823 Heise Pressure Calibrator- model PTE-1 found OOT and adjusted within specs. Not used in the OOT range of 5V, 10V and 20mA. No Plant Impact. DEF #6741A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
384659 | CR | 20180918 |  | 3 | Procedure change to OSP-SW-M102 |  |  |  | N | NO | <D> **** Detailed Description **** During performance of OSP-SW-M102 as part of the annual SW-SYS-B outage, a question arose concerning the required line up. This delayed completion during a 72 hour LCO. Clarification in the procedure could have avoided the delay. See EDMS for detail. <I> **** Actions Taken **** Completed surveillance. Generated CR.
384660 | CR | 20180918 |  | 4 | Degraded sidewalk N. of bldg. 88 near BRE 34 photos in EDMS |  |  |  | N | NO | <D> **** Detailed Description **** A small section of the sidewalk near BRE 34 is damaged. This creates a potential trip hazard and needs remediation in a timely matter. <I> **** Actions Taken **** Informed Facilities, had a deligneator/ cone placed on the damaged section of the sidewalk. Wrote this CR/ work request and attached photos in EDMS. <N> **** Equipment Description **** Near BRE 34 just N. of bldg. 88 inside the protected area. See the photos for location and details.
384661 | CR | 20180918 | CAQ | D | Reactor Building (RB) Roof Repairs | Y | Y |  | N | YES | <C> CR reopened to cross reference additional WR 29129027, then taken back to complete <D> **** Detailed Description **** In preparation for demobilization of the RB platform work area it was noted that several previous roof repairs outside of the platform work area were degraded. The areas in question were repaired with what look to be silicon Calk and the Calk was pealing up from the EPDM roof surface. These area are surface cut on the EPDM roof liner. None of these were deep cut but left exposed to water freezing action over time could begin to erode the liner and cause leaks. . None of these were deep cut but left exposed to water freezing action over time could begin to erode the liner and cause leaks. <I> **** Actions Taken **** Generated the AR/CR to document condition. Need a WR. <N> **** Equipment Description **** Reactor Building Roof East 20 foot of the building. | 02-00-R-BLDG-MISC
384664 | CR | 20180918 |  | 3 | Revision 016 for MOT-DIESEL-1-1 |  |  |  | N | NO | <D> Revision 016 for MOT-DIESEL-1-1 was not submitted to Document Control for Issuance. <I> MOT-DIESEL-1-1 Revision 017 returned to Engineering/System. <N> CR at INPROG, moved to APPROVED status.
384665 | CR | 20180918 |  | 4 | Shaft Guard needs removed from area |  |  |  | N | YES | <D> **** Detailed Description **** During walkdown it was discovered that pump shaft guard previously installed and determined to be a temp mod is still in the plant. Engineering previously reviewed and determined that the guard was not required per WAC and a design change would not be warranted based on impact to plant personel who rarely work in the area. Please remove the sheet metal guard so it can not be used. It is currently stored under the back side of the pump case. <I> **** Actions Taken **** Wrote CR, Notified CR. <N> Correction on original CR verbage. The guarde was never a temporary modification. It was previously found and recommended for evaluation as it was an unauthorized modification. The evaluation determined that it was not required. | 02-00-R-BLDG-MISC,02-00-RCC-P-1A
384667 | CR | 20180918 | CAQ | C | Rx Bldg Stack Critical Failure alarm In and Clear | N | Y |  | N | YES | <D> **** Detailed Description **** Received â€œReactor Building Stack Critical Failureâ€ alarm (H13-P851.S2.2-4) in and clear. Attempted to identify the source of the alarm on the Event Logs Detail Screen per the ARP, but there were no recent non-routine entries recorded. | 02-00-PRM-RIS-1
384668 | CR | 20180918 | CAQ | D | DG2 Walkdown observation, electrical | Y | N |  | N | YES | <D> **** Detailed Description **** Located near/below the generator shaft guard there is a coated flexible steel cable conduit which has cracked. The DG room is qualified for seismic and not HELB. Per the EQ engineer this is acceptable as there is not a concern of moisture instrusion. Recommend electricians evaluate for removal or repair. <I> **** Actions Taken **** Notified CR, FIN | 02-00-D-BLDG-MISC,02-00-DG-ENG-1B2
384670 | CR | 20180918 |  | 4 | TMU-P-1A would not start. | N | N |  | N | YES | <D> **** Detailed Description **** TMU-P-1A would not start. 2 attempts were made to start TMU to support of WO 02086851 (TMU-P-1B pump lift adjustment). It appears that TMU-FIS-5A is not functioning correctly to allow TMU-P-1A to start. TMU-P-1A was placed back in a stand by condition and the guidance in SOP-TMU-START P&L 4.13 was followed to de-energize TMU-RLY-62/P-1A with the fuses reinstalled. <I> **** Actions Taken **** Informed Supervision. FIN SRO and FIN electrial supervisor informed failure of pump start. | 02-00-TMU-FIS-5A,02-00-TMU-P-1A
384672 | CR | 20180918 |  | 4 | Found CPR-LIS-97A out of tolerance | N | N |  | N | YES | <D> **** Detailed Description **** While performing 02124472-01 CPR-LT-98A loop cal found CPR-LIS-97A out of tolerance the worst point was 75% and it was indicating 5% high. <I> **** Actions Taken **** only ajustment is the zero and would not bring it into specicfication. LIS needs to be replaced <N> **** Equipment Description **** RW control room | 02-00-CPR-LIS-97A
384673 | CR | 20180918 |  | 3 | Typo in calculation AED CAL 5.32.10 rev 002 |  |  |  | N | YES | <D> **** Detailed Description **** Calculation 5.32.10 revision 002 has a typo on page 2 of 6. The indicated calculated value of M for SA 134 A283 Gr C material at 309 psi is 0.01151. Running the numbers, the correct value for this M is actually 0.01511. This is a completely inconsequential typo with respect to the results of the calculation as the correct value for M (i.e., M = 0.01511) is actually used in the body of the calculation. Additionally, there is a minor pagination issue with this calculation (currently, there is no page 3 of 6 and there are two page 5 of 6 sheets). See the mark-up of AED CAL 5.32.10 R002 attached to the EDMS of this AR CR for suggested corrections. This is a legacy issue and is completely inconsequential to the calculation result - suggest nonCAQ resolution to Design Engineering. <I> **** Actions Taken **** Initiated this AR CR 384673. This was noted as a result of documentation reviews associated with OCC directed preparation activities for contingency EC DEC TMOD 17399. | 02-00-SW-PIPE-MISC
384675 | CR | 20180918 |  | 4 | Individual allowed to miss Pre-License Class (risk decision) |  |  |  | N | NO | <D> **** Detailed Description **** An individual was allowed to miss the Pre-License class for Operations ILC-24. This decision was made by Operations and Operations Training based on business needs and the specific individuals history and proven ability to obtain a license. <I> **** Actions Taken **** Initiated CR for trend. OI-27 requires a pre-License class to be used as a screening tool for ILC candidates.
384677 | CR | 20180918 |  | 4 | Source Locker Located in RW 525 will not open | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While attempting to return source 10-197 to its storage location in the RW 525 I/C storage locker the lock was unable to open. The locker is empty and source 10-197 is temporarily being stored in HP-1 storage locker located in RW 487â€™. <I> **** Actions Taken **** Contacted the source custodian and supervision, noted on the RW 525â€™ storage locker source check out log that source 10-197 is being stored in the HP-1 locker located in RW 487â€™. Source 10-197 is not classified as SNM. A work request will be generated to repair/replace the combination lock on the source locker located in RW 525 I/C shop. <N> **** Equipment Description **** Source Locker RW 525 I/C Shop
384678 | CR | 20180918 |  | 3 | Calculation AED CAL 4.21.04 for TMU-EJ-1A(B,C) | N | N |  | N | YES | <D> **** Detailed Description **** Calculation AED CAL 4.21.04 page 6 of 6 determines predicted axial and lateral thermal movements for the large bore (24" and 42" diameter) TMU pump discharge piping downstream of expansion joints TMU-EJ-1A(B,C) (reference CVI DWG 225-02,28). Currently, the calculation does not consider the effects of existing large bore pipe supports TMU-1, TMU-917, or TMU-918. Reference hanger isometric CVI DWG 225-08,32,1. TMU-1 (CVI DWG 225-08,26) and TMU-917 (CVI DWG 225-08,43) are 3-WAY restraints (vertical, N-S lateral, and E-W lateral) for the 24" diameter TMU lines near TMU-EJ-1A and TMU-EJ-1B. TMU-918 (CVI DWG 225-08,44) is a 2-WAY (vertical and N-S lateral) restraint under the 42" x 24" reducer for the TMU line near TMU-EJ-1C. Supports TMU-1 and TMU-917 will result in reduced axial and lateral displacements for TMU-EJ-1A and TMU-EJ-1B and will result in reduced axial displacements for TMU-EJ-1C. . The calculation should be updated by Design Engineering to consider the effects of these existing large bore pipe supports to re-verify acceptability of TMU-EJ-1A(B,C). . Additionally, CVI DWG 225-02,28 for TMU-EJ-1A(B,C) does not indicate whether or not an axial gap exists between the Item 6 axial rod nuts and the outside faces of the Item 4 axial rod lugs. It appears that a small gap should be present (particularly for TMU-EJ-1C) so that axial thermal contraction of the TMU pump discharge piping during the winter months will not result in axial loading of the TMU pump discharge nozzles. Please temporarily remove the existing insulation pads surrounding TMU-EJ-1A(B,C) for Design Engineering so that the field configuration of their axial rods can be verified. This information will need to be incorporated into the update for AED CAL 4.21.04 by Design Engineering and may need to be indicated on CVI DWG 225-02,28. . Whatever may be identified when the TMU-EJ-1A(B,C) insulation pads are removed (i.e., axial rod gaps as anticipated vs. no axial rod gaps), the condition will have existed for decades and has not caused any actual functionality issues for TMU-EJ-1A(B,C) or TMU-P-1A(B,C). As such, there are no functionality concerns for the subject TMU expansion joints, their associated TMU system pumps, or any other station SSCs associated with this AR CR 384678. . Recommend resolution of this legacy issue to Design Engineering for update of AED CAL 4.21.04. <I> **** Actions Taken **** Discussed with supervision, the Design Engineering Mechanical/Civil/Stress DA, the Pump Program Engineer, and the TMU System Engineer. | 02-00-TMU-EJ-1A,02-00-TMU-EJ-1B,02-00-TMU-EJ-1C
384680 | CR | 20180918 |  | 3 | Incorporate cycling of MBS breakers into SOPs for inverters |  |  |  | N | YES | <D> **** Detailed Description **** The following PMIDs will be cancelled and the required steps will be added to the operating procedures for the E -IN-1, 4 and 5 to ensure that the MBS breakers are cycled at the static switch on a routine basis. AR-SMS 384679 was generated to cancel the PMs and to update the MOT for each static switch for cycling its breakers. By completing this work through the SOPs it will have little impact on the operations crews and it will allow operations to complete this work on a more frequent basis and within a controlled procedure then by the existing PMIDs. Below are the PMIDs that will be cancelled as part of this AR-CR under AR-SMS 384679 PMID 25913-01 (E-MBS-IN1/1) PMID 25915-01 (E-MBS-IN5/1) PMID 25914-01 (E-MBS-IN4) <N> Recommend assignment to operations procedures. T. Mclaen | 02-00-E-MBS-IN1/1,02-00-E-MBS-IN4,02-00-E-MBS-IN5/1
384681 | CR | 20180918 | CAQ | D | Spray nozzle plugged | Y | N |  | N | YES | <D> **** Detailed Description **** A single spray nozzle on the SSW B spray ring header in the SSW A spray pond was clogged, allowing less than full flow through the nozzle. This nozzle was located about half way up the spray ring in the north east quadrent of the spray ring. This was identified as part of step 7.3.13 of OSP-IST-Q702 <I> **** Actions Taken **** Informed the MCR/CRS. No other nozzles indicated degraged flow <N> **** Equipment Description **** SSW B spray ring headwer nozzle
384682 | CR | 20180919 | CAQ | D | IDS 24 25 Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** IDS 24 25 are not functioning as designed. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervision notified. Initiated CR/WR <N> **** Equipment Description **** IDS 24 25 | 02-00-SEC-IDS-E/S/24/25/26
384683 | CR | 20180919 | CAQ | D | IDS 24 25 constant malfunction | N | N |  | N | YES | <D> **** Detailed Description **** IDS 24 25 constant malfuntion <I> **** Actions Taken **** Security conducted a walk down of the zones and found debris and copious amounts of spider webs. The debris was removed but the zones remained in alarm. zones are being comped, generated CR/WR, contacted plant electricians | 02-00-SEC-IDS-EVAL/24/25
384685 | CR | 20180919 |  | 3 | Work orders at H/OPS not on ops close out screen |  |  |  | N | NO | <D> **** Detailed Description **** WO's 02101857, 02101885, and 02108902 are at hold for ops but dont show up on the Dataglance OPS closeout screen. . Please fix this problem <I> **** Actions Taken **** Wrote CR <N> WO 02108902 was taken to working on 10/12/17 and was not in DataGlance. The Shop Tech Support Specialists are tasked with closing out old WO Packages and, in this case the WO was Finished and it went to H/OPS for Operability. Since this WO isnâ€™t in DataGlance it will not be on the Ops Closeout screen. . WOs 02101857 & 02101885 are at a DataGlance Status (Ops Review Complete) that we don't have the ability to complete and closeout the package. This is happening is due to the way EN wanted the package to be reviewed and released for operability prior to the package being reviewed by the Supervisor. With the next release of DataGlance it provides the ability to change statuses, so that the package can be set to â€œSupervisor Reviewâ€ from â€œOps Review Completedâ€. . Hard copies of the packages have been printed and given to the shops for their review and then be sent to records. . CR has been cross-referenced to the DG upgrade project.
384686 | CR | 20180919 |  |  | OSP-INST-H101 surveillance SRO review not stamped in eSOMS |  |  |  | N | NO | <C> Canceled this CR at the request of the initiator as it locked up on him. Additional CR 384705 was generated. <D> The night shift OSP-INST-H101 SRO review was not stamped in eSOMS. This was noticed by the oncoming dayshift CRO2. Upon discussion with the off-going shift manager, the surveillance had been reviewed by the CRS within the required surveillance periodicity but had not been stamped as complete in eSOMS. <I> Shift manager informed. Oncoming CRS reviewed OSP-INST -H101 and acknowledged SRO review in eSOMS.
384694 | CR | 20180919 | CAQ | C | (2018 FSA PI&R) CRs not being initiated in some cases | N | N |  | N | YES | <D> **** Detailed Description **** PI&R Self-Assessment Objective 2: Validate that issues are identified and addressed appropriately in a timely manner commensurate with their safety significance . Deficiency: Reviewed 29 DN, DC, CN, CC type WOTs completed in past 2 years. 24 WOTâ€™s did not document any new issues or concerns. One WOT identified an issue and a new CR was generated. Four WOTâ€™s had additional or new concerns/issues documented, but no new CRâ€™s were generated or could not be found. 2 of those issues were addressed under the WO or other process; 2 of the identified issues were not addressed further. Examples: . 02132272 CN 5/MUX2CMS-TR-5/mux1 and CMS-TR-5/mux2 have fail lights The Limitations on Use LOU for the replacement power supply states that reforming the capacitors would be required. An email discussion between technicians and procurement engineer concluded that it is suitable to waive that LOU requirement to reform the capacitors. That determination is documented in the email from the engineer and included in the WOT package. However, this exception to the LOU requirement should be documented in a CR along with the resolution for traceability in the future, and for revising the LOU requirements to include the criteria and basis for the exception. [resolved in the WO process] . 02126372 DN E-TR-4AA/1 REPLACE TRANSFORMER The craft performing the work identified a possible discrepancy regarding how the transformer was to be mounted. In question was a Â¼ inch clearance shown on a controlled drawing, and the new mounting plate would not allow for that Â¼ inch clearance. This issue was resolved through the ENG assignment on AR378488. . 02116797 DN REPLACE PRM-REC-1C During replacement, the first new cryostat from warehouse â€œwould not cool downâ€ per the technician notes (New cryostat SN P0-346666-02-01 UTC 546191). Another new cryostat was procured from stock (UTC Nbr: 0000524651 Trace: S 51-TP13099A) and installed with no further issues. However, the first cryostat that was obtained and did not cool down should have been identified in a CR for further evaluation as to why it was not functioning correctly. There was no additional information in the WOT to document what additional actions (if any) were taken to address the first cryostat cool down issues. This issue does NOT affect installed plant equipment. . 02122954 DN ROA-AD-1A LINKAGE REPAIR (GRINDING/WELDING) In the closure notes of the WOT the craftsman stated â€œPer conversation with management and engineering, installed assembly with #9 damper having damage and not quite full closed.â€ A CR was not found for this condition, and further actions addressing this condition could not be found. PMT task 18 closure notes states â€œROA-AD-1A OPERATION SAT, PMT SATâ€. . The first two examples above were resolved within the work order itself or other plant processes. The last two examples were not resolved, and a CR could not be found that addressed the issue. . See XRefs for affected WO Tasks <I> **** Actions Taken **** Discussed with focused SA team to validate information . Recommend severity C to maintenance to review and evaluate the issues identified. SM evaluated the last two items - PRM-RE-1C - equipment not installed in the plant. ROA-AD-1A - not TS nor non-TS equipment. | 02-00-ROA-AD-1A
384695 | CR | 20180919 |  | 4 | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065648 Industrial Scientific Gas Monitor- model iTX was not used during Calibration cycle. Rejected- UUT No Longer Able to get O2 sensors. DEF #6742A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
384697 | CR | 20180919 |  | 3 | 2018 FSA PI&R Adherence to GBP-ASU-03 |  |  |  | N | NO | <D> **** Detailed Description **** A deficiency was identified when reviewing Objective 12 and validating self-assessment information. During the review it was identified that two of focused self assessment had SARC type assignments that were closed without first documenting owed to group manager approval which is not in alignment with GBP-ASU-03 section 4.12. The associated focused self-assessments have been cross referenced. <I> **** Actions Taken **** Notified team lead and initiate CR.
384701 | CR | 20180919 |  | 3 | E-CB-1/500S failed to Open | N | N |  | N | YES | <D> **** Detailed Description **** While attempting to open E-CB-1/500S using the switch in the MCR, the breaker failed to open. While its switch was actually being held in the TRIP position, the red indicating light went out, but the green light never came on. Upon the switch returning to center-neutral position, the red light came back on and the green light stayed out. This happened twice; two attempts at opening the breaker were made. | 02-00-E-CB-1/500S
384702 | CR | 20180919 |  | 4 | TMU-P-1A started and tripped. | N | N |  | N | YES | <D> **** Detailed Description **** TMU-V-1A failed to open on TMU-P-1A start causing the pump to start and trip on a 2 minute time delay. <I> **** Actions Taken **** Backod out of procedure. informed CRS/SM <N> **** Equipment Description **** tmu pumphouse | 02-00-TMU-P-1A,02-00-TMU-V-1A
384703 | CR | 20180919 |  | 3 | Procedure enhancement OSP-SW-M103 |  |  |  | N | NO | <D> **** Detailed Description **** Minimum flow requirements for HPCS-P-2 are not well known or documented. The requirement has been evaluated in a past CR (299342). Recommending adding P&L to OSP-SW-M103 to state the minimum flow requirement to improve communication and as a sustainable action to help ensure DCW-HX-1C work is done during paragon orange HPCS windows (as opposed to DG-3 windows). <I> **** Actions Taken **** Initiated CR
384704 | CR | 20180919 | CAQ | D | OSP-INST-H101 surveillance SRO review not stamped in eSOMS |  |  |  | N | NO | <D> **** Detailed Description **** The night shift OSP-INST-H101 SRO review was not stamped in eSOMS. This was noticed by the oncoming dayshift CRO2. Upon discussion with the off-going shift manager, the surveillance had been reviewed by the CRS within the required surveillance periodicity but had not been stamped as complete in eSOMS. <I> **** Actions Taken **** Shift manager informed. Oncoming CRS reviewed OSP-INST -H101 and acknowledged SRO review in eSOMS. Reviewed TS SR 3.0.3. Ensured the OSP-INST-H101 readings were completed within 24 hours of discovery (completed by 10:30 on 9/19/2018.). **H101's were reviewed at 2204 on 9/18, however the CRS signed the wrong day. There is documentation in esoms of his review and it was within the time requirements.
384705 | CR | 20180919 | CAQ | D | Jumping terminals on WOA-EHC-54B ref. CR 371070 | Y | N |  | N | YES | <D> **** Detailed Description **** Annual surveilance and thermography requires electricians to install a temporary jumper inside the heater control cabinet (points C1 to C3). Pamona banana jack need to be installed to minimize the difficulty and danger. This has already been done on WOA-EHC-54A ref. 02118824-01 <I> **** Actions Taken **** Photos taken and attached to EWP WO#02124704-02 <N> **** Equipment Description **** W525 'B' HVAC room south side 10' in overhead | 02-00-WOA-EHC-54B
384706 | CR | 20180919 |  | 4 | 2 Pieces of M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** 2 pieces of M&TE were found OOT & adjusted within specs. Neither were used during Calibration cycles. Calcode #0068780 Ashcroft Sensor- model HQS-2 300psig. DEF #6743A written. Calcode #0066401 Heise Dig. Gauge- model 901B 200psig. DEF #6744A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
384709 | CR | 20180919 | CAQ | D | SW-TE-1BR not able to be removed for WO 02109506 01 | Y | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02109506, then taken back to complete <D> **** Detailed Description **** WO 0210950601 is a repair task for SW-TE-1BR. The probe was unable to be removed due to what appears to be rust binding on a wire support bracket at the bottom end of the probe insert (probe is inserted underneath the deck of SW pumphouse B. <I> **** Actions Taken **** Notified I/C supervision. Retermed and restored the probe and initiated CR. | 02-00-SW-TE-1BR
384710 | CR | 20180919 | CAQ | C | (QA) Deficient supplier documents approved by EN |  |  |  | Y | NO | <D> **** Detailed Description **** This CR is for a safety-related pump being purchased, it does not affect any plant installed equipment. . Columbia Generating Station (CGS) is purchasing a replacement safety-related ASME Section III Class 3 (ND) diesel fuel oil transfer pump on Purchase Order (PO) 00348152. The supplier has submitted documents to CGS for review and approval as required by the PO instructions. The supplier completed Net Positive Suction Head (NPSH) testing to a Commercial Grade Dedication (CGD) plan that was approved by an EN person not qualified for approval of CGD activities as required per PQD Qualification ESEV. The CGD Plan is deficient in several areas, but specifically the dedication of the Measuring & Test Equipment (M&TE) used to generate the NPSH test data does not comply with the NRC accepted process for safety-related calibrations. The supplier also completed the NPSH testing at an unapproved location outside of their EN accepted program. Supply Chain Services has notified the supplier that the pump is not to be shipped to their offsite location for the subsequent pump curve testing until these issues are resolved. . Additionally, the supplier provided Bill of Material to CGS which identify some parts as non-safety related that are required to perform the credited plant safety function and were inappropriately approved by EN. <I> **** Actions Taken **** The supplier has been notified of the concerns with the M&TE dedication plan and parts classification. Wrote this CR to document improper approval of supplier documents and the potential for delays and rework costs. Recommend CAQ-C and assign to Engineering
384711 | CR | 20180919 | CAQ | C | (2018 FSA PI&R) Some issues in Logs not identified with a CR | N | N |  | N | YES | <C> Per request from Operations, reopened CR to include notes discussing no corrective action was required. Operations determined no correctve action was required for this AR. The action was ASGN that communicated the error to all of ops that was described in the AR. Decisiion was approved by J Jones. The CR can be closed again with the note above <D> **** Detailed Description **** PI&R Self-Assessment Objective 2: Validate that issues are identified and addressed appropriately in a timely manner commensurate with their safety significance . Reviewed a sample of Operator Logs (10 daysâ€™ worth from 4 of the past 6 quarters) to ensure identified issues are entered into the CAP. . Examples: 08/14/2017 8/14/2017 8:28:16AM NLOGSLCO00 Opened: LCS-17-SRV-POSITION -001 Description of the problem: Surveillance ISP-MS-M201 went late 8/14/2017. This surveillance meets LCS 1.3.3.1, SR 1.3.3.1.1, Table 1.3.3.1-1, Function 1. . 08/16/2017 8/15/2017 8:05:00PM Entered LCS 1.7.1.B.2 for CMS ANNULUS AVE TEMP. greater than 150 degrees . 10/29/2017 10/28/2017 7:00:00PM Received H13-P800.C4.2-1, "TRANSFORMER TR-M2 TROUBLE" alarm. Dispatched OPS-4 to investigate. Ops-4 reports the trouble is loss of oil flow pump group 2 fans. Entered ABN-Transformer . 10/30/2017 10/29/2017 9:15:00PM Received H13-P800.C4.3-1, "TRANSFORMER TR-M3 TROUBLE" alarm. Dispatched OPS-4 to investigate. Ops-4 reports the trouble is COOLER 2 FAILURE OR OFF POSITION. Entered ABN -Transformer . 10/30/2017 10/30/2017 10:56:00AM Received a ground alarm on SL-21. 4.800.C2,8-1. For MC-2B and MC-2P. OPS-3 RESET per ARP and inspected MCs. Nothing abnormal found. . 02/16/2018 2/16/2018 1:45:00AM OPs4 reports 115KV OCB air pressure is 105# and down slow. No obvious signs of leakage or other system malfunction. The air compressor started during the investigation as air pressure reached ~103#. . 05/07/2018 5/7/2018 1:13:00PM Panel door gasket on WMA-AD-54A2 found to be degraded upon opening. Breach on WMA-AD-54A2 is updated to Major. Per PPM 1.3.57 a Major breach that can not be restored within 4 minutes requires entry to TS 3.7.3.B. Entered TS 3.7.3.B. TS 3.7.3.B.1 is complete with actions on-going to replace the door gasket with a gasket that was staged for this purpose. Reference WO 02046739. [no CR is referenced in the WO either] . <I> **** Actions Taken **** Discussed with SA Team to validate information. Initiated CR Recommend Sev C to Operations <N> **** Equipment Description **** See listed examples in body of CR text . Some plant issues were documented in the logs that did not reference a CR, but a search of the database determined that a CR did exist for the issue. In several other cases no CR could be found that identified the issue (7 cases).
384713 | CR | 20180919 |  | 4 | TMU/CBD Valve Box #8 Manway Cover | N | N |  | N | YES | <D> **** Detailed Description **** The ~2 ft diameter 1/4" thk steel manway cover for TMU/CBD Valve Box #8 is out of position (visible from the access road to the TMU pump house). See the photos attached to the EDMS of this AR CR 384713. Please reinstall the manway cover (should not require any tools - these manway covers have lift handles and are not bolted down to the Valve Box structure). Reference AED C539 and AED C537. The #1 through #13 TMU/CBD Valve Boxes are Quality Class 1 (design basis tornado missile barriers) but the manway covers are NOT for tornado protection of the contents within the valve boxes - tornado missile protection is provided by the shape of the civil reinforced concrete structure itself, not the manway covers. <I> Reviewed civil calculation 6.01.08-SI-2 for the TMU/CBD valve boxes. Only the interior TMU line/items require tornado missile protection by the valve box civil reinforced concrete structure and the valve box manway cover is not credited or evaluated as a tornado missile barrier. | 02-00-CGS-BLDG-MISC
384716 | CR | 20180919 |  | 3 | Keys missing |  |  |  | N | NO | <D> **** Detailed Description **** While doing a key audit per PPM 1.3.23 key M-249 is missing from the radwaste control room, and key M-221 is missing from the SSS office. <I> **** Actions Taken **** Wrote CR. Informed SSS and Radwaste operators. Also informed CRS
384719 | CR | 20180919 |  | 4 | while performing 02124470-01 found EDR-LIS-86 OOT | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** the as found was out due the zero being slightly off the worst case was 3% high at 75% and off scale high at 100% the adjustabe trip points adjusted per IMDS <I> **** Actions Taken **** Zero was adjusted and was to within tolerance
384720 | CR | 20180919 |  | 3 | 2018 FSA PI&R - No long term trending method for IOD quality |  |  |  | N | NO | <C> CR Changed from CAQ to NON CAQ at the direction of OFM on 9/24/2018. <D> **** Detailed Description **** During the 2018 PI&R focused self-assessment, immediate operability quality was reviewed. OI-75 provides guidance on the operability determination quality review board process. Section 3.2 provides guidance for trending and monitoring of IOD quality to assist in identification of declining trends. Not all of this guidance is currently being implemented. <I> **** Actions Taken **** Develop a trending and monitoring process for IOD quality that meets the guidance provided in OI-75.
384721 | CR | 20180919 |  | 4 | Employee bumped elbow upon exiting excavation |  |  |  | N | NO | <D> **** Detailed Description **** While exitiing excavation for FP-V-350, employee bumped elbow on protruding bolt. . No first aid needed. <I> **** Actions Taken **** Occupational health notified, industrial safety was notified. Notified component manager. <N> Incident report 18-0020 was initiiated.
384722 | CR | 20180919 |  | 3 | found locations wrong on IMDS EDR-LT-103 and EDR-LIS-86 | N | N |  | N | NO | <D> **** Detailed Description **** EDR-LT-103 says its located on RW467 it is Located RW437 IR-G11-P018 EDR-LIS-86 says its located on RW437 It is located RW467 RWCR panel P001 <I> **** Actions Taken **** Created CR to get locations on the IMDS corrected | 02-00-EDR-LIS-86,02-00-EDR-LT-103
384723 | CR | 20180919 | CAQ | C | DG2 Bar-over performed on old rev of OSP-ELEC-M702 |  |  |  | N | NO | <D> **** Detailed Description **** Prestart checks and bar-over of DG-2 per sections 7.1 and 7.2 of OSP-ELEC-M702 were performed on a superseded revision (major rev 62) instead of the current revision (major rev 63). This surveillance was performed on an iPad using eWP. Typically when a revision has occurred, the work package flags red, and cannot be opened until the package is validated for current revision. In this case the work package did not flag that validation was required. After performance of the bar-over, the work package flagged red at some point and upon performing validation; a new revision was shown as available. In the future, all packages should be checked for validated prior to commencing work. <I> **** Actions Taken **** Informed shift manager. Performed a line-by-line verification which showed no changes in the performed sections. Uploaded the new revision of OSP-ELEC-M702 into the work package and the remainder of the procedure will be performed on the current revision. <N> No action will be taken. SWP-PRO-02 already requires verification of procedure revisions. Individuals were coached and lessons learned disbributed to the department. NO further action required.
384724 | CR | 20180919 |  | 4 | TMU-V-7B will not go full open | N | N |  | N | YES | <D> **** Detailed Description **** TMU-V-7B (Sluice gate) indicates intermediate in the MCR. The valve continues to indicate intermediate even after its switch is taken to OPEN. It is possible this is a limit switch issue. Also note that CR 378608 documents the inability for operators to locally operate the valve manually. | 02-00-TMU-V-7B
384725 | CR | 20180919 |  | 4 | GEM-5 (TSC) failed to restart | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing 02132093-01 filter cleaning GEM 5 HP-EQ -42736 failed to restart. <I> **** Actions Taken **** Notified supervisor and initiated this CR <N> **** Equipment Description **** (TSC) Alternate access
384726 | CR | 20180919 | CAQ | D | Washington State CRASH phone inoperable | N | Y |  | N | YES | <D> **** Detailed Description **** Washington State did not receive a PM test call. All other CRASH circuits are functional. Washington State is reachable by dial up phone and fax. <I> **** Actions Taken **** Notified EP and had Telecom test the circuit. The problem appears to be with the service provider. Requesting call ticket. Recommend closing this CR to the WR. <N> **** Equipment Description **** TEC
384727 | CR | 20180919 |  | 3 | Diesel Generator System Description requires revision |  |  |  | N | NO | <D> **** Detailed Description **** SD000200, "Diesel Generator" needs to be updated to reflect the correct HPCS DG operation with the Engine Speed Selector switch in IDLE and a high drywell pressure or low RPV level condition occurs. FSAR page 8.3-19 confirms that If a high drywell pressure or low RPV level condition occurs, manual control is automatically bypassed and the engine is accelerated to rated speed. <I> **** Actions Taken **** Discussed with Operations and Ops training. | 02-00-DG-ENG-1C,02-00-HPCS-GEN-DG3
384729 | CR | 20180920 | CAQ | D | IDS 24 25 Not Functioning as Designed | N | N |  | N | YES | <D> **** Detailed Description **** IDS 24 25 are not functioning as designed and require maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Securtiy supervision notified. Initiate CR/WR. | 02-00-SEC-IDS-EVAL/24/25
384732 | CR | 20180920 |  | 3 | Minor enhancement to OSP-ELEC-M702 |  |  |  | N | NO | <D> **** Detailed Description **** Part of the pre-requisites for performing OSP-ELEC-M702 require validating if the DSA check valve task is due quarterly, and if electricians need to take vibes. Currently this data is in the work order cover page, however a minor enhancement would be to include the PMID numbers to the pre-requisites would be beneficial to the operators. Step 3.7 is for quarterly DSA check valve check recommend adding PMID number 17356 and for Electricians to take vibration data which is step 3.6 recommend adding PMID 16244. Simply adding parentheses with the PMID number would be adequate. Recommend doing the same to all other Diesel procedures that reference DSA check valves or electricians performing vibrations. <I> **** Actions Taken **** Discussed this with other operators.
384733 | CR | 20180920 |  | 3 | DRAWING ERRORS, UNABLE TO PROCESS. |  |  |  | N | NO | <D> **** Detailed Description **** DOCUMENT CONTROL RECEIVED THE FOLLOWING DRAWINGS: M664 REV 057 - EC IS AT "ASSIGNED" STATUS. M658 REV 068 - REVISION 068 HAS ALREADY BEEN ISSUED. EC IS AT "ASSIGNED" STATUS. 642-00,22 REV 008 - EC's ARE AT "ASSIGNED" STATUS. 206-01,469 REV 002 - REVISION # IN REV BOX IS INCORRECT. CANNOT NOT PROCESS ANY OF THESE DRAWINGS UNITL CORRECTIONS ARE MADE. <I> **** Actions Taken **** ERRORS HAVE BEEN INDICATED ON DRAWINGS LISTED ABOVE, AND HARD COPIES WILL BE RETURNED TO ENGINEERING FOR CORRECTIONS TO BE MADE.
384734 | CR | 20180920 |  | 4 | ASD Heat Exchangers need cleaning | N | N | N | N | YES | <D> **** Detailed Description **** ASD heat exchangers have debris that needs to be removed. <I> **** Actions Taken **** Informed CRS | 02-00-RRC-HX-ASD1A/1,02-00-RRC-HX-ASD1A/2,02-00-RRC-HX-ASD1B/1,02-00-RRC-HX-ASD1B/2
384737 | CR | 20180920 | CAQ | C | Dropped hammer on DG roof | Y | N |  | N | NO | <C> CR Bring Back - OPS review needed. <D> **** Detailed Description **** A small ball peen hammer red handle was dropped when finishing up grating installation. The Hammer is located on the Diesel Generator roof just under the HCV Line running up the outside of the Reactor Building (RB) about Seven to Ten feet off the RB wall. <I> **** Actions Taken **** 1. Verified hammer is easily retrievable. 2. Generated AR/CR to document event. 3. After discussion with HP & Security believe the hammer should be retrieve on the next schedule survey of the roof. . Added a comment to the associated WR 29144696 that in addition to retrieval of the hammer, the DGB roof should be checked for damage where it was struck by the falling item. . AED CAL 6.21.03-SVII-1 provides civil structural evaluation of the safety-related DGB roof. The design basis missile for qualification of the DGB roof is a Reactor Building superstructure girt (25 ft long W8x31 section - 775 lbs) free falling from elevation 665'-0" and striking the DGB roof in the worst-case orientation (max equivalent static load of 330,000 lbs). Clearly, the design structural capability of the DGB roof was not challenged by the AR CR 384737 subject dropped hammer. <N> **** Equipment Description **** DG roof under HCV line and 8' to 10' of Reactor Building Intermech. The (Intermech) individual displayed the proper behaviors of accountability in that he recognized it was his fault without excuses, owned what had happened, and demonstrated learning from it. He had re-positioned some knee pads that were apparently purposefully placed to cover up the gap between the grating of the platform and the pipe when he was inspecting some work. When he moved next, he accidentally knocked a small hammer into the gap and it fell. He didn't realize the purpose of the knee pads was to prevent that very thing, and was disappointed in himself that he didn't recognize that he had created an opportunity for error. He reported it immediately. (The job has completed, and he has outprocessed) 1) Cause: Individual inadvertently caused a hammer to fall from the hardened containment vent platform to the roof of the Diesel Generator building. 2) Corrective actions: a) Retrieve hammer, b) inspect roof for damage, c) if damage repair as needed | 02-00-D-BLDG-MISC
384738 | CR | 20180920 | CAQ | C | Discrepancy between the Top Tier prints for DG1 and ISOs. |  |  |  | N | NO | <D> **** Detailed Description **** There is a discrepancy between the Top Tier prints for DG1 and the ISO drawings. M512-2 rev 37 and M512-4 rev13, both Top Tier prints, show that for work on DO-FLX-1A2, that DO-V-609 vents the piping (1â€DO(2)-1-1 and is associated with DO-V-6A. 317-00,102,1 rev 0, 317-00,101 rev 6 and 317-00,100 rev 7 show that DO-V-610 vents the piping associated with DO-V-7A and is associated with DO-FLX-1A2. In the plant, the piping goes under a grating and there is a cover where the piping goes into the day tank room preventing a thorough walk down. Which vent valve should be used for this work? <I> **** Actions Taken **** Wrote CR and informed supervisor who contacted Engineering for support. | 02-00-DO-V-609,02-00-DO-V-610
384740 | CR | 20180920 | CAQ | C | CGS and OEM MSRV Drawings do not match. |  |  |  | N | NO | <D> **** Detailed Description **** The original equipment manufacturer (OEM) latest drawing DS-A-63790-3 Rev. C does not match with CGS drawing DS-A -63790-3 Rev.5 (CVI 932-00,1,1, Rev.5). During the review of the MSRV drawings provided by the OEM Emerson (formerly Crosby, Reference AR 00382525 and AR 00382510), it was discovered that the OEM drawings do not reflect the changes EN had made on the MSRVs (i.e. flex disc, etc.) through the formal design change process. This has caused the two sets of MSRV drawings to be out of sync which makes it difficult for Procurement Engineering and Purchasing to place an orders for parts. CGSâ€™ MSRV drawings reflect the current plant configuration per current design and licensing basis. The two sets of drawings will require design engineering review and reconciliation. Therefore this is an administrative issue and not an equipment issue which does not affect the CGSâ€™ SSC. Recommend Severity level â€œCâ€ to design Engineering (AR-DMC) for resolution. <I> **** Actions Taken **** Discussed this condition with Supply Chain, Design, Procurement, System, Material and Code Program Engineering. Notified Operations, Control-Room Shift Manager. There is no non-conforming condition.
384741 | CR | 20180920 |  | 3 | Need training and procedure for Remote Breaker Operating Dev |  |  |  | N | YES | <D> **** Detailed Description **** E-CB-1/500S would not open from the control switch in main control room. It was communicated that the plant had recently purchased a Remote Breaker Operating Device. This device was used successfully to open the breaker. Need to have training and a procedure written to use this device. <I> **** Actions Taken **** E-CB-1/500S opened successfully <N> **** Equipment Description **** T471 | 02-00-E-CB-1/500S
384742 | CR | 20180920 | CAQ | D | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0063371 Heise Pressure Calibrator- model PTE-1 found OOT & adjusted within specs. Not used in the OOT range of 5V & 10V. DEF #6745A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
384745 | CR | 20180920 |  | 3 | FAS Trend Identified- Lost training time due to Sim Upgrade |  |  |  | N | NO | <D> **** Detailed Description **** During the August Training Functional Area Scorecard Meeting a trend was identified related to the Simulator Model Upgrade. There have been four CRs written since the models implementation in July 2018 where training time was lost due to simulator discrepancies or aborts, see EDMS for trend validation worksheet. <I> **** Actions Taken **** Discussed with training management at Functional Area Scorecard monthly meeting and contacted Simulator supervisor.
384748 | CR | 20180920 |  | 3 | P&L is conflicting between PPM 3.2.6 and SOP-COND-START |  |  |  | N | NO | <D> **** Detailed Description **** P&L 4.5 of PPM 3.2.6 states to MAINTAIN Reactor Feedwater pump suction pressure GE 350 psig. . P&L 4.11 of SOP-COND-START states Maintain Reactor Feedwater pump suction pressure GE 400 psig. . please decide which is correct and make them the same in both procedures. <I> **** Actions Taken **** Wrote CR
384752 | CR | 20180920 |  | 3 | SOP-TMU-OPS needs an additional precaution and limitation. | N | N | N | N | NO | <D> **** Detailed Description **** SOP-TMU-OPS controls the operation of TMU-V-7A and 7B. If both of these valves are shut at the same time a trip signal is sent to all three TMU pumps. EWD-55E-002, EWD -55E-009, EWD-55E-016 and EWD-55E-017 show this fact. There are no precautions and limitations nor any notes prior to the operation of TMU-V-7A or 7B in SOP-TMU-OPS. Please consider adding this information to this procedure. <I> **** Actions Taken **** Discussed with supervisor and wrote this AR/PCR.
384753 | CR | 20180920 |  | 3 | OG-TS-64D and OG-TS-65D out of tolerance. | N | N | N | N | YES | <D> **** Detailed Description **** OG-TS-64D and OG-TS-65D out of tolerance. the Temperature switches were found out of tolerance duirng WO 02128866-03 PMT for replacement of OG-MV/I-20B. . OG-TS-64D tripped at 7.1 mA (96.9 F), OG-TS-65D tripped at 6.5 mA (79.7 F). OG-TS-64D and OG-TS-65D are Alarms that only function when the Dryer is used in Auto mode. By procedure (SOP-OG-OPS) the descicant dryers are only operated in manual. . By Procedure the Dyres are operated in manual. and the alarms do not function in manual (see IMDS for OG-TS-64D and 65D) . the Temperature switches were removed from PMRQ 1640601 because the alarms are never in service. . The alarms are not used because the system is operated in manual. REcommend engineering evaulate if the switches need to be calibrated. <I> **** Actions Taken **** Generated AR to ducument that the switches are out of tolerance. and Notified SM | 02-00-OG-TS-64D,02-00-OG-TS-65D
384754 | CR | 20180920 |  | 3 | Discrepancy between procedure Native File and Asset Suite | N | N | N | N | NO | <D> **** Detailed Description **** Description:A procedure in Asset Suite did not match the native file for the procedure which was approved through APPW. The change between the two versions occurred when the approved procedure was converted to a PDF and entered into Asset Suite. This is an issue applicable to any procedure where references to internal steps in the procedure are handled through MS Word macros. This caused a technician in the field to receive a procedure with different step references than what was approved through the APPW process. As an example: the native copy of PPM 16.8.1 in APPW directs workers with an â€œif/thenâ€ statement in step 7.3.15 to continue on to step 7.13. This is the correct direction. The copy of 16.8.1 in asset suite, however, incorrectly directs workers in step 7.3.15 to continue on to step 7.12.13a. <I> **** Actions Taken **** Discussed with other procedure writers.
384756 | CR | 20180920 |  | 3 | Data Access Desktop (SAP BI) system down |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The Data Access Desktop experienced a failure at approximately 10:45 am. The systems servers (S78 & S79) CMS application service shut down after experiencing multiple communication failure warnings. <I> **** Actions Taken **** Servers were rebooted, but the application will not continue to stay running. <N> Recommend NCAQ 3 ITMGMT | FW-00-SOFT-BUSN-BOE
384758 | CR | 20180920 |  | 3 | Maint craft pinched hand while staging equipment. | N | N | N | N | NO | <D> **** Detailed Description **** Maint craft pinched hand while staging equipment, which caused a small laceration. Craft was wearing gloves and incident did not cut their glove, but caused a small laceration on his hand. <I> **** Actions Taken **** Craft notified Supervision and was taken to Occupational Health. Occupational Health directed further medical investigation.
384759 | CR | 20180920 |  | 3 | EC 12277 MT-ELEV-4 Elev Upgrade Changes Affect Temp Power | N | N | N | N | YES | <D> **** Detailed Description **** EC 12277 MT-ELEV-4 Elevator Upgrade changes the power supplied. Changes affect the ability to provide temp power during R24. Currently EC 12277 does not include the scope to provide the means to connect temp power. Recommend that the project purchase the necessary equipment/incorporate changes to facilitate temp power needs in R24. AR EVAL 383911 Install a Temporary Power 200 amp fused disconnect, E-MC-3D and AR CR 381604 R24 procedure change MT-ELEV-4 - ELECTRICAL MODS (EC12277) have been initiated to provide guidance on the changes required. Estimated costs are ~25K labor and materials plus Engineering cost for a permanent solution (solution is to add a 200A bucket to MC-3D). <I> **** Actions Taken **** Discuss with Manager Outage Supervision. Prior discussions held with PM MT-ELEV-4 project. | 02-00-MT-ELEV-4
384760 | CR | 20180920 | CAQ | D | Partial core bores in TMU/CBD Valve Box #9, #12, & #13 roofs | N | N |  | N | YES | <D> **** Detailed Description **** Partial depth 2 inch diameter core bores from original plant construction were found to exist in the 2 foot thick reinfoced concrete roof slab areas of TMU/CBD Valve Box #9, #12, and #13. See the photos attached to the EDMS of this AR CR 384760. Reference AED C538 for valve box locations and reference AED C539 & AED C540 for valve box details. For resolution of this condition, these holes need to be grout repaired per PPM 10.2.33. The TMU/CBD valve boxes are Quality Class 1 per AED C539 and AED C540 (provide design basis tornado missile barrier protection for the TMU piping/components inside). Although drilled above the TMU line side of these valve boxes, none of these core bores were drilled completely through the full thickness of the roof slab - the deepest core bore hole discovered was approximately 11.5 inches deep (leaving more than 12 inches of undisturbed reinforced concrete thickness. Per civil calculation AED CAL CE-02-91-21 (CMR-96-0159), the maximum required concrete thickness to prevent local damage for FSAR Table 3.5-5 Tornado Missiles is 6.80 inches (for the 15 foot long section of 6 inch schedule 40 pipe traveling horizontally). As such, this AR CR 384760 condition does not challenge continued functionality of the tornado missile barrier function provided by any of the associated TMU/CBD valve boxes. In reality, the only FSAR Table 3.5-5 Tornado Missile potentially capable of actually fitting into any of the subject 2 inch diameter core bore holes is the 1 inch diameter 3 foot long steel rod traveling vertically. Per AED CAL CE-02-91-21 (CMR-96-0159), only 1.09 inches of concrete thickness is required to prevent local damage associated with this tornado missile. <I> **** Actions Taken **** This condition was noted when performing field walkdown of all thirteen (13) TMU/CBD valve boxes from the Protected Area to the TMU pump house associated with the AR CR 384713 condition (TMU/CBD Valve Box #8 Manway Cover). No other TMU/CBD valve boxes were found with their manway cover out of position. Notified Operations (Shift Manager and other Operations personnel in the Main Control Room) of the AR CR 384760 condition and provided supporting hardcopy information to assist with their review. <N> The subject partial depth core bores appear to have been associated with heat tracing whose installation was never fully completed and spared in place per AED C539 Note 1. | 02-00-CGS-BLDG-MISC
384762 | CR | 20180920 | CAQ | D | SW-TE-1BR unable to be removed for maintenance | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** SW-TE-1BR unable to be removed for maintenance during the performance of 02109506-01; the TE is either mechanically held in place which isn't shown very well on the prints OR is bound up in some other way. <I> **** Actions Taken **** Initiate CR, contacted WWM, contacted PSRO, contacted component manager, contacted system enginee, packages returned to add additional instructions for other craft(s). Recommending to planning to add another task to provide mechanical support on removing TE chase. <N> **** Equipment Description **** SWPH B | 02-00-SW-TE-1BR
384765 | CR | 20180920 | CAQ | C | Withhold from Public Disclosure Record left unattended | N | N | N | N | NO | <C> Reopened at the request of RA Manager to document approval for closure of assignment -01. <D> **** Detailed Description **** On 9/20/2018 a Withhold from Public Disclosure Record was left in the incoming Records box by Regulatory Affairs. Please refer to SWP-SEC-11 on the submittal process for these types of Records. <I> **** Actions Taken **** Notified my supervisor. C/R written for tracking purposes and placing the record in the Vault for processing.
384766 | CR | 20180920 |  | 3 | IMDS revisions need to be linked to PPM revisions | N | N | N | N | NO | <D> **** Detailed Description **** DSA-PCV-1A â€“ 2C IMDSs were revised and issued on 7-11 per AR-EVAL-378382. PPMs 10.27.63, 10.27.30A, and 10.27.30B are still in review routing. 10.27.30A is needed as a contingency procedure for the upcoming DG-1 outage. Unfortunately there is no indication or linkage to show that the procedure is out of compliance with the revised IMDS. This put us at risk of performing a procedure that is out of compliance with the source engineering documents. This also occurred several weeks back during performance of ISP-APRM-B303 (see CR-383981). <I> **** Actions Taken **** 10.27.30A should be approved and issued in time for the DG-1 outage. | 02-00-DSA-PCV-1A,02-00-DSA-PCV-1B,02-00-DSA-PCV-1C,02-00-DSA-PCV-2A,02-00-DSA-PCV-2B,02-00-DSA-PCV-2C
384767 | CR | 20180920 |  | 4 | Inadequate notification of PPM revision for EC-16858 | N | N | N | N | NO | <D> **** Detailed Description **** At T-3 week, was informed that revision to PPM 10.19.4 was needed for EC-16858, TMU-P-1A Pump Upgrade & Modification. This puts a strain on the limited resources available to ensure the revision is issued in time for work. <I> **** Actions Taken **** Recommend that notification of revisions needed is given earlier in the T process. <N> During generation of the EC an assignment to update the Vol 10 was generated to the pump engineer. This assignment asked for the procedure to be revised rather than a markup provided to maintenance procedures. Coaching was provided to the individuvals to ensure that adequate time is provided for all procedures to be updated. Recommend that this be trended.
384768 | CR | 20180920 |  | 4 | Adverse trend in CW-FN-19 oil addition | N | N | N | N | YES | <D> **** Detailed Description **** Over a 14-month period CW-FN-19 has required 5 oil additions, which may be indicative of gearbox degradation. Recommend inspection and replacement of gearbox as necessary. | 02-00-CW-FN-19
384770 | CR | 20180920 | CAQ | D | Documenting results for RHR-HX-1A thermal performance | Y | N |  | N | NO | <D> **** Detailed Description **** This CR is being initiated to document results of RHR-HX-1A thermal performance. Current margin is calculated to be 38.5%. Error in the test methodology is also calculated to verify test data accuracy is LE 10%. Heat Balance error is 3.5%. Past 4 surveillance margin were as such: 32%, 31%, 47%, 47%. The CR is being written for trending purposes only to document results of WO 02095968 for PMID 10159-04. <I> **** Actions Taken **** Discussed with CRS/SM | 02-00-RHR-HX-1A
384771 | CR | 20180920 |  | 4 | Air leak identified on SA-C-1 loading diaphragm | N | N | N | N | YES | <D> **** Detailed Description **** Note, this is not reworlk as this the loading diaphragm was not worked during this SA-C-1 maintenance window. Diiaphragm will need replaced. <I> **** Actions Taken **** Generated CR. Discussed with SSS. Compressor was being secured. | 02-00-SA-C-1
384773 | CR | 20180921 | CAQ | D | During OSP-MT-W701 SOV C trip time was GT400 milliseconds | N | Y |  | N | YES | <D> **** Detailed Description **** Results of the Quad Voter Solenoid Test ( OSP-MT-W701 ): SVA 0.27 sec 0.23 sec 0.27 sec SVB 0.27 sec 0.23 sec 0.23 sec SVC 0.59 sec 0.32 sec 0.32 sec SVD 0.27 sec 0.27 sec 0.27 sec <I> **** Actions Taken **** Reperformed two additional times. | 02-00-DEH-SV-TRIP/C
384774 | CR | 20180921 |  | 4 | NRC Identified - NRC resident not notified of 9/22 downpower |  |  |  | N | NO | <D> **** Detailed Description **** The NRC resident notified the control room staff that he was not informed about the upcoming 9/22/18 downpower. <I> **** Actions Taken **** Provided copies of the power profile and RCP to the NRC resident. Notified Licensing (on-call). <R> Reg Affairs verified with the SRI that the notification was made though it was made much earlier than normal (2 weeks vs. a couple of days) so they did not see it. Recommend this CR be closed.
384775 | CR | 20180921 |  | 4 | TOA-FL-1A not auto advancing. | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FL-1A, 1B, 2A and 2B are not auto advancing as evidenced by dirty roll filters. These filters all advanced manually and have recently worked in auto. Please investigate and repair the auto advance circuit. <I> **** Actions Taken **** Wrote this AR/WR. <N> **** Equipment Description **** T501 G0/4.5 T 501' F3/6.0 T501 G0/15.5 T501 G5/16.5 | 02-00-TOA-FL-1A,02-00-TOA-FL-1B,02-00-TOA-FL-2A,02-00-TOA-FL-2B
384776 | CR | 20180921 |  | 4 | TOA-HV-2B needs re-lamping. | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FL-2B compartment in TOA-HV-2B has no working lights and needs re-lamping. Please investigate and correct. <I> **** Actions Taken **** Wrote this AR/WR. <N> **** Equipment Description **** T501 G5/16.5 | 02-00-TOA-HV-2B
384777 | CR | 20180921 | CAQ | D | FP-V-83 Leaks by | N | N |  | N | YES | <D> **** Detailed Description **** Performing 15.3.12 FP-V-83 operated very hard. and leaked by 1 gallon every 3 minutes . <I> This is non-essential fire protection. FP-V-83 is normally locked open and is only throttled shut during testing (PPM 15.3.12). The seat leakage would only impact the system if this valve was used for leak isolation. Otherwise, the impact is only for testing as the valve is normally open. The valve isolates Deluge System #52 for feed pump oil piping. | 02-00-FP-V-83
384778 | CR | 20180921 | CAQ | D | Can't install a quick disc downstream of CRD-V-107/3047 | Y | N |  | N | YES | <D> **** Detailed Description **** Can't re- install a quick disconnect drain line downstream of CRD-V-107/3047 due to pressure lock. Need to resolve the issue. <I> **** Actions Taken **** SM informed | 02-00-CRD-V-107/3047
384781 | CR | 20180922 | CAQ | D | W-DOOR-C238 door knob is failing. | N | N |  | N | YES | <D> **** Detailed Description **** W-DOOR-C238 outer door knob for entry into the room is wearing out and skips if too much torque is applied when opening the door. If this conditions continues to worsen, access to the room will be prevented. This room contains div 2 battery chargers which are safety related equipment. Currently the door knob on the inside for egress works fine. Please investigate and repair. <I> **** Actions Taken **** Informed supervision and wrote AR/WR. <N> **** Equipment Description **** W 467 M0/10.0 | 02-00-W-DOOR-C238
384782 | CR | 20180922 |  | 3 | TSP-CRD-C101 procedure correction |  |  |  | N | NO | <D> **** Detailed Description **** While performing scram time retest for control rod 30-47 on 9/22/18 it was identified during step 7.2.8.l.2 that the N16 edit did not indicate that the recently scrammed rod had been updated. Step 7.2.8.l.1 did accurately display thta the control rod had scrammed with the appropriate scram times, however, the report function in N16 does not indicate as such until after section 7.5, Evaluation of Scram Times, is performed. After section 7.5 was performed, the N16 report function did identify that this control rod was included in the scram time data base appropriately. Step 7.2.8.l.2 is out of sequence, and should not be performed until the end of section 7.5. <I> **** Actions Taken **** Executed section 7.5 of the procedure and confirmed that N16 report functions did include the recently scrammed rod 30-47. Recommend updating procedure to move step 7.2.8.l.2 into section 7.5 of the procedure.
384783 | CR | 20180922 |  | 3 | Procedure Enhancement OSP-MS-Q702 |  |  |  | N | NO | <D> **** Detailed Description **** OSP-MS-Q702 step 7.1 should have If required before reduce reactor power. <I> **** Actions Taken **** Wrote CR
384784 | CR | 20180922 | CAQ | D | (NRC) Door between RHR A and B pump room | Y | Y |  | N | YES | <C> CR reopened to add completion required check mark to referenced WO 02057200 per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** The NRC resident during a walkdown noted that the door between RHR A and B pump rooms has no compression on the rubber seal. There is no immediate concern for operability of the barrier, but this condition should be evaluated for repair. | 02-00-R-DOOR-R006
384785 | CR | 20180922 | CAQ | D | (NRC) R-DOOR-R110 - loose strike plate | Y | Y |  | N | YES | <D> **** Detailed Description **** The NRC resident noted during a walkdown that the strike plate for R-DOOR-R110 was loose. An EO attempted to tighten it, but it requires a specialized tool. There is no immediate concern for operability of the door. | 02-00-R-DOOR-R110
384786 | CR | 20180922 |  | 3 | Work order stuck on iPAD |  |  |  | N | NO | <D> **** Detailed Description **** WO 02121910-01 iis on tablet ENT-DLXTQ51TGMLL. This tablet is normally located at the STA desk in the main control room. It is an iPad Pro . Dataglance says that the package is not checked out, and the work order is complete. <I> **** Actions Taken **** wrote CR
384787 | CR | 20180922 |  | 3 | Management texts not received |  |  |  | N | NO | <D> **** Detailed Description **** During the downpower and sequence exchange on 9/22/18, several management texts were sent to update the management team of the progress. The texts were not received. <I> **** Actions Taken **** Wrote this CR.
384788 | CR | 20180922 |  | 3 | PWC-XR-1 not restored as required by WCI-4 | N | N |  | N | NO | <D> **** Detailed Description **** The monitoring of potable water turbidity is a state requirement (WAC 246-290-660). PWC-TBIT-2 and PWC-XR-1 are the instruments used to meet this requirement. PWC-TBIT-2 is functioning properly but the effluent turbidity indication of the recorder (PWC-XR-1) is failed downscale. This effluent turbidity recorder information is used to satisfy Washington state flocculator efficiency requirements and the related CGS flocculator performance report to the state. Per WCI-4 recorder PWC-XR-1 is listed as state drinking water standards regulatory equipment and is therefore required to be graded as PRI-2 or 2A. WR 29144601 was initially graded as PRI-4A it has been changed to PRI-2A. Also WCI-4 requires that this equipment be restored to service within 5 days. This was not met. <I> **** Actions Taken **** PWC-TK-110 was sampled at ~1800 9/22/18 with a turbidity result of 0.44 NTU which is LT the limit of 1 NTU. Established a temporary log to record flocculator turbidity within 30 minutes of starting the flocculator and very 4 hours when running. <N> Chemistry left a voicemail with the WA Department of Health on 9/24/18 to inform them of the recorder down time. | 02-00-PWC-TBIT-2,02-00-PWC-XR-1
384791 | CR | 20180923 |  | 3 | Procedure enhancement for OSP-RHR/IST-Q703 |  |  |  | N | NO | <D> **** Detailed Description **** The second note before step 7.3.1 says to perform this section concurrently with section 1.1. it should be section 7.2 <I> **** Actions Taken **** Wrote CR
384792 | CR | 20180923 |  | 3 | I&C model WO does not match Ops surveillance |  |  |  | N | NO | <D> **** Detailed Description **** During OSP-RHR/IST-Q703, I&C connects test instruments for data collection during the pump run. For OSP-RHR/IST-Q703, the model WO connects the 0-300 psig fluke used for the 2 year CPT in a different location than directed by the OSP. OSP-RHR/IST-Q703 directs installation at the test connection of RHR-PS-16B. Model WO 00CVG3 (and 00CVG4) direct installation at RHR-PX-15. The model WOs appear to be a copy and paste of the steps from the OSP, with the exception of the location, and are unecessary. The surveillance provides appropriate steps that are I&C sign off. Recommend discontinuing the use of WO instructions for this task to eliminate this error trap. A review of similar Ops surveillances requiring test instrument installation by I&C should be performed as an extent of condition. This situation resulted in a delay in performance of OSP-RHR/IST-Q703 on 9/23/18 and challenged craft resources needed to support completion of the surveillance. <I> **** Actions Taken **** Directed I&C to perform restoration steps of the WO instructions to remove the 0-300 psig fluke from RHR-V-245, then perform the applicable steps in OSP-RHR/IST-Q703 to ensure the test instrument is connected in the correct location. Wrote this CR
384794 | CR | 20180923 | CAQ | D | Fluoresent light out in A8 stairwell. | N | N |  | N | YES | <D> **** Detailed Description **** Fluoresent light is out on the RW 507 A8 stairwell. This ia a blue dot lamp. Please relamp. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** RW 507 A8 stairewll | 02-00-W-BLDG-MISC
384795 | CR | 20180924 |  | 4 | TG 441 AMS 3 Has a Broken Chart Recorder | N | N |  | N | NO | <D> **** Detailed Description **** The AMS-3 on TG 441' has a broken chart recorder. Tagged Out of Service and placed a different CAM in service. (HP-EQ-34119) <I> **** Actions Taken **** Initiated Condition Report & Work Request. Notified Supervision via E-mail. <N> **** Equipment Description **** TG 441' (HP-EQ-34119) | 02-00-HP-EQ-34119
384803 | CR | 20180924 |  | 4 | Water hose bib through-wall leak between stabilization ponds | N | N |  | N | YES | <D> **** Detailed Description **** The water hose bib (possibly PWC system) on the south central side of the south stabilization pond (B24 sewer ponds) has a through-wall leak (TWL). The bose bib is not marked to indicate system or component identification but is near a valve tagged C-10 (South Stabilization Pond Crossflow). As there is above ground through-wall leakage from a buried hose bib valve, it appears that the hose bib valve leaks by (i.e., that there is an issue with the opening/closing mechanism and/or seat for this hose bib) and this TWL is likely damage from freezing last winter which will likely freeze again this winter and get worse if not addressed. At this time, leakage is minor. Photo attached to the EDMS of this AR CR 384803. <N> **** Equipment Description **** near valve C-10 - south stabilization point cross-flow. B24 sewer ponds
384805 | CR | 20180924 |  | 3 | Scaffold Tag System |  |  |  | N | NO | <D> **** Detailed Description **** The scaffold tag system that is currently being used is showing inefficiencies as scaffold tags are being developed for daily as well as outage(s). The scaffold tag system currently functions properly but an evaluation should be done with IS and operations department to determine if creating scaffold modules through ESOMâ€™s would be more user friendly and assist with tracking historical data. Using the ESOMâ€™s program would help with the development of long term scaffolds, pictures, dose savings and align with the stations long term goals. <I> **** Actions Taken **** Created CR and discussed with ESOM's program owner.
384807 | CR | 20180924 |  | 3 | Suggested TMU drawing clarifications/enhancements |  |  |  | N | YES | <D> **** Detailed Description **** Suggested TMU drawing clarifications/corrections: 1) Unnecessary details have been left included on structural drawing AED STL S877 associated with largebore TMU supports TMU-1 and TMU-917. The majority of the details currently provided by AED STL S877 SECTION 7-7, SECTION 42-42, and WASHER PLAT DETAIL are also currently provided by CVI DWG 225-08,26 (TMU-1) and CVI DWG 225-08,43 (TMU-917) and therefore shouldn't be shown in detail on an AED STL drawing. The only detail that needs to be retained on the AED drawing is the information for the 1-1/4" concrete anchors and anchor bolting (i.e., the details not already included on CVI DWG 225-08,26 and CVI DWG 225-08,43) - the rest should be removed or shown in phantom only on the AED drawing. 2) CVI DWG 225-08,43 for TMU-917 should reference AED STL S877 (i.e., like CVI DWG 225-08,26 for TMU-1 does). 3) The size of the embedded large bore pipe (i.e., 42" TMU PIPE) should be indicated on AED STL S877 'WALL ELEV. @ LINE B' detail and this AED STL S877 detail should reference back to AED STL S873. This Line B TMU wall penetration does not have a sleeve the 42" line passes through (the 42" line itself is embedded in the concrete wall) - reference AED STL S873 FOUNDATION PLAN. 4) AED STL S872 SECTION 1-1 incorrectly calls out CenterLine 42" Dia TMU as CenterLine 42" CONDUIT. 5) CVI DWG 225-02,25 should indicate 'FOR ANCHORS' in its references to AED STL S877 for the pipe supports near TMU-V-1A and TMU-V-1B. Additionally, the Sch. 40 ASTM A105 information indicated at the Line B wall pentration should be moved and indicated on the next penetration to the west (where the 48" sleeve information is currently indicated). Finally, the wall penetration information references to AED STL S877 should also include a reference to AED STL S873. . See the mark-ups attached to the EDMS of this AR CR 384807. . These changes are for clarification/enhancements - recommend nonCAQ resolution to Mechanical Design & Drafting. | 02-00-M-BLDG-MISC
384809 | CR | 20180924 |  | 4 | COND-P-1B Lower Oil Level LOW | N | N |  | N | YES | <D> **** Detailed Description **** Oil level is approximately 1/4'' below centerline (centerline ring isn't straight). Logs require LE 1/8'' departure from centerline. Oil addition needed. <I> **** Actions Taken **** Notified CRS | 02-00-COND-M-P/1B,02-00-COND-P-1B
384810 | CR | 20180924 |  |  | PWC-P-122 failed to start during Flocculator B/W |  |  |  | N | YES | <D> **** Detailed Description **** PWC-P-122, Flocculator surface wash pump, failed to start during backwash. The pump is started and stopped via the drum timer normally. All indications after backwash were that the backwash was sufficient and the flocculator was started. <I> **** Actions Taken **** Wrote CR. Informed CRS. | 02-00-PWC-P-122
384811 | CR | 20180924 |  | 4 | PWC-P-122 failed to start during flocculator backwash | N | N |  | N | YES | <D> **** Detailed Description **** PWC-P-122, Flocculator surface wash pump, failed to start during backwash. The pump is normally started and stopped via the drum timer. All indication were that the backwash was sufficient and the flocculator was started normally. <I> **** Actions Taken **** Wrote CR. Informed CRS. | 02-00-PWC-P-122
384812 | CR | 20180924 | CAQ | C | Offgas calculation from RPU exceeded dose limit | N | Y |  | N | NO | <C> CR reopened to add WO 02119702 - 27 to the cross reference panel and checked the Completion required box then taken back to complete <D> **** Detailed Description **** FSAR 1.2.2.8.3 says the gaseous radwaste system processes and controls release of gaseous radioactive so that total exposure doesnâ€™t exceed limits 10 CFR 20, 10CFR 50 Appendix I and 10 CFR 50.67. FSAR 11.3.1 says that the operating noble gas release rate of 100 uCi/sec per MWth source term should be used for the design basis analysis with concentration limits of 10CFR 20. FSAR Table 11.3-1 contains RPU Engineering Report source term for the design basis analysis, which was not uprated since it was deemed conservative enough at the time. Engineering has found that the gamma dose result exceeds the dose limit for the RPU OGS design basis upon reconstruction for AR OER 371045. Columbia can run for about 300 days at that elevated source term before challenging the gamma dose limit. Actual effluent results are lower than the design dose rate and well within the limits in the ODCM. <I> **** Actions Taken **** Discussed in meeting with concerned departments HP/ALARA, Chemistry, Licensing, Engineering Design, Systems and Rx Fuels and identified two-prong focus: (1) Document a new system design point in NE-02-03-04. Lower inleakage would provide better design. (2) Intrusive/non-intrusive inspection planning to find and reduce leakage. Offgas system flow is an indication of elevated inleakage to the condenser. After R-23 the flow rate ranged 30 up to 45 scfm, and after R-24 there was a step change +10 and drifted up another +5 before we started finding leaks. 48.5 scfm today vs 30 design.
384813 | CR | 20180924 | CAQ | D | (NRC) DRA-EUH-31 - Loose bolt | N | N |  | N | YES | <D> **** Detailed Description **** The NRC identified a loose bolt on DRA-EUH-31 at approximately the 2'oclock position. This is one of many bolts. There is no immediate concern for operability due to this being on of a large number of bolts. D030 screen indicates Critical Equipment N and Safety class AQ. <I> **** Actions Taken **** SM informed. | 02-00-DRA-EUH-31
384814 | CR | 20180924 |  | 4 | Faulty level indication of peroxide storage tank | N | N |  | N | YES | <D> **** Detailed Description **** The level indicator on SWCF-TK-1 (hydrogen peroxide storage tank) indicated full after tank was completely drained. Float level indicator did not adjust and may have dropped off of pully again. <I> **** Actions Taken **** Notified chemistry. Contacted FIN | 02-00-SWCF-TK-1
384815 | CR | 20180924 |  | 3 | Demin trailer lacks auto shut off feature | N | N |  | N | YES | <D> **** Detailed Description **** The demin water trailer is a vendor owned equpment. It was discovered that approximately two years ago the vendor for the demin trailer installed a new control modual. The new module did not include an auto shut off feature if water quality is out of specification. This auto shut off feature is required by contract wtih the vendor. The lack of auto shut off leaves us in jeopardy of sending out of specification water to the DWST. <I> **** Actions Taken **** Notified vendor of the descrepancy and requested that they fix the missing shut off feature . Trend only. <N> **** Equipment Description **** MUD trailer outside of bldg 33 | 02-00-DW-TK-1
384816 | CR | 20180924 | CAQ | D | Welder storage area needs protection of combustibles | N | N |  | N | NO | <D> **** Detailed Description **** TG 471â€™ west end of corridor is the welderâ€™s storage area. The south wall has multiple coil bundles of long welding leads that are 6.5 feet under the bottom cable tray. See pictures in EDMS. PPM 1.3.10C states to do not store combustibles in concentrated amounts directly under cable trays. NUREG-1805 fire plume analysis indicates there needs to be at least 11 feet of horizontal clearance to not have overhead cable damage (which could result in extended outage). The welding cables need to be either relocated, put in a metal box, or covered with ANSI/FM 4950 rated weld blanket. . This area has a moderate combustible load with no sprinklers, so is not a good location for storage. Housekeeping should be performed with includes putting as much misc area combustibles as possible in metal boxes or cabinets. The area is being placed on hourly fire tour. Note that placing the sheet metal over the cage entrance has hidden this hazard from view. Prompt correction is requested. This was identified as part of self-assessment AR 384793. <I> **** Actions Taken **** Wrote this CR and am notifying key people. <N> **** Equipment Description **** NO EPN | 02-00-T-BLDG-MISC
384817 | CR | 20180924 |  | 3 | 4.FCP1 and 2 ARPs in error |  |  |  | N | NO | <D> **** Detailed Description **** the new FCP-1 and FCP-2 panels do not operate the same as the old panels and a note on every module is wrong. See EDMS for details. Every window will be impacted - suggest search for string and replace with the truth or delete note since it is not applicable to the new panels. | 02-00-FP-CP-FCP1,02-00-FP-CP-FCP2
384818 | CR | 20180924 |  | 4 | Threaded bolt sticking up on concrete pad N. of bldg. 88 | N | N |  | N | NO | <D> **** Detailed Description **** A threaded bolt was observed sticking up approx. 1.5 inches on a concrete pad inside the fenced area N. of bldg. 88. This appears to be a legacy issue possibly left over from outage/ project trailers. The protruding bolt creates a potential trip hazard for individuals walking in that area. <I> **** Actions Taken **** Placed a heavy deligneator/ cone on top of the threaded bolt. Suggest facilities cut off flush with the surface of the concrete. Wrote this CR with a Work Request. <N> **** Equipment Description **** Concrete pad N. of bldg. 88 inside the fenced area. See photos in EDMS.
384819 | CR | 20180924 | CAQ | C | Storage area #209 has combustibles close to cable trays | N | N |  | N | NO | <D> **** Detailed Description **** Storage area #209 is located near the middle of the TG 471â€™ central E-W corridor. The cable trays drop down low in this area. There are four areas within #209 where there are coiled combustible tubes and hoses. See EDMS. PPM 1.3.10C states to do not store combustibles in concentrated amounts directly under cable trays. Assuming a small to medium fire, NUREG-1805 fire plume analysis indicates cable damage to the overhead cable trays is possible (which could result in extended outage). The cables need to be either relocated, put in a metal box, or wrapped in a NFPA 701 rated fabric cover. Tech Engineering is area owner. Prompt correction is requested. This was identified as part of self-assessment AR 384793. <I> **** Actions Taken **** Wrote this CR and am notifying key people. <N> Discussed corrective actions with Fire Protection Program owner that met expectations and obtained approval from Plant Programs Supervisor. J. Twomey. JR Cantrell X4535 | 02-00-R-BLDG-MISC,02-00-T-BLDG-MISC,02-00-W-BLDG-MISC
384820 | CR | 20180924 | CAQ | C | TG 441â€™ East PC clothing creates a fire hazard | N | N |  | N | NO | <C> CR reopened at the request of the initiator so that a second assignment can be created to determine the final resolution. <D> **** Detailed Description **** Authorized storage area #81 contains the PC clothing station. This area has multiple problems including: 1) There are 6 large bins that are not in the designated taped floor area of the authorized storage area #81. See EDMS. 2) When this storage are first established, the bins were added into the combustible loading calc. However, the newer 6 bins discussed above have not been added into the combustible loading calc. It is unclear whether their addition had FP review. 3) PPM 1.3.10C states to do not store combustibles in concentrated amounts directly under cable trays. NUREG-1805 fire plume analysis indicates there needs to be at least 11 feet of horizontal clearance to not have cable damage and the actual horizontal distance is ~7.5 feet. 4) E-PP-F11/2 and E-PP-F11/3 face into the open bins of cotton and rubber. Although the separation of 40â€ meets the PPM 1.3.10C minimum requirement of 36â€, a fault of the power panels has a moderate potential to ignite the PCs since they are open and directly facing the power panels. . In summary, a worst case fire at this location could result in cable damage and extended outage. The area does have sprinklers that would provide different levels of fire mitigation depending on actual fire location. RP should close the bin doors, but the largest one has no metal doors. The area is being placed on hourly fire tour. This was identified as part of self-assessment AR 384793. <I> **** Actions Taken **** Wrote this CR and am notifying key people. <N> Assignment 01 was closed by RP, but Fire Protection reopened it. This deviates from NEIL criteria and will need further actions to come to final resolution. New assignments are being generated. | 02-00-T-BLDG-MISC
384828 | CR | 20180924 | CAQ | D | (NRC) D-DOOR-D111 - DG-1 Storage Tank Room | N | N |  | N | YES | <D> **** Detailed Description **** During a walkdown the NRC resident found the outside door knob for D-DOOR-D111 was sticking. This would cause the door to not latch when closed at times. Verified with the Fire Marshall and engineering that this is not an essential fire door, and does not require any comp measures beyond a BI. <I> **** Actions Taken **** Issued BI 18-0400. | 02-00-D-DOOR-D111
384834 | CR | 20180924 |  | 3 | Storage area #339 cart combustibles | N | N |  | N | NO | <D> **** Detailed Description **** The RB 548 CMS-SR-20/21 sample rack cart is stored in room R512 which is storage area #339. All authorized storage areas are considered permanent storage and any enclosed combustibles must be added to the combustible loading calc. They are not treated as transient until they leave the authorized storage area. The cart has excessive combustibles. See EDMS. It is requested that the existing cart have unnecessary combustibles removed and in the longer term, an enclosed cart be used. Prompt correction is requested. This was identified as part of self -assessment AR 384793. <I> **** Actions Taken **** Wrote this CR and am notifying key people. | 02-00-R-BLDG-MISC
384839 | CR | 20180924 |  | 3 | Painterâ€™s cage needs housekeeping | N | N |  | N | NO | <D> **** Detailed Description **** The TG 441â€™ NE painters cage needs housekeeping to minimize the amount of combustibles (especially plastics). Also clean area SE of kelly building. Cable trays come out of the floor in the painterâ€™s cage. Although there is sheet metal up to ~4 feet, above that the cables are exposed. A fire in the painterâ€™s cage could impact these cables and cause extended outage to pull new cables. The area does have sprinklers. Prompt correction is requested. This was identified as part of self -assessment AR 384793. <I> **** Actions Taken **** Wrote this CR and am notifying key people. | 02-00-T-BLDG-MISC
384840 | CR | 20180924 |  | 3 | Sheet metal on fenced storage area prevents ease of fire fig |  |  |  | N | NO | <D> **** Detailed Description **** TG 471â€™ west end of corridor is the welderâ€™s storage area. At the entrance, there is sheet metal attached to the fencing 99 inches high. See pictures in EDMS. It requires a key to unlock the chain lock. If there were a fire with flames coming through the gate gap at the lock, it would not be safe to unlock the door for proper fire -fighting. The sheet metal prevents a clear view of the area by the fire brigade. Direct spray through the fencing would result in less property damage. Request that sheet metal be removed. <I> **** Actions Taken **** This was identified as part of self-assessment AR 384793 | 02-00-T-BLDG-MISC
384841 | CR | 20180924 |  | 3 | TG 471â€™ east storage area needs housekeeping | N | N |  | N | NO | <D> **** Detailed Description **** The TG 471â€™ corridor east end storage area has poor housekeeping. There is a large amount of yellow plastic string lighting in two locations that could expose overhead cable trays to heat. See EDMS for the various unenclosed combustibles. All the loose combustibles and string lighting should be removed or placed in steel job boxes. Prompt correction is requested <I> **** Actions Taken **** This was identified as part of self-assessment AR 384793. <N> Williams Plant Services is evaluating and will take action on their items. 9/25/18 The tool crib ownes the string lights. Contacted the responsible shop manager and supervisor. All WPS items have been corrected. As left Pictures have been added to the EDMS file that show the clean up has been completed by WPS. | 02-00-T-BLDG-MISC
384842 | CR | 20180924 |  | 3 | Storage area #240 is in a combustible free zone | N | N |  | N | NO | <D> **** Detailed Description **** PPM 1.3.10C states to maintain a three foot of combustible free zone around significant heat generating sources including boilers. Authorized storage area #240 is within a foot of the TG 441â€™ aux boiler. The items in authorized storage area #240 need to be relocated. Storage area is owned by Operations. Prompt correction is requested. <I> **** Actions Taken **** This was identified as part of self-assessment AR 384793. | 02-00-T-BLDG-MISC
384843 | CR | 20180924 |  | 3 | Charging man-lift under plant cable trays | N | N |  | N | NO | <D> **** Detailed Description **** PPM 1.3.10A states charging of large batteries can be a fire hazard and unattended battery powered manlifts/fork lifts should not be parked under plant cable trays while being charged. There is one charging man-lift under cable trays at TB 441â€™ NE and another at RW 437â€™ N. In addition, neither are located within a designated floor taped authorized storage area. These should be unplugged until a new storage location is found. Prompt correction is requested. <I> **** Actions Taken **** This was identified as part of self-assessment AR 384793.
384844 | CR | 20180924 |  | 3 | Storage Area #132 North Has Poor Housekeeping | N | N |  | N | NO | <D> **** Detailed Description **** Authorized storage area #132 N is near rollup door T113. It has many exposed combustibles, untreated wood, foam, plastic, etc. It has job box doors that should be closed when not attended (PPM 1.3.10C). Area is owned by scaffolders. Prompt correction is requested. <I> **** Actions Taken **** This was identified as part of self-assessment AR 384793. | 02-00-T-BLDG-MISC
384845 | CR | 20180924 |  | 3 | Scaffold storage areas need to housekeeping | N | N |  | N | NO | <D> **** Detailed Description **** Field walk down finds small to medium amounts of exposed combustibles in almost all scaffold authorized storage areas. Authorized storage areas are considered permanent storage and any enclosed combustibles must be added to the combustible loading calc. They are not treated as transient (where more combustible amounts allowed) until they leave the authorized storage areas. Update of the combustible loading calc is only pursued if the combustible is needed and cannot be stored in metal job boxes or cabinets (so no longer exposed). Fire Protection requests: 1) prompt cleanup of unnecessary combustibles in each area; and 2) a job box be staged at each scaffolding storage area specifically for combustible items (rope, mesh, foam pads, etc). PC racks and trash cans can remain. <I> **** Actions Taken **** This was identified as part of self-assessment AR 384793.
384846 | CR | 20180924 |  | 3 | AED TEC TM-2115 apparent deltas |  |  |  | N | NO | <D> **** Detailed Description **** The following apparent deltas were noted for AED TEC TM-2115 (Technical Support Guidelines - Mechanical Engineer): This is used by the TSC Mechanical Engineer. 1) In Table 4-1: TO-HV-1A (1B,2A,2B) are described as TOA-HAV-1A (1B,2A,2B). WMA-FN-51A, WMA-FN-51B, WMA-FN-54A, and WMA-FN-54B are described as WMN-FN-XX rather than WMA-FN-XX. 2) In Figure 5-1 and Figure 8-2, COND-TK1A & should be COND-TK-1A & 1B. 3) In Figure 5.2 (probably should be Figure 5-2): The column furthest to the right (ELEV FROM SEA LEVEL) is cut off such that all the inches portion of the listed data is suspect (i.e., incomplete). 4) Figure 5-8 is completely illegible. 5) The Figure on page 129 of the Tech Memo does not have an indicated Figure number and is almost completely illegible. 6) Legibility of Figure 5-9 and Figure 5-10 could be improved. . <I> **** Actions Taken **** These apparent deltas were noted while reviewing the TSG in preparation for the 09/25/18 ERO Drill for Team D. Notified EP/ERO personnel. <N> AED TEC TM- 2115 R6 Figure 5-8 is currently an excerpt of an old FSAR Figure (FSAR Figure 2.1-6) that was based upon AED MIS SM250. This FSAR Figure is still included in the FSAR (FSAR Figure 3A.2.1-6 but is HISTORICAL). The update for AED TEC TM-2115 Figure 5-8 should be an excerpt from AED MIS SM250. AED TEC TM-2115 R6 Figure 5-9 is currently an old version of FSAR Figure 5.1-2 (from Amendment 52). The update for AED TEC TM-2115 Figure 5-9 should be the current version of FSAR Figure 5.1-2 (i.e., that from Amendment 53). The fluid volumes presented in the FSAR Figure do not appear to have changed with issuance of Amendment 53. AED TEC TM-2115 R6 Figure 5-10 is currently an old version of FSAR Figure 5.1-1 (from Amendment 52). The update for AED TEC TM-2115 Figure 5-10 should be the current version of FSAR Figure 5.1-1 (i.e., that from Amendment 64). Some of the data presented in the FSAR Figure has changed with issuance of updates between Amendment 53 and Amendment 64. The unnumbered Figure on AED TEC TM-2115 R6 page 129 is currently an old version of FSAR Figure 5.3-2 (from Amendment 37). This information is currently provided by FSAR Figure 5.3-3 (Amendment 53). The update for the unnumbered Figure on AED TEC TM-2115 R6 page 129 should be the current version of FSAR Figure 5.3-3 (from Amendment 53).
384847 | CR | 20180924 |  | 3 | Chemistry EOP sampling procedures require enhancement |  |  |  | N | NO | <D> **** Detailed Description **** EOP sampling procedures are as follows: PPM 12.17.1, EOP Reactor Water Sampling; PPM 12.17.2, EOP Suppression Pool Sampling; PPM 12.17.3, EOP Containment Atmosphere Sampling. All three of these procedures reference GEN-RPP-02, ALARA Planning and Radiation Work Permit, which is an older version of the procedure as it is now known as Radiological Planning and Control Process. The EOP procedures should be evaluated to ensure that items contained within still align with the standards in the current procedure revision of GEN-RPP-02 . Along with this, PPM 12.17.2 Step 7.14 references CI-13.6, which is a superseded procedure. This was a procedure used in performing gamma analysis with older ORTEC software. The references of PPM 12.17.2 have been updated to reflect the newer gamma analysis procedure CI-13.12, however this step (7.14) seems to have been overlooked. <I> **** Actions Taken **** Initiated this condition report for procedure enhancement.
384848 | CR | 20180924 |  | 4 | TMU-V-32A stuck open. | N | N |  | N | YES | <D> **** Detailed Description **** While trying to operate TMU-V-32A for PMT per WR 29144664 the valve was found to be stuck in the open position. TMU -P-1A will be tagged out for overhaul in a couple of weeks. This would be a good opportunity to replace TMU-V-32A. Please investigate and plan repair / replacement. <I> **** Actions Taken **** Wrote this AR/WR. <N> **** Equipment Description **** TMU pumphouse. | 02-00-TMU-V-32A
384850 | CR | 20180924 | CAQ | C | Determine M944 Applicability for Rosemont 3150 Series |  |  |  | N | NO | <D> **** Detailed Description **** The obsolete Rosemount 1150 series instruments are being replaced by the 3150 series. Drawing M944 Requirement: 11 on p 17 only lists the 1150 series. During a recent performance of PPM ISP-CRD-X303 (see CR-383193), the techs were unable to follow the procedure as the cover could not be physically tightened metal to metal as required by the procedure, nor was the o-ring replaced. The Rosemount 3150 Series OMM requires that the o-ring is replaced each time that the cover removed. The cover is also required to be installed and tightened metal to metal. Recommend Engineering evaluate the applicability of M944 Requirement 11 for the new Rosemount 3150 series. <I> **** Actions Taken **** Notified supervision.
384851 | CR | 20180924 |  | 4 | TSW leak on RRA-CC-7 piping Rx bldg truck bay cooler | N | N |  | N | YES | <D> **** Detailed Description **** TSW leak on RRA-CC-7 piping Rx bldg truck bay cooler <I> **** Actions Taken **** Informed MCR Laborers placed bucket to catch drops | 02-00-R-BLDG-MISC,02-00-RRA-CC-7,02-00-TSW-PIPE-MISC
384852 | CR | 20180924 |  | 4 | RCC Water pH Gt 8.5 and Conductivity GT 2.0 ÂµS/cm3 | N | N |  | N | YES | <D> **** Detailed Description **** Testing completed 9/24/18 resulted in RRC Water testing above the Chemistry AL-1 level (2.0 ÂµS/cm3 ) for conductivity (3.0 ÂµS/cm3) and above the AL-2 level (8.5) for pH (8.58) as outlined in SWP-CHE-02 Rev 28 Section 6.3.9. The higher than normal pH was previously noted in CR 384200 with the corrective action identified as a demin change out. Demin change out is currently scheduled for the week of October 1st. WR 02108127. <I> **** Actions Taken **** For Chemistry AL-2 level, the recommend action is to return the parameter to within the prescribe control band within 30 days. For Chemistry AL-1 level, the recommended action is to increase monitoring frequency as appropriate and return the parameter to within the prescribed normal operating range within 90 days. <N> **** Equipment Description **** RCC demin | 02-00-RCC-DM-1
384854 | CR | 20180924 |  | 3 | Revise TM-2082 |  |  |  | N | NO | <D> **** Detailed Description **** In TM-2082 Figure 1 inaccurately displays WMA-AD-54A1 and WMA-AD-54B1 in place of WMA-AD-51A1 and WMA-AD-51B1. I recommend revising this figure to match M548-1. See attached EDMS. <I> **** Actions Taken **** None
384855 | CR | 20180925 | CAQ | D | Unable to obtain vibe data points due to seal leak by. | N | Y |  | N | YES | <D> **** Detailed Description **** Craft was unable to obtain vibe location â€œprobe locationsâ€ POV, POH and POA on FPC-P-1A due to pump seal spraying in these locations (spraying directly on POA of pump) craft was directed by supervisor not to take these locations due to contamination risk(s). These vibes were in support of WO 02093391-03 OSP-FPC/IST-Q701. Craft was able to obtain inner pump vibes and all of motor vibe for FPC-P-1A. <I> **** Actions Taken **** Took vibes where we could, Wrote CR | 02-00-FPC-P-1A
384856 | CR | 20180925 | CAQ | D | RRA-CC-19 flow low | Y | Y |  | N | YES | <D> **** Detailed Description **** RRA-CC-19 flow low below the minimum operability requirements per OSP-SW-M102 at 31gpm (minimum flow is 42gpm). <I> **** Actions Taken **** Supervision was informed a partial OSP-SW-M102 was performed and flow was adjusted to 48gpm which is above the minimum operability requirement. | 02-00-RRA-CC-19,02-00-RRA-FC-19,02-00-SW-FI-71B,02-00-SW-FS-71B
384857 | CR | 20180925 | CAQ | D | Unable to get base plate for SGT-TC-1B2 to line up due to co | Y | N |  | N | YES | <D> **** Detailed Description **** When installing replacement SGT-TC-1B2 we are unable to bolt up the base of the switch to the base plate due to the conduits existing offset doesnâ€™t match the offset needed for this particular switch box. The old bend has been removed and reinstalled for years and you can tell by the scarring from pipe wrenches that in order to get the base plate holes to line up you need to put an excessive amount of cold load in the conduit ( pull it into place with a bar) to get it to work. We either need an new piece of Â¾â€ ridged conduit ben (approx. 16â€ long) or see if the electrical spec allows us to use flex to the switch box and if so we need to have all of these similar connection changed to flex in the future to eliminate this issue. <I> **** Actions Taken **** Stopped work, Wrote CR, need electrical support | 02-00-SGT-TC-1B2
384858 | CR | 20180925 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 238kv B: 239kv C: 239kv E-TR-B A: 119kv B: 118kv C: 118kv The following sensors were tripped and are reset: J-7 BPA reports the following: a. Cause was Momentary open and reclose of vantage -Shultz#1 b. Relaying involved a single pole c. no damaged equipment d. line reclosed e. no emergent outage needed f. neither 230kv or 115kv involved g. no line equipment outage needed h. N/A i. 2327 j. 500Kv system k. no RAS initiated l. no Grid frequency change <I> **** Actions Taken **** Followed ARP
384860 | CR | 20180925 | CAQ | D | while performing 02118985-01 computer point L102 found OOT | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** computer point found OOT L102 for loop SGT-MT-16B 2% low at bottom of scale 4% low at top of scale the rest of the loop is SAT <I> **** Actions Taken **** Created CR&WR <N> **** Equipment Description **** SGT-MT-16B
384861 | CR | 20180925 |  | 3 | VESDA Fire Detection Modification EC 16066 | N | N |  | N | NO | <D> **** Detailed Description **** During the final testing of VESDA Fire Detection Panels FP-CP-ISD/2 and FP-CP-ISD/3 problems were identified with respect to a valve stuck open in one of the input piping (FP-CP-ISD/2) and relay operation (FP-CP-ISD/3). In both cases, the detection panels do not meet acceptance criteria for Post Modification Testing and Procedure 15.2.49. The vendor (Xtralis has been contacted and resolution strategies have been identified for both panels. There are no consequences since the VESDA panels are still going through the initial testing and have not been turned over to Operations. The smoke detection function in the affected area is performed by existing ionization detectors (Zones 22 and 23). <I> **** Actions Taken **** Contacted the Vendor (Xtralis) and based on their recommendations identified the following Corrective Actions: 1. Replace the control board in FP-CP-ISD/3. 2. Using the new software version VSC 3.07, correct the stuck open valve in the input piping associated with FP -CP-ISD/2. | 02-00-FP-CP-ISD/2,02-00-FP-CP-ISD/3
384862 | CR | 20180925 |  | 3 | Potential Trend: Personnel Contamination Events (PCEs) |  |  |  | N | NO | <D> **** Detailed Description **** During the August 2018 FAS meeting, a potential trend in Personnel Contamination Events (PCEs) was discussed. Since January there have been 4 PCEs (2-Level 1 and 2-Level 2). This condition report is being initiated to validate the potential trend by completing a Trend Validation Worksheet per TM-01, Trending Manual. <I> **** Actions Taken **** Recommend a NCAQ, 3/RPOPS.
384863 | CR | 20180925 |  | 3 | Potential Trend: RP Exposure Budget Performance |  |  |  | N | NO | <D> **** Detailed Description **** During the August 2018 FAS meeting, a potential trend in Radiation Protection Exposure Budget Performance was discussed. Over the last year, there have been 8 months where RP personnel exceeded the monthly dose budget and 5 months where the RMC Laborers exceeded the monthly dose budget. This condition report is being initiated to validate the potential trend by completing a Trend Validation Worksheet per TM-01, Trending Manual. <I> **** Actions Taken **** Recommend a NCAQ, 3/RADPL.
384864 | CR | 20180925 | CAQ | D | SFS-STORM-003 status indicates yellow | N | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02120279 then taken back to complete <D> **** Detailed Description **** SFS-STORM-003 status indicates yellow <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-SFS-STORM-003
384865 | CR | 20180925 |  | 3 | OPDS 230 kV bus pedestal jam nuts do not have threads showin | N | Y |  | N | YES | <D> **** Detailed Description **** During a walkdown for the CCVT project, BPA Civil Engineering representative identified that in nine 230 kV OPDS bus pedestal locations the jam nuts did not have threads protruding through them (see EDMS for picture example). Their concern is long term water accumulation will eventually lead to rusting. BPA recommends filling the voids with silicon sealant/RTV. Recommend filling the voids with RTV <I> **** Actions Taken **** Contacted Supervision and initiated work request to fill voids in jam nuts. <N> **** Equipment Description **** OPDS 230 kV Bus Pedestals North of TRS . Condition with jam nuts not having exposed threads is acceptable as is (see assignment 01 response) and it is recommended by engineering to seal the top of the nut and bolt with a silicon sealant/RTV (see WR 29144749). . No further actions required. This AR-CR is now closed. . | 02-00-OPDS-TR-S
384866 | CR | 20180925 |  | 4 | New clearance and ALARA Task needed for job at Ready status |  |  |  | N | NO | <D> **** Detailed Description **** Good catch by Ops Dose Champion (who is also the OPS PROCEDURE SUPERVISOR). They were reviewing up coming work schedules and recognized that a job (02031323) at T-4, in a High Rad Area, would need an Alara Task for Ops to hang tags. Although the job was at Ready status, they took the extra step to verify the alara task was ready and had a proper dose estimate. Ian discovered that the clearance order had been cancelled and a new one is required. This is a good catch. <I> **** Actions Taken **** Initiated this CR for trending. The ALARA Task is being reviewed to ensure it is still accurate (this job has been off the schedule for 2 years), and Ops WC is generating the new clearance. No additional actions required. <N> CR Edited to remove names. CR has been incorporated into the monthly dose budget planning process.
384871 | CR | 20180925 |  | 4 | eDNA Web - eDNA View Active X issue in TSC/OSC | N | N |  | N | NO | <D> **** Detailed Description **** When bringing up the Plant Status View, and others, the spinner appears for about 2 minutes, then stops and displays an Active X message. <I> **** Actions Taken **** Advised user to use te eDNA Veiw client installed on the PC.
384872 | CR | 20180925 |  | 4 | HP-EQ-42808 (chemistry sample cart) fan belt was cracked | N | N |  | N | YES | <D> **** Detailed Description **** While on operator rounds it was observed that the fan belt for HP-EQ-42808 was found cracked. The chemistry sample cart was not in service at the time. <I> **** Actions Taken **** Wrote CR and notified CRS | 02-00-HP-EQ-42808
384875 | CR | 20180925 |  | 4 | RB NE elevator is out of service | N | N |  | N | YES | <D> **** Detailed Description **** The RB NE elevator is stuck on the RB 471 elevation with the doors open and the elevator stuck one foot above floor level . The disconnect for the elevator was cycled twice but the elevator remains stuck. The doors on the elevator looked to be properly aligned. <I> **** Actions Taken **** Notified CRS and wrote CR. | 02-00-MT-ELEV-1
384876 | CR | 20180925 |  | 3 | MCR equip tag printer broken still (GT 2 months) | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Zebra ZT510 equipment tag printer in main control room from previous discussions it appears this may be a network card issue - remains unresolved after several months <N> CR found at INPROG, moved to Approved Status.
384877 | CR | 20180925 |  | 4 | Error code on FDR-CRS-35 | N | N |  | N | YES | <D> **** Detailed Description **** This is the conductivity meter used for FDR processing. The error is "E200 Operation aborted becuase an error was found on media." Speaking with With an I&C Technician, the code will require the memory card to be either replaced or reformatted. He recommended creating a WR and replacing it. Its currently reading properly, just not recording data. FDR processing can take continue as normal. <N> CR edited to remove names. | 02-00-FDR-CRS-35
384878 | CR | 20180925 |  | 3 | AR 00383632 improperly closed / rework |  |  |  | N | NO | <D> **** Detailed Description **** CR equipment tag printer still does not print. AR closed to an evaluation for different printers. The old style and the current style printers are available on site (one in the MCR and others in SSS office). The control room needs to have the ability to print tags now and at all times in the future. Do not close this to an evaluation for future equipment. Suggest OPS management be updated on status so this does not continue to be closed out with the equipment not functional. <N> CR edited to remove names.
384879 | CR | 20180925 |  | 4 | Training Records Sent to Records Control without Transmittal |  |  |  | N | NO | <D> **** Detailed Description **** On 9/25/2018 Two Training Records (ETARS) were submitted to records control without a transmittal attached. Please refer to SWP-REC-02 Section 4.3.2 and GBP-REC-04 Section 4.7.1 for the submittal process of these types of Records. <I> **** Actions Taken **** Notified my supervisor. Sending records back to Training Support for correction/resubmittal. <N> Records were received by Training Support, and individual who submitted records was coached by Records Coordinator's of the department to follow the correct submittal process. Records are to be resubmitted following the correct process. As a lesson learned, individuals who may be submitting records in the future have been coached as to the correct submittal process as well.
384880 | CR | 20180925 | CAQ | D | M&TE OOT | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #44932 Ashcroft Compund Gauge- model Duragauge 15psig/30inhg found OOT & adjusted within specs. EFIN Eval: #02100885-01 Not used for data. No further action required. #02100668-01 Gauge used for trending data only. No further action required. #02089593-01 Gauge used for Calibration of DO-PI-5. This Calibration will need to be re-performed. DEF #6736A written. <I> **** Actions Taken **** Notified I/C Supervisor to re-perform DO-PI-5
384881 | CR | 20180925 |  | 3 | (QA) Housekeeping on RW 487' does not meet station standards | N | N |  | N | NO | <D> I was doing an observation of Chemistry performing PPM 16.11.6 (WO 02124989) as part of a Chemistry Station Audit. I started to look around the WEA-SR-25 surrounding area, which is on Radwaste 487'. I was astounded by the housekeeping on the floor. We, as a station and every department within it, need to look at the attached pictures, look within, and address this floor immediately. It does not meet any of our standards and expectations. It is clear that multiple groups have contributed to the mess on this floor. This is a clear station problem, not one or 2 departments. Below is a list of items that I observed, some of which can be seen in the attached pictures. -2 instances of extension cords plugged in to pig tails. -Extension cords that are plugged in, but have nothing plugged in to them. -Grease on the floor underneath a piece of equipment. -Multiple pig tails that have nothing plugged in to them. -Extension cords lying on the floor, not being used. -Multiple locations where rope (flammable) is keeping extension cords in the overhead. -Multiple Work In Progress signs that are out of date. -Gas bottles that are not secured properly. A bottle is tied off loosely enough it could be easily knocked over. There is no cap on a stored gas bottle. -A Chemistry Keep Area Clear where the candy striped tape is almost gone. In addition, an extension cord and a Tygon tube are going through the Keep Area Clear. -Grease pads that are old, used, and need to be thrown away. -General items and garbage on the floor that need to be put or thrown away. -Work bench that needs to be cleaned up. <I> II have contacted individuals in Williams (Site Support), Chemistry, and I&C to take care of items that I know that they are responsible for. I have contacted an RP Supervisor as they are the Floor Coordinators. This will be discussed at the 1500 Work Production Accountability Meeting today. I have discussed this with my management. <N> CR status at INPROG, moved to Approved status at the request of the initiator. This was identified during a Chemistry Audit (AU-CH-18). | 02-00-W-BLDG-MISC
384883 | CR | 20180925 |  | 3 | HT-HTP-FP/23 |  |  |  | N | YES | <D> **** Detailed Description **** Craft was unable to start WO# 02094185-01 due to no support task assigned for local clearance, soil excavation, soil sampling, insulation removal and etc as per history located in PMRQ 00019867-02 <I> **** Actions Taken **** Craft advised supervision, WWM, PSRO and Planning, returned WO# 02094185-01 to returned status. <N> **** Equipment Description **** HT-HTP-FP23 is located in TG 441 A/15.1 Circuit 19F & 20F is located in Transformer Yard Per drawning AED-ELEC-E599-1 | 02-00-HT-HTP-FP/23
384884 | CR | 20180925 |  | 4 | E-FI-M1/80P2 indicating flow with pump off | N | N |  | N | YES | <D> **** Detailed Description **** E-FI-M1/80P2 was found indicating flow when E-P-M1/P2 was not running. <I> **** Actions Taken **** Notified CRS | 02-00-E-FI-M1/80P2
384885 | CR | 20180925 |  | 4 | Poor lighting in RX 501' hallway in stay clear area | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The lighting at the east end of the RX /TG 501' hallway is very poor. The area is marked stay clear but it is not easily seen due to the poor lighting. It is also hard to read the instrumentation at that end of the hallway. Recommend fixing the lighting in that area. <I> **** Actions Taken **** Notified MCR, supervision <N> **** Equipment Description **** the area where the stack monitor connections on the RX / TG 501' hallway east end. | 02-00-R-BLDG-MISC,02-00-T-BLDG-MISC
384886 | CR | 20180925 |  | 3 | ARP 4.603.A7.1-2 minor revision |  |  |  | N | NO | <D> **** Detailed Description **** The REACTOR SCRAM A1 AND B1 LOGIC alarm response procedure requires a minor editorial revision. The setpoint for the SRM HI HI trip is 2x10E5 CPS and the arp lists it as 2x105 cps. 4.603.A8 might requie the same revision.
384887 | CR | 20180925 |  | 3 | IEBS Computer not functioning as designed |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** It was discovered during the IEBS sync process that several badge photos had not transferred correctly. <I> **** Actions Taken **** Photos manually loaded to Lenel. Underlying cause under investigation by Computer Engineering.
384888 | CR | 20180925 | CAQ | C | (QA) SSW Scaling Risk Not Fully Evaluated | Y | N |  | Y | YES | <D> **** Detailed Description **** (QA) Unexpected level of Standby Service Water (SSW) pipe scaling discovered and removed in 2012 as part of High Pressure Core Spray Cooling Coil (RRA-CC-4) piping inspection/replacement was not fully evaluated for risk to the Standby Service Water (SSW) system for other similar configurations. (See EDMS for full details) <I> **** Actions Taken **** Notified Engineering, Chemistry, Quality, and Shift Manager. This issue was identified during the Chemistry Audit AU-CH-18. <N> **** Equipment Description **** Standby Service Water System, Both Trains, are potentially affected by chemistry conditions. | 02-00-SW-PIPE-MISC
384891 | CR | 20180925 |  | 4 | EOF Microphone System Not Functional During ERO Drill | N | N |  | N | YES | <D> **** Detailed Description **** The primary EOF microphone system was not functional during the ERO drill. <I> **** Actions Taken **** Performed initial troubleshooting. Found issue with receiver that could not be readily resolved. Placed secondary system in operation. <N> **** Equipment Description **** Kootenai Room 140
384892 | CR | 20180925 |  | 4 | Datapump Export Process Issue |  |  |  | N | NO | <D> **** Detailed Description **** Friday, Sept 21, the Datapump export processes ran as scheduled, but aborted apparently due to memory allocation issues. The abort left an internal session active that cannot be stopped using conventional means and can only be removed by an eSOMS database restart. The presence of this rogue session is preventing Datapump from running at all on this database, so logical backups are currently not being created. <I> **** Actions Taken **** IS to communicate and perform an eSOMS database restart. Notified IS Leadership. Created the CR.
384893 | CR | 20180925 |  | 3 | EOF Eng. Mgr. Computer Issues During ERO Drill |  |  |  | N | YES | <D> **** Detailed Description **** The EOF Engineering Manager computer (service tag BXX9QM1) could not access corporate applications. This computer is classified as a Critical Digital Asset (CDA). <I> **** Actions Taken **** Performed initial troubleshooting that did not readily resolve issue. Provided corporate laptop to EOF Engineering Manager for use. <N> **** Equipment Description **** EOF
384894 | CR | 20180925 |  | 3 | ERO personnel reported to EOF without DLR |  |  |  | N | NO | <D> **** Detailed Description **** On 9-25-18. an ERO drill participant reported to the EOF without their issued DLR. The individual was issued an ERO DLR. <I> **** Actions Taken **** Notified the EP Center Lead and the Emergency Director.
384895 | CR | 20180925 |  | 4 | GMA-M-FN/4, motor feet cracked | N | N |  | N | YES | <D> **** Detailed Description **** During sheave and pulley replacement of GMA-FN-4 on WR#29144591 it was noted that the two of four motor feet has a crack. Also, the ground strap from the motor to the frame is broken. GMA-FN-4 was returned to service and runs smoothly with not indication of near term failure. The intent of this CR and WR is to plan work order for future motor replacement when warranted. <I> **** Actions Taken **** Notified FIN electrical supervisor. <N> **** Equipment Description **** GMA-M-FN/4 is NSR, Quality class G and Crit R equip | 02-00-GMA-AC-3,02-00-GMA-FN-4,02-00-GMA-M-FN/4
384896 | CR | 20180925 |  | 4 | Outage tasks moved in schedule |  |  |  | N | NO | <D> **** Detailed Description **** Work order 02111978-01 and 02111979-01 were moved in the Outage schedule without consulting with the work group owner. The Scheduler placed this task into the schedule a few weeks prior based on the need for the Plant Vacuum pull. The Scheduler also placed a note on the task stating these work orders require vacuum pull. This also affects all of the efforts to levelize Outage resources and establish a Department budget as directed by Outage Management. Moving this task caused re-work to move the item into the correct schedule location. <I> **** Actions Taken **** Contacted individuals involved and placed the task into the correct location. | 02-00-MS-HX-1A,02-00-MS-HX-1B
384897 | CR | 20180925 |  | 3 | ECNF Software Stopped Working During Training Drill |  |  |  | N | NO | <D> **** Detailed Description **** During the training drill on 9/25/18, ECNF stopped responding at the Assistant EOF Managerâ€™s computer. CNFs were successfully filled out by hand but the software failure challenged the ability of the EOF to make timely notifications. <I> **** Actions Taken **** Discussed at the EOF drill debrief. Discussed with the EOF Coordinator. PPM 13.4.1 allows for either Form 24075 (CNF) or the ECNF to fillout the CNF. A failure of the ECNF would then require the use of the manual form (24075), so the ability to complete notifications was not restricted by a failure of the ECNF.
384898 | CR | 20180925 |  | 3 | Procedure change request for 10.25.141A |  |  |  | N | NO | <D> **** Detailed Description **** Request procedure revision per attached mark-up in EDMS to "Installation of Electrically Operated Ground Devices" to streamline the process of installing and removing ground test devices <I> **** Actions Taken **** Attached marked up copy of current revision, discussed changes with Operations management. <N> An assignment has been made within the Maint. Procedure revision data base. A link has been created within the edms of this AR to the Maint. procedure revision data base.
384900 | CR | 20180925 |  | 3 | NEIL Property Loss Control 2018 Should Observation |  |  |  | N | NO | <D> **** Detailed Description **** NEIL Property Loss Control 2018 Should Observation â€“ As documented in GI2-18-073, evaluate and document and/or correct the excessive storage of combustible materials in the Radiate 507â€™ demineralizer room. This is contrary to NEIL Standard 3.2.20.5.5 which states that automatic fixed extinguishing systems â€œshouldâ€ be provided for any building, room, or area where combustibles are stored; see 18-01-RW. Minimizing the amount of combustible material in this space could reduce the probability and severity of a loss occurring. <I> **** Actions Taken **** CR initiated.
384901 | CR | 20180925 |  | 3 | 2018 TFOF Evaluate Badge Types at Checkpoint (NRC) |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate access criteria for specific badges at Security Checkpoint.
384902 | CR | 20180925 |  | 4 | OPS 3 Watchstation AED's |  |  |  | N | YES | <D> **** Detailed Description **** OPS 3 Watchstation AED's were found to be facing the wrong way in the enclosure. The green rescue ready lamp should be readily visible through the clear glass on the front of the enclosure. With the AED's facing the wrong way, that was not the case. One encolsure was also found with the door unlatched and open. <I> **** Actions Taken **** AED's turned to face the right way, doors closed and latched. CR initiated. Supervision Notified. <N> **** Equipment Description **** AED's facing the wrong way in the enclosure.
384903 | CR | 20180926 | CAQ | C | Wrong Revision of OSP-ELEC-M703 in eWP After Validating |  |  |  | N | NO | <C> CR moved to CAQ and Severity C at the request of OFM on 9/27/2019 <D> **** Detailed Description **** Work order 02124840 task 01 is the monthly DG-3 operability test, OSP-ELEC-M703. In DataGlance, I selected â€œvalidate allâ€ from the validation screen. Normally if there is a more current revision, the program will flag it as such and give the option to append or replace the old revision. In this case, DataGlance stated that â€œDocuments are all valid.â€ Prior to commencing the surveillance, CRO3 did a second check comparing the revision in DataGlance to the revision in Portal J and found the DataGlance version was a superseded revision (Major rev 066, minor rev 001) while Portal J contained the current revision (Major rev 067, minor rev 001). <I> **** Actions Taken **** Informed shift manager that this could have easily resulted in performing a surveillance on the incorrect major revision. Printed a hard copy of the correct revision to be completed on paper then scanned into DataGlance. Until this issue is resolved, all surveillances performed in DataGlance should be rev-checked using portal J or other level 1 document sources. Reccomend considering a thorough audit of past surveillances to check for incorrect revisions of surveillances performed due to this previously unknown issue.
384913 | CR | 20180926 |  | 4 | BRE 31 Light bulbs |  |  |  | N | NO | <D> **** Detailed Description **** Bre 31 light bulbs inop <I> **** Actions Taken **** Supervision notifiyed CR Initiated
384925 | CR | 20180926 | CAQ | D | Franklin county siren C16 reported a partial alarm | N | Y |  | N | YES | <D> **** Detailed Description **** While doing the weekly poll test of the Franklin county sirens, 16 reported a partial alarm. This means one or more of the 10 amplifiers is not working and will reduce the output volume. <I> **** Actions Taken **** Notified EP, Dispatched techs to resolve the issue. Note: A follow-up status test was conducted and found the siren fully functional with no alarms. Telecom will still be doing an on sight inspection. Recommend closing to WR. ITMGMT 4 <N> **** Equipment Description **** Franklin county
384926 | CR | 20180926 |  | 3 | Report Phish button not showing on Outlook ribbon |  |  |  | N | NO | <D> **** Detailed Description **** Report Phish button is not available for users to report phishing emails on the Outlook ribbon. Attempts to run MS Office Repair or ensure Outlook Add-Ins is enabled does not fix this issue. <I> **** Actions Taken **** Generated CR to correct condition.
384928 | CR | 20180926 |  | 3 | Need procurement to communicate CAT ID LOU changes to Planni |  |  |  | N | NO | <D> **** Detailed Description **** LOU change on part where MR are assigned to Planned WOâ€˜s need to be communicated to planning so they can incorporate those changes. The limitations on use for CAT ID 68604340 had been recently changed and could have affected the upcoming DG1 Outage. The LOU required a burn in time and a Hot Restart per TSP-DG1-B502. This was not known at the time of planning the task. <I> **** Actions Taken **** Changed instructions in WO 02084370 to include burn in time and WC add TSP-DG1-B502 to the DG fragnet scheduled for next week. This was a good catch by a Relay tech.
384929 | CR | 20180926 |  | 3 | Exam Failure - ES000613 - PSA |  |  |  | N | NO | <D> **** Detailed Description **** One student failed the ES000613 - PSA exam conducted on 9/25/18. This CR is being writter per direction of TDI-02, Rev 35, section 4.4.10.p.3 <I> **** Actions Taken **** Notified appropriate line and training supervisors.
384934 | CR | 20180926 |  | 3 | Leads found lifted in E-CP-C91/P607E | N | N |  | N | YES | <D> **** Detailed Description **** During investegation of computer point F038 (COND-HX-2C SHELL PRESS) under WR 29123094 I&C Tech discovered that that the cause of the failed indication was that the leads to the computer input assembly were found determed and taped. <I> **** Actions Taken **** Wrote CR and WR | 02-00-BS-PT-2C
384935 | CR | 20180926 | CAQ | C | Work Order packages not sent to records |  |  |  | N | NO | <D> **** Detailed Description **** Work Order packages not sent to records prior to 60 days due to either lost or incorrect job type <I> **** Actions Taken **** uploaded a list to EDMS
384937 | CR | 20180926 |  | 3 | Near miss compressed gas bottles moved without transfer cart |  |  |  | N | NO | <D> **** Detailed Description **** Two individuals were observed moving compressed gas bottles in the 441 hallway without the use transfer carts. After coaching, the individuals stopped immediately, obtained carts and used them to continue their tasks. This behaviors does not meet the material handling standards as described in ISPM-15. <I> **** Actions Taken **** The individuals were interviewed to find out why they were not using the carts. They stated that carts were not available to use and did not think it was an issue and were not familiar with the requirements and they accepted the coaching they received. They were coached on evaluating the task and use error prevention tools and they must stop and ask questions when faced with uncertainty and not make assumptions. In addition a stand down was held with the whole group, the requirements of ISPM-15. ISPM-2. The discussion during the stand down also included stopping and expanding the team when uncertain in any situation not just transferring bottles.
384938 | CR | 20180926 |  | 3 | Outage walkdown indicator discrepancy |  |  |  | N | NO | <D> **** Detailed Description **** The outage indicator showing WOTs available for walkdown is not factoring in those WOTs with a Discipline Review (DR) hold code. The DR code is similar to a walkdown code, as it prevents the WO from advancing to Ready status until the hold is removed. This is a new hold code created during implementation of the electronic work package project. The discrepancy is not impacting the percentage of walkdowns completed shown on the indicator; itâ€™s only impacting the number of WOTs showing available for walkdown. Outage Management will revise the indicator to include the code. Assign as Severity 3 to AR-OTMG for resolution.
384939 | CR | 20180926 |  | 3 | Procedure change request for OI-12/ 1.3.64 |  |  |  | N | NO | <D> **** Detailed Description **** OI-12 step 3.2.2 currently requires a danger tagged vent /drain for personnel protection. In practice we always Danger tag at least one path to vent/drain in all cases. Clarification should be provided that explains this is only required if reaccumulation of hazardous energy is possible. Typically this should be for high energy boundaries where double valve isolation is not assured, or significant leak by requires the use of a drain path for worker safety. Open systems that lack any motive force to become hazardous do not require a Danger tag. An example would be the Service Water system where the pump itself is Danger tagged out. There is no credible method to repressurize the system without the pump. Please update OI-12 and 1.3.64 as needed to provide this clarification. Reference Self Assessment 358034-08. <I> **** Actions Taken **** initiated CR.
384940 | CR | 20180926 |  | 4 | TMU Pump A Prelube Flow Low alarm during WR 29144679 | N | N |  | N | YES | <D> **** Detailed Description **** During investigation of conditions described by WR 29144679, craft requested TMU-V-18A to be opened. When TMU-V-18A was opened, TMU PUMP A PRELUBE FLOW LOW alarm (H13-P824.M.7-3) soon followed. The craft was informed that this alarm had come in. After craft completed their work, TMU-V-18A was closed, and the alarm clearly shortly thereafter. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-TMU-FIS-5A
384941 | CR | 20180926 | CAQ | C | Mobile Fire Response Vehicle needs permanent relocation | N | Y |  | N | YES | <D> **** Detailed Description **** Security concern with the existing Mobile Fire Response Vehicle (Brigade Truck) adjacent to Building 62 needs to be evaluated and an acceptable new location found. FP Engineer and Security Officers conferred on possible relocation and found that moving the truck South of B62 and shifting the parking spot a few feet West of the SW corner of the building was adequate. A conflict arose because the truck's battery charger, a small (.8 amp) trickle charger, needs to be energized at all times to keep the vehicle operable. The current 120 VAC outlet for an extension cord is on the North side of B62. A 100 ft extension cord is barely long enough. This AR needs to be assigned to AR-TEFP to determine the optimum location for the Brigade truck and then ensure that an all-weather extension cord, with suitable waterproof end covers is purchased or custom made to accomodate this new location. Change Management should include notifications to all Brigade and Maintenance personnel on the new parking location and the means to keep the battery charger energized at all times. <I> **** Actions Taken **** 1. Brigade truck has been moved to accomodate Security concerns. 2. Existing 100 ft extension cord has been routed to the Brigade truck and the battery charger is still energized as required by CR 306670 and LCS 1.10.4.B. <N> **** Equipment Description **** Mobile Fire Response Vehicle located by Building 62
384942 | CR | 20180926 | CAQ | D | During Quarterly PM HPCS-B1-DG3 cell 1 did not meet criteria | Y | Y |  | N | YES | <D> **** Detailed Description **** While performing ESP-B1DG3-Q101 HPCs-B1-DG3 cell 1 cell voltage did not meet the 2.13 VDC criteria with a value of 2.12 VDC but was greater then the 2.07 VDC. <I> **** Actions Taken **** Notified Shift Manager of the requirement to enter into LCS MEasure 1.8.6.2F per Attachement 9.2 of ESP-B1DG3-Q101. Contacted System Engineer who recommended placing HPCS-B1 -DG3 on Equalize Charge. | 02-00-HPCS-B1-DG3
384944 | CR | 20180926 |  | 3 | Incorrect FD-P-15 connection on CVI 206-04,225 |  |  |  | N | NO | <D> **** Detailed Description **** The drain line connection from FD-P-15 to 3â€ FD(56)-1 is depicted on the incorrect side of the P-Trap on CVI DWG 206-04,225. The discharge of FD-P-15 is connected to the westernmost (upstream) side of the P-Trap, as the easternmost portion of the P-Trap is encased in concrete. Ref. M568 and see EDMS for picture. | 02-00-FD-P-15
384949 | CR | 20180926 |  | 3 | Missing Task for WO 02100571-01 |  |  |  | N | NO | <D> **** Detailed Description **** During performance of ISP-RBM-B302, the last step required the performance of ISP-RBM-S402. There was no support task to perform ISP-RBM-S402. Wrote CR for Trending Purposes <I> **** Actions Taken **** Wrote CR, provided feedback to planning to create a support task for future W/O's, Communicated with Shift Manager, CRS, Work Control.
384950 | CR | 20180926 |  | 4 | E-CB-1/500S shutter arm misaligned | N | N |  | N | YES | <D> **** Detailed Description **** While racking in E-CB-1/500S it was observed that the shutter arm lined up with the very edge of the shutter lift roller so breaker position was adjusted until it appeared a better alignment was created. After racking in breaker the shutter arm was found resting upon the E-Clip outside the roller edge. Work stopped and supervision was contacted by Ops and Elec. SSS took a look and agreed with elec recommendation to rack out the breaker and see if simple adjustment might fix alignment. See CR 384952 for rack out. The shutter arm appears to have a bend towards the right hand wall at the weld between the forward pivot point and the rear shutter lift section. <I> **** Actions Taken **** Informed CRS, SSS, Elec sup. racked out breaker. | 02-00-E-CB-1/500S
384952 | CR | 20180926 |  | 4 | E-CB-1/500S trouble racking out | N | N |  | N | YES | <D> **** Detailed Description **** See CR 384950 for rack in. Upon attempting to rack out E-CB-1/500S the screw got very stiff part way through the rack out and it seemed to be caught on something so it was racked back in and the breaker tension adjusted itself then ops reracked out. Discovered several stab clusters were now misaligned. Elec began to take data on breaker and it appeared that at least the upper right hand stab was higher than the other upper two. <I> **** Actions Taken **** Informed CRS, SSS, Elec sup; turned brkr back over to Elec. | 02-00-E-CB-1/500S
384953 | CR | 20180926 | CAQ | C | Lessons Learned SW pond inspection | Y | N |  | N | NO | <D> **** Detailed Description **** During cleaning activities of the SW spray pond walls in support of the MRule Structural Inspections (of the submerged portions) of the ponds that approximately a sixty foot by one foot strip of debris have collected at the bottom of the pools. The max depth was found to be approximately 4 inches. This (opportunistic and nonintrusive) structural inspection is in support of license renewal and is the 1st inspection (baseline) before an additional one before beginning of the period of extended operation (PEO) in 2023. This inspection was strategically selected to occur after sediment removal; in that manner, turbidity will be reduced to allow better water clarity; however, it was determined that the selected portions of walls could not be inspected because of the presence of large amount of buildup making the surface defect detection almost impossible. Because of of the License Renewal commitment, removal of the (algae, organic matter, nutrient, scale) buildups are required to allow the inspection to proceed. This removal resulted in approximately a Â¼â€ difference between the as found wall and the clean wall. A sample of the removed material was provided to chemistry for analysis. Initial opinion is that there is a mix of biologicals and concrete as the preparation of the surface removes a small amount of base material. Since the condition is localized, the continued functionality, operation, and ability to maintain design function for the SW ponds will remain unaffected by the aforementioned condition; it will contribute to the generation of (the suspended solids, insoluble organic buildups) sedimentation deposits. The current amount can be estimated as follows: If we just account for the walls we cleaned we have 561 gallons of displaced water or 75 cubic feet or a total distributed sediment depth of 7/64â€. Consideration being given to the fact that we removed some base material the net effect on the SW pond is negligible although this material may be identified by the sonar boat inspections. For future planning if the entire wall surface area is prepared or cleaned for inspection the material generated would be: 250â€™ x 15â€™ x 4 walls with .25â€ thick layer. This is 312 cubic ft displaced or 2337 gallons. Which equals .4488 inches of sediment if considered on the bottom. It would be necessary to prepare the walls before dredging of the ponds. Recommend action(s) to cross reference CR to WO for PMID (22156), â€œSTRUCTURAL MRULE, STRUCTURAL INSP - NON-OUTAGEâ€ and share lesson(s) learned with proper stakeholders (Civil Engineers and Rx Maintenance) to ensure walls are prepped prior to dredging and preventing similar issues from reoccurring during next SW pond inspection. <I> **** Actions Taken **** Wrote CR, Called SM <N> **** Equipment Description **** SW Pond equivalent depth is 1/64"
384959 | CR | 20180926 |  | 4 | Lost Simulator Time During EP Drill |  |  |  | N | NO | <D> **** Detailed Description **** On 9/25/2018, during the EP drill, a THOR abort occurred. 60 minutes of lost time occurred due to the abort. All but one EP objective was met when the abort occurred. EP completed the objective by providing instructor cues to drill participants. SR 2812 was written to document the THOR abort and resolve it in accordance with TDI-06, Simulator Management. <I> **** Actions Taken **** CR and SR written.
384967 | CR | 20180926 | CAQ | C | Typo in LCS 1.8.6.2.F Bases |  |  |  | N | NO | <D> **** Detailed Description **** LCS Compensatory Measure 1.8.6.2.F.1 has a completion time of 24 hours to verify all cell float voltages GE 2.07 VDC but the bases for compensatory measures F .1 says "2 hours is a reasonable amount of time to perform the required verification that the voltage GE 2.07 VDC". It appears that the bases need to be updated to reflect the allowed 24 hours vice 2 hours stated. <I> **** Actions Taken **** Wrote CR.
384971 | CR | 20180926 | CAQ | D | SGT-AD-1B2 flow is 2000 cfm at 85% now. | Y | N |  | N | YES | <D> **** Detailed Description **** Following lube and inspect of SGT-AD-1B2 the flowrate has changed. SGT-DPIC-1B2 flow at 85% is now 2000 cfm, historically the controller can be taken to 100% in manual before flow drops to 2000 cfm. WO# 02087556 <I> **** Actions Taken **** Informed CRS | 02-00-SGT-AD-1B2
384972 | CR | 20180926 | CAQ | D | while performing 02092541-06 found SGT-TC-1B1 OOT | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** the removed SGT-TC-1B1 as found was OOT during a bench calibration befor retuning to stores. <I> **** Actions Taken **** Adjusted to within specifications was 3.3 Â°F high at set point of 90Â°F tolerance of Â±2Â°F | 02-00-SGT-TC-1B1
384973 | CR | 20180927 |  | 4 | Yellow Barrell for ABN on Rx572 moved out of storage area |  |  |  | N | NO | <D> **** Detailed Description **** The yellow barrel containing the hoses for ABN-FPC-LOSS had to be moved due to the amount of water leaking out of the ROA HVAC unit and puddling on the floor in the vicinity of where the barrel is normally staged. The water is currently leaking out of the hvac unit from the airwash. However, this can also occur when the heating steam is in service in the fall and winter. Need new floor marking area for the barrel or relocate it or redirect the water on the floor. <I> **** Actions Taken **** informed Supervisor <N> **** Equipment Description **** Yellow Barrell for ABN on Rx572 moved out of storage area | 02-00-R-BLDG-MISC,02-00-ROA-HV-1
384974 | CR | 20180927 |  | 3 | Recommended change to SOP-RHR-SDC |  |  |  | N | NO | <D> **** Detailed Description **** SOP-RHR-SDC P&L 4.10 states that "To avoid pump damage/failure, verify RHR-FCV-64A(B) (Minimum Flow) open during low flow conditions." For all of the sections of this procedure that require initiating or securing flow, the minimum flow valve is first deactivated closed to prevent pumping reactor coolant to the suppression pool. This P&L should be removed. <I> **** Actions Taken **** None. | 02-00-RHR-FCV-64A,02-00-RHR-FCV-64B
384981 | CR | 20180927 | CAQ | C | 2018 TFOF Evaluate Target Set #3 (NRC) | N | N |  | N | NO | <C> At the request of the initiator, the verbiage in the detailed description was edited to reflect an NRC identified minor violation. LKW 9/27/2018 <D> **** Detailed Description **** Evaluate Target Set #3 for inclusion of additional components as described in other station target sets. NRC identified, this is considered a minor violation of 73.55 (f). <I> **** Actions Taken **** CR Submitted. . Contacted Security for furhter clarification.
384982 | CR | 20180927 |  | 4 | 4 Pieces of M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** 4 pieces of M&TE were found OOT and NONE were used during Calibration cycles. Calcdoe #0066321 Votes Infinity Data Acquisition Switch Unit- model 85004. Adjusted within specs. DEF #6746A written. Calcode #C011657 Sweeny Torque Mulitplier- model 235- Nonfunctional & Rejected. DEF #6747A written. Calcode #0065104 Industrial Scientific Gas Monitor- Model iTX Rjejected- Unable to adjust- parts not available. DEF #6748A written. Calcode #0066432 Hytorc Hyd. Torque Wrench- model AVanti P7 adjusted wtihin specs. DEF #6749A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
384986 | CR | 20180927 |  | 4 | Simulator THOR Abort |  |  |  | N | YES | <D> **** Detailed Description **** While performing Step 44 of Scenario LR001355, a malfunction to trip the 230 KV Breaker was inserted by the simulator operator . The simulator tripped the 230 KV Breaker as requested but 30 seconds later a THOR Abort occurred. This impacted Staff Crew Simulator Practice for Annual Exams. <I> **** Actions Taken **** Notified the training simulator group and LORQ supervisor. Wrote SR 2814. <N> **** Equipment Description **** N/A
384987 | CR | 20180927 |  | 3 | ppm 12.1.1 needs edit |  |  |  | N | NO | <D> **** Detailed Description **** PPM 12.1.1 section 8.2 references calibration checks to be evaluated per Section 8.2 but section 10.2 is the evaluation section of the procedure. Recommend fixing 8.2 to 10.2 <I> **** Actions Taken **** Notified chemistry supervision and procedure sponsor
384993 | CR | 20180927 | CAQ | D | Deteriorated portable ladder holder in SWPH A | Y | N |  | N | YES | <D> **** Detailed Description **** One of the portable ladder holders on the east interior wall of SWPH A is deteriorated and needs repaired. One of the two seismic latches for the ladder holder has become disconnected (laying on the grating below the ladder). See the photos attached to the EDMS of this AR CR 384993. Uncertain if it is just a missing wing nut or if the threaded stud for the wing nut is stripped and the wing nut is missing - please repair. Until repaired, the ladder holder is still functional. Though seismic latches are provided by the generic ladder holder design (AED S679-2) and appropriate, there is no uplift for the design basis earthquake that would load the seismic latch (AED CAL CE-02-93-22). The ladder would not be in danger of lifting off of the holder and falling if neither seismic latch were functional - in this case, there is still one of the two seismic latches that is functional. <I> DEFICIENCY ID TAG 41808 WITH CROSS-REFERENCE TO THIS AR CR 384993 AND WR 29144785 HUNG IN THE FIELD. | 02-00-A-BLDG-MISC
384994 | CR | 20180927 | CAQ | D | SW-V-2A very slow/not active oil leak. photos attached | Y | Y |  | N | YES | <D> **** Detailed Description **** The SW-V-2A has or had a very slow/not active oil leak. <I> **** Actions Taken **** SSS notified. Area cleaned after photos were taken. Will be monitoring for how often it drips. | 02-00-SW-MO-2A,02-00-SW-V-2A
384995 | CR | 20180927 |  | 3 | Phishing attempt made on Energy Northwest Employees | N | N |  | N | NO | <D> **** Detailed Description **** It was reported the Cyber team that a phone phishing campaign was combined with a email phishing attempt. The number in question made numerous attempts to IT individuals. Investigation also identified that 6 individuals recieved emails in conjunction with the phone call in which the tried to get users to click the email. <I> **** Actions Taken **** Scanned computer to validate no virus was present, deployed advanced virus protection, blocked the phone number, and let IS leadership and SM know of issues and that there are no known adverse impacts. This is not reportable by 10 CFR 73.77 <N> Created article to increase awareness to users. No further action is needed.
384996 | CR | 20180927 |  | 3 | Missed Manager/Supervisor continuing training 2018 Q3 |  |  |  | N | NO | <D> **** Detailed Description **** Post 2018 Q3 scheduled class presentations shows 55 of 220 managers and supervisors did not attend continuing training classes MT000712, Iron Excursion and MT000713, Managing Risk. This number was derived from Data Access Desktop (DAD) report. Pilot class was held 08/21/18 and subsequent classes were offered 08/28/18, 08/29/18, 09/06/18, 09/13/18, 09/20/18 and 09/24/18. Ten of the individuals did not attend due to Manager Certification class, (5) Operations Initial training class, (1) have been promoted since the schedule was first available, (2) and on leave/personal issue, (2). <I> **** Actions Taken **** Compared attendance rosters to DAD list to ensure accuracy. Informed Organizational Effectiveness Manager.
384997 | CR | 20180927 | CAQ | D | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0064089 Fluke Doc. Process Calibrator- model 743B was NOT used in the OOT Resistance Measurements. Adjusted to specs. No Plant Impact. DEF #6750A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
384998 | CR | 20180927 | CAQ | D | HPCS-M-P/2 low oil level | Y | Y |  | N | YES | <D> **** Detailed Description **** The HPCS-M-P/2 is below the level indication for oil level when the pump is not in use. About 1/16" below this oil mark. <I> **** Actions Taken **** CR written, SSS notified. | 02-00-HPCS-M-P/2
385000 | CR | 20180927 |  | 3 | 2CA11 key missing RWCR |  |  |  | N | NO | <D> **** Detailed Description **** IAW 1.3.23 key M249 2CA11-285 key should be in the RWCR key locker; it's not there and does not appear to be checked out. <I> **** Actions Taken **** Informed SSS, generated AR.
385001 | CR | 20180927 |  | 3 | WO that INOPs DG 1 rescheduled outside of DG 1 window |  |  |  | N | NO | <D> **** Detailed Description **** WO 02116408 DEA-42-7AA1D: REPLACE STARTER COIL DEA-FN-11 was rescheduled out of the 10/1/18 DG 1 window in July 2018 to limit the number of starter coil replacements to 3 per week in support of electrical shop loading. This will cause additional IINOP time for DG 1. <I> **** Actions Taken **** Working with Operations and work control to establish a proper schedule date.
385004 | CR | 20180927 |  | 4 | Lights need to be replaced in RWCR | N | N |  | N | YES | <D> **** Detailed Description **** Space inspection found 60 overhead lights out in the RWCR. They need to be replaced. <I> **** Actions Taken **** Documented in Space Inspection and initiated CR <N> **** Equipment Description **** RW control room | 02-00-W-BLDG-MISC
385006 | CR | 20180927 |  | 4 | Reactor Bldg Truck bay TSW Leak on RRA-CC-7 | N | N |  | N | YES | <D> **** Detailed Description **** Reference previously identified CR 384851. The leakage is through the weld at the elbow between TSW-V-H673 and TSW -V-268. Leakage is approximately 1 drop per second and is currently being caught by bucket. <I> **** Actions Taken **** Added additional information | 02-00-R-BLDG-MISC,02-00-RRA-CC-7,02-00-TSW-PIPE-MISC,02-00-TSW-V-268,02-00-TSW-V-H673
385007 | CR | 20180927 | CAQ | D | SW B low flow to RRA-CC-17 | Y | Y |  | N | YES | <D> **** Detailed Description **** 4.812.R2 Drop 5-4 Analyzer Room B cooler Flow low. OPS 2 reports flow on SW-FI-44 as 8.5 gpm. Min for operability is 8 gpm. <I> **** Actions Taken **** performed a partial OSP-SW-M102 to restore flow to normal band and alarm is clear. | 02-00-RRA-CC-17,02-00-SW-FI-44
385009 | CR | 20180927 |  | 4 | LER Supplement 2018-001-01 will not meet internal due date |  |  |  | N | NO | <D> **** Detailed Description **** LER Supplement 2018-001-01 will not meet the communicated due date of 9/30/2018. Per NUREG-1022 rev. 3 the supplement date, if communicated in an LER, is not a regulatory commitment. Recommend 4/Trend.
385010 | CR | 20180927 | CAQ | D | Asset Suite MEL Incorrect Seismic class for SLC-TK-1 | Y | N |  | N | YES | <D> **** Detailed Description **** This appears to be a documentation issue only. The Asset Suite MEL database currently lists SLC-TK-1 as Seismic IM. This is in contradiction to FSAR Table 3.2-1 and M522. EQ Engineer confirmed that SLC-TK-1 is seismically qualified per AED QID 343011-02. <I> **** Actions Taken **** Actions Taken Notified Shift Manager, System Engineer and EQ Engineer. <N> The seismic field in Asset Suite has been corrected. See e-mail string in EDMS. | 02-00-SLC-TK-1
385012 | CR | 20180927 |  | 4 | Unsafe ladder requires removal from Turbine Building |  |  |  | N | NO | <D> **** Detailed Description **** There is a 20 ft extension ladder on the TG 501 East (adjacent to steam tunnel entrance). The ladder has been tagged by Industrial Safety as UNSAFE for use. This ladder requires transport to the RW 437 for disposal (cut up and placed into an LSA box, by Laborers) . Because of its size, location and the lack of a full size elevator in this building, Maintenance support will be required to rig the ladder down to the 441 elevation. See attached EDMS Doc for pictures. A more visually robust sign will be put in place to heighten awarness. <I> **** Actions Taken **** Verified no practical means available to transport ladder to RW 437. <N> **** Equipment Description **** TG 501 East, by Steam Tunnel Entrance | 02-00-T-BLDG-MISC
385013 | CR | 20180927 | CAQ | C | Review for GL 2008-01 actions at RHR-V-42A and RHR-V-53A | Y | Y |  | N | YES | <D> **** Detailed Description **** Assignment AR 304308-48 was generated to determine if it was acceptable in the original GL 2008-01 response to not designate RHR-V-53A and RHR-V-42A as areas requiring UT to support that no gas was present. . Background Information: In our GL 2008-01 response to the NRC we indicated there are two methods for introducing air into the piping (see below): 1) Back-leakage across pressure isolation valves (PIVs) from the reactor coolant system into the suction of RHR piping systems, or the discharge of HPCS, LPCS or RHR piping systems, resulting in steam pockets due to exceeding saturation conditions. 2) Inadvertent draining, system realignments, and incorrect performance of maintenance and testing procedures associated with HPCS, LPCS, and RHR systems. . RHR-V-53A Review: As a result of this review Engineering determined it was acceptable that we did not perform checks at the RHR-V-53A susceptible location. The reason for that is simply because the RHR-V-53A is not between the pump and the injection valve. For T.S. 3.5.1/3.5.2 the purpose was to â€œverify that each ECCS injection/spray subsystem piping is filled with water from the pump discharge valve to the injection valveâ€. The Shutdown Cooling (SDC) valves in the RHR-A train arenâ€™t in that direct flow path, and therefore, they do not need to be monitored. . Conclusion: The susceptible location on the RHR-A LPCI injection line (RHR-V-42A) was not monitored and should have been following the original GL 2008-01 response. The susceptible location on the RHR-A SDC line (RHR-V-53A) was not monitored and this was acceptable. . There is no existing operability issue. With the implementation of TSTF 523 the current method for determining operability for RHR-A (OSP-RHR-M101) covers both the RHR-V-53A and RHR-V-42A locations. . Additional Information: Previous versions of the OSP-RHR-M101 (from Revision 1 through Revision 8, which covered the years of 1998 through 2011) were reviewed to determine if this location had been regularly monitored in the past and there was no evidence of this susceptible location on the RHR-A LPCI line being regularly monitored. . This issue was also discussed with two engineers associated with the development of the original site response. Neither was able to provide a sufficient justification for why the susceptible location on the RHR-A LPCI injection line was not monitored. The original program managerâ€™s thought process was that since we injected to vessel at the end of the refueling outage that was eliminate voids present. While this is true for voids generated from maintenance induced causes it doesnâ€™t address the possibility of voids generated due to this being a PIV. . The Quality audit from December 2010 was also reviewed to determine if this issue had been previously identified and there was nothing in the audit report concerning this issue. . Annunciator procedure 4.601.A4 was reviewed for Operator response to RHR-A system discharge pressure high/low actions. The high discharge pressure set point is 455 psi and for pressures above that value the procedure directs the Operator to verify RHR-V-53A and RHR-V-42A are closed and vent from valves RHR-V-73A/74A as required. The low discharge pressure set point is 50 psi and for pressure below that value the procedure directs the Operator to vent the Loop A per OSP-RHR-M101 if the keepfill pump (LPCS-P -2) operation is satisfactory. . Under work order 01156818-01 the RHR-A LPCI injection line had NDE UT performed for the original monitoring and no voids were discovered on that date. <I> **** Actions Taken **** CR written. Supervisor notified. Discussed with Licensing. See EDMS for a word copy of this CR. . Request action to Licensing for further review of this legacy issue. <N> **** Equipment Description **** RHR-A System | 02-00-RHR-V-42A,02-00-RHR-V-53A
385017 | CR | 20180927 |  | 4 | DLR placed in X-Ray machine |  |  |  | N | YES | <D> **** Detailed Description **** When processing through the search train in the PAAP, a contractor placed their DLR in the X-Ray machine. <I> **** Actions Taken **** HP and management notified <N> **** Equipment Description **** PAAP search area
385018 | CR | 20180927 | CAQ | C | Late entry in eSOMS for 5 Maintenance Supervisors |  |  |  | N | NO | <D> **** Detailed Description **** Five mainenance supervisors failed to ensure that time had been entered correctly in eSOMS prior to working extra hours during the SW-B outage window. <I> **** Actions Taken **** eSOMS was updated after errors were discovered during weekly audit of eSOMS. Supervisors were coached to check their time in eSOMS when working outside of their normal hours. . Confirmed with CR author there were no resulting violations.
385019 | CR | 20180927 |  | 3 | Degrading trend- RWCU leakage and SA vibration and noise | N | N |  | N | YES | <D> **** Detailed Description **** RWCU (high pressure, contaminated system) is leaking to Service Air (low pressure, clean system). Leakage is well documented in previous CRs. The leak started in 2013 as a drip from the SA-F-69 drain valve (SA-V-23) (see CR 282751). As of 8/1/2018, the leak has become to a constant stream (CR 382960). On 9/11/2018, the leak began producing a noise in the SA line. That noise was a cyclic whooshing noise ( sounded like a steam engine). Today (9/27/2018) the noise has progressed to a constant vibration/ rumble in the SA line. The vibration is noticeable when touching the line and the noise is quite loud. The leakage or problem causing the noise appears to be degrading fairly quickly and needs to be addressed before a failure occurs. Recommend addition to the PCL and dedicate resources to find the source of the noise. <I> Added to Plant Concerns List | 02-00-SA-F-69,02-00-SA-RV-265,02-00-SA-V-23
385021 | CR | 20180927 |  | 4 | Employee stung by bee |  |  |  | N | NO | <D> **** Detailed Description **** Employee stung by bee while conducting a take 2 in the Rattlesnake Mountain top building. CCCF <I> **** Actions Taken **** Notified supervisor and took employee to Occ Health. PTL Incident # 18-0022
385025 | CR | 20180927 |  | 4 | SA-V-164 adjustment issues | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of SA-V-164, the Unload stop screw could not be adjusted to set the sump PSI within IMDS tolerance (50 +-5 psi). The screw ran out of adjustment, and the sump pressure was only able to get down to 160. That is 5 PSI out of tolerance <I> **** Actions Taken **** Operations and I&C supervision was notified of the issue, and the system engineer was informed of the discrepancy. Videos of the issue are attached to the WO to reference. WO is 02134945-05. | 02-00-SA-V-164
385026 | CR | 20180927 |  | 3 | (QA) Identified Human Performance Issues |  |  |  | Y | NO | <D> (QA) During the Observation of PPM 16.11.6, Weekly Iodine, Particulate, and Tritium Analysis Results the following Human performance short falls from the previous week (September 17, 2018) were identified: â€¢ The Waste Exhaust Air WEA A on/off label from the previous week was only filled out with WEA. No designation of which sample rack was evident. â€¢ The WEA A right side air housing from the previous week had been installed upside down. This was evident by visual examination of the sample rack. This was identified during the observation when the right side air housing was valved in by a Chemistry Technician and the flow was not reading as expected. This could have led to FME in the WEA air sample line if the filter was pulled into the system. If not discovered by the current week Chemistry Tech, this would have led to a compromised sample that was not representative of the WEA effluent. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Chemistry. <I> Manager <N> CR found at INPROG and moved to Approved status. This AR-CR is being addressed under AR-CR 385134. Per SWP -CAP-01, an assignment under resolving AR-CR 385134 has been created to address the issue documented in this AR-CR. Appropriate cross references have been added.
385027 | CR | 20180927 |  | 3 | Degrading trend in MSR 1B performance | N | N |  | N | YES | <D> **** Detailed Description **** During monitoring and trending of MSR performance, MSR 1B (MS-HX-1B) west end tube bundle performance was found to be degrading. There has been an drop in crossover temperature of approximately 2.5 degrees since the May 2018 forced outage. This could be indicitive of tube leakage. This second stage tube bundle already has degraded performance from prior plugging. Recommend evaluation by heat exchange program owner. See EDMS eDNA plot for trend. <I> **** Actions Taken **** Discussed with MSR/Turbine Engineer. <N> **** Equipment Description **** T 501' D5/8.5-12.5 | 02-00-MS-HX-1B
385028 | CR | 20180927 | CAQ | D | Temporary extension ladder left up in W525' Cable Chase | Y | N |  | N | YES | <D> **** Detailed Description **** On the W525' elevation Cable Chase grating platform, an extension ladder providing access to the vicinity of 3/4" vent valve SW-V-604 in the overhead was found in the field. See the photos attached to the EDMS of this AR CR 385028. The temporary extension ladder had been left without PPM 10.2.222 tie-off in the overhead or an SWP-MAI-02 Work In Progress sign. The top of the ladder was physically resting against largebore SW B system piping and in close proximity to small bore SW-V-604. The nonconforming ladder was promptly taken down and put back in an established seismic storage location on W525'. Though not tied off, the ladder would not have toppled over during a seismic event due to the configuration of the nearby piping and trays in the overhead. | 02-00-SW-V-604,02-00-W-BLDG-MISC
385029 | CR | 20180927 |  | 4 | Three pallet jacks found in R441' rail bay w/o wheel chocks | Y | N |  | N | YES | <D> **** Detailed Description **** In the Reactor Building R441' rail bay, three pallet jacks were found without PPM 10.2.222 wheel chocks installed. Upon discovery, wheel chocks were obtained and installed. See the photos attached to the EDMS of this AR CR 385029. . Though in a safety-related (Seismic 1) area, the pallet jacks without chocked wheels per PPM 10.2.222 were sufficiently remote from any potentially impact sensitive SSCs. As indicated above, a wheel chock has been installed for each of the CR subject pallet jacks. | 02-00-R-BLDG-MISC
385030 | CR | 20180927 |  | 4 | Deteriorated W487' portable ladder holders | N | N |  | N | YES | <D> **** Detailed Description **** Stripped seismic latch studs exist for the W487' portable ladder holders at Ladder Storage location 12 and at Ladder Storage location 12.1. These need to be repaired to conform with the detail shown on AED STL S679-2. Per calculation AED CAL CE-02-93-22, there is no seismic uplift carried by the seismic latches under design basis seismic conditions. As such, this condition until repair will not result in any QC 2 over 1 concerns for any station SSCs. <I> DEFICIENCY ID TAG 41809 WITH CROSS-REFERENCE TO THIS AR CR 385030 AND WR 29144796 HUNG IN THE FIELD. | 02-00-W-BLDG-MISC
385037 | CR | 20180928 |  | 4 | Portable ladder holder in RWB north stairwell nonconformance | N | N |  | N | YES | <D> **** Detailed Description **** The portable ladder holder existing in the RadWaste Building (RWB) north stairwell near FP-V-136 does not conform with the typical detail provided by AED S679-2 and evaluated per AED CAL CE-02-93-22. Currently, this portable ladder holder has only 1 bracket (2 are required for conformance with the typical detail). Please make this portable ladder holder conform to the typical detail or remove it from the plant. When initially observed, a portable ladder had been stored on the subject nonconforming portable ladder holder. The portable ladder was removed from the holder and delivered to the W467' Tool Crib. In its as-found configuration, the portable ladder on the nonconforming portable ladder holder did not pose any threat to any nearby SSCs - the ladder was not large, there were no impact sensitive items under/near the ladder, and the ladder was trapped sufficiently by earby largebore FP system piping. See the photos attached to the EDMS of this AR CR 385037. Deficiency ID Tag 41810 with reference to this AR CR 385037 (and its associated WR) was hung in the field. | 02-00-W-BLDG-MISC
385038 | CR | 20180928 |  | 4 | Elevated dose rates on EDR-TK-5 | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Dose rates on EDR-TK-5, RW 437, are once again trending upward. All radiological postings remain satisfactory in the affected area but this trend needs to be monitored and a means of removing the source term should be explored. Reference VSDS survey # 20180821-2. <I> **** Actions Taken **** Initiated CR and notified HP Supervision <N> **** Equipment Description **** RW 437 North | 02-00-EDR-TK-5,02-00-W-BLDG-MISC
385039 | CR | 20180928 |  | 4 | TOA-FL-1A end of roll | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FL-1A end of roll alarm in <I> **** Actions Taken **** MCR notified <N> **** Equipment Description **** TB501 east end at HVAC units | 02-00-TOA-FL-1A
385040 | CR | 20180928 |  | 4 | Deteriorated R422' CRD pump room portable ladder holder | N | N |  | N | YES | <D> **** Detailed Description **** The portable ladder holder in the R422'-3" CRD pump room has a stripped stud for 1 of its 2 seismic latches and needs repair. Reference AED S679-2 details. Deficiency ID Tag 41815 has been hung in the field with this AR CR 385040 and its associated WR identified on it. . Until repaired, this condition does not pose any QC 2 over 1 concerns - there are no potential targets under/near the subject ladder holder in the field and per qualification calculation CE-02-93-22, there is no seismic uplift on the ladder holder during design basis seismic conditions. Even in its deteriorated state, the calculation indicates the ladder will not be dislodged from the ladder holder under design basis conditions. | 02-00-R-BLDG-MISC
385042 | CR | 20180928 |  | 4 | Deteriorated T441' portable ladder holder outside RFW B | N | N |  | N | YES | <D> **** Detailed Description **** pump room (@ Ladder Storage Location 10.4) is deteriorated and needs repair. 1 of the 2 seismic latches for this portable ladder holder has a stripped stud. Reference AED S679-2. This location is a Seismic Category 2 area - there are no QC 2 over 1 concerns associated with this condition (and the ladder would not be expected to become dislodged from the deteriorated ladder holder even under Seismic Category 1 conditions as there is no seismic uplift on the holder per qualification calculation AED CAL CE-02-93-22). . Deficiency ID Tag 41816 has been hung in the field at the subject ladder holder. The tag references this AR CR 385042 and its associated WR. The lower portable ladder holder on T441' outside the RFW B | 02-00-T-BLDG-MISC
385043 | CR | 20180928 |  | 4 | Deteriorated W525' portable ladder holders | N | N |  | N | YES | <D> **** Detailed Description **** The two lowest portable ladder holders on W525' (Vital Island) - Ladder Storage Locations 15.3 and 15.2 - have stripped studs for their seismic latches. Location 15.3 has 1 of 2 studs stripped and Location 15.2 has 2 of 2 studs stripped. Please repair. Reference AED S679-2. . Per review of seismic qualification calculation AED CAL CE-02-93-22, there is no anticipated uplift on the portable ladder holder seismic latches during design basis seismic conditions. As such, the subject ladders would not be expected to become dislodged from their deteriorated ladder holders under design basis loading conditions. Even if they did become dislodged, the ladders in these ladder holders are only a few inches off of the W525' floor. There is no QC 2 over 1 concern associated with this condition for any nearby SSCs. . Deficiency ID Tags 41813 and 41812 have been hung in the field (each is cross-referenced to this AR CR 385043 and its associated WR). | 02-00-W-BLDG-MISC
385044 | CR | 20180928 | CAQ | B | MS-RV-2A opened during ISP-MS/IST-A101 | Y | N |  | N | YES | <C> CR Bring Back- Engineering gathering more Information on this CR. - Risk - Medium (B) Cause - Uncertain/Complex - Investigation Template Required <D> **** Detailed Description **** See edms. per ABN-SRV step 4.11 an evaluation of the Reactivity event per PPM 1.3.79 is needed. <I> **** Actions Taken **** Entered ABN-Power and ABN-SRV. <N> ***General Notes*** During the Event Investigation, No Human Performance errors were identified. Written Statements have been uploaded into the EDMS of this AR, along with the work instructions being worked (WO# 02100861-01), and the procedure that was being worked through (IST-MS/IST-A101). this appears to be an equipment issue. Recomend this issue be screened as CAQ due to MS-RV-2A actuating. . This issue ranks as Medium risk (probability = Low x Consequence = medium). The probability is low because further testing of the MS-PS-39 switches has been suspended until the cause of this event is identified. This was of medium consequence because it challenged CR operators, but did not interupt power operations or negatively impact nuclear safety. The cause is uncertain at this time. Severity "B" with an EQIT. | 02-00-MS-PS-39A,02-00-MS-RMS-RV/2A,02-00-MS-RV-2A
385045 | CR | 20180928 |  | 3 | EWD-62E-015 does not match 217-00,84,21 and 25 |  |  |  | N | NO | <D> **** Detailed Description **** â€¢ The wires penetrating ZTB-6 on 217-00,84,21 match the wire numbers penetrating ZTB-4 on EWD-62E-015. One of these boxes is labeled incorrectly on the prints. CR 209036 was written because the electricians found the box they thought was supposed to be ZTB-4 labeled ZTB-6. WR 29080199 relabeled the terminal box ZTB-4. 217-00,84,21 and 217 -00,84,25 need to be updated to show that the wires for P67 come out of ZTB-4 not ZTB-6.
385047 | CR | 20180928 |  | 4 | T-DOOR-T114 does not completely shut without operator assist | N | N |  | N | YES | <D> **** Detailed Description **** The active leaf of T441' corridor door T-DOOR-T114 will not completely shut and latch without operator assistance to pull or push the door shut. Appears there may be an issue with the upper hinge for this door. Please repair as necessary. | 02-00-T-DOOR-T114
385048 | CR | 20180928 |  | 3 | PPM 1.3.76 Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Attachment 9.3 of PPM 1.3.76 describes the DG extended maintenance outage commitments. Page 58 describes limits on ignition source permits in this condition. After discussions with Fire Protection and Licensing, it was intended for Note 1 (discussion on specific locations within fire areas that contain PFSS circuits) to apply to ISP's as well as fire tours. That could be made more clear. <I> **** Actions Taken **** This came up while preparing for the upcoming DG1 outage on 10/1. Discussed with Fire Protection and Licensing.
385049 | CR | 20180928 |  | 4 | Tâ€“DOORâ€“T112 does not completely shut without operator assist | N | N |  | N | YES | <D> **** Detailed Description **** The active leaf of T441' sample room door Tâ€“DOORâ€“T112 will not completely shut and latch without operator assistance to pull or push the door shut. Please repair as necessary. | 02-00-T-DOOR-T112
385050 | CR | 20180928 |  | 4 | Repair ML #8 (UNSAFE EQUIPMENT) or remove it from the plant | N | N |  | N | YES | <D> **** Detailed Description **** Man-Lift #8 (ML #8) currently exists on R548' elevation in Storage Authorization Permit #168 (along the north wall) but this man-lift has been tagged in the field as UNSAFE EQUIPMENT - DON'T USE IT since 06/15/13 (GT 5 years). See the photos attached to the EDMS of this AR CR 385050. Please repair this man-lift as necessary or remove it from the plant. <I> Hung Deficiency ID Tag 41847 (referencing this AR CR 385050 and associated WR 29144805) on Man-Lift #8 in the field. | 02-00-R-BLDG-MISC
385051 | CR | 20180928 | CAQ | D | New fire door W-DOOR-C502 does not meet criteria of 15.3.17 | N | N |  | N | YES | <D> **** Detailed Description **** During the close out process of 01190518-01, replace fire door W-DOOR-C502, the new fire door installed does not meet the criterial of table 7.5A in procedure 15.3.17. Mechanic used a Go/NoGo gauge of a 1/4" gap from edge of door to door frame, new criteria is 1/8" from edge of door to door frame. <I> **** Actions Taken **** Reopen Barrier impairment 14-0291 and post on door C502 Take work package 01190518-01 back to working going to install shims 9/29 and 9/30 <N> **** Equipment Description **** W525 J0/14.9 | 02-00-W-DOOR-C502
385052 | CR | 20180928 |  | 3 | ILC 23 Simulator Exam #3 Student Failures |  |  |  | N | NO | <D> **** Detailed Description **** Three ILC 23 students failed their simulator exam #3.
385056 | CR | 20180929 | CAQ | D | I&C CART-2 found stored in a questionable location on R522' | Y | N |  | N | YES | <D> **** Detailed Description **** Observed I&C CART-2 had been temporarily stored in the NE corner of R522' which is close to DIV-1 electrical term box TB-R494 (and some RETIRED MSLC equipment EPNs). The SWP-MAI-02 Work In Progress sign found hanging on the cart indicates its presence is associated with WOT 02092551-01. However, this surveillance WOT is COMPLETE and the associated parent WO was taken to COMPLETE on 08/23/18. The as-found location of this cart did not appear to comply with the PPM 10.2.222 caution signage on the cart that states 'DO NOT STORE WITHIN 7 FEET OF SAFETY RELATED EQUIPMENT'. As such, the cart was repositioned by the observer to a nearby location that does comply with PPM 10.2.222. As-found and as-left photos are attached to the EDMS of this AR CR 385056. For resolution, please update the SWP-MAI-02 Work In Progress sign OR move this cart to its proper storage location when not in-use by Maintenance. . Though possibly noncompliant with PPM 10.2.222 in its as-found location, this cart did not pose an unacceptable QC 2 over 1 threat to any nearby safety-related SSCs because: 1) Although the cart is relatively tall, it is only tall on one end and is not top-heavy -- it would not have had a tendency to overturn during a design basis seismic event. 2) Even if it did overturn, it would have only overturned to the east or west because of its height/width (or length) aspect ratio (not south or north into the MSLC items). The as-found configuration/location of the cart and nonsafety-related items near the cart would not have allowed an impact into DIV-1 TB-R494 to occur. | 02-00-R-BLDG-MISC
385057 | CR | 20180929 |  | 4 | R522' portable ladder storage rack Location 4.1 needs repair | N | N |  | N | YES | <D> **** Detailed Description **** The threaded stud for the seismic latch on the north bracket of R522' portable Ladder Storage rack Location 4.1 has failed (failed attachment weld) and needs to be repaired (needs a new threaded stud welded in the existing bracket base). Reference AED STL S679-2 and the photos attached to the EDMS of this AR CR 385057. Deficiency ID Tag 41817 has been hung in the field (includes reference to this AR CR 385057 and its associated WR). . At this time, no portable ladder is being stored in this portable ladder storage location (even if there were a ladder being stored, there would be no QC 2 over 1 concern because there are no impact sensitive items or any important to safety or safety-related items in the vicinity). | 02-00-R-BLDG-MISC
385058 | CR | 20180929 |  | 4 | TSW-HX-6C metal label rivets are broken | N | N |  | N | YES | <D> **** Detailed Description **** There is a metal label on TSW-HX-6C (Cond. Booster pump LO cooler) that has broken off and is being held in place with duct tape. The other 5 booser pump LO coolers all have the same Metal labels which are still attached via thier rivets. Please evaluate if this label is actually required and should be properly secured to the HX or if it can be removed. See EDMS doc for pics of suspect label and an undamaged label. Note: the LO HXs are within close proximity to the Booster pump pressure switches (STAY CLEAR Area). <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** TG 441 W | 02-00-TSW-HX-6C
385059 | CR | 20180929 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 238 B: 239 C: 239 E-TR-B A: 118 B: 118 C: 118 The following sensors were tripped and are reset: J7 - 500KV Neutral Ground Overcurrent BPA reports the following: a. Cause was a momentary fault on the Sickler-Schultz #1 500KV Line b. Relaying involved a single pole ('C' phase) c. There is no damaged equipment d. The line reclosed e. There is no emergent work or line outage required, the fault did not involve the 230KV or 115 KV lines, and no RAS was required nor initiated. <I> **** Actions Taken **** For trending
385060 | CR | 20180929 | CAQ | D | Fluorescent lights need relamp. | N | N |  | N | YES | <D> **** Detailed Description **** The following lights ( blue dot ) need relamping. RW 525 outside comm. room, Rx 422 outside SW elevator, and 441 TG/RW hallway. Also 452 OG sample room C144 is dark. ( not blue dot). <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** RW 525 outside comm. room. Rx 422 outside SW elevator. TG/RW hallway 441. RW 452 OG sample room.
385061 | CR | 20180930 |  | 4 | PPC computer 8715 error lamp on | N | N |  | N | YES | <D> **** Detailed Description **** PPC computor 8715 error lamp on. System appears similar to TDAS unit. Internal red LED not flashing on PPC unit (3rd row of leds from left) | 02-00-PPC-COMP-8715
385067 | CR | 20180930 |  | 4 | SO-PI-236 having large pressure swings | N | N |  | N | YES | <D> **** Detailed Description **** SO-PI-236, supplied by discharge pressure of the seal oil air side pump, is having swings in pressure of nearly 30 psig (video of swings included). This could be an indication of pump degradation, or other issues. Should be investigated further. <I> **** Actions Taken **** Informed MCR, wrote CR. <N> **** Equipment Description **** Seal Oil Skid TG 441W . THis condition has been present for many years, the gauge is very susceptible to vibrations and should be replaced with a liquid filled gauge. | 02-00-SO-PI-236
385068 | CR | 20180930 |  | 3 | Revise PPM 1.3.76 Att 9.3 for Fire Area M-73 |  |  |  | N | NO | <D> **** Detailed Description **** Fire area M-73 no longer exists in the plant; however, PPM 1.3.76 Attachment 9.3 still lists it. Recommend deleting the fire area from the PPM. Reference EC 8711, LDCN-12-033 and AR 177201. It appears that this procedure change was inadvertently missed as part of the change management for the EC and LDCN. <I> **** Actions Taken **** Wrote CR.
385069 | CR | 20180930 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm | N | N |  | N | NO | <D> **** Detailed Description **** Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 238 B: 240 C: 239 E-TR-B A: 118 B: 118 C: 118 The following sensor was tripped and is reset: J7 - 500KV Neutral Ground Overcurrent BPA reports the following: a. Cause was McNary - Coyote Springs 500KV Line #1 single pole relayed off and reclosed b. No damaged Equipment, no outage required, no RAS was initiated. <I> **** Actions Taken **** for trend
385070 | CR | 20180930 |  | 3 | Plateau CBT system unavailable |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The Plateau CBT system was unavailable on 9/30/18 from ~6 AM to ~ 1:45 PM due to an Oracle database connection issue. Plateau Application Analyst contacted Orace DBA to investigate. Application Analyst verified the Plateau CBT system is working now but root cause is unknown. Recommend NON CAQ 3 to research. <I> **** Actions Taken **** Plateau Application Analyst contacted Oracle DBA. Notified IS Duty Officer and IS Leadership.
385072 | CR | 20180930 |  | 3 | work order validation in dataglance issues |  |  |  | N | NO | <D> **** Detailed Description **** WO 02125290 was validated in dataglance. Dataglance said that there is a new revision but when it got to the append/replace screen, there was no revision. Please Fix <I> **** Actions Taken **** ensured that the most current version of the surveillance was being used. <N> The requirements data was recently brought into the DataGlance package and so the validate button recognizes that there was a change to the package. If data on the requirements panel has changed, since the original package was built, it will show that the package can be replaced, but if information didnâ€™t change on the requirements panel it doesnâ€™t recognize what information changed. This CR will be closed and CR 384226-02 will drive a Datamod to correct the issue.
385073 | CR | 20181001 |  | 4 | Weekly Camera Cleaning | N | N |  | N | YES | <D> **** Detailed Description **** CCTVs 13, 45, and 46 require cleaning. <I> **** Actions Taken **** Weekly list generated by CAS Officer and sent to Security Supervision. Initiate CR/WR. <N> **** Equipment Description **** CCTVs 13/45/46
385132 | CR | 20181001 |  | 4 | CW-FN-1 | N | N |  | N | YES | <D> **** Detailed Description **** CW-FN-1 oil level low, also fans 4/5 are just above the add mark. request oil be added to all fans on CW-CT-1A <I> **** Actions Taken **** informed MCR i initiated CR/WR | 02-00-CW-FN-1
385134 | CR | 20181001 |  | 3 | (QA) Observation of Human Performance Issues |  |  |  | Y | NO | <D> (QA) During Observation of PPM 16.11.6 â€œWeekly Iodine, Particulate, and Tritium Analysis Resultsâ€ for the week of September 24, 2018 the following Human performance short falls were identified: â€¢ (Steps 7.4.3 & 4) When a flow issue was recognized on WEA A the Chemistry Tech went to the sample rack and valved out the right side air housing without re-zeroing and ensuring that he was on the correct rack and manipulating the correct valves. The Chemistry Tech appropriately re -zeroed and performed Touchâ€“Read-Read (TRR) when valving the right side air apparatus back in service. However, the Chemistry Tech did not get the expected flow the Tech immediately went back to the sample rack with no re-zero or TRR of the valves manipulated. â€¢ While performing Section 7.3, the Chemistry Tech read the wrong pressure indicator at Step 7.3.5. The Technician read vacuum from TEA-PI-14, rather than TEA-PI-12. This gave him an incorrect reading that he started to take action on. The auditor stopped the Technician from going any further and asked why he was reading from TEA-PI-14, rather than TEA-PI-12. â€¢ While the Chemistry Tech was replacing TEA filter housing cartridges (Section 7.3), the auditor questioned the individual on labeling of the cartridges. The cartridges were labeled with RR #1 & 2 and RL #1 & 2. At first, the Technician thought that the labels were correct, then after being questioned, re-zeroed, looked again and realized that the cartridge labels were miss-labeled and should have been labeled as LR #1 & 2 and LL #1 & 2. This was corrected in the field. â€¢ No bag was used for the Reactor Building Effluent filter and cartridge after it had been in the system. This introduces a potential for contamination of personnel and the sample transport container. This also introduces potential of sample compromise. The Reactor Building Effluent filter and cartridge have the greatest potential for radioactivity of the items obtained in PPM 16.11.6. Insights: â€¢ The Chemistry Tech stated that he felt that he needed to rush due to the dose in the area. â€¢ The procedure does not list the full EPN in the Note before Step 7.3.3, in Step 7.3.3, nor in Step 7.3.5 which may have led to confusion and an error-likely situation. â€¢ Had these behaviors not been observed and corrected at the time the potential to manipulate plant components contrary to procedure existed. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Chemistry. <I> Discussed this Issue with the Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager <N> CR found at INPROG moved to Approved status.
385137 | CR | 20181001 |  | 4 | Rx & MM Exceeded August Dose Goal |  |  |  | N | NO | <D> **** Detailed Description **** Rx & MM exceeded the August dose goal. Goal was 27 mrem, actual was 41 mrem. Reason for exceeding the goal: 1) emergent approved dose 10 mrem to support FIN Team for NSSE-EQ-8 troubleshooting and repairs, 2) emergent approved dose 11 mrem to support FIN Team for investigating flow rates for RWCU-V-266A & 266B. <I> **** Actions Taken **** Initated AR-CR for trending.
385142 | CR | 20181001 |  | 4 | SCH-CR-51 not running due to low suction. | N | N |  | N | YES | <D> **** Detailed Description **** SCH-CR-51 was found not running, with chill water return temperature greater than 70Â°F. The control panel display shows Sys#1 Low Suction. Please investigate and correct. <I> **** Actions Taken **** Informed supervisor and wrote AR/WR. <N> **** Equipment Description **** S425 E3/3.4 | 02-00-SCH-CR-51
385144 | CR | 20181001 |  | 3 | ROA-HV-1 Water Leakage - Investigation Required | N | N |  | N | YES | <D> **** Detailed Description **** ROA-HV-1 unit has had water leakage for years and requires investigation and action to prevent further corrosion. Unit requires Control Room support to enter due to Tech Spec requirements. A potential cause could be the air wash basin refilling after level is drawn down during pump starts - which after the pump stops overflows the basin. There are signs of corrosion on the unit which could be the cause of the leakage as well. Entry into the unit to confirm the cause (stop the pump with someone inside to see if basin overflows) or look for leakage. Please see previously identified CRs dating back to 2014 in cross references. <I> **** Actions Taken **** Put up wet floor signs and documented issue for correction. <N> **** Equipment Description **** RB 572 - North End | 02-00-ROA-HV-1
385145 | CR | 20181001 |  | 3 | Procedure PPM 11.2.24.2 Attachement 8.3 needs revision |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During HP Continuing training, it was noted that procedure PPM 11.2.24.2 Attachment 8.3 Surveillance and Response for Changing Plant Conditions needs to be revised. On page 26, section 9.1 it reads that the normal current posting of RW 452â€™ Offgas Pre Filter cubicle is posted a RA when in fact it is now posted HRA at the entrance. See quarterly survey VSDS Prod-M-20180707-5. Also, on page 24 section 7.1 where it says; During drain down of the RX cavity through FPC, dose rates in these same areas may change; in addition, the drain line on the west side of 572â€™ may experience elevated dose rates. It is believed the intent was for this description location to be RB 548â€™ not 572â€™. <I> **** Actions Taken **** Informed Training and RP Supervision. Wrote this CR. Made necessary corrections in training material until procedure gets revised. <N> Please contact Matt Pilgreen for follow up actions from his observation of the class. Student feedback from CT 18-03 class was to have more clarification given in PPM 11.2.24.2 on what the words â€œsignificant changeâ€ actually mean. This may be an additional change to the procedure.
385146 | CR | 20181001 |  | 3 | 2018 FSA PI&R Station awareness of implementing actions AMP |  |  |  | N | NO | <D> **** Detailed Description **** Station awareness of implementing actions for License Renewal and Aging Management Program (AMP) requires increased attention. Communication to Energy Northwest site personnel should occur to provide an enhanced understanding of our commitments related to the Period of Extended Operation (PEO). Various suggestions were also identified regarding Aging Management Program responsibilities - see EDMS for examples. <I> **** Actions Taken **** Discussed issue with CAP Supervisor, Technical Services Supervisor and Capital Projects Manager and initiated CR.
385147 | CR | 20181001 | CAQ | C | FSA Pre-PI&R 2018: SevLvl 2 non-CAQ CR used to address |  |  |  | N | NO | <D> **** Detailed Description **** In September 2016, a severity level 2 (non-CAQ) condition report (CR) was used to address a Green NCV, which was not in compliance with SWP-LIC-08, Preparation and Conduct of NRC Inspections. During the pre-PI&R FSA, one outstanding issue was identified from September 2016 that had resulted in a severity level 2 (non-CAQ) condition report being referenced to address a Green NCV, which was not in compliance with SWP-LIC-08, Preparation and Conduct of NRC Inspections. <I> **** Actions Taken **** Discussed issue with CAP Supervisor, Licensing Engineer, Regulatory Affairs supervisor and manager. Additionally, a review of the level 2 apparent cause evaluation (AR 353210) and assigned actions was completed by the licensing engineer. The evaluation and ensuing actions were completed in a timely manner commensurate with the safety significance of the issue. One action remains open which is tracking an ODMI closure to be completed by Operations, due October 23, 2018. <N> In reviewing this issue, the Reg Affairs team evaluated the referenced Sev 2 CR (353210) as stated in the immediate actions, and determined that appropriate actions were taken for the issue. However, the subject of this CR states that we failed to follow SWP-LIC-08, in that using a Sev 2 was not appropriate. A review of the SWP-LIC-08 revision that was in effect at the time (rev M5, m 1), revealed that there was no guidance that was missed; for the issue in question a Sev A CR was written as a result of the inspection finding (360113) that brings the issue into full compliance with applicable procedures. Additionally, in discussions with the Reg Affairs staff, the real thing that was missed was that the original CR (353210) should have been graded CAQ because the condition adversely affected an NRC performance indicator and cornerstone. At the time SWP-CAP-06 would not have directed the CR towards CAP. Since that time, SWP -CAP-06 has been revised to where the guidance would drive screening of a similar issue to CAP. No further actions are needed.
385148 | CR | 20181001 |  | 4 | Security CCTV19T needs maintenance |  |  |  | N | YES | <D> **** Detailed Description **** Security CCTV19T not functioning as designed. Contact Security at 2185. <I> **** Actions Taken **** contact security @ 2185 | 02-00-SEC-CCTV-19T
385150 | CR | 20181001 |  | 3 | Number sequencing is off in section 7.1 of 12.18.3 |  |  |  | N | NO | <D> **** Detailed Description **** Number sequencing is off in section 7.1 of On Line Noble Chemistry procedure 12.18.3. Starting after 7.1.2, the sequence needs to be corrected throught the rest of section 7.1 <I> **** Actions Taken **** told supervisor and wrote this AR
385152 | CR | 20181001 | CAQ | C | While replacing DSA-V-10A rust was found | Y | N |  | N | YES | <D> **** Detailed Description **** There was aproximately a 1/4 cup of fine dry rust found. The rust was up against the valve. the rest of the pipe looked clean. WO# 02122319-01 <I> **** Actions Taken **** Cleaned out the pipe and contacted engineering to evaluate. | 02-00-DSA-V-10A
385153 | CR | 20181001 |  | 3 | ALARA suggestion: Change drain method for OSP-SLC/IST-Q701 |  |  |  | N | NO | <D> **** Detailed Description **** ALARA suggestion: Evaluate if changing the method of draining MWR piping after performance of OSP-SLC/IST-Q701 from 55 gallon barrels on the RB501 to 250 gallon totes in the RB truck bay. Current method places the barrels on the RB501 in the vicinity of FPC system piping with an EO in attendnance . If utilizing 250 gallon totes in the RB truck bay, staging would be initially on the south side of the RB501 and the EO would be in the truck bay to monitor draining into the tote (lower dose). MWR piping utilized for draining after this surveillance is historically slow. With almost 60 feet of hose running from the MWR connection to the tote, draining should go more quickly. <I> **** Actions Taken **** Request system engineer evaluate whether this method of draining from MWR is allowable. Request ALARA evaluate potential dose savings.
385154 | CR | 20181001 |  | 3 | Personnel Contamination Event 18-006 |  |  |  | N | NO | <D> **** Detailed Description **** INPO personnel found contaminated, 300 cpm, while attempting to exit RX 606. Dispersed contamination found on the sole of the left shoe. No CAs entered. Contamination was removed with decon fluid and a wipe of a rag. <I> **** Actions Taken **** Notified supervision of event. Performed follow up survey of area traveled on RX 606'. Survey was inconclusive in identifying where the contamination originated from. <N> Under the direction of HP, the RMC laborers mopped all of the contaminated areas of the Rx606 floor on 10/02/18. No further action required.
385155 | CR | 20181001 |  | 4 | GCM appears to need a paper replacement | N | N |  | N | YES | <D> **** Detailed Description **** The generator condition monitor chart recorder paper on the TG 471 W appears to need a replacement. A picture of the current paper is attached for reference. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** TG 471 W | 02-00-TG-ID-1
385156 | CR | 20181001 |  | 4 | PPC Red 'Ice cubes' - misc red processes | N | N |  | N | YES | <D> **** Detailed Description **** PPCV is showing red ice cubes for ARI Mon, various TDAS remotes, and various PPC muxes. This is due to an Overflow condition on one of the DPU cards (DP20). PPC is currently the backup, but this condition would prevent Ops from being able to switch over to PPC if something were to happen to TDAS. . This is not a reportable condition. <I> **** Actions Taken **** Notified MCR, wrote CR, and generated WR. | 02-00-PPC-COMP-8715
385157 | CR | 20181001 |  | 3 | Operator log MS-PIC-18A limits need change |  |  |  | N | NO | <D> **** Detailed Description **** MS-PIC-18A steam pressure on operator logs is consistently out of spec high since the change to 100% thermal output with LEFM. Recommend an assignment to engineering to provide ops procedures with new limits and an assignment for ops procedures to update ops logs with the new limits. <I> **** Actions Taken **** Discussed with engineering and ops procedures. | 02-00-MS-PIC-18A
385158 | CR | 20181001 |  | 4 | Replace spare breakers in E-LP-7EA WO# 02085412-03 | N | N |  | N | NO | <D> **** Detailed Description **** Upon opening panel E-LP-7EA on the two spare breakers 29 and 31. It was discovered that there were wires terminated on 29 and 31. EWD-46E-433 REV.0 AND REV.1 indicate that breakers 29 and 31 do not have wires on them. <I> **** Actions Taken **** Planner will add steps to determ and spare conductors. <N> Engineering and Maintenance - Bring Back for more information A review of archival drawings (E734-1) shows that circuits 29 & 31 have been spared for at least 17 years. These are unscheduled circuits and disconnecting the wires on these circuits is inconsequential. <S> Work instructions have been updated as requested.
385159 | CR | 20181001 |  | 4 | Personal Medical Condition â€“ Transport Off-Site |  |  |  | N | NO | <D> **** Detailed Description **** On Monday, October 01, 2018 an Energy Northwest experienced a personal medical condition in their work area. A co -worker assisted the employee to the Occupational Health Clinic. The patient was evaluated by a Registered Nurse and determined to need an ambulance transport to the hospital. The Control Room was called and an ambulance was requested at 8:08 A.M. No first responder tone out was needed per PPM 1.9.14. Hanford Fire Department (HFD) Medic 1922 and Medic 1923 arrived at 8:21 A.M. The patient was further evaluated by HFD and transported to Kadlec Medical Center at 8:47 A.M. <I> **** Actions Taken **** The employee is from organization 54440. An acting supervisor left site to meet the patient at Kadlec Medical Center. Emergency Preparedness was notified of the event for ERO purposes.
385160 | CR | 20181001 | CAQ | C | PrePI&R FSA 2018: Guidance lacking to document risk for LTCA |  |  |  | N | NO | <C> Per MRT feedback on 10/04/2018, this CR was prioritized as CAQ/C. <D> **** Detailed Description **** During the pre-PI&R FSA, a review was conducted of the LTCA coded corrective action assignments. Of the twelve items reviewed, six of them have been rescheduled more than one time. When the LTCAs were approved for extension, there was no additional justification of risk documented for those extensions. SWP-CAP-01, Section 4.5 Long-term Corrective action, needs to be enhanced to require documentation to verify there is no additional risk being incurred if the completion date of the corrective action is extended beyond the upcoming refueling outage. <I> **** Actions Taken **** Discussed issue with CAP Supervisor and industry peer.
385161 | CR | 20181001 |  | 3 | Procedure enhancement/revision CI-9.13 |  |  |  | N | NO | <D> **** Detailed Description **** CI-9.13, Fuel Pool Sampling Document, needs an enhancement/revision. Step 6.1.3 substep d. says when sampling Fuel Pool Demineralizer to start sample pump, this is no longer always required. We usually get plenty of flow with the sample pump off. This step should say IF required, or if adequate flow not achieved THAN start sample pump. Also, the EPN for the sample pumps are incorrect. They should be PSR-P-25A/B. This procedure is a reference use procedure that has sign off steps, and really does not need sign off steps. <I> **** Actions Taken **** Talked to supervision, and wrote CR.
385162 | CR | 20181001 |  | 3 | (FP) Fire brigade grading criteria and critique process gap |  |  |  | N | NO | <D> **** Detailed Description **** An unnanounced drill has been performed and it showed that there is a gap in the new grading criteria and critique process . That gap is informing the fire brigade of the new grading criteria so that they are aware of the requirement .Unannounced drill was a successful/passing drill. <I> **** Actions Taken **** CR written and documented inpost drill critique write-up Recommend assign to Ops Training for dissemination of information
385164 | CR | 20181001 |  | 4 | WANO 2018 - Disposable PC container overflowing |  |  |  | N | NO | <D> **** Detailed Description **** During walkdown of the power block with the INPO Fire Protection evaluator, a protective clothing trash container on the refuel floor (Reactor 606) was found with disposable materials sticking out above the flame retaining ring. This condition defeats the purpose of the flame retaining ring as materials need to be maintained within the container below the top of the retaining ring to effectively put out any potential fire within the container. Labels have been installed on these flame retaining rings to inform the user of this requirement to ensure materials are kept below the top of the ring. In this case, the user(s) did not meet the requirement. However, upon follow-up inspection by the Fire Marshal, he found the condition to have been corrected (see photos in EDMS). This CR is being initiated to document that the as-found condition did not meet station expectations, but the as-left as corrected by other station personnel does meet requirements. This CR can be trended. <I> **** Actions Taken **** 1) Requested Fire Marshal perform follow-up inspection 2) Initiated this CR
385165 | CR | 20181001 |  | 4 | chemical locker inspections not IAW SWP-CHE-05 |  |  |  | N | NO | <D> **** Detailed Description **** The Chemical lockers owned by the IC shop were not inspected monthly as required by SWP-CHE-05. A recurring AR assignment was setup by the previous shop manager for a quarterly inspection with the last inspections occurring in 3/2018, 6/2018, and 9/2018. No discrepancies noted on any of these inspections. <I> **** Actions Taken **** Completed chemical locker inspections in September, 2018 with NO deficiencies noted. Created new monthly recurring Model AR 385131 for tracking purposes. Maintenance manager and chemistry manager informed.
385166 | CR | 20181001 | CAQ | D | CMS-SR-20 Particualte Filter Paper Green Color | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of WO# 02125259-01, Step 7.10.10, the removed filter paper had a green color. <I> **** Actions Taken **** Notified Supervision and wrote CR to documnet for trending purposes.
385167 | CR | 20181001 | CAQ | D | Transformer Pressure Low | Y | N |  | N | YES | <D> **** Detailed Description **** During system walk down, pressure gauges for E-TR-7/71 and E-TR-7/73 were identified to be reading close to zero psig. There is a need for nitrogen gas top up for these transformers to maintain the TRMX pressure. <I> **** Actions Taken **** Initated a CR | 02-00-E-TR-7/71,02-00-E-TR-7/73
385168 | CR | 20181001 |  | 4 | POC Meeting Scheduling Error |  |  |  | N | NO | <D> **** Detailed Description **** Plant Operations Committee (POC) meeting occurances were scheduled incorrectly on the SharePoint teamsite. These meeting occurances did not align with the schedule on the POC outlook calendar causing confusion for individuals scheduling an LCS review. <I> **** Actions Taken **** SharePoint calendar on the Plant Operations Committee Teamsite has been removed. Once the error likely situation was identified, the best action going forward was to have one clear schedule for POC meeting occurances which was detirmined to be the outlook calendar.
385169 | CR | 20181001 |  | 3 | RCIC Div 1 Out of Service alarm â€“ *NRC Identified* |  |  |  | N | NO | <D> **** Detailed Description **** SUMMARY: During the DG1 maintenance outage the NRC resident noted that the cause for â€œRCIC DIV 1 OUT OF SERVICEâ€ alarm (H13-P601.A4.6-8) was not stated explicitly in the ARP. Recommend following Note or something similar be added to the ARP for P601.A4.6-8. â€œNOTE: DG1 OUT OF SERVICE status light on DG DIV 1 BISI panel will also cause the SW A OUT of SERV and BATT B1-1 OUT OF SERV status lights to illuminate at the other BISI panels.â€ . DETAILS: Three BISI tiles were lit but only one actually causes the annunciator P601.A4.6-8 to alarm according to the ARP. The BISI that caused P601.A4.6-8 to alarm was â€œSW A Out of Serviceâ€. The other two BISIâ€™s were â€œBATT B1-1 Out of Serviceâ€ and BISI â€œBATT B2-1 Out of Serviceâ€. The BISI panel for SW A had two BISIâ€™s lit, but the â€œSW Div 1 Out of Serviceâ€ alarm was not lit and so no guidance was given in that ARP. The following Note is in the ARP for â€œDG 1 Out of Serviceâ€ (H13-P800.C1.10-1). â€œNOTE: DG1 OUT OF SERVICE status light on DG DIV 1 BISI panel will also cause the SW A OUT of SERV and BATT B1-1 OUT OF SERV status lights to illuminate at the other BISI panels.â€ Recommend this Note or something similar be added to the ARP for for â€œRCIC DIV 1 OUT OF SERVICEâ€ alarm (H13-P601.A4.6-8).
385172 | CR | 20181001 |  | 3 | Install welded handles on both sides of RX doors (all doors | Y | Y |  | N | NO | <D> **** Detailed Description **** Install welded handles on both sides of RX doors (all doors with DP on them and Security Doors) Some doors already have the welded handles. Need to get them on both sides so doors are easier to control and prevent injury. This a safety concern brought up by craft and would like this issue added to Safety Committee action list. <N> **** Equipment Description **** Doors through out the Plant AR 385172 and 385414 are duplicates of 339317. RIE 339317-01 and WR 29146555 will install the door handles listed in AR 385414. E Knibbe 1/10/19
385173 | CR | 20181001 | CAQ | D | DG-ENG-1A1 exhaust loop seal was found plugged | Y | N |  | N | YES | <D> **** Detailed Description **** while performing WO 02128139-02 the loop seal was found plugged were it makes the u-turn at the floor. the pipe going up to the exhaust was not plugged. <I> **** Actions Taken **** We replaced the loop seal piping with new pipe. Contacted the engineer. <N> **** Equipment Description **** DG-ENG-1A1 exhaust loop seal | 02-00-DG-ENG-1A1
385174 | CR | 20181001 | CAQ | C | LD-MON-1A,2A,1B,2B Terminal Board Ref. Temp difference | Y | N |  | N | YES | <D> **** Detailed Description **** Upon System Engineering walkdown in 10/1/18, LD-MON-1A and 2A are showing higher terminal board reference temperatures than LD-MON-1B and 2B. By 10 F difference but consistent on Input Status . ISP-LD-S901 and ISP-LD-902 last performance was completed SAT and test all ranges, trips and resets of each TE associated with the LD MONs. CVI -OMM 671-00,1 states the Terminal Board Reference Temperatures are used to determine values for the ambient channels. The lower leg of the TE is attached to the Terminal Board. There are no self-test faults present on any of the LD mons (Other than the known issue with LD-TE -45D to be worked in R24 in LD-MON-2B). Initiated CR to track issue which does not impact functions, consult vendor, and based on vendor feedback initiate additional actions or close issue by documentation. Request this as a 3 NON-CAQ to SEEIC (WR will be generated if needed) Pictures attached to EDMS <I> **** Actions Taken **** Notified SM and Supervisor <N> **** Equipment Description **** H13-P642 and H13-P632 Main Control Room | 02-00-LD-MON-1A,02-00-LD-MON-1B,02-00-LD-MON-2A,02-00-LD-MON-2B
385175 | CR | 20181001 | CAQ | D | Need Modified per FDI Sticker on APRM-LPRM Channel 1 |  |  |  | N | YES | <D> **** Detailed Description **** As part of the EC 8076 implementation, when APRM-LPRM Channel 1 was upgraded per WO 02087917 back in Nov 2017, we never put the Modified per FDI No 003N6234 REV 1 sticker. Channel 3 and 4 have the sticker. This issue is administrative in nature. See emds for image <I> **** Actions Taken **** Notified Supervisor, initiated CR/WR <N> **** Equipment Description **** Control Room | 02-00-APRM-CHS-1,02-00-LPRM-CHS-1
385176 | CR | 20181001 |  | 4 | pwc-v-512 | N | N |  | N | YES | <D> **** Detailed Description **** valve leakby is increasing again. flowmeter is showing approx 30-40 gpm. recommend replacing valve with a more suitible as this is a recurring issue as it was replaced 1-2 years ago and now we are having repeated issues with pond level <I> **** Actions Taken **** informed MCR initiated CR/WR tightened valve in the shut direction after flushing seat with little reduction in flow | 02-00-PWC-V-512
385177 | CR | 20181001 |  | 4 | 2018 WANO Evaluation - Potential Damaged Extension Cord |  |  |  | N | NO | <D> **** Detailed Description **** During walkdown of the power block with the INPO Fire Protection evaluator, an extension cord was found installed across the general floor area west of TOA-HV-1A. The cord has been in place for approximately 2-1/2 years and is in the travel path to an empty drum storage area south of TOA-HV-1A. The cord is taped to the floor, but does not have any protective device installed over it and appears to have damage to its insulation from travel across the cord. Recommend assignment to IS as the extension cord tag references AR-CAM 324642 which is for installation of cameras at the steam tunnel. Action would be to replace existing cord and provide a protective device over the new cord in case the 55 gallon drums are to be moved into or out of the storage area south of TOA-HV-1A. See photos in EDMS <I> **** Actions Taken **** 1) Discussed with WANO evaluator 2) Requested Fire Marshal walkdown 3) Initiated CR <N> **** Equipment Description **** Adjacent to TOA-HV-1A | 02-00-T-BLDG-MISC
385178 | CR | 20181001 |  | 3 | Sheave Beam repair has two misaligned plates | N | N |  | N | NO | <D> **** Detailed Description **** The sheave beam top flange repairs have two misaligned plates that require a weld repair to create an even transition. <I> **** Actions Taken **** Notified engineering, walked down and discussed possible repair details | 02-00-MT-ELEV-4
385179 | CR | 20181001 |  | 4 | 2018 WANO Evaluation - CAUTION sign laying on ground |  |  |  | N | YES | <D> **** Detailed Description **** Outside the northeast corner of the Transformer Yard inside the Protected Area, there is a metal CAUTION sign attached to a metal post laying on the ground next to FP-V-314. The sign says 'CAUTION Buried Electrical Conduit In Concrete Bases' with an arrow. See the photo attached to the EDMS of this AR CR 385179. This condition was noted and questioned by peer evaluators during field walkdown for the 2018 WANO Evaluation. Initial investigation determined that this condition was previously identified in July of 2014 via AR CR 310323 (CAUTION sign attached to metal post laying on the ground). But, AR CR 310323 and ASGN 310323-01 were completed by AR-RXMAINT to initiation of WR 29114789. Subsequently, WR 29114789 and WOT 02049135-73 were later cancelled in February of 2015. Meanwhile, the CR subject CAUTION sign remains laying on the ground next to FP-V-314 inside the Protected Area. For resolution, need to determine if this sign needs to be installed (or not). If it does not need to be installed, the sign needs to be thrown away. If it does need to be installed, the sign needs to be reinstalled. | 02-00-CGS-BLDG-MISC
385180 | CR | 20181001 |  | 3 | Could not advance WOâ€™s in Data Glance |  |  |  | N | NO | <D> **** Detailed Description **** During the DG1 annual maintenance outage two WOâ€™s 02103620-01 and 02103621-01 could not be authorized for work. Multiple individuals from Supervision to the CRS and OCC OPS rep tried with no success. Ext 5656 was called and I spoke to two individuals that werenâ€™t able to reach Data Glance assistance. The Shift Manager had to take the WOâ€™s to working in Portal J. <I> **** Actions Taken **** Generated CR for tracking and worked the packages on paper. <N> Both DataGlance audit trails for WO Tasks 02103620-01 and 02103621-01 were reviewed. There were no indications of any issues or problems with the package, plus there were no holds in place to prevent the packages from going to Authorized status. The package was taken to working by Operations in Asset Suite and the package was able to be worked and completed. Assignment Complete.
385181 | CR | 20181001 |  | 4 | TMU-V-88 will not close all the way | N | N |  | N | YES | <D> **** Detailed Description **** While operating TMU-V-88 open and closed it was observed that the valve would not close all the way. The leakby from the partialy open valve is around 2 gallons/minute. The leakby returns back to the TMU pumps intake basin. <I> **** Actions Taken **** Wrote CR and informed CRS. | 02-00-TMU-V-88
385182 | CR | 20181001 |  | 4 | PWC-SV-301 gasket leak | N | N |  | N | YES | <D> **** Detailed Description **** PWC-SV-301 gasket leaks an in almost 180Â° arc around valve body. Recommend replacing gasket <I> **** Actions Taken **** Informed MCR Discovered while securing system. Currently depressurized/ not leaking | 02-00-PWC-SV-301
385183 | CR | 20181001 |  | 4 | HP-EQ-53252 Hand Held Monitor CM-11 Malfunction / Cal Due | N | N |  | N | YES | <D> **** Detailed Description **** The hand held CM-11 contamination monitor located at the entrance to the main control room, is in FAULT alarm, does not pass the Beta response check, displays low gas flow, and is due for calibration as of 10/2/2018. There was an existing work request (#29143733) initiated for this equipment, but the deficiency tag was removed very recently, but the problem still exists (low beta count response). <I> **** Actions Taken **** Initiated this AR and a new work request. Attached a deficiency tag to this equipment. | 02-00-HP-EQ-42725,02-00-HP-EQ-53252
385184 | CR | 20181001 | CAQ | D | DSA-PCV regulator air leak | Y | N |  | N | YES | <D> **** Detailed Description **** WO 02122319 was completed to replace cross tie valve as IC identified that it may be leaking AR372214 during their initial set up and instalation of the new PCV. The PCV is still regulating or leaking even with the cross tie valve replacement, Rust was found in the DSA system when the cross tie valve was replaced as the valve makes a dead leg. Because of this engineering recommends that the PCV be inspected, rebuilt or replaced if necessary as either the regulator seat has particulate in it or the regulator is not fully funcational due to another reason. This PCV was recently installed and the condition has always existed. Operability is not challeneged as the leak is minor and no negative trends have been identified since this issue was identified by the original CR. Engineering recomends investigating during this DG window as this can not be worked online. <I> When walked down 10/2/18 AM, DSA-PCV-2A and DSA-PCV-1A were both leaking (minor but continuous leakage) from their exhaust ports. Though minor (i.e., not causing excessive cycling of the DSA air compressors), exhaust port leakage observed from 1A was more (louder wisping) than that from 2A. Updated AR CR and WR to indicate EPNs DSA-PCV-2A and DSA-PCV-1A instead of just DSA-V-10A. | 02-00-DSA-PCV-1A,02-00-DSA-PCV-2A,02-00-DSA-V-10A
385185 | CR | 20181002 |  | 3 | ops crew unable to access shared passwords |  |  |  | N | NO | <D> **** Detailed Description **** SOP-DEH-OPS directs operating crew mwmbers to access a shared password folder on S:Operations/Crops/Shared Passwords/DEH Passwords. The crew does not have the rights to open this folder. . Please fix the folder rights <I> **** Actions Taken **** wrote CR
385186 | CR | 20181002 | CAQ | D | DSA Leak detected after PMT signed complete. | Y | N |  | N | YES | <D> **** Detailed Description **** Mechanics performed and additional Snoop test and found the valve leaking at the body. Engineering was contacted to evaluate. Based on the design of the valve and the piping configuration it is possible that the preload is insufficent. Due to the impact of cumulative leaks engineering recomends further investigation and a sucessful PMT prior to restoring the DG. Best practice is to remove the air pressure when performing torque set of the bolts. If additional guidance is required for torque value design will need to confirm allowable limit. <N> Snoop check performed again on Morningof 10/2/2018. No leaks from any portion of the valve external were found with snoop. | 02-00-DSA-V-10A
385207 | CR | 20181002 |  | 3 | Sec computer sys/IEBS datapump import validation scripts | N | N | N | N | NO | <D> **** Detailed Description **** The data validation scripts that check the IEBS data need to be modified to accommodate non-US citizens due to the way they're Nat IDs are handled in SSIS. <I> **** Actions Taken **** Identified resolution
385210 | CR | 20181002 |  | 3 | Revise FLEX Procedures for Flow | N | N | N | N | NO | <D> **** Detailed Description **** Revise PPM 5.6.1, PPM 5.6.2, and the ABN-FSGs for flow (re-ordering the procedure for shorter duration actions up front, longer term actions in the back of the procedure). This was discussed with the NRC Resident during the FLEX Inspection June 2018 and captured in CR 381241, 381403, and 381430 but this CR is being written to provide a more overarching procedure review. This should be performed during the HCV order Phase II project. Assign to Ops EOP Coordinator.
385215 | CR | 20181002 |  | 3 | Procedure enhancement PPM 12.14.12 | N | N | N | N | NO | <D> **** Detailed Description **** PPM 12.14.12 needs updated for current system operation. For isolating RCC-DM-1, isolation boundaries have been moved to RCC-V-200 and RCC-V-199 and operations shut these valves using a standard clearance. Since Chemistry does not operate valves, I recommend removing steps 6.4.1 a and 6.4.1 b and using the Model Work order to control isolation boundaries. The MWO and Standard Clearnance should be updated also to remove the direction to coordinate with Chemistry to isolate the demin and hang the clearance. <I> **** Actions Taken **** Verified with chemistry that RCC-V-202, -203, -207, and -208 are not reliable isolation valves and are not the preferred isolations.
385216 | CR | 20181002 |  | 4 | Typo in ES001178 - Equipment Reliability Presentation | N | N | N | N | NO | <D> **** Detailed Description **** There is a typo in the Equipment Reliability (ES001178) Presentation. The typo is in a slide in the presentation and Student Handout 4. The slide and Student Handout are a snippet from page 9 of INPO AP-913, Equipment Reliability Process Description, Revision 6 April 2018. <I> **** Actions Taken **** Notified Supervisor and INPO Observer of CR initiation. Notified INPO of typo in AP-913 via email. Verified Typo does not exist in PPM 1.5.15
385221 | CR | 20181002 |  | 3 | 2018 WANO Evaluation - Protected sys methods for room doors | N | N | N | N | NO | <D> **** Detailed Description **** Evaluation is needed for the practice of using magnetic placards for protection of entire rooms. PPM 1.3.83 states "Barrier rope, plastic chain, physical devices and other similar devices or door handle covers for room doors" will be used for protected equipment. The WANO team dentified this deficiency. <I> **** Actions Taken **** Notified SM. Added plastic chains to the protection scheme for the DG1 outage.
385227 | CR | 20181002 |  | 4 | Broken cover on GSB exterior 120 VAC electrical outlet | N | N | N | N | YES | <D> **** Detailed Description **** The protective cover for the exterior 120 VAC electrical outlet at the southeast corner of the GSB (on the east exterior face of the building) is broken (off). Please replace this cover. A photo is attached to the EDMS of this AR CR 385227. | 02-00-GSB-BLDG-MISC
385228 | CR | 20181002 |  | 4 | RWCU-DM-1B flow continues to degrade. | N | N | N | N | YES | <D> **** Detailed Description **** RWCU-DM-1B is suffering from degraded flow and the inability to raise flow, due to a failed RWCU-FC-89B (ref. AR# 384561 and 384467). At some point on 10/1/18 RWCU-DM -1B flow lowered to ~ 105 gpm, which initiated the RWCU hold pump and hold valve. RWCU-DM-1B flow could not be raised with RWCU-FC-89B; therefore, flow was lowered in RWCU-DM-1A in an attempt to force flow through RWCU-DM-1B, to secure the hold pump. This was unsuccessful. RWCU-DM -1A flow was lowered to ~ 107 gpm and RWCU-DM-1B flow did not change. Hold pump actuation did not have a noticeable effect on RWCU-DM-1B D/P. Demin D/P remains steady at ~ 1.33 PSID. Continued hold pump operation is not believed to be detrimental to the operation of RWCU-DM-1B. Per 4 .RWCU.DM, drop 2-3, RWCU-DM-1B should not isolate and go into HOLD mode until flow lowers to 54 gpm. Note: RWCU -DM-1B health is currently a Plant Concerns item. <I> **** Actions Taken **** Informed MCR. Verified RWCU-DM-1B D/P not adversely affected by hold pump operation. <N> **** Equipment Description **** RW 467, RWCR | 02-00-RWCU-DM-1B
385233 | CR | 20181002 |  | 4 | Site 1, 2 & 4 Housekeeping |  |  |  | N | NO | <D> **** Detailed Description **** Following the resolved / removed tarp from the 115 kV Line (AR CR 383203 â€œAppears to be a Tarp on the 115 kV B Phaseâ€), BPA performed walkdowns of sites 1, 2 and 4 with the following observations and recommendation was made: â€œOn a drive into Benton Sub and WNP1 meter point I noticed a significant amount of debris at Sites 1, 2 & 4. I suggest CGS take a corrective action to pick up debris that can be wind carried or nesting material for the larger birds. Examples: Large piece of black plastic laying loose along WNP1 fence line (Range Road). Plastic near CGS cooling towers Site 1 is littered with 1â€™, 2â€™ 3â€™ lengths of wire, cable and metal strapping all possible source material for nesting crows, osprey, hawks and eagles. I have seen numerous nests were conductive objects have been used as nesting material. The debris I saw was easily found and took no effort to spot, all with a short distance of 115, 230 and 500kV lines that directly affect the CGS nuclear plant or site 1.â€ â€“Note: There are several spools of wire covered with weathered blue tarps which may or may not have been a source for the tarp found on the 115 kV line (AR CR 383203) - See EDMS for pictures. - Recommendation: Facilities to perform site 1, 2 & 4 walkdowns and address the housekeeping concerns. <I> **** Actions Taken **** Contacted Supervision and System Engineer. <N> **** Equipment Description **** Various locations at Sites 1, 2 and 4. See EDMS for pictures.
385235 | CR | 20181002 |  | 3 | DG-1 Outage Lessons Learned - 1.3.76 procedure enhancement | N | N | N | N | NO | <D> **** Detailed Description **** in attachment 9.3 for extended DG maintanance outages, recommend placing a note to verify CIA (ADS) bottle pressures and replace any before the outage, that may impact operability during the outage. We are currently in a situation where we have multiple bottles at or near the low spec that require changeout but cannot due to them being protected. <I> **** Actions Taken **** informed MCR <N> **** Equipment Description **** PPM 1.3.76
385239 | CR | 20181002 |  | 3 | (QA) Longstanding CWPH Safety/Housekeeping Issues | N | N | N | Y | NO | <D> **** Detailed Description **** (QA) Longstanding safety and housekeeping issues not addressed in a timely manner or with effective mitigating actions. While performing an observation of field work associated with the Halogenation Surveillance during a Quality audit, housekeeping/safety conditions in the Circulating Water Pump House (CWPH) were found to be unsatisfactory. Factual Basis: â€¢ An auditor noticed large amounts of water pooled in various parts of the CWPH main room due to designed pump leakage and water spraying from fire pump FP-P-3. This has allowed large amounts of water to pool in low lying areas of the room creating slip hazards. Other areas of the room have sizeable deposits due to standing water evaporating over time indicating that there are additional areas where water accumulates, but were not wet at the time of the observation. When the safety hazard was pointed out to the chemistry technicians they seemed to be accustomed to these issues, and stated that â€œwet floorâ€ signs are placed throughout the room. The technicians explained that an attempt was made to mitigate the FP-P-3 leak-by installing a makeshift catch container around the pump, but the container is ineffectively routed to a floor drain. â€¢ The auditor then proceeded to the sample room where it was noted that a sign is hung on the outside of the door warning of a floor drain that overflows when a sump pump is started. The chemistry tech performed a take 2 and advised the auditor that the room had the potential to flood if sump pump started and the floor drain began to back up. The technicians stated that at one point in time there was an alternate hose installed to help mitigate the flow of water out of that drain, but it was no longer installed. The floor of the room showed obvious signs of persistent water intrusion along with soaked carpet under the sample area. The techs stated that the issue has been identified with a Condition Report (CR) multiple times in the past, and a new CR was not needed because the issue was already in the Corrective Action process. â€¢ A short time later, the sump pump could be heard starting, and the Chemistry technician advised the auditor that now would be a good time to leave to avoid getting wet shoes. Within 10-15 seconds of this statement, the auditor found himself standing in approximately 0.5 inch to 1 inch of water. Insights: â€¢ A search of CRs, Work Requests (WRs), and Work Orders (WOs) in Asset Suite showed the most recent CR-377887 was written on 3/14/2018 (associated WR 29141603 was cancelled on 10/01/2018), the oldest CR-313350 was generated on 8/27/14 (associated WR 29115871 completed 09/03/2014, WR 29115672 completed 08/20/2014, and WR 29115454 completed on 08/12/2014). â€¢ A review of the Chemistry Top Ten Equipment issues list, which was updated on 9/17/18, has â€œFlooding CWPH RM B107 Test Roomâ€ listed as the 3rd highest priority. â€¢ Inadequate advocacy by the chemistry department to ensure resolution of this longstanding safety/housekeeping issue. This could potentially lead to a culture of acceptance of substandard safety/housekeeping issues at the station. â€¢ A work week manager explained that an increased chemistry involvement in the initial work week screening meeting as well as involvement in the T-week process could ensure the proper priority is assigned to the WRs and WOs intended to eliminate this unsafe condition. â€¢ Note: standing water was cleaned up by the end of the day. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Chemistry. <I> **** Actions Taken **** Discussed this Issue with the Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, and Chemistry/Rad Safety Manager <N> These issues were identified by an external Technical Specialist from St Lucie Nuclear Power Plant during the AU-CH-18 audit. Safety Committee has been notified of the issue (see attached e-mail in EDMS). | 02-00-P-BLDG-MISC
385242 | CR | 20181002 |  | 4 | SCH-CR-51 | N | N | N | N | YES | <D> **** Detailed Description **** System 1 is not operating within suggested operating ranges. System 2 is already unavailable. <I> **** Actions Taken **** Secured SCH-CR-51, notified supervisor, initiated this C/R <N> **** Equipment Description **** GSB basement | 02-00-SCH-CR-51
385245 | CR | 20181002 | CAQ | D | Received Oscillograph Started, H13-P800.C4.4-3, alarm | N | N | N | N | NO | <D> **** Detailed Description **** Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 238 B: 239 C: 238 E-TR-B A: 118 B: 118 C: 118 The following sensor was tripped and is reset: J12 - SM-8 under voltage BPA reports the following: a. Cause was John Day - Big Eddy 500 KV line #1 relayed off and reclosed b. Relaying involved a single pole c. There is no damaged equipment, no emergent outage required, and no RAS initiated <I> **** Actions Taken **** Trend
385246 | CR | 20181002 |  | 3 | (Near Miss) ladder fell approximately 30ft | N | N | N | N | NO | <D> **** Detailed Description **** While lowering a 20ft extension ladder from T501 to T441 through the crane bay the 1/4â€ natural fiber rope that was being used broke, this allowed the ladder to fall approximately 30ft to the floor below. The employees secured the area and contacted their Supervision. The area below was being monitored by a dedicated individual assigned to block traffic from entering the area. The weight of the ladder (40lbs) was well within the capacity of the Â¼â€ rope (540lbs min breaking strength). <I> **** Actions Taken **** Contacted Industrial Safety, OCC, Maintenance Manager, and Shift Manager | 02-00-T-BLDG-MISC
385247 | CR | 20181002 |  | 4 | EMIT Lab Temporarily Unavailable for Testing |  |  |  | N | NO | <D> **** Detailed Description **** EMIT Lab testing temporarily unavailable due to improper prior planning to have quality controls on hand to meet the NRC requirements (10 CFR section 26.137) for fitness for duty testing. <I> **** Actions Taken **** Fitness For Duty test samples sent to the HHS Certified Lab for testing until controls are received that meet NRC requirements. Notified Access Control and initiated this CR. . EMIT - (ENZYME MULTIPLIED IMMUNOASSAY TECHNIQUE) facility, located in Room 242 of the Willamette Building. HHS - Health Human Services, Certified Laboratory. <N> When EMIT Lab is unavailable an alternate process is in place to send samples offsite to continue meeting NRC requirements. There is no regulatory impact with this specific instance. The controls (i.e. calibration sample) were reordered and expedited to minimize the need for sending samples offsite. No further action is required at this time.
385248 | CR | 20181002 |  |  | PCR, DO-V-609 incorrect position on SOP-DG1-LU | Y | N |  | N | YES | <C> This was canceled and is a duplicate of 385251 <D> during the lift of a danger tag out it was noted that the restoration position for DO-V-609 was incorrect. After checking the SOP-DG1-LU which matched the position on the clearance, M512-4 was checked and the cap which was missing in the tag out and the Line Up. The correct position according to the M drawing is closed and capped. <I> initiate CR and inform CRS | 02-00-DO-V-609
385250 | CR | 20181002 |  |  | PCR, DO-V-609 incorrect position on SOP-DG1-LU | Y | N |  | N | YES | <C> Cancelling at the request of the initiator, this CR was improperly backgrounded for initiation, and is a duplicate of 385251. <D> during the lift of a danger tag out it was noted that the restoration position for DO-V-609 was incorrect. After checking the SOP-DG1-LU which matched the position on the clearance, M512-4 was checked and the cap which was missing in the tag out and the Line Up. The correct position according to the M drawing is closed and capped. <I> initiate CR and inform CRS CR stuck at inprog, asked initiator to create new one. This CR can be cancelled since it's a duplicate of 385251 | 02-00-DO-V-609
385251 | CR | 20181002 | CAQ | C | PCR- DO-V-609 incorrect position on SOP-DG1-LU | Y | N |  | N | NO | <D> **** Detailed Description **** while lifting a danger tag out on DO system it was noted that the restoration position was incorrect. The SOP-DG1 -LU procedure was referenced and the position matched the tag out. The position was still question so the drawing was referenced which showed the correct position which is closed and capped. (M512-4) <I> **** Actions Taken **** initiate CR and inform CRS. | 02-00-DO-V-609
385252 | CR | 20181002 |  | 3 | RAM found in Clean Area within RCA | N | N |  | N | NO | <D> **** Detailed Description **** A torque wrench labeled radioactive material was found on an I&C cart located inside the Main Control Room (MCR). The MCR is designated a â€œClean Areaâ€ inside the Radiologically Controlled Area within the power block. Documentation indicates that the torque wrench has been inside the MCR since 9-18-18. Torque wrench was labeled appropriately per applicable procedures. The torque wrench was direct frisked, smeared and monitored by an HP Technician using the SAM-12 outside the MCR. The torque wrench was found to be free of contamination. Extent of Condition survey of I&C cart and surrounding material revealed no contamination or additional radioactive material. <I> **** Actions Taken **** Wrote CR. | 02-00-W-BLDG-MISC
385253 | CR | 20181002 | CAQ | C | DG-VM-DG1/1 replacement has different fit |  |  |  | N | NO | <D> **** Detailed Description **** The replacement for DG-VM-DG1/1 was found to be of different fit than the installed unit. The mounting holes and conduit entry did not line up. This was identified during performance of WO 02102028-01 â€œDG-VM-DG1/1: REPLACEMENTâ€. See EDMS for photos. Recommend assignment to Procurement Engineering to perform item equivalency evaluation. <I> **** Actions Taken **** Discussed with OCC, Procurement Engineering | 02-00-DG-VM-DG1/1
385254 | CR | 20181002 |  | 4 | Flocculator Poly Pump Rate not enough to maintain turbidity | N | N |  | N | YES | <D> **** Detailed Description **** Poly chemical addition rate is not enough to maintain turbidity low enough for operation of flocculator. This is either due to clogged tubing or the need for a rate adjustment. The current rate is coming out of the tubing at 3 drops per second which is less than necessary. This is causing high turbidity spikes which trips the flocculator and challenges potable water volume available. <I> **** Actions Taken **** Backwashed and started flocculator. After 30 minutes of dumping, outlet turbidity was stable near .11 NTU. <N> Flocculator Poly Pump = PWC-P-125 (Polyelectrolyte Feed Pump)? Reference AED M573-1. | 02-00-PWC-FU-1
385255 | CR | 20181002 | CAQ | D | DG-VM-DG1/1 Not performed during DG1 Maint window |  |  |  | N | YES | <C> CR duplicate of 385253. D/T <D> **** Detailed Description **** DG-VM-DG1/1 Not performed during DG1 Maint window, due to old and new meters were not the same dimensions. WO needs to be re-planned and rescheduled. See EDMS for pictures and dimensions of the old and new meters. Mounting dimensions and conduit placement are different. The dip switch settings are also different. High current light comes on at a different value then the data sheet, this is a factory set value and is not adjustable. PM WO 02125012-01 (CWO) will need to stay with 02102028/. <I> **** Actions Taken **** Existiing meter was not removed or affected prior to noting thes issues. WO returned for planning and rescheduling. <N> ***General Notes*** This is not a planning issue, the cat id ordered by the planner was correct, but the cat ID needs to be evaluated by engineering because the vendor changed the specifics on the meter. The CAT ID that was listed in the BOM is what was installed prior to this work taking place. I ordered what was listed in the BOM. Unbeknownst to us, the manufacturer changed the details of this particular model. Since this is NOT a like for like, an Engineering Change is required for installation | 02-00-DG-VM-DG1/1
385256 | CR | 20181002 |  | 4 | TOA-FL-1A Has Fallen Down | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FL-1A has fallen out and fell to the floor see EDMS for photos. TOA-FL-1A was previously written up for end of roll see WR 29144798. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** TB 501' E | 02-00-TOA-FL-1A
385258 | CR | 20181002 | CAQ | C | Total RWCU Demin Flow by UT is GT P&L |  |  |  | N | NO | <D> **** Detailed Description **** Ultrasonic flow transmitters (UT) have recently been installed on the RWCU demineralizers. The UT indicates 128 GPM on RWCU-DM-1A and 165 GPM on RWCU-DM-1B, for a total demineralizer flow of 293 GPM. Per P&L 4.17 of SOP-RWCU -DEMIN, total flow through both RWCU demineralizers should be limited to approximately 270 gpm during steady state operation in order to reduce Flow Accelerated Corrosion (FAC) damage to the RWCU HXs and piping. Due to instrumentation problems with RWCU-FC-89B, the only way to reduce RWCU flow to within the 270 GPM limit is by placing RWCU-DM-1B in hold. Taking RWCU-DM-1B off-line is undesirable due to RWCU-DM-1A nearing exhaustion (on-line for 41 days). <I> **** Actions Taken **** Contacted OCC OPS and Engineering representatives. Discussed with Engineering Code Programs Supervisor. | 02-00-RWCU-DM-1A,02-00-RWCU-DM-1B,02-00-RWCU-FT-89A,02-00-RWCU-FT-89B
385259 | CR | 20181002 |  | 3 | Design Error on new Pipe Support RDV-S-7 | N | N |  | N | NO | <D> **** Detailed Description **** During installation of new pipe support RDV-S-7 per WO 02125913-10, for the Radwaste Chiller WCH-CR-51A Replacement Project, it was determined that this hanger could not be installed as designed (ref CVI 216-01,3893), due to interference of the knee brace with the adjacent Radwaste building west stem wall . This issue is the result of a design error by the A/E during development of EC 17099. This does not affect the current functionally of WCH-CR-51A as this chiller is currently out-of-service and undergoing replacement. <I> **** Actions Taken **** Communicated issue to EN Design and A/E - initial review indicates associated interfering knee brace is not required - FCR to be issued to document this resolution, including revision of associated calculation ME-02-18-05. <N> **** Equipment Description **** W507, sourth of new chiller WCH-CR-51A | 02-00-WCH-CR-51A,02-00-WCH-RV-1A
385260 | CR | 20181002 |  | 4 | Lowering FPC return flow on FPC-FI-17 | N | N |  | N | YES | <D> **** Detailed Description **** FPC return flow on FPC-FI-17 is reading 550 gpm and lowering. On 10/29/2018 FPC-FI-17 was reading 600 gpm. RWCR operator reports that FPC-FIC-15B indicated flow is departing from the setpoint with a 6 psig on the output signal. <I> Note: "10/29/2018" date referenced should be 9/29/2018. | 02-00-FPC-FI-17,02-00-FPC-FIC-15B
385261 | CR | 20181002 |  | 4 | BRE 33 AC unit | N | N |  | N | YES | <D> **** Detailed Description **** The AC unit in BRE 33 needs maintenance. It is making a loud buzzing sound in the on or off position. <I> **** Actions Taken **** Turned unit off, notified supervison and work week manager <N> **** Equipment Description **** BRE 33, NE corner of PA
385262 | CR | 20181002 |  | 3 | Electrical outlet arc during Security limited scope exercise | N | N |  | N | NO | <C> Per MRT feedback received on 10/04/2018 this item was reopened to enable documentation of the event investigation details by Nuclear Security. <D> **** Detailed Description **** Security Drill player received an elctrical arc/sparking from outlet LP-50-A24 on the '437 RW South near door C100. <I> **** Actions Taken **** Lead Controller immediately stopped drill play and made sure the player was safe. Upon verifying that the player was safe and uninjured, and that there was no fire risk, a call was made to the Control Room to report it. Drill play was ceased in that area until notification from Control Room operators that the area was safe to resume drill play. . Outlet is powered from E-LP-5DA ckt 24. <N> **** Equipment Description **** South East wall, facing north, RW '437 outlet LP-50-A24 | 02-00-E-LP-5DA,02-00-W-BLDG-MISC
385263 | CR | 20181003 |  | 4 | Itemizer 09 failed test | N | N |  | Y | YES | <D> **** Detailed Description **** Itemizer 09 failed midnight operability test <I> **** Actions Taken **** failed test, notified supervision, CR/WR generated | 02-00-SEC-XD-9
385264 | CR | 20181003 | CAQ | D | Work order returned to planning. | Y | N |  | N | YES | <D> **** Detailed Description **** Work order 02106433 task 01 discovered the wiring issue. Work order taken back to RETURN to update instructions. Engineering looking into options of updating drawings or rewiring. <I> **** Actions Taken **** 02106433 taken to RETURN <N> **** Equipment Description **** DG1 | 02-00-DG-RLY-DG1/VR1,02-00-DG-RLY-DG1/VR2
385265 | CR | 20181003 | CAQ | D | Received Multiple fire/trouble alarms on FCP-2. | N | N |  | N | YES | <D> **** Detailed Description **** On 10/3/18 0115, Received Multiple fire/trouble alarms on FCP-2 on rows 4 and 5. Tours were performed in the affected areas, and no evidence of fire or smoke. A reset of the alarms on FCP-2 was performed, all alarms reset on rows 4 and 5 on FCP-2. 4-1 SYS 56 WET PIPE TG BLDG 471â€™ CONDENSER NORTH 4-2 SYS 7 WET PIPE TG BLDG 471â€™ ELECT SWGR BAY 4-3 SYS 8 WET PIPE TG BLDG 471â€™ RFW HEATER BAY 4-4 SYS 67 WET PIPE TG BLDG 501â€™ TG BEARINGS 4-5 CO2 SYS 1 TG BLDG 501â€™ GEN EXCITER HOUSE 5-1 CO2 SYS 2 TG BLDG 501â€™ HOSE REEL STATION 5-2 SYS 49 DELUGE/SYS 19 WET PIPE TSC 5-3 SYS 57 DELUGE MAIN XFMR TR-M1 5-4 SYS 58 DELUGE MAIN XFMR TR-M2 5-5 SYS 59 DELUGE MAIN XFMR TR-M3 | 02-00-FP-CP-FCP2
385266 | CR | 20181003 | CAQ | C | Missed Fire Tour Check | N | N |  | N | NO | <D> **** Detailed Description **** Security failed to perform the 2200 Fire Tour Check in DG2. <I> **** Actions Taken **** Security Supervision Notified, Shift Manager Notified, Individual was relieved from duty. | 02-00-D-BLDG-MISC
385282 | CR | 20181003 |  | 3 | DG-RMS-DG1/VRS Procedure Impact | N | N |  | N | YES | <D> **** Detailed Description **** EC 0000016405 disable the manual mode for DG-RMS-DG1/VRS and removed the handle for the swicth. This switch is still listed in the SOP-DG1-STBY lineup for verification. The switch should be removed from the lineup (the DG2 swicth of the same function was removed following perfomance of similar EC on DG2) <I> **** Actions Taken **** A note was written on the SOP-DG1-STBY that was performed stating that the manual mode is disable and the swicth handle has been removed. This CR was initiated to correct the procedure. <N> PROC AS 314950-20 already exists to track updates for Operations Procedures including PPM SOP-DG1-STBY affected by EC MALT 16405. Per the PROC AS 314950-20 In-Progress Notes, PPM SOP-DG1-STBY rev 021/000 was submitted 10/02/18. It appears that PROC AS 314950-12 was errantly taken to COMPLETE on 05/01/18. | 02-00-DG-RMS-DG1/VRS
385288 | CR | 20181003 |  | 4 | HP/LAB dose over the monthly estimate for September |  |  |  | N | NO | <D> **** Detailed Description **** HP and Laborer department went over their monthly dose estimates. HP's received 402mrem against a goal of 355, 36 of this was due to emergent work. Laborers received 417mrem against a goal of 395, 87 of this was due to emergent work. <I> **** Actions Taken **** Wrote CR <N> See EDMS for details regarding emergent dose received during the month of September 2018.
385295 | CR | 20181003 |  | 4 | SAM-12 @ HP PAP is Out of Service | N | N |  | N | NO | <D> **** Detailed Description **** SAM-12 @ HP PAP is OOS. (HP-EQ-42814) SAM-12 was frozen on the "Clear Screen" and then after reboot it will update background and then be set on the "Ready Screen." After opening the SAM-12 Door, it will automatically go into the "Background Update" for 100 seconds repeatedly. <I> **** Actions Taken **** -Initiated CR & WR. -Notified HP Supervision. <N> **** Equipment Description **** HP PAP (HP-EQ-42814) | 02-00-HP-EQ-42814
385300 | CR | 20181003 |  | 3 | 2018 WANO Evaluation â€“ Oily Waste Can Liners |  |  |  | N | YES | <D> **** Detailed Description **** Columbia uses thin green plastic trash liners inside the plant oily waste cans containing oil soaked pads/rags. WANO has questioned whether the liner, hanging out over the lip, allows the lids to seal tight. A semi-tight seal is needed to limit oxygen in-case of exothermic spontaneous combustion within the oily waste can. The vendor data from Justrite indicates they discourage the use of liner bags. However without a liner, there would be a build-up of waste oil on the inside of the can. The newer, larger oily waste cans in the Turbine Building have heavier lids that help them to seal better with the overlapping liner. The older, smaller oily waste cans, with lighter lids, may need to be replaced with the larger size. Plus, their lid pivot point design makes them more prone to the liner wedging the lid slightly open. Laborers were requested to determine the number and locations of the smaller oily waste cans. Fire Protection needs to evaluate this condition and decide the best course of action, with input from RP. This issue has no impact on the functionality of plant fire systems. This concern was raised at a WANO interview. <I> **** Actions Taken **** Researched, contacted various people, and wrote this CR. <N> **** Equipment Description **** VARIOUS LOCATIONS
385303 | CR | 20181003 |  | 4 | Fire Brigade cart wheel chocks |  |  |  | N | NO | <D> **** Detailed Description **** working 15.1.22 Step 7.4 cart inspection , wheel brake doesn't keep cart from moving need brakes replaced. <I> **** Actions Taken **** put clamps on wheel to restrain cart and contacted fire marshall <N> **** Equipment Description **** Fire brigade cart TG 441 turnout station.
385304 | CR | 20181003 |  | 3 | Request enhancement to procedure 10.25.13 |  |  |  | N | NO | <D> **** Detailed Description **** Procedure enhancement required to maintenance procedure 10.25.13. Request a beginning step to section 7.15 to facilitate the remaining steps. Add step "Manually charge and close breaker" prior to existing step 7.15.1 on page 44 <I> **** Actions Taken **** Initiated CR. Added procedure change request to detailed description. <N> ****General Notes**** An assignment has been created within the maint. procedure revision data base. a link to the data base has been created and placed within the EDMS of this AR.
385306 | CR | 20181003 |  | 3 | Update SOP-ELEC-SM1-MAINT, 5.5, Remove E-MC-1C From Service |  |  |  | N | NO | <D> **** Detailed Description **** Update SOP-ELEC-SM1-MAINT, 5.5, Remove E-MC-1C From Service, to allow to perform in Any Mode. This is to support 02090246 in the 12/10/18 week. See EDMS for details. <I> **** Actions Taken **** Notified WWM, PSRO & Ops procedure Writer
385309 | CR | 20181003 | CAQ | D | Franklin county siren C16 reported a partial alarm | N | Y |  | N | YES | <D> **** Detailed Description **** While doing the weekly poll test of the Franklin county sirens, C16 reported a partial alarm. This means one or more of the 10 amplifiers is not working and will reduce the output valume. This occured 7 days ago but the alarmed cleared before the tech arrived and was unable to find a problem. Reference CR 384925. WR 9144764 <I> **** Actions Taken **** Notified EP, and Dispatched a tech to resolve the issue. Recommend closing to WR. ITMGMT. <N> **** Equipment Description **** Franklin County
385310 | CR | 20181003 |  | 4 | PROENG, remove LOU from CID 36493, EC 16405 installed |  |  |  | N | NO | <D> **** Detailed Description **** PROENG, remove LOU from CID 36493, EC 16405 installed <N> Limitation on Use has been removed from CID 36493 as requested on this CR. Although, it is worth noting that the specific LOU wording directed the requestor to initiate an AR type ENG assignment to Procurement Engineering rather than write a CR. This CR should be trended.
385311 | CR | 20181003 | CAQ | D | Pallet needs replaced or recoated | N | N |  | N | NO | <C> CR 385311 has been edited as requested from the author. The following word has been edited, instead of â€œCombustibleâ€ it now says â€œNon-Combustibleâ€. <D> **** Detailed Description **** RW 437â€™ center authorized storage area #49 has two large blue tanks sitting on an oversized wood pallet. The wood appears to have been painted with fire resistant paint. However, a portion of the paint coating has worn off. There are two locations where the wood slats are broken and have rough edges. PPM 1.3.10C requires plant wood to be fire treated or fire paint coated. This large pallet should either be replaced by a new Non-combustible pallet (preferred) or the pallet should be repainted per procedure FCEI-2.2.1. This is not so bad that is an immediate FP concern (so does not need a TCP or fire tour), but request this be corrected in the next 6 months, if possible (since would take removal of the 2 large portable tanks). <I> **** Actions Taken **** Wrote this CR and will be calling the owner. <N> **** Equipment Description **** RW 437 center | 02-00-W-BLDG-MISC
385314 | CR | 20181003 |  | 4 | TES to PADs update error reported |  |  |  | N | NO | <D> **** Detailed Description **** Individual reported dose presented an error during automated update because previous CGS dose reported was in date range of reported dates of exposure. Manual updates require annual dose entries versus time periods larger than 2 years. This is a significant amount of rework. Individuals assigned to CGS for example those with 25 years of service would require 25 line entries with 15 columns per entry. <I> **** Actions Taken **** Notified RP Supervision and PADs administrator
385315 | CR | 20181003 |  | 3 | NRC Observation |  |  |  | N | NO | <D> **** Detailed Description **** The resident noted a potential gap to Reg guide 1.114 in that there is no guidance to ensure operators performing clearance order checks while on watch do not lose sight of their fundamental duties of monitoring and responding to the plant. Operations should develop some guidance to ensure operators understand when clearance verifications are acceptable and what is required if they are requested to perform verifications while on watch outside those necessary to implement work or in response to emergent situations. <I> **** Actions Taken **** discussed issue with licensing and operations management. CR should be assigned to operations management. There are no safety concerns or vilolations associated with this issue.
385316 | CR | 20181003 |  | 3 | Potential Trend: Combustible Material Storage in Power Block |  |  |  | N | NO | <D> **** Detailed Description **** Current snapshot self-assessment of combustible material storage has identifed a potential trend in storage in the power block which is within our current processes but not reflective of industry best practices with regard to additional risks associated with storage under cable trays or near vital equipment. Walkdowns performed to support the self-assessment identified several approved storage areas which had combustibles within combustible limits but potential risks could be reduced or eliminated with additional protective measures (enclosed carts, job boxes, etc) or by relocating the storage area. There is no immediate threat to safe operation of any plant equipment. This CR is generated to roll all these issues into one CR to identify and implement any potential enhancements to Columbia's processes to reduce potential risks of combustible storage in the power block. <I> **** Actions Taken **** 1) Discussed with Performance Improvement and department CIC 2) Initiated CR
385318 | CR | 20181003 |  | 3 | Need Engineering Evaluation TSW insulation | N | N |  | N | NO | <D> **** Detailed Description **** Need Engineering evaluation to determine if install of insulation on new stainless steel TSW piping is necessary. Work order 0210 6125 is currently in place to replace TSW piping during R24, with directions to reinsulate (task 22) from the floor of the Heater Bay through the Steam Tunnel and down to el 471â€™ Reactor. Thermal Design Spec 15d.1 clearly states that before applying insulation to stainless steel piping and equipment it must be thoroughly scrubbed with detergent and rinsed twice. This presents an issue with remaining ALARA, as the Steam Tunnel has high dose fields that craft may be subjected to spending long amounts of time in while cleaning and then applying insulation. Also Thermal Design Spec 15d.1 clearly states that anti -sweat insulation (for this size piping) is to be 1â€ fiberglass, which has very little crush resistance even when used with a metal jacket. Under task 21 of this work order a boot style HELB seal (High Energy Line Break) is to be installed on the piping where it passes from the Steam Tunnel to the Steam Tunnel extension in the Heater Bay. The penetration seal installation detail shows the pipe to be insulated through the seal with the boot attached to the pipe with a stainless steel compression strap, which would crush the insulation, or (if left loose enough to not crush) possibly fail in the face of a HELB event. PPM 15.4.5 (Penetration Seal Installation and Maintenance) says that boot seals may be installed directly to penetrants less than or equal to 400 degrees and penetrants having insulation through boot seals may be sealed per pen seal detail 31 which calls for penetrants to have cal-sil insulation. (Which is resistant to crushing) In conclusion the Design Spec for insulation is in contradiction with the pen seal procedure for the type of pipe insulation. And if the Engineering evaluation determines that the insulation is not necessary then this argument is irrelevant and the pen seal installation detail just needs to be changed to reflect sealing the boot directly to the pipe. <I> **** Actions Taken **** Contacted plannerwith concerns who recommended creating CR for evaluation need, notified supervision <N> For answers regarding reinstallation of anti-sweat insulation on TSW system piping, see TER 96-0042-0 (a pdf copy is attached to the EDMS of this AR CR 385318). Although it provides allowance for permanent removal of original installation anti-sweat insulation from most TSW system piping, TER 96-0042-0 does direct re-installation of anti-sweat insulation on some TSW system piping. | 02-00-TSW-PIPE-MISC
385319 | CR | 20181003 | CAQ | D | DG1 ENG-1A1 Overspeed Lever difficult to reset | Y | N |  | N | NO | <D> **** Detailed Description **** During performance of PMT per WO 02119698-02 overspeed trip mechanisms for DG1 were tested per SOP-DG1-SHUTDOWN. The lever for the 1A1 engine was difficult to reset and lock in place, as compared to the 1A2 engine. <I> **** Actions Taken **** System engineer was contacted, he noted that this is a previously identified issue with these levers. CR written for tracking and trending. | 02-00-DG-ENG-1A1,02-00-DG-SV-1A1
385320 | CR | 20181003 | CAQ | D | Missing Storage PM Clause on newly received motor. CID 8639. |  |  |  | N | NO | <D> **** Detailed Description **** A Storekeeper displayed a good questioning attitude by bringing his concern that a newly received motor (CID 8639 PO 349962) has no receipt instructions regarding in storage requirements or a need for a SMS AR to evaluate requirements for storage. This is a 900 HP QL 1 motor that he believed would normally have clause 1.7.18 for storage maintenance . associated with the CID. <I> **** Actions Taken **** Expanded the team and notified his supervisor. Supervisor notified Procurement Engineering who addressed the issue and corrected the missing clause issue. Recommend trend only as identified issue was corrected. Excellent questioning attitude demonstrated by the Storekeeper. Good catch!
385322 | CR | 20181003 |  | 3 | New barrier wall between B-64 and PA Security fence |  |  |  | N | NO | <D> **** Detailed Description **** New barrier wall between B-64 and PA Security fence by the transformer yard creates an issue for warehouse to deliver materials to the B-26 delivery cage and credit card rack. Maintenance regularly requests materials be delivered to the B-26 cage to the west side of the deschutes. Also a substantial amount of materials are delivered by the warehouse to the Deschutes credit card delivery rack in the same area. The new barrier does not allow vehicle acces and causes the Storekeepers to park a long distance from the delivery point. This will be difficult to perform deliveries as outside conditions deteriorate due to weather and other obstacles. This could potentially expose the Storekeepers to additional hazards and roadblocks to safely performing there duties. Security also stated that parking next to the barrier is not acceptable. Nearest parking would require traversing over gravel thus making carts impractical. <I> **** Actions Taken **** Contacted facilities manager and discussed potential options including relocating the delivery point. No resolution was identified. Not sure who to assign the issue to for resolution. Security, Facilities or Industrial Safety. <N> Facilities has removed the "no parking anytime" sign near the new barrier and replaced with a loading/unloading sign so people can use the sidewalk to access B64 and B26 loading areas.
385326 | CR | 20181003 |  | 4 | GSB south exterior phone enclosure door latch is broken | N | N |  | N | YES | <D> **** Detailed Description **** The door latch is broken for the exterior telephone enclosure around the phone hanging on the south exterior outside face of the General Services Building (GSB). See the photo attached to the EDMS of this AR CR 385326. Please repair as necessary. | 02-00-GSB-BLDG-MISC
385327 | CR | 20181003 |  | 4 | No Voltage Condition | N | N |  | N | NO | <D> **** Detailed Description **** Work Order 02134236-15 installs a temp power connection for the TMU crew traile, to E-DISC-TMU/BB1. The 480V power source at the Bang board has a known phase that is inoperable .e. no voltage on â€œBâ€ phase. Temporary Power to the TMU trailer cannot be hooked up without the use of a portable generator. <I> **** Actions Taken **** Contacted Planning and Supervision | 02-00-M-BLDG-MISC
385328 | CR | 20181003 |  | 3 | UNABLE TO PROCESS AED CALCULATIONS |  |  |  | N | NO | <D> **** Detailed Description **** 10 AED CALCULATIONS WERE SUBMITTED TO DOCUMENT CONTROL TO BE PROCESSED. UNABLE TO PROCESS 7 OF THE 10 DUE TO ISSUES WITH THE ECâ€™S/CMRâ€™S. <I> **** Actions Taken **** ERRORS HAVE BEEN INDICATED AND RESPONSIBLE PERSONNEL WILL BE NOTIFIED TO MAKE CORRECTIONS.
385329 | CR | 20181003 |  | 4 | Camera 19 junction box is rusted out. | N | N |  | N | YES | <D> **** Detailed Description **** Upon access to the camera 19 juction for replacement of the camera, it was found that not only is the outside of the box rusty, but the interior is badly degraded as well and the bottom is covered with chunks of rusted material. The junction box needs to be replaced - see attached pictures in EDMS <I> **** Actions Taken **** Notified supervision, took pictures to document condition, initiated CR. | 02-00-SEC-CCTV-19
385330 | CR | 20181003 | CAQ | D | Document Control Received 5 procedures without AD | N | N |  | N | NO | <C> CR moved from Non-CAQ to CAQ by CAP Supervisor. <D> **** Detailed Description **** I received 5 procedures from Operations that were all major revisions that were reviewed, approved and submitted to Document Control without Applicability Determinations (AD) attached. <I> **** Actions Taken **** Notified Supervision and Operations Procedure Writer. All 5 procedures were sent back via the APPW system. <N> The AD screen and 5059SCREEN have been copied into the APPW document set. Individual has been coached on the use of HU tools to prevent repeat of error. Issue was discussed at D15 with workgroup. No further action required.
385331 | CR | 20181003 | CAQ | D | CAS back up radio is not operational | N | N |  | N | YES | <D> **** Detailed Description **** While conducting preventive maintenance on the CAS backup radio, testing revealed it is inoperable. The primary radio is functional and handheld radios can be used for backup if needed. <I> **** Actions Taken **** Notified Security and started troubleshooting. <N> **** Equipment Description **** CAS
385332 | CR | 20181003 |  | 4 | Clearance order with no closure mechanism |  |  |  | N | YES | <D> **** Detailed Description **** During review of clearance orders greater than one year old it was identified that the work order for addressing C -AS-V-37-004 had been cancelled to a diagnostic test on AS-PCV-1. Following maintenance and diagnostic testing under WO 02066867 the original issue is still occurring and the pressure control valve needs to be adjusted under load. CR and WR generated to perform tuning of the pressure control valve with the auxiliary steam system in service. <I> **** Actions Taken **** Notified operations, generated WR and CR | 02-00-AS-PCV-1
385333 | CR | 20181003 |  | 4 | Design error on EC17099-Radwaste Chiller Project | N | N |  | N | NO | <D> **** Detailed Description **** During installation of TSW piping to new, replacement Radwaste Chiller WCH-CR-51A, SSC noted that the flange on mating valve TSW-V-H18 is a 300# class valve when in fact the provided design per EC 17099, (ref CVI 216 -01,4250) indicates this flange to be a 150# class. This is a design error by the A/E. This condition does not affect any inservice equipment - the radwaste chiller WCH -CR-51A is out-of-service for replacement. <I> **** Actions Taken **** EN design engineering issued FCR EC0000017099R000G to correct this porblem. No further actxions required. <N> **** Equipment Description **** Radwaste Bldg elevation 507. | 02-00-TSW-V-H18,02-00-WCH-CR-51A
385334 | CR | 20181003 | CAQ | C | Update drawing to match field configuration | Y | N |  | N | YES | <D> **** Detailed Description **** CR 385264 identified expansion of scope on changing field wiring configurations to match design drawings. After review and discussion with engineering it was more appropriate to update the configuration drawings to match the plant configuration. This is an administrative issue only and has no impact on the design function of the components. This CR is being written to track update to the drawings since the original CR has been closed. See CR 385264 and WO 02106433 for additional information. <I> **** Actions Taken **** Created CR, Discussed with OCC and maintenance | 02-00-DG-RLY-DG1/VR1,02-00-DG-RLY-DG1/VR2
385336 | CR | 20181004 |  |  | CBD-V-1 minor packing leak |  |  |  | N | YES | <C> CR Canceled at the request of Maint. Supervisor. Duplicate CR 385338 was additional written to address the same issue. <D> Vavle CBD-V-1 has minor packing leak located at the steam. CBD-V-1 is located in next to the service water pump C. <I> CR | 02-00-CBD-V-1
385337 | CR | 20181004 |  | 4 | recommend confirmatory grease evaluation CW-MO-13B | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** As part of the external PM for CW-MO-13B representative grease samples of the valve main gear housing and motor pinion cavity are to be evaluated per section 7.16 of 10.25.4. Any grade of grease that is Grade 2 or higher should have a confirmatory evaluation performed. I have graded the grease samples as 2, based on the presence of contamination in the form of dirt/debris. Grease was drawn from the appropriate sample points and submitted to a plastic bag for evaluation. Craft identified a few flecks of debris from the main gear housing sample. Both samples share a common cavity and therefore I graded both samples as a 2. the elasticity of the grease is satisfactory. <I> **** Actions Taken **** Notified Supervisor, Notified CRS and write CR. a copy of the MOV grease evaluation sheet will be forwarded to engineer along with reference to this CR. <N> **** Equipment Description **** CWPH | 02-00-CW-MO-13B
385338 | CR | 20181004 |  | 4 | CBD-V-1 has packing leak | N | N |  | N | YES | <D> **** Detailed Description **** CBD-V-1 has a minor packing leak located at the steam. CBD-V-1 is located by CW pump C. <I> **** Actions Taken **** CR <N> **** Equipment Description **** CBD-V-1 | 02-00-CBD-V-1
385350 | CR | 20181004 |  | 4 | 3 Pieces of M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** 3 Pieces of M&TE were found OOT & NONE were used during Calibration cycles. Calcode #0053563 Arbiter Power System Analyzer- model 931A. Sent to Vendor for Repair. DEF #6755A written. Calcode #0065616 Industrial Scientific Gas Monitor- model iTX was Rejected- No Longer able to find replacement parts. DEF #6756A written. Calcode #0063550 Dresser Sensor- model HQS-2 15psia adjusted within specs. DEF #6758A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
385351 | CR | 20181004 | CAQ | C | E-B0-PBX batteries types installed don't match | N | Y |  | N | YES | <D> **** Detailed Description **** The battery E-B0-PBX consists of two parallel strings of cells. When they were replaced, the vendor inadvertently supplied 2 different types of batteries. One string consists of the manufactures newest cell type, these cells contain a catalyst. The other string contains cells that are of the older type which were accidentally delivered to CGS and installed. These do not contain the catalyst. The two types can by visually distinguished by the color of the caps on the battery cells. The new type of cell containing the catalyst has a dark grey cap, and the old type without the catalyst has a white cap. <I> **** Actions Taken **** The vendor for the batteries has been contacted and the difference between the two cell types has been determined. Currently in the process of communicating with the vendor to replace the non-catalyst cells (under warranty). <N> **** Equipment Description **** PAAP building | 02-00-E-B0-PBX
385352 | CR | 20181004 |  | 3 | Stairs in the plant considered ladders. |  |  |  | N | NO | <D> **** Detailed Description **** Additional stairs (actually classified as ladders) were identified in RW 437' and GSB (Service building) 422'. Recently these same type of stairs were marked with a placard for facing the steps when ascending/descending in the various Diesel Rooms (Upper HVAC areas). These additoinal stairs/ladders in the RW 437' and GSB 422' should be treated the same and marked for proper use. <I> **** Actions Taken **** Generated CR. Make an assignment to Mech shop for tracking generation of signs as recently done. Informed laborer lead as well for info. GSB 422' was disussed in mechanic shop D15 as info. | 02-00-GSB-BLDG-MISC,02-00-W-BLDG-MISC
385357 | CR | 20181004 |  | 3 | Unavailability Logging of DG-SYS-A outage. |  |  |  | N | NO | <D> **** Detailed Description **** Entries were completed to log DG-SYS-A unavailability however not all the panels were completed as required by PPM 1.5.11 and ESOMS Quick Guides (SOMS-LOGS-QR.pdf ). This information needs to be completed for the interface between eSOMS and Maintenance Rule programs to work properly. . Manual Configuration on the Equipment panel in eSOMS was not completed for DG-SYS-A for the following eSOM entries. Also the Attributes fields for Surv / LCO # and Work Order # was not completed. . 10/3/2018 7:20 AM - DG-1 verified in a standby lineup per SOP-DG1-STBY. DG1 is available and remains inoperable pending PMT. . This entry needs the same information place in the Attributes panel for Surv / LCO# and Work Order # fields as the eSOMS entry making the DG-SYS-A unavailable on 10/1/2018 @ 06:00. Surv / LCO # = TS-18-DG1 OUTAGE -001 and Work Order # = 02131310 . For the below entries need to add Manual Configuration and Surv / LCO # and Work Order #: . 10/3/2018 9:07 AM - DG-1 is unavailable per SOP-DG1-START to bar over the diesel, DG1 remains inoperable. . 10/3/2018 9:34 AM - DG-1 is available following bar over per SOP-SG1-START, DG1 remains inoperable. . 10/3/2018 10:49 PM â€“ DG1 is unavailable due to the hanging of D-DG1-INOP-005 for WO 02128136 task 2. . 10/4/2018 1:20 AM - DG1 is available after lifting of D -DG1-INOP-005 for WO 02128136. . 10/4/2018 2:52 AM - Declared DG-SYS A Operable
385359 | CR | 20181004 |  | 4 | OG-RF-20C D/P is low out of spec. | N | N |  | N | YES | <D> **** Detailed Description **** OG-RF-20C calculated D/P ( Oil pressure - suction pressure ) is 24 psid. The low spec per the OPS-2 logs is 30 psid. Please T/S repair as necessary. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** RW 452 | 02-00-OG-RF-20C
385360 | CR | 20181004 |  | 4 | MSP-SLC-B101 not identified in ADL for EC-PDC-12788 |  |  |  | N | NO | <D> **** Detailed Description **** CR-366573 identifies that the CAT ID for the 5 AMP fuses for SLC-V-4A/B needs to be corrected. The reason the CAT ID needed to be revised was the implementation of EC-PDC -12788 during R22. This CR is for trending that EC-PDC -12788 did not identify that a procedure revision was needed for MSP-SLC-B101. <I> **** Actions Taken **** Notified supervision and wrote CR. | 02-00-SLC-V-4A,02-00-SLC-V-4B
385362 | CR | 20181004 |  | 3 | House Keeping inspections WO 02125274-01 |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of wo 02125274-01 Several areas had issues with lights being out. I have attached pictures to the WO that can be looked up through EWP so lighting issues can be easily identified and corrected. Effected Areasâ€ Reactor 522 (2 light fixtures out) DG-3 (3 light fixtures out) Service Water Pump A (3 lights out). Reference attached pictures in EWP for better lighting identification. <I> **** Actions Taken **** Cr written. Effected Area supervisors notified of lighting issues. | 02-00-A-BLDG-MISC,02-00-D-BLDG-MISC,02-00-R-BLDG-MISC
385365 | CR | 20181004 |  | 4 | Offgas Glycol temperature high alarm alarms several times a | N | N |  | N | YES | <D> **** Detailed Description **** Offgas Glycol temperature high alarm alarms several times a shift. GY-TRS-630 indicates around 38Â°F continously. This is causing 4.672.A9 to alarm several times a shift and is a distraction. This is with 2 functioning Offgas refirigerant machines. Suspect that GY-TE-14 or GY-TT-600 may need calibration. The local temperatures taken at GY -TIC-17 reflect that the glycol are usually around 32-34Â°F as expected. GY-TIC-17 is fed from GY-TE-13. GY-TE-13 and 14 both measure glycol temperature at the combined suction of the glycol pumps. Additionally GY-TI-18 could be referenced as a cross check as well as local piping temperature to verify that the indication and bothersome alarms from GY-TRS-630 are invalid. Please investigate and correct the temperature issue. <I> **** Actions Taken **** Wrote this CR to seek resoloution of this annoyance. | 02-00-GY-TE-14
385366 | CR | 20181004 |  | 4 | Degraded signs near the CGS warehouse complex |  |  |  | N | YES | <D> **** Detailed Description **** See the photos attached to the EDMS of this AR CR 385366. There are two degraded exterior signs near the access road to the CGS warehouse complex (north east of the Protected Area). One intending to point the way to 'COLUMBIA GENERATING STATION WAREHOUSE COMPLEX RECEIVING' and one indicating 'NO CRAFT PARKING IN THIS AREA'. Please investigate and address as necessary. <N> **** Equipment Description **** Near the CGS warehouse complex - see photos attached to AR CR EDMS.
385369 | CR | 20181004 | CAQ | C | Procedure sent to Document Control missing AD; wrong signer |  |  |  | N | NO | <D> **** Detailed Description **** I recieved SWP-FFD-01 to process through the APPW process that had been reviewed, approved and submitted to Document Control. It was missing the Applicability Determination (AD) and was signed by someone other than the CNO which is needed for major revisions. <I> **** Actions Taken **** Informed supervision, sent back the procedure for more information with this CR # attached.
385372 | CR | 20181004 | CAQ | C | eSOMS late entries for Maintenance |  |  |  | N | NO | <D> **** Detailed Description **** Two Maintenance Supervisors and one maintenance craft person worked outside their scheduled eSOMS hours without updating eSOMS. The errors were discovered during a weekly eSOMS audit. No violations occured when the additional hours were added. <I> **** Actions Taken **** Updated eSOMS with the correct hours. Notified manager and supervisors of the errors.
385373 | CR | 20181004 |  | 4 | PWC-P-7 | N | N |  | Y | YES | <D> **** Detailed Description **** PWC-P-7 Has chemical deposits on the pump head and pump base. Which indicates a small leak All leakage is inside the pump base. Pump head bolts also show corrosion damage <I> **** Actions Taken **** Informed Chem Sup. and informed CRS. <N> **** Equipment Description **** blgd. #33 | 02-00-PWC-P-7
385374 | CR | 20181004 |  | 3 | Procedure 11.2.8.2 needs revision |  |  |  | N | NO | <D> **** Detailed Description **** Procedure 11.2.8.2, Radiation Work Permit Preparation and Use, has references to "High radiation material transfer plan" and references HPI 12-64 which is an in-active HPI. <I> **** Actions Taken **** Discussed with Rad Support Supervisor & initiated this CR
385375 | CR | 20181004 |  | 3 | Review PPM 11.2.14.4 Source Working Life |  |  |  | N | NO | <D> **** Detailed Description **** A review of PPM 11.2.14.4.6.11 needs to be performed relating to Source Working Life. The process now does not give the owners of sources any advance notice that their sources â€œworking lifeâ€ is about to be exceeded, giving them time to purchase a new source, prepare to dispose of the source, or having the working life extended by the Radiation Protection Source Program Owner (RPSPO). <I> **** Actions Taken **** Discussed with the Radiation Protection Source Program Owner Discussed with RP Supervision
385381 | CR | 20181004 |  | 3 | (QA) Unrestricted Internal Access to Cyber Document | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) An electronic cyber security related document marked â€œWithhold from Public Disclosure in accordance with 10 CFR 2.390â€ was found on the Energy Northwest (EN) internal SharePoint site, contrary to SWP-SEC-11 â€œProtection of Sensitive But Unclassified Informationâ€. This document has been stored there since at least August 2018, but there are no known consequences according to the Cyber Security Program owner. Factual Basis: â€¢ SWP-SEC-11 step 4.7.1 states, â€œâ€˜Withholdâ€™ from Public Disclosure in Accordance with 10 CFR 2.390â€™" or OUO information should not be disseminated in any manner - orally, visually, or electronically - to unauthorized personnel.â€™â€ â€¢ SWP-SEC-11 step 4.7.2 states, â€œAccess to â€˜Withhold from Public Disclosure in Accordance with 10 CFR 2.390â€™ or OUO information is based on â€˜need-to-knowâ€™. â€˜Need-to-knowâ€™ is the determination made by an authorized holder of this type of information that a prospective recipient requires access to specific information in order to perform or assist in an authorized function as a condition of employment i.e., access is required for the performance of official duties.â€ â€¢ On 10/4/18, an electronic cyber security related document marked â€œWithhold from Public Disclosure in accordance with 10 CFR 2.390â€ was found on the Energy Northwest SharePoint site without restrictions to access to employees. Insights: â€¢ The Cyber Security Program owner has a quarterly assignment for that the particular SharePoint site to ensure it remains restricted to only those with a â€œneed -to-knowâ€ and this is verified quarterly, but the access restrictions at some point during the quarter changed to inherit permissions of the site level giving users read access. â€¢ Immediately upon notification by Quality, the Cyber Security Program owner ensured access restrictions were placed on that SharePoint site, and Quality verified restrictions are in place. â€¢ SharePoint permission changes are not tracked in a manner in which they can be investigated for a â€œwhoâ€ and â€œwhenâ€. â€¢ Permission granting abilities were changed to only Cyber Program Manager and Cyber IT Lead. . <I> **** Actions Taken **** Notified the Cyber Security Program owner. . This is a Deficiency identified during the planning of the upcoming Cyber Security aduit AU-CSQ-18. . Recommend routing to ITMGMT. <N> Validated current access is as expected with only those approved personnel having access. Provided coaching to individuals with access to change permissions to site.
385382 | CR | 20181004 |  | 3 | ILC quarterly PI change from Green to Yellow |  |  |  | N | NO | <D> **** Detailed Description **** ILC quarterly PI changed from Green to Yellow due to written exam student pass rate < 95%. There have been four failures this quarter out of 42 exams provided. Recommend cat 3 assigned to operations training. <I> **** Actions Taken **** Reviewed the PI and initiated this CR. Informed Ops management, training management.
385383 | CR | 20181004 |  | 4 | SW1A bkr point (X320-12) no longer be working in eDNA | N | N |  | N | NO | <D> **** Detailed Description **** While monitoring and trending the service water system, it was noted that eDNA point X320-12 for the SW BKR SW1A Position appears to no longer be working. When comparing breaker position with SW Loop A return flow (eDNA point X451) the SW1A breaker position point stopped working properly on 9/13/2018. <I> **** Actions Taken **** discussed SM and supervisor
385384 | CR | 20181004 |  | 3 | Recommend enhancement to SOP-RWCU-DEMIN |  |  |  | N | NO | <D> **** Detailed Description **** Recommend enhancement to SOP-RWCU-DEMIN precaution and limitation 4.9. Per reactor engineering the reference to RWC-V-44 or RWCU-V-104 should be made conditional. The following should be added to the precaution; IF RWCU-V-44 or RWCU-V-104 are open then verify a substitute value of 0.08MLB/HR entered in the Plant Process Computer. This change should also be made to the CAUTIONS on pages 8, 9, 12, 53, and 57. Contact the author of this CR and/or reactor engineering with any questions. | 02-00-RWCU-V-104,02-00-RWCU-V-44
385385 | CR | 20181004 |  | 3 | Unavailable required to be recorded for ISP-MS-Q923 & Q918 |  |  |  | N | NO | <D> **** Detailed Description **** Subject: Unavailable required to be recorded for ISP-MS -Q923 for ASD-SYS-A Review if Unavailable is required to be recorded for ISP -MS-Q923 for ASD-SYS-A (MS-LIS-38A) and related surveillances (ISP-MS-Q918) per PPM 1.5.11. If required update procedure with steps for logging the unavailability in eSOMS per PPM 1.5.11. . Recommend that the CR be assigned to Maintenance Procedures group.
385387 | CR | 20181004 | CAQ | C | Cameron CIB 138 LEFM CheckPlus Coherent SNR Uncertainty | N | Y |  | N | YES | <D> **** Detailed Description **** Cameron (the LEFM OEM) has issued Customer Information Bulletin 138 R1 (CIB138R01 attached in EDMS) on the LEFM impact of coherent noise. The CIB discusses the treatment of coherent noise by the system and recommends action based on certain criteria. There is no immediate impact on the feedwater flow measurement performed by LEFM due to the issue described in the CIB and hence no core thermal power measurement impact. This CR is being initiated to drive actions to capture additional LEFM data for review by Cameron and to address any possible long term concerns arising from this CIB. Background: Coherent noise is signal noise that is of the same frequency as the transducer pulse that is used for LEFMâ€™s ultrasonic measurement. Coherent noise can at times be indistinguishable from the transducer pulse (and hence of greater system impact) because it cannot be averaged out over multiple samples. Our plantâ€™s LEFM uncertainty analysis (Cameron report ER -1049 Rev. 3. - documented in CVI DCR 1215-00,2) treats the effect of coherent noise across the two feedwater loops randomly and not systematically. Under certain conditions this treatment may not be valid. Specifically, when coherent signal-to-noise ratios are less than 100:1, according to the CIB, the LEFM system would require reevaluation (i.e. under these conditions the effect of coherent noise across the two feedwater loops should be treated systematically). We consulted the LEFM vendor on 10/4/2018. The last time coherent signal-to-noise ratios were measured was during R23 (WO 02077892-01) and the results were discussed with the vendor. The vendor clarified that since Columbiaâ€™s average coherent signal-to-noise ratio is above 100:1, the recommendation of the CIB is not applicable (due to current performance) and reevaluation of the system is not required. <I> **** Actions Taken **** Discussed with supervisor, SM | 02-00-RFW-CAB-FE3/FE4
385388 | CR | 20181005 |  | 4 | Security PTZ35 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security PTZ35 not functioning as designed. Contact security @ 2185 <I> **** Actions Taken **** contact security @ 2185 | 02-00-SEC-CCTV-35
385397 | CR | 20181005 | CAQ | C | PPM 15.1.26 Procedure Requires Revision |  |  |  | N | NO | <D> **** Detailed Description **** During review of PPM 15.1.26 FP-P-110 Loss of Power Test, it was identified that the procedure did not include steps to reset control circuitry. The reset control circuitry steps from SOP-FP-STBY should be implemented in this procedure. These steps have already been added to PPM 15.1.4 FP-P-110 Operability Test. This will help prevent any unexpected AUTO starts of the pump and ensure it is in a proper available standby lineup following testing. <I> **** Actions Taken **** SM/CRS informed, verified margin still exists until the late date of this PM. A marked up reccomendation for the procedure change has been attached to this CR. Reccomend replacing step 7.35 of the procedure as shown in the attached marked up copy of PPM 15.1.26. | 02-00-FP-P-110
385401 | CR | 20181005 |  | 3 | Maintenance Technical Fundamentals |  |  |  | N | NO | <D> **** Detailed Description **** Maintenance Technical Fundamentals are not fully integrated into the day to day activities of performing maintenance on the plant. The lists that are being used by the shops are incomplete and need to be updated to be shop specific and include the full lists of technical skills as outlined in 18-003. This AR will be used to document the actions necessary to ensure technical skills are reinforced positively and gaps identified. <I> **** Actions Taken **** No immediate actions required
385407 | CR | 20181005 |  | 4 | TB east double door (T-114) does not close all the way. | N | N |  | N | YES | <D> **** Detailed Description **** When shutting the door (T-114) from the distance required to enter and exit the doors do not completely seat properly. The top edge comes in contact with the adjacent door's edge. Due to the weight of the door it appears that a metal bracket is riveted along the doors edge to assist in maintaining the door's position. Some of the rivets near the top are loose. <I> **** Actions Taken **** Informed CRS Non-essential fire door. <N> **** Equipment Description **** Turbine Building hallway 441' East side at the double door. . Duplicate of existing AR CR 385047 / WR 29144803. | 02-00-T-DOOR-T114
385408 | CR | 20181005 |  | 3 | Lost badge T501 during work on FP-HS-CO2/1 hydro hose test |  |  |  | N | NO | <D> **** Detailed Description **** During work on T501 02125413-01 hydro hose test, mechanic noticed that his lanyard pulled off his neck during handling of hoses, found all items on lanyard except for badge. Supervisor went to check on job and mechanic informed him that he lost his badge. <I> **** Actions Taken **** Supervisor escorted mechanic to security, 1 electrician and 2 mechanics looking on T501, T471 & T441 Informed WWM, Maintenance Management, & Operations, <N> **** Equipment Description **** T501 Subject line (FS to FP) changed to match the correct system being worked on; as cross-referenced in the WO/WP (requested by OPS).
385412 | CR | 20181005 | CAQ | C | WA State EOC that dialup line was not working | N | Y |  | N | NO | <D> **** Detailed Description **** SCC was notified by WA State EOC that dialup line was not working. SCC attempted to call back on dialup line, but could not connect. Telephone analyst will attempt to contact EOC and open a ticket with the service provider. The Crash and alternate contact number remain operational.
385415 | CR | 20181005 | CAQ | D | WMA-AD-54A1 | Y | N |  | N | YES | <D> **** Detailed Description **** the air damper failed to indicate closed during restoration from OSP-WMA-M701.upon investigation, the damper was found in the closed position, but the linkage from the output shaft was misaligned slightly and not fully engaging the closed limit switch. <I> **** Actions Taken **** wiggled the limit switch arm and it popped into place on the output shaft arm and verified correct indication with the MCR -informed MCR -initiated CR/WR | 02-00-WMA-AD-51A1
385416 | CR | 20181005 | CAQ | D | MS-LIS-100A equalizing vlv leakage | Y | N |  | N | YES | <C> CR reopened to cross reference additional WR 29146873 then taken back to complete <D> **** Detailed Description **** during operator rounds it was noted that there was leakage coming from the equalizing valve (approx 5 dpm). the valve is #24 on E-IR-H22/P004. <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-E-IR-P004,02-00-IR-V-H22P004/V24,02-00-MS-LIS-100A
385418 | CR | 20181005 |  | 3 | RWCU-DPIS-88B drawing does not match in field configuration | N | N |  | N | YES | <D> **** Detailed Description **** A new valve was installed on the HP drain line on RWCU -DPIS-88B per 02134807-01, While filling out the weld record noticed that Weld Record/drawing did not match in field configuration. <I> **** Actions Taken **** Walk down by maintenance and operations verified in field configuration is correct and drawing 220-01, 1890.5 needs to be revised to match in field configuration. Notified Shift Mgr, Maintenance management and WWM <N> **** Equipment Description **** RW467 R3/11.3 CR Edited in I Notes to reflect correct wording (request of OPS) | 02-00-RWCU-DPIS-88B
385419 | CR | 20181005 |  | 4 | MS-TE-65A1 reading erratic | N | N |  | N | YES | <D> **** Detailed Description **** Computer point T085, MSR 1A/LP-1A XOVER, was noticed to be trending up approximatley 200F over the last 9 days. After evaluation of other parameters it appears to be an erratic instrument. <I> **** Actions Taken **** T085, T086 and T087 were evaluated and compared. The elements are not on the same line but come from the same MSR. Only T085 was changing. Pressure indication on the three lines, points T016, T013 and T011, were all steady. CRS informed. <N> **** Equipment Description **** MS-TE-65A1 | 02-00-MS-TE-65A1
385420 | CR | 20181005 |  | 3 | PPM 1.3.50 requires updating |  |  |  | N | NO | <D> **** Detailed Description **** Attachment 7.1 "Operator Aid Index" needs updating. #15-003 Effluent Monitor Classifications has been most recently superseded by #18-001
385421 | CR | 20181005 |  | 4 | Generator Condition Monitor out of paper | N | N |  | N | YES | <D> **** Detailed Description **** The Generator Condition Monitor (TG-ID-1) chart recorder is out of paper--please replace. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 471 W | 02-00-TG-ID-1
385422 | CR | 20181006 | CAQ | D | DSA-SPV-5A2/4 retaining clip for nameplate is missing (DG1) | Y | N |  | N | YES | <D> **** Detailed Description **** The retaining clip for the metal nameplate on DSA-SPV-5A2/4 (starting air motor SPV) is missing. The nameplate was placed back on the SPV, but the retaining clip could not be located. See attached EDMS doc for pic of DSA-SPV-5A2/4 and a picture of an identical SPV, which has its retaining clip. The nameplate/retaining clip do not serve a functional purpose; the lack of clip does not affect SPV operation. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** DG1 room | 02-00-DSA-SPV-5A2/4
385423 | CR | 20181006 |  | 3 | Operator Aid audit discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** An audit of the Operator Aids, per PPM 1.3.50, revealed several discrepancies. Operator Aids 01-001, 01-003, and 11-001 could not be located on the refuel bridge, as designated in the Operator Aid Index. AR 347508, AR 356124, 363679 have all been written to identify this issue during past Operator Aid audits. Furthermore, Operator Aids are not being governed in alignment with PPM 1.3.50. All of the operator aids currently in the field have been in place for GT 2 years. 2 of the 4, in field aids, have been in place for GT 20 years. These aids should be converted into Permanent Operator Aids so that they no longer fall under the PPM 1.3.50 umbrella of governance. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** PPM 1.3.50
385425 | CR | 20181006 |  | 4 | WCH-CR-51A supports RDV-S-7 & 8 installed at wrong location. | N | N |  | N | NO | <D> **** Detailed Description **** WCH-CR-51A Relief valve piping supports RDV-S-7 & 8 installed 2â€™ south of specified location on drawing. This was due to a mathematical error during to lay-out phase. The workers forgot to subtract the dimension from the overall piping length to account for the section of pipe that was past the column line. This made the dimension 2â€™ too long when transferred to the floor, moving the supports south. As a result of this error, the work group was required to add 2 extra 3â€ welds and 4â€™ of pipe. . <I> **** Actions Taken **** Project Mgmt was contacted as well as the project engineer. The new location was evaluated and found to be acceptable and within tolerance of the stress calculations. An FCR was generated. <N> **** Equipment Description **** WCH-CR-51A | 02-00-WCH-CR-51A,02-00-WCH-RV-1A
385426 | CR | 20181006 |  | 4 | Received ASD/A input transformer trouble alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received ASD/A input transformer trouble alarm 4.602.A6 drop 3-4. Alarm came in and cleared 2 times in rapid succession. All RRC-P-1A indications are normal for current plant conditions. Field Operator reported no abnormal indications found locally. <I> **** Actions Taken **** Followed ARP and informed CRS. Generated new WR as other WRs for this issue appear to be at complete. <N> **** Equipment Description **** ASD/A input transformer located by the ASD building. | 02-00-RRC-RLY-K10A,02-00-RRC-TR-ASD/A/1
385427 | CR | 20181006 |  | 4 | Additional fab required for Radwaste Chiller R/V hangers | N | N |  | N | NO | <D> **** Detailed Description **** During installation of the new Radwaste chiller 3â€ relief valve line and hangers, per WO 02125913-10, it was determined that additional fabrication efforts are required for new supports SN-17099-1 and SN-17099-2, then originally planned. This condition does not affect any plant equipment other than WCH-CR-51A, which is currently out-of-service for replacement. <I> **** Actions Taken **** Contacted the Planner whom revised the work instructions of WO 02125913-10 to reflect the correct design per EC 17099. <N> **** Equipment Description **** Radwaste Building elevation 507' Williams Plant Services. | 02-00-WCH-CR-51A,02-00-WCH-RV-1A
385428 | CR | 20181007 |  | 3 | New Hot Spot (HS-83) detected during RX 522' Monthly Survey |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of the RX Building 522' Monthly Survey, a new Hot Spot (HS-83) was discovered on the 2" Scram Volume Discharge piping. The hot spot is located on the underside of the piping near the weld that joins the bottom drain of SVD-TK-1B to the "T", which is connected to CRD-V-11. The "T" connects the bottom drain of SVD-TK-1B, CRD-V-11, and the common drain line leading to SVD-TK-1A. The dose rate on HS-83, taken with a teletector, is *700 mrem/hr on contact, 55 mrem/hr @ 30cm. The nearest Radiation Area boundary is 2.5 mrem/hr. <I> **** Actions Taken **** Created HS-83 in the Hot Spot Log, documented survey #VSDS Prod-M-20181004-9, initiated this AR/CR, attached HS-83 to the piping, took pictures and sent them to ALARA and RP Supervision. | 02-00-CRD-TK-SDIV1A,02-00-CRD-TK-SDIV1B,02-00-CRD-V-11,02-00-R-BLDG-MISC
385429 | CR | 20181007 |  | 3 | Evaluate add of reflective edge marks on cool. twr roads |  |  |  | N | NO | <D> **** Detailed Description **** Please evaluate the use of reflective paint to mark the edge of the roads in the cooling tower areas, along with reflective tape for any obstructions. The cooling tower area at night is very dark due to few lights. This, along with the drift that comes to the ground from the towers in winter, makes it very difficult to see road edges and obstructions. Reflective paint ould help this immensely. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** Cooling Tower Area
385430 | CR | 20181007 |  | 4 | TOA-AW-2B suction strainer rusted through and broken | N | N |  | N | YES | <D> **** Detailed Description **** TOA-AW-2B pump suction strainer screens are corroded and rusted through. Recommend investigate and repair/replace as necessary. <I> **** Actions Taken **** Informed MCR, generataed AR/WR. | 02-00-TOA-AW-2B,02-00-TOA-P-2B1,02-00-TOA-P-2B2
385434 | CR | 20181007 |  | 4 | TEA-FN-1A Squeaky | N | N |  | N | YES | <D> **** Detailed Description **** TEA-FN-1A is a bit sqeaky, and could probably do with some lubricating. <I> **** Actions Taken **** Informed MCR | 02-00-TEA-FN-1A
385435 | CR | 20181007 |  | 4 | RWCU-PS-94B found out of Cal. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing WO# 02074172-01 RWCU-PS-94B was found out of calibration low. <I> **** Actions Taken **** Calibrated RWCU-PS-94B per IMDS. Wrote CR for trending purposes. <N> **** Equipment Description **** RW 467 | 02-00-RWCU-PS-94B
385436 | CR | 20181007 |  | 3 | ISP-CRD-Q406 requires scaffolding |  |  |  | N | YES | <D> **** Detailed Description **** During walk down of surveillance ISP-CRD-Q406 (02113318) determined that surveillance could not be done safely without scaffolding <I> **** Actions Taken **** notified WWM, I&C management, operations and maintenance management <N> **** Equipment Description **** RX522 | 02-00-CRD-LT-13A
385437 | CR | 20181007 | CAQ | D | SW-FI-41 Failed Low | Y | Y |  | N | YES | <D> **** Detailed Description **** SW-FI-41 has failed low and the ultra sonic flow transmitter for this piping has also failed. OPS 2 reported 25 gpm on the ultra sonic flow transmitter before the transmitter failed. Reference WO 02113373 which is at plan to clean the instrument lines for SW-FI-41. <I> **** Actions Taken **** NDE called out to fix the transmitter, CR to document. | 02-00-RRA-CC-12,02-00-SW-FI-41
385438 | CR | 20181007 | CAQ | D | manhole ES1 | N | N |  | N | YES | <D> **** Detailed Description **** Manhole ES01 is not functioning as designed. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** initiated compensatory measures, security notification made. | 02-00-SEC-TAS-ES01T
385439 | CR | 20181007 | CAQ | C | Incorrect settings on ultrasonic flow meter for RRA-CC-12 | Y | N |  | N | YES | <D> **** Detailed Description **** In response to failure of the ultrasonic flow meter for RRA-CC-12 (CR 385437) it was identified that there were two issues. The first issue was that the setting for outside diameter was set to 2.37" (corresponds to 2" pipe) vice 1.90" (corresponds to 1.5" pipe). The second issue was that the medium used to couple the transducers was found to be dry and not adequate. When a new layer of medium was applied to the transducers a good signal was received. <I> **** Actions Taken **** Outside diameter settings were adjusted to the correct value for 1.5" pipe and a new layer of medium was applied to the transducers. SM/CRS notified of the discrepancies. | 02-00-RRA-CC-12,02-00-SW-FI-41
385447 | CR | 20181008 |  | 4 | AUTODESK DWG TrueView closes unexpectedly |  |  |  | N | NO | <D> **** Detailed Description **** The Portal J / Asset Suite image for AED MEC M546-2 is a .dwg file. On my PC, this file gets opened with AUTODESK DWG TrueView 2014. Once opened, I can view the drawing but if I try do anything else (e.g, pan around the drawing or plot/print the drawing), the program crashes/closes with a message indicating "Error Report - Required Value Missing" "An Autodesk product failed to send the required value for UP¦TOKEN." "The error report sent to Autodesk may be incomplete." "OK". When the "OK" button is pressed, a "DWG TrueView Error Report" is recieved which indicates "A software problem has caused DWG TrueView to close unexpectedly." "We applogize fro the inconvenience. An error report has been generated. Please click Send Report to help us analyze ...". This is adversely affected productivity and needs to be fixed. Screen snips are attached to the EDMS of this AR CR 385447. <N> I reached out to the user and uninstalled Trueview 2014 and installed Trueview 2018 which resolved the issue. No further actions required.
385448 | CR | 20181008 | CAQ | D | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0064151-81 F&J Rotometer- mdoel RMA-25 found OOT. Replacement gauge will be ordered- then will be Re- Calibrated. Chem Lab Eval: Not used in the OOT range negative pressure. This Rotometer was never used below -8inhg. DEF #6757A written. No Action Required, <I> **** Actions Taken **** None Trending purposes only.
385449 | CR | 20181008 |  | 3 | Corp Backup Server TSMSRV crashed | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Corporate TSM tape backup server TSMSRV crashed ~10pm Sunday. Alerts and notifications were via e'mail to domain admins and text alert sent to ISDO. <I> **** Actions Taken **** Recovery efforts began ~5am Monday. Unable to connect or ping the server. Physical investigation at alt datacenter showed server was in error state and powered down. Analyst powered up the server and after an extensive Power On Self Test, booted up without issue by 6am. Recommend NON-CAQ 3, with follow-up assignments to open case with IBM and setup alert e'mail forwarding to TSM analyst. <N> **** Equipment Description **** Corp server equipment. No EPN.
385454 | CR | 20181008 |  | 3 | 5.5.12 Procedure Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** For the purpose of attempting to open MSIVâ€™s faster add the option of installing the 5.5.6 keys (MS-RMS-S84 and MS -RMS-S85) to step 4.2.4. Note that all isolations should be isolated eventually; the 5.5.6 keys may help the operating crew begin depressurization faster. | 02-00-MS-RMS-S84,02-00-MS-RMS-S85
385456 | CR | 20181008 |  | 4 | RRC-VD-R673 dificult to read. | N | N |  | N | YES | <D> **** Detailed Description **** RRC-VD-R673 was replaced on 06-28-18. Since then the screen has been "white washed" and dificult to read. Trouble alarms are in white letters and are not visible. This impacts out ability to monitor and respond to abnormal conditions in the RRC system. <I> **** Actions Taken **** Found that the screen looks normal from the floor level. Still unable to read from that distance. | 02-00-RRC-VD-R673
385457 | CR | 20181008 | CAQ | D | No risk of hardware advisory for SCS |  |  |  | N | YES | <D> **** Detailed Description **** On 9/24/2018, SCS (Security Computer System) system engineer received a vendor notice indicating a possible hardware/software impact on time-keeping devices with GPS antennas. After verifying with vendor support against our specific configuration, our equipment is not at risk of impact. Vendor email and vendor bulletin included in EDMS. There is no equipment operability impact. Recommend cat. D for trending. <I> **** Actions Taken **** Contacted vendor, wrote CR. <N> **** Equipment Description **** Central Alarm Station | 02-00-SEC-TCS-1
385464 | CR | 20181008 | CAQ | D | SAS video controller | N | N |  | N | YES | <D> **** Detailed Description **** The video controller for WS 1 in SAS needs maintenance. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Security notification made, CR/WR generated <N> **** Equipment Description **** Main Control Room
385465 | CR | 20181008 | CAQ | C | DEH-SV-TRIP/C cycle time greater than AED CAL E/I-02-07-03 | N | Y |  | N | YES | <D> **** Detailed Description **** During the weekly Quadvoter valve surveillance conducted 05Oct2018 in accordance with PPI PPM OSP-MT-W701, the first stroke of DEH-SV-TIRP/C performed in Section 7.1.9 was recorded by Operations at 0.770sec (or 770ms). This cycle time is greater than described in AED CAL E/I-02-07-03 to mitigate a 120% overspeed event. The calculation assumes a nominal Quadvoter valve cycle time (220ms) plus additional margin allowed (497ms) for a total allowable time of 717ms. . Subsequent valve cycles as prescribed by Section 7.1.10 demonstrated two consecutive satisfactory stoke times of 360ms and 320ms. There has been an upward trend over the past month; previous test results were: 590ms/320ms/320ms on 28Sept2018, 590ms/320ms/320ms on 21Sept2018, 360ms on 14Sept2018, and 320ms on 07Sept2018. . [Reference: AR 217890 documented that AED CAL E/I-02-07-03 evaluated the various accident scenarios and determined that the maximum allowable turbine speed of 2160 rpm, (120% of rate speed) would not occur with a 220 milliseconds solenoid valve stroke time. The calculation further defined the margin to 120% speed as 497 milliseconds. This demonstrates that the solenoid valve stroke time could be 717 milliseconds without exceeding the 120% limit on turbine speed.] . At 770ms, this channel of the Quadvoter would not have TRIPPED the Main Turbine within the allowable time as defined by the calculation. However, the other channel of the Quadvoter demonstrated it would have TRIPPED the Main Turbine at less than half the allowable time necessary. . The pilot valve was previously replaced in Jan2018 due to slow cycle times in WO 02119703. The entire solenoid valve assembly is scoped to be replaced in R24 under PMRQ 24019-02 by WO 02112565. A WR will be auto-generated to replace the pilot valve online in order to restore normal cycle times and ensure the channel retains full functionality. <I> **** Actions Taken **** informed supervisor Referenced last occurence calc was exceed which was documented in CR AR 362820 <N> **** Equipment Description **** Quadvoter, third valve from the top, TG501 near 'TV/4 | 02-00-DEH-SV-TRIP/C
385469 | CR | 20181008 |  | 3 | False temperatue changes in eDNA plant computer signals | N | N |  | N | YES | <D> **** Detailed Description **** During system trending and monitoring, fluctuating temperatures were noted on MSR drain tanks. Further review showed that many BOP plant computer signals had the same reaction. These include MS line temps, MSR drain temps, heater shell drain temps, heater inlet/outlet temps, bypass valve tailpipe temp, and other signals (see EDMS plots). Pressures do not correspond to these temperature changes. This appears to be a plant computer issue. Similar to issue identified in CR 384331, but different points (See relevant cross-references). Recommend action to computer engineering. <I> **** Actions Taken **** Reviewed eDNA data. Consulted other system engineers. Consulted plant computer SME. Reviewed CR history. <N> **** Equipment Description **** Plant Process Computer
385471 | CR | 20181008 |  | 3 | SCW-V-513 copper results | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** SCW-V-513 comes off the stator coils outlet. The September 2018 copper samples showed elevated results. 6.6 ppb. Normal range is </=20 ppb but the reuslts trend around 1-2 ppb .There is no action level for this diagnostic parameter .The results were received on 10/8/18 and copper samples were retaken on 10/1/18. They are currently at the Environmental Services lab awaiting analysis. <I> **** Actions Taken **** Notified CRS, Chemistry Supervision / Managment, and system chemistry specialist. | 02-00-E-GEN-1,02-00-SCW-TK-1,02-00-SCW-V-513
385476 | CR | 20181008 | CAQ | D | DG5 failed to start | N | Y |  | N | YES | <D> **** Detailed Description **** During the performance of SOP-FLEX-GEN-DG5PM, when step 5.2.3 was performed the engine failed to start and a ENGINE SPEED SENSOR ERATIC OR LOSS ALLARM was received. There was no evidence the engine attempted to turn over <I> **** Actions Taken **** cr <N> **** Equipment Description **** bldg 600 | 02-CM-FLEX-GEN-DG5
385477 | CR | 20181008 |  | 3 | Procedure enhancement needed for ESP-BO1A-F101. |  |  |  | N | NO | <D> **** Detailed Description **** Enhancement needed for ESP-B01A-F101. the end of the procedure requires the battery to be placed on equalize charge after the completion of the discharge test. The data sheet also required a float charge after battery has been on equalize. Additionally, the surveillance requires a sign-off by the system engineer prior to closing out the surveillance. These steps make it difficuslt to close out the surveillance and the associated work order. <I> **** Actions Taken **** Generated CR to document needed actions. Contacted Electrical Component Manager. | 02-00-E-B0-1A
385479 | CR | 20181008 |  | 3 | GT 5 CMR's against E/I-02-95-01 |  |  |  | N | NO | <D> **** Detailed Description **** Issued per DES-4-1 to track incorporation of CMR's Assign to Design Basis Group (Vadoli) <I> **** Actions Taken **** n/a
385480 | CR | 20181008 |  | 3 | GT 5 CMR's against E/I-02-87-07 |  |  |  | N | NO | <D> **** Detailed Description **** Issued per DES-4-1 to track incorporation of outstanding CMR's. Assign to Design Basis Group (Vadoli) <I> **** Actions Taken **** n/a
385481 | CR | 20181008 |  | 4 | PAAP Vehicle Kiosk Inoperable |  |  |  | N | NO | <D> **** Detailed Description **** Craft reserved vehicle in advance. When arriving at kiosk it was found to have a white screen and unable to check out vehichles . Craft called both phone numbers that were posted on the kiok and was able to get assistance with a remote check out process. After several attempts to check the keys back in and calling both phone numbers, craft and Supervisor determined that they would keep the keys secure over night. <I> **** Actions Taken **** craft notified supervision and looked to him for decision. keys were secured over night. CR initiated <N> **** Equipment Description **** PAAP Kiosk Pool Vihicle Kiosk
385482 | CR | 20181008 |  | 4 | TMU-RLY-62/P1A As found time out of tolerance | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing relay calibrations under WO#02084457-01 TMU-RLY-62/P1A had an asfound time that was out of tolerance. Time dial was adjusted and as left time was in tolerance. <I> **** Actions Taken **** Notified Supervisor and Ops. Adjustee relay back into tolerance and wrote this CR | 02-00-TMU-RLY-62/P1A
385486 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ Housekeeping, barrel trucks |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following housekeeping issue was identified; 3 Barrel trucks lying on floor. Not secured. <I> **** Actions Taken **** Recommend assignment to OPS (Area Owner) <N> **** Equipment Description **** TG 441 / Column E/16 | 02-00-T-BLDG-MISC
385487 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ Batteries w/o terminal covers | N | N |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Large batteries on a metal pallet with no coverings on terminal posts to prevent possible fire. <I> **** Actions Taken **** Recommend assignment to Electrical Maintenance (AR-ELECM) <N> **** Equipment Description **** RW 437â€™ Q1-13.2 | 02-00-W-BLDG-MISC
385488 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ Tool cabinets w/o RP labels |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; 2 tool cabinets with no Rad material labels. All other cabinets on the 507' elevation labeled. <I> **** Actions Taken **** Recommend assignment to Radiation Protection. Tool cabinets have been labeled as appropriate per the RP Operations Supervisor. No further action required. <N> **** Equipment Description **** RW 507â€™ Demin Access â€“ ARSD (north wall) | 02-00-W-BLDG-MISC
385489 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Leak originating from Main Gen shroud | N | N |  | N | YES | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; 1-3 inch drain pipe originating from Main Generator shroud area, South side of MG next to H2 CLR headers is dripping water to a hub at rate of two drops per six second - source unknown. No def. tag observed. <I> **** Actions Taken **** CR and Work Request generated to investigate. <N> **** Equipment Description **** TG 471 under generator | 02-00-E-GEN-1,02-00-T-BLDG-MISC
385490 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Bottle cart w/o wheels locked | N | N |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Bottle cart stored in the storage area in the BOP Swgr is not secured with wheels locked like other equipment in the area. <I> **** Actions Taken **** Recommend assignment to OPS (Area Owner) <N> **** Equipment Description **** TG 441 . No bottle cart was found in this area on night shift when the operator investigated it 10/8/18 mshoup | 02-00-T-BLDG-MISC
385491 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ TG 501, Ext. cord across walkway | N | N |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Extension cord for portable equipment plugged in and run across the walkway. Located near T6B ventilation control panel. <N> **** Equipment Description **** TG 501, Column G/5 . This appears to be for the steam tunnel camera. It has a cover to prevent tripping. Does not appear to be a hazard. | 02-00-T-BLDG-MISC
385492 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ EPA Breaker Bump Covers |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; EPA BKRS A/C/E/F have plastic bump guards over the bkr switch. EPA Bkrs B/D do not have bump guards. All EPA Bkrs have key switches with key inserted, but no bump guards. The key switches appear to also be capable of tripping the EPA bkrs. <I> **** Actions Taken **** Recommend assignment to OPS <N> **** Equipment Description **** RW 467 / RPS room 2 | 02-00-W-BLDG-MISC
385493 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ Fall protection gear around equipment |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Fall protection equipment left on a cart and left in a manner that could result in damage to the equipment. <I> **** Actions Taken **** Recommend assignment to Reactor Maintenance area owner (AR-RXMAINT) <N> **** Equipment Description **** RX 572â€™ Near ROA-HV-1A Suction Valve | 02-00-R-BLDG-MISC,02-00-ROA-HV-1
385494 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ Missing temp. mod. tag | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Rm-73 on refuel floor does not have a temporary modification tag. Equipment is setting on a structural beam and is not hard-wired. <I> **** Actions Taken **** Recommend assignment to Reactor Maintenance area owner (AR-RXMAINT) <N> **** Equipment Description **** RX 606 Refuel floor west wall | 02-00-R-BLDG-MISC
385496 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ Spent Fuel Pool FM concern |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; A component / tools were wrapped with clear plastic near the spent fuel pool. This is potential for plastic being in SFP as foreign material. <I> **** Actions Taken **** Recommend assignment to Reactor Maintenance area owner (AR-RXMAINT) <N> **** Equipment Description **** RX 606 Refuel floor | 02-00-R-BLDG-MISC
385497 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ Spent Fuel Pool red label tags |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Red label tags in spent fuel pool area, used to affix rad tags to pool handrails. <I> **** Actions Taken **** Recommend assignment to Reactor Maintenance area owner (AR-RXMAINT) <N> **** Equipment Description **** RX 606 Refuel floor | 02-00-R-BLDG-MISC
385498 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Leak near RWCU-P-1A room | N | N |  | N | YES | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; A water leak was observed in reactor building elev 522'. The leak location was in front of RWCU-P-1A room. (not from the pump room itself) <I> **** Actions Taken **** CR and Work Request generated to investigate. <N> **** Equipment Description **** RX 522â€™ . Leak previously identified. Leak is in Contaminated Area already and under control. No further actions required by this AR. | 02-00-R-BLDG-MISC
385499 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ Ty-wraps around Spent Fuel Pool |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Refueling floor - black ty wrap(s) used to attach rad -tickets to fuel Pool hand rail. What is station std & do they meet it (e.g. do they have metal & do they float) <I> **** Actions Taken **** Recommend assignment to Reactor Maintenance area owner (AR-RXMAINT) <N> **** Equipment Description **** RX 606 Refuel floor | 02-00-R-BLDG-MISC
385500 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Scaffold carts w/o wheel locks | N | N |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Locking mechanism (wheel locks) not on cart holding scaffold poles WO 01158000-01 staged in Aux. Bldg. (Missile Hazard) <I> **** Actions Taken **** CR and Work Request generated to correct. <N> **** Equipment Description **** RX 522 . The three scaffolding carts in the area had wheel locks on them when inspected on night shift. 10/8/18 mshoup No further actions required for this AR. | 02-00-R-BLDG-MISC
385501 | CR | 20181008 |  | 3 | TMU-M-P/1A Motor Lead Degradation | N | N |  | N | YES | <D> **** Detailed Description **** Upon Determing TMU-M-P/1A it was noticed that the motor t-leads were showing signs of degredation. The conductor insulation was showing signs of cracking/splitting around the lug area. Multiple broken wire strands were also noted. <I> **** Actions Taken **** Took photos, informed our supervisor, contacted sysytem engineer, generated CR | 02-00-TMU-M-P/1A
385502 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Tools not secured | N | N |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; There are two identical tools laying on the floor next to the wall by a cart under work order 01158000-01 that are not secured. The posts are metal and approximately 12' long with an attachment that looking like 4- prong locking / unlocking device attached. Potential missile hazard. <I> **** Actions Taken **** CR and Work Request generated to correct. <N> **** Equipment Description **** RX 522 | 02-00-R-BLDG-MISC
385504 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Several broken light sockets on panel | N | N |  | N | YES | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Several broken light sockets on panel E-SM-82 <I> **** Actions Taken **** CR and Work Request generated to correct. | 02-00-E-SM-82
385505 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ E-IR-12 Bump sensitive instru. |  |  |  | N | YES | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Instrument Rack E-IR-12 Bump sensitive instrumentation. No stay clear boundary on floor. <I> **** Actions Taken **** Recommend assignment to Operations to evaluate <N> **** Equipment Description **** RX501 | 02-00-E-IR-12
385506 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ No red/white tape on floor for Inst. |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Caution signs on instrument rack stating to not use radio's in vicinity of rack. Floor does not have red/white tape - inconsistent with standard. (Radio-Free zone marking) <I> **** Actions Taken **** CR and Work Request generated to correct. <N> **** Equipment Description **** TG 501â€™ East side . Red/White tape is not a standard per PPM 1.3.72. WR 29144996 canceled. Recommend an assignment to evaluate currrent labeling practice for RF transmitting device control areas. M Mitchell 10/9/18 | 02-00-E-IR-6A,02-00-T-BLDG-MISC
385507 | CR | 20181008 |  | 3 | ppm 16.11.6 needs Pressure Indicator EPN in step |  |  |  | N | NO | <D> **** Detailed Description **** During the performace of PPM 16.11.6 - Weekly Iodine, Particulate, and Tritium survieillance Section 7.3 the pressure indicator EPN used to validate vacuum for TEA is in a note and not in the steps that have you use it. Step 7.3.3 should say :7.3.3 OBSERVE TEA sample line vacuum value on TEA-PI-12. (it does not state which pressure indicator to use in the step which could cause confusion and does not allow for TRR). Also in Step 7.3.5 It should read -ENSURE sample flow rate and vacuum, through the new filters, returns to values close to the values observed in Steps 7.3.3 and 7.3.4. using TEA-PI-12. <I> **** Actions Taken **** Notified Chemistry Supervision, chemistry system specialist and procedure sponsor.
385508 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Bolt missing from back panel cover | N | N |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Bolt missing from Aux Compartment #2 back panel corner. In BOP Swgr. <I> **** Actions Taken **** CR and Work Request generated to correct. <N> **** Equipment Description **** TG 471 West Col F/16 EPN not provided | 02-00-T-BLDG-MISC
385509 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Bolt missing from back panel cover... | N | N |  | N | YES | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Bolt missing from back panel cover on E-CB-1/2 Swgr. <I> **** Actions Taken **** CR and Work Request generated to correct. <N> **** Equipment Description **** TG 471 West Col G/14 | 02-00-E-CB-1/2
385510 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ Oil bath oil w/o labeling |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; FLEX Bldg. (inside PA); Found several gallons of oil bath oil started in black tote with no labelling of any hazard. I was told it was a Category 3 and did not need labels. Referred to FP. <I> **** Actions Taken **** Recommend assignment to Engineering to correct issue <N> **** Equipment Description **** Building 600
385511 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ Building 74 motors & outlets |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Warehouse walk down - it is clear if large motor stands in building 74 are engineered. It also isn't clear if the circuit is GFCI protected. <I> **** Actions Taken **** Recommend assignment to Reactor Maintenance to address question if motor stands are engineering and an assignment to Facilities to address GFCI protection in the building. <N> **** Equipment Description **** Building 74
385512 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Old work request challenge TMU-U-1C | N | N |  | N | YES | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Old work request challenge 04/19/2012 TMU-U-1C leaking oil. ENW insight - WO 02055111 TMU-MO-1C External PM completed 10/28/2014, identified leaking and refilled. Next PM scheduled in 2020. WO 02066125 added silicone to the outside of the gear box 02/21/2018. Due to not having internal drawings non -intrusive repairs were completed. TMU-MO-1C needs to be checked for leakage and if still leaking planned to be disassembled so that the gasket can be replaced. <I> **** Actions Taken **** CR & Work Request generated to investigate and correct. | 02-00-TMU-MO-1C,02-00-TMU-V-1C
385514 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ Step ladder sitting on floor |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; "Little Giant" step ladder sitting on floor, folded up. Does not appear to be a storage area. <I> **** Actions Taken **** Recommend assignment to OPS (Area Owner) <N> **** Equipment Description **** TG 501 Near DEH Fluid Reservoir | 02-00-T-BLDG-MISC
385515 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ FME cover and rad bags left Rad drums |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; FME cover and rad bags left unattended on Rad drums. Housekeeping <I> **** Actions Taken **** Recommend assignment to RP Laborers (Area Owner) FME cover and rad bags left on Rad drums have been removed. No further action required. <N> **** Equipment Description **** RW 437 K1/12.5 | 02-00-W-BLDG-MISC
385516 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ HRA rope limits access to area |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; HRA rope at top of ladder requires workers to duck under rope and posting to access the landing. Rope is fixed in place. <I> **** Actions Taken **** Recommend assignment to Radiation Protection <N> **** Equipment Description **** RW 437 Q1/15.9 WR 29145522 initiated to install swing gate at top of ladder in RW 437. | 02-00-W-BLDG-MISC
385517 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Valve wrench in an "oil absorbent pad |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Valve wrench / "persuader" in an "oil absorbent pads only" barrel near TO-EX-4B. <I> **** Actions Taken **** Recommend assignment to OPS (Area Owner) <N> **** Equipment Description **** TG 471 near TO-EX-4B Wrench placed in tool box. No further actions required for this AR. | 02-00-T-BLDG-MISC
385518 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ Generator condition monitor Housekeep |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Generator condition monitor (TG-10-1) shelf has tape, bulbs, chart recorder paper on it. <I> **** Actions Taken **** Recommend assignment to OPS (Area Owner) <N> **** Equipment Description **** TG 471 Gen Monitor Panel | 02-00-TG-ID-1
385519 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Tools & a chair propped against wall |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Switchgear room 1, there are breaker tools and a chair propped against a wall near E-CB-7/75/2. Housekeeping <I> **** Actions Taken **** Recommend assignment to Radiation Protection (Area Owner) <N> **** Equipment Description **** RW 467 . Breaker tools have been stowed 10/8/18 mshoup Chair still in area, unkown where it came from. | 02-00-W-BLDG-MISC
385520 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Insulation torn at joint | N | N |  | N | YES | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Insulation torn at joint on piping exposing a small portion of the pipe. <I> **** Actions Taken **** CR and Work Request generated to correct. <N> **** Equipment Description **** RX 572â€™ ROA-HV-1A Suction Valve | 02-00-R-BLDG-MISC,02-00-ROA-HV-1
385521 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ StorgeArea33 w/ material outside line |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Staging area permit 33 had a large number of materials stored outside of the line marked areas. The materials included tables chairs, tools, paper, etc. The materials were outside of the green / white marked area. <I> **** Actions Taken **** Recommend assignment to RP Laborers (Area Owner) Materials are staged in area for future HCU work. 'Staged for Use' signs have been added to material. No further action required. <N> **** Equipment Description **** RX 522 | 02-00-R-BLDG-MISC
385522 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“Valve in receipt insp. area missing FM |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Warehouse walkdown valve in receipt inspection area on table with two other valve; missing FME covers <I> **** Actions Taken **** Recommend assignment to SCS . Also; Valve in receipt inspection hold area missing FME covers . The FME issues in the receipt inspection area have been resolved, additional are walk down by Warehouse Supervisor was performed to ensure no other FME issues exist (none were found). This was also discussed with Supplier Quality group supervisor (area owner) and the receiving inspector to ensure FME covers are used when/as needed. <N> **** Equipment Description **** Warehouse
385523 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ Rad. sign hanging at head level as yo |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Radiation sign hanging at head level as you enter. <I> **** Actions Taken **** Recommend assignment to RP <N> **** Equipment Description **** RW 487 / Chem Lab This posting was reviewed by the RPM. It was determined that the Radiation Area Posting cannot be placed anywhere else and not limit access to the chemistry lab area. Additionally, the Radiation Posting is properly located for the given radiological conditions of the area. No further action required. | 02-00-W-BLDG-MISC
385524 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ No lighting, FP equipment in the area | N | N |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; 441 Turbine Bldg near Column A15 No lighting, FP equipment in the area. <I> **** Actions Taken **** CR and Work Request generated to correct. <N> **** Equipment Description **** TG 441 Column A/15 | 02-00-T-BLDG-MISC
385525 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ PCs stored/left in box on files cabin |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; PCs stored/left in box unattended on files cabinet in RP storage area. Housekeeping <I> **** Actions Taken **** Recommend assignment to Radiation Protection (Area Owner) Material has been removed and properly stored. No further action required. <N> **** Equipment Description **** RW 467 Column K/17 | 02-00-W-BLDG-MISC
385526 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ No GFCI for Eberline & pump placed... |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; No GFCI for Eberline and pump placed on cart. There are 2 GFCI 's on the cart, but they are not attached to anything. <I> **** Actions Taken **** CR and Work Request generated to correct <N> **** Equipment Description **** TG 501 Column D/6 | 02-00-T-BLDG-MISC
385527 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Manlift storage area ext. cord on flo |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Manlift storage area has extension cord on floor, no GFCI. Also charger for floor cleaner by elevator does not have GFCI. <I> **** Actions Taken **** CR and Work Request generated to correct. <N> **** Equipment Description **** RX 471 | 02-00-R-BLDG-MISC
385528 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Floor coating flaking off behind H2 d | N | N |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Floor coating flaking off behind H2 dryer <I> **** Actions Taken **** CR and Work Request generated to correct. <N> **** Equipment Description **** TG 471 | 02-00-T-BLDG-MISC
385529 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Overhead lights out, outside of lube | N | N |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Overhead lights out (NOT safety concern), just outside of lube oil room. <I> **** Actions Taken **** CR and Work Request generated to correct. <N> **** Equipment Description **** TG 471 East | 02-00-T-BLDG-MISC
385530 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Overhead lights out on TMU pump elev. | N | N |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Overhead lights out on TMU pump elevation - no safety concerns <I> **** Actions Taken **** CR and Work Request generated to correct. <N> **** Equipment Description **** TMU pump elevation | 02-00-M-BLDG-MISC
385531 | CR | 20181008 |  | 3 | 2018 WANO Evaluation â€“ Red duct tape used to label brkr. sto |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Red duct tape used to label some breaker storage boxes in BOP Swgr storage areas behind the Swgr panels. Housekeeping <I> **** Actions Taken **** Recommend assignment to Operations (Area Owner) <N> **** Equipment Description **** TG 471 | 02-00-T-BLDG-MISC
385532 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Battery charger room #2 floor dusty |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Battery charger room #2 floor is covered with clumps of dust. <I> **** Actions Taken **** Recommend assignment to Radiation Protection (Area Owner) RMC Laborers went into Battery charger room #2 with electrician escort and used micro fiber to the clean the clumps of dust on the floor. No further action required. <N> **** Equipment Description **** RW 467 | 02-00-W-BLDG-MISC
385533 | CR | 20181008 |  | 4 | 2018 WANO Evaluation â€“ Housekeeping outside FLEX Bldg. 600. |  |  |  | N | NO | <D> **** Detailed Description **** During WANO walkdown the following issue was identified; Walkdown of outside FLEX Bldg. 600. Clean well lit, no leaks noted. Spreadsheet marked for housekeeping. <I> **** Actions Taken **** CR and Work Request generated to correct. <N> **** Equipment Description **** B600
385534 | CR | 20181008 |  | 4 | NLO failed the biannual written exam |  |  |  | N | NO | <D> **** Detailed Description **** An NLO did not pass the biannual wriiten exam. <I> **** Actions Taken **** NLO Qualifications removed. Remediation package started. Notified Ops and Training Management. Remediation for exam failure IAW TDI-02
385535 | CR | 20181008 |  | 4 | Simulator Computer Room Burnt Smell |  |  |  | N | NO | <D> **** Detailed Description **** On 10/14/18, the simulator hardware technician noted a strong burnt odor in the simulator computer room. The odor was strong enough that it could be smelled outside the computer room in the simulator engineering offices. Facilities was contacted. A technician arrived to inspect the ventilation unit in the computer room. No signs of problems could be found. After the inspection, there have not been any further actions to identify the cause of the odor. Request facilities support to identify the cause of the smell. A fire in the simulator computer room would be a significant problem for CGS. Training was not impacted by this event. The oder disapated after approximately two hours. <I> **** Actions Taken **** Contacted facilities. Facilities conducted an inspection of the ventilation unit and found no issues. No further inspection has been conducted to identify the cause of the smell. Request support to perform inspections and identify the cause.
385536 | CR | 20181008 |  | 3 | Gloves found inside of TCSB1 and TCSB1A panels | N | N |  | N | NO | <C> Per MRT FEedback received on Thursday October 11, 2018, this CR was reopened and dispositioned to ITMGMT to document actions taken to correct behaviors. <D> **** Detailed Description **** while walking past TCB1 panel it was noted that the handle was left partly open. On further investigation it appears that people have been storing gloves inside the panel. Panel TCSB1A is just to the right of TCSB1 and it appears that people are also storing gloves this panel also. <I> **** Actions Taken **** Informed CRS and wrote the CR. CRS also had the operator take pictures and dispose of the gloves. <N> **** Equipment Description **** Panels TCSB1 and TCSB1A just inside west RCA enterence. | 02-00-T-BLDG-MISC
385537 | CR | 20181008 |  | 3 | CVI DWG 39-00,2 Note 6 is inaccurate | N | N |  | N | YES | <D> **** Detailed Description **** CVI DWG 39-00,2 Note 6 (PRIMARY CONDUIT BOX WTH 4" NPT CONNECTION LOCATED @ 180 DEG FROM DISCHARGE) is inaccurate with respect to the existing field configuration of all three TMU pump motors. If this existing drawing note were accurate, the primary conduit box for TMU-M-P/1A(B,C) should be on the east side of each motor (the pump discharge for each TMU pump is on the west side of each pump). For TMU-M-P/1A, this conduit box is on the south side of the motor. For TMU-M-P/1B, this conduit box is on the north side of the motor. For TMU-M-P/1C, this conduit box is on the west side of the motor. See the photos attached to the EDMS of this AR CR 385537. This is a legacy drawing issue only - there is absolutely no impact upon the continued operation, function, or qualification of the TMU motors, TMU pumps, or of any other station SSC. For resolution of this CR, Note 6 needs to be removed entirely from CVI DWG 39-00,2. Additionally, the depiction of Item 6 (including all dimensions associated with Item 6) should be removed entirely from CVI DWG 39-00,2 as all this information exists as part of separate CVI DWG 39-00,3. Finally, the dimension associated with Item 5 should be removed entirely from CVI DWG 39-00,2 as this information exists as part of separate CVI DWG 39-00,3 AND CVI DWG 39-00,2 Note 5 should be updated to add a reference CVI DWG 39-00,3. Suggest NonCAQ resolution to Design & Drafting. | 02-00-TMU-M-P/1A,02-00-TMU-M-P/1B,02-00-TMU-M-P/1C
385538 | CR | 20181008 |  | 4 | PWC-TBIT-2 (Effluent) reading -0.005. | N | N |  | N | YES | <D> **** Detailed Description **** After running the flocculator to fill PWC-TK-100, the OPs-4 went to check on the status of the flocculator. As he walked past the turbidity meters he noticed that the effuent PWC-TBIT-2 was reading negative (-0.005) which is not expected. <I> **** Actions Taken **** Informed the CRS, Initiated a CR and chemistry is performing 4 hour grab samples. | 02-00-PWC-TBIT-2
385540 | CR | 20181008 | CAQ | D | C408 Bolt stuck in alarm |  |  |  | N | YES | <D> **** Detailed Description **** Not operating as intended <I> **** Actions Taken **** Comp measure posted <N> **** Equipment Description **** Control room door | 02-00-SEC-TAS-BC408T,02-00-W-DOOR-C408
385541 | CR | 20181008 |  | 4 | E-TR-M2 Fan 10 overloads tripped | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-M2 fan 10 overloads found tripped. Overloads were reset and fan started successfully. <I> **** Actions Taken **** Informed MCR, generated AR/WR. | 02-00-E-TR-M2
385542 | CR | 20181008 |  | 4 | RRC-VD-R673 difficult to read. | N | N |  | N | YES | <D> **** Detailed Description **** RRC-VD-R673 used for controlling reactivity changes in the Main Control Room is not displaying correctly, making it difficult to read. Screen need to be replaced. <I> **** Actions Taken **** Opening WR to relaced old cloesd ones that did not fix the issue. <N> Duplicate of CR 385456. 4/T | 02-00-RRC-VD-R673
385543 | CR | 20181009 | CAQ | D | CRD-HCU-3803 trouble alarm High Water Level | Y | N |  | N | YES | <D> **** Detailed Description **** Recieved CRD-HCU-3803 trouble alarm. The alarm was due to high water level. OPs2 drained water from the HCU and the alarm is clear. <I> **** Actions Taken **** Trending | 02-00-CRD-HCU-3803
385544 | CR | 20181009 |  | 4 | Recieved 4.800.C4 2-1 "Main Tranformer TR-M2 trouble" alarm | N | N |  | N | YES | <D> **** Detailed Description **** Recieved 4.800.C4 2-1 "Main Tranformer TR-M2 trouble" alarm. The alarm was due to Cooler Group 2 and the alarm is reset. <I> **** Actions Taken **** trending | 02-00-E-TR-M2
385545 | CR | 20181009 |  | 4 | COND-V-34 Packing Leak | N | N |  | N | YES | <D> **** Detailed Description **** There is a packing leak from COND-V-34 approximately 6-10 drops per minute. The leak is falling on top of HVAC duct work for REA-FN-3 and forming a small puddle on the floor. COND-V-34 is located on RX 522â€™ along the south wall outside MC-8B Room between E-IR-H22/P002 and REA-FN-3 in the overhead. See EDMS for photos. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** COND-V-34 is located on RX 522â€™ along the south wall | 02-00-COND-V-34
385546 | CR | 20181009 | CAQ | D | CRD-HCU-1803 trouble alarm | Y | N |  | N | YES | <D> **** Detailed Description **** alarm is due to high water level, alarm is clear <I> **** Actions Taken **** trend | 02-00-CRD-HCU-1803
385550 | CR | 20181009 |  | 4 | Grip tread on Ladder rung is loose and needs to be attached | N | N |  | N | YES | <D> **** Detailed Description **** Permanent ladder leading to the top of SLC-TK-1 on RB 548 has a loose grip tread on one rung which needs to be reattached. <I> **** Actions Taken **** Discussed issue with HP Supervision. Wrote CR <N> **** Equipment Description **** RB 548 SE | 02-00-SLC-TK-1
385556 | CR | 20181009 |  | 3 | Procedure NOTE and CAUTION in SOP-CRD-HCU are incorrect |  |  |  | N | NO | <D> **** Detailed Description **** Regarding SOP-CRD-HCU Section 5.17, the second NOTE and second CAUTION on page 55 contains incorrect location of where the vent hose is now routed to. The vent hose is now routed to the Rx 606â€™ Equipment Pool, not the Rx 572â€™ Equipment Drain near ROA-FU-2A. The NOTE and CAUTION need to be corrected for accuracy.
385557 | CR | 20181009 |  | 3 | Procedure 5.5.12 needs Required Equipment list updated |  |  |  | N | NO | <D> **** Detailed Description **** The battery pack (with toggle switch) needed to perform Step 4.7.2 b needs to be added to the Required Equipment list. It would be nice to include a photo of the battery and toggle switch as an Attachment in back of procedure.
385561 | CR | 20181009 |  | 3 | NEED IMDS DATA SHEETS FOR HT-HTP-PTM/29 Thermostats |  |  |  | N | NO | <D> **** Detailed Description **** WO# 02083390 due to there not being any available IMDS Data Sheets for the thermostats located on the heat trace circuits for HT-HTP-PTM/29. Drawing E940-7 shows the thermostat wiring and set points, but both circuits are on Normally Closed contacts but there are not any specifics as far as the T-Stat closes at 300 and opens at 340 degrees. Request Engineering develp IMDS Data Sheets for the thermostats on circuits for HT-HTP-PTM/29. <I> **** Actions Taken **** Notified Engineering
385562 | CR | 20181009 |  | 3 | (FP) RW 487 Hot Instrument Shop -- Housekeeping/combustibles |  |  |  | N | NO | <D> **** Detailed Description **** Lots of combustibles staged all over the room. This room is not sprinklered and is not a designated storage area. Issues are as follows: 50-100 ft of small diameter Plastic tubing, 1- 50 ft rubber hose, upholstered office chair, two small plastic vacuums, one small cardboard box with a metal bracket in it, trash can full, three empty spools (one wood, two with cardboard interior and plastic ends), green bag of trash sitting next to trash can. trash can cover that had a swinging flap-lid but the swinging flap missing, Flamm Cab 03-0001 will self-close but the latch hangs up (possibly out of level), Flamm Cab 02-0037 has no self-closer and has a green deficiency tag with AR 342930 dated 13/3/16 written on it, AR has WR 29126116 xref that was cancelled 2/9/2016, citing ISPM-10 does not apply to power block, PPM-1.3.10C has the same requirement. <I> **** Actions Taken **** CR written, I/C notified via email, pictures uploaded to EDMS. | 02-00-W-BLDG-MISC
385563 | CR | 20181009 |  | 4 | Potable water turbidimeter needs repair | N | N |  | N | YES | <D> **** Detailed Description **** The outlet turbidimeter was displaying an error code. The error code was E-18, which from the tech manual reads â€œ Low signal. Possible causes: 1. Lamp out; 2. Offsets changed. May need system reset.â€ The chem tech did not lift up the head to see if the lamp was out but after she reset the warning, the turbidimeter did read in the negative. This turbidimeter is required per the WADOH drinking water regulations. <I> **** Actions Taken **** Compensatory measures are in place to take 4 hr readings when the flocculator is operating as per the WAC. | 02-00-PWC-TBIT-2
385564 | CR | 20181009 |  | 3 | Unable to process AED CALCULATION |  |  |  | N | NO | <D> **** Detailed Description **** Documnet Control received AED CALCULATION 6.15.01-SII-6, but is unable to process. Not all EC's listed on Cover Sheet are listed in Portal J in EC Panel for processing. <I> **** Actions Taken **** Issuing CR and informing responsible staff so that necessary changes can be made. <N> All actions completed as per assignment 01. No further actions required. This AR-CR is now closed. .
385565 | CR | 20181009 | CAQ | D | Prefabricated welds will have to be re-welded | N | N |  | N | NO | <D> **** Detailed Description **** 3 welds will have to be re-performed and accepted by QC in support of WO 02119556-01 COND-HX-6F. This is due to dimensional adjustments needed for proper plant connections. The connection point on the plant system is out of level. Making the connection in the current configuration would put more than the allowable amount of strain on the piping system. <I> **** Actions Taken **** Generated CR for documentation <N> EPN is TSW-HX-6F, not COND-HX-6F. | 02-00-TSW-HX-6F
385566 | CR | 20181009 |  | 4 | TMU-V-7A magnetic plug | N | N |  | N | NO | <D> **** Detailed Description **** magnetic plug in lower housing was unable to be removed due to heavy coating of paint and rounding of the square head. craft was unable to inspect for metal shavings. <I> **** Actions Taken **** notified supervision notified control room initiated CR informed Engineer <N> **** Equipment Description **** TMU-V-7A TMU pump house | 02-00-TMU-V-7A
385568 | CR | 20181009 |  | 4 | RHR-M-P/2B installed UTC desription does not match CAT ID |  |  |  | N | YES | <D> **** Detailed Description **** This is an administrative issue only. There is no issue with the installed motor (RHR-M-P/2B). The description for UTC 509251 does not match the associated CAT ID 8639 description for the installed RHR -M-P/2B . The CAT ID correctly descibes the motor as a 900 HP motor while the UTC still holds the old 800 HP description. This creates confusion when reviewing installed equipment information. Recommend the description be corrected to align UTC with CAT ID. <I> **** Actions Taken **** Verified information with component and procurement engineering. Discussed with Supervisor. <N> Updated UTC name using Update Equipment Name feature on D050 panel. No further actions necessary. | 02-00-RHR-M-P/2B
385569 | CR | 20181009 |  | 4 | RRC Loop Flow Indication Mismatch | N | N |  | N | YES | <D> **** Detailed Description **** There is a mismatch between the individual flow indications on the RRC Flow Manual/Auto (M/A) stations. Normally the total loop flow on the master M/A station (RRC-FI-M/A/R675) is the sum of the two individual loop indications (RRC -FI-M/A/R676A and RRC-FI-M/A/R676B). During an engineering walkdown today (10/9), however, the total flow indicator was reading around 81,000 gpm where the A and B flow indicators were reading 40,000 and 38,000 gpm respectively. Secondary flow indications showed both RRC loops flowing at around 40,000 gpm. Although these M/A station flow indicators are indication only devices that do not affect the ability of the RRC system to control flow, the cause of the mismatch should be investigated and corrected. <I> **** Actions Taken **** Discussed the mismatch with the Reactor Operator and the NSSS engineering supervisor. Created a WR to investigate and repair as needed | 02-00-RRC-FI-M/A/R675,02-00-RRC-FI-M/A/R676A,02-00-RRC-FI-M/A/R676B
385573 | CR | 20181009 |  | 3 | CBD-RLY-5 not working as designed |  |  |  | N | YES | <D> **** Detailed Description **** Per EWD-56E-135B CBD-SR-1 & 2 are supposed to be fed power from either E-PP-7R or E-PP-8R from a normal seeking power transfer relay (CBD-RLY-5). REMP program owner reports on the annual report when CBD-SR-1 & 2 are OOS for GT 24 hours. Apparently both CBD-SR-1 and 2 are OOS when SM-72 is de-energized. This is done annually. SOP-ELEC-SM7-MAINT addresses this with a step to notify REMP when SM-72 is removed from service. This CR is to determine the proper operation of CBD-SR-1 and CBD-SR-2. If it is concluded that the sample racks are not working per design, determine and complete the necessary repairs and revise SOP-ELEC-SM7 -MAINT. <I> **** Actions Taken **** Discussed with REMP program owner. Initiated CR/WR. | 02-00-CBD-RLY-5,02-00-CBD-SR-1,02-00-CBD-SR-2
385575 | CR | 20181009 | CAQ | D | SLC-P-1B Qrtrly test preconditioned | Y | N |  | N | YES | <D> **** Detailed Description **** During the SLC-P-1B Qrtrly test pressure conditions were not able to be met before tank level increased to high. This preconditioned the pump and required the test to be re-ran Per Step 7.4.9 of OSP-SLC/IST-Q701 <I> **** Actions Taken **** Informed MCR, Drained and re-ran test successfully CR is for documentation only | 02-00-SLC-P-1B
385576 | CR | 20181009 |  | 4 | Monthly Chemical Storage area inspection discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** The monthly inspection of Mechanical Maintenance chemical storage areas discovered the following discrepancies; FLSC 05-0005 had and unlabeled chemical (CP 0534). FLSC 16-0015 had an unlabeled chemical (CP 0261). FLSC 14 -0006 had an expired chemical (CP 0497). <I> **** Actions Taken **** Missing NFPA labels were applied to chemicals that needed it. Expired chemical brought waste collection site. No further action is required.
385577 | CR | 20181009 | CAQ | C | ABN-LEAKAGE Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** ABN-LEAKAGE does not reflect the current EAL classifications from PPM 13.1.1. Specifically steps 4.1.10 and 4.2.7 reference an older EAL classification scheme. The bases section also need to be updated to reflect the current PPM 13.1.1. <I> **** Actions Taken **** Submitted CR to update ABN-LEAKAGE
385579 | CR | 20181009 |  | 3 | ICP-MS/PRM-Q401 & Q402 need enhancement |  |  |  | N | NO | <D> **** Detailed Description **** When ICP-MS/PRM-Q401 & Q402 are performed, RRC-V-19 and RRC-V-20 are cycled shut and reopened. Each valve isolates SP-1 (Reactor water sample point). When these valves are reopened, pressure and flow do not return to the desired settings. There is no mention in the procedure to notify chemistry when these valves are cycled. There is only a Precaution to notify chemistry to perform a grab sample within 24 hours if SP-8 is also INOP. There needs to be a step after each valve is reopened to notify chemistry that the valve is open and to verify proper sample pressure and flow. <I> **** Actions Taken **** Adjusted sample pressure and flow. Notified CRS and supervision. Wrote CR. <N> ***General Notes*** an assignment has been created within the Maint. Procedure revision data base. No procedure revision assignment will be added to this CR. a link to the Maint. Procedure revision data has been uploaded into the EDMS of this AR | 02-00-PSR-CC-1,02-00-RRC-V-19,02-00-RRC-V-20
385580 | CR | 20181010 |  |  | ABN-CORE |  |  |  | N | NO | <D> **** Detailed Description **** Step 4.2.2.a.2 of ABN-CORE references peforming Section 1 Normal Power Reduction of the Fast Shutdown Sequence to exit Region A and the AIA. The fast shutdown sequence directs performing Section 2 if in the AIA. ABN-CORE, Step 4.2.2.a.2 should be revised to reference performing section 2 of the Fast Shutdown Sequence instead of Section 1.
385581 | CR | 20181010 |  | 4 | MCR SAM-12 Has Broken Handle & is Out of Service |  |  |  | N | NO | <D> **** Detailed Description **** -The SAM-12 @ the Main Control Room has a broken handle latch and has been taken Out of Service. (HP-EQ-42712) <I> **** Actions Taken **** -Notified HP Supervision -Initiated CR & WR. <N> **** Equipment Description **** 501' Main Control Room (HP-EQ-42712) | 02-00-HP-EQ-42712
385584 | CR | 20181010 | CAQ | C | AED CAL SW-1006-2 not updated with BDC 86-0068-0A | Y | N |  | N | YES | <D> **** Detailed Description **** In 1990, BDC 86-0068-0A authorized installation of the Standby Service Water (SW) B loop corrosion monitoring coupon station downstream of 3/4" SW-V-154G (reference AED MEC M524-3). Although pipe stress/support effects were addressed with words in the design change package itself, the existing pipe stress analysis for SW-V-154G piping (AED CAL SW-1006-2) was not updated via a formal supporting Calculation Modification Request (CMR) or revision. This is a legacy documentation issue only - there is no concern regarding continued qualification of the piping or piping supports (the issue is that the qualification wording was not provided in the most correct location). This discrepancy was discovered while reviewing documentation associated with AR EVAL 302752. For resolution of this AR CR 385584, AED CAL SW-1006-2 should be updated to include/address piping/supports depicted by SW-4752-1 (CVI ISO 317-00,5993) and PS-4753-1 (CVI ISO 317-00,5994). Per AED MEC M524-3 Note 34, SW-SV-918 and the associated carbon steel piping downstream of SW-V-154G is Code Group D (ANSI B31.1), Quality Class II, and Seismic Category II+ (+ = hangers to be designed to Seismic Category I loads). In todays vernacular, this QC/SC combination is an Augmented Quality designation (AQ, Seismic Category 1M). As such, Portal J MEL for EPN SW-SV-918 should also be updated to indicate Safety Class AQ (vs NSR), Seismic 1M (vs 2), and Quality Group A (vs 2). <I> Discussed with supervision, peers, and the Design Engineering Mechanical/Civil/Stress DA. <N> Suggest resolution assignment to Design Engineering Mechanical/Civil Design Basis group. This legacy issue will NOT be corrected via document updates associated with the AR EVAL 302752 proposed design change for the QC II SC II PVC PS piping downstream of the AR CR 385584 subject SW / PS carbon steel piping. | 02-00-SW-SV-918,02-00-SW-V-154G
385589 | CR | 20181010 |  | 3 | Some Yokogawa recorder compact flash cards too small | N | N |  | N | NO | <C> OFM today (10.15.2018) changed this from CAQ/C to AR-MFIN to Non-CAQ/3 to AR-MFIN <D> **** Detailed Description **** while performing wr 29144128 for RRC-TRS-601 "data storage card full", it was discovered that the CF card installed was only 121MB in size. The cards should be 16GB. <I> **** Actions Taken **** under separate WRs, Found 5 additional recorders with the 128MB size that have already been replaced with the 16GB cards. CGS85123 LD-TRS-608 CGS85164 ARM-RR-600 CGS85188 PRM-RR-3 CGS85109 COND-CR-1 CGS85149 MS-TR-614 If there are other recorders that have the 128mb cards, they will be identified by operator rounds and taken out of service. FIN Team Supervisor is ordering new 16gb cards as needed. <N> CR Edited to remove name and replaced with FIN Team Supervisor
385591 | CR | 20181010 |  | 4 | Individual sent home for Self Declaration of fatigue |  |  |  | N | NO | <D> **** Detailed Description **** Individual was sent home for self-declaration of fatigue. <I> **** Actions Taken **** Informed FFD. Completed form 26469
385592 | CR | 20181010 |  | 4 | Administrator User account locked out on Network switch |  |  |  | N | YES | <D> **** Detailed Description **** This switch is configured to lockout a login account if an incorrect password is entered 3 times in a row. During normal maintenance this occurred and the only administrator account on this switch has been locked out. This situation does not affect any function of the switch, so data is still being transmitted correctly. No current affect on Operations. But correcting the situation will require a reboot of the switch which will have minor impacts on operations and Cyber Security. <I> **** Actions Taken **** None at this time. Reboot of device will require coordination with Ops for use of alternate data source. | 02-00-NET4-NETSW-01
385595 | CR | 20181010 | CAQ | D | Received FCP3 drop 10-3 alarm for FP-P-2A . | N | Y |  | N | YES | <D> **** Detailed Description **** Started FP-P-2A per PPM 15.3.13 WO 02125555. Received FCP3 drop 10-3, FP-P-2A LINE PRESS LOW/PUMP FAILURE caused by FP-PS-8A with a setpoint of 100# . Operation of pump appears normal. FP-PI-10 in Main Control Room is at normal pressure of 152#. Alarm does not normally come in on pump starts and should not be in with pump running. <I> **** Actions Taken **** Pump left on for other surveillance. | 02-00-FP-P-2A
385596 | CR | 20181010 |  | 4 | Knocking/ringing sound from TMU piping in SWPH B | N | N |  | N | YES | <D> **** Detailed Description **** While completing a team field walkdown associated with AR EVAL 302752 in SWPH B on 10/10/18 at ~09:45AM, a distinct periodic knocking/ringing sound in the room was evident (not normal compared to experience of individuals on the walkdown). Initially, the noise sounded like something hard hitting an empty pipe. At the time, SWPH B was otherwise relatively quiet (SW-P-1B was not running at the time). Subsequently, the periodic knocking/ringing noise decreased to periodic knocking and then to tapping (almost unnoticable by ~10:15AM). The noise noted sounded like it was coming from the largebore TMU piping under the grating somewhere north of TMU-V-10A (i.e., upstream of TMU-LCV-1A) near the north wall of SWPH B but perhaps somewhere outside SWPH B. This CR is initiated to document the observation and to prompt additional investigation if deemed necessary by more knowledgeable station personnel. | 02-00-TMU-V-10A
385597 | CR | 20181010 |  | 3 | 205H resin was not re-ordered at the order point |  |  |  | N | NO | <D> **** Detailed Description **** 205H resin was not re-ordered by procurement when low inventory notification was sent to AAA in portal J. The notification was missed because the notification went to a portal J ID that was no longer valid. As a result, the RWCU-A demin was not able to be pre-coated untill the expedited resin was delivered. <I> **** Actions Taken **** The vendor was contacted and expedited delivery was initiated for the 205H resin. Warehouse and security personnel are being held over on overtime to deliver the resin.
385600 | CR | 20181010 | CAQ | D | Less than 5 gpm flow through SW B corrosion monitoring loop | Y | N |  | N | YES | <D> **** Detailed Description **** during field walkdown associated with AR EVAL 302752, it was noted that flow through the Standby Service Water (SW) system B corrosion monitoring loop (in SWPH B, only flows when SW-P-1B is running) may be lower than desired. This corrosion monitoring loop (PS-RO-1 and PS-RO-2) was designed to achieve a 175 psig pressure drop at 5 gpm flow The throttled position of SW-V-154G (3 turns open per PPM SOP-SW-LU and PPM 12.9.10) may need to be adjusted or there may be a partial blockage in the corrosion monitoring loop somewhere (e.g., at SW-SV-918, PS-ST-1, PS-RO-1 or PS-RO-2). Per conversation with Environmental Services personnel (see AED CAL NE-02-86-30). <I> Initiated this AR CR 385600 and its associated WR 29145053. | 02-00-PS-RO-1,02-00-PS-RO-2,02-00-PS-ST-1,02-00-SW-PIPE-MISC,02-00-SW-SV-918,02-00-SW-V-154G
385601 | CR | 20181010 |  | 4 | TSC water fountain drain clogged | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The TSC water fountain is not draining and water is pooling in the drain area. If it were left runing for a length of time it would overflow. This is the only drinkable water at that end of the plant. <I> **** Actions Taken **** Notified CRS, Supervision, Facilities <N> **** Equipment Description **** TECHNICAL SUPPORT CENTER between men and womens bathrooms
385602 | CR | 20181010 |  | 3 | AED MEC M780 DETAIL "E" is not correct |  |  |  | N | YES | <D> **** Detailed Description **** AED MEC M780 DETAIL "E" provides details of small bore piping passing through a 4" wall penetration in SWPH B. The existing AED MEC M780 detail shows two lines passing through the penetration (spared in-place 3/4"SW(100)-2 and spared in-place 1-1/4"SW(100)-2 associated with spared in-place SW-P-2B) but there are actually three lines passing through this wall penetration in the field. The third line not currently depicted in the AED MEC M780 detail is the 1"PS(46)-1CU discharge line from the SW B system corrosion monitoring loop (CVI ISO 317-00,5996,1). See the photos attached to the EDMS of this AR CR 385602. Please update AED MEC M780 DETAIL "E" as necessary. . This is a minor drawing issue only - there is absolutely no impact or effect upon the continued function, operation, or qualification of any station SSC. Suggest nonCAQ resolution by Mechanical Design & Drafting. <N> This condition was noted during field walkdown for AR EVAL 302752. | 02-00-B-BLDG-MISC
385603 | CR | 20181010 |  | 4 | CW-CT-1C Fan 18 Oil Level at Add Mark | N | N |  | N | YES | <D> **** Detailed Description **** Fan 18 oil miniscus level at add mark. Oil add needed. <I> **** Actions Taken **** Notified CRS | 02-00-CW-FN-18
385604 | CR | 20181010 | CAQ | C | SW B Corrosion Monitor on Unistrut not shown on drawings | Y | N |  | N | YES | <D> **** Detailed Description **** It was noted during field walkdown associated with AR EVAL 302752 that the NALCO Corrosion Monitor for the B Standby Service Water (SW) corrosion monitoring loop (AED MEC M524-3 and CVI ISO 317-00,5995 in SWPH B) has been hung with stainless steel tie wraps on Unistrut associated with SW-FS-42B / SW-FI-42B instrument valves. See the photos attached to the EDMS of this AR CR 385604. The presence of this item is not indicated on the configuration detail provided by CVI DWG 220-01,1277,3. Additionally, the configuration detail currently provided by AED MEC M524-3 and CVI ISO 317-00,5995 may not 100% clearly indicate that the corrator probe for this item is always installed (these drawings indicate a PVC plug for a corrator probe is installed). Resolution of this AR CR 385604 should consider if this NALCO Corrosion Monitor item should be given an EPN in Portal J MEL. Suggest resolution by Design Engineering Mechanical Design Basis group. . This item is currently hanging from a Unistrut support for safety-related instrumentation in SWPH B. However, there are no QC 2 over 1 issues/concerns associated with this condition. The item itself is light weight (poses no challenge to the capacity of the Unistrut support) and there are no safety-related components existing below the item (i e., there are no potential targets for the item to hit if it were to fail and fall). <N> The SW B system corrosion monitoring loop items (PS carbon steel & PVC piping and PS-PI-1) located below the subject NALCO Corrision Monitor item are nonsafety-related - see AED MEC M524-3 (Note 34). | 02-00-B-BLDG-MISC,02-00-SW-FI-42B,02-00-SW-FS-42B
385605 | CR | 20181010 |  | 4 | DG Turbo Testing Unsuccessful | Y | N |  | N | YES | <C> OFM today (10.15.2018) changed this from CAQ/D to Non-CAQ/4. <D> **** Detailed Description **** Engineering reviewed recent turbo charger data collected during DG1 maintenance window. Data collected did not provide the data point needed for evaluation. Also KW data was offset by 1460KW as the input was not zerod after the clearance was removed. WR have been generated to perform testing on DG2 and DG3. WR to repeat collection for DG1 will be created if needed after data for DG2 is reviewed. This information is needed to evaluate the need to replace the Turbochargers. The first PM due is in FY20 and is currently not funded. Data will also support a potential change to the survailance runs that will correct a long standing issue of running on the turbocharger gear trains. Recomendation is to perform DG2 data collection during the next available monthly run. And to perform the DG3 collection during the Jan work window as DG3 is not affected by the same failure mechanism. This CR is to document the need for additional data collection. There is not a concern for operability of any of the DG engines due to the data reviewed. | 02-00-DG-ENG-1A1,02-00-DG-ENG-1A2
385606 | CR | 20181010 |  | 4 | Broken Fluorescent Lamp with half of lamp in fixture socket. | N | N |  | N | YES | <D> **** Detailed Description **** The light fixture near the flocculator control panel has a broken lamp. One half of the lamp is still attached to its socket, with the broken pieces in eclosed fixture . See attached photo. Lamp needs to be replaced. <I> **** Actions Taken **** Notified CRS. <N> **** Equipment Description **** Flocculator Building (#33)
385607 | CR | 20181010 | CAQ | D | FP-P-2A Seal Water Supply Line Leak Getting Worse. | N | Y |  | N | YES | <D> **** Detailed Description **** FP-P-2A seal water supply line leak at motor case getting worse. See attached video. This was written up on 7/12/18, reference that AR video for comparison. Connection needs to be sealed. <I> **** Actions Taken **** Notified CRS. <N> As of 10/11/18 5:55AM, there is no video attached to the EDMS of this AR CR 385607. From the video attached to the EDMS of AR CR 382382, the leak is from the water lines to the FP-M-P/2A motor cooler. Added EPN FP-M-P/2A to this AR CR 385607. | 02-00-FP-M-P/2A,02-00-FP-P-2A
385608 | CR | 20181010 |  | 4 | Jet Pump #20 data point X053 appears to be drifting | N | N |  | N | YES | <D> **** Detailed Description **** Jet pump #20 flow rate datapoint (X053) in eDNA appears to be a degrading. The flow rate is degrading relative to the other double tap jet pumps; JP-5, 10, and 15 (pts:X037, X052, X038). The data point took a slight step change down on 10-4-18 and then began a slow decline on 10-9-18 (See EDMS file JP Flow Trend 10-10-2018). This trend is not seen on the other flow data points for these jet pumps (B064, B069, B074 and B079) (See EDMS). This appears to be an instrumentation issue only for this data point. <I> **** Actions Taken **** Discussed the trend with the RRC System Eng and Rx Eng. Recommend Broke/Fix to recalibrate the data point. | 02-00-MS-JP-20
385609 | CR | 20181010 | CAQ | B | Incorrect fuses installed for RHR-V-21 | Y | N |  | N | YES | <C> Risk - Medium (B) Cause - Uncertain/Complex - Investigation Template Required CR reopened to add completion required check mark to referenced WO/WR per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** During a fuse log audit, it was discovered that the main power fuses of RHR-42-8BA7A, motor starter for RHR-V-21, are the incorrect amp rating. The ITE starter was recently replaced by a NLI unit per EC 12164. Per the calculations of the EC, the NLI starter was to be fitted with TRS-12R fuses. When the replacement starter pre-installation setup and testing was performed per 02036301-05, TRS-8R fuses were procured and installed as directed by the work instructions. This was a QC step. When the NLI starter was installed in the plant on 8/22/18 per 02036301-01, it was not caught that the main power fuses were the wrong rating. From the nameplate data as documented on E528-36, the motor has a full load amp rating of 8.4 and locked rotor amp rating of 9.66 amps. Recommend installing TRS -12R fuses to restore the component to design specification. <I> **** Actions Taken **** Notified my supervisor <N> ***General Notes*** A fact finding process has been entered. From SWP-CAP-01 Bullets 1, 2 and 7 on page 22 are applicable which makes this CR a Bravo due to Risk: Medium, and the cause being complex/ unknown. an investigation Template is required. | 02-00-RHR-42-8BA7A,02-00-RHR-V-21
385611 | CR | 20181010 | CAQ | D | Transient item found questionably close to SW-FS-39 valve | Y | N |  | N | YES | <D> **** Detailed Description **** On R522' south of column N/4.1, a transient item (metal frame for used RCA PC laundry) was found in questionably close proximity to a local instrument tubing valve for SW-FS-39 / SW-FI-39. The condition was addressed immediately upon observation to ensure conformance with PPM 10.2.222. Regardless, this transient item needs to be removed. As-found and as-left photos are attached to the EDMS of this AR CR 385611. The subject transient item is not heavy and would not have resulted in damage to the safety-related tubing or instrument valve during a design basis event (e .g., OBE or SSE seismic condition). <I> **** Actions Taken **** This condition was noted while performing field walkdown to support resolution of AR CR 379990. | 02-00-R-BLDG-MISC,02-00-SW-FI-39,02-00-SW-FS-39
385612 | CR | 20181010 |  | 4 | Backflow preventer PWC-V-137 occasionally leaks/ sprays | N | N |  | N | YES | <D> **** Detailed Description **** Backflow preventer PWC-V-137 occasionally leaks/ sprays Drywall , paint in area also water damaged <I> **** Actions Taken **** Informed MCR, SSS | 02-00-PWC-V-137
385614 | CR | 20181010 |  | 4 | TMU-MO-1A Degradation | N | N |  | N | YES | <C> CR Edited at the request of the user (from 1C to 1A). <D> **** Detailed Description **** During inspection / trouble shooting TMU-MO-1A, identified oil in the limit switch compartment and when the valve cycled closed, it stopped every 10 seconds and then restarted. Recommend rebuilding the Rotork actuator and gear box. <N> TMU-V-1A via WO 0216140. This is is not TMU-V-1C | 02-00-TMU-MO-1A,02-00-TMU-V-1A
385615 | CR | 20181010 |  | 4 | CRD-V-732A missing nut on handle/stem | N | N |  | N | YES | <D> locking device on CRD-V-732A, this small nut can be CRD-V-732A is missing the nut on that holds the valve **** Detailed Description **** handle to the stem. (Normall closed). Valve currently has a locking device as part of bump hazard prevention based on the CRD-P-1A, gearbox work performed today. . At some time following the lift of D-CRD-P-1A-003 and removal of the replaced in the future via this WR. <I> **** Actions Taken **** Generated CR. No further action. <N> **** Equipment Description **** 3/4" CRD-PX-5A (Spared with a plug). Normally closed. | 02-00-CRD-V-732A
385618 | CR | 20181010 |  | 4 | Deviation from PPM 1.10.10 |  |  |  | N | NO | <D> **** Detailed Description **** Regulatory Affairs Management allowed deviation from PPM 1.10.10. This deviation will be corrected with a department data entry and verification performed in November 2018. <I> **** Actions Taken **** This is a trend only and again will be corrected in November 2018.
385619 | CR | 20181010 |  | 4 | Received 4.800.C4 2-1 MAIN TRANSFORMER TR-M2 TROUBLE | N | N |  | N | YES | <D> **** Detailed Description **** OPS4 investigaed. Cooler group 2 failure alarm was in and reset. Recomend trending with the numerous other alarms for this condition. <I> **** Actions Taken **** CR written to document. | 02-00-E-TR-M2
385620 | CR | 20181010 |  | 4 | X054 point causing spurious first out signal to GDS | N | N |  | N | YES | <D> **** Detailed Description **** Computer point X054, which is fed from MS-PT-51B, is causing spurious first out scram alarms on the GDS reactivity screen. See attached EDNA plot of degrading computer signal. There have been no indications of pressure fluctuations on any instruments noted in the control room. Request computer point be investigated and corrected <I> **** Actions Taken **** Discussed with CRS and SM. MCR staff monitoring GDS reactivity display and resetting first out scram alarm as it comes in. <N> **** Equipment Description **** TDAS MUX 01 | 02-00-MS-PT-51B
385621 | CR | 20181011 |  | 3 | 2018 TFOF Plant Personnel in Force on Force Play Area |  |  |  | N | NO | <D> **** Detailed Description **** During the 10/10/2018 Force on Force Exercise multiple plant personnel walked through the play area after announcements were made that the drill was in progress. Having personnel move through the drill play area can pose both safety concerns and drill control issues. There were multiple communications made to plant personnel in the weeks prior to drills commencing and PA announcement was made prior to the drill starting in attempt to prevent this from occurring. <N> Additional communications went out in D-15, plant announcements prior to drills as well as articles in EN news to notify plant personell of drill times and expectations. No further actions requried.
385625 | CR | 20181011 |  | 4 | HTP-FP-8 flocc bldg heat trace panel | N | N |  | N | YES | <D> **** Detailed Description **** htp-fp-8 circuit 44F loss of continuity light is blinking <I> **** Actions Taken **** informed MCR initiated CR/WR <N> **** Equipment Description **** HTP-FP-8 | 02-00-HT-HTP-FP/8
385626 | CR | 20181011 | CAQ | D | WFB-441/1 EBU | N | N |  | N | YES | <D> **** Detailed Description **** EBU WFB-441/1 battery fault code is lit <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-E-BU-WFB441/1
385632 | CR | 20181011 |  |  | Replan work orders for swap-out instead of rework actuators | [5 empty] | <D> Work orders to replace seals on air operated actuators need to be revised. The old actuators which were removed from CVB valves in R-23 need to have the seals replaced pre-outage in the shop and swap out the actuators during R-24. This will be the method of performing this work for the future. This will reduce time in the Drywell/Wetwell reducing dose. See Cross Reference for list of work orders to revise. Please assign appropriate actions as necessary to complete. This is for R-24 Outage work. <I> Initiated this CR in order to have trackable actions to ensure completion prior to R-24 Work Order Walkdown milestone due date. | 02-00-CVB-AO-1C1,02-00-CVB-AO-1C2,02-00-CVB-AO-1D1,02-00-CVB-AO-1D2,02-00-CVB-AO-1N1,02-00-CVB-AO-1N2,02-00-CVB-AO-1P1,02-00-CVB-AO-1P2
385633 | CR | 20181011 |  | 3 | Replan work orders for swap-out instead of rework actuators | N | N |  | N | YES | <D> **** Detailed Description **** Work orders to replace seals on air operated actuators need to be revised. The old actuators which were removed from CVB valves in R-23 need to have the seals replaced pre -outage in the shop and swap out the actuators during R-24. This will be the method of performing this work for the future CVB valve actuators. This will shorten the duration in the Drywell/Wetwell thus reducing dse. This is for R-24 Outage work. There is no Operability issues with this CR. <I> **** Actions Taken **** Initiated this CR in order to have trackable actions to insure completed prior to the R-24 Work Order Walkdown milestone due date. <N> **** Equipment Description **** Wetwell | 02-00-CVB-AO-1C1,02-00-CVB-AO-1C2,02-00-CVB-AO-1D1,02-00-CVB-AO-1D2,02-00-CVB-AO-1N1,02-00-CVB-AO-1N2,02-00-CVB-AO-1P1,02-00-CVB-AO-1P2
385634 | CR | 20181011 | CAQ | B | Received 125 VDC Charger Trouble, P601.A1,4-3 alarm. | Y | N |  | N | YES | <C> Risk - Medium (B) Cause is Uncertain or Complex - Investigation Template Required. <D> **** Detailed Description **** Received 125 VDC Charger Trouble, H13-P601.A1,4-3 alarm. Electrical craft had removed the Battery Charger from Equalize. The HPCS Voltage as denoted on H13-P601 is 123 VDC. <I> **** Actions Taken **** Notified the CRS and SM. Contacted the Craftsman. Established a Key Parameter on HPCS Battery Voltage. Reference TS 3.8.4 and 3.8.6 per the ARP. <N> Risk - Medium (B) Cause is uncertain or complex - Investigation Template Required. | 02-00-HPCS-C1-1
385635 | CR | 20181011 |  | 4 | MS-V-104B S5 packing leak | N | N |  | N | YES | <D> **** Detailed Description **** MS-V-104B has an S5 packing leak as identified on a camera tour of TG 501. This is NOT the source of the loud leak from the 501. Valve is normally closed. <I> **** Actions Taken **** Updated FLC map. | 02-00-MS-V-104B
385636 | CR | 20181011 |  | 4 | Security wrongway alarm noise dampening cover needs replaced | N | N |  | N | YES | <D> **** Detailed Description **** Security's wrong way alarm noise dampening cover at the security roadblock is inoperable and needs replaced. Item is located in BRE 21A. <I> **** Actions Taken **** Security supervision notified. CR/WR initiated. <N> **** Equipment Description **** Security BRE 21A at the security roadblock.
385638 | CR | 20181011 | CAQ | D | Analyzer Room B Cooler Flow Low alarm. | Y | N |  | N | YES | <D> **** Detailed Description **** Received Analyzer Room B Cooler Flow Low alarm, H13-P812 .R2, 5-4, alarm. OPS 2 reports SW-FI-44 denotes 8.5 gpm. The recommended band per OSP-SW-M102 is 10 - 15 gpm. The Minimum Operability value per OSP-SW-M102 is 8 gpm. <I> **** Actions Taken **** Notified the CRS. OPS 2 adjusting SW-FI-44 per a partial OSP-SW-M102. | 02-00-RRA-CC-17,02-00-SW-FI-44
385640 | CR | 20181011 | CAQ | C | (QA) 3 Sensitive EC Records Not Stored IAW Procedures |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Three sensitive Engineering Change (EC) package Quality Assurance Records were not stored in accordance with the storage requirements within Site-Wide Procedures. In addition, the second portion of one EC record does not have a Form 26809 â€œWithhold From Public Disclosure Cover Sheetâ€ on it, contrary to procedures and instructions. These are procedure use and adherence issues, but there is no known consequence at this time because these EC record files are currently password protected. These Cyber Security related EC records contain pages marked "Withhold from Public Disclosure in Accordance with 10 CFR 2.390", and are currently being stored under password protection in the Asset Suite EC module, which is not a current storage option authorized by SWP-SEC-11 â€œProtection of Sensitive But Unclassified Informationâ€ for sensitive information. Requirements: (see full details in EDMS) Factual Basis: â€¢ The following Plant Design Change (PDC) ECs required special handling for containing â€œWithhold from Public Disclosureâ€ sheets, but were stored as QA Records in EC EDMS, which is not authorized as a storage option by SWP -SEC-11 and is contrary to DES-2-25: o PDC EC 13222 â€œCyber Hardening of DEH, RFT and RFW Level 4 Systemsâ€ o PDC EC 13304 â€œCyber Security Time Synchronization & Level 3 Switchesâ€ o PDC EC 13492 â€œCyber Security Digital Asset Protection System (DAPS)â€ â€¢ In addition, EC 13492 rev 002 (Part 2 of 2) did not have a Form 26809 â€œWithhold From Public Disclosure Cover Sheetâ€, contrary to SWP-REC-02 and DES-2-1. Insights: â€¢ Contractor in Design Engineering stated he misunderstood the requirements in DES-2-25 and SWP SEC-11. â€¢ Contractor in Design Engineering surmises a Form 26809 coversheet missing from EC 13492 (Part 2 of 2) is because both Part 1 and Part 2 together form the complete EC record; however, the Cyber Security Program Manager agrees that Part 2 of 2 should have a Form 26809 coversheet because it is a separate file. . <I> **** Actions Taken **** Notified Design Supervisor and Design Engineering Manager. . This is a Deficiency that was identified during planning for the upcoming Cyber Security audit AU-CSQ-18. . Recommend routing to Design Engineering.
385641 | CR | 20181011 |  | 3 | DWST not filling with demin makeup at expected rate | N | N |  | N | YES | <D> **** Detailed Description **** With the demin trailer running, the DWST was only filling at 9 gpm. Inspection of the demin trailer revieled that the trailer output was less than expected (~50gpm). The relief valve on the trailer may be sticking and causing the product water to divert to the evaporation pond. This is vendor equipment and no work request is required at this time. <I> **** Actions Taken **** Callled vendor for the demin trailer. He is expected on site today to troubleshoot. EFIN was also contacted and determined that the two plant valves between the demin trailer and the DWST were not the issue. Notified Environmental group that the evaporation ponds may be recieving the bulk of the demin water produced. | 02-00-DW-TK-1
385644 | CR | 20181011 | CAQ | D | ES-01 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** ES-01 is not functioning as designed and requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervision notified. Initiate CR/WR | 02-00-SEC-TAS-ES01T
385646 | CR | 20181011 | CAQ | D | FP-P-110 engine coolant level low | N | Y |  | N | YES | <D> **** Detailed Description **** While performing PPM 15.1.4, FP-P-110 was found to have low engine coolant level. PPM 15.1.4 step 7.6 says to verify coolant level is within 2" below the filler neck/cap. The actual level is approximately 3 to 3.5" below. Recommend mechanical maintenance add coolant. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-FP-ENG-110,02-00-FP-P-110
385647 | CR | 20181011 |  | 4 | Water on floor in RW 487' Chem lab | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Water was discovered on the floor by PSR-SR-17. Chemistry technician contacted HP and a survey was conducted. The water was determined to be clean and laborers cleaned the water on the floor. Hours later, more water was discovered on the floor in the same location, HP again surveryed the area and determined the water was clean. Laborers again cleaned the water on the floor. No additional water has accumulated on the floor. Observation could not determine the source of the water, no leak could be seen from PSR -Sr-17. Water may be from a roof leak from the recent rain showers. <I> **** Actions Taken **** Contacted laborers and HP to surevey and clean water. Informed chemistry supervision. Wrote CR/WR to document. | 02-00-PSR-SR-17,02-00-W-BLDG-MISC
385648 | CR | 20181011 |  | 3 | Procedure 15.2.49, Function and Sensitivity Check of VESDA |  |  |  | N | NO | <D> **** Detailed Description **** During the initial use of Procedure 15.2.49 (Function and Sensitivity Check of VESDA), Electrical Maintenance identified a number of enhancements to improve the ability to implement the procedure. These enhancements were discussed with the Responsible Engineer and VESDA Project Manager. The procedure as written is acceptable for use. The recommended changes do not alter the intent of the procedure or acceptance criteria for the parameters being tested. The Corrective Action will be to initiate a Procedure Change via a PCN to revise 15.2.49 accordingly to incorporate the recommended chanages and enhancements. The recommended changes do not alter the intent of the procedure or acceptance criteria for the parameters being enhancements. <I> **** Actions Taken **** Notified Project Manager Design ENegineering Supervisor <N> This is associated with an in-progress EC 16066 and is part of the PMT being performed for that EC. It does not affect existing fire detection in the Vital Island, as that is still functional via zones 22 and 23. No impact to safety.
385649 | CR | 20181011 |  | 4 | HSSF Alarms | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** On HSSF HMI panel in RW 487' chem lab received following alarms: 1. PC SYS-STAT TROUBLE PCP trouble alarm, Chemistry actions per CI-14.4 are to contact CRS and write a CR. 2. HS PSL119-STAT LOSS Loss of Nitrogen Purge Pump A status in, Chemistry Actions per CI-14.4 are to contact the CRS write WR and CR. <I> **** Actions Taken **** Contacted MCR wrote CR and WR <N> **** Equipment Description **** HSSF
385650 | CR | 20181011 | CAQ | B | Faulted QC Inspection â€“ Incorrect Motor Starter Fuses | N | N |  | Y | NO | <C> CR was upgraded to Severity â€œBâ€ at the direction of OFM On 10.16.2018 Risk - Medium (B) Cause is Uncertain or Complex - Investigation Template Required. <D> **** Detailed Description **** Quality Control verified and accepted fuses that did not meet design requirements. Incorrect motor starter fuses were ordered by planning, verified by craft, accepted by Quality Control and installed during bench testing of new bucket RHR-42-8BA7A for RHR-V-21 per WOT 02036301-05 in June 2017. Step 4.8.1 of the WOT instructions contains a QC Hold Point for parts acceptance to verify fuses are correct per EC 12164, page 530 (E528-36) for the appropriate EPN. EC 12164, page 530 (E528-36), indicates that starter fuses for RHR-V-21 should be rated at 12.0. TRS-12R fuses should have been installed. Instead, TRS-8R fuses were procured, accepted by QC and installed. . . This CR specifically addresses the Quality Control Faulted Inspection lessons learned. CR 385609 documents the equipment issue, identified during a fuse log audit. Correct fuses were installed under WOT 02135437-01. . <I> **** Actions Taken **** Notified the Quality Manager and Quality Services Supervisor of condition. .
385652 | CR | 20181011 |  | 3 | (Non EN/CGS) Customer Email Notification of 7 NCR's |  |  |  | N | NO | <D> **** Detailed Description **** Non EN/CGS Customer contacted ENSL that they had 7 NCR's awaiting resolution and was looking for status of them. ENSL was unaware of these NCR's. It was determined that ENSL had not been notified through the proper channels of these NCR's. The customer then provided and email listing all 7 of them. Recommend assignment to AR-CALSERV. Recommend Severity 3. <I> **** Actions Taken **** Initiated Customer Complaint 160 and CR to track and trend.
385653 | CR | 20181011 | CAQ | D | Received FCP-2, 4-3 Fire Alarm. | N | N |  | N | YES | <D> **** Detailed Description **** Received FCP-2, 4-3 Fire Alarm, Sys 8 Wet Pipe TG Bldg 471â€™ RFW Heater Bay. The alarm will not reset. OPS 3 reports there is no evidence of smoke, fire or water flow. <I> **** Actions Taken **** Notified the CRS. Tour conducted by camera due to elevated dose rates. | 02-00-FP-CP-FCP2,02-00-FP-FS-8
385655 | CR | 20181011 |  | 4 | TMU-M-P/1A conduit for I&C thermocouple wires is broken | N | N |  | N | YES | <D> **** Detailed Description **** The conduit for I&C's thermocouple wires is broken at a fitting. Needs fixed/replaced will their thermocouple wires are still determed <I> **** Actions Taken **** informed supervisor, took pictures, initiated CR | 02-00-TMU-M-P/1A
385656 | CR | 20181011 |  | 4 | S5 Leak - HP Turb Exhaust to cross under pipe to MSR A | N | N |  | N | NO | <D> **** Detailed Description **** During a steam leak investigation of GV/1, a large (S5) steam leak was found at the base of the steam chest and the HP turb exhaust to cross under piping to MSR A. See EDMS for pictures Entry into the 501 turbine deck was made due to increased audible steam leak that was thought to be from the previously identified leak on GV/1 <I> **** Actions Taken **** Notified Shift manager . This steam leak does result in lost MWe and higher plant water usage. | 02-00-MS-DT-HP,02-00-MS-HX-1A
385657 | CR | 20181011 |  | 3 | PPM15.2.49 Function and Sensitivity check of VESDA | N | N |  | N | YES | <D> **** Detailed Description **** When craft was performing the commissioning the VESDA system in WO #02116227-01 under PPM 15.2.49, they received a Pre-Alarm on drop 16-3 with a Vesda Trouble on drop 11-5 on FCP3 while performing step 7.3.22, when enough test smoke sent the system into alarm and the craft received a proper indication on FCP1 drop16-1. FCP1 drop 16-1 fire stays locked in and will not clear. <I> **** Actions Taken **** Craft stop work notified supervision of the unexpected additional alarm received. Engineering, Control Room was also notified. Supervisor advised craft to reset system to see if Vesda Trouble on FCP3 drop 11-5 clears Craft resets system and FCP3 drop 11-5 clears with drop 16-3, but on FCP1 drop 16-1 fire stays locked in and will not clear. Advised engineering and Control Room unable to proceed with PPM 15.2.49 and CR was initiated. <N> **** Equipment Description **** RW 467 L9/13.2 | 02-00-FP-CP-ISD/1
385658 | CR | 20181011 |  | 3 | OI-41 Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** OI-41, Att 7.4, only references ODCM 6.1.2, Function 3a for PRM-RE-11. LCS Basis was revised Jan '18 under Rev 101 to include PRM-RE-11 along with the previously noted PRM-RE-12 and PRM-RE-13 as LCS 1.3.3.1, Function 19, related equipment. Recommend revision to OI-41 to reference LCS 1.3.3.1 PAM, Function 19 for PRM-RE-11.
385659 | CR | 20181011 |  | 4 | Personal vehicle contact |  |  |  | N | NO | <D> **** Detailed Description **** An employee contacted another employees vehicle in the Kootenai parking lot. No company vehicles or property were involved or damaged. There were no injuries. <I> **** Actions Taken **** Notified Industrial Safety, Security, and Management of both individuals.
385660 | CR | 20181011 | CAQ | D | CRD-CB-P1A some MOC switch contacts at or near the edge | Y | N |  | N | YES | <D> Some of the MOC switch contacts between the contact fingers and the contacts on the roller are at or near the edge. Pictures documented in the W.O. Evaluate future linkage adjustment. <I> Supervisor, Compont Manager and Engineering informed and pictures reviewed. Generated C.R. and referenced in the W.O. . Found CR at INPROG, moved to APPROVED. | 02-00-CRD-CB-P1A
385661 | CR | 20181011 |  | 4 | SA-C-1 was observed to have high discharge temperature | N | N |  | N | YES | <D> **** Detailed Description **** OPS 2 reported that SA-C-1 has high discharge temperature of 219Â°F with a log spec of 210Â°F. OPS 2 verified cooling line up. Please investigate and correct high temperature. <I> **** Actions Taken **** Secured SA-C-1, Placed CAS-C-1A in service, place CAS-DY-2A in service. | 02-00-SA-C-1
385662 | CR | 20181011 |  | 4 | Security BRE33 camera | N | N |  | N | YES | <D> **** Detailed Description **** Security BRE33 camera not functioning as designed <I> **** Actions Taken **** CR/WR generated <N> **** Equipment Description **** Security BRE33 in N.E. corner of Protected Area. Camera on top of BRE
385663 | CR | 20181012 |  | 4 | RWCU-RST-70A | N | N |  | N | YES | <D> **** Detailed Description **** RWCU resin trap D/P is rising rapidly following precoat. demin 1A and the resin trap were backwashed 10/9 and placed back in service with a fresh precoat 10/10/18. D/P was approx 8.2 at 1930 with demin D/P at 1, and rose to 9 psid by 0400. RWCU flow was lowered thru the A demin to 120 gpm to avoid the high d/p alarm. current D/P on the resin trap is 7 psid, and demin D/P is 1 PSID. recommend fill and vent of the instrument and/or investigation for septa breakthru <I> **** Actions Taken **** informed MCR and chemistry initiated CR/WR | 02-00-RWCU-RST-70A
385664 | CR | 20181012 |  | 3 | Asset Suite Title inaccuracies for ISOs issued in 2016 |  |  |  | N | NO | <D> ACTIVE status CVI ISO 317-00,5994 R000 was ISSUED 10/06/16 but its Asset Suite 'Title:' still errantly includes "HISTORICAL INFORMATION: NOT UPDATED" and its Notes (GENERAL Notes) still errantly say "THIS DOCUMENT WAS STATUSED "HISTORICAL INFORMATION" IN THE LEGACY DOCUMENT CONTROL SYSTEM (DCS)". This is also the case for ACTIVE status CVI ISO 317-00,5995 R000 (ISSUED 10/06/2016) and ACTIVE status CVI ISO 317-00,5996,1 R000 (ISSUED 09/07/2016). Finally, 'CORROSION' is misspelled in the Asset Suite 'Title:' for ACTIVE status CVI ISO 317-00,5993 R001. For resolution: CVI ISO 317-00,5993 â€“ change the Asset Suite â€˜Title:â€™ field from "CORRESION COUPON LOOP STBY SW PUMP HOUSE 1B 3/4" SW (46)-2-1" to "CORROSION COUPON LOOP STBY SW PUMP HOUSE 1B 3/4"SW(46)-2-1" CVI ISO 317-00,5994 â€“ change the Asset Suite â€˜Title:â€™ field from "HISTORICAL INFORMATION: NOT UPDATED PIPING ISOMETRICS CORROSION COUPN LOOP B" to "CORROSION COUPON LOOP STBY SW PUMP HOUSE 1B 3/4"PS(46)-2" CVI ISO 317-00,5995 â€“ change the Asset Suite â€˜Title:â€™ field from "HISTORICAL INFORMATION: NOT UPDATED PIPING ISOMETRIC CORROSION COUPON LOOP B" to "CORROSION COUPON LOOP STBY SW PUMP HOUSE 1B (FURNISHED BY CALGON)" CVI ISO 317-00,5996,1 â€“ change the Asset Suite â€˜Title:â€™ field from "HISTORICAL INFORMATION: NOT UPDATED PIPING ISOMETRIC CORROSION COUPON LOOP DISCHARGE TO PUMP PIT B" to "CORROSION COUPON LOOP DISCHARGE TO PUMP PIT STBY SW PUMP HOUSE 1B" Additionally, delete entirely the X293 â€˜Notesâ€™ (GENERAL NOTES) for CVI ISO 317-00,5994 and CVI ISO 317-00,5995 and CVI ISO 317-00,5996,1. . Suggest resolution by Records and Information Management (RIM). As an alternative, provide the necessary Asset Suite rights to the originator of this AR CR 385664 to be able to make these sorts of administrative corrections without requiring RIM staff assistance. <I> While generating this AR CR 385664 from the CR Initiation Wizard, an Asset Suite abend occurred and the CR became stuck at INPROG status. It is ready now and needs to be pushed along to APPROVED status. <N> This condition was observed while performing document reviews associated with AR EVAL 302752. A quick query identified 2 other documents with the same issues. The document titles have been corrected and the general notes have been deleted. No further actions are required. | 02-00-B-BLDG-MISC
385665 | CR | 20181012 |  | 3 | R5 calibrated bucket for determining leakage cracked/ broken | Y | N |  | N | NO | <D> **** Detailed Description **** The 'calibrated' container used for determining 'Identified"drywell leakage is cracked/ broken. The HEPA filter and the inlet piping sit at odd angles, causing the lid through which they protrude to break/ crack. The drain valve should also be replaced, as it moves very loosely and is difficult to verify valve is fully shut. The entire unit is an FME/ contamination concern <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** The bucket assembly used at the R5 EDR sump | 02-00-EDR-SUMP-R5
385666 | CR | 20181012 |  | 4 | Wrong type of fuse installed | N | N |  | N | YES | <D> **** Detailed Description **** During a recent motor starter inspection, a control power fuse was replaced with an incorrect type of fuse. Per drawing E528-39A, the control power fuse for EDR-42-8CA1D is to be a model ATM, A6Y, F60C, or KTK fuse with a 3 amp rating. Per the fuse log entry, an ATM-3 fuse was replaced with a FNQ-3. While the fuse has the correct amp rating, the fuse time curves are different. The ATM is a fast blow fuse while the FNQ is a time delay. In this case, the fuse may not clear quickly enough which could result in other starter components being damaged from the overcurrent. Recommend replacing the control power fuse with correct type. | 02-00-EDR-42-8CA1D,02-00-EDR-P-5A,02-00-EDR-P-5B
385667 | CR | 20181012 |  | 4 | Gate Latch Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** The gate latch on the outer delay fence located near zone 23 requires maintenance. The gate is currently being secured by a chain/lock. Contact 2185 for more information. <I> **** Actions Taken **** Security supervision notified. Gate secured by a chain. Initiate CR/WR. <N> **** Equipment Description **** Personnel gate in cooling tower area in vacinity of zone 23 .
385668 | CR | 20181012 | CAQ | C | Possible motor starter degradation -- RCC-42-8C7B | Y | N |  | N | YES | <D> **** Detailed Description **** The control power fuse for RCC-42-8C7B, motor starter for RCC-V-71, has cleared twice in a four month span. Valve indication was lost on 4/23/18 and again on 8/21/18. Both times, the loss of indication was due to the starter control power fuse clearing. Recommend system engineering consider doing additional investigation of the motor starter to determine why the fuse keeps clearing. The next starter inspection PM is currently scheduled for summer 2019. | 02-00-RCC-42-8C7B,02-00-RCC-V-71C
385669 | CR | 20181012 | CAQ | C | Design Spec 15B.1 does not include PS(46) design conditions | Y | N |  | N | YES | <D> **** Detailed Description **** Non-ASME Piping Design Specification AED SPC 15B.1 does not currently include Table 1 Design Condition information for PS(46)-2 or PS(46)-1 piping. Non-ASME QC 2 PS(46)-2 and PS(46)-1 piping exists downstream of SW-SV-918 as part of the SW B corrosion monitoring station in SWPH B (reference AED MEC M524-3 and BDC 86-0068-0A). The AED SPC 15B.1 Table 1 Design Condition information for the PS(46)-2 piping should be identical to that for the upstream SW(46)-2 and SW(49)-2 piping (i.e., identical to the SW(All)-2 information provided by ASME piping Design Specification 1 Table 1 (AED SPC 1 page Section 1-067)). However, AED SPC 15B.1 Table 1 Design Condition information for the PS(46)-1 piping will need to be determined. Once this design condition information is formally determined, AED SPC 15B.1 will need to be updated. Also, the CVI ISO 317-00,5993 and CVI ISO 317-00,5994 and CVI ISO 317-00,5995 and CVI ISO 317-00,5996,1 Design Temp and Design Press information will need to be updated accordingly. This is an administrative issue only. As recently discussed as part of AR CR 385584, this SW B corrosion monitoring loop piping was qualified with words in BDC 86-0068-0A - there is no concern regarding its continued function, operation, or qualification. <N> This is a legacy issue associated with BDC 86-0068-0A - suggest resolution assignment to Design Engineering Mechanical Design Basis group. | 02-00-PS-RO-1,02-00-SW-SV-918
385670 | CR | 20181012 |  | 3 | 2018 Dress Rehearsal TFOF Simulated Engagements |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate the conditions that led to the simulated neutralizations of security response players during the conduct of 2018 Dress Rehearsal FOF Exercise. <I> **** Actions Taken **** Security Programs Management notified.
385671 | CR | 20181012 |  | 3 | ODMI Action Value reached: COND-V-156B upstream connection | N | N |  | N | YES | <D> **** Detailed Description **** While performing OPS-3 temp. log, leak rate of COND-V-156B upstream threaded connection was measured at approximately 600mL/min. There is an ODMI action level when leak rate reaches 500mL/min. Action level states to write CR, increase leak rate monitoring to daily, and to hold a Challenge Meeting to plan for down power to repair. Leak rate is difficult to measure based on leak location and minimal elevation change from leak/catch to ground level. Because of this, leak rate was measured several times to eliminate variables and validate initial rate. Original AR#383881 <I> **** Actions Taken **** Notified SM | 02-00-COND-P-2B,02-00-COND-V-156B
385672 | CR | 20181012 | CAQ | D | FP-P-110 coolant leak when pump started | N | Y |  | N | YES | <D> **** Detailed Description **** During PPM 15.1.4, FP-P-110 developed a coolant leak. Approximately 30 seconds after the engine started, coolant began spraying out of what looks like an upward-facing weep hole on the brass-colored connection between the coolant tank and the piping. The local pump control switch was immediately taken to OFF and the MCR was informed. The leak stopped when the pump was secured. The pump was left in OFF. Pictures attached. <I> **** Actions Taken **** Secured the pump. Informed Supervision and MCR. Wrote CR. | 02-00-FP-ENG-110,02-00-FP-P-110
385673 | CR | 20181012 |  | 4 | Wasps at TMU Pumphouse | N | N |  | N | NO | <D> **** Detailed Description **** There are many wasps at the TMU pumphouse between the door and the locked gate. I was not able to identify the location of the nest. <I> **** Actions Taken **** Wrote CR. Informed supervision. | 02-00-M-BLDG-MISC
385674 | CR | 20181012 | CAQ | D | LCS 1.8.6.2.A 2hr completion time not met due to maintenance | Y | Y |  | N | NO | <D> **** Detailed Description **** During performance of HPCS-C1-1 repairs per WO 02135468 the charger was removed from service with no temporary power as planned. HPCS-B1-DG3 voltage dropped below 126VDC which required declaring the battery inoperable and entry into TS 3.8.4.E and LCS 1.8.6.2.A. The required completion time for LCS 1.8.6.2.A.1 is 2 hrs and requires verification that float voltage is GE 126 VDC which was not met due to the duration of the maintenance. HPCS-B1 -DG3 has already been declared inoperable and will be restored per WO 02135468 following repairs to HPCS-C1-1. This CR is written to satisfy LCS 1.8.6.2.I.1. <I> **** Actions Taken **** Initiated CR. CRS/SM informed. | 02-00-HPCS-B1-DG3,02-00-HPCS-C1-1
385675 | CR | 20181013 |  | 4 | Oscillograph start alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Startup and Backup voltages are as follows: E-TR-S A: 239 B: 240 C: 240, E-TR-B A: 118 B: 118 C: 117. The following sensors were tripped and are reset: J7; 500KV Neutral Ground Overcurrent. BPA reports the following: a. Cause was Ashe-Marion #2 line trip. b. Relaying involved a single pole "C" phase. c. nothing damaged. d. line reclosed. e. no emergent outage needed. f. 230kv or 115kv not involved. g. N/A h. N/A i. 0412 j. 500KV. k. No RAS. l. N/A.
385677 | CR | 20181013 | CAQ | D | DSA-V-77B is not opening fully and should be replaced | Y | N |  | N | YES | <D> **** Detailed Description **** DSA-V-77B is the normally closed desiccant dryer drain / blow down valve. DSA-V-77B will open just enough to blow down the DG2 desiccant air dryer, however, the further the ball valve is opened the more the air flow decreases. The ball valve needs to be replaced. <I> **** Actions Taken **** informed Shift Support Supervisor <N> **** Equipment Description **** DG2 desiccant air dryer blow down / drain valve | 02-00-DSA-V-77B
385678 | CR | 20181013 |  | 4 | Handle Broken on E-CB-LP3CB | N | N |  | N | YES | <D> **** Detailed Description **** Handle Broken on E-CB-LP3CB Door. Panel is located in the NW corner of the Transformer Yard. While performing a Clearance Order Tag Audit, it was discovered that the Lighting Panel Door could not be opened due to the handle being broken. <I> **** Actions Taken **** CR/WR Generated. Suervision Notified. Non-essential lighting. <N> **** Equipment Description **** Handle broken on E-CB-LP3CB Door
385679 | CR | 20181013 |  | 4 | The Rx 606â€™ floor coating needs inspected for paint chipping | N | N |  | N | NO | <D> **** Detailed Description **** On the 606 there are a few locations that the floor coating needs to be touched up with new coating. The paint chips show bare cement and small area cracking. Please inspect and repair as necessary. <I> **** Actions Taken **** informed Shift Support Supervisor <N> **** Equipment Description **** Rx Building 606 floor coating | 02-00-R-BLDG-MISC
385680 | CR | 20181013 | CAQ | D | had to calibrate RCIC-DPIS-13A, SAT | Y | N |  | Y | YES | <D> **** Detailed Description **** While performing WO#02102737 ISP-RCIC-Q901,we had to calibrate both switches on RCIC-DPIS-13A. The high switch 1 was AF trip 218 "H2O, limits were 220 to 225 "H20. Adjusted to 222 "H2O SAT. The Low switch 2 was AF trip -190 "H2O. Limits were -200 to-205 "H2O. Adjusted to -203 "H2O SAT. <I> **** Actions Taken **** adjusted switches within tolerance and wrote this AR | 02-00-RCIC-DPIS-13A
385681 | CR | 20181013 |  | 3 | ISP-RCIC-Q901 procedure enhancement. |  |  |  | N | NO | <D> **** Detailed Description **** Under section 3.3.1 the following annunciator should be added: H13-P601.A11-3.1 "Steam Supply Bypass RCIC-V-76 Not Full Closed. <I> **** Actions Taken **** This <N> **** Equipment Description **** Procedure . Revision request has been uploaded to the Maintenace Procedure database to be included in next major rev. See EDMS for link.
385682 | CR | 20181013 |  | 4 | Absorbent Pillows in FDR-SUMP-T5 need replacing. | N | N |  | N | YES | <D> **** Detailed Description **** While performing inspectiion of EDR and FDR sump absorbent pillows it was noted that the absorbent pillows in FDR -SUMP-T5 need replacing. <I> **** Actions Taken **** write a CR/WR, inform CRS. | 02-00-FDR-SUMP-T5
385683 | CR | 20181013 |  | 4 | FD-SUMP-T2 water looks murky. | N | N |  | N | YES | <D> **** Detailed Description **** while performing the absorbent pillow inspection it was noted that the water in FD-DUMP-T2 looked murky, it may be getting some oil in the sump coming from CAS compressors. <I> **** Actions Taken **** informed CRS and initiated CR. | 02-00-FD-SUMP-T2
385684 | CR | 20181014 | CAQ | D | ARM-RIS-33 Has Failed | N | Y |  | N | YES | <D> **** Detailed Description **** At approximately 0310 on 10/14/18 ARM-RIS-33 had a momentary spike to 9.0 E-1 Rem/Hr this was reset then shortly after a spike to 3.5E-0 Rem/Hr, this was also reset. The green operate light did not illuminate when the trip light was reset as was expected. Field investigation reported that the power light for ARM-RIS-33 was not illuminated. This appears to be a power supply failure. <I> **** Actions Taken **** CR, informed EP. | 02-00-ARM-RIS-33
385687 | CR | 20181014 |  | 2 | (Plant Evaluation) - Risk of Operational Events |  |  |  | N | NO | <C> Reopened to add final Effectiveness Review Plan document at OPS request, then taken back to complete. Reopened at the request of OPS. <D> **** Detailed Description **** An external evaluation identified an area for improvement where Operations, Maintenance, and Projects personnel do not consistently ensure the risk of operational events is identified and mitigating actions or margin established, prior to performing some plant activities. This has resulted in chemistry excursions that challenge the integrity of the fuel cladding, required a plant power reduction, delayed plant startup and inoperable safety related equipment. Contributing is department managers have not established an environment that ensures roles and responsibilities for the prevention of operational events are understood and reinforced. This condition does not directly affect any plant equipment. <I> **** Actions Taken **** Leadership team briefed. No immediate or urgent actions are required.
385688 | CR | 20181014 |  | 2 | (Plant Evaluation) - Maintenance Fundamentals |  |  |  | N | NO | <D> **** Detailed Description **** An external evaluation identified an area for improvement where station and supplemental mechanics do not apply proper maintenance technical fundamentals for working on mechanical joints in some cases. This has resulted in unresolved leaks on safety related equipment, rework, and addtional out of service time for plant equipment. Contributing, technical fundamentals, such as those required to assemble mechanical joints correctly, have not been routinely reinforced. This condition does not directly affect any plant equipment. <I> **** Actions Taken **** Leadership team briefed. No immediate actions are required.
385689 | CR | 20181014 |  | 2 | (Plant Evaluation) - Leader Intrusiveness in Equipment |  |  |  | N | NO | <D> **** Detailed Description **** An external evaluation identified an area for improvement where Engineering, Maintenance, and Operations supervisors did not ensure timely actions were implemented to prevent equipment failures, adequately mitigate risk, and did not provide intrusive oversight during trending to identify off-normal conditions with degraded equipment. This has resulted in a manual reactor scram, unplanned down power, and has the potential to result in inoperable safety equipment. Contributing is Engineering managers and other station leaders are not reinforcing fundamentals and providing engaged oversight of equipment reliability processes. This condition has no immediate or direct affect on plant equipment. <I> **** Actions Taken **** Leadership team briefed. No immediate actions are required.
385690 | CR | 20181014 |  | 2 | (Plant Evaluation) - Industrial Safety |  |  |  | N | NO | <D> **** Detailed Description **** An external evaluation identified an area for improvement where workers are not recognizing hazards while performing work in some instances. This resulted in recordable injuries and the potential for more consequential events. Contributing is supervisors are not engaging workers or addressing deviations until after events occur. This condition does not have any immediate or direct affect on plant equipment. <I> **** Actions Taken **** Leadership team briefed. No further immediate actions required.
385691 | CR | 20181014 |  | 2 | (Plant Evaluation) - Leader Fundamental Interventions |  |  |  | N | NO | <D> **** Detailed Description **** An external evaluation identified an area for improvement where managers and supervisors do not consistently take prompt action to intervene and use early warning signs to correct organizational and behavioral weaknesses. As a result, improvement in key focus areas has been slow or not sustained, leading to ongoing risks to equipment challenges and worker injuries. Contributing, key managers do not reinforce a bias for prompt action in response to precursor events to drive desired work fundamental behaviors that foster high levels of performance. This condition does not directly affect plant equipment. <I> **** Actions Taken **** Leadership team briefed. No further immediate actions required.
385692 | CR | 20181014 |  | 3 | Clarification needed for entry into sop-coldweather-ops |  |  |  | N | NO | <D> **** Detailed Description **** Step 6.1.1c of SOP-COLDWEATER-OPS directs verifying heat trace circuits have been functionally checked by annual PM's. A list of PMID's is also listed under the step. Need verification that these PM's have been completed so the heat traces can be turned on due to the cold weather we are starting to experience. <I> **** Actions Taken **** Initiated CR
385693 | CR | 20181014 |  | 4 | Received â€œThrust Bearing High B Trip" from DEH | N | N |  | N | YES | <D> **** Detailed Description **** 1605 received â€œThrust Bearing High B Trip". 1606 received â€œThrust bearing position B fail lowâ€, â€œThrust bearing Low B tripâ€, and â€œThrust bearing position B fail highâ€ <I> **** Actions Taken **** All parameters on TG-XR-TSI and TG-TR-48 were normal and steady. The transmitter selection screen shows everything Normal for thrust bearing inputs. The alarms were acknowledged and stayed cleared Request Engineering input on bypassing DEH input. | 02-00-E-GEN-1,02-00-TG-DET-TP/B
385694 | CR | 20181014 |  | 4 | WO 02132271 planning issues |  |  |  | N | NO | <D> **** Detailed Description **** WO 02132271 planning issues for RHR-B outage on 10-15-19. Task 01 the system overview contained information on a past RHR-A outage and referenced incorrect WO's as well as scope. Task 02 had an incorrect Paragon variable in the requirments screen for RHR-A. FPE's plannaned and listed as required were not required to be implemented due to outage duration however this is not reflected in the planning for task 01 and are listed as required. <I> **** Actions Taken **** returned task 01. corrected task 02 Paragon variable for RHR-B Contacted WWM and fire marshal to discuss requirments for FPE's and outage duration.
385695 | CR | 20181014 |  | 4 | PWC-P-2 leaking from swagelok fitting for seal injection | N | N |  | N | YES | <D> **** Detailed Description **** PWC-P-2 has a swagelok fitting that is spraying onto the skid from the seal injection/cooling line off the pump. Causing housekeeping issue in Service Building basement inside RCA. <I> **** Actions Taken **** Notified CRS and HP. Redirected spray to prevent potential for electrical hazards. | 02-00-PWC-P-2
385696 | CR | 20181014 |  | 4 | COND-V-206C did not open | N | N |  | N | YES | <D> **** Detailed Description **** uring precoat of CFD-â€œCâ€ COND-V-206C failed to open during step 42(precoat) of the backwash/precoat drum timer. This caused CF-TK-4 to overflow. After a period of time COND -V-206C opened with no operator action and level in CF-TK-4 dropped rapidly and had to be refilled with the local precoat tank fill valve. CFD-"C" was placed in a safe condition. <I> **** Actions Taken **** Informed MCR of issue | 02-00-CF-TK-4,02-00-COND-V-206C
385697 | CR | 20181015 | CAQ | C | DW Oxygen Concentration Rising | Y | N |  | N | YES | <D> **** Detailed Description **** DW Oxygen concentration is rising, see attached eDNA plot. Investigate potential sources for a leak (CMS-SR-13 and 14, etc). Leak appears to have started on 10/13/18. <I> **** Actions Taken **** Informed CRS, started a N2 feed and bleed to lower O2 concentration LT 2.5%. | 02-00-C-TK-1,02-00-CMS-SR-13,02-00-CMS-SR-14,02-00-CMS-SR-21
385698 | CR | 20181015 |  | 4 | Camera cleaning around PA | N | N |  | Y | YES | <D> **** Detailed Description **** following cameras needing cleaning: CCTV 01,03T,04,07,07T ,08,10,11,11T,12T,13,13T,20,33T,60T,61T <I> **** Actions Taken **** Generated list, notified supervision, WR/CR generated <N> **** Equipment Description **** Varias cameras needed to be cleaned in the protected area | 02-00-SEC-CCTV-1,02-00-SEC-CCTV-10,02-00-SEC-CCTV-11,02-00-SEC-CCTV-11T,02-00-SEC-CCTV-12T,02-00-SEC-CCTV-13,02-00-SEC-CCTV-13T,02-00-SEC-CCTV-20,02-00-SEC-CCTV-33T,02-00-SEC-CCTV-3T,02-00-SEC-CCTV-4,02-00-SEC-CCTV-60T,02-00-SEC-CCTV-61T,02-00-SEC-CCTV-7,02-00-SEC-CCTV-7T,02-00-SEC-CCTV-8
385703 | CR | 20181015 | CAQ | D | 4 Pieces of M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** 4 RM Young Probes for the Met Tower were found OOT. EFIN Eval: Calcode #0063113 RH/Temp Probe- model 41372LF. ICP-MET-S302 Met tower 245' temperature failure was differential was not within .18 degrees F, actual delta was <.25. FSAR section 2.3.3.2.4 lists a met tower temperature differential acceptance criteria of +/- 0.36 degrees F. DEF #6751A written. Calcode #0063342 Temp Probe- model 41342LF. ICP-MET-S302 Met tower 33' temperature failure was differential was not within .18 degrees F, actual delta was <.21. FSAR section 2.3.3.2.4 lists a met tower temperature differential acceptance criteria of +/- 0.36 degrees F. DEF #6752A written. Calcode #0064645 RH/Temp Probe- model 41372LF. ICP-MET-S302 Met tower 245' temperature failure was differential was not within .18 degrees F due to its matched pair MET-TE-11B RTD failed. Review of EDNA data shows this TE indcation matched MET-TE-11A prior to failure. DEF#6753A written. Calcode #0064289 Temp Probe- model 41342LF. CP-MET-S302 Met tower 33' temperature MET -TE-10A RTD failed. Failure was indicated by data showing pegged high. Review of EDNA data shows this TE indication matched MET-TE-10B prior to failure. Rejected- replacement probe purchased & Calibrated. DEF #6754A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only. eFIN identified no issues where used.
385704 | CR | 20181015 |  | 4 | TMU-M-P/1A bottom thermal couple pipe threads are pulled out | N | N |  | N | YES | <D> **** Detailed Description **** The threads are pulled out where the thermal couple meets the mounting plate. It was only origionally threaded in one thread. <I> **** Actions Taken **** Contacted fin wrote AR | 02-00-TMU-M-P/1A
385710 | CR | 20181015 |  | 4 | Critical Group Clinical Evaluation Meeting Missed |  |  |  | N | NO | <D> **** Detailed Description **** Employee did not attend a Clinical Evaluation Meeting scheduled in support of Critical Group Reinvestigation. This will require rework and the clinical evaluation Meeting to be rescheduled. <I> **** Actions Taken **** Supervisor notified. Coaching was provided. Clinical Evaluation Meeting will be coordinated and re-scheduled by Access Authorization.
385711 | CR | 20181015 |  | 3 | SOP-TMU-SHUTDOWN change to TMU pump trip |  |  |  | N | NO | <D> **** Detailed Description **** SOP-TMU-SHUTDOWN Precautions and Limitations (Section 4.5) indicate that a spurious signal from TMU-LT-1B may result in a pump trip; however, this auto-trip function was removed from the TMU pump trip logic by EC 11873. Recommend revising the Precautions and Limitations (Section 4.5) to reflect the change in trip logic. Note: The Precautions and Limitations, Section 4.1, has already incorporated this change in trip logic. | 02-00-TMU-LT-1B
385714 | CR | 20181015 |  | 3 | INPO NISP-RP procedure reviews |  |  |  | N | NO | <D> **** Detailed Description **** Radiation Protection was tasked with adherence to implement INPO NISP procedures in early 2018. Since the original implementation 4 identified NISP procedures have been revised since that implementation. There is currently no process in place to ensure timely review and updating of site procedures to align with these NISP-RP-xxx procedure revision. The CR is being generated to evaluate and determine if a process is needed that reviews NISP revisions and complete implementation. <I> **** Actions Taken **** Reviewed 2 procedures and identified the need for peer evaluation. Notified RP-Supervision
385715 | CR | 20181015 |  | 4 | Two 1.2 mile Exclusion Area signs down |  |  |  | N | NO | <D> **** Detailed Description **** Two 1.2 mile Exclusion Area sign poles need replaced. The support poles are snapped off near the ground. Locations are (N. Lattitude 46 27 38 // W. Longitude 119 18 25) and (N. Lattitude 46 29 07 // W. Longitude 119 19 29). The mechanisms of failure appear to be fire damage / dry rot weakening, followed by high winds. The support posts need replaced and the signs reposted. <I> **** Actions Taken **** Informed Facilities. Informed EP manager. <N> **** Equipment Description **** Two Exclusion Area Signs - See Detailed Description for loc ations.
385716 | CR | 20181015 |  | 3 | Incorrect RWP for floor plug removal. |  |  |  | N | NO | <D> **** Detailed Description **** While trying to log into the RWP for removal of the floor plug for WO 02114503-01 it was determined that the RWP needed to be a High Rad RWP due to the dose rates when the plug is removed. This caused a delay in getting started with the removal. <I> **** Actions Taken **** CR generated for documentation | 02-00-R-BLDG-MISC
385718 | CR | 20181015 |  | 4 | Plexiglas vs. Lexan for coupling guards. |  |  |  | N | NO | <D> **** Detailed Description **** During the prefabrication portion of WO 02115308-01 it was noticed that one of the pre-cut was Plexiglas when it cracked when installing the latch. Another piece had to be cut from Lexan which caused a delay in the installation. <I> **** Actions Taken **** CR generated for trending
385719 | CR | 20181015 | CAQ | D | Received RHR B low pressure alarm | Y | N |  | N | YES | <D> **** Detailed Description **** Received RHR B low pressure alarm while throttling open RHR-V-24B for the electricians during the RHR B outage. Lowest pressure on Tdas pt X076 was 57.5 psig, pressure recovered to 110 psig by RHR-P-3. CRS has taken steps to perform a fill and vent of the system by placing a note on the LCO sheet. | 02-00-RHR-V-24B
385720 | CR | 20181015 |  | 3 | unable to start ISP-MS-Q920 because of RHR outage |  |  |  | N | NO | <D> **** Detailed Description **** We were unable to start ISP-MS-Q920 CFT (WO#02103050-01) because there is an RHR-B outage. Steps 7.1.1 and 7.2.1 state â€œIF Reactor is in Operational Modes 1, 2, or 3, THEN VERIFY with operations that RHR system is in normal standby condition.â€ Operations informed me RHR is NOT in a normal standby conditions. Either these steps need to be eliminated, or there should be a prerequisite to VERIFY RHR system is in normal standby condition. <I> **** Actions Taken **** Stopped and talked to our supervisor. We were informed to stop the job. Informed operations that we are stopped. We staged all our test equipment in a safe condition near PO27. wrote this AR This CR should be screened to AR-MNTPROC to fix the procedure issue. <N> **** Equipment Description **** isp-ms-q920
385721 | CR | 20181015 | CAQ | C | RHR-MO-48B Full PM | Y | Y |  | N | YES | <D> **** Detailed Description **** **Good Catch** The Full PM for RHR-MO-48B identified the following issues when performing PPM 10.25.4: (1) The Limitorque actuator mounting bolts to valve yoke where not captured per procedure (staked, captured, lock wired, or had torque paint applied). (2) The torque switch mounting bolts were loose. <I> **** Actions Taken **** RHR-MO-48B actuator was refurbished in R22 (2015) via WO 02048821-01. The full PM is performed to inspect the actuator for degradation. (1) Refurb WO 02048821-01 identifies the actuator mounting bolts were torqued & verified by QC. Maintenance did not identify any bolt looseness when performing the Full PM. Maintenance resolved the issue by verifying the mounting bolts were torqued and correctly marked for future PMâ€™s. (2) Refurb WO 02048821-01 documented the torque switch was installed and peer checked per procedure. Additionally, as-left diagnostic WO 02048821-03 adjusted the torque switch to meet the minimum required values and did not identify any issues (switch setting from 1 to 2.25 (as-left setting)). The full PM WO identified the as-found setting to be 2.25 (no changes). To correct the issue, Maintenance tightened torque switch mounting screws. ** This condition was corrected. ** Level 1, 2 and 2a are currently required for the full PM. This leaves Level 6 eval: WO 02048821-03 (as-left) close torque switch setting was the same setting (2.25) as found during the Full PM performed on 10/15/2018. The as-left margin was 309.8% margin. MOVPP-01 states that high margin is anything greater than 10%. Therefore there is sufficient available margin in the closed direction to address any minor changes in thrust if any. The open direction is control by a limit switch. | 02-00-RHR-MO-48B
385722 | CR | 20181015 |  | 4 | BLDG192 Monaco Fire Transmitter is Drifting Off Frequency |  |  |  | N | YES | <D> **** Detailed Description **** While performing Preventative Maintenance WO #02102745-01, it was discovered the Monaco Fire Transmitter in Building 192 is drifting off the recommended frequency error specification. The system is operational, but the transmitter should be removed, replaced with a spare and sent to the factory for repair before a communication errors occur. <I> **** Actions Taken **** Notified Supervisor and Fire Protection. Created CR. Recommend closing to WR. ITMGMT. <N> **** Equipment Description **** Building 192 - Monaco Fire Transmitter
385724 | CR | 20181015 | CAQ | C | Need drawing changes on AED-EWD-EWD-81E-005, EWD-9E-118 |  |  |  | N | NO | <D> **** Detailed Description **** Need drawing changes on AED-EWD-EWD-81E-005, AED-EWD -EWD -9E-118. AED-EWD-EWD-81E-005 change EPN E-RLY-80/FN/3 to EPN E-RLY-80/FN3. AED-EWD -EWD-9E-118 change EPN E-RLY -80/FN/3 to EPN E-RLY-80/FN3 and remove the cloud around the EPN. <I> **** Actions Taken **** Corrected EPN location in Portal J from R522 to RW525. Relay is in E-MC-8F compt. 4c Added EPNs RRA-RLY-80/FN3 and RRA-RLY-80/FN/3 to the EPN cross-references for this AR CR. NOTE: AED ELC E536-2Q indicates RRA-RLY-80/FN3 is SPARE - AED ELC E536-2Q might also need correction. <N> **** Equipment Description **** E-MC-8F compt. 4c E-RLY-80/FN/3 and E-RLY-80/FN3 are not actually EPNs in Asset Suite / MEL. It appears that the intended desired drawing change is from RRA-RLY-80/FN/3 to RRA-RLY-80/FN3. RRA-RLY-809/FN/3 is a NONEQUIP EPN in Asset Suite MEL (duplicate of EPN RRA-RLY-80/FN3). | 02-00-E-MC-8F,02-00-RRA-RLY-80/FN/3,02-00-RRA-RLY-80/FN3
385725 | CR | 20181015 |  | 4 | WCH-V-8 Flange Leak - Radwaste Chiller 51A | N | N |  | N | YES | <D> **** Detailed Description **** During the filling of the WCH piping to new Radwaste Chiller WCH-CR-51A in-prep for testing, significant leakage was experienced at the lower flange of 6" valve WCH-V-8 that could not be remedied with additional torque checks. Note that this flange joint has a new 6" flat faced flange and gasket (garlock) mated to exising flat faced flange of valve WCH-V-8. It will be necessary to disassemble this joint and examine associated surfaces of new and old flanges to determine and correct cause of leakage. This rework has the potential of delaying Vendor startup of this chiller scheduled for 10-17-18. <I> **** Actions Taken **** Notified Responsible Engineer, Planner, SSS via EO's, CRS and SM. Also notified OCC. Planner has initiated WO task 02125913-53 to remove this WCH spool and rework the flange faces and replace the gasket, as necessary. | 02-00-WCH-CR-51A,02-00-WCH-V-8
385726 | CR | 20181015 |  | 3 | CW-CT-1B Missing Concrete Plug | N | N |  | N | YES | <D> **** Detailed Description **** During the semi-annual cooling tower sludge removal (WO 02103279) a worker noted an unexpected hole in the distribution flume of CW-CT-1B. The hole is located North-Northwest in the distribution flume and was described as roughly the size of the individualâ€™s heel (4-5â€ in diameter), and uniform in nature. After further investigation it was determined that this hole is one of the distribution flume clean out holes from initial construction. These holes are no longer used for tower maintenance and per CVI 223-00,15 these holes should contain a polymeric concrete plug during tower operation. Recommend reinstallation of the plug as part of the general cooling tower maintenance in R24 (WO 02071730). Although there is negligible impact on cooling tower operation without the plug in place, the plug should be reinstalled for configuration management and to reduce bypass flow past the cooling tower fill and drift eliminators. See EDMS for pictures and references. | 02-00-CW-CT-1B
385727 | CR | 20181015 |  | 4 | Fatigue Waiver Required |  |  |  | N | NO | <C> CR changed from CAQ/D to Non-CAQ/4 at the request of OFM on 10.18.2018. <D> **** Detailed Description **** A fatigue waiver is required IAW SWP-FFD-04. An extra reactor operator is required for post maintenance testing (PMT) procedures and restoration of a safety related system to return the system to operable status on nights, 10/17. The PMT is an infrequent test on the Remote Shutdown Panel, and a peer checker is warranted due to the elevated risk outside the MCR (main control room). Extension of the TS LCO will elevate the activity to high risk when >50% of 7 day LCO Time Completion has expired. Team was expanded to OPS management, Production/Planning and Shift Management. Discussed all other possible options of moving the in -progress activity which will has the same result. Paid rest was a potential solution but was not available due to on-going arbitration. There are no reactor operators available to perform this activity, including personnel on vacation, with the exception of the subject operator. <I> **** Actions Taken **** Initiated AR, messaged FFD personnel, initiated waiver process.
385728 | CR | 20181015 |  | 4 | TOA-TIS-12B Not Operating Correctly | N | N |  | N | YES | <D> **** Detailed Description **** TGHV-1B had an "Outside Air Temp High & Basin Level Low" alarm. The basin is drained per SOP-COLDWEATHER-OPS, and TOA-TIS-12B was set to 100Â°F. Indicated temperature was 60Â°, so the alarm should not have been present. The alarm cleared when the setpoint was raised to 180Â°, but indicated temperature rose to 80Â°. <I> **** Actions Taken **** Adjusted setpoint per SOP-COLDWEATHER-OPS Informed MCR <N> **** Equipment Description **** T 501 | 02-00-TOA-TIS-12B
385729 | CR | 20181015 | CAQ | D | Cardox Hose Reel Lamp Extinguished | N | N |  | N | YES | <D> **** Detailed Description **** The normally-on lamp by the CO2 hose reel has burned out. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** T 501 West
385732 | CR | 20181016 | CAQ | D | 4.800.C4 7-5 OCB low air pressure. | Y | N |  | N | YES | <D> **** Detailed Description **** 4.800.C4 7-5 (OCB Loss of Air Pressure) received. Ops 4 reported accumulator pressure 110# down slow and the compressor was not running. Normal pressure is 130psig. Ops 4 reported the compressor sounds like it is trying to start. 20 minutes later the compressor started and restored pressure. <I> **** Actions Taken **** WR written <N> **** Equipment Description **** Transformer yard. | 02-00-E-CB-TRB
385737 | CR | 20181016 |  | 3 | SOP-HVAC/WCH-LU is different that the M550-1 | N | N | N | N | NO | <D> **** Detailed Description **** SOP-HVAC/WCH-LU says that WCH-V-660, WCH-V-661, WCH-V-662 and WCH-V-663 should be closed. M550-1 says WCH-V-660, WCH-V-661, WCH-V-662 and WCH-V-663 should be closed and capped. These should be the same. | 02-00-WCH-V-660,02-00-WCH-V-661,02-00-WCH-V-662,02-00-WCH-V-663
385738 | CR | 20181016 |  | 3 | Enhancement for ABN-SRV | N | N | N | N | NO | <D> **** Detailed Description **** CR 385044 documents MS-RV-2A lifting and reseating during performance of ISP-MS/IST-A101. During this event, where MS-RV-2A lifted for ~31 seconds then reclosed, no appreciable change in reactor power was observed. ABN-SRV directs if power is GT 90%, THEN follow the open indication, and reduce power to LE 90% before attempting to close the open SRV. This may not be necessary and could result in unnecessarily prolonging the transient. During the 31 seconds that MS-RV-2A was open, suppression pool temperature rose 4 degrees F. <I> **** Actions Taken **** Discussed with AOM crew and AOM training.
385740 | CR | 20181016 |  | 4 | Grease not available for WO 02114556 RHR-42-8BA5D |  |  |  | N | NO | <D> **** Detailed Description **** Grease CID 32130 was not available for WO 02114556. During performance of work it was determined that the grease required by 10.25.187 was not available for use. In 2015 PPI 10.25.187 OMM manuals were updated and the grease was procured in 2015 however the grease was not cleared for use and had an OSD&D against it, and until performance of WO 02114556 this grease was not needed. No demand was placed against the material as a result the OSD&D was not resolved and without a demand against the material this would never be prioritized for procurement engineering to resolve the OSD&D. A dedication plan was needed from procurement engineering to authorize use of the material during the RHR B maintenance window. <I> **** Actions Taken **** The procurement dedication plant was issued and the grease is available for use. <N> Procurement Evaluation 8588 Revision 0 was developed to dedicate the grease for use on RHR-42-8BA5D on 10/15/18. | 02-00-RHR-42-8BA5D
385741 | CR | 20181016 |  | 3 | Missed Objectives in Training Material |  |  |  | N | NO | <D> **** Detailed Description **** During preparation for continuing training, Maintenance Training identified that ME000551 (taught in 2014) did not contain content necessary to ensure all required objectives were covered. This condition was corrected prior to implementation of ME000632, which covered all objectives required for the identified rotating equipment tasks. This CR is to document the legacy condition and determine extent of condition as appropriate. <I> **** Actions Taken **** Notified Training Management. Initiated extend of condition actions within Maintenance Training.
385742 | CR | 20181016 |  | 3 | Post-training Evaluations not Completed in a Timely Manner | N | N | N | N | NO | <D> **** Detailed Description **** In reviewing completed initial training post-training evaluations from 2018, Maintenance Training identified that ten evaluations failed to meet the timely completion guidance outlined in TDI-02. <I> **** Actions Taken **** Notified Training Management. Provided coaching to responsible training staff. Recommend Severity 3 owed to AR-MTTRN
385745 | CR | 20181016 |  | 4 | Substandard lighting conditions in RW 437â€™ processing area | N | N | N | N | I DONT KNOW | <D> **** Detailed Description **** There are approximately 20 different light fixtures that are either burnt out or have no light bulbs installed at all. Given the type and volume of work being performed and the amount of heavy equipment placed and moved in this area, inadequate lighting could lead to an industrial safety related event. The total number of available light fixtures in this area versus the number of light fixtures that are NOT being utilized is quite disconcerting. <I> **** Actions Taken **** Discussed with Supervision , Instigated CR <N> **** Equipment Description **** RW 437' processing area | 02-00-W-BLDG-MISC
385746 | CR | 20181016 |  | 3 | PPM15.2.49 Function and Sensitivity check of VESDA | N | N |  | N | YES | <D> **** Detailed Description **** When the craft was performing a draft version of the commissioning test for VESDA system WO 02116227 for ISD/2 under PPM 15.2.49 the smoke test from performing step 7.3.22 sent the system into alarm as expected. However, FCP-1 fire alarm stayed locked in and will not clear even after the acknowledgement and reset buttons were pushed. Potential for a failed relay on ISD/2. <I> **** Actions Taken **** Revision to w/o 02116227 to replace broken relay System not yet turned over to operations. <N> **** Equipment Description **** vital island | 02-00-FP-CP-ISD/2
385747 | CR | 20181016 |  | 4 | DataGlance Tablet option not working properly | N | N | N | N | NO | <D> **** Detailed Description **** Operations will check out a package onto the tablet for review and then release the package for operability. When the package is checked back in, the software will sometimes bypass additional review steps and cause the package to be placed in a status that will not progress to the QA record being generated. <I> **** Actions Taken **** Notified Operations that the option for Release for Operability needs to be completed from the desktop version of DataGlance and not on the tablet.
385748 | CR | 20181016 | CAQ | D | Door C-222 not meet criteria PPM 15.3.17 | N | N | N | N | YES | <D> **** Detailed Description **** Performing 15.3.17 Door C-222 Gap exceed 1/4" allowable, top middle. Screw head broken off top middle. Door knob need Repaired / Replaced.. <I> **** Actions Taken **** Contaced Supervisor , and Fire Protection. | 02-00-W-DOOR-C222
385750 | CR | 20181016 | CAQ | D | Door C-226 not meet criteria PPM 15.3.17 | N | N | N | N | YES | <D> **** Detailed Description **** Performing PPM 15.3.17 Door C-226 has a rip in the door metal ,inside, bottom left. <I> **** Actions Taken **** contacted supervisor ,and Fire Protection. <N> CR updated to reference the correct PPM (15.3.17) per direction of initiator. | 02-00-W-DOOR-C226
385751 | CR | 20181016 | CAQ | D | DOOR C-238 not meet criteria PPM 15.3.17 | N | N | N | N | YES | <D> **** Detailed Description **** Performing 15.3.17 Gap exceeds 1/4" top left . door knob needs replaced existing WO # 29144709 CR # 384781 <I> **** Actions Taken **** Contaced supervisor , and Fire Protection. <N> CR updated to reference the correct PPM (15.3.17) per direction of initiator. | 02-00-W-DOOR-C238
385752 | CR | 20181016 | CAQ | D | DOOR C-214 not meet criteria PPM 15.3.17 | N | N | N | N | YES | <D> **** Detailed Description **** Performing 15.3.17 rip in door metal, top right side. <I> **** Actions Taken **** contacted supervisor, and Fire Protection. <N> CR updated to reference the correct PPM (15.3.17) per direction of initiator. | 02-00-W-DOOR-C214
385753 | CR | 20181016 | CAQ | D | DOOR C-242 not mmet criteria PPM 15.3.17 | N | N | N | N | YES | <D> **** Detailed Description **** Performing 15.3.17 Found Gap exceeds 1/4" Bottom left. <I> **** Actions Taken **** Contacted supervisor, and Fire Protection. <N> CR updated to reference the correct PPM (15.3.17) per direction of initiator. | 02-00-W-DOOR-C242
385754 | CR | 20181016 | CAQ | C | EWD-84E-045C needs update | N | N | N | N | NO | <D> **** Detailed Description **** EWD-84E-045C for CCH-CR-1B at position D/9 references you to EWD-84E-044D however that drawing is for CCH-CR-1A 120VAC. I believe the reference should be to EWD-84E-045D. Request updating EWD with correct information.
385755 | CR | 20181016 | CAQ | D | DOOR C-240 not meet criteria PPM 15.3.17 | N | N | N | N | YES | <D> **** Detailed Description **** Performing 15.3.17 Found Gap exceeds 1/4" , Top Left. <I> **** Actions Taken **** Contacted supervisor, and Fire Protection. <N> CR updated to reference the correct PPM (15.3.17) per direction of initiator. | 02-00-W-DOOR-C240
385756 | CR | 20181016 |  | 3 | PMID-RQ has rotating scope with varying impacts |  |  |  | N | NO | <D> **** Detailed Description **** PMID-RQ 18479-01 is to perform ISP-EFC-B108 on a 2-year basis. The valves tested in this surveillance only need to be tested once every 10-years. The instructions rotate scope to test a different set of valves every 2-years. Issue is that the valves tested have very different plant conditions required (some online, some outage) and very different plant impacts. This CR is to drive necessary actions to align, and schedule this PMID appropriately. Assign to AR-OPSWM <I> **** Actions Taken **** Discussed with engineering, PSO, and maintenance. Imitated CR. There is no DNC.
385757 | CR | 20181016 | CAQ | D | H2/O2 analyzer heat trace trouble. | Y | N |  | N | YES | <D> **** Detailed Description **** 4.814.J1 3-2 H2/O2 analyzer heat trace trouble alarm is in. Operator found HT-TS-SR14/2 trouble light on reading 105F. The low temperature is 100F so there may be a temperature switch issue. <I> **** Actions Taken **** WR written. MCR informed. | 02-00-HT-TS-SR14/2
385758 | CR | 20181016 | CAQ | D | H2/O2 analyzer heat trace trouble. | Y | N |  | N | YES | <C> Duplicate of CR 385757. D/T <D> **** Detailed Description **** 4.814.J1 3-2 H2/O2 analyzer heat trace trouble alarm is in. Operator found HT-TS-SR14/2 trouble light on reading 105F. The low temperature is 100F so there may be a temperature switch issue. <I> **** Actions Taken **** WR written <N> **** Equipment Description **** rb522 | 02-00-HT-TS-SR14/2
385759 | CR | 20181016 | CAQ | D | CRD-V-111/2655 | Y | N |  | N | YES | <D> **** Detailed Description **** valve has a stem leak and requires replacement. during draining of a high water level in the accumulator, small bubbles were seen slowly forming on the stem indicating a slow nitrogen leak. <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-CRD-V-111/2655
385760 | CR | 20181016 |  | 4 | E-TR-M2 Cooler group 2 leak | N | N |  | N | YES | <D> **** Detailed Description **** While performing a walkdown of the transformer yard it was noticed that the rags under E TR-M2 cooler group 2 we covered in oil. The purpose of this CR is to document the need to replace the rags and put a bucket under the cooler group for E-TR-M2. This cooler group is scheduled to be replaced in R24 under the ABB transformer warranty repairs due to the leaking from the cooler. Notified Operations and they requested the SSS have the operators address the leak. <I> **** Actions Taken **** See pictures in EDMS | 02-00-E-TR-M2
385761 | CR | 20181016 |  | 3 | Condenser Hotwell Iron Levels trending up | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The concentration of Insoluble Iron in the condenser hotwell is trending up. The average concentration for Cycle 24 through the end of June 2018 was 13 ppb. Since then the concentration has trended up to the current value of 32.7 ppb. Feedwater Iron has been in the normal range through this period indicating that the Condensate Filter Demins are successfully removing the Iron. The source of the Iron is unkown at this time. The sample frequency is weekly. <I> **** Actions Taken **** Discussed at the Chemistry Trending Committee. Sent a trend chart to the condensate system engineer and the FAC engineer. | 02-00-COND-HX-9
385762 | CR | 20181016 |  | 3 | Chemistry Technician Initial Training Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** A student in the Chemistry Technician initial training program failed an exam. <I> **** Actions Taken **** Performed a review of exam with student. Developed a remediation plan and documented in eTAR. Notified line and training management.
385763 | CR | 20181016 |  | 3 | RAD Material found in the Main Control Room |  |  |  | N | NO | <D> **** Detailed Description **** An individual took a Fluke multi-meter that was labeled Radio Active Material (RAM) into the Main Control Room (MCR), which is a designated clean area. MCR staff recognized the RAM label on the instrument and notified HP. A follow-up survey was conducted and the instrument was deemed non-radioactive material (review survey # 20181016-2 for details). The HP technician informed the MCR staff that ALL RAM is not permitted in the MCR (unless escorted by HP), even if an instrument/tool passes the Sam Article Monitor (SAM). Although the Fluke was deem to be non-radioactive following an investigative survey, it is imperative that all RAD workers adhere to the procedural guidance that governs: Entry Into, Conduct In, and Exit from Radiologically Controlled Areas (GEN-RPP-04). This procedure provides guidance for working inside "clean areas" that are located within the RCA. The potential for RAM to enter clean areas clearly exists. It is the responsibility for all RAD workers to be familiar with the guidance in GEN-RPP-04, to help mitigate this potential. Although this incident was non-threating, there was a breakdown in the process. Achieving excellence is predicated on worker knowledge and utilization of our error prevention tools. When in doubt, ask HP and we will gladly provide assistance. <I> **** Actions Taken **** HP Supervision was informed and a follow-up survey was conducted. Initiated minor fact finding in operations.
385768 | CR | 20181016 |  | 3 | Need new guidance for getting rid of bad water in FDR-TK-22 |  |  |  | N | NO | <D> **** Detailed Description **** Work instruction steps or a new procedure needs to be written to allow pumping of the â€œiron waterâ€ in FDR-TK-6 and/or FDR-TK-22 to EDR-TK-5. The following steps will help the Radwaste Operator maintain storage capability in the FDR system. The iron water will be stored during the short term in EDR-K-5. Once FDR-TK-22 has been completely pumped empty, the bad water in EDR-TK-5 can be processed by normal means in small quantities. SEE EDMS SCEEN FOR WORD DOCUMENT | 02-00-EDR-TK-5,02-00-FDR-TK-22,02-00-FDR-TK-6
385769 | CR | 20181016 |  | 4 | EDR/FDR processing degraded - need FDR-TK-22 resin transfer | N | N |  | N | YES | <D> **** Detailed Description **** EDR/FDR filters are rapidly depleting due to the iron in FDR-TK-22 and water is backing up in the Radwaste processing tanks. Recommend moving up resin transfer to address this problem. <I> **** Actions Taken **** Placed item on PCL. Initiated actions with Ops, Chem, HP, Eng, and WWM to address resin tranfer date, alternate water storage location (EDR-TK-5) and evaluating impact on COND-DM-1D work the week of 10/22/2018. | 02-00-FDR-TK-22
385770 | CR | 20181016 |  | 3 | Incorrect work order scope to credit another work order. |  |  |  | N | NO | <D> **** Detailed Description **** During the performance/completion of work order 02118454, to replace the starter coil for RHR-FCV-64B, was to credit work order 02114048 which performs a " TEST AND INSPECT " of the same starter. The work performed under starter coil replacement work order does not perform the correct work scope to credit the "test and inspect" starter work order. The work step to credit work order 02114048 at the completion of work order 02118454 will have to be N/A'd. <I> **** Actions Taken **** Generated this CR to document that WO 02114048 cannot be credited by the completion of work order 02118454. Recoment extent of conditiion be performed by planning to identify other work orders that may be incorrectly credited. Notified OCC, and Electrical Component Group Manager of findings. | 02-00-RHR-42-8A2E,02-00-RHR-FCV-64B
385772 | CR | 20181016 |  | 3 | Shilelding installed too close to RHR-MO-40 |  |  |  | N | NO | <D> **** Detailed Description **** Work on RHR-MO-40 refursbishment was delayed by about 4 1/2 hours until tempoary shielding was readjusted. The shielding was installed too close to the work area such that the work couldn't be efficiently completed with the orignial shielding configuration. In addtion to the work delay this rework caused 46 mrem of unnecessaary dose to be accrued. <I> **** Actions Taken **** Notified RPM and OCC. Held a meeting to organize response Reoriented the shielding so that work could proceed. | 02-00-RHR-MO-40
385773 | CR | 20181016 |  | 3 | WO Package stuck in Hold for Ops status |  |  |  | N | NO | <D> **** Detailed Description **** WP task 02118454-01 is stuck in eWP step Ops Review, Asset Suite status was READY. The option to set to working was grayed out, and the task did not appear on the Ops Review screen. <I> **** Actions Taken **** WO package was taken to working in Asset Suite.
385774 | CR | 20181016 | CAQ | D | FP-P-110 coolant leak during pump run | N | Y |  | N | YES | <D> **** Detailed Description **** FP-P-110 had another coolant leak when the pump was started for PPM 15.1.4. The leak was from multiple rubber gaskets circled in the attached photos. <I> **** Actions Taken **** Placed local control switch in OFF. Notified MCR. Wrote CR. | 02-00-FP-P-110
385775 | CR | 20181017 |  | 3 | Zebra ZT510 equipment tag printer in main control room | N | N |  | N | YES | <D> **** Detailed Description **** MCR equipment tag printer still not functioning. Suggest OPS management get involved in resolution or lack of any solution for GT 6 months. last CR closed out indicating it was too expensive to fix. Not an excuse when there is a spare within 5 feet of the existing unit. <N> **** Equipment Description **** Equipment tag printer in MCR
385776 | CR | 20181017 |  | 3 | OCA Camera 90 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** OCA Camera 90 requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervision notified. Initiate CR/WR <N> **** Equipment Description **** OCA Camera 90 Rebooted camera to restore functionality. See IS ticket 34727.
385777 | CR | 20181017 |  | 3 | 2018 TFOF Minor Damage to ENW Vehicle |  |  |  | N | NO | <D> **** Detailed Description **** On 10/16/2018 at approximately 2134 hours during a NRC Evaluated Force on Force Exercise the CAF team chose to utilize a vehicle located inside the Protected Area for their assault. A CAF team member entered a ENW vehicle located east of Building 17 with his controller and attempted to back the vehicle up to the Building 17 roll up door located on the Southeast side of the building. He adjusted his approach to avoid a dumpster but made minor contact with a bollard. Vehicle was traveling approximately 1-2 mph, resulting in superficial paint transfer from the bollard to the man lift gate. <I> **** Actions Taken **** CR Submitted. Shift Manager and Security Management notified. OI-34 notification. Witness statements collected. <N> Conducted safety briefings to all drill participants and controllers on the importance of reporting events and reinforcing vehicle usage and safety requirements. Event investigation has been loaded in EDMS.
385779 | CR | 20181017 |  | 4 | Exterior lights on auxillary buildings inside the PA are out | N | N |  | N | NO | <D> **** Detailed Description **** Multiple lights on the exterior of the auxillary buildings inside the protected area are not functioning. Repair or replace as necessary. <I> **** Actions Taken **** Generated work request. <N> **** Equipment Description **** Exterior lights on auxillary buildings inside the PA
385781 | CR | 20181017 |  | 3 | Individual was delayed by 30 min from entry into RCA. |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** NRC employee supporting FoF activities was unable to gain access to the RCA in a timely manner. Delay of approximately 30 mins due to TES access description error â€œINDIVIDUAL IS NOT QUALIFIED.â€ Individualâ€™s Rad Worker training was verified correct on R-011 panel as compared to D-411/412 panel. Induvial qualifications indicated as qualified. Individualâ€™s DLR (00014418) was returned and new DLR (00167956) issued, then Individual was then able to log-in. Review of DLRs did not indicate potential cause, but access by HPAC was approved after a DLR change. <I> **** Actions Taken **** Notified Supervision, Reviewed TES transactions recommend CR review by IS to investigate issue
385782 | CR | 20181017 | CAQ | D | FP-PR-1 not advancing | N | N |  | N | YES | <D> **** Detailed Description **** FP-PR-1 has not advanced since 10/16/18 at 0800. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-FP-PR-1
385788 | CR | 20181017 |  | 3 | CR closed without resolution |  |  |  | N | NO | <D> **** Detailed Description **** CR 384792 was written to address differences between surveillance OSP-RHR/IST-Q703 and I&C work instructions to install test gages from MWO 00CVG3. The MWO needs to be changed to match the surveillance for task 3.
385790 | CR | 20181017 |  | 3 | 2018 TFOF No Restroom Breaks During FOF Activities |  |  |  | N | NO | <D> **** ANONYMOUS CR - Detailed Description **** In accordance with DOSH Directive 5.98 (Department of Labor and Industries Division of Occupational Safety and Health section VI, para-4, "The employer must not impose unreasonable restrictions on employee use of bathrooms or toilet facilities." During the FOF activities conducted on the night of October 16th, 2018, Security Officers were sent to posts such as BREs and other locations where they had to remain in those locations for up to 6 hours without an opportunity take a restroom break. The drill allowed a number of opportunities where officers could have rotated accordingly to allow for rest periods which would have given them the time to use the restrooms, but none such actions were taken. Officers, controllers, and support must be allowed to take restroom breaks when there is a lull in FOF activities. Instructions were to stay in place without breaks, with posts locked in place without rotating. <I> **** Actions Taken **** Iniated CR. <N> **** Equipment Description **** CGS Anonymous CR Generated. Moved to CR-SRO for OPS Reivew. Item was added as talking point to controller/player briefing prior to FOF exercise.
385792 | CR | 20181017 |  | 4 | Tripping hazard outside the Deschutes Bldg south entrance. |  |  |  | N | NO | <D> **** Detailed Description **** In front of the Deschutes Bldg main (south) entrance on the southwest side of the concrete, where the concrete meets the asphalt, the asphalt is a little higher than the concrete and may be a tripping hazard. <I> **** Actions Taken **** Notified supervision.
385793 | CR | 20181017 |  | 4 | Widen sidewalks near Bldg. 9 and 17 |  |  |  | N | NO | <D> **** Detailed Description **** The sidewalks that lead from the front doors of Bldg. 9 and between Bldg. 9 and 17 to the road should be widened to accommodate 2 people walking side by side. Itâ€™s narrow enough that when two people walk side-by-side one of them inevitably slips their foot off the pavement, into the gravel or walks off the paved path. This poses a safety concern and should be remedied. WR has been initiated to widen the walkway. <I> **** Actions Taken **** Discussed at PSO's D15
385794 | CR | 20181017 | CAQ | C | FP-ENG-110 repeat issue of overheating in standby | N | Y |  | N | YES | <D> **** Detailed Description **** FP-ENG-110 has had multiple work orders and work requests to have this issue resolved and it has not been addressed or corrected. Reference WR 29126904, 29077842, 29068560, 29033623 and WO 02070475, 02088770, 02029952 for hot coolant which has been as high as 210 degrees noted per operations logs which puts this engine in an overheated condition just in standby. Reference WR 29118669, 29094695, 29077891, 29029186 and WO 02069604, 02026673, 02020736, 02003331, 02000064 for the tell tale leaks which are caused by the o-rings being degraded from the extreme temperatures and cracking on the inner diameter which in turn creates a leak path through the seal ring and seal gland. Maintenance has suggested changing from convection style heating to a circulating pump style heater to resolve this issue. Reference CR 325296 for previous attempts at fixing <I> **** Actions Taken **** Notified main control room, my supervisor, fire protection engineering <N> **** Equipment Description **** FP-ENG-110 | 02-00-FP-ENG-110
385796 | CR | 20181017 |  | 4 | Missing Security badge |  |  |  | N | NO | <D> **** Detailed Description **** An individual called to report their badge as lost. <I> **** Actions Taken **** Notified Security.
385797 | CR | 20181017 | CAQ | D | DOOR C-418 Not meet criteria PPM 15.3.17 | N | N |  | N | YES | <D> **** Detailed Description **** Performing PPM 15.3.17 found Gap to be greater than 1/4" . <I> **** Actions Taken **** contacted supervisor, Fire Protection | 02-00-W-DOOR-C418
385799 | CR | 20181017 |  | 4 | IDC Pumphouse Fire Extinguisher Not Compatble with Chlorine | N | N |  | N | NO | <D> **** Detailed Description **** IDC Building 515, Pumphouse Number 1, has a chlorinator that is used to inject chlorine into the potable water system. The building is required to have a portable fire extinguisher per the Fire Code and ISPM-10. The use of a multipurpose ABC Dry Chemical fire extinguisher is incompatible with chlorine. The dry chemical fire extinguishing agent contains ammonium compounds that shoud not be mixed with oxidizers that contain chlorine. Any mixing of the oxidizer and the ammonium salts in the dry chemical fire extinguishing powder can generate a chemical reaction with violent results. NFPA 10, the Standard for Portable Fire Extinguishers requires that only water or foam extinguishers be installed in areas where chemicals containing chlorine are stored. . Work Request written to purchase and install an AFFF Foam type fire extinguisher in the building. This is the same type of portable fire extinguisher that is used at the Columbia Circulating Water Pumphouse and in the Flocculator building due to the presence of chlorine. <I> **** Actions Taken **** Notified IDC Site Manager of the problem through EMail. WR written to purchase and replace existing fire extinguisher. <N> **** Equipment Description **** IDC Building 515 Pumphouse No.1 Portable Fire Extinguisher
385801 | CR | 20181017 | CAQ | C | Late eSOMS entries for Mainenance - Week of 9/29/18 |  |  |  | N | NO | <D> **** Detailed Description **** Maintenance had several late eSOMS entries the week of 9/29, none of which resulted in a violation: a supervisor worked two hours over his scheduled time on four days; two craft people worked twelve hours when they were scheduled to work ten; a craft person and a supervisor each worked for two hours on days when they were scheduled to be off; and a craft person left two hours after his personal time was scheduled to begin. <I> **** Actions Taken **** Updated eSOMS with correct times <N> CR Title and Description changed at the request of maintenance to reflect the correct day (9/26, not 9/29).
385802 | CR | 20181017 | CAQ | C | Late eSOMS Entries for Maintenance - Week of 10/6/18 |  |  |  | N | NO | <D> **** Detailed Description **** Maintenance had several late eSOMS entries the week of 10/6, none of which resulted in a violation: one craft person worked on a day when he was scheduled to be off; three craft people left one hour after personal time was scheduled to begin; and four craft people failed to notify scheduler or a supervisor when their travel schedule changed by four hours on each travel day. <I> **** Actions Taken **** Updated eSOMS with correct hours <N> ***Gerneal Notes*** This issue is being addressed by coaching that will be documented on an ETAR within each Maint. Shop. This documentation can be found under AR# 385801 within the EDMS. Due to this issue being addressed under CAQ CR# 385801, no further actions are required under this AR. Permission to close this AR was obtained by the Maint. programs supervisor.
385804 | CR | 20181017 |  | 3 | Network Switch in Engineering Computer Lab version mismatch | N | N |  | N | YES | <D> **** Detailed Description **** A network switch in the ECL has a different Operating System Version than the production switch in the Plant. The Plant has CISCO ASA 15.2 The ECL has CISCO ASA 15.0 This situation reduces the effectiveness of testing in the ECL. The risk is not high, but there is a chance of an EC change that is tested in the ECL will not catch an issue before the EC is implemented in the Plant. <I> **** Actions Taken **** Contacted Vendor to get installation instructions/package to change the ASA operating system to match the plant. The Vendor has responded that the version we want to change the switch to is 4 years old and no longer supported. They do not support the configuration correction we would like to make. Suggest that we document the difference and accept the risk with no change. | 02-00-NET4-NETSW-02
385805 | CR | 20181017 |  | 3 | Conductive grease not available for scheduled work |  |  |  | N | NO | <D> **** Detailed Description **** During preventive maintenance on a safety related bucket, RHR-42-8BA5D (RHR-V-27B), it was identified that conductive grease as specified in maintenance procedure 10.25.187 was not available for issue. The grease DSLUBEKIT catalogue ID 32130 was added to the procedure in 2015 per NEMA recommendation. It is procedurally required to be used in certain applications to correct for high contact resistance. Recommend that this item is stocked and available for use. Recommend that model work orders for related PMs get updated appropriately. <I> **** Actions Taken **** Reported the need for this grease to the OCC. It was obtained and applied as directed by the procedure - work order completed satisfactorily. Initiated this CR <N> Procurement Evaluation 8588 Revision 0 was developed to dedicate the grease for use on RHR-42-8BA5D on 10/15/18.
385806 | CR | 20181017 | CAQ | D | CPR-V-357B Dual Indication | N | N |  | N | YES | <D> **** Detailed Description **** During resin transfer operation from CPR-TK-92B the suction line unplugging valve, CPR-V-357B, indicates intermediate following after closing the valve. When CPR-V-357B is switch is held in the open position the valve does indicate open but when the switch is released the indication remains dual, Note this switch is spring return to close. Recommend investigation and adjustment of limit switches. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** RW 444' Behind the Shield Wall | 02-00-CPR-V-357B
385808 | CR | 20181017 |  | 3 | SOP-RHR-FILL requires revision |  |  |  | N | NO | <D> **** Detailed Description **** SOP-RHR-FILL has I&C steps with no configuration control, routinely these steps are added to work instructions to allow technicians the ability to place keep during venting. Recommend adding the steps to the SOP to remove the error potential of having multiple location of instruction. <I> **** Actions Taken **** Wrote CR Added work orders steps to EDMS as guidance (recommend using RHR A for format, B and C for locations and valve number) Spoke with OPS Procdure Supervisor
385809 | CR | 20181017 |  | 3 | EWP sending multiple revisions of work order to Asset Suite |  |  |  | N | NO | <D> **** Detailed Description **** EWP/DataGlance is sending multiple revisions of a work order to Asset Suite. This creates multiple revisions until such time that the image is attached. For example 0211716101 has 200 revisions all issued on 8/16/18 with only one image attached at revision 200. Initial investigation indicates 263 work orders have been impacted by this issue. This is not a QAR record issue. No QAR record integrity has been compromised or lost. Recommend Category 3, assignment to ITMGMT <I> **** Actions Taken **** Immediate actions taken â€“ Notified IS and Supervisor. Started investigation to determine extent of condition.
385811 | CR | 20181017 |  | 4 | Records Submitted without Corrections being Rectified |  |  |  | N | NO | <D> **** Detailed Description **** A CR was written 8/14/2018 because a Software Classification form was Submitted to Records Control without a valid EPN. (Ref CR # 00383451.) This is the third time this record had been submitted to Records Control without the underlying issue being rectified. They were submitted again, and the EPN is still invalid. <I> **** Actions Taken **** Notified my supervision. Sending Record back to Radiation Protection for corrections and re-submittal.
385812 | CR | 20181017 | CAQ | C | TiP Machine E flux reading erratic and not useable | Y | Y |  | N | YES | <D> **** Detailed Description **** TIP Machine E flux readings remained flat while in core reading between 6 and 8 for entire TIP trace in common channel (other machines ranged up to 60+ in common channel). While withdrawing the TIP detector back to position 0001 TIP readings spike while out of the core up to 140 before dropping back to 0. Suspect TIP connection for machine E may be loose, or detector itself may need replacement. <I> **** Actions Taken **** Completed LPRM calibration with remaining 4 machines which all worked well. Notified SM. | 02-00-TIP-DET-3E
385813 | CR | 20181017 |  | 3 | Clearance order released and lifted then had to be rehung. |  |  |  | N | NO | <D> **** Detailed Description **** Clearance Orders L-RHR-MO-48B -001 and D-RHR-MO-48B -001 were hung then lifted before all the work requireing the clearances was completed. See EDMS for detail. Per OI-12 this is a level 4 clearance event â€“ tags lifted before work complete with no safety significance. This CR should be evaluated to identify any primary and contributing causes and any actions to correct.
385814 | CR | 20181017 |  | 3 | 2018 TFOF Verify Security Response to Off-Site Locations |  |  |  | N | NO | <D> **** Detailed Description **** During night 1 of evaluated force on force exercise security personnel did not respond as expected. <I> **** Actions Taken **** Security Operations Manager briefed applicable personnel of expectations.
385816 | CR | 20181017 |  | 3 | 2018 TFOF Lack of Communication of Security Drill Player |  |  |  | N | NO | <D> **** Detailed Description **** Lack of communication of security drill player resulted in being located in an unexpected location. Creating a friendly fire near miss. <I> **** Actions Taken **** Securty Programs Supervisor and Security Operations Manager advised.
385817 | CR | 20181017 |  | 3 | procedure update for OSP-CCH/IST-M701 and M702 |  |  |  | N | NO | <D> **** Detailed Description **** Periodicities have changed for prerequisites 3.3 and 3.4. PMIDs are listed in the survellances for help verifying. <I> **** Actions Taken **** verified work not due.
385818 | CR | 20181017 |  | 4 | PWC-P-7 leaking | N | N |  | N | YES | <D> **** Detailed Description **** PWC-P-7 was found leaking about a drop every 10 seconds. This is a NaOCl pump for the potable water system. The leaking chemical is all contained within the berm, and so none has spilled. <I> **** Actions Taken **** Contacted supervision and specialist. Closed supply valve, PWC-V-761, to isolate chlorine leak. Unplugged PWC-P-7. | 02-00-PWC-P-7
385820 | CR | 20181017 |  | 4 | PWC-P-8 degraded | N | N |  | N | YES | <D> **** Detailed Description **** PWC-P-8 has been found air bound two days in a row, and multiple times recently, and needs to be looked at and possibly worked on. This pump is a NaOCl pump for the potable water system. <I> **** Actions Taken **** Contacted supervision and specialist. | 02-00-PWC-P-8
385821 | CR | 20181017 |  | 4 | TMU-M-P/1A Motor Terminations | N | N |  | N | YES | <D> **** Detailed Description **** During the removal & replacement of the TMU-P-1A pump, the motor was determinated from the field leads. (1) The initial concern noted is that two of the leads were fully tapped out and one lead was not. (2) Moving forward with determing the leads found the motor side single lugs had indications of partial discharge. The lugs were twisted over greater than 30 degrees and (3) broken wire strands were noted as well. (4) The insulation was degraded on each of the leads from the motor itself. (5) The field side leads were found with no stress cones, (6) the grounds were broken or barely intact and corroded, (7) the insulation was found degraded and in poor conditions with splitting up the wire. (8) The terminal box interior has indications of moisture and corrossions. * WO 02134236-07 is working the repairs to the motor terminations per the directions of PPM 10.25.19 * Programs Engineering and Design Electrical Engineering colabrated for the repairs required. Directions were prepared and provided to the electrical craft for implementation. * This motor termination for TMU-M-P/1A was performed 2/23/13; and from an extent of conditions a review of the TMU-M-P/1B was performed 12/12/13 and TMU-M-P/1C was performed 06/20/2013. Though the time lines are all within 6 months, this is an isolated event for the time frames. Thus no concern with reliable operations of the other two TMU Motors 1B & 1C. <I> **** Actions Taken **** 1. Notified my supervisor 2. Collected field data to support the details of this CR 3.Field walkdown and photos taken. 4.Reviewed PPM 10.25.19 for adequacy. 5. Techical details was prepared to support the craft for the final field activites prior to making thetermination. 6. Consulted with Design Electrical Engineering on the technical details provided. 7. Provided techical details to the planning organization for the WO. performing the work. 8. Verfied in the warehouse that the materials & CATID were in stock and for the proper voltage application for 4160. 9. Held a pre-job brief with the lead electrican performing the work. 10. Initiated and Prepared this CR 11. Ensured the craft supervisor had engineering support at any time during field implementation 12. Due to the as-fopund conditions of the motor to field cables condition, discussed with the Cable Testing Program Engineer the value of performing TAN DELTA testing. 13. The Cable Testing Program Engineer, contacted the planner and provided directions for performing the Tan Delta Testing. Work Order instructions were provided. <N> **** Equipment Description **** TMU River Pump House ***General Notes*** the shop has been coached on the condition of the TMU motor, no further actions required. | 02-00-TMU-M-P/1A
385823 | CR | 20181017 | CAQ | D | CRD-LT-12D found out of tolerance | Y | Y |  | N | YES | <D> **** Detailed Description **** During the performance of ISP-CRD-X306 under WO 02120683 01 CRD-LT-12D was found out of tolerance low. Per step 7.1.44 the transmitter was found slightly low and out of as Left tolerance. <I> **** Actions Taken **** Calibrated into as left tolerance per procedure, notified CRS, Supervision, and writing this CR to document. <N> **** Equipment Description **** R522 SDV | 02-00-CRD-LT-12D
385824 | CR | 20181017 | CAQ | C | (PCSC Good Catch) â€“ Mechanical drawings require revision | N | N |  | N | NO | <D> **** Detailed Description **** While performing a walk down to perform work order 02103756 task 08 (M) REMOVE CHECK VALVE TO SUPPORT DRAINING (CBD -V-10), mechanics identified that the field configuration of check valves CBD-V-28 and CBD-V-29 did not match AED MEC M507-1. The mechanics used Give 2 and notified their supervisor. The supervisor also noted that CVI ISO 215 -00,14712 showed the same configuration as AED MEC 507-1. <I> **** Actions Taken **** The supervisor notified Operations and the mechanical planner of the discrepancy between the field condition and mechanical drawings. The field configuration was noted as being correct per SOP-CW-OPS for performing CW blowdown using submersible or temporary pumps. Further investigation revealed that the check valves had been documented as an unauthorized modification per AR 245851 and an ACCEPT AS IS had been performed for the check valves in the current field configuration. EC ADOC 14956 was approved to revise AED MEC M507-1, CVI ISO 215-00,14712, and AED MEC M658 but it appears the revisions were performed incorrectly. The Minor MALT Supervisor confirmed that these three drawings require a revision to reflect the correct configuration. | 02-00-CBD-V-28,02-00-CBD-V-29
385825 | CR | 20181017 |  | 4 | September Legionella sample results elevated | N | N |  | N | NO | <D> **** Detailed Description **** The results of the Legionella samples taken 9/18/18 were elevated based on the previous testing results and trends. Test results have been uploaded into the EDMS doc folder as reference. Evaluation of the September data by the Chemistry Specialist concludes that there may have been a problem with the testing. Resampling is scheduled for the week of October 22nd. All levels, including these results, are still low with the exception of APEL but elevated for CGS trending. <I> **** Actions Taken **** No action is recommended. Test results are suspect and may not be correct. Retesting/monthly testing to confirm trending will be performed next week â€“ Oct. 22, 2018.
385826 | CR | 20181017 |  | 4 | S5 steam leak on HD-TK-3B instrument tree. | N | N |  | N | YES | <D> **** Detailed Description **** An S5 steam leak exists on the HD-TK-3B instrument tree. Due to the size of the leak, likely culprit is HD-LT-11A. A mobile scaffold is in the way of the camera, preventing positive identification. Heater bay entry is required to identify. <I> **** Actions Taken **** Updated FLM map, informed SM. | 02-00-HD-TK-3B
385827 | CR | 20181017 |  | 4 | SRS-PPC/SYSHEALTH-01 software version documentation | N | N |  | N | YES | <D> **** Detailed Description **** This is documentation issue and does not impact software functionality. The current installed version of PPC-SOFT -SYSHEALTH is v16.2, which is correct. However, sequential version numbers have not been maintained and not all versions were approved as equipment minor revisions per DES-6-1 and DES-6-3. EC 8461 and EC 15965 did not include equipment minor revisions to update the software version to match the Software Requirements Specification. Equipment minor revisions 3 and 4 (EC 7855 and 12155) do not list the correct version of the software documented in the Software Requirements Specification. EC 15092 did not follow sequential versioning. EC 15092 created version 16.2 after version 17.0 was created by EC 13492. <I> **** Actions Taken **** Software version history uploaded to EDMS and related EC's added to Xref. Recommend COMP-NA. No corrective action is required. The current configuration is correct. | 02-00-PPC-SOFT-SYSHEALTH
385829 | CR | 20181017 | CAQ | C | Unidentified leakage reading >0gpm. | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** FDR-FQ-38 and EDR-FRS-623 are reading >0 gpm. These are used for determining Primary Containment Unidentified leakage and have read 0gpm for years. This maybe do to calibration or ISP-FDR/EDR-X301 but needs to be evaluated. This is not a normal value for the reading on our H101. <I> **** Actions Taken **** Told NRC resident CR would be written. informed CRS.
385830 | CR | 20181017 |  | 3 | Missing vendor drawing 34CS750001 sheet W2 of W3 found |  |  |  | N | YES | <D> **** Detailed Description **** Existing CVI DWG 225-04,31,W1 Note 4 states that drawing W-2 was never transmitted to EN. However, drawing W-2 (vendor drawing 34CS750001 sheet W2 of W3) was found to exist in the existing hardcopy of CVI OMM 225-11,11. A pdf copy of the missing vendor drawing is attached to the EDMS of this AR CR 385830. For resolution of this AR CR 385830, vendor drawing 34CS750001 sheet W2 of W3 needs to be entered into the station CVI drawing system as CVI DWG 225-04,31,W2 and CVI DWG 225-04,31,W1 needs to be updated accordingly (at least to remove its Note 4 entirely). This is a legacy drawing issue only - suggest resolution assignment to Mechanical Design & Drafting. There is no associated impact or effect upon continued functionality, operation, or qualification of any station SSCs. | 02-00-E-IR-30,02-00-TMU-PI-4BG,02-00-TMU-V-713B
385831 | CR | 20181017 |  | 3 | VESDA equipment purchased through unauthorized dealer | N | N |  | N | YES | <D> **** Detailed Description **** During the installation of Very Early Smoke Detection Apparatus (VESDA) the manufacturer (Xtralis) informed the PM that equipment recently purchased was bought from an unauthorized dealer known as Architectural Builders Supply or www.abssupply.net. Xtralis has issued a ceased and desist order to ABS. Xtralis further indicated they will not provide support nor warranty of faulty equipment when purchased from an unauthorized dealer. None of the equipment purchased from ABS is safety related. See EDMS for details. <I> **** Actions Taken **** Notified Supply chain services of condition. Provided supply chain a list of approved vendors.Fire Protection project is performing the rework associated with equipment failures under w/o 02116227. no work request needed. <N> **** Equipment Description **** EPN's are located in the Vital island. | 02-00-FP-CP-ISD/1,02-00-FP-CP-ISD/2,02-00-FP-CP-ISD/3,02-00-FP-CP-ISD/4
385834 | CR | 20181018 |  | 4 | RFW-DT-1A steam leak off governor valve body | N | N |  | N | YES | <D> **** Detailed Description **** A steam leak has been identified on what appears to be the body of RFW-DT-1A's governor valve. There is a hole blown in the insulation and steam is coming out. The leak is on the east side of the A feed turbine. There is a video attached that shows the audible change when a object is pushed over the opening to verify that is the correct source of the steam. The hole in the insualation is about 2-3" in diameter. | 02-00-RFW-DT-1A
385835 | CR | 20181018 |  | 4 | PWC-P-2 seal water fitting significant leak | N | N |  | N | YES | <D> **** Detailed Description **** The seal water line compression fitting connection on PWC -P-2 has a significant leak and needs to be repaired. It is spraying water all over the skid, but dispersal had been reduced by a plastic/rubber deflector. This is the exact same problem one of the other PWC pumps had on that same skid some 6 months ago (or so). The leak lasted a week or two before the pipe connection underwent utter failure. Video and photo attached in EDMS. | 02-00-PWC-P-2
385836 | CR | 20181018 | CAQ | C | DSA-V-15B/DSA-V-16B Operability Check failed | Y | N |  | N | YES | <D> **** Detailed Description **** During OSP-ELEC-M702, Att. 9.3, DSA-V-15B AND DSA-V-16B Operability Check, DSA-PI-9B increased from 0 psig to 75 psig over the 15 minute wait. This is greater than the 10 psig limit directed by the procedure. CR initiated to evaluate the possible degradation of DSA-V-15B and/or DSA -V-16B. <I> **** Actions Taken **** Informed MCR. Wrote CR | 02-00-DSA-V-15B,02-00-DSA-V-16B
385837 | CR | 20181018 |  | 4 | Plot 25 in MCR needs configured properly | N | N |  | N | YES | <D> **** Detailed Description **** PLOT 25 xerox changed out with Canon plotter but driver not updated and IP address may need updated as well. <N> **** Equipment Description **** MCR PLOT 25 in back
385840 | CR | 20181018 |  | 3 | (QA) Cannot Follow One PPM 16.6.1 Step as Written |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) One step in PPM 16.6.1 â€œCC/RC - TSW Radiation Monitorâ€ requires evaluating a test ratio in a table not found in the procedure; therefore, this step cannot be followed as written. SWP-PRO-01 â€œProcedure and Work Instruction Use and Adherenceâ€ requires the user to stop work when a document cannot be followed as written. Requirements: â€¢ SWP-PRO-01 rev 030 step 2.6 (also rev 027 and rev 027-001 step 2.10) states, â€œIf a document cannot be used as written, then the activity is stopped and the issue is resolved before the user continues.â€ â€¢ SWP-PRO-01 rev 030 step 2.10 (also rev 027 and rev 027 -001 step 2.14) states, â€œProcedures and work instructions are reviewed prior to use to ensure that potential adherence problems are resolved.â€ Factual Basis: â€¢ PPM 16.6.1 rev 013 step $ 7.5.49 states, â€œIs transfer ratio recorded in Table 7.6b is [in] between 0.80 and 1.20?â€ â€¢ PPM 16.6.1 rev 013 does not contain any Table 7.6b; therefore, step 7.5.49 cannot be followed as written. â€¢ QAR HP 0207803701 for WOT 02078037-01 (CRS/Shift Manager Review signed on 1/14/16) shows work did not stop and step $ 7.5.49 was answered â€œNoâ€ and initialed. â€¢ QAR MAI 0208737001 for WOT 02087370-01 (CRS/Shift Manager Review signed on 1/14/16) shows work did not stop and step $ 7.5.49 was answered â€œYesâ€ and initialed. â€¢ QAR HP 0209667001 for WOT 02096670-01 (CRS/Shift Manager Review signed on 7/12/17) shows work did not stop and step $ 7.5.49 was answered â€œYesâ€ and initialed. Insights: â€¢ Two different individuals answered the above step that cannot be followed as written. â€¢ PPM 16.6.1 rev 009-003 (issued 11/2/2008) was last time this â€œ$â€ step to evaluate acceptance of the â€œtransfer ratioâ€ pointed to the correct PPM 16.6.1 Table 7.5b, which contains a â€œtransfer ratioâ€ value. â€¢ In PPM 16.6.1 rev 010 (issued 5/4/2011), the change from â€œTable 7.5bâ€ to â€œTable 7.6bâ€ was not cited within the Synopsis on page 1 of this revision; therefore, this change may have been inadvertent. â€¢ The behaviors of not recognizing the table number was incorrect and not stopping work to correct it does not demonstrate an engaged thinking worker for the last seven years. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Chemistry. <I> **** Actions Taken **** Discussed this Issue with the Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager <N> Issue with procedure was corrected on 10/15/18
385841 | CR | 20181018 |  | 4 | M&TE Rejected | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0060456 Simpson Clampon Ammeter- model HE94 was Not Used During Calibration cycle. Rejected- Broken and Inop-. DEF #6762A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
385842 | CR | 20181018 |  | 3 | (QA) Conflicting Step in PPM 16.8.1 CC/RC-SW A |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) One conditional step in PPM 16.8.1 â€œCC/RC â€“ Standby Service Water System Effluent Radiation Monitor Ch Aâ€ conflicts with itself with respect to which steps are to be marked â€œN/Aâ€ and which steps are to be completed. Errors in surveillance procedures could cause confusion and misunderstandings that may set up a worker to fail and may result in an invalid surveillance. SWP-PRO-01 â€œProcedure and Work Instruction Use and Adherenceâ€ requires the user to stop work when a document cannot be followed as written. One actual consequence is that Work Order Task (WOT) 02111562-01 contains a step marked â€œYesâ€ for values in a table being within limits, but there were no values entered into that table that fell in the range of steps allowed to be marked â€œNAâ€ by the step that conflicts with itself. Requirements: â€¢ SWP-PRO-01 rev 032 (issued 03/05/18) step 2.6 states, â€œIf a document cannot be used as written, then the activity is stopped and the issue is resolved before the user continues.â€ â€¢ SWP-PRO-01 step 2.7 states, â€œProcedures and work instructions are followed as written, and users do not deviate except when specifically allowed by approved processes.â€ â€¢ SWP-PRO-01 step 2.9 states, â€œVariances from the guidance contained within the document require an approved change.â€ â€¢ SWP-PRO-01 step 2.10 states, â€œProcedures and work instructions are reviewed prior to use to ensure that potential adherence problems are resolved.â€ â€¢ SWP-PRO-01 step 4.7.1 â€œUse of Not Applicable (NA)â€ NOTE states, â€œNA is not to be used to bypass step(s) that are inadequately or improperly written and is not to be used in lieu of an approved change.â€ see EDMS for word document for more details. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Maintenance. <I> **** Actions Taken **** Discussed this Issue with; Craft/Maint Supervisor III, Component Group Manager, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager <N> Issue with procedure was corrected on 10/8/18
385845 | CR | 20181018 | CAQ | C | (QA) Missing Significant Digits for ODCM Surv. Results | N | Y |  | Y | NO | <D> **** Detailed Description **** (QA) Quality Assurance Records (QARs) show results in multiple Work Order Tasks (WOTs) contain Offsite Dose Calculation Manual (ODCM) surveillance â€œas-foundâ€ and/or â€œas-leftâ€ values that lack enough significant digits to verify these values fall within acceptable limits specified utilizing more significant digits. This does not meet the Chemistry industry standard practices for significant digits and rounding when logging data, and does not meet the expectations of the Maintenance department. Eight ODCM surveillance WOT examples were identified that contain recorded data that are missing significant digits. Because other initialed steps within the WOTs verified that the results were within specified limits, there are no operability/functionality concerns for the ODCM equipment. Factual Basis: See EDMS word document for more detail . This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Maintenance. <I> **** Actions Taken **** Discussed this Issue with: Craft/Maint Supervisor III, Component Group Manager, Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385846 | CR | 20181018 |  | 4 | INFO ONLY - HSSF Alarm Tube Low Pressure | N | N |  | N | NO | <D> **** Detailed Description **** Alarm HS PAL124-PRES STAT LOW recieved. This is the hydrogen storage tubes pressure low alarm. <I> **** Actions Taken **** Contacted the CRS. Informed MCR and chemistry supervision. Wrote WR and CR. VENDOR CONTACTED TO DELIVER H2 <N> **** Equipment Description **** Hydrogen Storage Area
385847 | CR | 20181018 |  | 3 | (QA) M&TE Data Left Blank (Instead of NA) in 3 ODCM WOTs |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The Quality Assurance Records (QARs) for three Work Order Tasks (WOTs) contain blanks for the Measuring and Test Equipment (M&TE) Number and Calibration Due Date for a Scaler-timer, contrary to SWP-PRO-01 â€œProcedure and Work Instruction Use and Adherenceâ€, which requires an entry of â€œNAâ€ for Not Applicable. Scaler-timers were not needed for subsequent conditional steps in the associated Volume 16 surveillance procedures within these WOTs based on acceptable â€œAs-Foundâ€ data recorded in several earlier steps. These are procedure non-compliances with no known consequence. Requirement: â€¢ SWP-PRO-01 requires the use of â€œNAâ€ when data entry is not needed in a Continuous Use procedure. Factual Basis: These QARs for three WOTs each contained a completed Volume 16 procedure with blanks in Section 5.1 â€œCalibrated Equipmentâ€ table instead of â€œNAâ€ for â€œM&TE Numberâ€ and â€œCal. Due Dateâ€ for Scaler-timer: â€¢ QAR HP 0205597501 for WOT 02055975-01 â€œ16.8.3 SW-RIS-604 - CFTâ€ â€¢ QAR HP 0205299601 for WOT 02052996-01 â€œ16.8.4 SSW System Effluent Monitor CH B - CC/RCâ€ â€¢ QAR HP 0211308001 for WOT 02113080-01 â€œ16.8.4 SW-RIS-604 - CCâ€ This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Maintenance. <I> **** Actions Taken **** Discussed this Issue with; Craft/Maint Supervisor III, Component Group Manager, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385849 | CR | 20181018 |  | 3 | PCR: SOP-CRD-HCU |  |  |  | N | NO | <D> **** Detailed Description **** section 5.3 charging N2 with out draining accumulator has you inop the HCU affected, while the section for clearing high water level does not have us inop the hcu. these sections both only manipulate the 111 valve and the P6 connection. do we need to inop for charging without draining? recommend eval and changing procedures to match. <I> **** Actions Taken **** informed MCR initiated CR <N> **** Equipment Description **** sop-crd/hcu-ops
385850 | CR | 20181018 |  | 3 | MTE labeled as RAM, but then cleared. |  |  |  | N | NO | <D> **** Detailed Description **** Two instances of RAM mte taken into a clean area (501 main control room). See AR/CR 00385252 and 00385763. Those were good catches. After both instances it was found that the ram labeled MTE was clean. This leads to the question, how much MTE that is labeled RAM is actually contaminated and how much of it is clean? How often is contaminated MTE re -evaluated? The cost savings in not having to purchase new clean MTE so we have clean tools to use should be factored in. <I> **** Actions Taken **** Added this to the CHAMPS action list to track, wrote CR, spoke with others with no definite answer or path forward. <N> **** Equipment Description **** no epn
385851 | CR | 20181018 | CAQ | C | (QA) Required M&TE No./Cal. Due Date are Blank in ODCM WOT |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The Quality Assurance Record (QAR) for one Work Order Task (WOT) contains blanks for the Measuring and Test Equipment (M&TE) Number and Calibration Due Date for a Frequency Counter required for at least three work steps. Potential consequence is that â€œifâ€ the two blanks indicate that a calibrated frequency counter was not used, this would question the validity of the WOT, as well as, the operability/functionality of the equipment tested, which was SW-RIS-604 for the 18-month Offsite Dose Calculation Manual (ODCM) Surveillance Requirement (SR) 6.1.1.5 Table 6.1.1-1 Function 4. Factual Basis: â€¢ WOT 02111562-01 â€œ16.8.1 SW-RIS-604 - CCâ€ required completing PPM 16.8.1 â€œCC/RC - Standby Service Water System Effluent Radiation Monitor Ch Aâ€ rev 012, which specified the use of a â€œfrequency counterâ€ in at least the three 7.13.1, 7.13.2, and 7.13.13. â€¢ Within QAR WOT 0211156201 for WOT 02111562-01, PPM 16.8.1 step 5.1 â€œCalibrated Equipmentâ€ contains a table for the technicians to enter the â€œM&TE Numberâ€ and â€œCal. Due Dateâ€ for a â€œFrequency Counterâ€; however, both columns were left blank in the row for this M&TE item. â€¢ Additionally, PDF page 58 within QAR WOT 0211156201 for WOT 02111562-01 contains an â€œM&TE Informationâ€ section that does not list any M&TE Numbers, but lists UTC Numbers and Model Numbers for two of the three M&TE items, and is missing the M&TE information for the Frequency Synthesizer with â€œM&TE Numberâ€ C001638 and â€œCal. Due Dateâ€ of 10/12/18. Insight: â€¢ Upon notification by Quality, and further research and investigation, a Maintenance Supervisor determined the â€œM&TE Numberâ€ of C004929 and the â€œCal. Due Dateâ€ of 5/18/18 listed in the table in step 5.1 for a â€œScaler -timerâ€ is the correct M&TE information for the â€œFrequency Counterâ€. Therefore, a calibrated frequency counter was used, but its M&TE information was inadvertently entered on the wrong row in the table in step 5.1 in the WOT. â€¢ Quality verified with the Tool Room that M&TE Numberâ€ C004929 is a frequency counter. â€¢ A â€œScaler-timerâ€ was not used because it was only needed for the conditional steps in section 7.11 that were correctly marked â€œNAâ€ based on acceptable â€œAs-Foundâ€ data recorded within several earlier steps. â€¢ As of 10/3/2018, the TIMM305 panel in Asset Suite now lists all three M&TE used; however, the QAR WOT 0211156201 record is still incorrect for the M&TE information on the PDF pages 12 and 58. See EDMS for more detail. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Maintenance. <I> **** Actions Taken **** Discussed this Issue with; Craft/Maint Supervisor III, Component Group Manager, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385852 | CR | 20181018 |  | 3 | RHR System restoration tasks with no ALARA Tasks |  |  |  | N | NO | <D> **** Detailed Description **** There were three WOTs on that required entry into High Radiation Area that did not have ALARA Tasks associated with them. WOT 02132271 06, â€˜PMT PERFORM OSP-RHR/IST-Q703â€™, did not have an RWP Hold and thus never had an ALARA Task planned. Also WOTs 02132271 08 & 09 , â€˜SP (ELEC) ELECTRICAL SUPPORT FOR OSP-RHR/IST-Q703â€™, and â€˜SP ( I&C) SUPPORT TO INSTALL GAUGE OSP-RHR/IST-Q703â€™, respectively, did not have RWP Holds and thus never had ALARA Tasks planned. A call from the OCC expressed concern with the potential delay while the ALARA Tasks were created and planned. Instead, these WOTs were referenced to existing ALARA Task 02125817 01 01 and dose for both I&C and Electricians was added to that AT. The 80 p-mrem that was added was not in the October dose budget, but was not processed as Emergent work as these tasks were planned as part of the RHR System window all along. To expedite the work, save transit dose, minimize HRA briefings and avoid potential system window closure delays there were two additional WOTs referenced to ALARA Task 02125817 01 01. WOT 02111391 06 for â€˜RHR-M-P/2B PMT: SIGHT GLASS LEAK CHECK.â€™, WOT 02114147 08 for â€˜PMT LEAKAGE INSPECTION RHR-M-P/2Bâ€™ and also the taking of vibration readings on both RHR-M-P/2B and RRA-FN-3 was scope performed by Electricians on this HRA entry. <I> **** Actions Taken **** Processed the WOTs/ALARA Tasks to facilitate completion of required work, informed my supervision of the unbudgeted dose expenditure and documented this CR.
385853 | CR | 20181018 | CAQ | C | (QA) Initials of 1 Performer Not Recorded in ODCM WOT |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Quality Assurance Record (QAR) shows that the initials of one performer were not recorded within an Offsite Dose Calculation Manual (ODCM) Surveillance Work Order Task (WOT) package, contrary to MI-3.6.4 â€œWork Package Closureâ€. There are no known consequences of this non-compliance with MI-3.6.4. Requirement: â€¢ MI-3.6.4 rev 022 step 3.1.4d states, â€œAll individuals signing for steps will place their initials and name in the â€˜Record Initials of Performerâ€™ section of the work order.â€ Factual Basis: â€¢ QAR HP 0211308001 for WOT 02113080-01 â€œPPM 16.8.4 SSW System Effluent Monitor CH B - CC/RCâ€ contains PPM 16.8.4 rev 014 with step 7.3.10e signed by someone that did not place their initials and name in the â€œRecord Initials of Performerâ€ section of the work order. â€¢ The individual did not place their initials and name on the PPM 16.8.4 cover page within this WOT. Insights: â€¢ Upon notification by Quality, and further investigation, a Maintenance Supervisor recognized the initials of the individual. â€¢ Quality verified that the individual is a qualified Instrumentation and Controls (I&C) Technician. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Chemistry. <I> **** Actions Taken **** Discussed this Issue with the Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385855 | CR | 20181018 | CAQ | C | (QA) Inaccurate Annual Radiological Environmental Operating | N | Y |  | Y | NO | <C> At the direction of OFM on 10.23.2018 â€“ CR 385855 Priority and Severity changed from Non-CAQ 3 to C/CAQ assigned to ENLAB. <D> **** Detailed Description **** (QA) (Finding) Justification was not provided in the Annual Radiological Environmental Operating Report (AREOR) for monthly Offsite Dose Calculation Manual (ODCM) liquid sample and analyses that were not obtained in accordance with ODCM guidance. The carboy at Station 26, Intake -River/Drinking water control station, was found overflowing its 6 gallon capacity. Justification was not provided in the AREOR why the sample was considered a valid composite sample nor an accurate analysis given that the carboy had overflowed during collection. Results from this sample point during this time were still reported in the 2017 Annual Radiological Environmental Operating Report (AREOR) with no additional parameters discussed. The sample at Station 26 is obtained using a composite sampler that draws water from the plant intake water system (TMU). The source of this water is the Columbia River. The station serves as a control location, as it is upstream of the plant discharge location, and also as a drinking water location as drinking water for CGS comes from this source. The sampler should have dispensed 2.4 gallons of water over the 19 days but instead dispensed an unknown volume over 6 gallons, thus some of the contents of the 19 day composite sample mixture were lost. At the time the overflowing carboy was discovered it was replaced with an empty one and set aside. There is no documentation in the AREOR on which carboy was used for analysis thus making the Results in Table A-7.1 for the time from between 2/2/17-3/1/17 invalid. Factual Basis: See EDMS for more detail This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Prigram Audit AU-CH-18. Quality recommends this CR be routed to Environmental Services. <I> **** Actions Taken **** Discussed this Issue with: Environmental Services Supervisor, Environmental Scientist III, Environmental Specialist - REMP Sampler, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385857 | CR | 20181018 | CAQ | C | (QA) ODCM Actions to Prevent Recurrence Not Documented |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) (Finding) When RFO 6.3.1 A is entered, the ODCM required Compensatory Measures are not being met to take corrective actions to prevent recurrence and document actions in the Annual Radiological Environmental Operating Report (AREOR). Not meeting ODCM required Compensatory Measures could affect regulatory margin. Factual Basis: See EDMS for more detail. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Chemistry. <I> **** Actions Taken **** Discussed this Issue with the Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385858 | CR | 20181018 |  | 3 | (QA) Insufficient Chemistry Oversight of ODCM Surveillances |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) (ARMA) Increased Chemistry oversight of the Offsite Dose Calculation Manual (ODCM) Surveillance program is needed as exemplified by multiple problems identified in a sampling of Volume 16 procedures and related ODCM surveillance Work Order Task (WOT) implementation by Maintenance, invalid ODCM sampling, and corrective actions not fully meeting ODCM Compensatory Measures. Results of procedure reviews identified two of ten ODCM Surveillance procedures were incorrect. Results of WOT reviews identified issues with 17 of 44 WOTs for ODCM Surveillances. .Examples of a lack of Chemistry oversight include Volume 16 procedures containing internal conflicts and steps that cannot be followed as written, surveillance data logged without using sufficient significant digits, leaving data entry blanks on surveillance records, and initials of all performers not on surveillance records. Invalid ODCM sampling resulted in an inaccurate annual report submitted to the NRC. The potential consequences of Chemistry continuing to provide insufficient ODCM surveillance program oversight are invalid surveillances resulting in non-functional equipment and a loss of regulatory margin for not meeting ODCM requirements. Factual Basis: See EDMS for more derail. . This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Chemistry. <I> **** Actions Taken **** Discussed this Issue with the Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385859 | CR | 20181018 |  | 4 | (QA) damaged insulation at CF-FLX-41A/1 and CF-V-804A | N | N |  | Y | YES | <D> **** Detailed Description **** (QA) During a plant walkdown, identified damaged insulation at CF-FLX-41A/1 and CF-V-804A, verified no WR in the system and generated AR-CR (pictures in EDMS) and WR | 02-00-CF-FLX-41A/1,02-00-CF-V-804A
385860 | CR | 20181018 |  | 4 | (QA) TSW-P-1B motor drain pipe missaligned to floor drain | N | N |  | Y | YES | <D> **** Detailed Description **** (QA) During a plant walkdown, identified that the TSW-P-1B motor drain pipe is not aligned with the floor drain causing a wet floor, verified no WR in the system and generated AR-CR (pictures in EDMS) and WR <I> **** Actions Taken **** Wet floor sign is already in place to address safety hazard <N> See existing AR CR 380015 / WR 29142519. | 02-00-TSW-M-P/1B,02-00-TSW-P-1B
385861 | CR | 20181018 |  | 3 | (QA) Chemistry instrument calibration checks not evaluated |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Calibration checks for Chemistry Laboratory instrumentation are not consistently evaluated for acceptance. PPM 12.1.1 â€œLaboratory Quality Assuranceâ€ provides guidance on evaluating calibration check results to determine if the instrument is reliable (i.e. analytical results are statistically valid) or should be declared out of service. Contrary to this requirement, several examples were noted where calibration checks fell outside of acceptance criteria but were not evaluated or instruments that failed calibration checks were not declared out of service. There is no evidence that instruments that failed calibration check were used for analysis. Factual Basis: The following examples occurred March â€“ September 2018: â€¢ Twelve calibration checks were outside of the 2 sigma acceptance band for the following instruments and the appropriate actions were either not taken or not documented: o gas chromatograph (4 examples) o ion chromatography (5 examples) o total organic carbon (3 examples) â€¢ Four examples where instruments fell outside of the 3 sigma acceptance band and were not declared out of service. Requirements: See EDMS for more details. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Chemistry. <I> **** Actions Taken **** Discussed this Issue with the Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385862 | CR | 20181018 |  | 4 | (QA) TSW-P-1B has excessive packing leakage | N | N |  | Y | YES | <D> **** Detailed Description **** (QA) During a plant walkdown, identified that TSW-P-1B has excessive packing leakage that sprays past the plexiglass shield onto the floor, noted TSW-P-1A has no plexiglass shield and appears to not spray out past the gland area. Verified no WR in the system and generated AR -CR (pictures in EDMS) and WR. The leakage to the floor drains to a deck plate gap in an area outside of a walkway mitigating the safety risk. | 02-00-TSW-P-1B
385863 | CR | 20181018 |  | 4 | (QA) TSW-F-1A has 80 dpm packing leak | N | N |  | Y | YES | <D> **** Detailed Description **** (QA) During a plant walkdown, identified that TSW-F-1A has approximately 80 dpm packing leak to floor. Verified no WR in the system and generated AR-CR (pictures in EDMS) and WR. The leakage to the floor drains to a deck plate gap in an area outside of a walkway mitigating the safety risk. | 02-00-TSW-F-1A
385864 | CR | 20181018 |  | 3 | (QA) Out Of Date Lab Quality Control Standard Used |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Out of Date Lab Quality Control standard used without extension date labeling in accordance with SWP-CHE-05. The use of out of date standards could invalidate the sample due to not validating the accuracy of the instrument. Factual Basis: During the Halogenation surveillance step 8.4.3.A provides guidance for using a HACH Colorimeter to determine Chlorine (Total, Free, and Combined) concentrations in blowdown for use in the NPDES permit. Per the first note in section 6.2.1 â€œA QC check should be performed with each set of samples analyzed using this method. A set of samples is typically defined as once per shift.â€ And â€œSecondary standards serve as a quality control check to verify that the instrument is operating correctly. Use of these standards verify that the instrument performance has not changed from the initial performance evaluation.â€ During the Audit observation it was noted by the auditor that the QC standards had an expiration date of August 2018, printed on the side. The auditor stopped the evolution and challenge the chemistry tech on whether the use of these standards would invalidate the QC. The Chemistry Tech stated that he believed a Laboratory Standard Expiration Date Extension Form was filled out, permitting him to use these standards. The Chemistry tech stopped, placed his work in a safe condition and verified with supervision that the standards were extended. While extensions are permitted within plant procedures, there was no indication of this anywhere within the sample room or on the standards. Chemistry Leadership was able to produce the extension form upon request. However, this form would not have been available to the tech during the audit observation,or to any previous techs performing this analysis unless the documentation was requested from the Chemical Management Program Lead. Insights: Per SWP-CHE-05, â€¢ Expired chemical materials may be used if user managers/supervisors evaluate the materials and determine the chemical integrity does not compromise the end-use application. This evaluation should be documented and such documentation retained with the expired chemical material. â€¢ The container label should be marked to indicate that itâ€™s acceptable to use past the expiration date This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Chemistry. <I> **** Actions Taken **** Discussed this Issue with the Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385865 | CR | 20181018 |  | 3 | (QA) Use of Expired Reagent/Standard |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Expired Reagent/Standard was used during the ICP metals analysis (CI 11.1 Metals Analysis). Chemistry has been using an expired Reagent/Standard for almost 2 months. Since this is an internal standard, it is common to all samples, standards, and blanks, there is no impact to the validity of the analysis results. Any change to the internal standard would have been seen by the results and the analysts/Chem Techs. However, it could lead to inaccurate results if expired chemicals are used in general. It is why expiration dates are shown and reviewed continually. Factual Basis: â€¢ Per PPM 12.1.1, Laboratory Quality Assurance, Section 5.1.6c, â€œReagents that have exceeded their shelf life should not be used. Shelf lives may be extended by Chemistry Supervision if evidence of reagent integrity or acceptance of possible error is documented. Expiration date extension will be documented on Attachment 15.4â€¦â€ â€¢ Per PPM 12.1.4, Laboratory Standards Program, the definition of â€œExpiration Date â€“ The date beyond which a standard/chemical shall not be used unless extended by the Laboratory Supervisor/Designee.â€ â€¢ Per PPM 12.1.4, Step 5.3, â€œNo standard may have an expiration date exceeding that of its parent.â€ â€¢ Per PPM 12.1.1, Section 5.1.6, a Stock Chemical Inventory is â€œto be performed monthlyâ€¦â€ â€¢ A 250 ppm Yttrium (Y) Internal Standard/Reagent that expired on 07/31/18 was being used. The Chem Tech that was using the Internal Standard was unaware that it had expired. â€¢ The only Yttrium Internal Standard (10000 ppm) that could be found had a different lot number than the one that made the Internal Standard/Reagent that was being used per the Reagent Log (Refer to Reagent #14089). â€¢ This chemical has been used at least twice per week (Mondays and Thursdays) from August 1 through the present. This means that more than one Chem Tech has had the opportunity to identify this issue. â€¢ This issue was not caught during the required Monthly Stock Chemical Inventory. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Chemistry. <I> **** Actions Taken **** Discussed this Issue with the Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385866 | CR | 20181018 | CAQ | D | Received 4.826.P1(1-2) alarm | Y | N |  | N | YES | <D> **** Detailed Description **** â€œSWITCHGEAR FILTER 53A DIFFERENTIAL PRESSURE HIGH/LOW alarm Alarm came in and immediately cleared twice. Ops2 investigated and found WMA-DPIS-53A is reading high at 0.75 â€œH2O with a setpoint of 0.8â€ H2O. WO 02124441 is being processed for WMA-FL-52A/53A being at end of roll which was initially identified 9/2017 under WR 29138723. ARP direction to MANUALLY ADVANCE WMA-FL-53A could not be completed due to being at END OF ROLL. <I> **** Actions Taken **** Recommend expediting WO 02124441 | 02-00-WMA-FL-52A
385868 | CR | 20181018 | CAQ | D | FP-ENG-110 coolant temp gage | N | Y |  | N | YES | <D> **** Detailed Description **** coolant temp gage low peg is 100, with the engine block heaters secured and the engine at approx 60 degrees. the gage currently reads 120 degrees. PPM 15.1.4 has pre-req's for temp being greater than 110, but with the gage not indicating correctly at low temps we would have to verify temps with a pyro or infared thermo. <I> **** Actions Taken **** informed the MCR initiated CR/WR | 02-00-FP-ENG-110
385869 | CR | 20181018 |  | 3 | (QA) Cross Check Sample Recovery Accuracy |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Expectation for cross check sample recovery not met for three chemistry analysis. Improper Cross Check samples can call in to question results for analyses where a report of accuracy is not given. Factual Basis: â€¢ In NWT BWR/Q-Chem Set 123 Analysis Results (May 2018), the Nickel (Ni) and Zinc (Zn) % Average Recoveries were 162% and 148%, respectively. This did not meet the expectation for Cross Check Sample Recovery. As documented in CR 379622, the reported values for Ni and Zn were incorrect as the proper dilution factor had not been included as part of the reporting. â€¢ In NWT BWR/Q-Chem Set 119 Analysis Results (May 2017), the Ni (Ni) % Average Recovery was 156%. This did not meet the expectation for Cross Check Sample Recovery. â€¢ In NWT BWR/Q-Chem Set 118 Analysis Results (January 2017), the Nickel (Ni) % Average Recovery was 72%. This did not meet the expectation for Cross Check Sample Recovery. â€¢ As documented in CR 379617, it was found that the Yttrium (Y) internal standard was off and was attributed to an old auto pipette. (NWT BWR/Q-Chem Set 119 Analysis Results) â€¢ As documented in CR 381888, the reported values for Ni was incorrect as the wrong dilution factor was entered. (NWT BWR/Q-Chem Set 118 Analysis Results) Insights: â€¢ The only way to truly know if routine samples results are accurate is to review the results themselves and to compare them to the results that are normally seen from a given sample point. â€¢ If Chemistry Techs were reviewing the ICP data and the internal standard recovery on a routine basis, this may have been caught. (NWT BWR/Q-Chem Set 119 Analysis Results) The Yttrium yields are normally evaluated when entering sample data to the paper data sheets, but NWT data sheets did not have a place to enter Yttrium yields for their data analysis results. The paper data sheets for NWT now contain a column for Yttrium yields. â€¢ CR 379617 states that there was the pipette used was drifting. Since the pipet was suspect, then data taken since the last good NWT results (Set 118) could have been potentially impacted by this pipet. This issue was reviewed by the Chemistry Operations Supervisor and the yields were all within +/- 10% It was determined that no questionable data was reported. However, this review was not documented. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Program Audit AU-CH-18. Quality recommends this CR be routed to Chemistry <I> **** Actions Taken **** Discussed this Issue with the Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385870 | CR | 20181018 |  | 3 | (QA) HU Tools Not Consistently Applied in Chemistry |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) ARMA Multiple behavior shortcomings, lack of human performance/error prevention tool use and human performance errors were identified during the Chemistry audit that demonstrate Chemistry personnel are not consistently engaged nor routinely applying EPTs. This has resulted in failure to meet ODCM action requirements and inaccurate regulatory reporting. Additionally, a plant component was installed incorrectly and a Laboratory Quality Control standards was not labelled as required. In several instances an audit team member needed to intervene to correct behaviors or prevent a mistake. These examples pose an increased risk to personnel and plant safety. See EDMS for more detail This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Chemistry. <I> **** Actions Taken **** Discussed this Issue with the Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385872 | CR | 20181018 |  | 3 | No isometric drawings for TMU-AV-4A(B,C) & TMU-V-713A(B,C) |  |  |  | N | YES | <D> **** Detailed Description **** WO 02132538 is being planned to address AR CR 383572 but piping isometric drawings for the existing 2" piping to/from TMU-AV-4A(B ,C) and its 3/4" branchlines to TMU-V-713A(B,C) at the discharge of TMU-P-1A(B,C) cannot be identified in the currently active CVI files. Reference AED M660 Detail F. The isometrics may exist in the Contract 225 record (vault) files or the isometrics may need to be created based upon field as-built effort. | 02-00-TMU-AV-4A,02-00-TMU-AV-4B,02-00-TMU-AV-4C,02-00-TMU-V-713A,02-00-TMU-V-713B,02-00-TMU-V-713C
385873 | CR | 20181018 |  | 3 | Evaluate verbage and instruction of ABN-SECURITY |  |  |  | N | NO | <D> **** Detailed Description **** During conduct of Security Integrated Force on Force exercise including shift manager and control room supervisor verbiage and actions were questioned from ABN -Security. ABN-Security 4.1.5 has a note above indicating that the control room will minimize Public Address system, PA, announcements allowing security use of the PA system. Question arose that 4.1.5 a/b/c drives control room to use the PA. Please evaluate language and steps involved to include suggestion of an â€œorâ€ announcement from control room if security has already made the announcement. Complete additional assignments as needed. <I> **** Actions Taken **** Notified Security Management.
385874 | CR | 20181018 |  | 3 | Security controller and player radios not receiving |  |  |  | N | NO | <D> **** Detailed Description **** Security controller and player radios not receiving information from specific security responder location. Contact Security Drill Program Coordinator for additional information. <I> **** Actions Taken **** IS Change Gear ticket initiated to evaluate transmission and or interefernece (IR -0034629). Security Management was notified.
385875 | CR | 20181018 | CAQ | D | PRM-SR-1 failed to restart | N | Y |  | N | YES | <D> **** Detailed Description **** PRM-SR-1 failed to restart correctly following a manual shutdown and restart of PRM-SR-1 per WO 02135216. . PRM-SR-1 failed to connect. The screen displayed "Unable connect to socket, trying to reconnect" and is hung up <I> **** Actions Taken **** Notified Sys Engineer. Vendor has been contacted for support. wrote CR. | 02-00-PRM-SR-1
385876 | CR | 20181018 | CAQ | C | Updates for FSAR Tables 3.6-6 and/or 3.6-9 needed |  |  |  | N | YES | <D> **** Detailed Description **** FSAR Table 3.6-6 presents a summary of Design Loads (including differential pressures) in Reactor Building areas where pipe breaks (failures) are postulated to occur and FSAR Table 3.6-9 presents a summary of subcompartment pressure analyses (Maximum Differential Pressures) between Reactor Building rooms associated with postulated pipe breaks. For each area, the FSAR Table 3.6-6 differential pressure Design Load should always be greater than or equal to the FSAR Table 3.6-9 maximum differential pressure subcompartment pressure analysis load. In some cases, the data currently presented by these FSAR Tables appears to be contrary to that convention (rooms R509, R510, and R511) as a result of not administratively updating the FSAR Table information when the analysis information has changed. For resolution, these FSAR Tables need to be reviewed and updated as appropriate for the current subcompartment pressure analyses and the current structural analyses for each room area. This is an administrative issue only - adequacy of the existing subcompartment pressure analyses and structural analyses is not being questioned. Additional editorial corrections for FSAR Table 3.6-6: Remove the k or K from the Equipment Load indicated for Pipe Break 120-8, Pipe Break 126-3, 5, and Pipe Break 139-1. The k or K is redundant. Additional corrections for FSAR Table 3.6-9: 1) The Line Designation presented for 422 ft Elevation Room R15/R112 is incomplete (appears to be missing -4 at the end). 2) The Line Designation descriptions throughout the Table are unconventional with respect to their associated flow diagrams. For example, 4 in. RCIC (13)-4 should be changed to 4"RCIC(13)-4, 4 in. AS (11)-2 should be changed to 4"AS(11)-2, 6 in. RWCU (2)-4 should be changed to 6"RWCU(2)-4, etc. 3) 548 ft Elevation Room R510 is described as Valve room (should be RWCU heat exchanger room). . This is a legacy issue - suggest resolution assignment to Design Egnineering Mechanical Design Basis group. <I> **** Actions Taken **** Room R509: Existing AED CAL 6.19.53-SV-94 includes evaluation of 1 psi room pressure for R509 (conservative compared to the 0.9 psi maximum differental pressure for room R509 currently indicated by FSAR Table 3.6-9). Other existing calculations include evaluation of even higher room pressures for room R509 - AED CAL 6.19.53-SV-95 and AED CAL 6.19.18-SV-95. Room R510: Existing AED CAL CE-02-84-51 includes evaluation of R548 room R510 for 2.9 psi differential pressure (conservative compared to the 2.7 psi maximum differential pressure for room R510 currently indicated by FSAR Table 3.6-9). Room R511: Existing AED CAL 6.19.18-SV-95 includes evaluation of 6.6 psi room pressure for room R511 (conservative compared to the 6.3 psi maximum differential pressure currently indicated in FSAR Table 3.6-9 for room R511). | 02-00-R-BLDG-MISC
385881 | CR | 20181018 | CAQ | C | (QA)Safety related parts bypassed Quality Receipt Inspection |  |  |  | Y | I DONT KNOW | <D> **** Detailed Description **** This CR is to document an issue with EN fabricated safety related parts bypassing Quality Receiving Inspection. While investigating an issue with parts fabricated for CID 12065, it was discovered the O-Ring retainer clips fabricated for R23 assembly did not go through Quality Receiving Inspection. The parts created on WO 02066096 never went through receipt inspection as required for first time receipt inspection of EN fabricated parts. The traceability of the parts remaining in the warehouse is in question, as the last QC Receipt inspection in 2015 approved 50 items and more than 60 items have been issued with a significant quantity still in stock against this tag. Recommend CAQ assigned to SCS <I> **** Actions Taken **** Notified Supply Chain Warehouse Supervisor Removed Suspect material from inventory. | 02-00-MS-RPV-3
385884 | CR | 20181018 | CAQ | C | (QA) Vessel Head O-Rings Retaining clips do not match CID | Y | N |  | Y | YES | <D> **** Detailed Description **** This condition report is to identify a material specification change that was not reviewed and approved prior to use. Reactor vessel head O-Ring retainer clips used during R23 were fabricated from SA240 Type 316 material when the approved Catalog ID description calls out ASTM A479 Type 316 material. . During Receipt Inspection of Reactor Vessel Head O-Rings fabricated to support R24, a material discrepancy with the CID 12065 description was identified. The clips were fabricated on WO 02100601 from SA240 Type 316 instead of A479 Type 316 as required by the CID. While investigating the issue, it was discovered the O-Ring retainer clips fabricated for R23 assembly were also made from the SA240 Type 316 material purchased on CID 36149. . WO 02066096 to fabricate the clips for R23 cancelled the material request for the A479 on CID 14676 that has been used in the past. The planner created CID 36149 requesting the SA240 material. There is no information in the work order to support the material change. Both of the material CIDs are safety related material, both are Type 316 stainless steel. . Based on discussion with Reactor Maintenance, the clips serve as an installation aid to keep the Inconel vessel head O-rings in place and seated while the vessel is assembled. The clips and associated retainers are captive after the vessel head is in place. <N> After reviewing PPM 10.3.22 steps 6.1.8 - 6.1.13, CVI-DWG- 02B13-06,20 and discussions with Reactor Maintenance, the clips serve as an installation aid to keep the Inconel vessel head O-rings in place and seated while the vessel is assembled. Based upon the PPM 10.3.22 and CVI-DWG-02B13 -06,20 the retainer clip is held in place by a snap ring to the retainer pin and thus fully captured during assembly, thus there is no concern with the clip being dislodged. Additionally, after reviewing the material stress allowable the two clip materials have identical values. Both have similar chemistry values and the chemistry behavior in the head flange environment is expected to be identical. Based upon this information the difference in materials does not impact the design function of any components. . Recommend Assignment to Maintenance | 02-00-MS-RPV-3
385887 | CR | 20181018 |  | 4 | Two Dead Birds in N1-Spare Berm |  |  |  | N | YES | <D> **** Detailed Description **** This CR is on a spare transformer located on the warehouse grounds. Two dead birds were found in the berm for E-TR-N1-SPARE. Recommend removal of the birds. <I> **** Actions Taken **** Contacted supervision and generated work request. | 02-00-E-TR-N1-SPARE
385888 | CR | 20181018 |  | 3 | Benches/overhang for Boot gripper for building 88 |  |  |  | N | NO | <D> **** Detailed Description **** It has been brought to CHAMPS attention that, with icy winter conditions on the way, Building 88 does not have a bench in which to safely don and doff shoe grippers. Slips, trips and falls are just some of the many safety hazards that can cause serious injury if not mitigated correctly. With the bench and possible construction of an overhang this will promote safely donning and doffing of shoe grippers for all those who travel in and out of 88. Whether it be Contractors, Security, Quality or someone grabbing lunch. <I> **** Actions Taken **** Wrote this CR, added it the CHAMPS backlog to maintain tracking. Will bring the next EN safety committee/hazards meeting <N> **** Equipment Description **** Building 88
385889 | CR | 20181018 |  | 3 | Missing Key PSRO Key Audit |  |  |  | N | NO | <D> **** Detailed Description **** Key audit of PSRO keys found that there are two tags for M260, but only 1 key. Informed OPS coordinator to replace key. Reference WO 02125870.
385891 | CR | 20181018 |  | 3 | 2018 NRC 71111.11 Debrief Observations |  |  |  | N | NO | <D> **** Detailed Description **** The NRC provided two observations during their site debrief on 10/18/2018 for the 71111.11 inspection. First, the NRC commented on scenario critical tasks for two scenarios. In one scenario, a critical task did not materialize. In another scenario (administered during week 1), the evaluators identified an additional critical task not mentioned in the scenario guide. Second, the NRC felt that enhancing the amount of detail in LORQ written exam question answer explanations would benefit the station in that it would be a better study tool for operators and anyone that takes the exams. <I> **** Actions Taken **** Assign to G. Wyatt to enhance scenarios and evaluate enhancement feedback on written exam answer explanations.
385892 | CR | 20181018 |  | 4 | Repair/replace EDR-TM-603 | N | N |  | N | YES | <D> **** Detailed Description **** while performing ISP-FDR/EDR-X301 step 7.14.4, we were unable to see the pilot light illuminate when we jumpered terminals 87 and 88. We could hear relays energize. while holding the jumper on the terminals, we momentarily lost contact and the annunciator A3-5.8 alarmed. We stopped informed CRS that the annuciator came in and we were effectively on step 7.14.6, but we did not have about 1 minute delay per step 7.14.5. <I> **** Actions Taken **** talked with CRS and supervisor. We all agreed we could continue with step 7.14.8 and the rest of the procedure, making note that we did not have about 1 minute delay between jumpering 87 and 88. After performing step 7.14.8 we noted the pilot light was extremely dim, but it was illuminated. This AR needs to address replacement of timer EDR-TM-603 | 02-00-EDR-TM-603
385893 | CR | 20181018 |  | 4 | HSSF alarm with both pumps found off. | N | N |  | N | YES | <D> **** Detailed Description **** Supply Facility alarm received at P500 panel. Found HSSF -P-1A tripped off with suction valve indicating open, and HSSF-P-1B ( standby pump ) not running with suction valve indicating closed. <I> **** Actions Taken **** Performed ARP 4.500, section 2-7. When the start button was depressed, heard a relay pick up and cooldown/ recirc. .started as indicated by dropping temp. on their respective controllers. When Temp. stpts. were reached HSSF-P-1A started. Noted that the seal temp. controller did not indicate a dropping temp. HSSF-P-1A also sounded like it was struggling while running. Emmitted a rubbing/mech. noise from within what appears to be a belt housing. No other local alarms noted, and a light test of the individual alarms was performed. | 02-00-HSSF-P-1A,02-00-HSSF-P-1B
385894 | CR | 20181018 | CAQ | D | Benton County Siren D1 reported a partial alarm. | N | Y |  | N | YES | <D> **** Detailed Description **** During the river siren polling for the annual Exclusion Area Siren test, Benton County Siren D1 reported a partial alarm. The siren is fully functional, just one out of the ten drivers has failed which will reduce the output volume slightly. The test observer at siren D1 reported a successful alert tone test. . Also during the Annual Exclusion Area Siren Test an observer at Benton County siren site D6 reported they did not hear the initial Benton County PA announcement but did hear the alert tone and the second PA announcement once they removed their ear plugs. They were also able to hear the Franklin county PA tests and Alert tone. All the other thirty three siren site observers we able to hear all four PA announcements and both alert tones. <I> **** Actions Taken **** Notified EP, and dispatched a tech to resolve the issue. Recommend closing to WR. <N> **** Equipment Description **** Benton County Siren D1
385895 | CR | 20181018 |  | 3 | Failures during LORQ Biennial Requal Written Exam |  |  |  | N | NO | <C> At the direction of OFM on 10.23.2018 â€“ CR 385895 Severity changed from Non-CAQ 4 to 3 assigned to OPSMGT. <D> **** Detailed Description **** 3 Individual failures occurred during the biennial written exam administered on 10/17/18. Remediation will be in accordance with TDI-02. <I> **** Actions Taken **** I: De-certified individuals in PQD. Notified Operations and Operations Training Management. A: Recommend Severity Level 4. Additional detail withheld due to exam security requirements. R: Remediation IAW TDI-02.
385896 | CR | 20181018 |  | 3 | Failures during LORQ Annual Requal Simulator Exam |  |  |  | N | NO | <C> At the direction of OFM on 10.23.2018 â€“ CR 385896 Severity changed from Non-CAQ 4 to 3 assigned to OPSMGT. <D> **** Detailed Description **** One Crew and six individual failures occurred during the Annual Requal Simulator Exam administered on 10/18/18. Remediation will be in accordance with TDI-02. <I> **** Actions Taken **** I: De-certified individuals in PQD. Notified Operations and Operations Training Management. A: Recommend Severity Level 4. Additional detail withheld due to exam security requirements. R: Remediation IAW TDI-02.
385897 | CR | 20181018 |  | 4 | Radwaste Chiller E/P not correctly installed | N | N |  | N | YES | <D> **** Detailed Description **** During the functional check of new Radwaste Chiller WCH -CR-51A with the Vendor (Trane Technician), it was discovered that condenser outlet air operated valve TSW-V -H51 would not stroke when directed to from the associated 0 to 10 VDC chiller output signal. Troubleshooting revealed newly installed electro pneumatic transducer WCH-E/P -PCV/H51 air supply was not properly connected â€“ it was inappropriately connected to bulkhead fitting A7 when it should have been connected to air supply valve S2, as indicated in WO 02129940-05 and EC 17099 page 32.9. Work instructions were correct â€“ field installation was wrong. This condition caused a delay in the startup testing of the new chiller, requiring a reschedule of the Trane Technician to come back for a second day of testing. <I> **** Actions Taken **** Investigated reason for TSW-V-H51 not responding. Developed work instructions, corrected the issue and satisfactorily performed retest and stroke of TSW-V-H51 with the chiller output signal of 0-10 VDC. Notified Operations (SSS) of this issue and subsequent corrective actions. | 02-00-TSW-PCV-H51,02-00-WCH-CR-51A,02-00-WCH-E/P-PCV/H51
385901 | CR | 20181019 |  | 4 | WCH-V-664 leaking | N | N |  | N | YES | <D> **** Detailed Description **** WCH-V-664, vent valve for WCH-EV-51B (507' chiller B), is leaking at a rate of approximately 1 drop every 6 seconds. The associated piping with this valve is in a corroded state as well. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** RW 507' | 02-00-WCH-V-664
385902 | CR | 20181019 | CAQ | D | Damage to 525' flood barrier flooring in Div 1 HVAC Rm | Y | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02103869-01, then taken back to complete <D> **** Detailed Description **** During rounds on 10/19, it was discovered that there are multiple gouges in the flood barrier flooring in the Division 1 HVAC room. Pictures are attached to this CR. <I> **** Actions Taken **** Informed Shift Manager, initiated CR. <N> **** Equipment Description **** RW 525' Div 1 HVAC Rm southwest in room | 02-00-W-BLDG-MISC
385903 | CR | 20181019 |  | 4 | TMU-V-1B leaks by when closed electrically | N | N |  | N | YES | <D> **** Detailed Description **** After securing TMU-P-1B per SOP-TMU-SHUTDOWN the EO noted that TMU-P-1B was rotating backwards, indicating leakby on the pump discharge valve, TMU-V-1B. The EO took manual control of the MOV and shut the valve an additional half turn , stopping the reverse rotation of the pump. Request maintenance evaluate the cause for the leakby (either MOV torque switch improperly set or valve seat leakby) and repair. | 02-00-TMU-P-1B,02-00-TMU-V-1B
385904 | CR | 20181019 |  | 3 | WO 02116845-03 Returned to Planning |  |  |  | N | NO | <D> **** Detailed Description **** Before implementation of WO 02116845-03, craft identified multiple enhancements that needs to address contingencies for the â€œwhat ifâ€ scenarios. The housing cover rotation requires installed set screws to be removed and directs a torque wrench be used to with a maximum of 35 in/lbs applied during removal. Set screw final torque spec is 33 in/lbs in conjunction with high strength thread locker. The WO does not identify a contingency if the set screws are unable to be removed applying the maximum torque value. The WO also requires a foam applicator be used to clean residual lock tight from the set screw holes to prevent FME from becoming lodged in the transmitter housing. The maintenance of CRD-LT-13B requires a 12 hour action statement to be entered and warrants the additional planning and resource allocation prior to implementation. <I> **** Actions Taken **** Informed supervision, returned WO to planning, wrote CR. <N> **** Equipment Description **** 522 RX | 02-00-CRD-LT-13B
385905 | CR | 20181019 |  | 3 | minor oil leak upper sightglass TMU-M-P/1A | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of WO#02123140-04 electricians looked for leakage at the bearing oil sight glass per work steps. a very small amount of bearing oil can be seen accumulating along the bottom edge of the upper sight glass. Work steps provide no direction or action to remedy the leakage, if detected. Work steps only direct craft to notify supervision if leakage is detected. <I> **** Actions Taken **** followed work steps as written. Notified Supervisor and CRS of condition and write CR. <N> **** Equipment Description **** TMU pumphouse TMU-M-P-1A upper bearing sightglass | 02-00-TMU-M-P/1A
385906 | CR | 20181019 |  | 4 | Flexible conduit not completely made-up TMU-M-P/1A | N | N |  | N | I DONT KNOW | <C> At the direction of OFM on 10.23.2018 - CR Priority and Severity changed from D/CAQ to 4/Non-CAQ â€œOps should update Ops Review for TS SSC Flagâ€ <D> **** Detailed Description **** During the performance of activities associated with WO #s 02123140 and 02134236-28, electricians noticed a Flexible conduit, that is associated with TMU-M-P/1A, is not made up on one end. One end of the Seal-tight terminates on a junction box. The other end is not completely made up to the Rigid Steel conduit where the Flex transitions to rigid Conduit. The flex conduit in question is NOT associated with the main Motor Leads. <I> **** Actions Taken **** Notified Supervisor, Notified CRS, Write CR and WR. attached pictures <N> **** Equipment Description **** TMU-M-P-1A Flex Conduit TMU pumphouse | 02-00-TMU-M-P/1A
385907 | CR | 20181019 |  | 3 | RRC-M-P/1A(B) oil level sensor drawing depcitions |  |  |  | N | YES | <D> **** Detailed Description **** Not all drawings depicting the RRC pump motor (RRC-M-P/1A(B)) upper and lower oil reservoir level sensors (for level switches RRC-LS-1A(B) and RRC-LS-2A(B)) were updated for the EC MALT 8941 design change. AED D-OILLEVELSENSOR-282 provides details for the new piping/tubing installation and AED D-OILLEVELSENSOR-279 provides details for the new oil level sensors. 1) The description of Item 1 on AED D-OILLEVELSENSOR-282 should be enhanced to reference AED D-OILLEVELSENSOR-279. 2) AED D-OILLEVELSENSOR-279 should be enhanced to reference AED D-OILLEVELSENSOR-282 for the complete installation configuration (sensors, piping/tubing, and manual valves). 3) Provided the above drawing enhancements are made, the existing update for CVI 02B35-13,11 Item 46 should be sufficient. But should consider modifying the Item 46 update to include reference to AED D-OILLEVELSENSOR-282 (not just AED D-OILLEVELSENSOR-279). 4) CVI 02B35-05,26,1 and CVI 02B35-05,26,2 both depict the subject oil level sensors with details very similar to CVI 02B35-13,11 but were not updated by EC MALT 8941. 5) CVI 02B35-09,23 and CVI 02B35-13,20 both depict the subject oil level sensors (though in less detail) but were not updated by EC MALT 8941. 6) The height of the main conduit box depicted in CVI 02B35-09,23 (48 inches) is discrepant with that depicted on CVI 02B35-13,20 and CVI 02B35-13,18 (77-3/8 inches or 6 feet 5-3/8 inches). . Suggest nonCAQ resolution assignment to Design & Drafting. This condition is a minor drawing issue only and does not have any impact or effect upon the continued functionality, operation, or qualification of any station SSCs. <I> **** Actions Taken **** This was noted while performing document reviews associated with AR EVAL 382943. | 02-00-RRC-LS-1A,02-00-RRC-LS-1B,02-00-RRC-LS-2A,02-00-RRC-LS-2B,02-00-RRC-M-P/1A,02-00-RRC-M-P/1B,02-00-RRC-V-921A,02-00-RRC-V-921B,02-00-RRC-V-922A,02-00-RRC-V-922B,02-00-RRC-V-923A,02-00-RRC-V-923B,02-00-RRC-V-924A,02-00-RRC-V-924B
385908 | CR | 20181019 |  | 4 | CW-FN-27 Oil Level Low | N | N |  | N | YES | <D> **** Detailed Description **** CW-FN-27 (CW-CT-2B) oil level is about 1/8" above the ADD Line. Recommend Adding Oil <I> **** Actions Taken **** Informed MCR | 02-00-CW-FN-27
385909 | CR | 20181019 |  | 3 | not able to enter planner feedback on EWP for WO#02134236 |  |  |  | N | NO | <D> **** Detailed Description **** Electricians performed Baker Testing on TMU-M-P/1A, per work instructions. step 4.1 has electricians make test equipment connections per attachment 1 (aka master 3). However, the attachment does not reflect learnings/feedback provided when the same task was performed per WO#02028121 -13. I attempted to add the feedback using EWP, in the attributes panel, but the process would not allow notes. <I> **** Actions Taken **** made test equipment connections and obtained data <N> **** Equipment Description **** EWP
385910 | CR | 20181020 |  | 4 | H13-P840.A4 drop 8-5 not lighting up on alarm test | N | N |  | N | YES | <D> **** Detailed Description **** H13-P840.A4 drop 8-5 â€œCW PMP LUBE HDR FILTER B D/P HIGH not lighting up on alarm test. When the test button is released, the tile is illuminating | 02-00-E-CP-H13/P840
385911 | CR | 20181020 |  | 4 | Housekeeping on the RW 507' floor |  |  |  | N | NO | <D> **** Detailed Description **** While conducting a monthly routine survey on the RW 507â€™, an excessive amount of debris was noticed on the floor next to the Chillers. The floor is coated with a film of concrete and welding debris. Although the Chiller replacement work is still in progress, the clean as you work standard is not being upheld. The station CRS performed a walk down of the area, and concurred that housekeeping was lacking. <I> **** Actions Taken **** The CRS and Shift Manager were informed of the findings. | 02-00-W-BLDG-MISC,02-00-WCH-CR-51A,02-00-WCH-CR-51B
385912 | CR | 20181020 |  | 4 | PWC-V-407 (flocculator drain valve) partially plugged | N | N |  | N | YES | <D> **** Detailed Description **** While trying to drain down the flocculator using PWC-V-407 for performance of WO 02095274-01 ( loop calibration of PWC-LC-101) very little flow was observed. This has been a problem in the past and has been fixed with successful loop calibration in the afterwards. See CR265201 and WR 29098358 <I> **** Actions Taken **** Notified Supervision | 02-00-PWC-V-407
385913 | CR | 20181020 |  | 3 | Dataglance validation problem |  |  |  | N | NO | <D> **** Detailed Description **** WO 02125838, when validated in Dataglance syay there is a new revision but does not show a revision when I get to the review screen. This is a repeat problem. <I> **** Actions Taken **** Verified the procedure was current with the index of controlled documents. Wrote CR <N> The requirements data was recently brought into the DataGlance package and so the validate button recognizes that there was a change to the package. If data on the requirements panel has changed, since the original package was built, it will show that the package can be replaced, but if information didnâ€™t change on the requirements panel it doesnâ€™t recognize what information changed. This CR will be closed and CR 384226-02 will drive a Datamod to correct the issue.
385914 | CR | 20181020 |  | 3 | Vision Learning Data Base Issues |  |  |  | N | NO | <D> **** Detailed Description **** Vision Learning data base does not load when attempting to logon. <I> **** Actions Taken **** Called IS duty officer. Wrote CR. <N> **** Equipment Description **** LAN
385915 | CR | 20181020 |  | 4 | Main Generator shaft ground brush is no longer a brush | N | N |  | N | YES | <D> **** Detailed Description **** Main Generator shaft ground brush inside in no longer a brush. it is metal on metal. see pictures. Please replace. <I> **** Actions Taken **** Informed MCR, brush will be lifted off of shaft till it can be replaced. <N> **** Equipment Description **** MG shaft ground brushes | 02-00-E-GEN-1
385916 | CR | 20181020 | CAQ | D | emergency light charger failure 02131819 SWS2/1 | N | N |  | N | YES | <D> **** Detailed Description **** During E-Lite QTR inspection 02131819, E-Lite SWS2/1 charger failed, (charger fault) <I> **** Actions Taken **** Wrote CR, informed OPS, Maintenance superviosr & WWM <N> **** Equipment Description **** TG SW stairwell 460 | 02-00-E-BU-SWS2/1
385917 | CR | 20181020 |  | 4 | RB 606 area temp low out of spec | N | Y |  | N | NO | <D> **** Detailed Description **** RB 606 area temp is low out of spec, 64F against a spec of >=65F. Currently not an issue while no crane operations are planned; this will be corrected as the plant transitions into SOP-COLDWEATHER-OPS. <I> **** Actions Taken **** Informed CRS, generated AR. | 02-00-R-BLDG-MISC
385918 | CR | 20181020 |  | 4 | Cooling Tower 2C is Overflowing | N | N |  | N | YES | <D> **** Detailed Description **** Cooling Tower 2C is overflowing. Please sweep this tower. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** CW yard. | 02-00-CW-CT-2C
385919 | CR | 20181020 |  | 4 | CW-FN-35 has low oil. | N | N |  | N | YES | <D> **** Detailed Description **** CW-FN-35 is below the add oil mark. Please add oil to this fan. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** CW-CT-2C. | 02-00-CW-FN-35
385920 | CR | 20181020 |  | 3 | OSP-SLC-B703 Procedure Enhancements |  |  |  | N | NO | <D> **** Detailed Description **** 1. Change required number of barrels in Materials Section from â€˜at least 6â€™ to â€˜at least 8â€™. 7.5 barrels were filled during the process this time. 2. Add prerequisite step to get key# M246 from SSS office. This key is for the boron contaminated tools/hoses cabinet on R501â€™ elevation. 3. Steps 7.50, 7.54, and 7.63 require throttling drain valves before opening MWR-V-101. Recommend allowing MWR-V -101 to be unlocked and opened prior to draining the test tank and piping if there is an operator available to do it. Throttling all of the drains prior to opening MWR-V-101 runs the risk of backing up and potentially overflowing the floor drains into the berm area surrounding the SLC skid. 4. The note before step 7.63 says â€œThe IVâ€™s in step 7.63â€¦.â€ It should say â€œThe IVâ€™s in step 7.65â€¦.â€ <I> **** Actions Taken **** Wrote CR
385921 | CR | 20181020 |  | 4 | COND-V-12B not closing completely | N | N |  | N | YES | <D> **** Detailed Description **** After closing COND-V-12B per SOP-DW-OPS step 5.2.2 using only hand force hanging on the valve, flow was checked on flow gage at SB 420', reading 2.7x10 1 gpm. Returned to valve after expanding the team to use the valve operator tool, flow reading now 4.9x10 0 gpm. Twenty minutes later flow is 3.3x10 0 gpm. Expanded the team again, another EO and SSS went to the valve and that EO was able to get another 1/8 plus turn on the valve. Flow now at 0.00 gpm. 45 minutes of time spent to close the valve and risk damage to the valve using the valve operator tool and a lot of force. <I> **** Actions Taken **** SSS notified, this CR written. | 02-00-COND-TK-1B,02-00-COND-V-12B
385922 | CR | 20181020 | CAQ | D | SJAE Condenser Rad High Alarm | N | Y |  | N | YES | <D> **** Detailed Description **** Received P602-A5 drop 4-3 (SJAE Condenser Rad High) alarm. OG-RIS-612 Off Gas Pre-Treat Activity, indicates a change from approximately 30 mR/hr to 50 mR/hr and then returned to a normal reading over the next few minutes. The Shift Chemistry Technician reported moisture in the sensing lines impacting the sample flow; the problem was corrected by clearing out the water. <I> **** Actions Taken **** Notified Shift Management and the Shift Chemistry Technician. there are no EPlan entries off this indicator. | 02-00-OG-RIS-612
385925 | CR | 20181021 |  | 3 | Dataglance validation issue |  |  |  | N | NO | <D> **** Detailed Description **** While validating WO 02126045 dataglance says that there is a new revision available. There is nothing to revise on the review screen <I> **** Actions Taken **** Verified references aganist Portal J. <N> The requirements data was recently brought into the DataGlance package and so the validate button recognizes that there was a change to the package. If data on the requirements panel has changed, since the original package was built, it will show that the package can be replaced, but if information didnâ€™t change on the requirements panel it doesnâ€™t recognize what information changed. This CR will be closed and CR 384226-02 will drive a Datamod to correct the issue.
385926 | CR | 20181021 |  | 3 | Dataglance Revision issues |  |  |  | N | NO | <D> **** Detailed Description **** While validating WO 02126048 dataglance says that there is a new revision available. there is nothing to revise on the review screen <I> **** Actions Taken **** Verified revisions against the Index of Controlled Documents <N> The requirements data was recently brought into the DataGlance package and so the validate button recognizes that there was a change to the package. If data on the requirements panel has changed, since the original package was built, it will show that the package can be replaced, but if information didnâ€™t change on the requirements panel it doesnâ€™t recognize what information changed. This CR will be closed and CR 384226-02 will drive a Datamod to correct the issue.
385927 | CR | 20181021 |  | 4 | E-TR-6/62 door and beneath the door has corrosion. | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-6/61, 6/62, 5/51 and 5/52 have a corrosion line in approx the same spot on the door I dont know if the rust is all the way thru that is what this CR is for to evaluate if the enclosures are adequate to protect the high voltage disconnect and bus work inside form the inclemental weather. the corrosion is in a broken line across the lower 1/3 of the door. Additionally there appeared to be some metal missing from below the door on E-TR-6/62. please see attached pictures. <I> **** Actions Taken **** wrote CR | 02-00-E-TR-5/51,02-00-E-TR-5/52,02-00-E-TR-6/61,02-00-E-TR-6/62
385928 | CR | 20181021 |  | 4 | PWC-V-476 leaked by while performing SOP-PW-OPS (PW crossX ) | N | N |  | N | YES | <D> **** Detailed Description **** PWC-V-476 leaked by while performing SOP-PW-OPS (PW crossX) sect 5.2 step 5.2.8.b.4. Leak by was not originally detected until the following step where PWC-V -503 was shut (step 5.2.9) after that a high pitch flow was heard from PWC-V-476. Intitial isolation of PWC-V-413 did not islolate ithe sound but diminished it. While obtaining permission to use a leveraging device we were pleasantly surprised to find that the flushing of the valve seat was sufficient to allow the valve to seat with no flow noise present at PWC-V-476 after the subsequent reshutting of the valve (PWC-V-413). <I> **** Actions Taken **** contacted the MCR cr as directed | 02-00-PWC-V-476
385929 | CR | 20181021 |  | 3 | Dataglance Revision issues |  |  |  | N | NO | <D> **** Detailed Description **** While validating WO 02126070 dataglance says that there is a new revision available. there is nothing to revise on the review screen <I> **** Actions Taken **** Verified revisions against the Index of Controlled Documents <N> The requirements data was recently brought into the DataGlance package and so the validate button recognizes that there was a change to the package. If data on the requirements panel has changed, since the original package was built, it will show that the package can be replaced, but if information didnâ€™t change on the requirements panel it doesnâ€™t recognize what information changed. This CR will be closed and CR 384226-02 will drive a Datamod to correct the issue.
385930 | CR | 20181021 |  | 4 | MSR A Drain Tank 3B Level High alarm in | N | N |  | N | YES | <D> **** Detailed Description **** 4.840.A3 "MSR A Drain Tank 3B Level High" alarm received in the MCR. HD-LIC-11A and 11A2 are in auto and controlling normally. There is a steam leak from the 3B drain tank instrument tree (WR 29145188). <I> **** Actions Taken **** Camera tour of heater bay. WR written. <N> **** Equipment Description **** 479 A/12.5 | 02-00-HD-LS-11AH,02-00-HD-TK-3B
385931 | CR | 20181022 | CAQ | D | NRC Identified - DSA-FLX-6A may exceed max allowable offset | Y | N |  | N | YES | <D> **** Detailed Description **** DSA-FLX-6A hose may be exceeding its maximum offset based on its flex hose length, hose diameter, and minimum allowable bend radius. This was NRC identified. | 02-00-DSA-FLX-6A
385932 | CR | 20181022 |  | 3 | Clearance order revision needed during implementation. |  |  |  | N | NO | <D> **** Detailed Description **** When hanging clearance order D-COND-DM-1D-001, operators questioned hanging tags in HRA C-Zones. Upon further investigation the clearance order should have made these tags "No Tags" per 1.3.64 section 2.2.6 and tag shared with D-COND-V-79/80-001. This is an obscure step in 1.3.64 and further training or controls should be considered to prevent an error like this from happening again. This is not believed to be a severity level 4 Clearance Order error but it had the potential to slow down scheduled work. <I> **** Actions Taken **** Revised the clearance order.
385934 | CR | 20181022 | CAQ | D | DCW-FLX-8 label missing (NRC Identified) |  |  |  | N | YES | <D> **** Detailed Description **** NRC identified the label for DCW-FLX-8 was missing <I> **** Actions Taken **** Informed the MCR and generated a label request. Marked up reference print located in EDMS | 02-00-DCW-FLX-8
385935 | CR | 20181022 |  | 3 | (QA) Discrepancies between FSAR & SharePoint Chemistry Org. |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Two discrepancies exits between the Chemistry organizational charts listed in Columbiaâ€™s Final Safety Analysis Report (FSAR) Chapter 13 and those posted on SharePoint. Having organizational structures depicted differently can lead to a missed license commitment. Factual Basis: â€¢ FSAR Amendment 64, Chapter 13, Figure 13.1-12, shows an Environmental/Analytical Support Supervisor which is annotated indicating a functional rather than an organizational structure. â€¢ The Chemistry Organizational chart posted on SharePoint does not show any reference to an Environmental/Analytical Support Supervisor. â€¢ FSAR Amendment 64, Chapter 13, Figures 13.1-3, 13.1-11 and 13.1-12 shows the Chemistry Organization Manager title as Chemistry/Radiological Services Manager. â€¢ The Chemistry Organizational chart posted on SharePoint shows the manager title as Chemistry Radiological Safety Manager. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. <I> **** Actions Taken **** Discussed this Issue with the Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385936 | CR | 20181022 |  | 3 | (QA) Error Corrections in 3 WOTs Did Not Meet SWP-PRO-01 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Three Work Order Tasks (WOTs) each contain data recording error corrections that do not meet the requirements within SWP-PRO-01 â€œProcedure and Work Instruction Use and Adherenceâ€. This is a procedure non -compliance issue with no known consequences. Requirements: â€¢ SWP-PRO-01 rev 031 step 4.10.8 states, â€œIF a data recording error is made, THEN PERFORM the following: o DRAW a single line through the entry (error) taking care not to obscure the data or information. o INITIAL the lined out entry. o DATE the lined out entry. o ADD the correct information. Factual Basis: â€¢ QAR HP 0208645801 for WOT 02086458-01 â€œ16.8.6 SW-RIS-605 -CFTâ€ contains a table in step 5.1 where the Frequency Counter â€œMT&E Numberâ€ and the â€œCal. Due Dateâ€ were scribbled out in a manner that obscures the previous information. â€¢ QAR HP 0210927301 for WOT 02109273-01 â€œ16.8.6 SW-RIS-605 -CFTâ€ contains a Table 7.5a where it looks like an entry in the as-found box was changed from 1.2 to 1.0 by overwriting the â€œ0â€ onto the â€œ2â€. â€¢ QAR HP 0209666901 for WOT 02096669-01 â€œ16.6.3 TSW-RIS-5 - CFTâ€ contains a Table 7.2c where it looks like an entry in the top right box was changed from 1.16 to 1.06 by overwriting the â€œ0â€ onto the â€œ1â€. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Maintenance. <I> **** Actions Taken **** Discussed this Issue with: Craft/Maint Supervisor III, Component Group Manager, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385937 | CR | 20181022 |  | 3 | (QA) FSAR LDCN Processing Step Missed in SWP-LIC-03 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Pending Final Safety Analysis Report (FSAR) changes were not captured by the Regulatory Affairs staff in Attributes field of AR-LDCN 349740, contrary to one step in SWP-LIC-03 â€œLicensing Document Change Processâ€. This is a procedure non-compliance with no known actual consequence. The potential consequence is pending FSAR changes for License Document Change Notice (LDCN) package LDCN-16-022 for EC 11288 â€œReplace Stack Monitorâ€ would not be identified by procedurally-required searches in Asset Suite while this LDCN was on hold for over 11 months. Factual Basis: See EDMS for more details This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Regulatory Affairs. <I> **** Actions Taken **** Discussed this Issue with; Licensing Supervisor, Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager Quality recommends this CR be routed to Regulatory Affairs. <N> Coaching provided to applicable staff. AR-LDCN 349740 attributes will not be updated as the LDCN has already been implemented. No further actions required.
385938 | CR | 20181022 |  | 3 | (QA) Incomplete Organization Change Forms |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Two Chemistry/Radiation Protection Organizational Change forms (Form 26239) were processed without completing all information as required by SWP-ORG-01 and form instructions. Not completing all required information may lead to missed requirements, confusion or incorrect administrative processing and programmatic updates. No consequences to these omissions were found. Factual Basis: â€¢ Organization change 0321-001, Radiation Protection positon description change was processed with Section 8 A thru E blank. â€¢ Organization change 0319-001, Pg. 43, Department Record Update form does not contain all signatures. Specifically, the Requester, Copy to HR, Input by PeopleSoft and Passport signatures and dates are blank. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Chemistry. <I> **** Actions Taken **** Discussed this Issue with the Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385939 | CR | 20181022 |  | 3 | (QA) Incorrect Change Types on LDCN Form 24341 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Form 24341 "License Document Change Notice" (LDCN) incorrectly designates type "LBIE" instead of "RR" for all 8 changes within approved LDCN-16-057 for the Offsite Dose Calculation Manual (ODCM), contrary to SWP-LIC-03 "Licensing Document Change Process". These are procedural non-compliances with SWP-LIC-03 which requires providing the change type on the LDCN form for each change. These incorrect change types do not invalidate the 8 changes made by LDCN-16-057 to the ODCM. Factual Basis: â€¢ SWP-LIC-03 Rev 018 (issued 11/02/17) section 4.2.16b states, "IDENTIFY the applicable change process for each change in Block 17 on the LDCN form. Examples include: 1) IF any of the blocks of Section II of the AD form are checked â€˜yesâ€™, THEN PLACE â€˜RRâ€™ on the LDCN form.â€ â€¢ The LDCN-16-057 package was initially placed in the AR-LDCN 358835 EDMS for review on 02/08/18 and final approval of LDCN-16-057 was 08/14/18. â€¢ The LDCN-16-057 package contains AD-17-0425 with a "yes" in for item 9 Section II (RR); therefore, "RR" is the change type required within Block 17 for the 8 ODCM changes on the LDCN Form 24341. â€¢ The LDCN-16-057 package contains a Form 24341 incorrectly showing "LBIE" instead of "RR" within Block 17 for all 8 changes. Insights: â€¢ This issue repeats the same procedural non-compliances identified by Quality during the last Chemistry audit AU -CH-16 for LDCN 13-060 and LDCN 15-051 within AR-CR 355418, for which no corrective actions were implemented by the Chemistry department. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Chemistry. <I> **** Actions Taken **** Discussed this Issue with the Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385940 | CR | 20181022 |  | 3 | Procedure enhancement SOP-AS-START |  |  |  | N | NO | <D> **** Detailed Description **** Several times in SOP-AS-START CO-HX-1A and CO-HX-1B are mentioned in noun names. Neither of those exist. What the procedure refers to as CO-HX-1A and 1B is actually CO-HX-1, the boilers deaerator. In portal J the noun names for CO -P-1A and 1B also need to be changed to reference the proper heat exchanger, that being CO-HX-1. <N> **** Equipment Description **** SOP-AS-START enhancement | 02-00-CO-HX-1,02-00-CO-P-1A,02-00-CO-P-1B
385941 | CR | 20181022 |  | 3 | (QA) JHA Not Signed by I&C Supervisor in 2 WOTs |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Two Instrumentation and Controls (I&C) Work Order Tasks (WOTs) each contain a Job Hazard Analysis (JHA) form with no signature on the Supervisor sign-off line on the form. This does not meet ISPM-14 â€œJob Hazard Analysisâ€, which directs the Supervisor to complete the JHA. There are no known consequences for these two instances where a Supervisor did not sign the JHA in the WOT. Requirement: â€¢ ISPM-14 rev 004-001 (and rev 004-002) step 3.1.2 states, â€œThe JHA originator and supervisor should complete the JHA with the assistance of Industrial Safety and other subject matter experts as necessary (see Attachment 7.1 for an example of a JHA form).â€ â€¢ ISPM-14 Attachment 7.1 includes an example JHA with two signature lines (one for the Originator and one for the Supervisor). Factual Basis: â€¢ WOT 02092899-01 â€œ16.6.3 TSW-RIS-5 - CFTâ€ contains a JHA form similar to ISPM-14 Attachment 7.1 that was signed by the Originator, but this JHA was not signed by the Supervisor. â€¢ WOT 02096688-01 â€œ16.8.3 SW-RIS-604 - CFTâ€ contains a JHA form similar to ISPM-14 Attachment 7.1 that was signed by the Originator, but this JHA was not signed by the Supervisor. Insight: â€¢ The 2 I&C WOTs with JHAs missing Supervisor signatures were found out of a sample of 20 WOTs. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Maintenance. <I> **** Actions Taken **** Discussed this Issue with: Component Group Manager, Craft/Maint Supervisor III, HUMAN Performance /Industrial Safety Supervisor, Quality Services Supervisor, and Quality Manager
385942 | CR | 20181022 |  | 3 | (QA) OE assignments not closed IAW OPEX-01 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Six of ten OE assignments were evaluated and closed without complete documentation as directed in the assignment in-progress notes contrary to OPEX-01 2.7. Insufficiently analyzed Operating Experience can expose Columbia to increased risk of events. No OE assignments reviewed appear to have been incorrectly screened. Factual Basis: â€¢ Ten OE assignments were reviewed for adequate resolution and timeliness of closure, six of the assignments were found to not be closed IAW OPEX-01. o 2.7.1, states, "To complete an OEE assignment, FOLLOW the assignment description AND ENTER evaluation information in the In-Progress notes as outlined therein. Completion of OEE assignments is approved by the assigneeâ€™s Manager or Supervisor by means of an Asset Suite routing list (for approval) created by the assignee." o 2.7.2, states, "To complete an OEI or OEB assignment, ENTER required information in the In-Progress notes as outlined therein AND DOCUMENT distribution of the information (i.e., post e-mail or pre-job briefing notes in the EDMS panel). The assignee then takes the assignment to COMPLETE status. o 2.7.3, states, "To complete an OES assignment, FOLLOW the assignment description AND ENTER screening information in the In-Progress notes as outlined therein. The assignee then takes the assignment to COMPLETE status. â€¢ Closure documented in the completion notes did not address the in-progress notes direction for the following OE assignments: o 358247-03 and 364087-02 (OEE) o 358860-01, 360265-01, 372334-01, and 372462-01 (OES) This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Corrective Action Program. <I> **** Actions Taken **** Discussed this Issue with: Corrective Action Program Supervisor, Senior Performance Improvement Coordinator, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager
385943 | CR | 20181022 |  | 4 | (QA) Signed LDCN Not Scanned/Uploaded to EDMS |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Signed License Document Change Notice (LDCN) package LDCN-16-027 was not scanned and uploaded to the Electronic Document Management System (EDMS), contrary to two steps within SWP-LIC-03 â€œLicensing Document Change Processâ€. This is a procedure non-compliance with no known actual consequence. Factual Basis: â€¢ SWP-LIC-03 Rev 017 (issued 11/24/15) section 4.2.21 â€œLDCN Processing - Regulatory Affairsâ€ states: â€œa. SCAN the signed LDCN package . . . b. UPLOAD the scanned LDCN package to EDMS . . .â€ â€¢ The last assignment for AR-LDCN 351431 for LDCN-16-027 was completed on 01/23/17. â€¢ On 9/17/18, the EDMS for AR-LDCN 351431 did not contain a scanned signed copy of LDCN-16-027, contrary to steps 4.2.21a and 4.2.21b in SWP-LIC-03. Insights: â€¢ Upon notification by Quality, Regulatory Affairs uploaded a signed copy of LDCN-16-027 into the EDMS for AR-LDCN 351431. This problem is considered a Deficiency identified during the 2018 Chemistry and Environmental Monitoring Program Audit AU-CH-18. Quality recommends this CR be routed to Regulatory Affairs. <I> **** Actions Taken **** Discussed this Issue with; Licensing Supervisor, Chemistry Operations Supervisors, Chemistry/RP Support Supervisor, Chemistry/Rad Safety Manager, Quality Services Supervisor, and Quality Manager <N> A signed copy of LDCN-16-027 was uploaded to the EDMS of parent AR 351431. No additional actions are needed.
385953 | CR | 20181022 |  | 3 | Redesign method to secure FDR-FT-38 during calibration. |  |  |  | N | YES | <D> **** Detailed Description **** The current method to calibrate FDR-FT-38 uses a wood block to secure the FT to a plate (See ISP-FDR/EDR-X301 attachment 9.2). It is difficult to get the proper alignment to safely secure the transmitter in place. We should change the securing method and store it in the calibration weight set tool box (see Webb for design idea). This would be quicker and safer and minimize the possibility of dropping the transmitter and reduce dose. Changing the method would require an update to the procedure attachment 9.2. <I> **** Actions Taken **** wrote this AR | 02-00-FDR-FT-38
385959 | CR | 20181022 |  | 3 | TMU-M-P/1A - Tan Delta and Withstand Testing | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WO 02134236, the field leads for TMU-M-P/1A were found in a degraded condition. WO task 07 was revised to include steps to remove the degraded portions of the field cable insulation at the motor end and install new stress cones. PPM 10.25.19 has a requirement to test high voltage connections (5kv through 15kv) in accordance with 10.25.65 for the continuity/megger check. 10.25.65 requires DC Hipot testing for these connections which could potentially damage aged cables. Task 35 was generated to perform Tan Delta testing which is a non -destructive alternative to DC Hipot testing to verify the integrity of the repaired termination but was not worked because there were no steps in the reterm task to perform the testing per task 35 after installing the stress cone but prior to reterm. / Since the Tan Delta testing must be performed with the field cables determed from the motor, the termination would have to be broken and insulation removed to perform the test. The risk of damage to the stress cones and cable insulation is high with this task and is not recommended as this type of damage may require pulling new cables from the breaker. / Since DLRO and PI testing will be performed on the motor and field cables per task 11, the electrical continuity of the cable termination will be verified. Although this does not verify the integrity of the repaired termination with respect to potential long term impact from electrical stresses, this testing will provide assurance that there are no gross failures in the termination. / Recommend the following actions: Initiate a new procedure for Tan Delta testing. Revise PPM 10.25.65 to remove the option for testing existing cables using DC Hipot and point to the Tan Delta test procedure for existing cables. Revise PPM 10.25.19 to require testing of high voltage connections prior to terminating the connection and clarify that this requirement is only for new connections/splices. Perform Tan Delta test of the TMU-M-P/1A feeder cables the next time the cables are determed. <I> **** Actions Taken **** Discussed CR with the Component Engineering Large Pump & Motor Engineer and supervisor. Initiated CR. <N> Request has been turned into a procedure (MI-2.3.17) and it currently in routing within APW. | 02-00-TMU-M-P/1A
385966 | CR | 20181022 | CAQ | D | check valve for EDR-P-5B is questionable | Y | N |  | N | YES | <D> **** Detailed Description **** While performing section 7.12 of ISP-FDR/EDR-X301(WO# 02102735-01) , we noticed EDR-P-5Bâ€™s coupling was slowly rotating after the pump discharge pressure dropped to zero on EDR-PI-5B. Our measurement for EDR-LS-14A was out of tolerance, HI (65â€ instead of 72â€ from sump cover). At that time, we saw no perceived rotation of pump 5B coupling. Per procedure, we continued with the calibration and made sure to immediately take the sump level measurement when the pump stopped. When EDR-P-5B stopped, EDR-LS-14A was in tolerance (71.5" from sump cover). It seems like there could be some backflow into the sump after the pump stops. Wrote this AR for ops to investigate if this is an issue or not. <I> **** Actions Taken **** Wrote this AR for ops to investigate if this is an issue or not | 02-00-EDR-LS-14A,02-00-EDR-P-5B
385968 | CR | 20181022 | CAQ | D | RHR-MO-40 declutch mechanism - Tripper fingers | Y | N |  | N | YES | <D> **** Detailed Description **** RHR-MO-40 actuator was recently refurbished, the as-left diagnostic test identified the declutch lever required to be manually held down to maintain the valve in the manual mode. This represents an alignment issue with the tripper fingers. It does not impact motor operation (normal operation. The valve stays in motor operation. It requires the motor to be pulled and the tripper fingers to be adjusted. Recommend repairs should be done during the next diagnostic test (8 years from now). <I> **** Actions Taken **** It takes 7-3/4 handwheel turns to open and close RHR-MO-40. This will require the declutch lever to be held down to keep the valve in manual operation. It does not have any impact/effect during electrical operation. | 02-00-RHR-MO-40
385969 | CR | 20181022 |  | 4 | Reactivity Management mtg failed to meet quorum |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.3.79, Reactivity Management Administration, section 4.2 lists the quorum requirements for Reactivtity Management Review Committee meetings. One of the required members is an Operations Training Manager, or their delegate. Operations Training was not represented at the 10/22/18 meeting. <I> **** Actions Taken **** Meeting was held, and the absence was noted. <N> Further investigation revealed that Operations Training was on the invitation, however it was not on his calendar. . A makeup meeting has been scheduled for 11/26/18. (required quarterly)
385972 | CR | 20181022 | CAQ | D | Door R-108 latch sticks open | Y | N |  | N | YES | <D> **** Detailed Description **** The latch on door R-108 (441 RB inner airlock door) sticks open after the handle is taken open. Door does not latch after its let swing closed. The security latch still works, so it does not open when the outside door is opened. | 02-00-R-DOOR-R108
385973 | CR | 20181022 |  | 3 | found an issue with IMDS COND-FQ-200D | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** while performing WO# 02066589-01 found issue with new IMDS COND-FQ-200D rev. #5 Parameters #5 in the old FQ was 010000 IMDS is 011000 Parameters #30 in the old FQ was 9.61111 IMDS is 9.6111 <I> **** Actions Taken **** Contacted Supervisor and Engineer and the new Rev. has some typo's Engineer approved using as found Paramiters. Armin Mehinagic Engineer is going uptade IMDS'S for all the Cond-FQ-200? indicators <N> **** Equipment Description **** rw467 CR | 02-00-COND-FQ-200A,02-00-COND-FQ-200B,02-00-COND-FQ-200C,02-00-COND-FQ-200D,02-00-COND-FQ-200E,02-00-COND-FQ-200F
385974 | CR | 20181022 |  | 3 | Security Computer data file transfer not functional | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The dmp file transfer process from the SCS to the corp network stopped working on 10/19/2018 at approximately 2000hrs. <I> **** Actions Taken **** Comp engineering is looking into the cause and resolution. IS will assist as needed. Access Authorization is standing by, badging is on hold. <N> CR reopened at the request of ENG.
385975 | CR | 20181022 |  | 3 | Procedure enhancement 12.2.9 needed |  |  |  | N | NO | <D> **** Detailed Description **** PPM 12.2.9, Circulating and Plant Service Water Halogenation Surveillance, needs enhancement. Step 8.2.17, VERIFY the following valves are SHUT, needs to be placed before step 8.2.16, VERIFY the following valves are OPEN. This needs to happen to prevent possible flow of chemical out of the system into the berm. <I> **** Actions Taken **** Discussed this change with supervision and specialist. | 02-00-P-BLDG-MISC
385977 | CR | 20181022 | CAQ | C | NRC Questioned 104F limiting temp for rm R611 in LCS | Y | N |  | N | NO | <D> **** Detailed Description **** LCS table 1.7.1-1 lists limiting temperatures of < 104Â°F/ <129Â°F for the Hydrogen Recombiner Room Div 1 (R611). LCS Table 1.7.1-2 states that the 104Â°F is the limiting temperature for SGT Div 1 and 129Â°F is the limiting temperature for E-MC-7BB. It appears that the 104Â°F reference in the LCS table is incorrect. QID 829213-01 lists the bounding lower temperatures for safety related rooms. The H2 Recombiner (R611) room lowest temperature is 129L, where the L designates lowest temperature. The 104Â°F referenced in LCS table 1.7.1-1 was for E-CP-CAC/HR1A+ which had a 106Â°F temperature limit has been deactivated. The lowest temperature limit for any SGT component within R611 is bounded by the 129L per QID-829213-01. The LCS table 1.7.1-1 and 1.7.1-2 does not accurately reflect QID 829213-01. Temperature limit for R611 (H2 Recombiner Room Div 1) should be 129Â°F and not 104Â°F/129Â°F as it currently is. | 02-00-E-CP-CAC/HR1A,02-00-R-BLDG-MISC
385978 | CR | 20181022 | CAQ | D | CW-PHITS-1 Error Code E5.1 | N | Y |  | N | YES | <D> **** Detailed Description **** During system walkdown it was noted that CW-PHITS-1 was displaying error code E5.1 (Impedance of input 1 too high). During the walkdown the pH meter appeared to be responsive to changes in pH and continued to read within the expected range of 8.29 to 8.31; however, a review of eDNA data revealed that CW pH readings have been fluctuating between 8.45 and 7.9. According to the eDNA data, these fluctuations began on 10/20 and are an order of magnitude greater than the typical fluctuations in pH. The unusually rapid changes in pH signal (F141 including high speed and backup signals) and the E5.1 error code both indicate an issue with pH signal. CW-PHITS-1 provides input to the sulfuric acid pump controller CW-PHIC-1, and CW-PHR-1, which supports NPDES reporting requirements. Recommend troubleshooting and repair of CW-PHITS-1. Per SOP-CW-OPS, If CW-PHR-1 becomes inoperable or is known to be in error, blowdown grab samples per PPM 12.2.9 are necessary and every reasonable attempt to return CW-PHR-1 to service should be made. Verify the method for monitoring pH is noted on the Outside Tour Log sheets. Per CVI OMM 659-00,15 possible causes for error code E5.1 include a disconnected sensor or loss of ground connection. | 02-00-CW-PHITS-1
385979 | CR | 20181022 |  | 4 | SA-C-1 Low Oil Level | N | N |  | N | YES | <D> **** Detailed Description **** SA-C-1 oil level was at the bottom of the sight glass and has been shutdown for oil add. <I> **** Actions Taken **** Contacted maintenance supervisor, and verified local clearance order was hanging. Added oil. Restarted SA-C-1. | 02-00-SA-C-1
385980 | CR | 20181022 |  | 4 | Increasing Trend in Plant Water Usage Rate | N | N |  | N | YES | <D> **** Detailed Description **** Increasing Trend in Plant Water Usage Rate since 9/23/2018. It is max out on 9/25 at 15.5 GPM. Need to investigate and correct the source of water usage. There are several CR that identified steam leak since 10/11/2018. CR#385656. 385826,385834 and 385930 <I> **** Actions Taken **** SM informed <N> **** Equipment Description **** Water balance log for Operations
385981 | CR | 20181023 |  | 3 | PPM 1.3.23 update needed for key 215 |  |  |  | N | NO | <D> **** Detailed Description **** Attachment 5.2 of PPM 1.3 23, key 215 for building 82 and building 600 should have two keys, one for the buildings and one for the lockboxes. Attachment 5.2 lists that key 215 is only one key. The key was added to the lockbox in the MCR by the system engineer and now the procedure needs to be updated. <I> **** Actions Taken **** Informed the Shift Manager and the System Engineer
385984 | CR | 20181023 |  | 3 | ABN-WIND needs updated to reflect TMU position |  |  |  | N | NO | <D> **** Detailed Description **** Following the ruling regarding TMU and it's relationship to the UHS, ABN-WIND needs to be updated to reflect the postion that should all spray trees associated with SSW become damage, TMU must be able to makeup to the SSW ponds in the event of a tornado. This position does not relfect an operability concern and ABN-WIND currently has guidance to ensure TMU is operating and available if the spray trees are damaged. This CR is an enhancement to ensure a solid understand by the operating crew. <I> **** Actions Taken **** discussed issue with licening and operations management. <N> files outlining position and mark up of ABN-WIND located in the EDMS.
385986 | CR | 20181023 | CAQ | D | M&TE Rejected | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #C005412 Fluke Dig. Thermometer- model 52 found OOT. EFIN Eval: Not used on failed range. Rejected- Unable to adjust. DEF #6760A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
385987 | CR | 20181023 | CAQ | C | Records submitted with invalid EPN |  |  |  | N | NO | <D> **** Detailed Description **** A Software Classification form was submitted to Records Control for processing with an invalid EPN. <I> **** Actions Taken **** Notified my supervision. Tried to make contact with sender on multiple occasions and left messages. Sending Record back to Design Engineering for corrections and re -submittal.
385990 | CR | 20181023 |  | 4 | Telemetry monitoring base station not working | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Wireless base station wrm2-8014 was reported as inoperable. The station is located at the RCA access point used for sign in verification of telemetry devices. Local switch configuration and cabling was verified correct. <I> **** Actions Taken **** Notified IS and IR-0012923 was generated to investigate potential issues. CR generated for trending telemetry hardware software issues to help evaluate system reliability and identify re-occurring issues. Recommend all follow-up action completed in IR request
385993 | CR | 20181023 |  |  | Inspect Packwood Compressor | [5 empty] | <D> Schedule inspection. Take appropriate actions based on inspection results. <N> Packwood's warehouse compressor failed it's State inspection. A scan by NDE determined that the compressor walls were too thin for pressure vessel requirements. The required resolution is to dispose of the compressor. The vessel showed signs of min-wall areas that was determined by the ANI to be beyond repair. The vessel was taken out of service. The vessel was scrapped locally.
385994 | CR | 20181023 |  | 4 | 3rd Qtr 2018 Security Training Roll Up |  |  |  | N | NO | <D> **** Detailed Description **** 3rd Quarter 2018 Security Training consisted of Tactical Course Qualifications, Table Top Drills and Adversary Team Training. There was an 89% first attempt passing rate on the Tactical Course. All students who failed their first attempt successfully passed their second attempt. Table Top Drills and Adversary Team Training met all associated requirements. This CR is for trending purposes only. <I> **** Actions Taken **** Student Feedback Forms and MOT's reviewed. End of Cycle Report completed. CR submitted for trending.
385995 | CR | 20181023 |  | 4 | S5 through wall steam leak downstream of BS-V-54B | N | N |  | N | YES | <D> **** Detailed Description **** Leak investigation revealed a through wall steam leak (S5) just downstream of BS-V-54B. Attempt to patch during December downpower. <I> **** Actions Taken **** Updated FLM map, informed SM. <N> **** Equipment Description **** TG 471 NW corner | 02-00-BS-V-54B
385998 | CR | 20181023 |  | 3 | SA-C-1 | N | N |  | N | YES | <D> **** Detailed Description **** Replace SA-HX-1 and 2 Due to the lack of a yearly PM to clean and inspect the Heat EXchangers . We chased and wasted money on parts and labor trying to figure out the cause of over heating . We need to go back to a yearly clean and inspect of the Heat Exchangers <I> **** Actions Taken **** Spoke to suppervision and im writing the CR <N> **** Equipment Description **** 467 SA-C-1 | 02-00-SA-C-1,02-00-SA-HX-1,02-00-SA-HX-2
385999 | CR | 20181023 |  | 4 | Piping on SA-C-1 needs to be replaced to prevent future leak | N | N |  | N | YES | <D> **** Detailed Description **** Due to the age and degradation , The piping on the oil , Air, and water sides should be replaced along with the connection fittings. I do not believe if there is anymore work done on the heat exchangers that the piping will seal. There for we will have leaks and rework <I> **** Actions Taken **** Spoke to my suppervisor and wrote the CR <N> **** Equipment Description **** 467 SA-C-1 | 02-00-SA-C-1
386000 | CR | 20181023 |  | 3 | Washington State EFSEC Annual Report (enhancement only) |  |  |  | N | NO | <D> **** Detailed Description **** This is an enhancement to the process of gathering data in support of the annual report. There is no adverse regulatory impact. Energy Northwest is required to file an annual report with the State of Washington Energy Facility Site Evaluation Council (EFSEC), to document the amount of diesel fuel that is consumed monthly by the Auxiliary Boiler (EFSEC Order No. 873). There have been some difficulties with obtaining accurate data to support this annual report, in particular with the aux boiler. To alleviate the issues we suggest the following changes: In eSoms logs, add a requirement to record FO-TK-1 level on the first day of every month. This will be in addition to the existing logging requirements for FO-TK-1. Revise SOP-AS-START to require a narrative log entry be made every time the aux boiler is started up. Include the Date, Time, and a brief reason for running the boiler. <I> **** Actions Taken **** This was discussed with E&RP, Ops Coordinator, and Ops Shift Manager. Consensus was obtained on the suggested changes above. Suggest Severity 3 to Ops Staff <N> Also, Revise SOP-AS-SHUTDOWN to require a narrative log entry be made for the time the aux boiler was shutdown. In conjunction with the proposed revision to SOP-AS-START above, this will help determine the total time the aux boiler was running. (if not needed, then disregard this recommendation) . Ref OPS4 Log form 27156
386004 | CR | 20181023 |  | 3 | upper bearing oil sample on CW-M-P/1A unaccessible | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Per work order 02103290-01, electricians set out to obtain 250mL of oil from the upper and lower bearing reservoirs. The new motor was supposed to have an oil sample port installed for easy sample access. Per step 4.1 obtain 250mL sample from upper bearing reservoir is not possible at this time. A CR was generated in January of 2017 (CR # 360004) to capture the lack of sample point. It seems as though no action has been taken to remedy the lack of sample port on the upper reservoir. <I> **** Actions Taken **** notified Supervisor, obtained supervisor instrucions to proceed per actions noted in reference WO#02074296. write this CR <N> **** Equipment Description **** CW-M-P/1A CW pumphouse ***General Notes*** This issue is being addressed by engineering under AR-eval 310858 | 02-00-CW-M-P/1A
386007 | CR | 20181023 |  | 4 | TDAS | N | N |  | N | YES | <D> **** Detailed Description **** During performance of ISP-MS-X304, 20100669-01, the TDAS point x054 was found Out of Tolerance. The value of the TDAS point seemed to randomly fluctuate between 1000 to 1500 psi. <I> **** Actions Taken **** Followed work instructions, wrote CR for tracking purposes. CR and WR has already been initiated to fix the broken TDAS. CR# 00385620, WR# 29145071 <N> **** Equipment Description **** TDAS MUX 1
386010 | CR | 20181023 |  | 4 | CJW valve leaking | N | N |  | N | YES | <D> **** Detailed Description **** CJW-V-132 is leaking through the quick disconnect leading to build-up on the floor. The leak is roughly one drop per 10 seconds. <I> **** Actions Taken **** Informed chemistry supervision | 02-00-CJW-V-132
386011 | CR | 20181023 | CAQ | D | CST external inspection trending data | Y | Y |  | N | YES | <D> **** Detailed Description **** CST external inspection was performed under WP 02105750; this CR is to document the external condition of the tanks for trending and to include in WOT-01. Overall both tanks had a few areas of minor surface/paint corrosion. There are a few pictures located in the EDMS that can be used for trending coating appearance. . Two tank locations (one per tank) were identified for NDE inspection; these were the nozzles for the pipe penetrations associated with COND-V-11A (11B), Nozzle â€œNâ€. The nozzle thickness should be greater than the normal shell wall (.375â€, CVI 204-00,97). Examination results ranged from UT thickness of .690â€-.742â€, which is well above the normal shell wall thickness so there are no min wall issues for this location. NDE report is located in EDMS. . Anchor bolts, ladders, valves, and other connections appeared in good condition. Manway bolts appeared SAT, few inches of moss growth on one COND-TK-1B manway (external). <I> **** Actions Taken **** NDE inspection performed as part of PM. There is no further action recommended for this CR, it is for trending and documentation only. EDMS contains pictures and NDE file. WP 02061574 is to perform internal Camera/UT inspection. | 02-00-COND-TK-1A,02-00-COND-TK-1B
386012 | CR | 20181023 | CAQ | D | HT-HTP-FP/7 | Y | N |  | N | YES | <D> **** Detailed Description **** During insulation testing of HT-HTP-FP/7 circuit 1F, the criteria of 1Gig ohm was not met. A reading of around 60 Meg ohms was achieved. The testing of HT-HTP-FP/7 circuit 27F could not be performed due to the degraded condition of the heat trace circuit power head. Both circuit are located at SWPH-A, north and south side. <I> **** Actions Taken **** Stopped work, backed out of the procedure and returned everything to its as found contion. Notified supervisor and intiated CR <N> **** Equipment Description **** SWPH-A | 02-00-HT-HTP-FP/7
386013 | CR | 20181023 | CAQ | C | EWD-7E-041 drawing does Not match installed bucket | Y | N |  | N | YES | <D> **** Detailed Description **** While performing WO 02083349, electricians identified indication lights, auxiliary contacts and a relay inside DSA-42-6B4E NSR bucket . EWD-7E-041 does Not indicate any of the aboved mentioned components on the drawing. The identified configuration has and is operating as expected but is different from the design configuration. <I> **** Actions Taken **** Called the CSM Initiated a CR <N> Approved for Closure by Acting Supervisor, Jim Hysjulien. | 02-00-DSA-42-6B4E
386015 | CR | 20181023 |  | 3 | unable to obtain lower bearing sample CW-M-P/1C | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Per work order # 02103292-01, electricians are not able to obtain lubrication sample without a special check-valve adapter on the sample port. The whereabouts of the adapter are unknown at this time. The work order is graded a "C" but engineering evaluation is needed to determine alternate methods if adapter cannot be located in a timely manner. <I> **** Actions Taken **** Notified Supervisor, Writer CR and notified engineer via e-mail. <N> **** Equipment Description **** CW-M-P/1A CW Pumphouse This AR is being closed to AR# 386004, no further actions requred | 02-00-CW-M-P/1C
386016 | CR | 20181023 | CAQ | C | eSOMS Late Entry for Maintenance for the week of 10/13/18 |  |  |  | N | NO | <D> **** Detailed Description **** Two maintenance craft worked for less than 1 hour over their scheduled time in eSOMS without updating eSOMS or requesting that eSOMS be updated. A mainenance supervisor came in and worked on a day he is normally off without updating eSOMS. Errors were discovered during weekly eSOMS to Payroll audit. No violations occurred when hours were entered in eSOMS. <I> **** Actions Taken **** Updated hours in eSOMS.
386017 | CR | 20181023 |  | 4 | CW-CT-2A broken ground wire clips | N | N |  | N | YES | <D> **** Detailed Description **** During ESAA walkdown of CW-CT-2A it was noted that several clips securing the grounding wire between CW-CT-19 and CW -CT-20 were broken. This condition does not impact the functionality of the ground wire; however, the unrestrained line does represent a potential tripping hazard. Recommend replacement of broken clips. Pictures in EDMS of AR 00386017 <N> **** Equipment Description **** CW-CT-2A: ground line between CW-FN-19 and CW-FN-20 | 02-00-CW-CT-2A
386018 | CR | 20181023 |  | 4 | RFW-MOD-L012A Redundancy Comm Module â€œRemote Readyâ€ LED out | N | N |  | N | YES | <D> **** Detailed Description **** A recent walkdown of the Digital Feedwater Level Control System (E-CP-H13/P612) noted that the â€œRemote Readyâ€ LED on RFW-MOD-L012A is not lit. This indication is off-normal and may imply that the systemâ€™s redundancy is not functioning. RFW-MOD-L012A Redundancy Communications Module is a subcomponent of the Feedwater Level Control PLC necessary for the systemâ€™s â€œHot Standby CPU Redundancyâ€. A loss of the redundancy would result in several conditional single point vulnerabilities. Currently there is no impact on RPV level control. Since it is possible that the problem is limited to the indication (i.e. a faulty LED), further investigation is needed. The cross-referenced work request has been generated to investigate and ultimately correct the issue. This was identified by the craft during WO 02116569-10 package walkdown. | 02-00-E-CP-H13/P612,02-00-RFW-MOD-L012A
386019 | CR | 20181023 | CAQ | C | PRM-SR-1 realigned during maintenance | N | Y |  | N | NO | <D> **** Detailed Description **** When performing the 1700 PRM-SR-1 flow checks per ODCM-18 -PRM-SR-1-002, the Shift Chemistry Technician identified that the sample flow had realigned to the accident alignment. This must have occurred during approved repair efforts after 1300, since the 1300 flow check was completed satisfactorily. This rendered ODCM functions 6.1.3.F3b and 3c nonfunctional. The Chemistry Technician realigned the sample rack to the normal mode. This complies with RFO 6.1.2.E since the condition is known to have existed for less than 4 hours (the recorder shows a response around 1602). <I> **** Actions Taken **** Documented ODCM entry and exit. | 02-00-PSR-SR-1
386020 | CR | 20181023 |  | 3 | FDR-FQ-38 esoms reading calc | N | N |  | N | NO | <D> **** Detailed Description **** CRO was forced to manually calc containment identified leakage do to esoms not placing the correct time in the current time slot for computer to calculated the leakage. <I> **** Actions Taken **** CRS informed manually calculated. <N> Due to a calculation error in eSOMS for Identified Leakage Rate, the rate was manually calculated. The OSP-INST-H101s for 10/24/18 night shift were reviewed by an SRO on 10/23/18 2225. Due to attempts to fix the calculation error in eSOMS, the SRO Review stamp in eSOMS did not occur until 10/23/18 2240. Shiftly logs were reviewed within the required periodicity. | 02-00-FDR-FQ-38
386021 | CR | 20181024 |  | 4 | TMU-P-1B lower motor oil level is at the low spec | N | N |  | N | YES | <D> **** Detailed Description **** TMU-P-1B lower motor bearing oil level is at, but NOT below, the low spec. TMU-P-1B is currently in STANDBY, with lower motor bearing oil level at -1/4 from the STANDBY mark. Note: a 2A SM key is required for enty into the TMU pumphouse. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TMU pumphouse | 02-00-TMU-M-P/1B
386022 | CR | 20181024 |  | 4 | GY-F-10A2 requires change out. | N | N |  | N | YES | <D> **** Detailed Description **** GY-F-10A2 resistivity is currently 4.90 MOHMs. Per PPM 3.1.10, operator rounds, the filters should be changed out at 5 MOHMs. Note: a 2A SM key is required for entry into the ASD building. <I> **** Actions Taken **** informed MCR <N> **** Equipment Description **** ASD Building | 02-00-GY-F-10A2
386023 | CR | 20181024 |  | 4 | GY-F-10B2 resistivity is below 5 MOHMs | N | N |  | N | YES | <D> **** Detailed Description **** GY-F-10B2 resistivity is currently 4.70 MOHMs. Per PPM 3.1.10, operator rounds, the filters should be changed out at 5 MOHMs. Note: a 2A SM key is required for entry into the ASD building. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** ASD building | 02-00-GY-F-10B2
386024 | CR | 20181024 |  | 4 | Recombiner A Inlet Temp Low alarm locked in when it shouldnt | N | N |  | N | YES | <D> **** Detailed Description **** Received â€œRecombiner A Inlet Temp Lowâ€ alarm (H13-P672.A9 .1-2). ARP says that alarm is caused by OG-TIS-601A indicating LE 300F, but that indicator was reading 410F. All other indications of OG-RC-5A (Recombiner A) temperature were normal and the preheater lineup was verified correct. Request maintenance repair OG-TIS-601A. | 02-00-OG-RC-5A,02-00-OG-TIS-601A
386025 | CR | 20181024 |  | 3 | I&C surveillance did not require H/OPS reveiw |  |  |  | N | NO | <D> **** Detailed Description **** ISP-MS-X304 was performed IAW WO 02100669. After the surveillance was completed is was processed to FINISHED without first going to H/OPS. This could have allowed the sureillance requirment to be credited without an SRO reviewing for satisfactory completion. <I> **** Actions Taken **** Reviewed surveillance and wrote CR. <N> In order for the WO Package to be reviewed after it was performed the Review Required flag needs to be set on the M111-Task Nuclear Details Panel. In the Case of 02100669-01 the flag was not set, so it would not have gone to the DataGlance Operations panel for review. . Reviewed the Model WO and the next generated WO and the Review Flag was checked.
386029 | CR | 20181024 | CAQ | D | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0063867 Agilent Function Generator- model 33250A found OOT & adjusted within specs. EFIN Eval: Failed flatness test @ 75 MHZ & 80 MHz. Not used in the OOT range. DEF #6761A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
386031 | CR | 20181024 |  | 3 | Failure of Records Dataload process |  |  |  | N | NO | <D> **** Detailed Description **** Failure of the Records Dataload Process occurred on 10/23/18. The process used to write data to Asset Suite failed and the output file did not receive the metadata used to import files and write data to SharePoint. Notified IS of failure and request was made for the process to be rerun. After rerunning, files created for the output file WOTARCH were successfully created. File for the output file OTHARCH failed. IS implemented what was thought to be a resolution and the decision was made to process a test batch and let it run that night. On 10/24/18, the process failed again to write the test data to Asset Suite and the output file. No Quality Assurance Records were affected or lost by the failure of this process to run. <I> **** Actions Taken **** Notified IS Appl Systems Analyst, Database Analyst and Supervision Recommend assignment to ITMGMT as Cat 3
386036 | CR | 20181024 | CAQ | C | Maintenance late entries into eSoms |  |  |  | N | NO | <D> **** Detailed Description **** As part of cognitive trending the Maintenance eSoms program owner had noticed potential a trend for eSoms hour that needed to be corrected. Program owner was asked to document this within the CAP program so that data could be visible and be trended. It appears that at this point data can start to be analyzed. This CR is to evaluate, validate any commonalities or themes and create actions necessary to improve performance. Recommend assignment to AR-MNTPROG
386038 | CR | 20181024 |  | 3 | Enhance SOP-ELEC-SH6-MAINT |  |  |  | N | NO | <D> **** Detailed Description **** The following note was copied from C-TMU-LIC-2A -016: NOTE: TMU-LCV-2A CAN BE OPERATED WITH TMU-LIC-2A IN MANUAL WITH SL-61 DEENERGIZED. THIS CLEARANCE WAS NOT USED. <I> **** Actions Taken **** CR written.
386039 | CR | 20181024 | CAQ | D | Rad material receipt issues during receipt inspection |  |  |  | N | NO | <D> **** Detailed Description **** During the receipt inspection of BADGER testing equipment on 10/18/18 from an off-site vendor, several issues were identified by the HP technician performing PPM 11.2.14.2, Receipt of Radioactive Material. No regulatory limits described in PPM 11.2.14.2 were exceeded. The drum containing the source was controlled in accordance with site procedures. A 30 gallon drum containing a Cf-252 neutron source had a Yellow-III shipping label with a Transport Index number of 1.2 on the label. Based on the receipt survey of gamma and neutron radiation the Transport Index number on the label should have been 3.2. This is contrary to 49 CFR 172.403 (g) and 173.403. The shipping paper also had the incorrect Transport Index number contrary to 49 CFR 172.203 (d). This error was performed by the consignor of the shipment. A review of the shipping paperwork provided by the consignor noted that the radiological survey included in the paperwork only documented gamma radiation dose rates. Neutron radiation dose rates were not documented on the survey. The consignor failed to include the contribution of neutron radiation from the source in preparation of the shipment paperwork and label. <I> **** Actions Taken **** RP Supervision notified Radiological controls of the drum and boxes established in accordance with 10 CFR 20 and site procedures.
386041 | CR | 20181024 |  | 4 | Did not meet required quorum for T-2 meeting. |  |  |  | N | NO | <D> **** Detailed Description **** T-2 meeting did not meet required quorum on 10/24/18. <I> **** Actions Taken **** Meeting was cancelled and will be rescheduled. <N> **** Equipment Description **** N/A
386042 | CR | 20181024 | CAQ | D | DG4 PMT Coolant leak, exhaust leak | N | Y |  | N | YES | <D> **** Detailed Description **** DG4 PMT system engineer walkdown. DG4 mechanical functions all SAT, engine internals all sounded normal. Observed the following which need to be corrected in the next maintenance window for the engine. 1. Coolant leak at coupling, it is less than 1 drip per minute. Will cause a small loss of inventory however will not impact the fucntion of the engine because SOP-START-DG4-QC has prerequisit to validate fluid levels prior to starting and there is no fast start function. 2. The exhaust is leaking at the turbo charger outlet which does not impact the turbochargers performance . The clamp was verified tight by mechanics durring PMT and leak did not improve, it did not improve with engine warmup. Suspect a hole in the exhaust pipe or degradation at the joint. 3. Starter wires have corosion since they are exposed and they should be cleaned, did not impact the engines start ability. Recommended compensatory action to validate and top off coolant fluid level atleast monthly to ensure standby heater has minimum coolant available to operate correctly . <I> **** Actions Taken **** Notified SM, Photos in EDMS | 02-00-E-DG-4
386043 | CR | 20181024 |  | 4 | Boom Truck deficiencies found during PM |  |  |  | N | NO | <D> **** Detailed Description **** During WO 02103308-01 the annual inspection, it was noted that the warning stickers are showing signs of wear due to the weather conditions and should be replaced. It was also noted that there is a minor leak on the hydraulic hose to the winch motor and this also should be corrected. This does not affect the operability of this equipment. <I> **** Actions Taken **** Notified my supervisor the main control room and vehicle maintenance, Recommend evaluating the upgrading of this equipment due to age and wear. <N> **** Equipment Description **** Manitex Boom Truck
386046 | CR | 20181024 | CAQ | D | DG-B0-DG4/A, B voltage | N | Y |  | N | YES | <D> **** Detailed Description **** Battery voltage out of recommended voltage range due to abient temperature. <I> **** Actions Taken **** Notified supervisor initiated CR <N> **** Equipment Description **** DG-B0-DG4/A, B
386047 | CR | 20181024 |  | 3 | 70 Ton Grove deficiencies found during the PM |  |  |  | N | NO | <D> **** Detailed Description **** During WO 02103308-01 the annual inspection of the 70 ton Grove crane it was found to have all of the mirrors with a glaze over them from the cooling tower fallout and should be replaced, as well as the headlights have a glaze over them from cooling tower fallout which should be replaced. The rollers on the PAT system reels need to have some replaced due to the cooling tower fallout build up. This does not affect the operability of the crane <I> **** Actions Taken **** Notified my supervisor the main control room and vehicle maintenance, Recommend evaluating the upgrading of this equipment due to age and wear. <N> **** Equipment Description **** 70 Ton Grove Crane
386049 | CR | 20181024 |  | 4 | (FP) Inop E-BU-SWA7/9 | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-SWA7/9 was found with a fault light flashing. EBU is a non-essential 1.5 hour life safety light. <I> **** Actions Taken **** CR written, photo uploaded to EDMS, WR written | 02-00-E-BU-SWA7/9
386050 | CR | 20181024 |  | 4 | Flammable Liquid Storage Bldg TG 441 lighting not working | N | N |  | N | NO | <D> **** Detailed Description **** The painters flammable liquid storage building explosion proof light is not working. This makes it difficult to see in the building. Replace light as soon as possible. <I> **** Actions Taken **** Notified FIN initiated CR and WR <N> **** Equipment Description **** TG 441 east side
386053 | CR | 20181024 |  | 3 | Design Error Identified in RW Elevator EC-12277 |  |  |  | N | NO | <D> **** Detailed Description **** Issue Summary: When the elevator installation vendor was going through the newly installed fire alarm system it was discovered the fire alarm design did not bring the elevator into compliance with current Washington state elevator codes. During a fire on any floor other than the 441â€™ the elevator is supposed to return to the 441â€™. If there was a fire on the 441â€™ then the elevator would go to the 467â€™. The fire alarm design has this arrangement in reverse. The EN project team telephoned the fire alarm design vender and asked why it was designed this way and not to Washington State code. EN was told several years ago EN directed them to design the fire alarm system in this configuration so the car would go to the 467â€™ because that is where the RW control room and fire brigade leader is located. <I> **** Actions Taken **** The EN project team has directed the fire alarm design vender to redesign the system and bring it into compliance with current Washington state elevator codes. This will impact the project budget and cost. Itâ€™s too early in the redesign process to understand whether it will impact the project schedule. <N> Assignment 01 issued the field change that corrected the field condition. No further action is required. This AR is now closed. | 02-00-MT-ELEV-4
386054 | CR | 20181024 |  | 3 | Failures during LORQ Annual Requal Simulator Exam |  |  |  | N | NO | <D> **** Detailed Description **** One Crew and six individual failures occurred during the Annual Requal Simulator Exam administered on 10/23/18. Remediation will be in accordance with TDI-02. <I> **** Actions Taken **** I: De-certified individuals in PQD. Notified Operations and Operations Training Management. A: Recommend Severity Level 3. Additional detail withheld due to exam security requirements. R: Remediation IAW TDI-02.
386055 | CR | 20181024 |  | 4 | MT-ELEV-3 is stuck on the 501 elevation | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-3 the turbine building elevator is stuck on the TB 501 elevation. Power was cycled however the elevator still will not move. Placed the elevator out of service signs to prevent use of elevator. <I> **** Actions Taken **** Generated WR to repair | 02-00-MT-ELEV-3
386056 | CR | 20181024 | CAQ | D | (NRC Observation) Question regarding CCH log taking | Y | Y |  | N | YES | <D> **** Detailed Description **** On step 7.1.39 of OSP-CCH/IST-M702 the operator is to â€œVERIFY compressor discharge temperature is between 90F and 200F as read on the compressor refrigerant outlet temperature gauge below CCH-PI-5B.â€ The NRC resident is questioning why this gauge has no official label and what the impact is on the validity of the reading and surveillance testing. <I> **** Actions Taken **** Notified SM. | 02-00-CCH-CR-1A,02-00-CCH-CR-1B
386058 | CR | 20181024 |  | 3 | CVI documentation for spare TMU pump motor (CID 32272) |  |  |  | N | NO | <D> **** Detailed Description **** CVI documentation issues noted for the spare TMU pump motor (CID 32272): 1) Motor Weight and Center of Gravity (C.G.) information similar to that provided by CVI DWG 39-00,3 for the original TMU pump motors was not provided in the CVI documentation for the spare TMU pump motor. This should be indicated on CVI DWG 39-00,10 and in CVI OMM 39-00,4. 2) The 7.5 degree rotational offset for the hole locations in the motor foot for the 8 mounting holes on a 32 inch bolt circle similar to that shown on CVI 39-00,3 for the original TMU pump motors is not indicated on CVI documentation for the spare TMU pump motor. This should be indicated on CVI DWG 39-00,10 and in CVI OMM 39-00,4. 3) Dimensions for the Winding Thermocouple Termination Box indicated on CVI DWG 39-00,6 conflict with those indicated on CVI DWG 39-00,10. The 8.00 in x 8.00 in x 4.00 in dimensions currently indicated on CVI DWG 39-00,6 likely should simply indicate 8x8x4 nominal dimensions (like those indicated on CVI DWG 39-00,5). 4) The spare TMU pump motor has an upper bearing oil cooler with water cooling inlet and outlet piping (CVI DWG 39-00,5 and CVI DWG 39-00,7 and CVI 39-00,10 and CVI OMM 39-00,4) but the original TMU pump motors have no cooling water supply or return piping. CVI DWG 39-00,7 indicates 4 gallons/min, 60 psi max, and 90 deg F inlet cooling water for the spare TMU pump motor. If cooling water supply and return piping is required for installation of the spare TMU pump motor, it will complicate the configuration change considerably. If cooling water supply and return piping is not actually required for installation of the spare TMU pump motor, the CVI drawings should be updated appropriately to indicate as such. . Photos of the spare TMU pump motor (CID 32272) existing in the warehouse are attached to the EDMS of this AR CR 386058. . Suggest resolution assignment to Technical Services (Large Pump/Motor Program Owner) to coordinate with the motor vendor and obtain CVI documentation updates needed. . This condition is for the spare TMU pump motor only - it is not associated with any currently installed equipment. There is no impact or effect upon the continued function, operation, or qualification of any currently installed SSCs.
386059 | CR | 20181024 |  | 3 | Walking on the access roads instead on walking path |  |  |  | N | NO | <C> Dispositioned to HR / to Occ. Health to communicate additional information regarding walking paths on site. <D> **** Detailed Description **** On occassion I see people walking in the middle of the roads instead on walking on the shoulder of the roads. I know we have walking paths on the Energy Northwest property. driving slow <I> **** Actions Taken **** Created a CR for safety <N> **** Equipment Description **** None
386060 | CR | 20181024 |  | 3 | eSOMS incorrect EPN's, need changing | N | N |  | N | YES | <D> **** Detailed Description **** In eSOMS the power cord connections for PWC-P-7 and PWC-P-8 are labeled exactly that. In eSOMS they EPN's are PWC -CONN-P/7 and PWC-CONN-P/8. The noun names are accurate but the eSOMS EPN's need to be changed to match the labels in the field. Oddly enough, there is a valid portal j EPN for PWC-CONN-P/8 but not PWC-CONN-P/7. Regardless, the power cord and pumps are a single unit, so there is no reason to have a EPN for both the cord and the pump. <I> **** Actions Taken **** Informed CRS. | 02-00-PWC-CONN-P/8,02-00-PWC-P-7,02-00-PWC-P-8
386062 | CR | 20181024 |  | 3 | Scope side of outage box turned Yellow |  |  |  | N | NO | <C> Found CR at INPROG status. Reviewed for content per SWP -CAP-01 and changed to APPROVED for disposition. <D> Scope side of outage box is turned Yellow at the outage manager discretion. Electrical and mechanical shop resources are 100 percent allocated based on R23 comparisons. Means to add additional scope for these shops are constrained because of the current resource loading. In addition, WPS sources are at or near budgeted allotments causing work addition constraints. <I> Help discussions at the outage meeting on 10/24/18 and decision made to turn the scope side of theoutage box Yellow. Action to outage management to evaluate and address. <N> Evaluation was completed and uploaded to EDMS.
386064 | CR | 20181024 |  | 3 | The EPN placard for CAS-CP-C/1B found on floor | N | N |  | N | YES | <D> **** Detailed Description **** The EPN placard for CAS-CP-C/1B found lying on the floor next to CAS-C-1B. This does not affect the functionality of any plant equipment. EPN on placard is CAS-CP-C/1B/2, this EPN is not in passport. <I> **** Actions Taken **** Informed supervisor <N> **** Equipment Description **** T441' East | 02-00-CAS-CP-C/1B
386065 | CR | 20181024 | CAQ | D | CW-PHR-1 pH reads lower than Lab samle. | N | Y |  | N | YES | <C> CR reopened to cross reference additional WR 02126023, then taken back to complete <D> **** Detailed Description **** Lab samples taken from Circ Water for pH read 8.52 and 8.48. CW-PHR-1 read 8.23 and 8.24. Difference is greater than 0.2. <I> **** Actions Taken **** Resampled CW with same results. Recalibrated both pH meters in Lab. Results were still the same. Informed MCR. <N> **** Equipment Description **** CW pump House | 02-00-CW-PHR-1
386066 | CR | 20181024 | CAQ | C | Additional software needed to recover the Stack Monitor | N | Y |  | N | NO | <D> **** Detailed Description **** Investigations to recover the Stack Monitor found that a corrupted file was preventing the system from restarting. During the process of obtaining the backup software in the Software Repository it was discovered that additional software was needed to properly load the backup copy onto a compact flash card. This software is not in SQA or any of the documentation. Discussion with the vendor confirmed that our backup file needs additional software and that it cannot simply be dragged and dropped onto a compact flash card. <I> **** Actions Taken **** Discussed with vendor on the correct software needed, discussed with supervisor, Maintenance FIN I&C supervisor, IS mgmt., initiated AR-ITSR 386048 to obtain and install the new software, wrote this CR.
386067 | CR | 20181024 | CAQ | D | CBD-FI-1A indicates down scale regardless of flow | N | Y |  | N | YES | <D> **** Detailed Description **** CBD-FI-1A indicates downscale despite the fact that blowdown flow been established at 2300 gpm as indicated by CBD-FR-10. Request maintenance repair as required. | 02-00-CBD-FI-1A
386068 | CR | 20181025 | CAQ | D | SYS-66 Preaction Air Pressure Low Alarm | N | Y |  | N | YES | <D> **** Detailed Description **** FCP.3 3-1 SYS-66 Preaction Air Pressure Low Alarm. OPS2 investigated and found Pressure at 0.812psig stable. leak in system or PCV issue <I> **** Actions Taken **** walkdown and continue monitoring. informed CRS/SM | 02-00-FP-V-P66/45
386069 | CR | 20181025 | CAQ | D | E-BU-SWS6/3 Emergency Lamp Fault Light | N | N |  | N | YES | <D> **** Detailed Description **** The red Service Alert LED indicator is blinking 5 times which indicates an Emergency Lamp Fault. This was previously reported WR 29125662 please investigate and repair. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RW 467' Stairs adjacent to MC-3D | 02-00-E-BU-SWS6/3
386070 | CR | 20181025 | CAQ | C | 4.DG3 Drop 6-1 Low Air Pressure Procedure Enhancement | Y | N |  | N | NO | <C> At the request of OFM on 10.29.2018. This CR (386070) upgraded from Severity 3 to Priority CAQ, Severity C assigned to AR-OPSPROC. â€œProcedure cannot be performed as writtenâ€ <D> **** Detailed Description **** During scheduled maintenance DSA-C-1C was tagged out. A low air pressure alarm (4.DG3 drop 6-1) was received due to DSA-AR-1C pressure LT 241 psig (DSA-PS-15). Per the ARP step 3. â€œIF the air pressure is low in either Air Receiver AND neither air compressor is in operation, Then consider manually starting the Diesel Air Compressor.â€ This step does not work as written as DSA-PS-35 does not actuate until ~238 psig and low pressure in one of 4 possible pressure switches could cause the alarm. The Diesel was manually cranked per the ARP and would not start. Please revise step 3 of ARP to IF DSA-PI-8 is LT 235psig or add a conditional step that if desired to manually start DSA-C-2C refer to SOP-DG-DSA to start DSA-C-2C which will blowdown DSA-AR-2C. If DSA-C-2C does not auto start with DSA-PI-8 LT 235 psig then manually start DSA-C-2C (with the steps currently in step 3). <I> **** Actions Taken **** Informed MCR | 02-00-DSA-AR-1C,02-00-DSA-AR-2C,02-00-DSA-C-1C,02-00-DSA-C-2C,02-00-DSA-PI-8,02-00-DSA-PS-15,02-00-DSA-PS-35
386071 | CR | 20181025 |  | 3 | WCH-CR-51A Logs OOS | N | N |  | N | NO | <D> **** Detailed Description **** Multiple logs for WCH-CR-51A were found to be out of spec during OPS-2 rounds. The values logged may not have been those intended by the logs, also the min and max range for logs may be dependent on compressor loading. The logs in eSOMs Rounds do not match those suggested in the owners manual (see EDMS for manual found online, not provided to OPS by vendor or Engineering). Recommend Just in time training for operators on new Chiller, specifically on navigating the control panel for logs and other system checks. Also recommend talking to the vendor about what logs should be taken based on the owners manual. Also recommend updating eSOMs Rounds with clearer notes on which menu to find each log. <I> **** Actions Taken **** Informed MCR | 02-00-WCH-CR-51A
386072 | CR | 20181025 | CAQ | D | LCS 1.3.3.1 Completion time exceeded for PRM-SR-1 | N | Y |  | N | NO | <D> **** Detailed Description **** This CR is being written to satisfy LCS 1.3.3.1.E and failure to restore the Reactor Building Elevated Release radiation monitoring system (Noble gas â€“ Function 19a) within the required 7 days per LCS 1.3.3.1.C. During performance of WO 02135216 PRM-SR-1 was not able to be restored. This issue was documented in CR 385875 and PRM-SR-1 was declared non-functional and associated LCS and ODCM actions statements were entered. During investigation it was identified that a corrupted file was preventing the system from restarting. While obtaining the backup software it was identified that additional software was needed to properly load the backup copy onto a flash card. This additional information was documented in CR 386066. Engineering is working with information services to obtain the additional software to allow loading the backup and get rid of the corrupted file. Once this is complete then restoration of the system will follow. This issue is being tracked on our plant concerns list and expected completion date for repairs is 10/26/18. <I> **** Actions Taken **** CR written to meet required actions of LCS 1.3.3.1.E.
386073 | CR | 20181025 |  | 4 | WOA-CB-FN1A charging spring motor abnormal operation | N | N |  | N | YES | <D> **** Detailed Description **** WOA-CB-FN1A was being racked in, after breaker overhaul (WO 02124155), After inserting the CLOSE power fuse block, there was no response of the Charging Spring Motor. The CLOSE power fuse block was removed, fuses were re-verified to be making good electrical connection with the fuse clips and being held snug in place. The CLOSE power fuse block was once again firmly installed, with no immediate response of the Charging Spring Motor (The Charging Spring motor normally responds immediately as the CLOSE power fuses are being installed). ~ 1 minute after the CLOSE power fuses had been reinstalled, the Charging Spring Motor then actuated and Charged the Breaker Closing Springs. MCR was informed of the abnormal breaker response and permission was obtained to rack out WOA-CB-FN1A to allow further inspection/repair. WOA-CB-FN1A is located on SL-53, TG 501E <I> **** Actions Taken **** Informed MCR. Racked out WOA-CB-FN1A due its abnormal Charging Spring Motor response <N> **** Equipment Description **** TG 501E, @ SL-53 | 02-00-WOA-CB-FN1A
386074 | CR | 20181025 |  | 4 | RFW-LOC-1A Cable outer sheath is damaged, may be a safety ha | N | N |  | N | YES | <D> **** Detailed Description **** RFW-LOC-1A ( Marine Oil Seperator) Cable outer sheath is damaged, may be a safety hazard. outer sheath was damaged in several places exposing the individual insulated conductors. I didnt see any direct conductor but it is a dark area. Cable is moved shiftly to clean up the excessive oil that leaks from the coupling area making it an already slick area additionally the pipe you have to lean over is at an elevated temperature due top a leak. so be careful while inspecting the cable. Please see picture attached. <I> **** Actions Taken **** WR? CR informed the SSS. | 02-00-RFW-LOC-1A
386078 | CR | 20181025 |  | 4 | M&TE Rejected | N | N |  | N | NO | <C> Updated details to remove proper name. <D> **** Detailed Description **** Calcode #0065438-26 Mitutoyo Dial Caliper- model CD-8" CSX belongs to Receipt Inspection. Per QC Inspector: Last digit on the digital display started to flash 'E'. Immediately requested an 'as found' and it passed 'as found' & still passes Calibration. However, due to the last digit not functioning properly- the unit was Rejected. DEF #6763A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
386079 | CR | 20181025 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calocode #43314 Mitutoyo OD Mic- model 103-221A 6-7" found OOT & adjusted within specs. Not used during Calibration cycle. DEF #6764A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
386083 | CR | 20181025 | CAQ | D | oscillograph started alarm | N | N |  | N | NO | <D> **** Detailed Description **** Received an oscillograph started alarm due to J7 500KV neutral ground sensor. BPA reports McNary - Coyote Springs single phase relayed off and reclosed on first attempt. No RAS was initiated. S/U voltages 236/237/236KV. B/U voltages 117/117/117KV.
386085 | CR | 20181025 |  | 3 | Ashe 4.16kV Station Service not returned to sevice | N | N |  | N | NO | <D> **** Detailed Description **** ASHE 4.16kv redundant station service breaker, E-CB-1/500S, was racked out on 9/19/18 putting ASHE station in a single point vulnerability. With a loss of ASHE 4.16kv service both the 230 and 500kV lines that connect Ashe to CGS will be on battery power and a loss of breaker control when the batteries are depleted. Currently the breaker remains open with all work complete. This is a repeat issue identified in CR 290909. See EDMS for previous email from ASHE operations. <I> **** Actions Taken **** Contacted WWM to drive restoration. <N> reviewed issue and due to breaker issues, it took longer to restore then originally planned. ISsue will be trended and schedule followed in the future. no further actions necessary.
386086 | CR | 20181025 |  | 3 | NRC observation â€“ PPM 1.3.47 |  |  |  | N | NO | <D> **** Detailed Description **** Step 7.4 in PPM 1.3.47, Fuse Replacement, has confusing verbiage regarding the use of mixed fuse â€œtypesâ€. The example given in this step compares the use of FRS and TRS fuses, which are not different types but are from different vendors. This step should be clarified to state that fuses from different vendors should not be used. <I> **** Actions Taken **** Discussed with NRC and procedure sponsor.
386088 | CR | 20181025 | CAQ | D | FP-P-2A line press low alarm | N | Y |  | N | YES | <C> CR reopened to cross reference additional WR 29145048 then taken back to complete <D> **** Detailed Description **** After starting FP-P-2A the FP-P-2A line press low/ pump failure alarm came in. The alarm source is from FP-PS-8A (100 PSIG). Locally the pump was running and the pressure is normal. | 02-00-FP-P-2A,02-00-FP-PS-8A
386090 | CR | 20181025 |  | 3 | CI-9.1, Chemical Hygiene Plan requires revision |  |  |  | N | NO | <D> **** Detailed Description **** CI-9.1, Chemical Hygiene Plan requires a revision. Step 3.2.7 identifies WISHA as Washington Industrial Safety and Health Administration. WISHA actually stands for Washington Industrial Safety and Health Act. Recommend assignment to Environmental Services (AR-ENLAB) for procedure revision. <I> **** Actions Taken **** Notified environmental services group. Initiated this CR.
386091 | CR | 20181025 |  | 4 | Cleanup Main Transformer Oil Spills Post R24 Repairs |  |  |  | N | YES | <D> **** Detailed Description **** This AR CR is to facilitate removal of oil spilled from the Main transformers after they are repaired in R24. - Cleanup oil spills around Main transformers M1, M2 and M3 online after R24. <I> **** Actions Taken **** Notified System Engineer and Environmental Services | 02-00-E-TR-M1,02-00-E-TR-M2,02-00-E-TR-M3
386095 | CR | 20181025 |  | 3 | MCR equip tag printer broken still | N | N |  | N | NO | <D> **** Detailed Description **** MCR equip tag printer broken still causing a delay in hanging clearances in the control room. Zebra ZT510 equipment tag printer in main control room appears to have a network card issue - remains unresolved after several months
386097 | CR | 20181025 |  | 4 | PWC-TK-100 is empty | N | N |  | N | NO | <D> **** Detailed Description **** Chemistry technicians found that PWC-TK-100 is empty. A minimum of 10 feet is required before the tank is returned to the distribution system. This is to ensure appropriate contact time for the chlorine and is a DOH requirement. <I> **** Actions Taken **** Contacted Shift Manager, chemistry supervision <N> **** Equipment Description **** pwc-tk-100 needs filled | 02-00-PWC-TK-100
386099 | CR | 20181025 | CAQ | D | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0068231 Amp Crimper- model 69061 Passed post use verifications by S/L. No Plant Impact. Rejected- Does not operate correctly. Found sheared pin & leaking seals along with external damage. DEF #6765A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
386101 | CR | 20181025 |  | 4 | PWC-LI-100 not responding as expected | N | N |  | N | YES | <D> **** Detailed Description **** PWC-LI-100 does not respond as expected. The level is slow to respond when the vent valve is opened and closed. No water comes out of the vent valve when opened. <I> **** Actions Taken **** contacted FIN | 02-00-PWC-LI-100
386102 | CR | 20181025 | CAQ | D | received oscillograph started alarm. | Y | N |  | N | NO | <D> **** Detailed Description **** Received an oscillograph started alarm due to J7 500KV neutral ground sensor, J11 SM-7 UV, J12 SM-8 UV and J15 230KV UV. BPA reports Vantage substation relayed off and relayed off again on attempt to reclose. Both busses are OOS. S/U voltages 237/237/236KV. B/U voltages 117/117/117KV.
386103 | CR | 20181025 | CAQ | D | OSP-INST-H101s Approved after 10:30 | Y | Y |  | N | NO | <D> **** Detailed Description **** The OSP-INST-H101s were approved at 11:02 AM on 10/25/18 which is after the administrative time limit of 10:30 AM. This was within the 125% time allowance of SR 3.0.2 because the previous shift signed the OSP-INST-H101s at 9:56 PM on 10/24/18. The reason that the H101s were approved after 10:30 AM was that the CRS was responding to an emergent issue with the ASD gylcol system. CR written for trending.
386104 | CR | 20181025 |  | 4 | ASD 1A/2 alarm came in due to low resistivity | N | N |  | N | NO | <D> **** Detailed Description **** ASD 1A/2 alarm 4.602.A13.4-3 alarm came in due to low resistivity. Fin was adding to the glycol tank. Resistivity recovered and alarm was reset in less than 1 hour. <I> **** Actions Taken **** Followed ARP and informed CRS.
386105 | CR | 20181025 |  | 4 | ASD 1B/2 alarm came in due to low resistivity | N | N |  | N | NO | <D> **** Detailed Description **** ASD 1B/2 alarm 4.602.A13.4-3 alarm came in due to low resistivity. Fin was adding to the glycol tank. Resistivity recovered and alarm was reset in less than 1 hour. <I> **** Actions Taken **** Followed ARP and informed CRS.
386106 | CR | 20181025 |  | 3 | noncompliant Keurig appliances on site |  |  |  | N | NO | <D> It has been identified that various Kureg coffee makers are not compliant with fire protection procedures on site due to the coffee makers not being comercial grade. This was identified when an EN Employee would not allow another EN work group use a company purchased Kureg in BLDG. 88. why are we making decisions that cost the company large amounts of money because no one challanges other groups opinions, we should focus on required facts instead of one groups opinions. Buying a comercial coffee maker will cost three times more than a normal one. why can't other groups use company purchased equipment if there is a good cause, and it will save money? Does this mean that all appliances will be remved from site because they are not comercial grade? while we're at it, we might as well close the plant down, if we are going to enforce procedures like this that require us to spend money on things that are not needed because we are not challanging the various group on their requirements. our fire protection procedures should only have NEIL requirements, or other state requirements within them. not additional things that the fire marshal thinks are a good idea. <I> wrote this CR <N> CR was edited to remove specific name or job title in accordance with SWP-CAP-01.
386108 | CR | 20181025 |  | 3 | (NRC) Enhancements for EES-5 |  |  |  | N | NO | <D> **** Detailed Description **** The resident inspectors recommended a revision to EES-5 for the following: - Update the manufacturer name Gould Shawmut to the new name of Ferraz Shawmut - Correct the misspelling of Shawmut in two locations on page 72 - Images on pages 27-51, 61-65, and 70 should be replaced as they are illegible. <I> **** Actions Taken **** Discussed with NRC and Design Engineering.
386109 | CR | 20181025 |  | 3 | Incomplete work order packages |  |  |  | N | NO | <D> **** Detailed Description **** During a review of WO 02123631, WO02123237, and WO02123502, it was identified that completed Form 26909 was not included in the work package documentation. The package had been signed off that the Form was completed, however, there was no way to verify if the amounts matched the inventory or if replacements were necessary. These WOs were completed in Aug 2018 and a modification of the package is not possible at this time. On a separate note, it was identified that part of what may have led to the discrepancies, was the overall quality of the work packages. Therefore, it is recommended that EP, RP, and Occupational Health review and modify the work packages and associated form for efficiency of completion. Because the package was signed off, this does not constitute a failure of the surveillance but instead documents an administrative process issue with appropriate completion. In WO ending in 3237 and 3502 had documentation issues associated with Appendix 1 and Attachment A associated with quantity validation. <I> **** Actions Taken **** Discussed the issue with the Radiological Operations Supervisor.
386112 | CR | 20181025 |  | 3 | 2018 Annual Force on Force Engagements |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate the conditions that led to the simulated neutralizations of security response players during the conduct of October 24, 2018 FOF exercise. <I> **** Actions Taken **** Security Program Supervisor advised,
386114 | CR | 20181025 |  | 4 | West BRE window at Post 31 needs to be addressed | N | N |  | N | YES | <D> **** Detailed Description **** West BRE window at Post 31 needs to be addressed to meet expected condition. <I> **** Actions Taken **** Security Programs Supervisor advised <N> **** Equipment Description **** Security Post 31 west BRE window
386115 | CR | 20181025 |  | 3 | BRE 36 thermal camera needs maintenance | N | N |  | Y | YES | <D> **** Detailed Description **** BRE 36 thermal camera picture quality does not meet expections and needs maintenance. <I> **** Actions Taken **** Security Programs Supervisor advised. <N> **** Equipment Description **** Security BRE 36 thermal camera
386116 | CR | 20181025 |  | 2 | Demin water used for ASD drives caused resistivity to lower | N | N |  | N | YES | <D> Work request 29145270 generated to replace ASD filters due to resistivity below required value. The demin water used to mix with glycol was obtained from building 19 (battery storage facility). During addition to tanks resistivity values dropped low enough to cause alarms. Technicians immediately called the Main Control Room. The values dropped to around 0.3 on A2 before values started increasing. <I> Communicated with Main Control Room, PSRO. Informed Managers. Chemistry has tested samples of bottle storing demin water, mixture used for installing in ASD tanks and Plant demin water. Disposed all demin water from Building 19. See attached email in EDMS. <N> ASD building ***General Notes*** Statements from the craft and the supervisor have been uploaded into the EDMS of this AR. Along with emails from Chemistry which ran tests of the various chemical solutions involved in the vent. Pictures of the chemical containers were also uploaded into the EDMS. | 02-00-GY-F-10A2,02-00-GY-F-10B2
386117 | CR | 20181025 | CAQ | D | Transposition error found in RHR B Thermal Perf analysis | Y | N |  | N | NO | <D> **** Detailed Description **** While evaluating past trends of RHR-HX-1B thermal performance, a transposition error was discovered on the analysis for the thermal performance test conducted on 12/12/2017 (WO 02095969). The incorrect RHR outlet temperature was used which resulted in HX margin being calculated ~30% lower than what the actual HX margin should have been. The incorrect HX margin was calculated to be 21.5% when the correct HX margin was actually 53.9%. The last 4 RHR-HX-1B thermal performance tests were also all evaluated for any similar errors and peer checked with none being found. Current margin in RHR-HX-1B per the last thermal performance test conducted 6/12/2018 (WO 02124902) is 52%. HX margin is trending steady. <I> **** Actions Taken **** Discussed with shift manager <N> The RHR-HX-1B thermal performance trend has been updated to reflect the correct value for margin within the HX. The past two surveillances since R23 have yielded margins of 54% (12/12/17) and 52% (6/12/18). | 02-00-RHR-HX-1B
386118 | CR | 20181025 | CAQ | D | HT-HTP-FP/7 | Y | N |  | N | YES | <D> **** Detailed Description **** W/O number 02094048-01. During performance of ppm 10.25.213 insulation test for circuit 27F, the criteria was not met for the resistance reading of 1 gig ohm. located on the south side of SWPH-A <I> **** Actions Taken **** Stopped work and returned everything to its as found condition, notified supervision and intiated CR. Also requesting that a WR be made to replace the heat trace (MR number 240901). <N> **** Equipment Description **** SWPH-A | 02-00-HT-HTP-FP/7
386119 | CR | 20181025 |  | 3 | 2 spare rechargeable radio batteries are missing from FB Stn |  |  |  | N | NO | <D> **** Detailed Description **** Two spare rechargeable radio batteries are missing and need to be replaced as soon as possible from Fire Brigade Staion #1 on TG 441 . This in turn causes the monthly Fire Brigade package to fall below the minimum number of rechargeable batteries that need to be available. <I> **** Actions Taken **** Notified RP Supervision
386120 | CR | 20181025 |  | 3 | 1 spare rechargeable radio battery is missing from FB Stn #2 |  |  |  | N | NO | <D> **** Detailed Description **** One spare rechargeable radio battery is missing and needs to be replaced as soon as possible from Fire Brigade Station #2 in Biulding 62. This in turn causes the monthly Fire Brigade package to fall below the minimum number of rechargeable batteries that need to be available. <I> **** Actions Taken **** Notified RP supervision
386121 | CR | 20181025 |  | 4 | SA-FN-1 belt is worn. | N | N |  | N | YES | <D> **** Detailed Description **** SA-FN-1 drive belt is split all around the outside edge about every four inches causing the unit to make an abnormal noise. Please investigate and replace the drive belt. <I> **** Actions Taken **** Informed supervisor. Wrote AR/WR. <N> **** Equipment Description **** W467 S0/15.9 | 02-00-SA-FN-1
386122 | CR | 20181025 | CAQ | D | SR-21 Particulate Filter Color Is Green | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of WO# 02126054-01, step 7.10.10, upon removal of the Particulate Filter for CMS-SR-21, it was noted that the filter had a green color instead of white. <I> **** Actions Taken **** Informed Supervision, continued with surveillance, and wrote CR to document | 02-00-CMS-F-SR21/1,02-00-CMS-SR-21
386123 | CR | 20181025 |  | 4 | Broken Term Strip will require Repair / Replacement | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WO#02135395, Craft discovered a broken or cracked term point on TB3A point 14. The metal bus for this term point appears to be detaching from the Bakelite. Additionally, there is either a crack between Term points 13 and 14 or two separate term strips are pressed together there. This term strip is located on E-IR-8, inside the Bravo (Right) side term box. The term strip is mounted on the ceiling of the box. Suggest repair or replacement of the term strip at the earliest convenience. S. Oltjenbruns 10/25/18 <I> **** Actions Taken **** This CR & WR written in order to rectify the situation. <N> **** Equipment Description **** TG 501 East side | 02-00-E-IR-8
386124 | CR | 20181025 |  | 3 | Exam Failure - ES000195 - BWRI |  |  |  | N | NO | <D> **** Detailed Description **** One student failed the ES000195 - BWRI exam conducted on 10/25/18. This CR is being written per direction of TDI -02, Rev 35, Section 4.4.10.p.3 <I> **** Actions Taken **** Informed training and line supervision.
386125 | CR | 20181025 |  | 4 | Fire Alarm at APEL |  |  |  | N | NO | <D> **** Detailed Description **** Fire Alarm activated at approximately 0800 hours on October 24, 2018. Manual pull station 1:003 near the West exit door was inadvertantly pulled while an employee was putting on their jacket. <I> **** Actions Taken **** Richland Fire Department responded. APEL building staff were evacuated to the assembly area and appropriate emergency procedures were followed by the APEL Facility Emergency Director and Staging Area Supervisor. Upper Management was notified. No further actions required.
386126 | CR | 20181025 | CAQ | D | SW flow found outside recommended range during walkdown | Y | N |  | N | NO | <D> **** Detailed Description **** While performing system walkdown of the Service Water system, two Service Water flow indicators were found out of the recommended flow range per OSP-SW-M102. SW-FIS-15 as found flow was ~1900 gpm. Recommended flow range is 1650 -1850 gpm. SW-FIS-15 is the flow indication for Service Water flow through DCW-HX-1B1/1B2. There is no upper requirement for flow. SW-FI-29 as found flow was reading 10.5 gpm. Recommended flow range is 12-15 gpm. Minimum operability value is 8 gpm. SW-FI-29 is the flow indication for Service Water flow through RRA-CC-6 which is the room cooler for the RCIC pump room. All other as found flows from the system walkdown were within the recommended flow range. All identified flows were above the minimum operability value. This CR is being initiated for trending purposes. <I> **** Actions Taken **** discussed flows with CRS in control room. | 02-00-SW-FI-29,02-00-SW-FIS-15
386127 | CR | 20181025 |  | 4 | CM-11 not functioning properly | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** CM-11 HP-EQ-53253 at the HP Primary Access will not exit "monitoring" mode. When the paddle is in the craddle, the unit stays in "monitoring" mode. <I> **** Actions Taken **** Initiated CR, tagged instrument "deficient". <N> **** Equipment Description **** GSB HP Primary Access | 02-00-HP-EQ-53253
386129 | CR | 20181025 |  | 4 | Potable water chlorine concentration above 4.0 PPM limit | N | N |  | N | NO | <D> **** Detailed Description **** Upon returning the potable water system to service a slug of chlorine that had collected in the recirc line was added to PWC-TK-100. This brought the chlorine concentration to 5.0 PPM which is above our DOH maximum limit of 4.0 PPM. (Normal value 1.3PPM) We do not need to secure the potable water system as the 4.0 PPM is an annual average. The DOH does require us to take action to reduce the concentration to below 4.0 PPM. <I> **** Actions Taken **** Notified Shift Manager via e-mail. Notified Chemistry supervision of required actions | 02-00-PWC-TK-100
386131 | CR | 20181025 |  | 4 | COND-PI-201D2G is pegged off scale, High | N | N |  | N | YES | <D> **** Detailed Description **** COND-PI-201D2G (COND-DM-1D inlet pressure) is pegged off -scale, High. The indicating needle is stuck on the back side of the low peg stop. COND-DM-1D outlet pressure and all other D CFD parameters are indicating normally. Suspect this condition resulted from water hammer on restoring the D CFD, on 10-23-18. Reccomend COND-PI-201D2G indications be checked again after the next COND-DM-1D change out on 11-5-18. If COND-PI-201D2G still indicates erroneously we should then attempt repair/replacemet. This is not a logged parameter. <I> **** Actions Taken **** Informed MCR, verified all other COND-DM-1D paramaters were indicating normal operation. <N> **** Equipment Description **** RW 467, behind RWCR | 02-00-COND-PI-201D2G
386132 | CR | 20181025 | CAQ | D | ARM-RIS-25 alarms below the set point | N | N |  | N | YES | <D> **** Detailed Description **** On 10/24/2018, approximately 30 bags of used WEA filters were temporarily stored in the RW 487' Hot Machine Shop. These bags created an expected High Radiation Area and the area was posted appropriately. RP notified Operations in the main control room of an expected dose rate alarm at the ARM-AUX-25 detector located in the room. The set point for ARM-RIS-25 is 15 mrem/hr +/- 3 mrem/hr. The dose rate at the detector was 12 mrem/hr as left and the alarm came in. <I> **** Actions Taken **** Nightshift RP moved all the bags south in the room and maximized the distance relative to the ARM-AUX-25 detector on the north wall. The dose rate at the detector was reduced to 6 mrem/hr and the alarm was able to be cleared in the main control room. Approximately 45 minutes later, Op's noted two separate alarms at ARM-RIS-25 of 8-9 mrem/hr. The dose rate at the detector locally was verified to be unchanged at 6 mrem/hr. It is currently not understood by those involved, why alarms were experienced at such low local dose rates. This room does need to be available for higher dose rate work than it is currently limited to by alarming at 8-9 mrem/hr. Action requested is for I&C to verify calibration or recalibrate. | 02-00-ARM-AUX-25,02-00-ARM-RIS-25
386134 | CR | 20181026 |  | 4 | CAS-C-1A low oil level | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1A has oil level just below the minimum spec of 1/8". Compressor was shut down at the time. Logs require oil level between 1/8 and 1/2 while the compressor is shut down. <I> **** Actions Taken **** Wrote CR and informed CRS. | 02-00-CAS-C-1A
386135 | CR | 20181026 |  | 3 | Out Of Tolerance Calibration Standard |  |  |  | N | NO | <D> **** Detailed Description **** During routine calibration of EN Standards Laboratory owned Doble F6150 Power System Simulator (Asset # 0064639), the Standard was found to be out of tolerance (DC Current 0 to 10A Range) . Per ENSL SLI (Standards Laboratory Instruction) 2-33 an investigation is required to identify any instruments that may have been calibrated with the Standard since its last successful calibration. The investigation revealed there were no Plant assets calibrated using the out of tolerance parameter noted. There were 2 instruments calibrated for an external commercial calibration customer using the out of tolerance parameter discovered on the Standard. Use of the Standard reduced the test uncertainty ratio (TUR) of each of the 2 calibrations to less than 1:1 (the target is greater than 4:1) . This reduction of TUR requires recalibration of the instruments affected by the out of tolerance condition. <I> **** Actions Taken **** The commercial calibration customer affected has been notified and a request has been made to have the customer return the affected instruments to ENSL for recalibration.
386136 | CR | 20181026 | CAQ | C | E507-1 references an incorrect print |  |  |  | N | NO | <D> **** Detailed Description **** E507-1 says that the logic drawer is on CVI 01-11,58 it should say it is on 01-00,58
386137 | CR | 20181026 |  | 3 | Valve misposition found in Makeup Demineralizer Trailer | N | N |  | N | YES | <D> **** Detailed Description **** During data collection, Chemistry technician observed makeup demineralizer trailer (MUD) output flowmeter at 0 gpm. At this time, the MUD trailer had been in operation for 10 hours with all water going to reject. Upon investigation, the chem tech discovered V-42 was shut inside the MUD trailer. This valve is normally open. <I> **** Actions Taken **** Chem tech contacted Chemistry on call supervision. Per Supervisor agreement V-42 was opened. Trailer output flow was observed at 44 gpm. Chemistry technician contacted MCR and was notified that demin water storage tank (DWST) level was at 55 inches. DWST level was observed rising after re-establishment of flow from MUD trailer. Chemistry sampled MUD Trailer and confirmed water quality in specification with SWP-CHE-02. V-42 is not normally operated by station personnel. The MUD trailer vendor was on site performing maintenance inside the trailer the previous day. CR written to document event.
386140 | CR | 20181026 |  | 4 | Steam leak from 1 inch piping elbow in RFT-A | N | N |  | N | YES | <D> **** Detailed Description **** Steam leak from 1 inch piping elbow in RFT-A. leak was identified in CR 385834 on the 18th of OCT as coming from the valve body but I belioeve there is a small hole in the piiping that is blowing into the lagging. please investigate and evaluate a fix for the steam leak. I believe the piping is the above seat drains for MS-V -172A. <I> **** Actions Taken **** wr and CR please see the videos attached to CR 385834 | 02-00-MS-V-172A,02-00-RFW-DT-1A
386146 | CR | 20181027 | CAQ | D | TEA-SR-26 indicates "no flow control" message | N | Y |  | N | YES | <D> **** Detailed Description **** It was observed while performing CSP-INST-D201 that TEA -SR-26 display has a message "no flow control" in addition to the message "no isok control" that has already been written up ref CR/WR 383740/29144252. This message may be related to the previous one. TEA-SR-26 sample flow is similar to recent sample flow rates that have been recordered, all the operate lights are on, and the sample rack is in service. <I> **** Actions Taken **** Notified OPS, Wrote CR/WR, Notified supervision. | 02-00-TEA-SR-26
386147 | CR | 20181027 |  | 4 | RRC-IMD-ASD1A/2 comms failure | N | N |  | N | YES | <D> **** Detailed Description **** RRC-IMD-ASD1A/2 comms failure / does not communicate with main control room. Prevents the ability to monitor drive status / faults from the control room. Suggest assign to I&C FIN as they have successfully reset this connection several times. | 02-00-RRC-IMD-ASD1A/2
386148 | CR | 20181027 |  | 4 | E-BU-SWA7/9 Lamp Fault light flashing | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-SWA7/9 Lamp Fault light flashing. <I> **** Actions Taken **** Wrote this CR and informed Main Control Room. | 02-00-E-BU-SWA7/9
386149 | CR | 20181027 |  | 4 | E-BU-SWS6/3 Lamp Fault light is flashing | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-SWS6/3 Lamp Fault light is flashing <I> **** Actions Taken **** Wrote this CR and informed Main Control Room. | 02-00-E-BU-SWS6/3
386150 | CR | 20181027 |  | 4 | E-BU-SWA6/2 Battery Fault light flashing | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-SWA6/2 Battery Fault light flashing <I> **** Actions Taken **** Wrote this CR and informed Main Control Room. | 02-00-E-BU-SWA6/2
386151 | CR | 20181027 |  | 4 | Cooling Tower 2C fan 35 motor oil at the add point | N | N |  | N | YES | <D> **** Detailed Description **** Cooling tower 2C fan 35 motor needs oil | 02-00-CW-FN-35
386152 | CR | 20181027 |  | 4 | ASD1B/2 out of paper | N | N |  | N | YES | <D> **** Detailed Description **** ASD1B/2 paper light is flashing red and the DTR green light that is normally illuminated is off. <I> **** Actions Taken **** Informed MCR | 02-00-RRC-IMD-ASD1B/2
386153 | CR | 20181027 |  | 4 | Cathodic Protection Box Corroded - CP-RECT--6/3 | N | N |  | N | YES | <D> **** Detailed Description **** Cathodic Protectioon test station terminal box CP-RECT-6/3, locaated outside GSB single door is significantly corroded and needs replaced. See attached pictures. <I> **** Actions Taken **** Notified Buried Piping Program Engineer. <N> **** Equipment Description **** CP box loccated outside single door into GSB | 02-00-CP-RECT-6
386154 | CR | 20181027 |  | 3 | Cathodic Protection Term Box has Water inside - CP-RECT-10 | N | N |  | N | YES | <D> **** Detailed Description **** Cathodic Protection terminal box CP-RECT-10 test station #4 located outside south side of SW pumphouse A has water inside the terminal box. As shown by attached pictures, this water appears to collect as a result of this box and associated concrete housing being at low point and collecting carry over from the spray ponds. Recommend drilling weep hole in bottom of term box to allow it to drain. <I> **** Actions Taken **** Notifiied Buried Piping Program Engineer <N> **** Equipment Description **** outside south side SWPMHSE A | 02-00-CP-RECT-10
386155 | CR | 20181027 | CAQ | C | E520-4 correction |  |  |  | N | NO | <D> **** Detailed Description **** On E520-4 it has the + fuse going to the main drain valve indications as 2A. E555-E-IR-08 says it is 10A. EWD-66E-023 also says this fuse it 10A.
386156 | CR | 20181027 |  | 3 | Demin water trailer is not operating as expected | N | N |  | N | YES | <D> **** Detailed Description **** The demin water trailer was found with Bank 1 selected and the transfered light on. Flow was verified through bank 2 as expected, however flow was also observed through Bank 1. Normal flow is trough only one demin bank at a time until exhausted, then the other bank goes in to service. There are also continuous Email notifications being received of an "RO fault". There are no alarms indicated at the control panel except the transfer light. <I> **** Actions Taken **** Sampled the trailer outlet to verify water quality then shutdown the trailer pending sample results. Restarted the trailer after satisfactory sample results with supervision permission. Attempted to contact the vendor twice and have left voicemails. Notified supervision and OPS. Wrote CR <N> **** Equipment Description **** Demin water trailer
386157 | CR | 20181027 |  | 3 | Blue equipment tag printer in MCR continues to be INOPERABLE |  |  |  | N | YES | <D> **** Detailed Description **** Blue equipment tag printer in MCR continues to be INOPERABLE. This is an essential piece of equipment for Operations. This has been out of service for an expended period of time for what appeared to be a failure of the communications module and for the Optical tag locating system. This item has been CR'd multiple times. Though the small caution tag printer has been rendered functionable all 4 printers are constantly needed.With out these machines working a considerable time is spend to move tags about from the SSS office in the GSB to the MCR. On a busy week there is probably half a shift wasted (in aggregate) for the transportation of tag simply to do work. Please repace this printer posthaste. It is incomprehensible that one of the 4 idle machines in the SSS office could not be repurposed and placed in the MCR. <I> **** Actions Taken **** Wrote this AR after the SSS made a special trip to the MCR to deliver 1 tag so oil could be added to CAS-C-1A at the cost of EOs, Craft, and supervisions time. <N> **** Equipment Description **** Blue tag printer in MCR W 501 Replaced printer and tested satisfactorily per WR 29145334.
386159 | CR | 20181028 |  | 4 | TMU-P-1B lower bearing oil level is low | N | N |  | N | YES | <D> **** Detailed Description **** TMU-P-1B lower bearing oil level is low, oil level was previously identified as at the low level under WR 29145266. Please add oil when the pump is tagged out for impeller lift or immediately. <I> **** Actions Taken **** wr/cr field sup notified. | 02-00-TMU-M-P/1B,02-00-TMU-P-1B
386160 | CR | 20181028 |  | 3 | TMU-P-1A lower oil glass is not marked properly | N | N |  | N | YES | <D> **** Detailed Description **** TMU-P-1A lower oil glass is not marked properly. There is no min, max or standby levels as required per the logs or like the other pumps have. please see pictures. motor was recently replaced. <I> **** Actions Taken **** CR | 02-00-TMU-M-P/1A,02-00-TMU-P-1A
386161 | CR | 20181028 |  | 4 | TMU-SR-1 is has a large amount of dead bugs inside | N | N |  | N | YES | <D> **** Detailed Description **** TMU-SR-1 is has a large amount of dead bugs insidethe cabinet. in addition it also has spiders living off of the bugs and making webs inside of the cabinet. the cabinet is sealed around the door but there are several holes (knock outs that arenet sealed in the bottom. the whole corner the cabinet is in could use a spraydown due the layers of dead bugs. please see pictures attached,. request the cabinet holes and penetrations be sealed to protect the companies asset and its operability <I> **** Actions Taken **** wr/cr | 02-00-TMU-SR-1
386162 | CR | 20181028 | CAQ | C | Adverse Impact of PC venting on DW Oxygen Concentration | Y | N |  | N | YES | <C> This CR reopened based on MRT review. This has been changed from a CAQ D to CAQ C to the OPSPROC owed to group. <D> **** Detailed Description **** Venting and purging operations are currently being performed on the Primary Containment (PC) in order to reduce Drywell (DW) Oxygen (O2) concentrations. DW O2 concentration continues to rise, questioning the effectiveness of the vent and purge. A review of Div 1 and Div 2 O2 concentration over time shows that the Div 2 O2 concentration (CMS-SR-14, aligned to the DW) rises after venting the WW and DW. This has been seen in the past, but DW O2 levels tended to restore to normal values. This has not been happening with the latest series of vents and purges. Recommend securing the vent and purge of PC until the PC O2 concentration has been verified and the O2 response to venting and purging is better understood. A plot of recent vent and purges has been attached to the EDMS. <I> **** Actions Taken **** CRS and SM have been informed. <N> This CR trended to CR 385697 (C/CAQ) | 02-00-C-TK-1
386163 | CR | 20181028 |  | 4 | Security XD3 needs maintenance |  |  |  | N | YES | <D> **** Detailed Description **** Security XD3 is not operating by design and needs maintenance. <I> **** Actions Taken **** CR/WR initiated. Security supervision notified. Equipment taken out of service. | 02-00-SEC-XD-3
386169 | CR | 20181028 | CAQ | D | RCIC-TK-1 Drain pan drain line clogged | N | N |  | N | YES | <D> **** Detailed Description **** OPS2 reports the RCIC-TK-1 drain pan drail line is clogged resulting in water backing up in the drain pan. Current level in the drain pan is approximately 1/2 inch of water. The drain pan will overflow at about 1 inch of water in the pan. Request maintenance personnel rod out the drain pan drain line to prevent overflow of the drain pan and adverse radiological consequences. <I> **** Actions Taken **** Discussed with CRS/SM. | 02-00-RCIC-TK-1
386170 | CR | 20181028 | CAQ | D | SLC tank level higher than normal | Y | Y |  | N | YES | <D> **** Detailed Description **** SLC-LI-601 indicates ~5050 gal, SLC-LI-1 indicates 5000 gal, and TDAS pt X077 indicates 4962 gal. SLC tank level is definitely above the low spec of 4587 gal identified in TS 3.1.7.1. OSP-INST-H101 suggests sparging the SLC tank to reduce level if greater than 4950 gal. Also note that SLC -LI-601 identifies a high level alarm at 5046 gal which is NOT in at this time. <I> **** Actions Taken **** Notified shift management | 02-00-SLC-LI-1,02-00-SLC-LI-601,02-00-SLC-TK-1
386171 | CR | 20181028 | CAQ | D | CMS-SR-21 vacuum indication low. | Y | N |  | N | YES | <C> CR reopened to cross reference additional WR 29143975, then taken back to complete <D> **** Detailed Description **** From 10/25 to 10/26/18 the logged value for CMS-SR-21 vacuum went from a value of 7 inches to a value of aroue 2-2.5". Suspect the there is a leak on the vacuum side of CMS-SR-21 and this is currently contributing to the rise in containment oxygen concentration. Please investigate and correct. <I> **** Actions Taken **** Wrote this CR. Informed supervision and recomended that attention be given to CMS-SR-21. | 02-00-CMS-SR-21
386172 | CR | 20181028 |  | 4 | WOA-FN-9 belt degrading | N | N |  | N | YES | <D> **** Detailed Description **** WOA-FN-9 belt is degrading, making an irregular noise and there's a visible protrusion on the belt. Recommend replace belts before complete failure. <I> **** Actions Taken **** Informed MCR, generated AR/WR. | 02-00-WOA-FN-9
386173 | CR | 20181028 |  | 4 | CAS-C-1C has low oil | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1C oil level is below the low spec of 1/8". Please add oil. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 441 | 02-00-CAS-C-1C
386174 | CR | 20181028 |  | 4 | (NRC) Rope found in Rx 422 NE stairwell |  |  |  | N | NO | <D> **** Detailed Description **** The NRC resident informed the MCR of approximately 20 ft of manila rope in the Rx 422 NE stairwell. The rope was found coiled under a sign that indicated the area was a combustible free zone. The rope was removed and placed in the tool crib. This CR documents the NRCâ€™s observation, and serves to remind the station to follow signage. <N> OPS2 found additional items during an extended walkdown. See EDMS for pictures. | 02-00-R-BLDG-MISC
386175 | CR | 20181028 |  | 3 | (NRC) E-BU-SWA7/10 aux unit 10A occluded by FP piping | N | N |  | N | YES | <D> **** Detailed Description **** The NRC resident informed the MCR of the E-BU-SWA7/10 aux unit 10A being partially blocked by FP piping (reference FP-V-127 for a location). A small portion of the light is blocked, so there is no immediate concern for functionality of the light, but the light should be adjusted away from the pipe. <I> **** Actions Taken **** Informed SM and Fire Marshal | 02-00-E-BU-SWA7/10
386183 | CR | 20181029 |  | 4 | DW-V-100/53 is leaking by at 6 dpm. | N | N |  | N | YES | <D> **** Detailed Description **** DW-V-100/53 located in the Aux Condensate Room , Reactor Bldg.422' level , is leaking on the floor at a rate of about 6 dpm. There is a small stream leading to a near by floor drain. <I> **** Actions Taken **** Notified CRS, attempted to tighten the valve in the closed position to stop the leak. No success. <N> **** Equipment Description **** Rx 422. Aux condensate room. | 02-00-DW-V-100/53
386190 | CR | 20181029 |  | 3 | SS-RV-12B isometric differs from M200-460 | N | N |  | N | NO | <D> **** Detailed Description **** The configuration of the vent piping downstream from SS -RV-12B shown on CVI ISO 215-00,13814 differs from the configuration shown on AED MEC M200-460. M200-460 was revised in 2013 per EC 11736 to include dimensions as well as configuration changes. ISO 215-00,13814 was also revised in 2013 per EC 11736, but the only change identified was the material spec. No piping configuration changes were made to the ISO. Based on conversation with Design Engineering, the Isometric requires an update. <I> **** Actions Taken **** Notified Supervisor. Validated drawing discrepancies with Design Engineering. Initiated CR. | 02-00-SS-RV-12B,02-00-SS-V-606
386191 | CR | 20181029 |  | 3 | RWCU-RST-70A requires change out. | N | N |  | N | YES | <D> **** Detailed Description **** RWCU-RST-70A has been operating at an elevated D/P which has caused RWCU-DM-1A to be operated at reueced flow. We are approaching the point where this will be impacting when RWCU-DM-1B is taken out of service. This is an unusually short life for this resin strainer. Tags were lifted on 5/31/18 for WO 02128789. Previous change outs were 8/6/2015 WO 02080584, and 2/28/10 WO 01182732. Recomend changing this strainer and evaluating if there is a possiblity of resin leakage past the septa. Please see attached graphs of logged values for RWCU-RST-70A. It appears that during the backwash and precoat on 7/17/18 caused a step jump in D/P. The backwash of RWCU-DM-1B 10/4/18 also caused a step increase of RWCU-RST-70A. On 10/27 Operations backwashed the strainer with no change. On 10/28 I&C vented RWCU -DPIS-88A with no change. The leaves the strainer itself as the cause of D/P <I> **** Actions Taken **** Informed Supervision. Wrote this AR. Attached Grahps to EDMS | 02-00-RWCU-RST-70A
386192 | CR | 20181029 |  | 4 | Need temperature monitoring instrument installed by CN-TI-2 | N | N |  | N | YES | <D> **** Detailed Description **** Operations Department is anticipating inerting containment on 10/30/2018 per SOP-CN-CONT-INERTING. Request I&C shop install additional temperature monitoring per step 5.1.1 of SOP-CN-CONT-INERTING. <I> **** Actions Taken **** Discussed with SM. | 02-00-CN-TI-2
386193 | CR | 20181029 |  | 3 | Work not completed based on safety concern. |  |  |  | N | NO | <D> **** Detailed Description **** Work order 02114472 (FP-ZONE-18, 2-YR SENSITIVITY CHECK) was not completed during the week of 10/22/18 based on an increased threshold related to industrial safety. Fire protection zone 18 covers the Reactor building 572 elevation and requires the craft to free climb to different fire zone dectectors utilizing a fall protection plan. <I> **** Actions Taken **** Generated CR to document the need to minimize/eliminate the industrial hazard. <N> Intent of CR is trending why work was not completed during the week. No further actions required.
386198 | CR | 20181029 |  | 3 | (NRC) PPM 10.2.13 Revision based off review |  |  |  | N | NO | <D> **** Detailed Description **** Based off of a review of PPM 10.2.13 Maintenance Programs has identified items within the procedure that need to be updated. Sections 7.2 and 7.3 â€“ Define or make reference to Primary and Non-Primary systems definitions. Sections 7.2 and 7.3 â€“ Update or remove references to specific chemicals that can be used in primary or non -primary systems. <I> **** Actions Taken **** Recommend assignment to AR-MNTPROG
386201 | CR | 20181029 |  | 3 | update ISP-FDR/EDR-X301 FOR correct gasket |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** per step 4.5 of WO# 02102735-01, update ISP-FDR/EDR-X301 for proper CGI style of gsket Cat ID 27592 <I> **** Actions Taken **** wrote this AR
386202 | CR | 20181029 |  | 3 | Revision required for MI-1.8 |  |  |  | N | NO | <D> **** Detailed Description **** Need to add rounding criteria and significant digit criteria to MI-1.8. No procedural guidance exists for this currently in maintenance. See document in EDMS for previous guidance. <I> **** Actions Taken **** Initiated CR for procedure revision <N> Revision has been migrated into Maintenance Programs database, link attached to EDMS.
386203 | CR | 20181029 |  | 4 | Late eSOMS entries for Maintenance |  |  |  | N | NO | <D> **** Detailed Description **** An electrician worked 2 days he was scheduled to be off (10/24 & 10/25) without notifying the eSOMS scheduler to update his eSOMS time. A mechanic was called out to work on 10/21 without hours being entered in eSOMS prior to his working. Two mechanics were asked to start work at 0600 instead of at the scheduled time of 0645 without the time being changed in eSOMS. No violations occured when eSOMS was updated. <I> **** Actions Taken **** Updated eSOMS with correct hours.
386204 | CR | 20181029 |  | 4 | ISFSI Light Plant burms not meet expectations |  |  |  | N | NO | <D> **** Detailed Description **** During a walk down in the ISFSI it was observed that a couple of the light plants placed around the ISFSI had ecology burms that did not meet expectations. One on the south side appeared to be wind blown and would not have contained fuel in the event of a catastrophic spill. Another on the northside appeared to have one side colapsed and also would not prevent a spill. <I> **** Actions Taken **** Discussed with the security officer onsite and followed up with the Security shift leutenant. Confirmed facilities initiated a ticket to resolve. Recommend close to trending.
386207 | CR | 20181029 |  | 3 | CRG and WRSC communication |  |  |  | N | NO | <D> **** Detailed Description **** The station has 2 separate committees that review items input to the corrective action program. The Condition Review Group (CRG) reviews CRs and if it determine a condition is best corrected by maintenance, it closes the CR to a Work order or WR with the owed to group being CR -TRNDREP. The work request screening committee (WRSC) reviews work requests (WR) and if it determines a WR is an administrative issue that requires no maintenance it cancels the WR with a reference that the condition will be corrected by the CR that generated the WR. These groups do not have any individuals in common and many times come to different conclusions ending with both the CR and WR closed with no actions. Recommend including a member of CRG in the WRSC to concur with any WR closures.
386209 | CR | 20181029 |  | 4 | MT-ELEV-3 is stuck on the 501 elevation and will not move | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-3 the turbine building elevator is stuck on the TB 501 elevation. Placed the elevator out of service signs to prevent use of elevator. <I> **** Actions Taken **** Initiated CR, contacted MCR | 02-00-MT-ELEV-3
386210 | CR | 20181029 |  | 3 | Unable to replace CBD valves due to excessive leakage. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Attempted to perform replacement of CBD-V-10 on WO 02103756 and install CBD-V-40 & 41 on WO 02129365 but could not due to excessive leakage. Not sure if the water is coming from the river or through the isolation valves. <I> **** Actions Taken **** Contacted Work Week Manager and Supervisor.
386212 | CR | 20181029 | CAQ | D | R-DOOR-R304 Doors jamb bolt stripped. | Y | Y |  | N | YES | <D> **** Detailed Description **** Working on WO # 02128337-01 repairing threshold and seal, found a bolt on the door jamb to be stripped . and the bottom Dog latch degraded. Door still functions, | 02-00-R-DOOR-R304
386213 | CR | 20181029 | CAQ | C | PRM-SR-1 Software issue | N | Y |  | N | YES | <D> **** Detailed Description **** following replacement of of the CF card in PRM-SR-1 (WO 02135734) and powering up the sample rack, PRM-SR-1 had a trouble alarm that would not clear until a Manual Check source was performed. Then the rack completed its start routine. WO 02135734 . . thie PMT was performed under WO 02120843 Satisfactorily. . This issue was discussed with the SME today and he stated that this issue had also occurred during the site acceptance testing. The Vendor updated the software during the accepance testing to correct the issue. . WHen the software was loaded onto the CF card during WO 02135734. the version of the software may not have included this change. The version of the software may be incorrect. . WO 02135734-01 verified that the parameters in the CPU matched the IMDS for PRM-CPU-1 and the PMT PPM 16.1.12 was performed sat. . <I> **** Actions Taken **** discussed with FIN engineering and wrote CR | 02-00-PRM-CPU-1,02-00-PRM-SR-1
386214 | CR | 20181029 | CAQ | D | Extent of Condition analysis from CR 385044 | Y | N |  | N | YES | <D> **** Detailed Description **** As a part of the Extent of Condition analysis from CR 385044, the alarm typer from 9/29/2017 was pulled from the vault to see what alarms were received during the last performance of ISP-MS/IST-A101 IN SERVICE TESTING OF MAIN STEAM RELIEF VALVE ACTUATION SWITCHES. The alarm typer showed that six valves (including MS-RV-2A, which opened during this test on 9/28/2018) had intermittent tripped signals when the control switches were operated (MS-RMS -RV/3A, MS-RMS-RV/2D, MS-RMS-RV/2B, MS-RMS-RV/3B. MS-RMS -RV/1A). These valves had the SRV Pilot Solenoid Tripped signal come in for approximately 0.4 seconds and cleared when the switch movement ended. The control switches for these valves are maintained contact switches and the SRV Pilot Solenoid tripped signal will come in when both the AUTO and OFF contacts are open or when the pressure switch relay energizes. These intermittent tripped signals occurred when the control switches were being operated, which is a sign of the switches not maintaining contact when changing position. The alarms all cleared when the switches re -established continuity/contact after changing position. There is no evidence that the OPEN function of the switch is affected since this signal only comes in when manipulating the switch. These switches do not affect pressure relief function of SRV and all of the affected switches are NON-ADS valves. A photo of the alarm typer is located in the EDMS folder. <I> **** Actions Taken **** Contacted Shift Manager | 02-00-MS-RMS-RV/1A,02-00-MS-RMS-RV/2B,02-00-MS-RMS-RV/2D,02-00-MS-RMS-RV/3A,02-00-MS-RMS-RV/3B
386215 | CR | 20181029 |  | 4 | WOA-FN-5 has 1 of 2 belts broken | N | N |  | N | YES | <D> **** Detailed Description **** WOA-FN-5 has 1 of 2 belts broken. please replace belts as needed. <I> **** Actions Taken **** CR/WR | 02-00-WOA-FN-5
386216 | CR | 20181029 | CAQ | D | please evaluate priority on W-DOOR-C238 repair 29144709 | N | N |  | N | YES | <D> **** Detailed Description **** please evaluate priority on W-DOOR-C238 repair 29144709. Door knob is degrading and is a single poing entry to Division 2 battery chargers and other equipment that is adressed in the EOP's. If the door knob broke it would deny us access to that equipment during daily routines and Casulty actions. Please repair promptly original WR was written last month. <I> **** Actions Taken **** wrote CR discussed with field supervisor. | 02-00-W-DOOR-C238
386217 | CR | 20181029 |  | 4 | Scaffolding around RCC-P-1A is no longer required | N | N |  | N | YES | <D> **** Detailed Description **** Scaffolding around RCC-P-1A is no longer required Taf has it installed under 01158000. RCC-P-1A has been running for a while now. <I> **** Actions Taken **** CR/WR | 02-00-R-BLDG-MISC,02-00-RCC-P-1A
386218 | CR | 20181029 |  | 4 | BRE 36 AVSS Monitor |  |  |  | N | YES | <D> **** Detailed Description **** The AVSS monitor in BRE 36 for the OCA camera system needs to be replaced. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Security notification made, IS help ticket IR-0035060 initiated <N> **** Equipment Description **** BRE 36 located SE of bldg 88
386219 | CR | 20181030 |  | 4 | Operations tool box Moved from designated storage and blocke |  |  |  | N | YES | <D> **** Detailed Description **** Operations tool box moved from designated storage (southwest r 522) and blocked from opening in new position with carts and scaffolding. Tool box has necessary toold and equipments to respond to HCU alarms, Poor communications between departments. affected individuals last to know. Please return locker to the proper position. Locker is marked that it contains radioactive material. <I> **** Actions Taken **** Informed the MCR response would be delayed as the tools and equipment would have to be obtained from the opther side. <N> **** Equipment Description **** sw R 522 oPS TOOL BOX . Is an SWP-MAI-02 Authorized Storage Area Permit needed? | 02-00-R-BLDG-MISC
386223 | CR | 20181030 | CAQ | D | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0066042 Fluke Doc. Process Calibrator Found OOT & adjusted within specs. EFIN Eval: ALL except usages #11 & #13: Either the OOT range was not used or the reading was in PSI. The PSI uses the 743B as a display unit only. Usages #11 & #13 Work Orders was canceled. No Impact. DEF #6766A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
386226 | CR | 20181030 |  | 3 | Decision making, need to document DO Pump extension |  |  |  | N | YES | <D> **** Detailed Description **** In review of the T-20 work for DG2 in March it was discovered that the DO pump work has been moved out. System Engineer requests to formally document management decision. This work has been moved multiple times, it is on the system health report improvement plan and is a risk to the SBAC reliability as a first time PM. <I> **** Actions Taken **** Wrote CR, Discussed with Pump Program Owner <N> A quick search of ECs and ARs associated with this DO pump shows that there is no approved EC for doing the pump replacement and thus this work would not be scoped at T-20 for implementation. Further, AR 307241-04 documents the management decision requested regarding when this work is approved on the LRP. This CR can be trended to this pre -existing documentation. I have cross referenced AR 307241 to this CR for ease of reference. | 02-00-DO-P-1A
386230 | CR | 20181030 |  | 3 | Software status in Catalog not accurate for corp software |  |  |  | N | NO | <D> **** Detailed Description **** The current status of corporate software in the Software Catalog at Design status is not correct for many software EPNs. It is important to keep the status of the software up-to-date so individuals know what software is allowed to be installed on corporate computers. Recommend assignment to ITMGMT as Category 3 <I> **** Actions Taken **** Generated CR; notified supervision <N> There is minimal risk to these softwares being at the incorrect state as they are corporate side software and have been in this state for some time. The cause of them not being advanced to Active is unknown but will be reviewed as the CR is resolved. Many of the software EPNs have ARs cross-referenced that show all work complete so it is just a matter of the EPN not being advanced to Active state.
386231 | CR | 20181030 |  | 4 | Need 0-250 psig gauge installed at CN-V-96 |  |  |  | N | YES | <D> **** Detailed Description **** SOP-CN-SHUTDOWN prerequisite 3.1 requires installation of the test pressure gauge at CN-V-96 if adjusting CN-PCV-4. Operations department will be inerting containment and adjusting CN-PCV-4 on 10/30/18 so this gauge is required. Request I&C install the required gauge to support reducing drywell oxygen concentrations. <I> **** Actions Taken **** Discussed with CRS and PSRO. <N> This pressure gauge is installed and removed for adjustment of CN-PCV-4 per PPM SOP-CN-SHUTDOWN. The SOP prerequiste is to verify I&C available to install a gauge - SOP step 5.4.18 b. 11) installs the gauge and SOP step 5.4.18 b. 16) removes the gauge. | 02-00-CN-PCV-4,02-00-CN-V-96
386236 | CR | 20181030 | CAQ | D | Inadvertant TMU Fire Alarm at FCP1 during 15.2.49 Test | N | N |  | N | YES | <C> CR reopened to cross reference additional WR 29136925, marked completion required box, then taken back to complete <D> **** Detailed Description **** During the implementation of Procedure 15.2.49 (Function and Sensitivity Check of VESDA), the electricians noticed that when the fire alarm for some of the zones being tested is received at Fire Panel FP-CP-FCP1 and they attempt to Acknowledge the Alarm, drop 8-2 for TMU Building fire alarm is also received. Once the RESET button is pushed, in addition to the zone being tested the TMU Fire alarm also goes away. The wiring and some of the components associated with TMU fire alarm circuit were modified as part of EC 13537. This identified issue does not impact the fire detection and alarm function associated with the TMU Building or the VESDA system and as such there are no operability concerns. <I> **** Actions Taken **** 1. Notified Supervisor 2. Initiated review of changes implemented during EC 13537 installation to determine potential causes of inadvertant fire alarm. <N> **** Equipment Description **** RW 501" | 02-00-FP-CP-FCP1
386237 | CR | 20181030 |  | 4 | Broken fluorescent light bulb discovered in building 32 |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** This morning upon entering the carpenter's shop area, employees discovered a fluorescent light bulb shattered on the ground.The cause of the occurrence is yet unknown. <I> **** Actions Taken **** The area was taped off with Caution tape and signage and facilities was contacted about the occurrence. <N> Area has been cleaned up. No further action required.
386239 | CR | 20181030 |  | 4 | SA-PS-8 local gauge not indicating |  |  |  | N | YES | <D> **** Detailed Description **** SA-PS-8 local gauge not indicating. During Aux Boiler run, on step 5.2.28 of SOP-AS-START, we verify that SA-PS-8 local gauge indicates about 10psig. The gauge never left the 0(zero) mark. Air was being supplied, the Aux Boiler did start and fire up, but it is unknow what supplied air pressure was due to the gauge not working. <I> **** Actions Taken **** Wrote this CR and informed control room. Recommend replacing the gauge. | 02-00-SA-PS-8
386243 | CR | 20181030 | CAQ | C | ENPWRK SIEM SQA paperwork missing SVVR and BDR |  |  |  | N | NO | <D> **** Detailed Description **** AR 381123 is missing SVVR and BDR. The AR assignment was mistakenly associated with SQA documentation that was already submitted and this AR was prematurely closed. <I> **** Actions Taken **** SVVR needs to be completed. BDR needs to be completed. Submit hard copies to records.
386247 | CR | 20181030 | CAQ | D | MS-V-120B downstream temps indicated leak-by | Y | N |  | N | YES | <D> **** Detailed Description **** MS-V-120B, which has been identified as spuriously opening and recently closed via temp mod, appears to be leaking by. Downstream temperatures from cycle isolation monitoring show that the temperature is ~40-45 DegF higher than prior to when the valve began spuriously opening (See EDMS email for trend info). These main steam trap bypass valves have shown evidence of internal erosion previously. Recommend downstream temperatures continue to be monitored and valve inspection/replacement be planned for R25. <I> **** Actions Taken **** Discussed with thermal performance engineer and supervisor. Notified AOV engineer. <N> **** Equipment Description **** T478 B6/7.5 | 02-00-MS-V-120B
386248 | CR | 20181030 |  | 4 | Deschutes sink filtered water faucet leaking | N | N |  | N | NO | <D> **** Detailed Description **** filtered water faucet in the main lunch room is leaking at the drain line air gap in the faucet body. Most likely a clogged drain line. <I> **** Actions Taken **** turned off the water supply to the faucet and cleaned up water on the floor. <N> **** Equipment Description **** filtered water faucet in deschutes lunchroom sink
386251 | CR | 20181030 | CAQ | C | eSOMs did not correctly calculate some readings | N | Y |  | N | NO | <D> **** Detailed Description **** Stations 124 and 147 did not calculate correctly. Station 124 showed 177Â°F with a manual calculation value of 142.67. Station 147 showed a calculation of 0Â°F and a manual calculation of 122.66Â°F. Additonallyseveral values were show in red for being out of specification which were not. Stations 12,13,14,15,16,18,19,20,22,23,25,26,27,28,172,173, 174,175,628. The original approval for OSP-INST-H101 was 10:30:12. After unapproving the surviellance to put notes in for the manually calculated values the H101's were reapproved at 10:51. <I> **** Actions Taken **** Wrot e this CR to document this issue and inputed manually calculated values. Attempted to get the 101's to calculated correctly with no success. Recommend close to trend.
386252 | CR | 20181030 |  | 4 | PS-V-4 & PS-V-5 will not fully close | N | N |  | N | YES | <D> **** Detailed Description **** PPM12.9.11 section 7.7 has chemistry close PS-V-4 and PS -V-5 to isolate TSW flow so we can clean PS-ST-2. These are 90 degree PVC valves and will not shut to the full 90 degree position. Precaution and limitation 4.1 states that flow must be secured whenever a station needs to be opened. Without confirmation of valve travel to the full closed position, the strainer was not cleaned and the valves were returned to the normal open position. Debris is suspected of preventing full closed position. Both valves need to be replaced or repaired. <I> **** Actions Taken **** Notified supervision OPS, and wrote CR/WR. | 02-00-PS-CPST-TSW/1,02-00-PS-ST-2,02-00-PS-V-4,02-00-PS-V-5
386253 | CR | 20181030 |  | 3 | Cycle Isolation Monitoring signals not working | N | N |  | N | YES | <D> **** Detailed Description **** 32 out of 57 newly installed (R23) cycle isolation monitoring signals are not working based on todays eDNA data. Several signals are intermittently working. MS-TT-V/120B has shown to be providing an inverse signal. See excel file listing in EDMS for a snapshot of faulty signals. Recommend evaluation by thermal performance engineer and vendor. <I> **** Actions Taken **** Discussed with thermal performance engineer and supervisor. | 02-00-MS-TT-V/120B
386254 | CR | 20181030 |  | 4 | ARGOS @ HP PAP is Out of Service (Safety Concern) | N | N |  | N | NO | <D> **** Detailed Description **** (HP-EQ-42784) has the detector screen peeling out and has created a Safety Concern for anyone using it. ARGOS was taken OOS to eliminate any potential injury. <I> **** Actions Taken **** -Initiated CR & WR. -Notified Supervision. <N> **** Equipment Description **** HP PAP (HP-EQ-42784) | 02-00-HP-EQ-42784
386256 | CR | 20181030 |  | 4 | Oily water found outside of SLOP drum | N | N |  | N | NO | <D> **** Detailed Description **** Water puddle with a trace of oil was found by Slop drum on 441 TG leading to drain connected to T3 sump. Drum was found to be approximately Â¾ full with hose secured in drum. Cause believed to be hose over pressurized allowing water to spill outside of drum. Roughly 1/2 gallon of oily water enter T3 sump through drain. <I> **** Actions Taken **** Cleaned up spill and reported to appropriate personal <N> **** Equipment Description **** T3 sump | 02-00-FD-SUMP-T3,02-00-T-BLDG-MISC
386257 | CR | 20181030 |  | 3 | Beta gamma to alpha conversion factor delated from 11.2.13.1 |  |  |  | N | NO | <D> **** Detailed Description **** During implementation of the Nuclear Industry Standard Procedures for RP the correction factor for converting mad/hr to dpm when counting smears was removed from PPM 11.2.13.1. This conversion factor is needed in order to calculate beta-gamma to alpha ratios. These ratios are needed to properly classify areas for alpha contamination risk level. Recommend revision of 11.2.13.1 to add the conversion factor back into procedure. This issue does not represent a challenge to RP controls. The conversion factor is available in HP calculation 15-01. <I> **** Actions Taken **** Wrote this CR.
386258 | CR | 20181030 | CAQ | C | Adverse Trend, TEA-SR-26 representative sample degrading | N | Y |  | N | YES | <D> **** Detailed Description **** An adverse trend of CRs was identified (CRs 379155, 383740 and 386146). This condition has been escalating from a simple increase in system vacuum in April 2018, to increased error messages on the TEA-RIT-13 in August and now October. This slow degradation of sample flow would be an expected response to occlusion of the sample nozzles at TEA-RSM-93. There is a PM to clean the sample nozzles (PMID 26156), but the frequency is 4 years and may be too long given the increased amount of smoke contaminants seen the past couple years. The current sample flow is still high enough to prevent the skid from shutting down on Low Flow, but occlusion degrades the representative requirement of the sampling system for particulates (does not degrade representative sampling for Noble Gases or Tritium). Work to clean the sample line per the PM must be moved up in the schedule. <I> **** Actions Taken **** Contacted Shift Manager, System Engineer, Chemistry Supervision, and Maintenance <N> **** Equipment Description **** Sample nozzles are in TEA duct on rad waste building roof. | 02-00-TEA-SR-26
386259 | CR | 20181030 |  | 3 | Unexpected start of SEA-FN-5 during clearance temp lift | N | N |  | N | NO | <D> **** Detailed Description **** During performance of a temporary clearance lift (2018-072) for D-SEA-FN-5-001, the supply breaker was restored to the ON position per the temporary lift and SEA-FN-5 started unexpectedly. The operator heard a significant abnormal noise and re-opened the breaker to prevent any equipment damage. Operations and craft supervision were notified and the temporary lift was restored. Initial investigation showed that a rope tied to an FME plate got caught in the motor which caused the abnormal noise. Neither the craft nor operations expected the fan to start at this point as it was going to be started via work order instructions. There are start/stop buttons for this fan that stay engaged when pressed and the START button was still pressed in. The clearance had notes to the effect that these buttons were not tagged due to no procedure existing to start this fan and no labels existed for the buttons at time of clearance preparation. This fan has been out of service since 2014 and was originally investigated under WR 29115429 and L-SEA-FN-5-001. <I> CRS/SM notified and temporary lift was restored. | 02-00-SEA-FN-5
386260 | CR | 20181030 | CAQ | D | SEC-CCTV-14 Tamper | N | N |  | N | YES | <D> **** Detailed Description **** CAS received a high tamper alarm rate on CCTV 14. <I> **** Actions Taken **** Compensatory measures were posted. A walk down of the area was conducted. Electrical maintenance was notified. A CR/WR was generated. | 02-00-SEC-CCTV-14
386261 | CR | 20181030 | CAQ | C | Damaged oring found on CMS-SR-21 | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of WR 29143975 to perform leak check and repair leaks on CMS-SR-21. a damaged particulate filter o-ring was found. . The O-rings are replaced monthly by ISP-CMS/PRM-M402 and was last replaced on 10/25/19. . A check of the computer points for Drywell O2 (X395 and X456) show drywell o2 levels steday on the 25 and the on the 26th the day after, the O2 level started an increasing trend. the Orings used to be lubricated and are no longer lubricated because oils from the lubrication would leach onto the filter paper and cause plugging. there are sharpedges that with out lubrication the o-ring has the potential to be damaged on installation. It appears from the computer point data that the o-ring failed the day after replacement. <I> **** Actions Taken **** Wrote CR to document. No WR is needed, the o-rings were replaced under WR 29143975. | 02-00-CMS-SR-21
386263 | CR | 20181030 |  | 4 | B17 Fire Alarm Strobes are not Synchronized | N | N |  | N | YES | <D> **** Detailed Description **** Fire alarm testing today in B17, the Wenatchee Building, discovered that the fire alarm strobe lights in the corridor are not synchronized. Synchronization of strobe devices in the same room or same field of view is required by the Fire Alarm Code. This is because the flash rates of high intensity strobe lights pose a potential risk of seizure to people with photosensitive epilepsy. The Siemens PAD3 Notification Appliance Extender controls the strobe light synchronization. A work request will be written to check out the PAD3 to ensure all of the dip switches are in correct position and the jumpers are set correctly. If necessary the PAD3 motherboard will be replaced. The fire alarm system in B17 is maintained by Plant electricians. <I> **** Actions Taken **** Completed the testing portion of PPM-15.2.22 with no further issues. Problem will be turned over to the FP Engineer and Maintenance to troubleshoot, repair or replace the PAD3 Note that this problem was discovered in 2017 and it was believe that a dip switch was out of place. The dip switch was restored, the PAD3 reset and PMT confirmed that the strobe synchronized. See WR 29139158. <N> **** Equipment Description **** Building 17 PAD3 Notification Appliance Extender
386264 | CR | 20181030 |  | 3 | (QA) Scaffold Not Tagged for Use |  |  |  | Y | NO | <D> **** Detailed Description **** Factual Basis: â€¢ PPM 10.2.53, Scaffolding, states, â€œINSPECT scaffold AND sign off Scaffold tag (log tag).â€ â€¢ Investigation found that the scaffold assembly, which is used by Mechanical Maintenance for draining fire hoses after testing, did not have a scaffold tag and was not listed in the Scaffold Log. No observations were made of the scaffold being used. Insights: â€¢ Subsequent observation on the following day found that the scaffold was tagged with a red â€œDo Not Useâ€ scaffold tag. The Mechanical Maintenance Component Manager stated that the scaffolders â€œred taggedâ€ it because they felt it could use some enhancements. â€¢ In addition to the lack of a tag, the auditor recommends that this arrangement be evaluated for whether it should be classified as a rigging structure since it uses a rope/pulley mechanism to lift and suspend fire hoses. (see photo in EDMS) <I> **** Actions Taken **** This issue was identified during the Materials Management Audit, AU-MM-18. Informed Quality and Maintenance Management, recommend assignment to Maintenance. Safety risk addressed with addition of "do Not Use" tag to scaffold. <N> Mechanical Component Manager stated this is an outside scaffolding and the tag probably blew away. They replaced tag and placed it into system so it won't be missed. Coaching was provided and no further action is needed..
386265 | CR | 20181030 |  | 3 | (QA) Gas Cylinders Not Firmly Secured at Warehouse |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Multiple examples were identified at Warehouse Building 73 where gas cylinders were not secured firmly as required by ISPM-2, Compressed Gases and Welding/Cutting. While the majority of bottles had a chain draped in front of them, the distance and/or height of the chain was such that it would not prevent the bottles from falling over. Factual Basis: â€¢ ISPM-2 states, â€œCylinders shall be stored in a well -ventilated area, and shall be stored in an upright position and be firmly secured with a single heavy rope, or nylon belt, or, preferably, chain or cable or metal strap.â€ â€¢ Observation identified Multiple examples were identified at Warehouse Building 73 where gas cylinders were not secured firmly (See photos in EDMS). While the majority of bottles had a chain draped in front of them, the distance and/or height of the chain was such that it would not prevent the bottles from falling over. Insights: â€¢ Warehouse personnel tightened the gas bottle chains to mitigate the safety risk. <I> **** Actions Taken **** This issue was identified during the Materials Management Audit, AU-MM-18. Informed Quality and SCS Management, recommend assignment to SCS. Warehouse personnel tightened the gas bottle chains to mitigate the safety risk
386266 | CR | 20181030 |  | 3 | wire diagram for FPC-LIS-2B needs update |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** while performing wo o2066474-01 step 4.14 says to generate AR if wire do not match the AED and to have them updated to match on EWD-98E-116 wire colors from E-IR-67 are correct white, orange to the condulet in the condulet at FPC-LIS-2B the white wire is spliced a black wire and the ogange wire is spliced to a green wire. in FPC-LIS-2B the wire colors on the contacts are as follows Term. #8 Orange to N.C Term. #9 purple Common Term. #10 Black to N.O the wires from the condulet, black wire to Term. #8 Orange to N .C then Green wire to Term. #9 Purple to common and spare white wire to Term. #10 Black to N.O <I> **** Actions Taken **** notified supervisor <N> **** Equipment Description **** R572 | 02-00-FPC-LIS-2B
386267 | CR | 20181031 |  | 4 | SEC-XD-6 | N | N |  | N | YES | <D> **** Detailed Description **** SEC-XD-6 is not functioning as designed. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Unit taken out of service, security notification made, CR/WR generated | 02-00-SEC-XD-6
386268 | CR | 20181031 |  | 4 | DWR B2 | N | N |  | N | YES | <D> **** Detailed Description **** The badge reader (DWR B2) at the Security Checkpoint is not functioning as designed. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Removed unit from service, security notification made, initiated IR-0035124 help ticket wth IS <N> **** Equipment Description **** Badge reader is located at post 21 security checkpoint.
386285 | CR | 20181031 |  | 3 | SWP-CSW-15 revision needed |  |  |  | N | NO | <D> **** Detailed Description **** Step 3.3.7 requires that the delegated custodian verify that hte induvidual requesting the PMDD is qualified to Qual group CSAI. However the diesignated custodian does not havve this qual group and neither do cyber security specialists. So I cannot by this procedure give PMDD to another custodian or the cyber securtity specialist if I am following this as writtern, this step needed to include qual groups CSAH and CSAA. <I> **** Actions Taken **** Wrote CR
386291 | CR | 20181031 |  | 4 | Operators observed not using handrail |  |  |  | N | NO | <D> **** Detailed Description **** There have been multiple observations of operators not using the handrail when ascending the outside stairs on the west side of Kootenai. For the most part, the operators have been responsive to the feedback but on occassion have given justification as to why they aren't using the safety measure. <I> **** Actions Taken **** Coached the individuals. Informed the AOMC.
386295 | CR | 20181031 |  | 3 | (QA) Multiple Transient Combustible Permits are expired |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Out of the fifteen Transient Combustible Permits (TCP) open on 10/30/18; five were expired. TCP # 18-0094 owned by Site Support Contractor (SSC) for the RW chiller project expired on 10/25/18 TCP # 18-0105 owned by SSC for the RW elevator project expired on 10/25/18 TCP # 18-0125 owned by Project Management for the RW elevator project expired on 10/25/18 TCP # 18-0131 owned by Mechanical Maintenance for general equipment storage on RW 507' expired on 10/18/18 TCP # 18-0142 owned by Reactor Maintenance for the Backup Transformer outage expired on 10/15/18 This procedure compliance issue exists with multiple groups. Refer to EDMS for additional details. Recommend assignment to Maintenance. This issue is considered a Deficiency identified during Quality SR-19-01 Continuous Monitoring Roll-Up Surveillance. <I> **** Actions Taken **** Discussed with the permit owners to take actions to close or extend the permits. Initiated this CR. <N> ***General Notes*** The Mechanical Maint. shop has corrected TCP# 18-0131 .
386302 | CR | 20181031 |  | 4 | Significant air leak coming from "D" service box on RX 606 | N | N |  | N | YES | <D> **** Detailed Description **** An air leak was heard while performing BADGER testing on the RX 606 coming from the "D" service box. SA-V-112/4 is closed and there is a sizable leak coming from the pipe nipple. <I> **** Actions Taken **** Verified EPN and "D" servcie box. This service box also has a leaking Condensate Valve in it. Per AED M739, the leaking condensate valve is COND-V-44D - see existing AR CR 379563 and AR CR 350322 with associated existing WR 29128782 / WO 02107591. WOT 02107591-01 for replacement of COND-V-44D is currently RETURNED status as access limitations with the service box walls apparently will not allow replacement of the valve as had been planned. | 02-00-COND-V-44D,02-00-SA-V-112/4
386303 | CR | 20181031 |  | 4 | Need to evaluate wifi strength classroom 225 Kootenai bldg |  |  |  | N | NO | <D> **** Detailed Description **** Need to evaluate wifi strength classroom 225 Kootenai bldg. Extremely slow accessing intranet based applications by the multiple computer that the students use during class/ exams <I> **** Actions Taken **** Informed NLO Continuing Training <N> **** Equipment Description **** Consider adding wireless router to classroom 225 Kootenai
386304 | CR | 20181031 | CAQ | C | Incorrect Due Dates identified in SMS 379895 for RV testing | Y | N |  | N | NO | <D> **** Detailed Description **** The due dates identified in AR SMS 379895 for SW-RV-001A (PMID 12302) and SW-RV-001B (PMID 12303) in accordance with the IST Program, were incorrectly identified. The incorrectly identified due dates for both valves places their next test at 12/29/20 (6 year frequency from the last test on 12/29/14). ASME OM Code Mandatory Appendix I require that at least 20% of the valves from each valve group be tested within any 48-month period. A correct due date of 12/30/18 for either one of these two valves will ensure the 48-month criterion for this valve group is met. 6 months grace is allowed for these PMs, making the late date 7/1/19. The next opportunity to test SW-RV-001A is during the SW-A window scheduled for the week of Jan 7, 2019. Otherwise, either SW-RV-001A or SW-RV-001B will need to be tested during R24 in order to meet the late date. Per the Code, if a valve fails testing, the other valve in the group will need to be tested. In the case of these specific valves, rotational spares are installed and the removed ones are bench tested and prepared as rotational spares for next time. Whichever valve is not tested next should have its due date set such that each valve in this group is independently tested every 6 years, but still tested within 48- months of the other valve. This staggered testing will ensure the requirements of the ASME OM Code and IST Program are met. This is an administrative issue only and has no impact on operability of these valves. Recommend C to AR-PPROG. <I> **** Actions Taken **** Discussed with supervisor. Prepared new SMS. No dates were exceeded. There is no DNC. | 02-00-SW-RV-001A,02-00-SW-RV-001B
386308 | CR | 20181031 |  | 4 | Testing GAP annunciator does not sound horn. | N | N |  | N | YES | <D> **** Detailed Description **** When testing the annunciators at the GAP pannel the horn did not sound as expected. <I> **** Actions Taken **** Informed MCR & initiated AR. | 02-00-E-CP-GEN/AUX
386310 | CR | 20181031 |  | 3 | Potential Trend: Demineralized Water Trailer Performance | N | N |  | N | NO | <D> **** Detailed Description **** Since September 2018, there have been 6 condition reports initiated regarding the demineralized water trailer performance. This condition report is being initiated to validate the potential trend by completing a Trend Validation Worksheet per TM-01, Trending Manual. <I> **** Actions Taken **** Recommend NCAQ Severity 3 to AR-CHEM.
386313 | CR | 20181031 |  | 4 | RFW-P-1B lagging has oil on it | N | N |  | N | YES | <D> **** Detailed Description **** RFW-P-1A lagging was noted to have oil on it. No active leaks were notes. <I> **** Actions Taken **** Informed Ops 3 and the Shift Manager. Contacted the Fire Marshall to determine if the lagging is a fire hazard. . <N> RFW-P-1B has the lagging with oil on it. | 02-00-RFW-P-1A
386314 | CR | 20181031 |  | 3 | 4.TGHV.1B has a typographical error. |  |  |  | N | NO | <D> **** Detailed Description **** 4.TGHV.1B page 9 for drop 1-5 is for TOA-FL-1B, but it recommends securing TOA-HV-1A for filter replacement. This should recommend securing TOA-FL-1B. Please investigate and correct. <I> **** Actions Taken **** Wrote this procedure change AR.
386315 | CR | 20181031 |  | 3 | Procedure enhancement to PPM 10.2.10 |  |  |  | N | NO | <D> **** Detailed Description **** Attachments 9.7 needs to be reviewed for inclusion into PPM 10.2.10. From reading the 2017 National Electrical Code handbook it is my understanding that this table pertains to wire that is going to be installed under a terminal screw not wire that has a lug terminated on it. That is why the wire size is included in the table. <I> **** Actions Taken **** Generated this CR to document the issue. <N> ***General Notes*** An assignment has been made within the maint procedure revision data base. No further action is required. A link has been uploaded into the EDMS of this AR. No actions required. Per Informative Annex I of the 2017 NEC, torque tables provided in the NFPA are for informative purposes only and are not a requirement of the NFPA. They are provided in the absence of connector or manufacturers sp ecifications
386316 | CR | 20181031 |  | 3 | (QA) FIN Team backlog of minor work requests is excessive |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Fix It Now (FIN) Team backlog of minor work requests is excessive in total number and age. Currently over 700 work requests (WR) are sitting on the FIN Team backlog. Over one hundred are greater than one year old and four were written in 2015. Delaying the repair of equipment can adversely impact the plant and cause additional burden for personnel to work around the degraded or failed equipment. Refer to details in EDMS This problem is considered a Deficiency identified during Quality SR-18-16 FIN Effectiveness Surveillance Recommend assignment to Maintenance FIN Team <I> **** Actions Taken **** Discussed with the FIN Team Manager and Maintenance Manager.
386317 | CR | 20181031 |  | 3 | (QA) Management of minor work requests is deficient |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Management of minor work requests is deficient. There are currently over 1800 work requests (WR) open. Over 50 work requests are greater than 5 years old with one initiated in 2008. The number of WRs has increased over the last year by approximately 15% from 1541 to 1810. The average age of the WRs has also increased by approximately 17% over the last year from 415 to 501. The corrective action process assumes that when a work request is written with a CR, the work management process will usually correct the condition. Some of these problems are not being corrected in a timely manner. This problem is considered a Deficiency identified during Quality SR-18-16 FIN Effectiveness Surveillance. Recommend assignment to Maintenance <I> **** Actions Taken **** Discussed with the Maintenance Manger and FIN Team Manager.
386318 | CR | 20181031 |  | 3 | Operation of PWC-P-107 for Hanford sampling doesn't work |  |  |  | N | NO | <D> **** Detailed Description **** Performed Hanford sample. Procedure has not been updated in years. Does not work as written. <I> **** Actions Taken **** Marked steps not required. Copy available in EDMS. | 02-00-PWC-P-107
386319 | CR | 20181031 |  | 4 | WOA-AH-9 ductwork is damaged | N | N |  | N | YES | <D> **** Detailed Description **** WOA-AH-9 ductwork is damaged. There is a ~7â€ crack forming along the side of the unit where the mounting bracket for WOA-M-FN/9-is installed. The damaged ductwork creates inadequate support for the motor which is contributing to excessive vibration in the fan/motor/pulley. Reference CRâ€™s 386172. Recommend repairing damaged ductwork and replacing belt prior to complete failure. Issue discovered during system walk-down. This fan is Critical Class N and Not Safety Related. As described in FSAR Section 9.4; this air handling unit provides ventilation and cooling to the Counting Room. This condition does not render inoperable equipment that is a Technical Specification Safety Related System, Structure, or Component (SSC). This fan remains in service and functional. <I> **** Actions Taken **** Informed MCR. Generated WR. The fan provides supply air and is not subject to ODCM 6.2.2.5, Ventilation Exhaust Treatment System. | 02-00-WOA-AH-9
386320 | CR | 20181031 |  | 4 | Air is leaking from lower access panel on WOA-AH-5 | N | N |  | N | YES | <D> **** Detailed Description **** The lower access panel to WOA-AH-5 is not tightly secured causing an air leak. Air can be felt blowing past panel door at a distance of ~6â€™. The panel door is typically flush with the side of the air handler. It is currently extended ~1â€ past the surface. See photos attached to EDMS of this CR. Please investigate cause of issue and repair as necessary. Issue discovered during system walk-down. This fan is Critical R and Not Safety Related. As described in FSAR Section 9.4; this air handling unit provides ventilation and cooling to the Hot Instrument Shop. This condition does not render inoperable equipment that is a Technical Specification Safety Related System, Structure, or Component (SSC). This fan remains in service and functional. <I> **** Actions Taken **** Informed MCR. Initiated WR. Uploaded pictures to EDMS of this CR. | 02-00-WOA-AH-5
386321 | CR | 20181031 | CAQ | C | Loss of supervised FP detection circuit. | N | Y |  | N | YES | <D> **** Detailed Description **** Fire Suppression PreAction zone 66B and 66D will not enter into trouble condition under current design when a smoke detector is removed from itâ€™s base for the applicable zones also identified by AR-CR 00374802. On 10-31-18, utilizing WO 02122279 and WR 29145402, multiple troubleshooting attempts were successfully made to place zone 66B and 66D into a trouble configuration. Both ZU-35DS modules for the applicable zones, located in FP-CP-FSP10, were taken through multiple evolutions to demonstrate the ZU-35DS module are functioning as designed. Both ZU-35DS modules functioned as designed. It appears placement of the capacitor on the ZU-35DS module affects functionality for the modules ability to supervise the detection circuit. It appears the capacitor is not placed in the correct location in accordance with vendor (Siemens) recommended wiring for the module. Reference EC 13537, Fire Detection Upgrade Project, and EWD-62E-016. Detectors are locked in place upon installation (twist in place) and unlikely to fall from base. Supervisory function is primarily to identify when detector is not in the detector base (reinstalled correctly after maintenance and/or dislodged by inadvertent contact). Troubleshooting verified that detectors in place in their bases will perform their fire alarm function and provide a fire alarm signal in the event of a fire. . Incorrect placement of the capacitor on the PreAction 66B and 66D zones does not prevent the zones from sending the applicable fire alarm signal in the event of a fire. This deficient condition would not prevent the zones from performing their design function. To be clear, the improperly placed capacitors are incorrectly placed, per design, in accordance with EWD -62E-016 and EC 13537. This condition is a condition where the design of the circuit is incorrect, not the field installation. . PreAction zone 66B detection zone is located in the RadWaste 525â€™ EL. Cable Chase. . PreAction zone 66D is located in the RadWaste 441â€™ El. Corridor (corridor between RadWaste and reactor building directly outside old laundry room). <I> **** Actions Taken **** Initiated CR, informed SM of condition. | 02-00-FP-CP-FSP10
386322 | CR | 20181031 | CAQ | D | Failing Fire Detection Circuit Capacitor | N | Y |  | N | YES | <D> **** Detailed Description **** While performing WO 02122279, troubleshooting of FSP-10, the CP-35 panel located inside FP-CP-FSP10 was reset numerous times throughout the day to support the troubleshooting. Towards the end of the day, Pre-Action zone 66C would intermittently enter into a trouble condition and then clear after approximately 30-40 seconds. This indicates the capacitor for the Pre-Action 66C zone is likely in the process of failing. FP-CP-FSP10 did not have any locked in trouble indications upon completion of WO 12122279. Pre-Action zone 66C capacitor should be replaced. A locked in trouble indication on FP-CP-FSP10 zone C would not prevent the zone from sending a fire alarm in the event of a fire in the 66C zone (437â€™ RadWaste North Corridor). The capacitor is to monitor the circuit only and will not prevent the panel from sending fire alarms as required. <I> **** Actions Taken **** Initiated CR, contacted SM. | 02-00-FP-CP-FSP10
386323 | CR | 20181101 |  | 4 | Seal Oil room lighting needs to be replaced | N | N |  | N | NO | <D> **** Detailed Description **** Half of the lighting in the seal oil room is out and requires bulbs changed out. <I> **** Actions Taken **** Initiated AR/WR to correct. Notified CRS. <N> **** Equipment Description **** Seal Oil Skid room TB 441
386366 | CR | 20181101 |  | 3 | Security exceeded dose budget for Oct/18 |  |  |  | N | NO | <D> **** Detailed Description **** Security department exceeded our dose budget of 14 MR by receiving 16 MR for the month of October 2018. This is mainly due to NRC evaluated FOF drills and associated training prior to inspection. Good ALARA techniques were practiced during the month. <I> **** Actions Taken **** CR generated
386368 | CR | 20181101 |  | 3 | Level 3 IPS Disk usage |  |  |  | N | YES | <D> **** Detailed Description **** During quarterly Walkdown and Password change it was observed that there was unusually high disk usage on NET3-COMP-IPS1 and NET3-COMP-IPS2. These are Cyber security devices that monitor the level 3 network traffic. If the disk space were to become completely used up, the device would lockup and stop passing traffic. These 2 devices are redundant, so it would take both failing to have an impact on the level 3 network. . This is not a reportable condition. There is currently no impact on the network or to Operations. Recommend this as a 3 to AR-COMPENG. <I> **** Actions Taken **** Generate CR and opened support case with the vendor | 02-00-NET3-COMP-IPS1,02-00-NET3-COMP-IPS2
386369 | CR | 20181101 |  | 3 | NET3 KVM web certificates expired |  |  |  | N | YES | <D> **** Detailed Description **** NET3 KVM web certificates have expired. Java security features prevent Java applications from running when certificates are expired. Due to this, the KVMs do not currently function for their intended purpose. The KVMs are used by Computer Engineering as a tool for managing the Level 3 network. . These devices do not perform a Cyber function. This does not impact Operations. This is not a reportable condition. Recommend as a 3 to AR-COMPENG. <I> **** Actions Taken **** Generated CR | 02-00-NET3-KVM-SW/1,02-00-NET3-KVM-SW/2,02-00-NET3-KVM-SW/3,02-00-NET3-KVM-SW/4
386371 | CR | 20181101 |  | 4 | Overhead Lights Out Above OG-FU-11B | N | N |  | N | NO | <D> **** Detailed Description **** The overhead lights in the offgas pre-filter 11B vestibule (RW 452' elevation) are almost completely out. The lights are flickering and visibility in the room is minimal. <I> non-essential lighting <N> **** Equipment Description **** Overhead lighting in the OF-FU-11B cubicle on the Radwaste 452 elevation. | 02-00-OG-FU-11B,02-00-W-BLDG-MISC
386372 | CR | 20181101 |  | 4 | Combustibles identified under egress stairs |  |  |  | N | NO | <D> **** Detailed Description **** Several combustible items (snow fencing, tape rolls, tape scraps, and cable ties) were found on a cart staged under the egress stairs on the RW 452 elevation. All items relocated to an appropriate storage location nearby. This is generated for trending purposes only. | 02-00-W-BLDG-MISC
386374 | CR | 20181101 |  |  | Bottled Gas Plant delivery Process Concerns |  |  |  | N | NO | <D> assignment to either Supply Chain or Industrial safety for find a safer more efficient process. The team should include Industrial safety, Supply Chain, Health Physics and safer more efficient process that we may identify. There are no scheduled deliveries to the RCA of this type until next Wednesday 11/07/2018. Supervisor will be present to <N> CR Canceled at the request of Initiator. CR 00386389 written to compliment this.
386375 | CR | 20181101 |  | 4 | TMU-V-7B mechanical condition in question. | N | N |  | N | YES | <D> **** Detailed Description **** While performing WO 02093778 mechanics experienced extreme vibrations, noise and pit level increases when manually opening TMU-V-19B. One of the mechanics has performed this twice before, once in March of 2014 and again in November of 2015. He does not recall what he saw yesterday, 10/31/18, and what he saw would have been memorable. Prior to performing this work order electricians investigated why TMU-V-7B would not go full open per WR 29144687 and ultimately were able to get the valve to stroke the full length as measured by the valve stem travel compared to valve engineerâ€™s data. If the stem travel is correct then the condition of the actual gate is in question as the indications the mechanics saw were that the sluice gate was not full shut. Recommend using an underwater camera on the pit side of the sluice gates, both TMU-V-7A and 7B for examining the condition of both sluice gates. <I> **** Actions Taken **** Discussed with supervisors and CRS. Sent the work order back to planning. Wrote this AR/WR. <N> **** Equipment Description **** TMU pumphouse | 02-00-TMU-V-19B,02-00-TMU-V-7A,02-00-TMU-V-7B
386377 | CR | 20181101 |  | 3 | Work order 02093778 returned for added work steps |  |  |  | N | YES | <D> **** Detailed Description **** Return work order 02093778 back to planning to add SOP-TMU-OPS to work steps to align TMU system prior to cycling TMU-V-19B. See AR 386375 for more info on waht took place when we opened TMU-V-19B. <I> **** Actions Taken **** 02093778 at returned status Make sure we update model work order. <N> **** Equipment Description **** TMU | 02-00-TMU-V-19B
386378 | CR | 20181101 |  | 4 | Temp acid trailer |  |  |  | N | NO | <D> **** Detailed Description **** Temp acid trailer needs some addtional guards (covers) established for some exposed sharp edges of trailer at back edge adjacent to the trailer tail lights. <I> **** Actions Taken **** Generated CR and will contact SSS to put up some Tape for now with addtional barrier/guard to follow. Attached picture with Arrows where areas need addressed. <N> **** Equipment Description **** Temp acid trailer by CWPH.
386382 | CR | 20181101 | CAQ | D | Degraded CW-PHITS-1 data | N | Y |  | N | YES | <D> **** Detailed Description **** Data from CW-PHITS-1 appears to be degrading. Data from eDNA point F141 shows multiple occasions where signal has rapidly dropped for a short time (LT 1 second) before returning to the expected value. Additionally, CW-PHITS-1 signal has recently exhibited unexpected step changes in pH, approximately 0.1 pH in magnitude (see EDMS). The instantaneous changes in pH indicate an error with CW -PHITS-1 signal. These events are similar to those previously identified in CR 00376726 and CR 00385978. <N> CW-PHITS-1 provides input to the sulfuric acid pump controller CW-PHIC-1, and CW-PHR-1. If CW-PHR-1 becomes inoperable or is known to be in error, blowdown grab samples per PPM 12.2.9 are necessary and every reasonable attempt to return CW-PHR-1 to service should be made. Verify the method for monitoring pH is noted on the Outside Tour Log sheets <R> E&RP Notes: F141 data is used on the monthly NPDES discharge monitoring report. The NPDES permit WA002515-1 section S2 requires continuous monitoring of the CW blowdown pH where â€œContinuous means uninterrupted except for brief lengths of time for calibration, power failure, or unanticipated equipment repair or maintenanceâ€ and â€œThe Permittee must report the instantaneous maximum and minimum pH monthly. Do not average pH values.â€ | 02-00-CW-PHITS-1
386383 | CR | 20181101 |  | 4 | Slip Resistant Strips Degraded or Absent |  |  |  | N | NO | <D> The RB NW and SE airlock door ramps need the slip resistant surface enhanced. The foot ramp going over instrument tubing on the RB 572' N near SBGT 1B has no slip resistant surface enhancement. RB 548' N foot ramp slip resistance surface is worn. Also, the four concrete berm ramps on the RB 522' should be considered to have some type of slip resistance surface enhancement. See photos in EDMS. <I> Took photos of deficiencies and generated a work request. WR number? <N> RB 441 NW and SE airlock door ramps RB 572 N instrument tubing foot ramp near SBGT 1B RB 548 N foot ramp RB 522 four concrete berm ramps located in each corner Need WR(s)? | 02-00-R-BLDG-MISC
386384 | CR | 20181101 |  | 4 | WCH-V-5 has packing leak | N | N |  | N | YES | <D> **** Detailed Description **** WCH-V-5 has what appears to be a packing leak at a rate of 40 drops per minute. See photos attached to the EDMS of this CR. Water has puddled near WCH-CR-51B. Please investigate and repair. Issue discovered during system walk-down. This valve is Critical R and Not Safety Related. This condition does not render inoperable equipment that is a Technical Specification Safety Related System, Structure, or Component (SSC). This valve remains in service and functional. <I> **** Actions Taken **** Initiated WR. | 02-00-WCH-V-5
386386 | CR | 20181101 |  | 4 | minor oil leak found during PMT (RFT-LOC-1B) | N | N |  | N | YES | <D> **** Detailed Description **** During WO # 02124822-05 it was discovered to have a 2 bolt flange gasket leak at one of the connections removed for the overhaul. This has been an issue in the past and should be addressed, we should reface the flanges to have full contact of the mating surfaces. <I> **** Actions Taken **** Had the operator shut down the unit, notified my supervisor and the SSS Initiated this CR and WR <N> **** Equipment Description **** RFT-LOC-1B | 02-00-RFT-LOC-1B
386387 | CR | 20181101 | CAQ | D | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0067789 Astro-Med Input Module- model UNIV-6 found OOT. EFIN Eval: The M&TE used card was reviewed and was found to have no impact to the operability of the plant. No issues were found and No Further Evaluation is required. Usages #1 & #2 were for collecting information used in Troubleshooting and Trending but are not used for operability or functionality purposes. Sent to Vendor for Repair. DEF #6759A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
386388 | CR | 20181101 | CAQ | D | Incomplete WORK ORDER Submitted to Records Control |  |  |  | N | NO | <D> **** Detailed Description **** WORK ORDER 02115890-12 Replace Obsolete Analog Seismic Monitoring was received in Records Control for processing with the QC Inspection Hold still in effect in Asset Suite. The WORK ORDER nees to have the QC inspection completed and the Hold removed from Asset Suite. <I> **** Actions Taken **** WORK ORDER was pulled from processing and sent to Records Coordinator Org Code 8400 <N> Record was on hold and was not released before submitting. WBL was coached on recognizing "on-hold"priorities - no additional actions required. notes entered at request of Reg AFfairs Administrator
386389 | CR | 20181101 |  | 3 | Potential Safety Concern delivering bottled gases RCA441 |  |  |  | N | NO | <D> **** Detailed Description **** Warehouse Craft Personnel have identified a potential safety concern regarding the delivery of bottled Gases to the 487" Chemistry Lab and HP delivery locations. The concern specifically is with the method of entry and exit for delivery to and returns from the RCA 441. The current delivery entry is Main RCA 441 personnel entry, the congested area and volume of gas delivered and removed creates a pinch point for personnel. Also when moving bottles between the RCA rope barrier bottles have no storage racks to secure them while transferring additional bottles. Recommend assignment to either Supply Chain or Industrial safety for the purpose of assembling a team to address the concerns. The team should include Industrial safety, Supply Chain, Health Physics and Maintenance. <I> **** Actions Taken **** Initiated CR. There is no immediate risk to the station or personnel however a more in depth review of the process is warranted. Positive behaviors by Craft personnel displaying a healthy questioning attitude towards safety and expanding the team for resolution . There are no scheduled deliveries to the RCA of this type until next Wednesday 11/07/2018. The Warehouse Supervisor will be present to support evaluation for possible actions.
386390 | CR | 20181101 |  | 3 | Corporate Network Distribution Switch DST-PEC 1 failed | N | N |  | N | YES | <D> **** Detailed Description **** DST-PEC chassis 1 Supervisor module failed causing full chassiis failure, and network conectivity loss for attached corporate network switches downstream. <I> **** Actions Taken **** Migrated network switch links from DST-PEC chassis 1 to DST-PEC chassis 2, the second chassis had enough unused ports to restore connectivity to affected network switches downstream. Cisco TAC case #685548946 has been opened for troubleshooting and hardware replacement. <N> **** Equipment Description **** DST-PEC-1
386391 | CR | 20181101 |  | 3 | Right Cat ID ordered, wrong part received |  |  |  | N | NO | <D> **** Detailed Description **** WO 02121014 was returned as the part received is for liquid flow with a GPM scale. The part is supposed to indicate in SCFH (air flow). Cat ID 0000038026 was ordered to be installed as SLC-FIC-4 per WO 02131014. WO 02131014 is RETURNED pending a proper replacement part. <I> **** Actions Taken **** Initiated this CR. Placing Procurement Engineering Hold on WO 02131014. <N> **** Equipment Description **** This issue is for a replacement part. | 02-00-SLC-FIC-4
386392 | CR | 20181101 | CAQ | C | Need IMDS for FP-PRV-CO2/915 |  |  |  | N | NO | <D> **** Detailed Description **** Need IMDS for calibration of FP-PRV-CO22/915 per WO 02116062. <I> **** Actions Taken **** Initiated CR and placed engineering hold on 02116062. <N> **** Equipment Description **** Missing documentation. Not and EPN issue. FP-PRV-CO2/915 | 02-00-FP-PRV-CO2/915
386393 | CR | 20181101 |  | 3 | Failure during LORQ Biennial Requal Written Exam |  |  |  | N | NO | <C> Per MRT feedback received on 11/6/2018 - this was designated as NCAQ. The roll up CR to be initiated once the exam cycle is completed will be prioritized as CAQ. This will be addressed by the ACE tracked under AR 387428. No further action is required <D> **** Detailed Description **** One failure occurred during the biennial written exam administered on 11/1/18. Remediation will be IAW TDI-02. <I> **** Actions Taken **** I: De-certified individuals in PQD. Notified Operations and Operations Training Management. A: Recommend Severity Level 3. Additional detail withheld due to exam security requirements. R: Remediation IAW TDI-02.
386394 | CR | 20181101 |  | 3 | Procedure Enhancement to SOP-HWC/HSSF-OPS |  |  |  | N | NO | <D> **** Detailed Description **** Changed the Sections 5.1, 5.2, and 5.3. To change the way that the tube trailers are installed and vented and the way the tube trailers are removed and vented off. The current procedure vents piping that isn't purged upon new trailer installation. Also Added section 5.9 for Hydrogen Trailer #2 Removal and Installation. See EDMS for suggested changes. <I> **** Actions Taken **** Informed Supervision, Contacted System Engineering to validate new procedure change.
386396 | CR | 20181101 | CAQ | C | Maintenance Rule Structural Inspection of the SW spray ponds | Y | Y |  | N | NO | <D> **** Detailed Description **** The intent of this CR is to document the occurrence of the (baseline) Maintenance Rule Structural Inspection (MRSI) of the submerged portion of the SW spray ponds (under WOT 2117112) in late September 2018. This visual inspection is in support of License Renewal commitment #53 needed for CGSâ€™s renewal application. Per Commitment #53, CGS is committed to performing a baseline inspection of the ponds (including the submerged portions) plus a minimum of one additional prior to entering the period of extended operation (PEO). The non-submerged portion was previously covered in June 2018 under WOT 02085605-01 for the 2018 Non-Outage Maintenance Rule Structural Inspection (PMID 22156). . Performance of the two pond inspections meets the intent of the baseline inspection. An additional inspection will be necessary before PEO. Based on the exposure conditions, crack profiles, and concrete mix design, the incipient results of this walkdown indicate that the ponds are structurally able to meet their design functions as there were no visible signs of deteriorations that require immediate attention. The acceptance criteria for the inspections were in accordance with ACI 349.3R-96 (as committed by CGS) and inspection by the divers was witnessed by a qualified Civil Engineer (that meets the requirements of Chapter 7 of ACI 349.3R, Qualification Evaluation Teams). . For each pool, the SE corner (and floors), and the West and North wall (and their respective floors) at midspan were inspected (see EDMS for pictorial depiction). The floor inspections included sections of expansion joints. . The concrete and steel substrates (reinforcements) in both ponds were overall in acceptable condition. There were no exposed rebars, aggressive (chemical or biological attack), significant material loss, no leakage, fatigue, deflection or visible defects that require immediate actions. However, few surface defects were noted on the walls. Those defects included scaling, spalling and concrete cracks for both ponds. The vast majority of those defects met tier 1 or 2 of ACI 349.3R and a small number met tier 3. For those cracks that meet tier one, no action is required, for those meeting tier 2, trending is generally suggested. Tier 3 requires further technical evaluation and potential repair to restore of the concrete back to its original design and minimize/prevent further deterioration. As such, assignment #1 will generate a summary of the entire inspection using attachment 8.2 of ENG-SMP-01, Maintenance Rule Structural Inspections. Assignment #2 will evaluate the defects that exceeded tier 3 acceptance criteria of ACI 349.3R. <I> **** Actions Taken **** Talked to Design Authority and Immediate Supervisor to discuss results of visulal inspection and initiated CR. <N> **** Equipment Description **** SWPONDA - SW POND A SWPONDB - SW POND B
386401 | CR | 20181101 | CAQ | C | Common Cause for Drywell Oxygen increases |  |  |  | N | NO | <D> **** Detailed Description **** Since March this year, there have been seven CRs related to Drywell oxygen concentration going up. Recommend an evaluation of the referenced CRs to determine if there is a common cause and create appropriate corrective actions to reduce the occurrence of oxygen in-leakage into the Drywell. Assign to group AR-SEEIC. <I> **** Actions Taken **** Discussed with supervision See individual CRS for IOD information.
386402 | CR | 20181101 | CAQ | C | New RHR B Mtr outside of acceptance criteria for resistance |  |  |  | N | NO | <C> Names removed from I Notes CR; changed to reflect titles. <D> **** Detailed Description **** Performing W.O.# 02117218-59 Motor Inspection and insulation testing for the new RHR B motor staged in the GSB machineshop step 4.6 of the work order instructions performs a low resistance test of the windings phase to phase. The acceptance criteria for this test as defined per EC-14635 is 0.334 ohms +/- 0.069 ohms @ 77 deg. F. Readings are as follows: T1-T2: 0.4707 ohms @ 74.2 deg. F T1-T3: 0.4735 ohms @ 74.2 deg. F T2-T3: 0.4688 ohms @ 74.2 deg. F. All other steps of this work order completed sat. <I> **** Actions Taken **** Supervisors from maintenance informed. Engineering informed. Initiated this CR. Documented CR in the Work Order. <N> **** Equipment Description **** New RHR B motor staged in the GSB Machine shop WP 02117218 and EC 14635 are for/associated with replacement of RHR-M-P/2A (RHR A motor, not RHR B motor).
386403 | CR | 20181101 |  | 3 | Chemistry Technician Initial Training Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** A chemistry technician failed an exam in the initial training program. Exam failure does not impact the technicians qualifications to perform work. <I> **** Actions Taken **** Notified training supervision and submitted CR.
386404 | CR | 20181101 |  | 3 | Chemistry Technician Initial Training Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** A chemistry technician failed an exam in the initial training program. Exam failure does not impact the technicians qualifications to perform work. <I> **** Actions Taken **** Notified training supervision and submitted this CR.
386405 | CR | 20181101 |  | 3 | Wrong revision of procedure submitted for processing. |  |  |  | N | NO | <D> **** Detailed Description **** Wrong Revision of ENG-PSE-01 submitted to Document Control for Implementation <I> **** Actions Taken **** Returned to Engineering via Needs More Information button in APPW.
386406 | CR | 20181101 |  | 4 | MT-ELEV-2 Stuck on the 606' | N | N |  | N | YES | <D> **** Detailed Description **** MY-ELEV-2 is stuck on the 606 elevation and will not move. <I> **** Actions Taken **** Initiated CR & WR, notified MCR | 02-00-MT-ELEV-2
386407 | CR | 20181101 |  | 3 | Update instructions for all upcoming LIS-XX replacements |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of work order 02066474-01 several issues were identified that created work delays and instrucitions were amended during perfomrance of the work order. Going forward a look ahead should be performed to amend Instructions for similar work in the weeks to come; amending work instructions will reduce delay time. <I> **** Actions Taken **** Planning contacted, CR initiated, contacted WWM.
386409 | CR | 20181101 |  | 3 | Wall loss in CW buried pipe | N | N |  | N | NO | <D> **** Detailed Description **** During the inspection of 18â€ CW(5)-1 line per WO 02094048 outside of SWPH-A, the min wall thickness measured by UT was 0.238â€. The wall loss is calculated to be 0.137â€ (37% wall loss). As per ENG-SPS-07, a CR needs to be initiated whenever the measured min wall thickness is below 87.5% of the nominal wall thickness of the pipe (0.375â€). As per EC 15440, a similar line (18" CBD(1)-1) has the same material and the same design pressure and temperature with a design tmin of 0.1â€. This means that the corrosion rate is 4.5 mpy (mills per year). Using this rate (assuming linear trend) this line will get to its design minimum thickness in 30 years (2048). As shown, there is more than twice the necessary thickness. Recommend action to Buried Piping engineer in Cope Programs <I> **** Actions Taken **** Discussed the line with Design engineering and initiated this CR Parent AR closing comments: The next inspection day is calculated to be in 2027 (see task 01 and WO 02094048 for more information). The software program used "MAPPro" is used to track the re-inspection of the piping in 2027. No further actions are required. | 02-00-A-BLDG-MISC,02-00-CW-PIPE-MISC
386410 | CR | 20181101 | CAQ | C | SQA documentation sequencing & revision tracking issues |  |  |  | N | NO | <C> Per feedback recieved from MRT on Tuesday 11/6/2018, this CR was reprioritzed as a CAQ / C as the SQA process is a quality process. <D> **** Detailed Description **** During processing of SQA documentation associated with various ECs, it was identified that a large amount of SQA documents were not processed with the proper revision numbers or in the correct sequence. This was due to the complexity of the Engineering Changes often modifying the same documents in parallel and being implemented at the same time. To aid in close out, the documents were often updated with revision numbers that may not have reflected the correct sequence complicating document processing later. Engineering and Document Control are in the process of correcting the sequence of these documents. This CR is to document the issues associated with these SQA documents and to document the resolution. The title page of these files will have the revision numbers corrected, with this CR number annotated. The rest of the document will not have revision numbers corrected. Associated ECs xref'd <I> **** Actions Taken **** n/a
386411 | CR | 20181101 | CAQ | D | The Emergency DC Lighting in Remote Shutdown Room is not lit | N | Y |  | N | YES | <D> **** Detailed Description **** Both Division 1 and both Division 2 emergency DC lighting fixtures in the Remote Shutdown Room and the Division 2 emergency DC lighting fixture just outside of the Remote Shutdown Room are not lit. Per Paragraph 9.5.3.2.3 of the FSAR, the emergency DC lighting in the Remote Shutdown Room and the access route from the Main Control Room to the Remote Shutdown Room are to be continuously lit. Suspect that the bulbs are burned out and will need to be replaced. The emergency DC lighting for both divisions in Stair No. 7 are lit and they are fed from the same disconnects (E -DISC-S11D1 and E-DISC-S12D1) as the unlit fixtures in and just outside of the Remote Shutdown Room. <I> **** Actions Taken **** Informed the CRS and created WRs to have the bulbs replaced. <N> **** Equipment Description **** E-DISC-S11D1 E-DISC-S12D1 | 02-00-W-BLDG-MISC
386420 | CR | 20181102 |  | 3 | Additional issues for EC CC 16858 (TMU-P-1A replacement) | N | N |  | N | YES | <D> **** Detailed Description **** 1) EC CC 16858 did not address the weight change associated with recent replacement of TMU-P-1A (e.g., with discussion in the design change or via an update (EC CMR or revision) for calculation AED CAL 6.20.04-SVI-1). Per the DDC for CVI 39-00,11 in the EC CC 16858 package, the total weight of the replacement pump-motor assembly is 20,900 lbs (12,500 lbs for the pump, 1,000 lbs for the pump foundation plate, and 7,400 lbs for the original pump motor). Per the DDC for CVI DWG 39-00,2 in the EC CC 16858 package, the total weight of the original pump-motor assembly was 18,900 lbs (11,500 lbs for the original pump plus 7,400 lbs for the original pump motor). This weight change should have been addressed by EC CC 16858. 2) CVI DWG 39-00,11 (DDC in EC CC 16858) for the replacement pump at TMU-P-1A) does not include maximum foundation bolt loading information like that included on CVI DWG 39-00,2 for the original TMU pump-motor assemblies. The maximum foundation bolt loads will change as a result of TMU-P-1A replacement per EC CC 16858. 3) CVI DWG 39-00,11 (DDC in EC CC 16858) for the replacement pump at TMU-P-1A) includes an inaccurate detail for the pump-to-motor flange mounting holes. Contrary to the drawing, the mounting holes are only 7.5 degrees rotated (not 22.5 degrees rotated). 7.5 degrees rotated is required to match with the associated mounting holes in the original TMU pump motors (CVI DWG 39-00,3). Additionally, 7.5 degrees rotated is what exists in the field for the installed replacement pump at TMU-P-1A (photo attached to the EDMS of this AR CR 386420). . In-progress EC CMR 17044 against AED CAL 6.20.04-SVI-1 initiated in support of similar replacement of TMU-P-1B per EC CC 17117 concludes that the weight changes and new maximum foundation bolt loads are acceptable. Although not identical, the installed replacement pump for TMU-P-1A per EC CC 16858 weighs the same as the replacement pump for TMU-P-1B per EC CC 17117 (CVI DWG 39-00,13,3) and should have similar (if not identical) maximum foundation bolt loads as those for TMU-P-1B per EC CC 17117 (CVI DWG 39-00,13,3). This existing in-progress EC CMR 17044 supports the conclusion that this condition for TMU-P-1A does not affect the continued function or qualification of the installed EC 16858 replacement pump at TMU-P-1A. . For resolution, CVI DWG 39-00,11 needs to be updated in include maximum foundation bolt loads from the vendor for TMU-P-1A and needs to be updated to correct its depiction of the pump-to-motor mounting flange holes. In-progress EC CMR 17044 will be updated to include evaluation of the EC CC 16858 replacement pump at TMU-P-1A. . Suggest resolution assignment to AR-EFIN. | 02-00-M-BLDG-MISC,02-00-TMU-P-1A
386421 | CR | 20181102 | CAQ | D | RPV Level Continuous Backfill OOS low. | Y | N |  | N | YES | <D> **** Detailed Description **** Found CRD-FI-4A low out of spec, min spec 0.12. Recommend Backfill System Flow Adjustment ppm 10.27.75 <I> **** Actions Taken **** Initiated AR, Informed MCR. | 02-00-CRD-FI-4A
386422 | CR | 20181102 |  | 3 | SOMS takes too long |  |  |  | N | NO | <D> **** Detailed Description **** SOMS takes too long when moving from one panel to another.
386423 | CR | 20181102 | CAQ | D | WEA-FN-1B low d/p alarm across hepa filter. | N | Y |  | N | YES | <D> **** Detailed Description **** Low D/P across hepa filter alarming in and out. D/P per WEA-DPIS-1B2 reading 0.7" H20, low alarm setpoint is 0.5". This d/p seemed abnormally low in comparison to other fans. <I> **** Actions Taken **** Informed MCR, initiated AR. MCR swapped from 1A & 1B to 1A & 1C WEA fans. | 02-00-WEA-DPIS-1B2,02-00-WEA-FN-1B,02-00-WEA-HF-1B
386424 | CR | 20181102 |  | 3 | Unable To Edit Hot Spot Trend Log |  |  |  | N | NO | <D> **** Detailed Description **** The hot spot trending log does not have an edit function. If a HP tech enters survey data incorrectly the information cannot be corrected or deleted and inaccurate data is left on the database. <I> **** Actions Taken **** Generated CR. Supervision informed.
386425 | CR | 20181102 |  | 4 | EDR-DPIS-27 red needle adjustment is broken | N | N |  | N | YES | <D> **** Detailed Description **** The knob for the red needle adjustment on EDR-DPIS-27 broke when the needle was taken to GT50 dp setting per SOP -RW/EDR-OPS. Repair as necessary. <I> **** Actions Taken **** informed Shift Support Supervisor | 02-00-EDR-DPIS-27
386426 | CR | 20181102 |  | 4 | Abnormalities noted after BW/PC on EDR and FDR filters | N | N |  | N | YES | <D> **** Detailed Description **** A couple abnormalities were noted during and after both backwash/precoat cycles for both EDR and FDR filters. When the precoat cycle completed fro the FDR filter the hold pump contactor was heard to actuate inside the hold-pump breaker cubicle, however the hold-pump did not start. The hold push button had to be depressed to save the precoat from sluffing off the septa. And at the end of the EDR filter precoat cycle, even though the hold-pump started and hold-valve opened, I had to reset the disconnect inside the control panel G11-P003 because an unknown glitch in the programmer would not allow the system to start processing water from EDR-TK-2. After the disconnect was cycled then everything worked normally. <I> **** Actions Taken **** informed Shift Support Supervisor | 02-00-EDR-PROG-1
386427 | CR | 20181102 |  | 4 | Could not locate open procedure volume for SOP-RW/FDR-INFREQ |  |  |  | N | NO | <D> **** Detailed Description **** During performance of SOP-RW/FDR-INFREQ jumpers were installed to permit pumping FDR-TK-22 to 0 percent full. The open volume for this procedure could not located when the normal lineup for FDR-TK-22 was restored. <I> **** Actions Taken **** Informed the CRS and Shift Manager. Utilized a fresh copy of SOP-RW/FDR-INFREQ to remove the jumpers and restore the system to its normal lineup | 02-00-FDR-TK-22
386428 | CR | 20181102 |  | 3 | PPE at CWPH for Acid Tanker | N | N |  | N | NO | <D> **** Detailed Description **** Gravity feed to the CW basin from the temporary acid tanker was initiated on 11/30/2018 per SOP-CW-CHEM-MAINT. This procedure requires the area around the controlling valves and transfer hose to be roped off with Danger tape. As a result, personnel adjusting flow will be required to don full PPE to enter the area. On the day flow was inititiated, there was a lack of appropriately sized booties available. Fortunately, an additional pair was found int he OPS4 truck allowing flow to be initiatated. Recommend staging multiple sets of PPE suitable for work around sulfuric acid be staged in the Ops locker at CWPH. <I> **** Actions Taken **** Discussed with SM. | 02-00-P-BLDG-MISC
386437 | CR | 20181103 | CAQ | D | Spurious temp alarm HPCS-TIS-DG3 | Y | N |  | N | YES | <D> **** Detailed Description **** Spurious temp alarm on phase B, HPCS-TIS-DG3 DG3 in Standby status <I> **** Actions Taken **** Responded to alarm, RESET light was already flashing, Temp on Phase B was 46Â° C. All other indications normal for DG not running. | 02-00-HPCS-GEN-DG3,02-00-HPCS-TIS-DG3
386438 | CR | 20181103 |  | 3 | DEH PT2s need added to RO2 computer (tristation 1131) | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** DEH PT2 files were on the RO2 C drive then when upgraded the files were in the BACKUP CRO2 file. Now that file is empty. Computer is CN-1053V12. Latest PT2 files can be provided if necessary but IS should have the controlled copy or contact system engineer. In addition ops outage coordinator would also like 1311 and PT2s added to his computer. (x 4328)
386439 | CR | 20181103 |  | 3 | ALARA Suggestion: Eliminate posting hot spots in HRA's |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Eliminating the need to post radiological hot spots in posted high radiation areas would better align our Radiation Protection program with the industry. Currently, RP is required to survey hot spots, including hot spots in posted HRA's, semiannually. Annually, RP receives approximately 40 mREM to survey hot spots. <I> **** Actions Taken **** Notified RP Supervision of ALARA Suggestion Initiated this Condition Report <N> **** Equipment Description **** Various Locations in the RCA
386440 | CR | 20181103 |  | 3 | 230KV CT Trouble alarm lit in the MCR. | N | N |  | N | YES | <D> **** Detailed Description **** 230KV CT trouble alarm recieved in MCR. Sel Set 1 CT Trouble PH A and B and Sel Set CT Trouble PH A and B were alarming and flashing. Acknowledged alrams, went from flashing to solid, then per MCR direction pressed reset and they cleared. On OPDS-RLY-S3/5E and OPDS-RLY-S4/5E A and B PHS alarm and Open CT alarm are lit and did not reset. <I> **** Actions Taken **** Entered room, noted alarms. Acknowledged alarms and reset per MCR direction. Informed MCR of current status. | 02-00-OPDS-CONT-3/3H,02-00-OPDS-RLY-S3/5E,02-00-OPDS-RLY-S4/5E
386441 | CR | 20181103 |  | 4 | COND-TI-27B is consistently high out of spec | N | N |  | N | YES | <D> **** Detailed Description **** COND-TI-27B hot leakoff on RFT B is high out of specification. MD-TCV-3B/4B are full open. <I> **** Actions Taken **** Informed MCR | 02-00-COND-TI-27B
386442 | CR | 20181104 |  | 3 | (NRC) Recommend graded approach to containment O2 actions |  |  |  | N | NO | <D> **** Detailed Description **** The NRC resident questioned the CGS approach to elevated containment O2 levels. Recommend establishing graded approach to elevated containment O2 actions. Recommend these action levels be documented in OSP-INST-H101 in Note4 under Step #48. This information should also be added to SOP-CN-OPS as a precaution and limitation.
386443 | CR | 20181104 | CAQ | D | Security Grenade netting blocked |  |  |  | N | NO | <D> **** Detailed Description **** Ladders hung on the wall in the RCA blocking security netting and hung improperly <I> **** Actions Taken **** Remounted ladder properly and moved it out of the drop zone. Communicated with shift manager. CR generated.
386447 | CR | 20181104 |  | 4 | PPC-TCG-1 fault led illuminated | N | N |  | N | YES | <D> **** Detailed Description **** PPC-TCG-1 fault led illuminated investigate and restore to normal. could be related to return to PST. | 02-00-PPC-TCG-1
386448 | CR | 20181105 | CAQ | D | (NRC) R-DOOR-R013 has slight play when dogged shut | Y | Y |  | N | YES | <D> **** Detailed Description **** The NRC identified that R-DOOR-R013, the RHR C pump room east entrance door, has slight play when dogged closed. The door, hinges, and dogging mechanism are in good condition and work well. | 02-00-R-DOOR-R013
386449 | CR | 20181105 |  | 4 | SEC-XR | N | N |  | N | YES | <D> **** Detailed Description **** The power to SEC-XR inside warehouse is off without any identifiable reason. <I> **** Actions Taken **** Took the unit out of service, contacted Security Equipment coordinator and generated CR/WR <N> **** Equipment Description **** SEC X-RAY Machine inside the warehouse | 02-00-SEC-XR-5
386450 | CR | 20181105 | CAQ | C | (NRC) Two loose cover fasteners found on E-TB-B2/1 | Y | N |  | N | YES | <D> **** Detailed Description **** The NRC identified two of five fasteners on E-TB-B2/1 loose. E-TB-B2/1 is the terminal box for E-B2-1 fuses located in the division 1 battery charger room on RW 467'. The other three fasteners were tight and were maintaining the cover tightly closed. <I> **** Actions Taken **** The two loose fasteners were tightened <R> The REP/REGE assignments for this CR are not required and are being cancelled. This condition is not reportable to the NRC and does not challenge past operability of plant equipment. Concurrence for cancellation has been obtained from Regulatory Affairs Management. | 02-00-E-TB-B2/1
386452 | CR | 20181105 |  | 4 | Over November Dose Goal |  |  |  | N | NO | <D> **** Detailed Description **** Williams Plant Services was over on the Departments November dose goal of 56 MR with an actual of 81 MR. This was mainly due to emergent work requested of our Insulators to remove and re-install insulation on the RHR B piping. This was located in the South Pipe Chase on the 548â€™ RX, 58 MR was received performing this work. <I> **** Actions Taken **** Notified Supervison and Management.
386453 | CR | 20181105 |  | 3 | Re-create tasks 02116845-03 & 04 (Tracking only) |  |  |  | N | NO | <D> **** Detailed Description **** Re-create tasks 02116845-03 & 04 to be completed on the next PM. 02116845-03 & 04 had to be cancelled so that the PM could be closed for ISP-CRD-X307. <I> **** Actions Taken **** notified planner, notified WWM, notified Component Manager and initiated CR for tracking. | 02-00-CRD-LT-13B
386454 | CR | 20181105 |  |  | Quarterly CORC Caution Tag Audit (WO 02122674) |  |  |  | N | NO | <D> **** Detailed Description **** Quarterly CORC Caution Clearance Audit 10CFR50.59 The Quarterly CORC Caution Tag Audit (WO 02122674) has documented the caution clearances that have been hanging for GE 30 days. There are 19 new Caution clearances added to this total since the last audit: C-ANN-P800/C3 -002, C -E-DISC-7A2E -001A, C-E-TR-N1 -001, C-HD-V-18D -001, C-HV -V-30D -001, C-IRM-RMS-S6 -001, C-OG-DY-30A -001, C-OG-RF -20C -002, C-REA-FU-3 -001, C-RFW-TR-1 -001, C-RPS-RLY-K10F -001, C-RPS-RLY-K10F -002, C-RRC-VMP-1 -003, C-SS-V-41 -001, C-TMU-V-104 -001, C-TO-EX-1A -001, C-TO-P-BLP -003, C-TOA-AW-1A -002, C-TOA-DPIC-2A -001. <I> **** Actions Taken **** Wrote CR. <N> CR Requested to be canceled at the request of Initiator. Previous CR (383971) addresses this issue.
386455 | CR | 20181105 |  |  | Quarterly CORC Caution Tag Audit (WO 02124824) |  |  |  | N | NO | <C> CR canceled at the request of Initiator. Another CR (386467) has been generated. <D> **** Detailed Description **** Quarterly CORC Caution Clearance Audit 10CFR50.59 The Quarterly CORC Caution Tag Audit (WO 02122674) has documented the caution clearances that have been hanging for GE 30 days. There are 16 new Caution clearances added to this total since the last audit: C-CRA-42-8B10 -001, C-E-CB-LP7EA/29-001, C-E-DISC-6B3A -001, C-FDR-P-8 -001, C-FP-V-5 -001A, C-FPC-P-1A -001, C-MS-RMS-RV/2A -001, C -MS-V-115B -001, C-MT-DISC-6B2D -001, C-OG-RF-20B -003, C -PWC-P-103 -001, C-SMA-CC-1 -001, C-SW-RECIRC -002, C-TB BLDG HVAC -001, C-TMU-V-1B -001, C-WCH-V-658 -001B. <I> **** Actions Taken **** Wrote CR.
386466 | CR | 20181105 |  | 3 | Quarterly CORC Danger & Local Tag Audit (WO 02124823) |  |  |  | N | NO | <D> **** Detailed Description **** Quarterly CORC Danger & Local Clearance Audit 10CFR50.59 The Quarterly CORC Danger & Local Tag Audit (WO 02122671) has documented the danger & local clearances that have been hanging for GE 30 days. 2 new clearances added to this total since the last audit; L-TMU-MO-19B -001 & L-E-CO -PBX/1&2 -001. Request Technical Services/Systems Engineering Manager (or designee) to determine whether a 50.59 review is required. <I> **** Actions Taken **** Wrote CR.
386467 | CR | 20181105 |  | 3 | Quarterly CORC Caution Tag Audit (WO 02124824) |  |  |  | N | NO | <D> **** Detailed Description **** Quarterly CORC Caution Clearance Audit 10CFR50.59 The Quarterly CORC Caution Tag Audit (WO 02122674) has documented the caution clearances that have been hanging for GE 30 days. There are 16 new Caution clearances added to this total since the last audit: C-CRA-42-8B10 -001, C-E-CB-LP7EA/29-001, C-E-DISC-6B3A -001, C-FDR-P-8 -001, C-FP-V-5 -001A, C-FPC-P-1A -001, C-MS-RMS-RV/2A -001, C -MS-V-115B -001, C-MT-DISC-6B2D -001, C-OG-RF-20B -003, C -PWC-P-103 -001, C-SMA-CC-1 -001, C-SW-RECIRC -002, C-TB BLDG HVAC -001, C-TMU-V-1B -001, C-WCH-V-658 -001B. Request Technical Services/Systems Engineering Manager (or designee) to determine whether a 50.59 review is required. <I> **** Actions Taken **** Wrote CR.
386468 | CR | 20181105 | CAQ | D | LPCS-FIS-4 Instrument Valve 9 packing leakage (1.2 dpm) | Y | N |  | N | YES | <D> **** Detailed Description **** Small packing leak from LPCS-FIS-4 Instrument valve 9. Leakage was approximately 1.2 dpm (1 drop in 50 seconds). This was previously identified (CR 358750) with a much less than 1 dpm leak in November 2016 (WO 02089655-01). The leakage rate has increased slightly since then and was visibly dripping. Found during TSP-LPCS-B801. <I> **** Actions Taken **** CR written and CRS notfied. | 02-00-LPCS-FIS-4
386469 | CR | 20181105 |  | 3 | RWCU-RST-70A/B | N | N |  | N | YES | <D> **** Detailed Description **** When replacing strainer it is very difficult to keep strainer in place. The fit inside the strainer housing is very shallow and loose and if the strainer is allowed to drop at all it falls out of the fit and then tilts, when that happens you can not get the assembly to realign and you have drop everything out of the housing and start over. Various methods have been tried to work through the problem. The job always gets done eventually, sometimes has to be reworked becasue it was thought everything stayed in place but didn't and so end up with leakby, and leaks from flange as not seated corrretly because crushing strainer. Need help from engineering to find a way to make this job more manageable. We are taking extra dose trying to do this job without the correct tooling. Also has been an injury doing this job because of the weight of the lower flange assembly. <I> **** Actions Taken **** Writing this CR to bring attention to problem and get additional help in solving the issues, to allow doing the job more efficiently, safer and take less dose. <N> **** Equipment Description **** RW 467 valve room A RW 467 valve room B | 02-00-RWCU-RST-70A,02-00-RWCU-RST-70B
386470 | CR | 20181105 |  | 3 | E-RLY-27/75 As found pickup voltage out of tolerance | N | N |  | N | YES | <D> **** Detailed Description **** During As found testing of E-RLY-27/75 per WO#02102732-01 the pickup voltage was found out of tolerance at 84.75 VAC. The pickup should be 82 VAC per E514-11 with a data sheet tolerance of 79.54 - 84.46 VAC. This relay was replaced with a calibrated replacement relay per WO#02102732-01. The removed relay is staged in relay shop. If it is used in the future it will be tested and calibrated before being used. <I> **** Actions Taken **** Notified supervisor and PSRO. This relay was already replaced with a calibrated replacement relay and would have to be calibrated before using. | 02-00-E-RLY-27/75,02-00-E-RLY-27/85
386473 | CR | 20181105 |  | 4 | PCSC Committee meeting quorum not met |  |  |  | N | NO | <D> **** Detailed Description **** A PCSC Committee meeting was conducted on 11/5/2018 at 1130 in Yakima GSB1. Chemistry member nor an alternate did not attend. Electrical craft were 5 minutes late. Outlook appointments were scheduled for over a month and an agenda/ reminder was sent out the week prior to meeting. <I> **** Actions Taken **** Attempted to locate members, supervisors have been informed.
386475 | CR | 20181105 |  | 4 | No Eng support task prevented proper eng dose budget for WOT |  |  |  | N | NO | <D> **** Detailed Description **** System Engineering support is required to perform the 01 task for WO 02118085 for RRA-CC-20 water side inspect/clean. There was no budgeted dose for engineering due to the lack of an engineering support task that would have prompted HP planning dose budget for engineering. This is work in the Fuel Pool Cooling HX room which is a HRA/HCA requiring a high rad brief. <I> **** Actions Taken **** Contacting HP Planning to put notes in the WOT and notified supervisor. | 02-00-RRA-CC-20
386478 | CR | 20181105 |  | 3 | Evaluate Safety of Refuel Bridge Upper Deck Access Ladder |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The ladder on the side of the refuel bridge is used to access the upper deck. Although the ladder meets the requirements of ISPM-9, it can be akward to make the transition to the upper deck with the amount of toe engagement on the top few rungs. Additionally, the swing gate as installed provides a pinch hazard on the user's hands. There are also a couple of rungs in the middle with limited toe engagement that can make descending the ladder feel dangerous (ie landing on an HP stanchion in the case of a fall). Recommend adding a cage around the top half of the ladder and/or rebuilding the ladder to avoid these issues. <I> **** Actions Taken **** Notified supervisor, wrote this CR. <N> **** Equipment Description **** Refuel Bridge Ladder | 02-00-NSSE-EQ-8,02-00-R-BLDG-MISC
386479 | CR | 20181105 | CAQ | D | Late eSOMS Entries for Maintenance - Week of 10/27 - 11/2/18 |  |  |  | N | NO | <D> **** Detailed Description **** An I&C supervisor failed to update his time when he held over for an extra hour, and a mechanic's overtime hours were entered incorrectly as 10 hours instead of 12 hours, which is what he worked . <I> **** Actions Taken **** Updated eSOMS with the correct hours for both individuals. No violations occcurred.
386481 | CR | 20181105 |  | 4 | E-CB-LPFP7/12 CKT BKR FOR LIGHTS - WATER FILTRATION BLDG is | N | N |  | N | YES | <D> **** Detailed Description **** E-CB-LPFP7/12 CKT BKR FOR LIGHTS - WATER FILTRATION BLDG is tripped open and is still open due to a bad circuit. | 02-00-E-CB-LPFP7/12
386483 | CR | 20181105 | CAQ | C | (QA) M&TE Recording Errors |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) M&TE used for WO 02100585-01 was not recorded properly. First, the handwritten M&TE in the "Calibration Tools Used" box was missing two items (0067429 and 45136) that were recorded as being used in the procedure attached to the record on page 6 of 34. Also, no M&TE was recorded in the TIMM305 "Calibration Instruments" panel in Asset Suite. It is suspected that personnel may have become accustomed to not needing to fill out the Asset Suite panel when using electronic work orders. This work order was printed, completed by hand, and then uploaded to Dataglance. A vulnerability may exist for other completed or planned work orders if this was more than a one time mistake. <I> **** Actions Taken **** Informed Mechanical Maintenance Supervisor and Component Group Manager.
386484 | CR | 20181105 |  | 3 | PMID 16954-01 periodicity needs to be changed back to 2 year |  |  |  | N | NO | <C> Per MRT feedback received Thursday 11/08 this is to be prioritized as Non-CAQ due to it being a recommendation to change the PMID periodicity back to 2 years. <D> **** Detailed Description **** AR 358067 was written to address SW-P-1A being in the aleart range. AR 357529 changed the frequency of this PMID to annual to meet the intent of increased CPT. However what was requested under AR 358067 was that a new PMRQ be created to take care of the increased testing. The PMID that was changed increased the frequency of the VPI portion of OSP-SW/IST-Q701 which requres cycling SW-V-69A and SW -V-70A. This takes a considerable amount of this and resources and is not warranted. Request that there is a new PMRQ created for an annuualized CPT for this and change the 2 year VPI back to the 2 year periodicy. <I> **** Actions Taken **** Infomed supervision that the PMID appears to be incorrect for what is needs after this work was pulled forward. | 02-00-SW-P-1A,02-00-SW-V-69A,02-00-SW-V-70A
386485 | CR | 20181105 |  | 4 | Shift Manning not per PPM 1.3.1 | N | N |  | N | NO | <D> **** Detailed Description **** On 11/5/2018, an Equipment Operator was sent home to handle an emergent situation. This left the crew with only four Equipment Operators to man the shift which is below the minimum manning requirements of Note 4 of PPM 1.3.1 Section 4.10. Attempts to call out an additional operator on overtime were unsuccessful. As a result, OPS4 logs at TMU will not be taken in order to maintain Fire Brigade and Safe Shutdown requirements. Manning remains above minimum tech spec requirements. <I> **** Actions Taken **** Discussed with SM.
386495 | CR | 20181106 | CAQ | C | TMU-MO-7B needs adjustment/repair | N | N |  | N | YES | <D> **** Detailed Description **** During investigation of TMU-MO-7B intake sluice gate valve under WR#29144687 the following issues were identified. This CR/WR written in order to address the following issues. 1) Limit#7 to be set according to MDS sheet and EWDâ€™s EWD -55E-012/EWD-55E-012A, note: limit #7 is not red light indication only, limit #7 also controls TMU-RLY-33XO/V7B which has contacts 9-10 in series with motor close coil 2) The top tier drawing EWD-55E-012 and supporting EWD -055E-012A both have incorrect EPNâ€™s listed. They call out TMU-RLY-33X1O/V7B instead of TMU-RLY-33XO/V7B. 3) RELAY TMU-RLY-33X0/V7B was observed stuck closed (energized position) after one of the strokes closed and functioning intermittently during other strokes of TMU-V -7B.relay group notified and looking into replacing relay. 4) Valve position indicator rod needs to be re-welded back onto the top of the valve stem. 5) MDS sheet/prints need to be corrected. MDS sheet showing the switch info is written in limitorque fashion and this valve is a Tork-master. Tork-master uses 10 individual micro switches and the MDS leads you to believe that limit 7 is red light onlyâ€¦ refer to EWD-55E-012 and EWD-55E-012A for clarification. 6) Declutch lever is not operating properly. In order to operate the valve manually, declutch lever had to be held down the entire time. 7) Top of operator with declutch lever needs to be opened to check the overall condition and repair declutch lever mechanism. 8) Label the relay with the correct EPN, not sharpie 9) Close limit switch (7) and close Torque switch is in series, therefore the valve only closes to 95% max. Is this acceptable? <I> **** Actions Taken **** This AR/CR and WR written to address the issues. <N> **** Equipment Description **** TMU pumphouse | 02-00-TMU-MO-7B,02-00-TMU-RLY-33XO/V7B,02-00-TMU-V-7B
386497 | CR | 20181106 |  | 4 | Name miss identified on Whole Body Count |  |  |  | N | NO | <D> **** Detailed Description **** The name on the WBC report was incorrect. This resulted in the personnel exposure record not being properly maintained and updated. WBC was conducted on 9/20/18. Associated with DLR 00120355. This resulted in updating his TES record. There was also a delay in locating and returning the individualâ€™s DLR for â€œreturning to work.â€ <I> **** Actions Taken **** Notified supervision, located and returned DLR, reprinted report and requested review of report by SME. Report was sent to exposure record to update correct and update exposure record.
386498 | CR | 20181106 | CAQ | D | E-C2-1 voltage needs adjusted (bottom of log band) | Y | N |  | N | YES | <D> **** Detailed Description **** E-C2-1 voltage band per operator logs is 258-264 V in float. The voltmeter on the charger is reading right about 258 V. The voltage needs to be adjust to prevent from going out of band. <I> **** Actions Taken **** Informed CRS. | 02-00-E-C2-1
386500 | CR | 20181106 | CAQ | C | Wrong CRD flow direction on M528-1 dwg. |  |  |  | N | NO | <D> **** Detailed Description **** The CRD flow direction arrow on M528-1 at (D/7) doesnâ€™t match the flow direction for the same CRD line flow coming from M528-2 at (K/6). Drawing M528-2 has the correct flow direction. Recommend assigning to Mechanical/Civil Design & Drafting Group (AR-DESDFTM) for correction. <I> **** Actions Taken **** Discussed the issue with CRD system backup engineer and design & Drafting group then initiated this CR.
386501 | CR | 20181106 |  |  | OPS LORQ & ILC Training has been in decline for years |  |  |  |  | NO | <C> Potential SCWE issue. Per SWP-CAP-01, specific details have been redacted, but original information resides with ECP Manager for follow up action. CR found at INPROG moved to APPROVED. <D> **** ANONYMOUS CR - Detailed Description **** This potential SCWE issue has been pulled and assigned to ECP. <N> See ECP case 2018-C3
386502 | CR | 20181106 | CAQ | D | (NRC) E-BU-C120/441/3X has a charger fault light on | N | Y |  | N | YES | <D> **** Detailed Description **** E-BU-C120/441/3X has a charger fault led lit. This is an essential EBU per LCS 1.10.7. | 02-00-E-BU-C120/441/3X
386503 | CR | 20181106 |  | 4 | Fit Test Porta-Count as found Calibration failed | N | N |  | N | YES | <D> **** Detailed Description **** As found calibration of ProtaCount instrument ID 0065843 used for respirator fit test, had a significant failure. The failure was so high that unit operational ability would have been impractical. The cause of the failure was chemical buildup on the nozzle retainer. The unit s nozzle was replaced and cleaned and calibration was successful. <I> **** Actions Taken **** The unit has been returned as available to service. The as found calibration failure evaluation indicated two factors 1- the unit could not possibly have provided a pass for respirator fit test(failed conservable) 2- Unit could not have passed daily prior to use checks. The CR trends calibration by off-site vendor. Recommended no further actions. <N> **** Equipment Description **** Instruent ID 0065843
386504 | CR | 20181106 | CAQ | D | SW-V-193 yoke lock nut found loose | Y | N |  | N | YES | <D> **** Detailed Description **** While performing maintenance on nearby equipment, it was noticed that the lock nut on SW-V-193 was loose. This lock nut has a gap tolerance and a torque value per DWG 215 -09,57,1. This valve may require rotation of the yoke to achieve the gap tolerance which in turn requires valve manipulation. Ensure work order has proper PCSC steps. <I> **** Actions Taken **** Notified Supervisor. <N> **** Equipment Description **** R 555 K9/9.0 | 02-00-SW-V-193
386505 | CR | 20181106 |  | 4 | RHR-RO-5A- New Fabrication machined out of tolerance | N | N |  | N | NO | <C> Per MRT Feedback received Thursday 11/08, this item is reprioritized to NCAQ as the issue is with the CNC milling machine and not parts or specification related. <D> **** Detailed Description **** While machining blank plate to fabricate a new restricting orifice for RHR-RO-5A on WO 02033672-16 and ASME Sect. XI plan 2-2973 the inner diameter was machined out of tolerance. This work was performed on a CNC milling machine. The The final bore dimension was supposed to be 13.000" + .000 / -.003. When the bore ID was at 12.995", the machinist programmed the machine to remove .001" (.002" total) to bring it into tolerance at 12.997". After the mill was finished, the machinist noticed the mill had removed .007" instead thereby making the inside diameter out of tolerance per DWG 250-01,2. <I> **** Actions Taken **** Notified Supervisor. Notified ASME PLE. | 02-00-RHR-RO-5A
386506 | CR | 20181106 |  | 3 | (QA) Heat trace energized on abandoned piping | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) Heat trace is energized on piping that was never placed in service in the abandoned MWR resin processing system. Panel HT-HTP-PMT/1 on Rad Waste (RW) 437' supplies heat trace to MWR-TK-31A & 31B process piping. This piping was never placed in service and should not have heat trace energized. Other heat trace panels that support additional MWR resin process piping are de-energized including HT -HTP-PTM/2A, 2B & 3 on RW 467'. Ten separate circuits of heat-traced piping are using electricity unnecessarily. Refer to EMDS for details Recommend assignment to Engineering. This issue is considered a Deficiency identified during Quality SR-19-02 Continuous Monitoring Roll-Up Surveillance. <I> **** Actions Taken **** Discussed with Design Engineering personnel. Initiated this CR and a Cost Saving Idea on SharePoint. <N> AR EVAL needed? MWR-TK-31A and MWR-TK-31B are not EPNs in MEL. | 02-00-HT-HTP-PTM/1,02-00-HT-HTP-PTM/2A,02-00-HT-HTP-PTM/2B,02-00-HT-HTP-PTM/3
386507 | CR | 20181106 |  | 3 | Training Re-Scheduled Within 7 Day Window |  |  |  | N | NO | <D> **** Detailed Description **** Electrical Maintenance Training was moved within the 7 day window due to conflicting electrical training priorities. The training that was moved results in a qualification and no students will become delinquent as a result of this move. This training is rescheduled for late November / early December. The training move was approved by the Maintenance TAG chair and Training Department Manager. <I> **** Actions Taken **** Generated this CR per TDI-02 step 4.4.2.
386509 | CR | 20181106 |  | 4 | (LL)Warehouse Material not Issued Prior to Work Order Closed |  |  |  | N | NO | <D> **** Detailed Description **** Ground fill material purchased through the Warehouse for ISFSI Pad Expansion in 2016 was not verified to be issued (Issue Ticket) by the Warehouse prior to work order 02066396 closure. The ground fill material was delivered directly to the ISFSI site and used. Arrangements were made with the Warehouse to allow the ISFSI assigned QC inspector to perform receipt inspection since the material would not physically pass through the Warehouse. Since the Warehouse purchased the material with Supply Chain budget, the material had to be issued to ensure costs were directed to the correct project. There was no confirmation to ensure the Warehouse issued the material following receipt inspection and acceptance, or prior to closure of the work order containing the associated Material Requests (MR). Unissued material on MRs are automatically cancelled when the associated work order is closed. As a result, the material costs remained with the supply chain budget. To correct the cost misallocation, MR 240630 was initiated. . The lessons learned is to review all incomplete MRs and verify no unissued material was not used prior to closure of the associated work order. . Recommend this CR as Trend only. <I> **** Actions Taken **** MR 240630 was initiated.
386510 | CR | 20181106 |  | 4 | 8/4/18 downpower constituted Reactivty Management event |  |  |  | N | NO | <D> **** Detailed Description **** The plant downpower executed on 8/4/18 to replace ASD cards constituted a Reactivity Management Level 4 event per PPM 1.3.79: "Downpower GE 1.0% RTP In Accordance with Approved Operating Procedures Not Due to Cycle Management Activities or Required Surveillances, (4-1) " This CR initiated for tracking only. This is not an equipment issue or operability concern. <I> **** Actions Taken **** Discussed issue with Reactor Engineering to ensure there were no surveillances performed, which would remove the need to classify as RM.
386511 | CR | 20181106 |  | 3 | FPC-P-1A lessons learned | N | N |  | N | YES | <D> **** Detailed Description **** During seal replacement of FPC-P-1A under WO 0201240201 an unexpected ammount of water drained form the FPC-P-1A suction flange. It is unclear if the vent and drain lines functioned adequately to handle draining the isolated portion of the FPC system before maintenance began. <I> **** Actions Taken **** Maintenance stopped work and expanded the team (give 2). Recommend incorperating lessons learned for future clearancr orders and maintenance activities. <N> **** Equipment Description **** FPC-P-1A | 02-00-FPC-P-1A
386515 | CR | 20181106 | CAQ | D | Backed out of ISP-CMS/PRM-X306 | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02100680-01, had to back out of surveillance and restore CMS-SR-20 due to possible damaged detector. <I> **** Actions Taken **** Informed Supervision, CRS, and Shift Manager. Decision was made to back out of surveillance and restore sample rack. WR 29145475 written to isolate sample rack.
386516 | CR | 20181106 |  | 4 | Backup power supplies don't have power on RFT Switches | N | N |  | N | YES | <D> **** Detailed Description **** During quarterly walkdown Computer Engineer noticed that 1 of 2 power supplies on each of 2 RFT Switches did not show power lights. The power supplies are redundant, so the device function has not been affected. Power circuits are shown on EWD-72E-024. suggest this CR should go to maintenance for investigation. <I> **** Actions Taken **** Discussed issue with System Engineer. | 02-00-RFT-NETSW-1A,02-00-RFT-NETSW-1B
386517 | CR | 20181106 |  | 3 | E-M-M2/F4 and F5 fail to start | N | N |  | N | YES | <D> **** Detailed Description **** The fans on cooler group 2 of E-TR-M2 both failed to start. The EO responded to the CR alarm and found E-M-M2/F4 not running, but the breaker had not tripped. While investigating the event with no actions yet taken, the fan circuit opened so all fans/pump turned off, then the pump and only one fan started back up. Visual verification confirmed E-M-M2/F4 and F5 were both not running. Again, no fans had actually tripped but 2 failed to start. The contactors of the 2 fans were not energized as evidenced by the white indicator not sticking out. This occurs fairely regularly during fall/spring but normally only a single fan fails to start. ARP actions restored the fans to normal and cleared the alarm. <I> **** Actions Taken **** Informed CRS and took ARP actions. | 02-00-E-M-M2/F4,02-00-E-M-M2/F5,02-00-E-TR-M2
386518 | CR | 20181106 | CAQ | C | Wedge for16â€ RHR-V-16B is not usable for ASME Section III/2 |  |  |  | N | YES | <D> **** Detailed Description **** During the planning of the guide repairs for RHR-V-16B WOT 02107553 , CID 54200405 for the wedge has a limitation on use that states that the Code Data Report N-2 is missing. This wedge is listed against BOM but has no green tag which indicates that the wedge was never was accepted by QC. Recommend that valve manufacture be contacted to determine if the code data report can be found for the part in question. This issue does not impact the installed valve <I> **** Actions Taken **** contacted QC Reciving and validated no green tag was issued for this part | 02-00-RHR-V-16B
386519 | CR | 20181106 | CAQ | D | E-IR-81 Tubing leaks | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of ISP-RPS-S901 it was discovered several peices of tubing with small leaks. One of the more significant leaks is connected to RPS-PS-5A, and appears to be coming from the swedgelock fitting going into the bottom of PS-5A. The leaks found are not steadly leaking, they are droplets which pool around tubing ferrils and collect on the underside of the tubing. <I> **** Actions Taken **** Supervision was notified, CR generated. WR generated. <N> **** Equipment Description **** 471 TB | 02-00-E-IR-81
386520 | CR | 20181106 | CAQ | C | ISP-RPS-S902 RPS test box not extinguished. | Y | N |  | N | YES | <D> **** Detailed Description **** RPS test box not extinguished in step 7.3.37. WO#02122424 -01 <I> **** Actions Taken **** CR for trending purposes. <N> **** Equipment Description **** RPS-RLY-K8C
386521 | CR | 20181107 |  | 3 | ISP-RPS-S901 and ISP-RPS-S902 Were Not OPS Auth. |  |  |  | N | NO | <D> **** Detailed Description **** I/C surveillances ISP-RPS-S901 and ISP-RPS-S902 (WO 02122427 and 02122424) were not flagged OPS Authorization. This bypassed the OPS closeout of the surveillance. Please ensure these surveillances receive OPS authorization in DataGlance.
386522 | CR | 20181107 |  | 3 | RFT B Vibes Trouble | N | N |  | N | YES | <D> **** Detailed Description **** 4.840.A1 7-5 (Turbine B Vibration Trouble) was received in the MCR. RFW-VBI-XE/P1B (Pump Axial Thrust Displacement) was in ALERT at 15 mils in the Normal direction. The alarm was reset locally per the ARP and it cleared. Mils is hanging out just below 15 mils. <I> **** Actions Taken **** Responded per ARP. <N> **** Equipment Description **** TB 441 | 02-00-RFW-P-1B,02-00-RFW-VBI-XE/P1B
386534 | CR | 20181107 |  | 4 | FPC-LIS-2A |  |  |  | N | NO | <D> **** Detailed Description **** Upon replacement of FPC-LIS-2A, work order task instructions has a step to return removed unit to warehouse.This cannot be done, due to unit installed in the FPC system and radiological conditions exist that prevents unit being released from the RCA. <I> **** Actions Taken **** Wrote CR to alert Engineering, discussed with Manager. | 02-00-FPC-LIS-2A
386536 | CR | 20181107 |  | 4 | CF-P-42B wonâ€™t pump. | N | N |  | N | YES | <D> **** Detailed Description **** When starting CF-P-42B per SOP-CW-CHEM per chemistry request, the pump started, but would not pump. This pump needs to be filled and vented per SOP-CW-CHEM-MAINT. <I> **** Actions Taken **** Informed supervisor and chemistry. <N> **** Equipment Description **** cwph | 02-00-CF-P-42B
386537 | CR | 20181107 |  | 4 | Pressure gauge on PWC-V-453 not working. | N | N |  | N | YES | <D> **** Detailed Description **** While investigating PWC-P-122 per WR 29144722, the gauge on PWC-V-453 was found to not be working. Prior to starting PWC-P-122 this gauge was reading 11 psig. After starting PWC-P-122, this gauge still indicated 11 psig. Please investigate the functionality of this gauge and the port / fitting that it is attached to for blockage. <I> **** Actions Taken **** Informed supervisor and wrote this CR/WR. <N> **** Equipment Description **** Bldg 33 | 02-00-PWC-P-122,02-00-PWC-V-453
386538 | CR | 20181107 | CAQ | D | EDNA points W140 and W150 not reading as expected | Y | N |  | N | YES | <D> The EDNA point W140 for RHR-A Pump Motor Lower Guide Bearing temperature and W150 for RHR-C Pump Motor Lower Guide Bering temperature are not reading as expected. The temperature reading for W140 and W150 read ~90-105 deg when the pump is secured compared to the Motor Thrust Bearing temperatures (W139/W149) that return to a lower temperature when the pumps are not running. The temperature reading for W140 and W150 trend upward slightly when the pump is running, but does not read as expected when the pump is secured. The RHR-B Lower Guide Bearing temperature EDNA point (W145) trends as expected when the pump is running and returns to a similar temperature as the Thrust bearing when the pump is secured. All other RHR-A and RHR-C motor temperature and vibration parameters are trending normally within acceptable bands. These EDNA points are used for trending only. EDNA graph examples are saved in the EDMS. The EDNA points are supplied by RHR-TE-503 (W140) and RHR -TE-509 (W150). Recommend maintenance investigate if the installed temperature elements are attached properly. | 02-00-RHR-TE-503,02-00-RHR-TE-509
386541 | CR | 20181107 |  | 4 | Inadequate lighting in LAB 10 classroom. | N | N |  | N | NO | <D> **** Detailed Description **** Inadequate lighting in LAB classroom; lighting in classroom seems to be either inadequate or multiple lamps need to be replaced due to aging. Additionally multiple diffusers have debri in them. Area with issue: BLDG 35- LAB 10 <I> **** Actions Taken **** Briefed with the instructor, identified in a MOT and initiated CR
386543 | CR | 20181107 | CAQ | D | NSSE-EQ-8 Intermittent Actuation of Main Hoist Motor Brake | Y | Y |  | N | YES | <D> **** Detailed Description **** The Main Hoist Motor Brake is being applied sporadically when raising and lowering the mast. It's recommended that the overspeed switch be adjusted to allow for more motor RPM's before switch contacts open. <I> **** Actions Taken **** Discussed with Reactor Maintenance Supervisor. <N> **** Equipment Description **** RB606 | 02-00-NSSE-EQ-8
386546 | CR | 20181107 |  | 4 | DG Building Lighting Replacement | N | N |  | N | YES | <D> **** Detailed Description **** The lighting in the DG1 room has continued to deteriorate. The low light condition makes any work performed in the room more difficult. It also hinders daily rounds and system monitoring as material condition becomes difficult to asess The EC has been processed for LED lights and planning is working on the packages currently. Management should review priority for replacement as low light conditions can contribute to HU events, safety events and poor performance of equipment monitoring. <I> This is non-essential lighting. | 02-00-D-BLDG-MISC
386548 | CR | 20181107 |  | 4 | DEH-COMP-4 fan failing | N | N |  | N | YES | <D> **** Detailed Description **** The rear fan of DEH-COMP-4 (Engineering Workstation) is failing. It is noisy and starting and stopping rapidly. The fan should be replaced. Identified during system engineering walkdown. | 02-00-DEH-COMP-4
386550 | CR | 20181107 |  | 3 | loose tarp covering boxes of used turbine blades |  |  |  | N | NO | <D> **** Detailed Description **** Tarp covering boxes of turbine blades loose of at one end. Satellite RCA adjacent to the Spray Ponds contains a flatbed trailer with boxed used turbine blades. The tarp used to wrap the boxes has become detached from its anchorage at the west end of the flatbed trailer. The bungee cords used to anchor the tarp were found as failed. The bungee cords on the east side of trailer were still providing anchorage but were degraded. <I> **** Actions Taken **** Notified HP Supervision. wrote CR
386552 | CR | 20181107 |  | 4 | EDR Filter High Diff Press Alarm locked in | N | N |  | N | YES | <D> **** Detailed Description **** Currently, EDR-DPIS-27 is indicating 18 PSID. The red alarm setpoint needle is at 30 PSID. However, the EDR filter high differential pressure alarm for EDR-DM-9 is locked in and cannot be reset in the RWCR. The PLC was reset twice to no avail. Please investigate. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RWCR | 02-00-EDR-DM-9,02-00-EDR-DPIS-27
386555 | CR | 20181107 | CAQ | D | EDR-P-12 (EDR-DM-9 Hold Pump) will not run | N | N |  | N | YES | <D> **** Detailed Description **** EDR-P-12 was discovered not running on G11-P003. Indication in RWCR is that the pump is on and the hold valve is open. At P003, we only have indication of the hold valve open. The green "off" light for the pump is on. A reset of the PLC did not fix the situation--pressing ther ON-HOLD button opens the valve, and the pump indicates start, but then immediately trips. Believe this could be related to CR 386552. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 467, RWCR | 02-00-EDR-DM-9,02-00-EDR-P-12
386556 | CR | 20181107 |  | 3 | CWPH Basin Netting | N | N |  | N | NO | <D> **** Detailed Description **** AR 378267-01 classified the netting over the CWPH basin a non-conforming condition, with WR 29143405 initiated to correct the discrepancy by removing the net. Per SWP-CAP -01 section 4.10, the CA AS was closed to the WR. However, the WR was cancelled the following day. Subsequently AS 02 of the same AR was initiated prior to AS 01 completion to update SOP-CW-CHEM by reflecting proper configuration after WR completion. SOP-CW-CHEM was recently issued to show the net removal, even though the WR was cancelled and never worked. WR 29145514 has now been initiated to remove the netting and correct the situation. <I> **** Actions Taken **** Discussed with supervisor and acting design engineering manager. <N> **** Equipment Description **** SOUTH OF CWPH OUTSIDE | 02-00-P-BLDG-MISC
386557 | CR | 20181107 |  | 3 | (Trend) CW-PHITS-1 repeatedly found out of tolerance |  |  |  | N | YES | <D> **** Detailed Description **** This CR identifies a long-term trend with CW-PHITS-1 repeatedly being found out of tolerance (GT 0.3 units pH). Recommend assignment to AR-SEBOP to evaluate effectiveness of maintenance and document long term maintenance strategy. <I> Trend CR - see individual CRs for IODs. <N> Routine maintenance and periodic grab samples ensures regular verification of pH accuracy. When the pH signal is known to be in error, PPM 12.2.9 provides procedural guidance for conducting grab samples. WR 29145429 has been generated to address the most recent signs of degradation, identified in CR 386382. | 02-00-CW-PHITS-1
386558 | CR | 20181108 |  | 3 | COND-V-208F Dual Indication when open. | N | N |  | N | YES | <D> **** Detailed Description **** COND-V-208F showing Dual Indication when open durring a backwash evolution. Durring the backwash of COND-DM-1F that was scheduled for 11/07/18 COND-V-208F was stuck in the closed position and when it finally opened, it was giving dual indication (Throttled). Durring the backwash evolution, if this valve is to open it must fully pen and never be in the throttled position. We have had a similar event with COND-V-206C with is a similar valve. Recomend that engeneering look into this issue and determine if this ight happen to all silmilar valves in the Condensate system. <I> **** Actions Taken **** CR/WR written Supervision Notified. | 02-00-COND-V-208F
386563 | CR | 20181108 |  | 4 | Excessive BW/PC of FDR-FU-19 | N | N |  | N | YES | <D> **** Detailed Description **** Excessuve BW/PC on FDR-FU-19. BW/PC and Placed in service at 1700 on 11/07 BW/PC and Placed in service at 2245 on 11/07 BW/PC and Placed in service at 0400 on 11/08 tripped again on high DP at 0515 on 11/08 Filter is only capable of processing water for 1HR 15MIN before it tripps on high D/P. <I> **** Actions Taken **** CR/WR Supervision Notified This issue is on PCL. | 02-00-FDR-FU-19
386564 | CR | 20181108 |  | 4 | 2 Pieces of M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** 2 Pieces of M&TE were found OOT & adjusted within specs. Both were NOT used during Calibration cycles. Calcode #C003954 Shopmade ARM Power Supply. DEF #6768A written. Calcode #0063626 Movats Torque Thrust Cell- model 2-22100 SMB-000 (RA). DEF #6769A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
386565 | CR | 20181108 |  | 4 | 2 Pieces of M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** 2 Clemco Carbon Monoxide Alarms- model CMS-2's were NOT used during Calibration. Rejected- Replaced Sensors & UUT's still will not respond properly. Calcode ##0063706. DEF #6770A written. Calcode #0063707. DEF #6771A written. New units will be purchased for replacements. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
386566 | CR | 20181108 |  | 4 | Poor lighting/Lights out TB stairwell #A1 | N | N |  | N | YES | <D> **** Detailed Description **** The lighting in stairwell #A1 in the Turbine Bldg. is getting bad. Some lights are out and some are flickering and dimming. <I> **** Actions Taken **** CR notified, CR written. <N> **** Equipment Description **** TB stairwell #A1 poor lighting. | 02-00-T-BLDG-MISC
386568 | CR | 20181108 |  | 3 | Procedure needed to receive Acid Sulfuric to temp. tanker |  |  |  | N | NO | <D> **** Detailed Description **** Procedure needed to receive Acid Sulfuric to temporary tank trailer. <I> **** Actions Taken **** Inform SM and environmental scientist. <N> **** Equipment Description **** Temporary acid tanker at the CW tower area.
386570 | CR | 20181108 |  | 4 | Dead bird found in the protected area fence line |  |  |  | N | NO | <D> **** Detailed Description **** There is a dead raven in the security fence line of the PA. consulted with E&RP for disposal. <I> **** Actions Taken **** CR generated, E&RP consulted for disposal Bird was removed, no further actions necessary.
386571 | CR | 20181108 |  | 3 | Metal Shielding Bands Difficult to Work With |  |  |  | N | NO | <D> **** Detailed Description **** While banding the lead shielding installed in the RB 522' N Pipe Chase, the RMC Laborers had difficulties tightening the metal banding and it also would break if tightened too much. These difficulties meant more time spent in the area, which of course means more dose to perform the task. <I> **** Actions Taken **** Informed shielding coordinator. Recommend benchmarking to find an alternative product. | 02-00-R-BLDG-MISC
386572 | CR | 20181108 |  | 3 | TRB and 115 kV OCB Deluge PM not Scheduled Online or Outage |  |  |  | N | YES | <D> **** Detailed Description **** PMs for the Backup Transformer and associated Oil Circuit Breaker were looked at by a team to be evaluated for performance online or during refueling outages. The PM to perform deluge testing was not included in the list of PMs for the group to evaluate. Possibly missed due to the PM being associated with a work item and not an EPN. As of this CR, PM work order 02111575 PPM 15.3.14 TR-B DELUGE SYSTEM (D60) is coded RP 00, has a due date of 05/11/2019 and a late date of 05/15/2021. Reference: PMRQ 18296-04 TR-B (SYS 60) DELUGE TRIP TEST- Recommend evaluate if work order 02111575 PPM 15.3.14 TR-B DELUGE SYSTEM (D60) may be worked online during the upcoming TRB outage on March 1st 2019, during R24 or another online window prior to encroaching the late date. Recommend evaluation lead be assigned to Work Control with input from Operations, Fire Protection, Outage Management, Transformer Yard Coordinator and Maintenance. - <I> **** Actions Taken **** CR initiatorâ€™s initial input is the Deluge PM would adversely impact the March 1st 2019 TRB outage based upon scheduled scope conflicts and should be evaluated for R24 or a following online TRB outage. - Notified Supervision and Outage Management. <N> **** Equipment Description **** Fire Protection Deluge System for the Backup Transformer and 115 kV Oil Circuit Breaker
386574 | CR | 20181108 |  | 4 | OG Analyzer LEFT N2 bottle press less than min spec | N | N |  | N | YES | <D> **** Detailed Description **** while performing rounds it was noted that the OG Analyzer LEFT N2 bottle pressure was less than minimum spec. <I> **** Actions Taken **** Initiate CR and WR , inform CRS and recommend replacement. <N> **** Equipment Description **** TB 441 OG Analyzer LEFT N2 bottle | 02-00-OG-AY-12A,02-00-OG-AY-12B,02-00-OG-V-200
386575 | CR | 20181108 |  | 3 | AE did not upload native files to EWIP directory |  |  |  | N | NO | <D> **** Detailed Description **** Word versions of instrument master data sheets were not uploaded to EWIP directory for EC's 13417, 15499, 15502, CW vibration monitoring. <I> **** Actions Taken **** AE did not return call | 02-00-CW-M-P/1A,02-00-CW-M-P/1B,02-00-CW-M-P/1C,02-00-CW-P-1A,02-00-CW-P-1B,02-00-CW-P-1C
386576 | CR | 20181108 |  | 3 | LP Revision Process Does not Include Impact on Equivalencies |  |  |  | N | NO | <D> **** Detailed Description **** TDI-02 (Systematic Approach to Training) Lesson Plan revision process does not include assessment for impact on equivalent qualification relationships. Equivalent qualification relationships are defined in each section of the Qualification Directory and approved by the qualification owner and Training. Credit for the primary course can be granted based soley on the equivalent course relationship defined. If a Lesson Plan is revised changing the course objectives, equivalent qualifications are not reviewed to ensure the equivalency is still true. Recommend assignment to Training Support to determine scope and correct the issue. Recommend severity 3 <I> **** Actions Taken **** Notified Training Management
386577 | CR | 20181108 |  | 4 | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #25961 Biddle DLRO- model 247000 was NOT used during Calibration cycle. Rejected- No Longer Needed. DEF #6772A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
386585 | CR | 20181108 |  | 4 | Leak by into the Aux Boiler | N | N |  | N | YES | <D> **** Detailed Description **** Leak by continues into the Aux Boiler while the Seal Steam Evaporator B Feed System is in operation. <I> **** Actions Taken **** Wrote AR and WR for potential leaking CO valves and hung C-AUX-BOILER-002. Clearance provides instruction for venting when high pressure is observed. | 02-00-AS-BLR-1,02-00-CO-V-12,02-00-CO-V-21,02-00-CO-V-22,02-00-CO-V-24
386586 | CR | 20181108 |  | 3 | procedure enhancement PPM 1.3.84 |  |  |  | N | NO | <D> **** Detailed Description **** see EDMS
386587 | CR | 20181108 |  | 3 | ISP-EFC-B108 requires revision |  |  |  | N | NO | <D> **** Detailed Description **** Need to revise ISP-EFC-B108 to allow certain sections to be performed online. Email attached to EDMS with sections to be performed online. <I> **** Actions Taken **** Discussed revision with procedure writer and initiated CR.
386589 | CR | 20181108 |  | 4 | COND-FCV-41 position indication is wrong. | N | N |  | N | YES | <D> **** Detailed Description **** While investigating COND-FCV-41 open position indication per WR 29143832 it was discovered that the wiring for both the open and closed indicating lights and associated limit switches are not correct. EWD-69E-113 shows that while the valve is intermediate there should be dual indication. Instead, while the valve is intermediate there is no indication, both lights out. COND-FCV-43 was stroked to verify what the position indication showed while it stroke and it was dual while intermediate as EWD-69E-113 shows it should be. Please plan work to correct COND-FCV-41 position indication show that it works as drawn in the EWD. <I> **** Actions Taken **** Iinformed supervisor and wrote this AR/WR. <N> **** Equipment Description **** R426 N4/7.7 | 02-00-COND-FCV-41
386593 | CR | 20181108 |  | 4 | Safety related CWPH rm B104 diesel tk rm light is out. | N | N |  | N | YES | <D> **** Detailed Description **** The CWPH rm B104 diesel tk rm light is not working. <I> **** Actions Taken **** CRS notified, CR written. <N> **** Equipment Description **** CWPH rm B104 diesel tk rm. | 02-00-P-BLDG-MISC
386594 | CR | 20181108 |  | 3 | Procedure enhancement to SOP-SW-OPS |  |  |  | N | NO | <D> **** Detailed Description **** see EDMS
386598 | CR | 20181108 |  | 3 | MOT INFORMATION CUT OFF |  |  |  | N | NO | <D> **** Detailed Description **** MOT WAS SUBMITTED TO DOCUMENT CONTROL FOR PROCESSING. DOCUMENT CONTROL CANNOT PROCESS DUE TO INFORMATION WITHIN THE DOCUMENT BEING CUT OFF. <I> **** Actions Taken **** CR INITIATED, MOT WAS RETURNED TO OWNER FOR CORRECTIONS.
386604 | CR | 20181108 |  | 4 | Combustibles stored in Temporary Combustible Free Zone |  |  |  | N | NO | <D> **** Detailed Description **** There are many combustible items stored under the RB NW stairwell at the 422' level. This includes several quarts of oil, plastics, fabrics and tygon tubing. These need to be removed ASAP. <I> **** Actions Taken **** Notified SMgt, wrote CR. Notified maintenance supervisor to address. <N> **** Equipment Description **** RB 422 NW stairwell (outside RCIC and RHR A rooms). | 02-00-R-BLDG-MISC
386605 | CR | 20181108 |  | 3 | Asset Suite not updated with BS-PIC-18A replacement |  |  |  | N | NO | <D> **** Detailed Description **** The installlation history has not been updated for replacement of BS-PIC-18A per WO 02128896 (EWP). The work order is listed in the EPN history, but the installed UTC and serial number have not been updated. Recommend review by I/C Maintenance. | 02-00-BS-PIC-18A
386606 | CR | 20181108 |  | 3 | Exam Failure - ME000796 - Leak Path Sealing |  |  |  | N | NO | <D> **** Detailed Description **** One student failed the ME000796 - Leak Path Sealing exam conducted on 11/8/18. This CR is being written per direction of TDI-02, Rev 35, 4.4.10.p.3 <I> **** Actions Taken **** Informed training and line supervision.
386607 | CR | 20181108 |  | 4 | Chronic toxicity sample shipment delayed |  |  |  | N | NO | <D> **** Detailed Description **** For NPDES permit renewal CGS must perform quarterly chronic toxicity tests on CW. This test consists of 3 consecutive x20L samples (collected M,W,F) which are shipped overnight to a bioassay lab in Corvallis, Oregon for testing. The second sample in the series for 4Q-2018 chronic test was erroneously sorted by UPS and did not make it to the lab overnight. This does not invalidate the test but will be a deviation noted in the report. <I> **** Actions Taken **** Notified supervisor, attempted to get sample from UPS Seattle to UPS Corvallis, to no avail. Discussed issue with lab and determined that missed sample arrival will not ify test. Asked for refund from UPS. CR written for documenting/trending.
386609 | CR | 20181108 |  | 4 | Label for PSR-V-SR6/V13 is laying in the bottom of the SR |  |  |  | N | NO | <D> **** Detailed Description **** While observing work on CMS-SR-20 it was noted that the EPN label for PSR-V-SR6/V13 was laying in the bottom of the SR. Label needs to be reapplied to the appropriate valve. <I> **** Actions Taken **** Initiated CR and informed CRS <N> **** Equipment Description **** R548 - PSR-V-SR6/V13 | 02-00-PSR-SR-6,02-00-PSR-V-SR6/V13
386612 | CR | 20181108 | CAQ | C | SW-V-192 Missing and Loose Packing Nut | Y | Y |  | N | YES | <D> **** Detailed Description **** While lifting a clearance for RRA-CC-20 it was noted that one of SW-V-192's packing nuts was missing and the other was not tightened. <I> **** Actions Taken **** CRS informed, SW-V-192 was left CLOSED and not OPENED. | 02-00-RRA-CC-20,02-00-SW-V-192
386613 | CR | 20181109 | CAQ | D | Oscillograph start alarm due to 500KV grid | N | N |  | N | NO | <D> **** Detailed Description **** OSCILLOGRAPH STARTED alarm received due to 500KV Neutral Ground (J7 sensor) and SM-8 Undervoltage (J12 sensor). The sensor has been reset. BPA reports that the Ashe-Slatt 500KV line relayed off and back on. TR-S voltages are 237/238/238 kV and TR-B voltages are 1187117/117 kV respectively. All plant controllers and equipment exhibited normal operation
386614 | CR | 20181109 | CAQ | C | procedure enhancment OSP-INST-H101 |  |  |  | N | NO | <D> **** Detailed Description **** attachment 9.9 of OSP-INST-H101 which evaluates SR 3.6.4.1.1 does not take into account breach size as determined by TSP-RB-501. It is possible using this attachement to have a breach of secondary continment beyond the drawdown test limits and get an accepetable result. These breach sizes are controlled per PPM 1.3.57 and must be evaluated as part of secondary containment operability. | 02-00-R-BLDG-MISC
386615 | CR | 20181109 |  | 4 | COND-V-208C indicated dual position during BW opertions | N | N |  | N | YES | <D> **** Detailed Description **** COND-V-208C indicated dual position during BW opertions. <I> **** Actions Taken **** wr/cr | 02-00-COND-V-208C
386616 | CR | 20181109 |  | 4 | SEA-FN-51 Low Flow Alarm | N | N |  | N | YES | <D> **** Detailed Description **** The SEA-FN-51 low flow alarm is in at the HVAC panel in SB 456 fan room. Along with this, a smell of burnt rubber permeated the building. SEA-FN-51 is a roof-mounted exhauster. Please investigate and repair. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** SB roof. | 02-00-SEA-FN-51
386617 | CR | 20181109 |  | 4 | Flocculator stop filling early at a level of 25.5 | N | N |  | N | YES | <D> **** Detailed Description **** After backwashing the flocculator and letting it run on night shift it was noted that the flocculator had stopped and that PWC-TK-100 level was rather low for the demand. So the follow dayshift EO Restarted the flocculator and again it stopped about 2 hours later with a tank level of 25.5. when it should stop at a tank level of 30.8. Recommend recalibrating level transmitter. <I> **** Actions Taken **** initiate CR and WR, inform CRS. | 02-00-PWC-FU-1,02-00-PWC-LI-100,02-00-PWC-LT-100,02-00-PWC-TK-100
386618 | CR | 20181109 | CAQ | D | Received Oscillograph Started, H13-P800.C4.4-3, alarm | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm at 05:49 on 11/09/2018. BPA reports the cause was a momentary single phase opening on the Ashe-Slatt #1 500KV line with auto re-closure. 500 kV bus voltage at Ashe is 538 kV. Startup and Backup voltages are as follows: E-TR-S A: 236 kV B: 237 kV C: 237 kV E-TR-B A: 117kV B: 117kV C: 117kV The following sensors were tripped and are reset: J7 Sensor - 500kV Neutral Ground Overcurrent J11 Sensor - SM-7 Undervoltage J12 Sensor - SM-8 Undervoltage Plant controllers and equipment response was normal.
386619 | CR | 20181109 | CAQ | C | PRM-SR-1 critical fault / S/D | N | Y |  | N | YES | <D> **** Detailed Description **** PRM-SR-1 critical fault / S/D Normal flow indications on TG 501' hallwat instrument per chemist. Per ARP I7C needed for further investigation. | 02-00-PRM-SR-1
386620 | CR | 20181109 |  | 3 | change MT start process and save dose |  |  |  | N | NO | <D> **** Detailed Description **** SOP-MT-START step 5.2.7 tests extraction non return valves during turbine start. These tests should be done by latching the turbine when the plant is shut down as allowed by the new DEH system. This not only saves dose but also allows for needed repairs with less dose and prevents stalling out the Rx start up until repairs can be completed. Possible solution is to make it a W/O task and perform during outages (also forced outages as necessary) must be done quarterly if first startup. Supervision has refused to allow test to be completed in the past since we wer not on that step.
386621 | CR | 20181110 |  | 4 | Small Glycol leak from filter housing for GY-F-10A1 | N | N |  | N | YES | <D> **** Detailed Description **** A small glycol leak from the upper portion of were GY-F -10A1 connects. Wiped the glycol and it slowly began to bead up at connection portion. Level in tank was the same as last several readings. <I> **** Actions Taken **** Informed MCR. Wiped up leakage. | 02-00-GY-F-10A1
386622 | CR | 20181110 |  | 4 | CF-TK-43 digital reading displays E2. | N | N |  | N | YES | <D> **** Detailed Description **** The digital reading of CF-TK-43 was indicating E2. Prior reading was 986 gallons and trending slowly down (between 3 and 10 gallons per day). <I> **** Actions Taken **** Informed MCR. | 02-00-CF-LI-43,02-00-CF-TK-43
386623 | CR | 20181110 | CAQ | D | FDR-P-17 stopped when it should have remained running | N | N |  | N | YES | <D> **** Detailed Description **** While precoating FDR-FU-19 the Pprecoat sequence was finishing up and step 5.4.11-D-1 and D-2 had completed, the hold pump turned on and discharge valve opened. This was witnessed on G11-P001-1 in the RWCR. The operator exited the RWCR and proceeded to G11-P004 (FDR B/W and P/C panel) and after the 30 second timer the hold pump unexpectedly went off and its discharge valve when closed. The HOLD push-button on G11-P004 did not restart the hold sequence. The FDR filter STOP pushbutton on G11-P001-1 was pressed within about a minute of the probablem and the hold pump started and discharge valve opened. The hold pump was not suppose to stop when it did, if it is off for too long the filter will absolutely be lost. At this time with FDR iron problems the water volume in FDR-TK-22 is very problematic and having unnecessary backwash's only makes it worse. | 02-00-FDR-FU-19,02-00-FDR-P-17
386624 | CR | 20181110 | CAQ | D | DO-TK-1B low alarm in at 134.6 in with max 135 in. | Y | N |  | N | YES | <D> **** Detailed Description **** MCR recieved a DO-TK-1B low alarm with DO-LITS-10B reading 134.6 inches. The procedure has a Caution that reads "DO NOT intentionally fill DO-TK-1B above 135 inches. This minimizes chances of overfilling or 'Burping' the oil tank." This is a small margin from current level to the considerd full level with a transfer operation that 'coasts' after stopping. <I> **** Actions Taken **** MCR directed stopping transfer operation, istituted a 3 times a shift temp log to verify level, and CR written while evaluating sititation. | 02-00-DO-LITS-10B,02-00-DO-TK-1B
386625 | CR | 20181110 |  | 4 | Security Post 21A Camera System | N | N |  | N | YES | <D> **** Detailed Description **** The camera system at security post 21A is not functioning as designed. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Security notification made, initiated help request # IR -0035436 with telecom. <N> **** Equipment Description **** BRE Tower located NE of the security checkpoint
386630 | CR | 20181110 | CAQ | D | HT-HTP-FP/7 ckt 27F Low Temp Light Blinking | Y | N |  | N | YES | <D> **** Detailed Description **** HT-HTP-FP/7 ckt 27F Low Temp Light Blinking. This heat trace is for "18" spray pond blowdown line" This maybe related to the issue described in CR 386118 <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** SWPH-A | 02-00-HT-HTP-FP/7
386632 | CR | 20181110 |  | 4 | CW Chemical Pump CF-P-42B Found Not Pumping | N | N |  | N | YES | <D> **** Detailed Description **** During an inventory check to determine addition rate for CF-P-42B it was found that the inventory had not changed and the pump not pumping. This pump was switched to on Thursday 11/8/18 and had indication of flow. <I> **** Actions Taken **** Attachment 10.2 from PPM 12.14.3 was submitted to go back to CF-P-41B and increase pumping rate to maximum. TK-41 currently has only 648 gals, approximately five days of inventory. <N> **** Equipment Description **** CF-P-42B | 02-00-CF-P-42B
386633 | CR | 20181110 | CAQ | D | SW-V-153Z packing gland leak | Y | N |  | N | YES | <D> **** Detailed Description **** During leak check of RRA-CC-20 (02118085) outlet vent valve, found packing gland leak, 1-2 DPM, not part of the PMT <I> **** Actions Taken **** Reprorted to ops, WWM and maintenance, wrote CR and WR <N> **** Equipment Description **** R560 K9/9.0 | 02-00-RRA-CC-20,02-00-SW-V-153Z
386634 | CR | 20181110 |  | 3 | Gate locked by security for no known reason |  |  |  | N | YES | <D> **** Detailed Description **** The 471 west hallway between the turbine and RW buildings has a gate (as you walk east) that normally has 2 locks on it in series. One is a operations lock and the other was from the 467 tool crib. Beyond that gate there is some maintenance stuff and heating steam piping that operations periodically adjusts when heating steam is in service. It is a dead-end, there isnt any other way in/out of there. On the gate there is a sign that says contact the SSS to get the key. There are no security postings at all. Now a security lock going through the chain prevents access completely without security's presence. Security was contacted as to why and the response was that the reason was unknown and they will look into it next week but for now it stays as it is. This prevents operations from responding to heating steam transients in a timely manner. The security value of that lock is highly questionable. <N> **** Equipment Description **** 471 TB/RW hallway gate Gate was checked by security operations and lock was not identified as a security, however the lock was removed. No further actions required. | 02-00-W-BLDG-MISC
386635 | CR | 20181110 |  | 3 | Surveillance not reviewed by SRO | Y | N |  | N | NO | <D> **** Detailed Description **** Work order 02035897 included a surveillance ESP-MOVTL-B301 that was not reviewed by an SRO before the package as completed and sent to records. The surveillance test data are satisfactory. <I> **** Actions Taken **** CRS reviewed completed surveillance that was sent to records and signed entry out of control room log.
386636 | CR | 20181110 | CAQ | C | SJAE Condenser Rad High alarm | N | Y |  | N | YES | <D> **** Detailed Description **** Received P602-A5 drop 4-3 (SJAE Condenser Rad High) alarm. OG-RIS-612 Off Gas Pre-Treat Activity, indicates a change from approximately 38 mR/hr to 56 mR/hr and then returned to a normal reading over the next few minutes. Entered and exited ABN-OG. Notified the Shift Chemistry Technician. The Shift Chemistry Technician responded and adjusted the sample flow. <N> Fission gas sample for Xe-133, 135, 138, KR-85, 87, and 88 indicated a gross gamma activity rate @ 30 min did not change between november 1 and november 15. November 1 was 3.59E-02 milliCi/sec. November 15 was 3.53E-02 milliCi/sec. This supports no changes in fission gas (TS SR 3.7.5.1). This information is extra information associated with the alarm but was not required. | 02-00-OG-RIS-612
386637 | CR | 20181110 |  | 3 | Surveillance not reviewed by SRO | N | Y |  | N | NO | <D> **** Detailed Description **** Work order 02135598 included a surveillance 10.27.31 that was not reviewed by an SRO before the package as completed and sent to records. The surveillance test data are satisfactory. <I> **** Actions Taken **** CRS reviewed completed surveillance that was sent to records and signed entry out of control room log.
386638 | CR | 20181110 |  | 4 | CO-TK-1 level low alarm with low level. | N | N |  | N | YES | <D> **** Detailed Description **** CO-TK-1 low level was recieved. Level was 1/3 of tank. Lineup was correct, made up with demin bypass valve. Possible level control valve sticking. <I> **** Actions Taken **** Restored tank level. Monitored and verified normal LCV was maintaining level. Informed MCR. Increased tank level monitoring. | 02-00-CO-TK-1
386639 | CR | 20181110 |  | 4 | Operator stung by wasps in TMU Pumphouse |  |  |  | N | NO | <D> **** Detailed Description **** An operator was stung multiple times by wasps inside the TMU pumphouse. Recommend spraying inside the building to remove the wasps. <I> **** Actions Taken **** Wrote CR. <N> **** Equipment Description **** Inside TMU Pumphouse | 02-00-M-BLDG-MISC
386640 | CR | 20181111 | CAQ | D | Essential Fire Door not closing as required by 15.1.2 | N | Y |  | N | YES | <D> **** Detailed Description **** Door R-DOOR-R408 did not close during step 7.1.3 of 15.1.2. Please fix. <I> **** Actions Taken **** Wrote CR. Opened Barrier Impairment 18-0501. Verified Door R-408 is on LCS-18-FIRE DOORS-001. | 02-00-R-DOOR-R408
386641 | CR | 20181111 |  | 3 | SOP-RCC-START Procedure Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** 1. Copy the note that is before step 5.2.4.c to before step 5.1.4.d also. 2. Change step 5.1.4.e to match wording in other parts of procedure: WHEN RCC-V-6 closes, THEN OPEN RCC-V-6 (H13 -P825). <I> **** Actions Taken **** Wrote CR. | 02-00-RCC-V-6
386642 | CR | 20181111 |  | 4 | Steam return line to WHCO-CU-1 has a pipping leak. | N | N |  | N | YES | <D> **** Detailed Description **** In RW437 above FDR-P-21 on the steam return line to WHCO -CU-1 steam is spraying from a through wall leak in the piping. The steam spray is 2 feet in length and is condensing on nearby piping. The condensed water is dripping at a rate of around 10 drops/second and is pooling on the ground below. The puddle on the floor is around 8 feet in diameter and is encroaching on the step off pad of a nearby contaminated area. Radiation protection took smears of the water on the floor and said it was currently clean. This issue was written up earlier this year (AR 377988 WR 29141035) when there was lagging on the steam piping. The lagging has since been removed and the catch devices that contained the dripping from the lagging are no longer effective. <I> **** Actions Taken **** Informed CRS and wrote CR | 02-00-WHCO-CU-1
386643 | CR | 20181111 |  | 4 | Turbine HVAC and aux boiler heating steam leaks | N | N |  | N | YES | <D> **** Detailed Description **** There are numerous small packing leaks on valves on the steam traps in the turbine and aux boiler steam HVAC systems and piping. HCO-V-T1CA and 4-5 other components have small leaks that care easily identified on TOA-HV-1A. On the aux boiler heating steam side HCO-V-T13D and HS-V -T53 have light steam leaks. After admitting steam to TOA -HV-1B, 2 steam leaks were identified in the heating tubes. They both appeared to be previous leaks but the crimping didn't hold. They are the first and second tubes immediately above the horizontal C-channel that sits between 3 and 4 feet off the ground inside the unit. Heating steam was secured by means of closing TOA-RMS-31B to TOA-HV-1B. It would be a good idea to send craft on a walkdown to adjust packing as needed/allowed on the numerous small heating steam valves that are leaking. <N> **** Equipment Description **** . | 02-00-HCO-V-T13D,02-00-HCO-V-T1CA,02-00-HS-V-T53,02-00-TOA-HV-1B
386644 | CR | 20181111 |  | 4 | Steam leak WOA-HV-1 | N | N |  | N | YES | <D> **** Detailed Description **** Steam leak in heating coil WOA-HV-1 <I> **** Actions Taken **** Isolated coil , shut HS-V-W9O, HCO-V-W9BB and opened drain HCO-V- W9BD | 02-00-HCO-V-W9BD,02-00-HS-V-W9O,02-00-WOA-HV-1
386645 | CR | 20181111 |  | 4 | Steam leak from pipe wall near WHCO-CU-1. | N | N |  | N | YES | <C> Duplicate of CR 386645. 4/Trend <D> **** Detailed Description **** 3 foot steam plume from pipe wall hole near elbow bend directly above FDR-P-21. It is downstream from WHCO-CU-1 past HCO-V-51 up and across room to the elbow above FDR-P -21 going up. <I> **** Actions Taken **** Isolated steam to RW BLDG per SOP-COLDWEATHER-OPS section 6.4.4.a. leak has stopped. HP informed, water cleaned up. | 02-00-WHCO-CU-1
386646 | CR | 20181111 | CAQ | D | Door T118 | N | N |  | N | YES | <D> **** Detailed Description **** Door T118 is not functioning as intended. Contact Security at 2185 for details. <I> **** Actions Taken **** Notified S/M, contacted Electrical Maintenance, generated CR/WR. | 02-00-T-DOOR-T118
386647 | CR | 20181111 |  | 4 | TOA-HC-1B Heating coil "O" steam leak | N | N |  | N | YES | <D> **** Detailed Description **** TOA-HC-1B Heating coil "O" has a steam leak (~ 2ft plume). The "O" heating coil has been isolated and drained. A Local Tagout will be generated by the MCR for Configuration Control. Please repair/plug as necessary. <I> **** Actions Taken **** Informed MCR. Isolated and drained heating coil "O" <N> **** Equipment Description **** Turbine 501 E | 02-00-TOA-HC-1B
386648 | CR | 20181111 |  | 4 | TOA-TIS-24B has failed and does not operate properly | N | N |  | N | YES | <D> **** Detailed Description **** TOA-TIS-24B has failed. The setpoint adjustment knob no longer moves the setpoint needle. Additionally, TOA-TIS -24B indicated temperature is grossly inaccurate. See attached EDMS for Pic of TOA-TIS-24B indicated temp compared to TOA-TIS-24A. TOA-TIS-24B is required to allow heating steam to be admitted to TOA-HC-2A steam coils. <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** TG 501 W, at TBHV 2A | 02-00-TOA-HC-2A,02-00-TOA-TIS-24B
386649 | CR | 20181111 |  | 3 | SOP-COLDWEATHER-OPS for CW to change door closure |  |  |  | N | NO | <D> **** Detailed Description **** SOP-COLWEATHER-OPS for CW to change door closure setting following damper closure per step 6.1.16 of SOP -COLDWEATHER-OPS. Refer to WO#02102566-14 <I> **** Actions Taken **** Initiated CR/WR <N> **** Equipment Description **** Change door closure setting at CW pump house.
386650 | CR | 20181111 |  | 4 | SOP-COLDWEATHER-OPS ROA Heating Steam Coil Isolation | N | N |  | N | YES | <D> **** Detailed Description **** During performance of SOP-COLDWEATHER-OPS, ROA HVAC was entered to inspect heating steam coils and a leak was found. HS-V-R7N was shut to isolate the leak, and HCO-V -R7DD blowdown valve was opened. Subsequent investigation revealed the leak was isolated with this action. Request a work order and local clearance be generated to drain and repair the leak on the N coil. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** ROA HVAC unit RB 572' | 02-00-HS-V-R7N,02-00-ROA-HC-1
386651 | CR | 20181111 |  | 4 | Plant telephone not working | N | N |  | N | YES | <D> **** Detailed Description **** There is a plant telephone not working in the Radwaste building. Extension 2558 in the corridor on 467 elevation has no dial tone. Plugging an external phone into the wall jack also showed no dial tone. <I> **** Actions Taken **** Tried emailing TELECOM 10-26-2018 with no response <N> **** Equipment Description **** Plant phone RW 467 corridor
386652 | CR | 20181111 |  | 4 | TSW-TI-10AG greater than 120 deg F | N | N |  | N | YES | <D> **** Detailed Description **** The temp instrument TSW-TI-10AG is taken shiftly, its a H2 HX TSW outlet temp gauge. Normal band is >120 deg F but at 100% power it normally sits at 119-120 degrees F. The other heat exchangers (4 total) have more margin and the respective temperatures are as low as 96 deg F. On operator logs the instument in question showed 121 deg F, so it was aobve the normal band. This CR is for trending. <I> **** Actions Taken **** Informed CRS. <N> The controller TSW-TIC-9 has been adjusted many times and is controlling on the warm side. WO 02095467 will repalce this controller in R24. Current temperatures are within the generator capabilities and are not a problem. | 02-00-TSW-TI-10AG
386653 | CR | 20181111 | CAQ | D | (NRC) SL-71 GFIP has broken light covers | Y | N |  | N | YES | <D> **** Detailed Description **** SL-71 has several broken plastic light bulb covers. All lights are lit, indicating continuity in the respective circuits. <I> **** Actions Taken **** Wrote CR. Could not locate identical replacement covers. | 02-00-E-SL-71
386654 | CR | 20181112 |  |  | Camera cleaning |  |  |  | N | YES | <D> **** Detailed Description **** Following cameras needing cleaning. CCTV4, CCTV7, CCTV8, CCTV10, CCTV12, CCTV13, CCTV14, CCTV28, CCTV29, CCTV32, PTZ39 <N> **** Equipment Description **** Varias cameras located inside the PA, notify security prior to work
386655 | CR | 20181112 |  |  | Camera Cleanining needing to be cleaned |  |  |  | N | YES | <D> **** Detailed Description **** Following cameras need cleaning: CCTV4,CCTV7,CCTV8 ,CCTV10,CCTV12,CCTV13,CCTV14,PTZ28,PTZ29,CCTV32,PTZ39 <N> **** Equipment Description **** Cameras needing cleaning within the protected area. contact security prior to work
386656 | CR | 20181112 | CAQ | D | R-DOOR-R305 â€“ Door Handle not Latching | Y | N |  | N | YES | <D> **** Detailed Description **** R-DOOR-R305 is on the Rx 501 NW on the Rx Building side. The mag lock that enforces the interlock between R-DOOR -R305 and R304 is functional. There is no secondary containment concern. R-DOOR-R305 is not in LCS 1.10.5 (See CR 376590). This issue has been written up twice and work requests closed with no work performed see WR 29139451 and WR 29141035. DO NOT Close this work request without work performed this door must work in all Reactor building dP conditions. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RX 501 NW Airlock Door | 02-00-R-DOOR-R305
386660 | CR | 20181112 |  | 4 | Undeclared Alcohol at the Security Checkpoint |  |  |  | N | NO | <D> **** Detailed Description **** At approximately 0645, 1 non-badged visitor with Org Code 84000 arrived at the Security Checkpoint with undeclared alcohol. <I> **** Actions Taken **** Security Supervision, Shift Manager, and Benton County Sheriff's Office were notified. BCSO did not respond and individual was denied access.
386661 | CR | 20181112 |  | 4 | M&TE Suspended until Needed | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0059964 Biddle DLRO- model 247000 Passed Calibraiton- But Now Suspended until Needed. DEF #6774A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
386662 | CR | 20181112 |  | 4 | WOA-FN-9 | N | N |  | N | YES | <D> **** Detailed Description **** WOA-FN-9 is making a sound like the belts are bad and seems to be shaking excessively .. <I> **** Actions Taken **** told my suppervisor and wrote the CR. <N> **** Equipment Description **** On 507 next to chiller. | 02-00-WOA-FN-9
386663 | CR | 20181112 |  | 4 | CO-V-64B leaking | N | N |  | N | YES | <D> **** Detailed Description **** CO-V-64B, suction strainer drain for CO-P-2B, is currently leaking at a 6 drop/min rate. This valve has an open chicago fitting at the end, which is where the leak is coming from. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** TG 441 E Aux Boiler Room | 02-00-CO-V-64B
386664 | CR | 20181112 | CAQ | D | TG 501W CO2 Hose Reel Red Light Out | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The normally on red light for the TG 501W CO2 hose reel is currently out. Recommend replacing light bulb or investigating for failure. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** TG 501 W CO2 Hose Reel
386665 | CR | 20181112 |  | 3 | TSW-TI-10AG High OOS | N | N |  | N | NO | <D> **** Detailed Description **** TSW-TI-10AG is currently reading 122 F, with a max of 120 F per the OPS3 logs. Previously written up high at 121 F. CR written for trending purposes. <I> **** Actions Taken **** Initiated CR | 02-00-TSW-HX-7A,02-00-TSW-TI-10AG
386666 | CR | 20181112 | CAQ | C | (QA) Inadequate Parts Traceability Documentation in WO | Y | Y |  | Y | NO | <D> **** Detailed Description **** (QA) Work Order (WO) Task 02085978-01 installed a Quality Level 1 orifice but failed to retain the issue ticket and acceptance tag in the quality record. Additionally a UTC was not updated for an installed flow element. Incomplete parts tracking documentation could result in a loss of traceability required by 10 CFR 50 Appendix B and Columbiaâ€™s OQAPD. See EDMS for detailed description <I> **** Actions Taken **** This was identified as a Deficiency during the Materials Management Audit, AU-MM-18. Informed Quality, Supply Chain Services, and Maintenance Management, recommend assignment to Maintenance <N> Williams Plant Services work.
386667 | CR | 20181112 | CAQ | C | (QA) Stainless Steel Interacting with Carbon at Warehouse |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) One example was identified where stainless steel piping stored outdoors at the warehouse was in contact with a carbon steel rack contrary to procedural requirements in SWP-MMP-02, Warehousing. Storing stainless steel in this manner can cause degradation of the material potentially challenging the ability of the SSC to perform its function over its intended lifespan when installed. See EDMS for detailed description <I> **** Actions Taken **** This was identified as a Deficiency during the Materials Management Audit, AU-MM-18. Informed Quality, and Supply Chain Services, recommend assignment to Supply Chain Services.
386668 | CR | 20181112 | CAQ | C | UTC information not consistently updated in Asset Suite |  |  |  | N | NO | <D> **** Detailed Description **** This is an Asset Suite configuration control issue only and does not affect plant equipment. Uniquely Tracked Commodity (UTC) information ties the actual Manufacturer, Model Number, and Serial Number of a component to a particular EPN, to reflect installed plant equipment in Asset Suite. Since 2008 there have been at least 13 separate CRs (see cross references) written concerning UTC information in Asset Suite being incorrect (UTC not installed/removed on D034 panel). Maintaining accurate and up-to-date UTC information in Asset Suite is necessary to maintain configuration control of our equipment data. This is important information for OER searches, Part 21 notices, generic issues, and determining obsolescence information for our equipment. . Extensive actions taken under AR-CR 181641 to ensure UTC data is being updated has not been effective. AR-CR 386605 was written 11/8/18 documenting an example of how Asset Suite was not updated when BS-PIC-18A was replaced under WO 02128896; UTC 551696 should have been installed but was not. I was able to quickly identify three more examples of UTC information not being updated: UTC 546808 was not installed (fitted) in RCIC-42-S21A9C as a part of WO 02072926, UTC 550598 was not installed (fitted) in COND-V -260D as a part of WO 02050982, and UTC 550602 was not installed (fitted) in COND-V-260E as a part of WO 02127712. . MI-3.6.4 gives direction to Craft supervisors to ensure UTC information is updated in Asset Suite as a part of the work order process; however, these instructions seem to not be rigidly followed. Note that in two of the referenced examples (WO 02050982 and 02127712), Maintenance Planning did not include steps in the work instructions to document the replacement UTC information, contrary to their desktop guide which may have contributed to the UTC information not being updated. The underlying issue seems to be a gap in understanding the UTC update process and ownership responsibility. . Recommend Craft Supervisors and Maintenance Planning work together to ensure process and/or training gaps regarding UTC updates are bridged AND that the previously mentioned UTC information for RCIC-42-S21A9C, COND-V-260D, and COND -V-260E be corrected. <I> **** Actions Taken **** Discussed with Craft Supervisor, Maintenance Planning Supervisor and Procurement Engineering. Performed a CR search for past UTC information update issues; provided cross references to AR type CRs; however, there are many others that are AR type ITSR . Identified current examples of UTC information not being updated; these examples require action/update as a part of this CR. | 02-00-COND-V-260D,02-00-COND-V-260E,02-00-RCIC-42-S21A9C
386669 | CR | 20181112 | CAQ | D | LEVEL 1 FILING ERROR IN THE TSC |  |  |  | N | NO | <D> **** Detailed Description **** DOCUMENT CONTROL PERSONNEL MISFILED A LEVEL 1 PROCEDURE WITHIN THE TSC. THE ERROR WAS CAUGHT DURING THE PERFORMANCE OF A WEEKLY AUDIT. <I> **** Actions Taken **** LEVEL 1 PROCEDURE WAS FILED IN CORRECT TAB AND THE PROCEDURE THAT WAS REMOVED WAS REPLACED. SUPERVISION WAS INFORMED AND CR WAS ISSUED.
386670 | CR | 20181112 | CAQ | C | (QA) Materials stored on ground at Warehouse |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Multiple examples were identified where materials stored outside at the Warehouse were either stored on or touch the ground contrary to procedural requirements in SWP-MMP-02, Warehousing. Storing materials in this manner can cause premature degradation rendering it unusable or challenging the ability of the SSC to perform its function over its intended lifespan. See EDMS for detailed description <I> **** Actions Taken **** This was identified as a Deficiency during the Materials Management Audit, AU-MM-18. Informed Quality and Supply Chain Services, , recommend assignment to Supply Chain Services.
386671 | CR | 20181112 |  | 4 | CF-P-41B was found to not be pumping on 11/12/18 | N | N |  | N | YES | <D> **** Detailed Description **** CW scale dispersant pump CF-P-41B was found to be not pumping based on the inventory not changing over the last 24 hours. Usage rate is approximatekly 75 gals/day. Over the weekend CF-P-42B was found not to be pumping. Current tank inventories are TK-41 (607 gals) and TK-42 (4601 gals). Shift manger has been alerted to this situation. <I> **** Actions Taken **** A request has been made to setup and manually feed 150 gals of the DVS3A002 dispersant to the CW basin. Attachment 10.3 of PPM 12.14.3 has been sent to the Control Room for action. Daily manual additions may be required until a pump is functional on TK-42. <N> **** Equipment Description **** CW Chemical Pumps CW-P-41B | 02-00-CF-P-41B
386672 | CR | 20181112 | CAQ | C | (QA) Materials Stored without Equal Weight Bearing |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Multiple examples were identified where materials at the Warehouse were stored in a manner where the rack or shelves were not equally supporting the weight of the material, contrary to procedural requirements in SWP-MMP -02, Warehousing. Storing materials in this manner can cause distortion of the material potentially challenging its integrity or the ability of the SSC to perform its function over its intended lifespan. See EDMS for detailed description <I> **** Actions Taken **** This was identified as a Deficiency during the Materials Management Audit, AU-MM-18. Informed Quality and Supply Chain Services, recommend assignment to Supply Chain Services.
386673 | CR | 20181112 | CAQ | C | (QA) Non-Conforming Cables Not Controlled As Required (ARMA) |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Over 100 spools of electrical cabling stored outdoors at the warehouse are known to be improperly stored and significantly deteriorated, however procedural requirements to identify and segregate the cabling as Non-Conforming have not been carried out as required by SCSI-5.4, Control and Disposition of Non-Conforming Material. Additionally, the majority of the cable spools are not labeled which results in a loss of traceability as required by SWP-MMP -02, Warehousing. See EDMS for detailed description <I> **** Actions Taken **** This was identified as a Area Requiring Management Attention (ARMA) during the Materials Management Audit, AU-MM-18. Informed Quality and Supply Chain Services, recommend assignment to Supply Chain Services.
386675 | CR | 20181112 | CAQ | C | (QA) Inadequate Guidance for Warehouse Humidity Levels |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The guidance in SWP-MMP-01, Control of Ageable Items, for maintaining warehouse humidity levels to ensure unlimited shelf life of elastomers is not specific and open to interpretation. A review of the previous 21 months identified multiple occasions where the 60% humidity was exceeded, with one occasion lasting 156 hours, which could easily be interpreted to either meet or exceed the criteria currently in SWP-MMP-01. Failure to maintain humidity levels appropriately could ify the allowance for an unlimited shelf life as intended by MWES-1, â€œPart 1 â€“ Polymers, Subpart 1B â€“ Guidelines On The Use Of Polymer Materials.â€ See EDMS for detailed description <I> **** Actions Taken **** This was identified as a Deficiency during the Materials Management Audit, AU-MM-18. Informed Quality and Supply Chain Services, recommend assignment to Supply Chain Services.
386677 | CR | 20181112 | CAQ | C | (QA) SWP-MMP-02 Doesnâ€™t Ensure OQAPD Requirements Met |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) SWP-MMP-02 Warehousing, does not contain the requirements for five elements of OQAPD-01, Operational Quality Assurance Program Description section 15.2 and 5.3 as required by SWP-PRO-04, Nuclear Procedure Program. All OQAPD-01 section 15.2 requirements not in SWP-MMP-02 are provided in associated department instructions. See EDMS for detailed description <I> **** Actions Taken **** This was identified as a Deficiency during the Materials Management Audit, AU-MM-18. Informed Quality and Supply Chain Services, recommend assignment to Supply Chain Services.
386678 | CR | 20181112 | CAQ | C | (QA) No Process to Control QL 1-3 Items With Removed Parts |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Columbia Generation Station does not have a process to control Quality Level 1, 2, or 3 issued items that have had subcomponents removed to prevent installation as a fully conforming item. A lack of consistent control elevates the risk that an item missing subcomponent(s) could be inappropriately installed in the plant causing challenges to operability and rework due to failed functional/post maintenance testing. See EDMS for detailed description <I> **** Actions Taken **** This was identified as a Deficiency during the Materials Management Audit, AU-MM-18. Informed Quality, Supply Chain Services, and Maintenance. Recommend assignment to Maintenance.
386679 | CR | 20181112 | CAQ | C | Elevated corrosion rates in open cooling systems | Y | N |  | N | NO | <D> **** Detailed Description **** Short-term corrosion coupons were removed from TSW, CW, and SSW systems on 9/12/2018. Corrosion rates of individual metal samples were calculated by mass loss and expressed relative to the exposure time as mils per year (mpy). Corrosion coupons are used to assess long-term trends or adverse effects from changes in system chemistry. A synopsis of results follows. The following carbon steel and cast steel materials exceeded the EN criteria of 2.0 mpy after 91-days of exposure: TSW2-hot leg C1010 (11.12 mpy), A106GrB (12.22 mpy) CW A36 (5.63 mpy) SSW C1010 (4.05 mpy) and A36 (4.77 mpy). The corrosion rates for the following copper alloys exceeded the EN criteria of 0.2 mpy after 91 days of exposure: TSW2-hot leg CDA706 copper-nickel alloy (0.44 mpy); SSW CDA122 (0.41 mpy) and CDA443 admiralty brass (0.42 mpy). These values have exceeded the EN criteria in the past. <I> **** Actions Taken **** Notified chemistry specialist. Recommend assignment to chemistry. Full corrosion coupon report is provided in EDMS docs. | 02-00-CW-PIPE-MISC,02-00-SW-PIPE-MISC,02-00-TSW-PIPE-MISC
386680 | CR | 20181112 | CAQ | B | (QA) Ineffective CAs for Contracts Process (Finding) |  |  |  | Y | NO | <C> RISK: Medium (B) CAUSE: Clear - Document known Cause and create Corrective Actions. <D> **** Detailed Description **** (QA) Ineffective Corrective Actions for Contracts Process (QA) Actions to address a Quality identified weakness from the 2016 Materials Management Audit were ineffective. The 2016 weakness identified that the contracting process was not obtaining required Certificates of Conformance from Suppliers on Safety-Related (SR) contracts. Actual consequences are ten of twelve SR contract files closed in the last 19 months did not contain a Supplierâ€™s Certificate of Conformance, contrary to contract requirements. Closing contracts without receipt of the Supplierâ€™s Certificates of Conformance removes a barrier ensuring services provided conform to ENâ€™s contract requirements. This is a repeat issue from the 2016 Materials Management audit, where Quality initiated AR-CR 357980 â€œ(QA) No Process to Verify Certs of Conformance for Contractsâ€, which was a Condition Adverse to Quality (CAQ). <I> **** Actions Taken **** This was identified as a Finding during the Materials Management Audit, AU-MM-18. Informed Quality and Supply Chain Services, recommend assignment to Supply Chain Services. <N> The certificate of conformance issue cause is known. Causes are 1) Failure to follow desktop instructions for closeout of safety related contracts. 2) Lack of utilization of contract file index closeout form which requires the certificate of conformance inclusion in the closeout documentation. Current corrective actions completed have been an organization stand down with all contracts personnel. An email sent on 11/2/2018 to all contracts personnel which states â€œEffective immediately part of the closeout process for all safety related or augmented quality contracts (Q level 1, 2 or 3) a one over one review is required by the contracts supervisor prior to closeout completion, no exceptions. with aknwoledgement received.
386681 | CR | 20181112 | CAQ | C | (QA) No Process to Verify Receipt of CofC for AQ Contracts |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) There is no existing process to verify receipt of a Supplierâ€™s Certificate of Conformance when required for Augmented Quality (AQ) contracts. One actual consequence is a Supplierâ€™s Certificate of Conformance was not found in the closed Augmented Quality (AQ) contract file 339422 â€œDesign Fabricate and Deliver Stack Monitor Systemâ€, contrary to contract requirements. According to the approved Services Evaluation, this contract was AQ because the work must meet Regulatory Guide (RG) 1.97 â€œCriteria for Accident Monitoring Instrumentation for Nuclear Power Plantsâ€. See EDMS for detailed description <I> **** Actions Taken **** This was identified as a Deficiency during the Materials Management Audit, AU-MM-18. Informed Quality and Supply Chain Services, recommend assignment to Supply Chain Services. <N> CR reopened at the request of the owed to group.
386685 | CR | 20181112 | CAQ | D | (QA) Incorrect QAR File Number for Contract |  |  |  | Y | NO | <C> Supervisor initiated a data modification to correct the error and index the contract as Type: QAR, Subtype: ADM, and contract number â€œ342789â€. The record with the incorrect document number â€œ3342789â€ was deleted, and the record has now been indexed under the correct document number â€œ342789â€. <D> **** Detailed Description **** (QA) Incorrect Quality Assurance Record (QAR) file indexing number used for Safety-Related (SR) Contract 342789 due to data entry error, which includes releases 19 and 20 with associated amendments. The potential consequence is it is more difficult to retrieve a QAR when filed using an incorrect file indexing number. See EDMS for detailed description <I> **** Actions Taken **** This was identified as a Deficiency during the Materials Management Audit, AU-MM-18. Informed Quality and Supply Chain Services, recommend assignment to Supply Chain Services.
386686 | CR | 20181112 |  | 3 | (QA) Conflicting Critical Component Criteria in Procedures |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) SYS-4-42, Critical Spares Process, contains a critical and non-critical component criteria different than provided in PPM 1.5.13, Preventive Maintenance Optimization Living Program. PPM 1.5.13 was revised in 2016 to the AP-913 criteria, which created the difference between the procedures. Station components are currently categorized by the PPM 1.5.13 criteria. See EDMS for detailed description <I> **** Actions Taken **** This was identified as a Deficiency during the Materials Management Audit, AU-MM-18. Informed Quality, Supply Chain Services, and Engineering, recommend assignment to Engineering
386691 | CR | 20181112 |  | 4 | XD-05 Requires Maintenance |  |  |  | N | YES | <D> **** Detailed Description **** SEC-XD-05 requires maintenance. Contact X2185 for more information. <I> **** Actions Taken **** Security Supervision notified. XD placed out of service. I&C Supervisor notified to coordinate work. | 02-00-SEC-XD-5
386692 | CR | 20181112 | CAQ | D | FP-V-189 leaking past its seat | N | Y |  | N | YES | <D> **** Detailed Description **** While attempting to do a calibration check on FP-PI-9 (WO 02116254-01) we found the local isolation valve FP-V-189 would not completely isolate. This caused our test pressure to leak past the valve and made it impossible to perform the calibration check. <I> **** Actions Taken **** Notified supervision | 02-00-FP-V-189
386693 | CR | 20181112 | CAQ | D | LEVEL 1 FILING ERROR IN TSC |  |  |  | N | NO | <C> Duplicate of CR 386669. <D> **** Detailed Description **** DOCUMENT CONTROL PERSONNEL MISFILED A LEVEL 1 PROCEDURE WITHIN THE TSC. ERROR WAS CAUGHT DURING THE PERFORMANCE OF A WEEKLY AUDIT. <I> **** Actions Taken **** LEVEL 1 PROCEDURE WAS FILED IN THE CORRECT PLACE AND THE PROCEDURE THAT WAS REMOVED WAS REPLACED. SUPERVISION WAS NOTIFIED AND CR WAS ISSUED.
386694 | CR | 20181112 |  | 4 | Damaged electrical outlet Turbine Bldg 501 | N | N |  | N | YES | <D> **** Detailed Description **** LP-8EC-13 2 plug electrical outlet is damaged. The top half of the receptacle is broken and not usable. This is the electrical outlet between door C422 (electrical chase) and C409 (Control Room). <I> **** Actions Taken **** Wrote this CR with a work request. Suggest Electricans replace outlet asap. <N> **** Equipment Description **** LP-8EC-13 Electrical outlet | 02-00-T-BLDG-MISC,02-00-W-BLDG-MISC
386695 | CR | 20181112 |  | 3 | CC-162 (NON EN/CGS) Data Report listed wrong unit of measure |  |  |  | N | NO | <D> **** Detailed Description **** Customer called with questions regarding the certificate of calibration that was received with their torque wrench, as it was in the units of measure (uom) of newton meters (nm) and not foot/pounds (ftlb) as the torque wrench is labeled. Recommend assign to AR-CALSERV category 3 <I> **** Actions Taken **** Units of measure determined to be consistent with data in database but unit recalled for recalibration and restored confidence of data.
386696 | CR | 20181112 | CAQ | C | Need 10.25.136 revised (missing information) |  |  |  | N | NO | <D> **** Detailed Description **** Need 10.25.136 revised (missing information). Added markups and information to EDMS.
386699 | CR | 20181112 |  | 4 | CW Scale Dispersant - O-Phosphate Below Target | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** CW Dispersant residual ortho-phosphate test for 11/12/18 was below target limits. Target is 5 to 9 mg/L. Test result was 3.37. This was caused by the failure of the chemical feed pump. See CR 386632 and CR 386671. Manual feed of dispersant has been started to bring the residual up to target. CR's listed above are for action to repair the chemical feed pumps. This CR is for trending only. <I> **** Actions Taken **** Manual feed of the dispersant was started 11/12/18 to bring the residuals up to target levels. Chemistry Management was informed of the trend.
386700 | CR | 20181112 |  | 3 | TSW-HX-9 end bell oil leakage | N | N |  | N | YES | <D> **** Detailed Description **** The west end of TSW-HX-9, HX in the seal oil system, is leaking more oil than normal. This CR is written for trending and investigation purposes. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** TG 441 W Seal Oil Skid | 02-00-TSW-HX-9
386701 | CR | 20181112 |  | 4 | WOA-FN-9 damaged ducting on motor mount | N | N |  | N | YES | <C> Duplicate of CR 386662 <D> **** Detailed Description **** WOA-FN-9 (counting room fan) has had two other CR's written recently due to noise and vibration. It has now been identified that the motor mount for the fan attaches to the ducting, and this ducting is damaged where it attaches. There is at least 6 positively identified inches (likely a few more) of sheared ducting due to the fan and with the vibration as bad as it is (has been getting noticably worse) the damage will get worse. EDMS has several attached photos and a video of the vibration. <I> **** Actions Taken **** Informed CRS <N> **** Equipment Description **** 507 RW | 02-00-WOA-FN-9
386702 | CR | 20181113 |  | 4 | RFT-LOC-1B heater would not fill with oil | N | N |  | N | YES | <D> **** Detailed Description **** While taking operator rounds it was observed that RFT-LOC -1B "oil temp low, heater overtemp, and alarm" amber lights were lit. The alarms were reset, but the heater on light was not illuminated with temperature on RFT-TI-7B at 92 degrees F. The lube oil conditioner was shut down and subsequently restarted up to the portion of the procedure that involves filling the LOC heater (SOP-LO-START step 5 .3.5). The heater vent valves were cycled for 10 minutes, but no oil was observed in the cylindrical sight glass downstream of the vent valves. The LOC was then shut down. <I> **** Actions Taken **** Wrote CR and informed CRS. | 02-00-RFT-LOC-1B
386710 | CR | 20181113 |  | 3 | Incorrect scope for CCH-CR-1A electrical work |  |  |  | N | NO | <D> **** Detailed Description **** 02100874-06 CCH-CR-1A Electrical Inspect Chiller PM Tied to PM Requirement 00000721-15 A01 Mechanical PM CCH -CR-1A, Replace Chiller Oil & Filter MOT-CHILL-1-1 A01 Scope: Replace the Chiller Oil and Oil Filter, Cut open and inspect filter for foreign materials and wear products, Change purge unit oil filter-drier, Replace oil educator filter, Replace filter drier in motor cooling line, Replace refrigerant filter driers, Clean drip leg on educator nozzle oil return system, Remove screwed cap on the bottom of the drip leg on the refrigerant vet line and drain any moisture from the system. Check for leaks (refrigerant, oil and water). No electrical scope under MOT A01. Current Electrical task has Checking oil heaters and meggering compressor from SL-71 cubicle. <I> **** Actions Taken **** Work Order Returned to Planning. Notified Work Week manager. Planning Supervisor notified. Electrical Component Manager Informed. | 02-00-CCH-CR-1A
386712 | CR | 20181113 |  | 4 | Challlenge meeting not completed by end of T4 |  |  |  | N | NO | <D> **** Detailed Description **** RHR-SYS-A challenge meeting was not completed by the end of T4 as required. This was due to not all work orders being at the correct status (READY). <I> **** Actions Taken **** Rescheduled challenge meeting to T3 and held a 'readiness/scheduling meeting in its place. <N> **** Equipment Description **** N/A
386713 | CR | 20181113 |  | 3 | CAS Radio console time different from SCS | N | N |  | N | NO | <D> **** Detailed Description **** The computer that runs the radio system in CAS displays a time that is approximately 10 minutes different from the security computer. The time should be synced or as close as possible for the 2 systems. <I> **** Actions Taken **** Notified Security Management/staff. This is not a reportable or loggable issue.
386715 | CR | 20181113 |  | 3 | Hose control audit outdated/missing initiating documents |  |  |  | N | NO | <D> **** Detailed Description **** The Hose Control Audit WO 0212686301 could not be completed for the Turbine Building as the initiating documents could not be validated (i.e., TER 99-0004, TER, 00123101, etc.). This issue was previously written up CR 257174. SWP-MAI-02 should be updated to remove permanent hose installations from the Hose Control Log. And permanent (non-paper) Tags are needed for these permanent hoses. <I> **** Actions Taken **** Informed MCR <N> Crew has been engaged with engineering and will need additional time to support hte required changes. Extending this CR to post outage to allow for the additional investigation required.
386716 | CR | 20181113 |  | 3 | ARP for the Stack Monitor is Inadequate (see edms) |  |  |  | N | NO | <D> **** Detailed Description **** The Alarm Response Procedures for the newly installed Stack Monitor are woefully inadequate for use by Operations. The ARP is generally unclear and non-specific with even simple solutions to common problems left unaddressed. For example, the RB Stack Critical Failure alarm received on 8/19/18 at 15:27 had nothing relevant displayed on the Event Log Detail screen, despite the ARP saying that it would. Zero guidance was given for what to look at or how to fix the problem. It turns out the issue was a dirty filter which the Chem Tech identified and was able to correct, but tribal knowledge is not a satisfactory replacement for a decent ARP. The ARP says to check the Main Screen display Event Logs Detail Screen for the source of the alarm, which would be fine except that several conditions which do cause the Critical Failure alarm do not appear on this screen and there is no other guidance as to where to look and what to do about any of these alarms. The ARP makes plentiful use of acronyms with no explanation for what they mean (e.g., RDU/LPDU, PAP, P&I, etc.). The cause of the Critical Failure alarm received on 11/9/18 at 20:18 as listed by the Event Logs Detail screen was â€œRP P&I Filter Unavailableâ€; this cause is not even listed in the ARP as a possibility and no specific instructions on what to look at or corrective actions to take are delineated. Since Chemistry and Operations both have an interest in adequately addressing problems with the Stack Monitor, I recommend that Operations, Chemistry and Engineering work together to make a useful ARP or other document such as possibly a Chemistry Instruction that would assist Operators and Chem Techs in responding to Stack Monitor alarms. This approach has been taken before with the HSSF; the response documents has a mix of Chemistry Instructions, Ops procedures and ARPâ€™s in order to address problems.
386717 | CR | 20181113 | CAQ | C | Incorrect CVI Drawings for RHR-ST-4C in Asset Suite |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Incorrect CVI Drawings for RHR-ST-4C in Asset Suite. . The strainer module drawings in Asset Suite for RHR-ST-4C (CVI DWG 914-00,15 and CVI DWG 914-00,16) refer to a different style of strainer. Correct strainer drawings for RHR-ST-4C are not posted for this EPN. . This is a documentation issue only and does not affect any plant equipment. <I> **** Actions Taken **** Initiated AR-CR to capture lack of correct documentation. . Correct EPM drawings are necessary for R24 outage work on RHR-V-4C. Ref: WO #02107551. <N> **** Equipment Description **** RHR-ST-4C. | 02-00-RHR-ST-4C
386719 | CR | 20181113 |  | 4 | Foam backer rod wedged between pipe and fan screen | N | N |  | N | YES | <D> **** Detailed Description **** A ~ 3â€™ length of foam backer rod was found wedged between the RRC-FN-1B2 fan screen and the RRC-HX-ASD1B/2 glycol return piping. A piece of tape is attached to the backer rod, creating an FME concern. See pictures in EDMS. <I> **** Actions Taken **** Notified PSRO and Initiated CR. PSRO stated that he will notify SSS to have backer rod removed. EO verified the material was removed. <N> **** Equipment Description **** Outside ASD Building on east side of RRC-FN-1B2. | 02-00-RRC-FN-1B2,02-00-RRC-HX-ASD1B/2
386720 | CR | 20181113 |  | 3 | DUPLICATE REVISION ON DRAWING |  |  |  | N | NO | <D> **** Detailed Description **** EWD DRAWING WAS SUBMITTED BY DESIGN ENGINEERING ORG 54410 TO DOCUMENT CONTROL FOR PROCESSING. DRAWING CANNOT BE PROCESSED BECAUSE IT IS A DUPLICATE REVISION. <I> **** Actions Taken **** DOCUMENT CONTROL SUPERVISOR WAS INFORMED OF ERROR. DRAWING WILL BE SENT BACK FOR CORRECTIONS TO BE MADE. CR WAS ISSUED.
386723 | CR | 20181113 |  | 4 | Security BRE port plugs degraded | N | N |  | N | YES | <D> **** Detailed Description **** The BRE port plugs are degraded or missing. Request facility support to repair or replace port plugs to assist in maintaining acceptable temperatures. <I> **** Actions Taken **** CR/WR generated, coordinated with facilities, a specific list of ports provided to facilties <N> **** Equipment Description **** BRE's around the site
386726 | CR | 20181113 |  | 3 | Enhancement to Procedure 11.2.8.2 RWP Prep and Use |  |  |  | N | NO | <D> **** Detailed Description **** During RWP planning and using the referenced procedure a Standard Hold Point in Attachment 8.4 references HPI-12.64 that is no longer in use. Suggest removing "High Dose Rate Radioactive Material Transfer Plan and Instructions (HPI 12.64) Required Prior to Transfer of ." from Att 8.4. <I> **** Actions Taken **** Discussed with HPS and initiated this CR
386728 | CR | 20181113 |  | 4 | Monthly Chemical Storage area inspection discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** The following discrepancy was discovered while performing monthly inspecions of chemical storage areas; expired chemical found in FLSC# 16-0016. 1 tube of Dow corning RTV 732 (CP# 0261). <I> **** Actions Taken **** Removed expired chemical and delivered to E & RP for disposal.
386735 | CR | 20181113 |  | 4 | Vendor pump equipment failure during SAT-TK-2 work | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02126073-22 (HRP) drain remaining acid (CONTINGENCY) the pump provided by the vendor to support this task would not start, the vendor will replace the pump 11/14/18. The package to be returned to the planner for revision and a new clearance order built in order to replace this pump to continue work. <I> **** Actions Taken **** Notified WWM and PSRO. Returned package to planning for revision, contacted CORC for new clearance order, initiated CR. | 02-00-SAT-TK-2
386736 | CR | 20181113 |  | 4 | ARGOS Out Of Service At HP PAP |  |  |  | N | YES | <D> **** Detailed Description **** ARGOS HP-EQ-42783 located at the HP PAP is out of service due to a "low background rate" fault on foot detector 2C. No obvious holes in the detector's mylar were found. There are now (2) out of (3) ARGOS out of service at the PAP. This is significant due to this time of year when Radon levels are high. <I> **** Actions Taken **** Placed ARGOS OOS, contacted RP Supervision and initiated this CR and WR. | 02-00-HP-EQ-42783
386742 | CR | 20181113 |  | 4 | SAT-TK-2 degraded coating | N | N |  | N | YES | <D> **** Detailed Description **** Degradation of the sulfuric acid tank (SAT-TK-2) internal coating was noted during WO 02126073-06. The coating below the sulfuric acid liquid line was noticeably deteriorated and distinctive bands of exposed carbon steel were present, indicating potential horizontal grooving. The horizontal grooving was most noticeable at the mid-elevation of the tank, where the liquid level is most frequently maintained. Historic trends and recent NDE inspections provide a level of confidence that adequate wall thickness will remain until a complete re-coating of the tank can be planned and performed. Additional NDE inspections shall be performed under WO 02126073-05 to ensure adequate wall thickness before returning the tank to service. Pictures in EDMS. <I> **** Actions Taken **** Informed System Engineering Supervisor, Maintenance Supervisor, and Chemistry. | 02-00-SAT-TK-2
386745 | CR | 20181113 |  | 4 | Material not ordered | N | N |  | N | NO | <D> **** Detailed Description **** It was discovered that one media converter for the Camera Tower Project, CAS component and cable installation was not available. When Work Order 02128612 was created, material for all of the tasks were ordered under the 01 task. At this time, there was one media converter in stock and the second media converter was on order. When the 01 task was taken to Finished status this cancelled all of the MRâ€™s that had not been called in or picked up at the warehouse. To solve this problem, planning had to go back and create new MRâ€™s for the MRâ€™s that were cancelled or closed due to the task closing. This is affecting the schedule and resources. Work order 02128612-07. <I> **** Actions Taken **** Contacted Planning and Management to order the material.
386750 | CR | 20181113 | CAQ | A | 11 parameters for PRM-SR-1 were incorrect | N | Y |  | N | YES | <C> CRBB - CR Bring Back: Maintenance, Engineering and Emergency Preparedness - All Are Gathering More Information on this CR. RISK: High (A) CAUSE: Uncertain or Complex - Root Cause Evaluation Required <D> **** Detailed Description **** While performing WR 29145546 to investigate a critical failure PRM-SR-1 . Technicians discovered that IMDS values for time to filter swap had not been updated from the default during software re-installation 2 weeks ago timing out. . The software values for the parameters that were uploaded on 10/26/2018 were contained 11 errors in the parameters. . As part of the WO that installed the new CF card (WO 02135734) the values were supposed to be checked against the IMDS values. TDue to a lack of prfiency, The technicians involved thought that the laptop was commubnicating with the CPU in the Sample rack, But it was not sothe values they checked were not the vaules in the PRM-CPU-1. The UDP commincations parameters that were used were not correct and the laptop was communication with the PRM-CPU-1. the File that was installed on The CF card on 10/26/2018 is located in the Stack monitor laptop in the 02-PRM -SOFTGEMS folder, in the LPDU SWv1.1 folder. the file is config PLC. . ther are 11 parameters that were incorrect . including the composite channel oaleart alarm setpoint and the composite channel high alarm setpoint. . A copy of the IMDS with the 11 parameters highlighted and the values the were installed is attached to the EDMS button. . We were able to establish comnications with the PRM-CPU-1 using the correct UDP commuynications protocol. and wrote the correct parameter values to the PRM-CPU-1 and the read them back from the CPU and validated them against the IMDS. Whe the laptop is commnicating correctly the hte software show that it is sending and recieving and when the values are returned from the PRM-CPU-1 to the laptop if the value returned matches the value turns green. this was verified for all the IMDS parameters for PRM-CPU-1. <I> **** Actions Taken **** Discussed with engineering and operations and wrote CR <N> During todayâ€™s activities, the laptop successfully connected to the PLC where the parameters were compared to the IMDS values for PRM-CPU-1. All parameters that did not match were changed to the IMDS values [see attachment in EDMS folder]. These parameters were then written to the PLC and as a check, were read back from the PLC to ensure the values were still correct. Based on this, the sample rack is correctly set and Functional. | 02-00-PRM-CPU-1,02-00-PRM-SR-1
386751 | CR | 20181113 | CAQ | D | Surveillance Cover Sheet not signed off Correctly | Y | Y |  | N | NO | <D> **** Detailed Description **** It was discovered that the surveillance form ESP-MOVTOL -B301 for the Bench test on the new 480 VAC cubicle, CIA -42-8B7D was not signed off by the SRO for final review. The only sign off was the permission to perform the bench test which was signed off by the SRO. The performed by section was not signed off by the Craft performing the work on the same form. The form needed to be printed off, signed by all of the responsible parties and re-submitted to Records. The Foreman and the Supervisor missed this during the work package closeout. This is not an Operability issue, as this cubicle has not been installed yet. This bucket is scheduled to be installed during the R 24 Outage. Work order 02035959-02. <I> **** Actions Taken **** Contacted SRO and the Craft to review and sign off the form as required. | 02-00-CIA-42-8B7D,02-00-CIA-M-V/30B,02-00-CIA-V-30B
386752 | CR | 20181113 |  | 3 | Station awareness regarding ANI needs improvement |  |  |  | N | NO | <D> **** Detailed Description **** Station awareness of responsibilities and obligations under American Nuclear Insurance (ANI) policies needs improvement. There is no station policy that describes ownership and interface with ANI which has led to confusion about decision making and communication expectations.
386753 | CR | 20181113 | CAQ | D | FP-V-SGT/21 has large packing leak. | Y | N |  | N | YES | <D> **** Detailed Description **** Upon clearing a tagout for SGT, FP-V-21 was opened. Upon opening the valve, a packing leak of approximately four drops per second started. The leak was made worse by backseating the valve, so it was backed off. Please repair this valve. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RB 572 near RCC surge tank. | 02-00-FP-V-SGT/21
386754 | CR | 20181114 | CAQ | D | EBU failed surveillance 10.25.175 during WO 02132104-01 need | N | N |  | N | YES | <D> **** Detailed Description **** EBU failed surveillance 10.25.175 during WO 02132104-01 needs repair, light light indicates battery not connected <I> **** Actions Taken **** fsip 18-0342 made stage lantern, wrote cr made WR to fix. | 02-00-E-BU-W525/3
386755 | CR | 20181114 |  | 4 | Oil drain sump in TB Bowser room needs to be pumped. | N | N |  | N | NO | <D> **** Detailed Description **** The oil drain sump in the Bowser room, TB 441E, is indicating half full and needs to be pumped. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** Oil drain sump, bowser room, TB 441. RMC laborers pumped oil from oil drain sump in TB bowser (TB441E) on 11/14/18. No further action required. | 02-00-T-BLDG-MISC,02-00-TO-TK-1
386761 | CR | 20181114 | CAQ | D | M&TE Suspended/ Lost |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0067714 Proto Torque Wrench- model 6060A 50in/lb Missing from Clean Tool Crib. Suspended/ Lost. EFIN Eval: The M&TE being lost has no afffect on the maintenance performed for the Non Safety Related CW pump. PMT was performed statisfactorily showing that the M&TE worked properly during the maintenance. Pump vibrations were accepatable. DEF #6773A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
386765 | CR | 20181114 |  | 3 | HP-EQ-42808 Sample Cart blower at reduced capacity | N | N |  | N | YES | <D> **** Detailed Description **** When calibrating the flow meter for HP-EQ-42808, the highest flow achievable was 165slpm. The max per the IMDS is 300slpm. This is an annual calibration, and every year the max flow gets lower. <I> **** Actions Taken **** According to chemistry, the max operating range is 113slpm. Recommend revising the IMDS to a max of 150slpm. Also, recommend repairing or replacing the pump. It could be done coincident with the next planned calibration. | 02-00-HP-EQ-42808
386768 | CR | 20181114 | CAQ | D | Floater in Cell 47 of E-B1-7 | Y | N |  | N | YES | <C> CR reopened to cross reference additional WR 29135016, 29124691 and CR 364994, then taken back to complete CR reopened to add completion required check mark to referenced WO/WR 02102802-01 per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** A floating piece of debris was identified in Cell 47 of E -B1-7 during the monthly battery test under WO#02126852-01 <I> **** Actions Taken **** Took Pictures, Notified Supervisor, Wrote CR. Notify CRS and Engineering w/CR number. WR needed? | 02-00-E-B1-7
386770 | CR | 20181114 | CAQ | D | FLEX-P-1 requires coolant | N | Y |  | N | YES | <D> **** Detailed Description **** Coolant level in FLEX-P-1 is not visible. Request maintenance add coolant to support semi-annual PM per SOP HHGP-PM. <I> **** Actions Taken **** Notified PSRO <N> **** Equipment Description **** FLEX-P-1 located in Bldg 82 | 02-CM-FLEX-P-1
386772 | CR | 20181114 | CAQ | D | FP-V-18 Very hard to operate. | N | Y |  | N | YES | <D> **** Detailed Description **** Working WO# 02124518-01 fouond FP-V-18 operated very hard. the amount of force to cycle valve was excessive. VALVE IS RB Standpipe Supply ( PIV ) essential <I> **** Actions Taken **** Valve was returned to the open position. | 02-00-FP-V-18
386778 | CR | 20181114 | CAQ | C | Procedure clarification |  |  |  | N | YES | <D> **** Detailed Description **** PPM 15.3.17 page 14 of 24 states in comments that "UL Normally Locked Door". However R-DOOR-R408 is not locked. <I> **** Actions Taken **** Competed repairs on door per work order 02135289. <N> **** Equipment Description **** Reactor building | 02-00-R-DOOR-R408
386779 | CR | 20181114 |  | 3 | Camera install/remove tasks deleted from WOs |  |  |  | N | YES | <D> **** Detailed Description **** Camera install and remove tasks were deleted from WO 02105832. This was done a year ago when cameras were allowed to be left installed in the plant for long periods of time. However, this is no longer allowed and the cameras are required to be installed/removed with each Work Order. PMID 14979 and 14988 generated WOs need to be examined for extent of condition to ensure that camera install/remove tasks are intact. Also, IS does not track the camera installed per the WO process, instead using AR -CAM. There needs to be some direction in the WO for the AR-CAM to be written in preparation for the work. Suggest that IS write the AR-CAM during the walkdown of the WO task. <I> **** Actions Taken **** Discussed with WWM. Arranged with Telecom to install the required camera for performance of WO 02105832. | 02-00-TEA-SR-26
386782 | CR | 20181114 | CAQ | D | CRD-HCU-3839 excessive N2 leakage | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-TK-128/3039 has been recharged a number of times as of late. A review of operations log has shown dates of 6/22, 7/8, 8/28, 9/3, 9/10, 9/16, 9/22, 9/28, 10/4, 10/9, 10/15, 10/20, 10/29, 11/3, 11/8, 11/14. At approximately 0.3 mrem this is about 5 mrem exposure to operators that is unnecessary. OPS 2 investigated and stated at the base of the "blue tank" (CRD-TK-128/3839) there was leakage observed with snoop applied. Suggest that this be worked during or before the 12/15/18 down power. <I> **** Actions Taken **** Informed supervision of findings. Wrote this CR <N> Author should have used EPN of CRD-HCU-3839 as opposed the 3039 stated originally CR was edited at the request of the initiator, from HCU 3039 TO 3839. | 02-00-CRD-TK-128/3839
386785 | CR | 20181114 |  | 4 | T+1 Cancelled due to not meeting Quorum |  |  |  | N | NO | <D> **** Detailed Description **** T+1 meeting was cancelled due to not meeting Quorum. Required Quorum is 3 out of 7 department managers (no delegates). <I> **** Actions Taken **** Lessons learned were captured by WWM and component managers. This meeting will not be rescheduled. <N> **** Equipment Description **** N/A
386787 | CR | 20181114 |  | 3 | SOP-HHGP-PM procedure revision |  |  |  | N | NO | <D> **** Detailed Description **** The note immediately after step 5.1.2 of SOP-HHGP-PM states that Facilities should replensihh fuel/oil/coolant. Facilities has transferred this function to FIN. Revise the procedure note to reflect the correct organization responsible for replenishing fluids. <I> **** Actions Taken **** Discussed with PSRO.
386788 | CR | 20181114 |  | 3 | RHR-V-23 not in Sections 5.6 and 5.7 of SOP-FPC-ASSIST-ALT |  |  |  | N | NO | <D> **** Detailed Description **** Sections 5.6 and 5.7 of SOP-FPC-ASSIST-ALT do not discuss RHR-V-23. Every other valve in RHR-P-2B discharge flow path is verified closed with the exception of RHR-V-23. Should this valve be in sections 5.6 and 5.7 and if so does it require to be caution or danger tagged. If not, should a note be added in those sections or in the precautions and limitations explaining why it is not? | 02-00-RHR-V-23
386789 | CR | 20181114 |  | 3 | Calibration scheduled before required replacement | N | N |  | N | YES | <D> **** Detailed Description **** PSR-FIT-SR49/3 was identified as not being able to be calibrated in June, 2018. CR 381110 and WR 29143118 were written to document the issue, and to replace the equipment. The calibration WO was inadvertently taken to FINISHED status, then subsequently canceled. On November 14, the calibration PM was scheduled again, without the replacement being resolved. This was not noticed until the day of implementation. The true late date for the PM is 12/30/18. <I> **** Actions Taken **** Informed WWM and FIN manager that the transmitter replacement needs to be prioritized, since it directly feeds the chemistry effectiveness indicator. | 02-00-PSR-FIT-SR49/3
386795 | CR | 20181114 |  | 4 | (NRC) PRM systems text not up to date in portal |  |  |  | N | NO | <D> **** Detailed Description **** The NRC resident questioned the revision of the process radiation monitor systems text (SD000147) that appears in portal J. The revision date in portal shows 2/23/18 with major rev 14 and minor rev 03. The document has the same revision numbers but a date of June 16. The status of the document show CHANGE. The current form of this system text has not been updated with the new PRM system description. <N> see cross-referenced AR assignment for tracking of the changes to the system description
386800 | CR | 20181114 | CAQ | D | B5B-P-1 Cannot Establish Prime (Non-Functional for FLEX) | N | Y |  | N | YES | <D> **** Detailed Description **** While performing the annual full flow test on B5B-P-1 the pumper truck would not establish a prime of the pump when drafting from the test reservoir. The reason it didn't prime was due to a failed priming relay. Before the truck could be shutdown the priming pump had overheated and had visibly changed color. The vendor has recommended replacing both the priming and priming relay. Facilities mechanics have reviewed the work scope with the vendor and are comfortable performing the work on site. The replacement parts are in the process of being procured. . It was found that FLEX-P-1 had low coolant level during the surveillance on B5B-P-1. This resulted in two FLEX water sources being non-functional at the same time. Coolant level was restored. Oil level was verified to be in specification and no coolant was observed in the oil. It appears that the decrease in coolant is due to evaporation since the last operational check. Following the coolant addition FLEX-P-1 was started and no active coolant leaks were observed. . B5B-P-1 must be repaired in the next 90 days or an equivalent water pump will need to be rented. The Pumper Truck can be operaed using a pressurized suction source (hydrant) and procedures exist to support this configuration. Hydrants are not available for FLEX strategies and no procedural guidance exists for establishing prime for draft using a supplemental water source (submersible pump or equivalent) to preclude overheating. A hydrant was used to establish a prime and allowed completion of the surveillance. The main water pump successfully passed the full flow test. Once the priming pump and relay are replaced a PMT will be performed to verify the pumper can prime and establish a draft from a water source. <I> **** Actions Taken **** Discussed issue with Supervisor. Coordinated with Facilities to determine if work could be performed on site. Contacted Xylem to determine the availability of a rental pump (not necessary at this time). Initiated the parts procurement process. Determined the functionality of FLEX -P-1. Discussed the issue with the Shift Manager, Maintenance Supervisors and Equipment Operators. <N> **** Equipment Description **** Building 600 | 02-00-B5B-P-1
386802 | CR | 20181114 | CAQ | D | ISP-IRM-X303 | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing ISP-IRM-X303 (WO 02104172-01) As-Found Zero 1 voltage on step 7.3.5 was found OOT at -0.017 VDC. Tolerance is -0.005 VDC to 0.005 VDC. Adjusted per step 7.3.6 to As-Left value of -0.000 VDC. As Found Zero 2 voltage on step 7.3.9 was found OOT at 0.009 VDC. Tolerance is -0.005 VDC to 0.005 VDC. Adjusted per step 7.3.10 to As-Left value of -0.001. <I> **** Actions Taken **** Informed supervision, adjusted per ISP-IRM-X303, wrote CR. | 02-00-IRM-DET-2C
386803 | CR | 20181114 |  | 4 | CW TSS Elevated due to CW Pump Work |  |  |  | N | NO | <D> **** Detailed Description **** Observation during halogenation found that the CW was very turbid and muddy. Inaccordance with procedure, a sample was run for TSS to determine if it was above the 120 mg/L target. Two tests were run and the results were 320 mg/L and 285 mg/L. Action for this is to increase CW blow down rates by 1,000 gpm. Operations was notified and the blow down was increased. <I> **** Actions Taken **** Notification was made to all parties. As per procedure, TSS tests were run and as a result blow down was increased. This CR is for trending only. All appropriate and procedure driven actions and cause determination have been completed. | 02-00-CW-PIPE-MISC
386804 | CR | 20181114 |  | 4 | TSW-FIS-33A has incorrect gaskets installed | N | N |  | N | YES | <D> **** Detailed Description **** I&C Technician observed that the gaskets installed on TSW -FIS-33A flanges are flexitallic sprialwound gaskets. this was noticed while replacening TSW-FIS-33B. due to the FIS being made of a disimular metal than the piping, the gaskets need to be nonmetallic. With isolaotrs installed to prevent contact between the disimular metals. the isolating kit is installed on TSW-FIS 33A, but the flexitallic gaskets are metal insteasd of the type f gasket material that is supposed to be used. the FIS was removed, cleaned and reinstalled with the incorrect gaskets on A WR is not needed. WO 02130260 exists to replace TSW-FIS -33A. this work order needs to installe the correct gaskets when the FIS is replaced. <I> **** Actions Taken **** wrote CR. WO 02130260 will be replacing the gaskets to the correct gaskets. WO# 02101782 installed the incorrect FIS gaskets on june 5, 2018. <N> CVI ISO 317-00,4776 calls out insulating flange kits for TSW-FIS-33A. | 02-00-TSW-FIS-33A
386806 | CR | 20181114 |  | 3 | B.5.b and Flex Equipment Needs to be Added to PPM 1.3.83 |  |  |  | N | NO | <D> **** Detailed Description **** LDCN-18-027 will be adding LCS 1.11, BEYOND DESIGN BASIS EQUIPMENT. Completion times for restoring out of service FLEX equipment will depend on what equipment is out of service. Prudent planning and conservatism would suggest we never plan to perform maintenance on two SSC's that perform the same function (i.e., water addition, electrical power, tow vehicles, debris removal vehicle, etc.) simultaneously. FLEX and B.5.b equipment should be added to PPM 1.3.83 to address appropriate protection schemes when FLEX or B.5.b is out of service. See also CR 386800. <I> **** Actions Taken **** Discussed with FLEX Engineer.
386807 | CR | 20181114 |  | 4 | Steam Tunnel Camera only works intermittently |  |  |  | N | YES | <D> **** Detailed Description **** The steam tunnel camera only works occasionally. This was CR'ed as broken in Dec 2017 and evaluated for replacement in R24, then during a job walkdown the camera worked so the task was removed from FO 18-01 outage planning. Various EO's have differing experiences but the common theme is that the camera setup is not functioning reliably at producing a lighted controllable picture. All the documents I reviewed showed that this task has been closed out. Recommend an evaluation on re-adding WO package for R24 as this appears to be a long term issue. <I> **** Actions Taken **** Informed MCR; <N> **** Equipment Description **** Steam Tunnel Camera setup East TB501 | 02-00-R-BLDG-MISC
386816 | CR | 20181115 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065205 Industrial Scientific Gas Moniotr- model iTX found OOT & adjusted within specs. Not used during Calibration cycle. DEF #6775A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
386818 | CR | 20181115 |  | 3 | Evaluate Revising ABN-RCIC-START Entry Conditions |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate changing ABN-RCIC-START entry conditions to just manual RCIC operation due to equipment failures. The current entry conditions of "RCIC operation required with no AC and DC power is available" is overly restrictive and would prevent use of this procedure until all electric power is lost. This may require additional changes to the text of the procedure. <I> **** Actions Taken **** wrote CR
386822 | CR | 20181115 |  | 4 | DLR placed in X-ray machine |  |  |  | N | NO | <D> **** Detailed Description **** When processing through the search area, an Ops staff member placed their DLR in the x-ray machine <I> **** Actions Taken **** HP Management coached the individual who understand the importance of this error. No further action iis required.
386824 | CR | 20181115 | CAQ | C | CCH-CR-1A/1B compressor refrigerant outlet gauge | Y | Y |  | N | YES | <D> **** Detailed Description **** CR 386056 identified that OSP-CCH/IST-M702 references a temperature gauge that has no EPN and is not calibrated. The CR was canceled to the WR with no clear action. Recommend actions for engineering to evaluate the use of the temperature gauge and if it needs a PM for calibration. If it requires a label, an EPN needs to be generated in portal J (IS) and OSP-CCH/IST-M702 needs to be updated with the EPN (Ops). The same situation exists for OSP -CCH/IST-M702. | 02-00-CCH-CR-1A,02-00-CCH-CR-1B,02-00-CCH-TI-3A,02-00-CCH-TI-3B
386825 | CR | 20181115 | CAQ | D | 2 of 4 Emergency DC Lighting in Remote Shutdown Room not Lit | N | Y |  | N | YES | <D> **** Detailed Description **** 2 of the 4 total emergency DC lighting fixtures in the Remote Shutdown Room and the emergency DC lighting fixture outside of door C403, Main Control Room exit into Stair No. 7, are not lit. Per Paragraph 9.5.3.2.3 of the FSAR, the emergency DC lighting in the Remote Shutdown Room and the access route from the Main Control Room to the Remote Shutdown Room are to be continuously lit. Suspect that the bulbs are burned out and will need to be replaced. A similar occurrence was documented in AR-CR 386411 and WR 29145439 replaced bulbs in the Remote Shutdown Room, however, only 2 of the 4 fixtures had bulbs replaced. Since the similar occurrence, the emergency DC lighting fixture outside of door C403 has gone out. <I> **** Actions Taken **** Informed the CRS and created WRs to have the bulbs replaced. <N> **** Equipment Description **** E-DISC-S11D1 - Remote S/D Room E-DISC-S12D1 - Remote S/D Room | 02-00-W-BLDG-MISC
386826 | CR | 20181115 |  | 4 | Cancelled RHR-A High Risk Challeng Meeting (2nd occurance) |  |  |  | N | NO | <D> **** Detailed Description **** The high risk challenge meeting for RHR-A safety system window that was scheduled for 11/14/18 was cancelled due to excessive work not being at the correct status. <I> **** Actions Taken **** Cancelled High risk challenge meeting. Institued daily recovery meetings and established expectation for CMPM to develop a recovery plan. <N> **** Equipment Description **** N/A
386827 | CR | 20181115 | CAQ | C | Failure to initiate a CR when issues were identified |  |  |  | N | NO | <D> **** Detailed Description **** Problems were identified with a clearance a year ago and Ops failed to issue a condition report. Clearance orders were written identifying a lack of procedure guidance, labels, and adequate prints. Although noted in the clearance, no action was taken to address the gap in standards. An AR/CR should have been generated to address these shortfalls prior to performing the work. The Corrective Action Program is used to address problems, identify issues and support safe, reliable operations. <I> **** Actions Taken **** Operations issued a department clock reset published in the D15 on 11/15/2018. (386259) <N> The issue of failing to initiate a CR occurred approximately 1 year ago. Operations took the initiative to reset the department clock as a coaching method to the entire department about ownership and resolution of issues. No further action required for this issue.
386829 | CR | 20181115 |  | 4 | TSW-FIS-33B OSCAR'd into the CW maint window without review |  |  |  | N | NO | <D> **** Detailed Description **** WO# 02083519-01, Remove and Replace of TSW-FIS-33B was OSCAR'd into this weeks Circ/Water Maintenance window without proper package review/walkdown or manning impact. FIN manning was pulled to the main shop to cover work. Package had to be rewritten to cover proper parts and qualifications. Add to this the work was deemed medium risk (due to plant configuration). <I> **** Actions Taken **** Wrote this CR and spoke with supervision. Suggest that it gets trended as other technicians have spoke to a history of this type of thing happening and that we are getting lucky that we are catching it and working it error free. | 02-00-TSW-FIS-33B
386830 | CR | 20181115 |  | 4 | Minor leak downstream from WCH-V-664 | N | N |  | N | YES | <D> **** Detailed Description **** Water is dripping at a rate of 10 drops per minute downstream from WCH-V-664 (WCH-EV-51B Vent). The leak appears to be originating from the chicago coupling downstream of valve . See EDMS folder of this CR for a picture of the valve . This valve is installed on WCH-CR -51B located on RW 507. A puddle has formed as a result of this leak. WCH-CR-51B is currently out of service. Please investigate and repair and install a catch basin until leak can be repaired. This issue was discovered during a system walk-down. This valve is Critical R and Not Safety Related. This condition does not render inoperable equipment that is a Technical Specification Safety Related System, Structure, or Component (SSC). This valve remains in service and functional. <I> **** Actions Taken **** Initiated WR. Notified Rad Material Control Waste Supervisor. <N> **** Equipment Description **** Mounted to WCH-CR-51B | 02-00-WCH-V-664
386832 | CR | 20181115 |  | 3 | Review Hazard Communication Training for adequacy |  |  |  | N | NO | <D> **** Detailed Description **** After a review of ISPM-11 requirements and existing training, the Station may not be adequately covering all required information. Per ISPM-11 section 3.4. â€œHazard communication information SHALL BE PROVIDED to all Energy Northwest employees and applicable contractor employees in accordance with WAC 296-901-14016. Currently this is accomplished by completing Nantel Hazard Communication Training and review of applicable procedures and instructions as directed by supervisors. â€œ The procedure then lists the required information to be covered by the training. Based on the current training material used to cover these requirements, we may not be adequately covering all required information. For example there is no "explanation of the labels received on shipped containers" which is specifically listed as needing to be in the training. See EDMS doc. <I> **** Actions Taken **** Wrote CR, informed safety rep
386833 | CR | 20181115 |  | 3 | Trend â€“ Maintenance Fuse Control |  |  |  | N | NO | <D> **** Detailed Description **** From January 2017 to current Maintenance has had five instances where a fuse was installed with the incorrect rating or style causing equipment to be declared degraded or removed from service until corrected. Trend needs to be reviewed to determine commonalties or themes and create actions as necessary to improve performance. Recommend assignment to AR-MNTPROG <I> **** Actions Taken **** Discussed with Maintenance Department and Maintenance Services Manager. Trend validation sheet completed and uploaded to EDMS.
386834 | CR | 20181115 |  | 4 | Personal Medical Condition - Transported to Offsite Medical |  |  |  | N | NO | <D> **** Detailed Description **** On Thursday, November 15, 2018, an individual experienced a personal medical condition. The person sought assistance from the Occupational Health Nurses at the Occupational Health Facility at the Willamette Building. The Control Room was contacted for ambulance response. The on-duty RNs requested no first responder tone out. The Hanford Fire Department was called at 7:40 am and arrived at the security checkpoint at 7:55 a.m. One HFD ambulance M1923 and one HFD ladder truck L1923 arrived at Occ Health at 8 :00 a.m. and provided care for the patient. The individual was transported to Kadlec Regional Medical Center at 8:18 a.m. The manager/ supervisor was notified of the condition. <I> **** Actions Taken **** Documented the off-site medical transport via this CR.
386835 | CR | 20181115 |  | 3 | Stack monitor equipment exposed to damage in TG/Rx corridor |  |  |  | N | YES | <C> CR Priority moved from CAQ to NON-CAQ and CR Severity moved from C to 3 at the direction of OFM on 11/20/2018 (No Current Deficiency <D> **** Detailed Description **** Equipment which supports the stack monitor is installed in the east end of the 501â€™ TG/Rx building corridor and is exposed to collision with scaffold carts and other potentially damaging items moving down the hallway. Scaffold carts are of particular concern since scaffold is frequently moved back and forth pre-and post-outage between the TG and Rx buildings through the NW 501 Rx building airlock. Recommend some sort of barrier be built to protect this equipment. <I> **** Actions Taken **** Notifed operations Wrote this CR <N> **** Equipment Description **** 501 TG/Rx corridor | 02-00-PRM-SR-1
386838 | CR | 20181115 | CAQ | D | M&TE Rejected |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0064959 Fluke Module- model 700P05 30psig Rejected because the pins were bent and broken beyond repair. All items in the Usage Card were reviewed. The as found readings were in the range expected and there was no indication on the WOs reviewed that there was any issue with this M&TE. Therefore, there is a reasonable expectation that this condition did not impact the operability of any plant SSC. See EDMS for full eval. DEF #6767A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
386840 | CR | 20181115 | CAQ | C | SGT-EHO-1A1 stroke length out of tolerance, AD stroke SAT | Y | Y |  | N | YES | <D> **** Detailed Description **** SGT-EHO-1A1 stroke lenth did not meet tolerance, AD stroke is SAT. Email from Holle:"As found stroke length on SGT-EHO-1A1 is acceptable. SGT-AD-1A1 was verified to fully stroke closed and then open with the as found stroke length. Increased stroke length would lead to putting force on a full open or full closed vortex damper which could damage the EHO or the vortex damper. As left stroke length is adequate for the SGT system to perform its current licensed design basis functions and will be verified via the PMT which will perform the surveillance procedure for SGT-FU-1A.--MJ Holle 11/15/18" Adjustments made to SGT-EHO-1A1/SGT-AD-1A1 will slightly decrease theflow in when the damper is in both the open and clsoed positions. <I> **** Actions Taken **** Will need Engineering to look at SGT-EHO-1A1 stroke set point and tol. When those values are determined (or other corrections) 10.25.136 will need to be corrected accordingly. | 02-00-SGT-EHO-1A1
386841 | CR | 20181115 |  | 3 | BS-PT-10 IMDS head correction is wrong |  |  |  | N | NO | <D> **** Detailed Description **** The pressure head correction specified in the IMDS for BS -PT-10 is incorrect. The difference in height between the sample point (T517'7'' crossover piping) and Instrument (T474'8'' E-IR-10) is 42'11'', not 32'11''. This is not an equipment issue because the head correction error was identified during the last calibration (June 2007) and the IMDS was redlined which allowed proper calibration (ref. WO 01127376-07). But a new IMDS was never issued. The IMDS should be revised. | 02-00-BS-PT-10
386842 | CR | 20181115 | CAQ | C | Weak link calculation error 216-92-001 | Y | N |  | N | NO | <D> **** Detailed Description **** Weak Link Calculation 216-92-001 for valves RHR-V-21, 24A, 24B, 48A and 48B used a non-conservative weight for the actuator and motor. This impacted the valve mounting bolts and mounting flange. <I> **** Actions Taken **** Rerunning the calculation with the non-conservative acatuator weight did not impact the overall weak link. Recommended formally revising the weak link with the correct actuator/motor weights. <N> This existing calculation error was noted while performing reviews associated with EC DEC 17459. | 02-00-RHR-MO-21,02-00-RHR-MO-24A,02-00-RHR-MO-24B,02-00-RHR-MO-48A,02-00-RHR-MO-48B,02-00-RHR-V-21,02-00-RHR-V-24A,02-00-RHR-V-24B,02-00-RHR-V-48A,02-00-RHR-V-48B
386843 | CR | 20181115 | CAQ | C | (QA) R-24 WOs requiring QC inspection not routed to QC |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) R-24 work orders requiring QC inspection were not routed to QC for review per QAP-ASU-06, QC Inspection Planning. Work order 02118747 RFW-42-7A4B (RFW-V-65B) REPLACE STARTER COIL (POD 369412) is assigned to be worked by Site Support Contractor Electricians in R-24. QAP-ASU -07, Peer Verification Program Planning, requires QC inspection of this work. The work order instructions have QC inspections sign offs, however this work order did not have a QCI hold placed on it per QAP-ASU-06 QC Inspection Planning Activities, therefore no QC inspector reviewed this work order for adequacy. The impact of this could be a missed required inspection and/or a delay in working this job in the outage in order to obtain the required reviews and, if necessary, work order revisions. An auditor identified this deficiency during a Long Path Review Meeting that contained this work order. Review of other work orders found 02118745 WMA-42-7F1D: REPLACE STARTER COIL WMA-FN-53A (POD 369412), 02117680 RHR-42 -8BA2A: REPLACE STARTER COIL RHR-V-9 (POD 369412) and 02117255 MS-42-7BA9B: REPLACE STARTER COIL MS-V-67C (POD 369412) with the same deficiency. The auditors' work order review was limited to type 42 devices (motor starters) planned by the same planner, therefore, the extent of condition beyond motor starter work orders is unknown. All four work orders were at the ready status and have been returned to the planner to review for adequacy and to apply the required QCI holds. This problem is considered a Deficiency identified during Quality SR-19-02 Continuous Monitoring Roll-Up Surveillance. Recommend assignment to Maintenance Planning <I> **** Actions Taken **** Discussed with the Planning Supervisor. Returned the four work orders to planning. <N> Maintenance Planning.
386844 | CR | 20181115 |  | 3 | Temporary collection bottle at sump R5 |  |  |  | N | YES | <D> **** Detailed Description **** There is a temporary poly collection bottle, about 5 gallon capacity, located on the floor near R5 sump. It is connected to plant piping with tygon tubing. This collection bottle is used during SOP-EDR-OPS for Manual Determination of Drywell Identified Leakrate. The SOP is written such that the bottle is connected, used per the procedure, then disconnected and stored. However, there is a NOTE in the SOP that allows the bottle to remain connected "If multiple samples are anticipated, sample hose and container may be left connected at discretion of CRS/SM." However, this section of the procedure is apparently not performed on a regular basis, and not frequently. It would seem that this bottle should not be routinely left connected to the system via the tygon tubing. This was identified during review of CR 385665. See EDMS for photo. <I> **** Actions Taken **** Contacted shift manager to discuss. | 02-00-EDR-SUMP-R5
386845 | CR | 20181115 |  | 3 | Enhancement needed for Filter Replacement PM | N | N |  | N | NO | <D> **** Detailed Description **** The PM task for H2-F-DRP/2A & 2B to replace filters needs to be enhanced to include the as necessary replacement of the filter unit gaskets. The PMT portion of the PM requires a leak check to verify no leaks. It may be necessary to also replace the gasket if a leak is found during the PMT. The PM only includes the replacement filter in the MR. <I> **** Actions Taken **** Wrote CR, Contacted Manager, Work Week Manager, Operations, & provided feedback in W/O package. | 02-00-H2-F-DRP/2A,02-00-H2-F-DRP/2B
386850 | CR | 20181115 |  | 4 | Individual Bumped Head On Metal Box |  |  |  | N | NO | <D> **** Detailed Description **** While trying to obtain permission to enter the main control room to file documents, a Records Management Specialist (RMS) failed to notice a metal box overhead and bumped their head on it. <I> **** Actions Taken **** Per ISPM-01, Supervisor escorted individual to Occupational Health. There was no first aid required and the individual was released to return to work. Generated incident report and informed both industrial safety and department manager.
386851 | CR | 20181115 | CAQ | C | Incorrect software version stored in IS as part of EC 11288 | N | Y |  | N | YES | <D> **** Detailed Description **** The incorrect software version to support PRM-SR-1 was submitted to IS. The version submitted to IS was from the factory acceptance testing in August 2016 and should not have been submitted. When settings were updated as part of commissioning of the stack monitor, a new version of the software should have been submitted to IS as part of final PMT and tuning of the PRM-SR-1. The cause is known as this was not explicitly specified at the time in DES-6-1 Design of Digital Plant Systems and Components, Revision 17. This has since been corrected as it is identified and included in DES-6-3 Software Life Cycle Management for the revision of software during implementation in Section 6.6, and the processing of a master copy of the software to IS for retention in section 6.5. <I> **** Actions Taken **** Discussed with manager and peers and initiated CR. Note, immediate actions taken were to revise EC 11288 and update the associated SQA documentation to support a new revision to the software. | 02-00-PRM-SOFT-GEMS,02-00-PRM-SR-1
386853 | CR | 20181115 |  | 3 | Installed NMC Air Monitors are chronically out of service | N | N |  | N | YES | <C> CR (386853) Severity moved from 4/Trend to 3 and assigned to AR-SEEIC at the direction of OFM on 11/20/2018. <D> **** Detailed Description **** The Nuclear Measurements Corporation (NMC) Model AM-221 installed Continuous Air Monitors (CAMs) have been chronically out of service for extensive periods and are unreliable and not dependable. This chronic out of service condition is a drain on resources for maintenance and repair. In addition these are not available for Radiation Protection personnel for plant monitoring as designed for responsive personnel protection and plant surveillance. The NMC CAMs, RRA-RIS-3, WRA-RIS-1, and WRA-RIS-2 are installed in the plant ventilation return air system. These monitors are not Safety Related SSCs. . This equipment is described in the FSAR 12.3.4.2.b and 12.3.4.4 (but not in TS, ODCM, LCS, or EP 13.1.1). Each of the three channels of the airborne radioactivity monitors has an independent local visual and audible alarm. High radioactivity or equipment failure will generate an alarm signal. These also have readout and recording features in the main control room on panel BD-RAD-24. No automatic system functions are performed by the alarm signals. This equipment should not continue to be accepted in the current condition. A determination needs to be made involving RP, Engineering and Maintenance if these monitors are necessary for Radiation Protection functions as describe in the FSAR and information provided is valuable. If the equipment as designed, can be updated to be more reliable and durable; or if it should just be replaced. Or, if there are alternate means of air monitoring are suitable if the equipment should be removed or abandoned in place. Even if the electronic function cannot be restored these instruments may still capable of collecting a valid air sample and filter can be analyzed with results used for trending purposes and early leak detection. <I> **** Actions Taken **** Discussed with RP Supervision, Chemistry ODCM/Effluents Specialist, FIN Maintenance, System Engineer Electrical/I&C. Initiated AR-EVAL to evaluate and document this determination. AR Eval number is listed in cross reference. Reviewed other AR-CR related to subject. Most notably : AR-CR 00316031 NMC RRA-RIS-3 And WRA-RIS-2 extended out of service period. AR-CR 00303133 RRA-RIS-3 out of service for extended period | 02-00-RRA-RIS-3,02-00-WRA-RIS-1,02-00-WRA-RIS-2
386854 | CR | 20181115 |  | 4 | Late entry in eSOMS for Maintenance |  |  |  | N | NO | <D> **** Detailed Description **** An I&C tech was asked to work the two days of his long change. The Maintenance scheduler was not notified and eSOMS was not updated until the end of the 2nd day he worked. No violations occurred when eSOMS was updated <I> **** Actions Taken **** Updated eSOMS with correct hours. Notified supervisor of late entry.
386856 | CR | 20181115 |  | 4 | Service Building Heater Corrosion inhibitor chemicals low | N | N |  | N | NO | <D> **** Detailed Description **** Per SWP-CHE-02 the service building heater is below limits and is currently in CCW action level 1. Chemistry will need to perform a chemical addition and operations will need to assist in the valve manipulations for the system. The corrosion inhibitor chemicals always tend to be low upon initial start up for cold weather operations. <I> **** Actions Taken **** MCR, chemistry supervision, chemistry specialist | 02-00-SHHW-HX-51
386857 | CR | 20181115 |  | 3 | (QA) Fin Team management of leaking equipment is deficient |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) FIN Team management of leaking equipment is deficient. There are currently over 30 work requests (WRs) assigned to the FIN team with a leak code. In addition to the WRs with leak codes, there are over 40 WRs on leaking equipment without a leak code in the problem type field. Over 50 of these WRs are at least 100 days old. There are at least 11 leaks identified on steam plant equipment that should be promptly evaluated, and if validated, considered for scope addition to R24. The leaks that do not have a leak code in the problem type field (over 40 right now) are not included in the performance indicators. The external leak performance indicator shows a decreasing trend of external leaks over the last year from 88 to 59 and the high priority leaks from 25 to 23. Three of the high priority leaks are currently assigned to the FIN team and one of those is over 100 days old. In 2008, Columbia had a seven-day maintenance outage to repair steam leaks. The current plant water use rate is slowly climbing but is not challenging plant operation. Focus and management of leaking equipment, especially steam plant equipment, will not challenge continued plant operation. There are four WRs documenting roof leaks that are around 200 to 300 days old. In 2014 Columbia had an extended unplanned downpower to repair E-TR-5/53 that was damaged due to turbine building roof leakage. Refer to highlighted crystal report in EDMS for the list. This problem is considered a Deficiency identified during Quality SR-18-16 FIN Effectiveness Surveillance Recommend assignment to FIN Team <I> **** Actions Taken **** Discussed with the Maintenance Services Manger and FIN Team Manager.
386858 | CR | 20181115 | CAQ | C | Slow trend down on SLC boron concentration | Y | N |  | N | NO | <D> **** Detailed Description **** The Standby Liquid Control boron concentration has been slowly trending down since July 2017. It is not out of specified limits currently but it may be time to plan a chemical addition to prevent sudden response to low boron concentration. It does appear that when chemistry samples and the sparge is open more or it sparges longer that we get a better value (or it is better mixed) but it is still a slow trend down. <I> **** Actions Taken **** MCR, Chemistry Managment, Chemistry Supervision, Chemistry System Specialist | 02-00-SLC-TK-1
386860 | CR | 20181115 |  | 4 | WRA-SUH-5 has a steam leak | N | N |  | N | YES | <D> **** Detailed Description **** WRA-SUH-5 has a steam leak from relief valve on return side of unit. It is approxiamately 2-3 ft plume of steam. <I> **** Actions Taken **** Isolated supply steam valve HS-V-W52 | 02-00-WRA-SUH-5
386861 | CR | 20181115 | CAQ | C | EOC CR for AR-CR 385634 | Y | Y |  | N | YES | <D> **** Detailed Description **** This CR is being written for extent of condition per SWP -CAP-01 for AR CR 385634. HPCS-C1-1 potentiometers are original plant equipment and based on the failure report the potentiometers that failed were 45 years old. The affected EPNs for the Extent of condition include: E-C1-1A, E-C1-1B, E-C1-2A, E-C1-2B, E-C0-1A, E-C0-1B, E-C0-2A, E -C0-2B, E-C1-7, E-C2-1 E-C1-3, E-C1-4, and HPCS-C1-1. All but E-C1-7 had the pots replaced within the past 10 years due to failures. There is no evidence of past issues with either the FLOAT or EQUALIZE potentiometers in E-C1-7, but it must be assumed that the potentiometers are old and in need of future replacement based on the recent failure of HPCS-C1-1 potentiometers (see CR 385634). The failure analysis done by Exelon Power Labs on the degraded potentiometers from HPCS-C1-1 show that there is a risk of mechanical degradation that could cause the potentiometers to fail to operate in the expected fashion based on age and debris that was found in the potentiometers mechanism. The most likely case where this can occur is when adjustments are being made to the output voltage after switching from FLOAT to EQUALIZE mode using a toggle or control switch. Instead of using the FLOAT/EQUALIZE switch to change voltage on E-C1-7 the FLOAT potentiometer is used to adjust voltage (preferred method in PPM 10.25.134) There is no indication that, once set to give a certain output voltage that voltage will drift. The FLOAT and EQUALIZE potentiometers in the station chargers may not respond correctly when required due to age and mechanical wear. Based on the age of the potentiometer in E-C1-7 and the current voltage trends for the charger there is no immediate concern with proper voltage control using the potentiometers. Currently there is no impact to the other chargers based on voltage trending and the potentiometers have been replaced in the last 10 years. Recommend assignment to system engineering to evaluate PM frequency for Potentiometer replacement. <I> **** Actions Taken **** Notified Supervisor and manager and prepared the CR. Discussed issue with shift manager prior to initiating CR. | 02-00-E-C1-7
386862 | CR | 20181115 |  | 4 | Sim Thor Abort during ILC training |  |  |  | N | NO | <D> **** Detailed Description **** During scenario LO000040a (IC151) we got a "THOR has a problem cell" lock- up of the simulator. 10 min training time lost. <I> **** Actions Taken **** Followed the "THOR Abort" procedure and captured data as instructed. Sim SR report 8242
386863 | CR | 20181115 |  | 3 | 5.5.26 Procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Please add a note to 5.5.26 to allow the performance of steps 4.1.3, 4.1.4, and 4.1.5 to be performed in parallel with steps 4.1.1 and 4.1.2.
386864 | CR | 20181115 | CAQ | D | E-BU-SWA6/3 service alert light | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-SWA6/3 has a service alert light blinking. Light is blinking 5 times which means a "lamp fault" per the label plate. <I> **** Actions Taken **** Initiated AR/WR <N> **** Equipment Description **** R468 N/9.0 IN STAIRWELL "A6" | 02-00-E-BU-SWS6/3
386865 | CR | 20181115 |  | 4 | Heating steam leak on WOA-HC-1 "K" coils | N | N |  | N | YES | <D> **** Detailed Description **** Steam leak with a 2-3' plume coming from the lower portion of the "K" coil. <I> **** Actions Taken **** Initiated AR/WR <N> **** Equipment Description **** RW487 | 02-00-WOA-HC-1
386866 | CR | 20181116 |  | 3 | New Chemical feed pumps need oil dipsticks | N | N |  | N | YES | <D> **** Detailed Description **** CF-P-42A & CF-P-41B are both new pumps and motors. They are similar to the previous setup except that the new oil caps are threaded without any dipstick method to measure oil level. This new cap arrangement does not meet with log instructions to verify oil level between 1/4 and full because we have nothing to confirm correct depth of the oil reservoir. Recommend either changing the log to a new method of measuring the oil or replacing the cap with a different style that provides the correct measurement ratios. The old caps seem to be similar in size and might provide the necessary depth measurement after evaluation. <I> **** Actions Taken **** Informed MCR. | 02-00-CF-M-P/41B,02-00-CF-M-P/42A,02-00-CF-P-41B,02-00-CF-P-42A
386867 | CR | 20181116 |  | 4 | Light burned out in Room B104 at CW |  |  |  | N | YES | <D> **** Detailed Description **** The light is burned out in Room B104 at CW which contains DO-TK-3. Diesel storage tank for FP-P-1 <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** CWPH room B104 behind door B-112 | 02-00-P-BLDG-MISC
386868 | CR | 20181116 |  | 4 | TO-HX-1B upper end bell is weeping oil around lift point | N | N |  | N | YES | <D> **** Detailed Description **** TO-HX-1B upper end bell is weeping oil around lift point. <I> **** Actions Taken **** Field supervisor | 02-00-TO-HX-1B
386869 | CR | 20181116 |  | 4 | TOA-V-31B open indication is not working | N | N |  | N | YES | <D> **** Detailed Description **** TOA-V-31B open indication is not working. valve appears to be open but the open light on the HVAC panel is not lit, bulb changed same result. <I> **** Actions Taken **** see above. | 02-00-TOA-V-31B
386870 | CR | 20181116 |  | 4 | CW-CB-CW1B closed light doesnt work, changed bulb | N | N |  | N | YES | <D> **** Detailed Description **** CW-CB-CW1B closed light doesnt work, changed bulb. <I> **** Actions Taken **** WR/CR | 02-00-CW-CB-CW1B
386871 | CR | 20181116 |  | 3 | evaluate if a TMR is required for vent connections on t501 |  |  |  | N | YES | <D> **** Detailed Description **** There temp blower hooked up to the ventilation of the turbine buliding 501 and routed up to the crane for cooling. Discussion with shift management on whether a TMR was required or if it was being controlled via a wo/WR resulted in the direction to write this CR to ensure we are in the right process with the connections to the ventilation. <I> **** Actions Taken **** discussed with crew supervision, wrote CR <N> **** Equipment Description **** ventilation connections on the turbine 501 . WO 02114492 tasks 04 and 11 are correctly identified as Temporary Alteration in Support of Maintenance (TASM) and meet the requirements of SWP-CM-02. No TMOD is required. No further action required. | 02-00-MT-CRA-1,02-00-T-BLDG-MISC
386872 | CR | 20181116 | CAQ | C | No config/tracking assignment for EC MALT 13667 |  |  |  | N | YES | <D> **** Detailed Description **** Minor Alteration EC MALT 13667 (RHR-MO-40 GEAR RATIO CHANGE TO OBTAIN MARGIN) was recently implemented (~10/20/18) via RHR-MO-40 refurb WO 02093536 but the associated configuration control actions have not been started/completed by the responsible Engineering group. EC MALT 13667 was prepared as part of AR EVAL 314868 (MALT AS 314868-06). The failure to perform the DES-2-22 and DES-2-23 actions associated with implementation of this MALT appears to have occurred because the Responsible Engineer in Portal J for the MALT was not updated when that engineer left the company and because a tracking assignment under AR EVAL 314868 for implementation/turnover/closeout of the MALT was not created per DES-2-10 by that Responsible Engineer when the MALT was approved. Although EC MALT 13667 and its associated EC CMR 14707 were cross-referenced to parent AR EVAL 315868, the AR EVAL was advanced to COMPLETE on 09/18/17. Although actually implemented, EC MALT 13667 was set to administratively EXPIRE on 11/19/18. . 1) AR-EFIN alert group personnel for EC MALT 13667 have been notified of this issue. 2) The EC MALT 13667 'Expires On' date has been administratively adjusted from 11/19/18 to 11/19/20. 3) The Resp Engr for EC MALT 13667 has been updated to indicate an E-FIN engineer currently employed by EN CGS. 4) EC CMR 14707 associated with EC MALT 13667 has been advanced to MODIFIED status. . Recommend resolution assignment to AR-EFIN for completion of the remaining DES-2-22, DES-2-23, and DES-2-25 actions associated with EC MALT 13667. The only document on the ADL for EC MALT 13667 is Update Priority 2 (update within 90 days) AED MMDS RHR-MO-40. . This condition is an administrative issue and does not affect the continued operation, function, or qualification of any station SSCs. | 02-00-RHR-MO-40
386873 | CR | 20181116 |  | 4 | OG-RF-20A oil level high. | N | N |  | N | YES | <D> **** Detailed Description **** OG-RF-20A oil level is high when S/D. Spec is 1/3 to 1/2 of S/G when S/D. Actual level is about 7/8 ( nearly full ) when S/D. Plaease adjuist oil level as necessary. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** RW 452 | 02-00-OG-RF-20A
386874 | CR | 20181116 |  | 3 | Improper use of keys in miscellaneous key locker. |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.3.23 requires individuals requiring use of a key to obtain permission from either a PSRO or the CRS and then check out the key by filling out the key log. Numerous instances of keys missing without being checked out have occurred and continue to occur. The key to the key locker is normally left in the door to the locker. None of the keys are bypass, interlock, or cyber keys as those type of keys are not stored in the miscellaneous key locker <I> **** Actions Taken **** Informed the shift manager and removed the key to the key locker which will force people to comply with the procedure and contact the PSRO or the CRS in order to obtain the key which they need.
386885 | CR | 20181116 | CAQ | D | Suspected failed SW-TE-110A | Y | N |  | N | YES | <D> **** Detailed Description **** As SW-P-1A was started, SW-TE-110A (upper thrust bearing temp) spiked to 300F, the upper end of the elements range. Lower thrust brg and stator temps are all normal. There are no indications locally of overheating on the thrust bearing. See computer point W089 at about 1300 on 11/16. <I> **** Actions Taken **** Ops 4 investigated. WR written. eDNA trend image attached to EDMS docs <N> **** Equipment Description **** SW A pumphouse. | 02-00-SW-M-P/1A,02-00-SW-TE-110A
386886 | CR | 20181116 |  | 3 | NRC Concern: Discrepancies with posted FSIPs and work plan. |  |  |  | N | NO | <D> **** Detailed Description **** NRC Concern: FSIP 17-0377 was posted at CAS but had been CLOSED since 4/26/18. FSIP 16-0293 was also posted at CAS but is PENDING. FSIP 16-0293 is tied to WO# 02094505 to repair an issue noticed in 2016, which has been returned to planning. NRC resident would like to be updated (via e -mail) the status of the WO concerning when the repairs will be made. <I> **** Actions Taken **** Both impairments were removed.
386887 | CR | 20181116 |  | 3 | Different style of gasket identified than issued for SAT-V-1 | N | N |  | N | NO | <D> **** Detailed Description **** During SAT-V-17 removal WO 02126073-01 it was identified that the gaskets removed were a Teflon style vs the CGI style issued. The flanged connection was blind flanged reusing one of the old Teflon style gaskets. This issue will need to be addressed/verified prior to final installation of SAT-V-17. <I> **** Actions Taken **** Documented in CR, will work with planning / engineering for correct gasket type | 02-00-SAT-LG-2,02-00-SAT-V-17
386888 | CR | 20181116 |  | 4 | TMU-P-1C has excessive packing leakage. | N | N |  | N | YES | <D> **** Detailed Description **** TMU-P-1C has excessive packing leakage. see video <I> **** Actions Taken **** wrote cr | 02-00-TMU-P-1C
386889 | CR | 20181116 |  | 4 | RRC-IMD-ASD1B/2 alarm recorder is out of paper | N | N |  | N | YES | <D> **** Detailed Description **** RRC-IMD-ASD1B/2 alarm recorder is out of paper/ please see video | 02-00-RRC-IMD-ASD1B/2
386890 | CR | 20181116 |  | 3 | osp-sgt-m701(-m702) procedure change. | N | N |  | N | NO | <D> **** Detailed Description **** PMID 16310 and 16311 frequencies have changed from 6 months to annually. Update prerequisite 3.3 to reflect this or remove the frequency. This may affect other procedures and surveillances. <I> **** Actions Taken **** Verified change in requirements
386891 | CR | 20181117 | CAQ | D | Temporary Ultrasonic flow instrument for SW-FI-41 frozen | Y | Y |  | N | YES | <D> **** Detailed Description **** Found flow indications frozen on SW-FI-41 ultrasonic frozen or paused. Clock on the detector was still working. Temporary detector installed for WR 29143908. <I> **** Actions Taken **** Informed MCR, expanded team to debate on attempting to reset detector by cycling power, we determined at this time only to initiate an AR. | 02-00-SW-FI-41
386897 | CR | 20181117 |  | 3 | RW 467â€™ VESDA 1 Trouble is locked in. | N | N |  | N | NO | <D> **** Detailed Description **** RW 467â€™ VESDA 1 Trouble alarm is locked in. This system is not currently turned over to Operations at this time; this CR is for information for the VESDA project to ensure they are aware of this trouble alarm. <I> **** Actions Taken **** Informed MCR <N> EPN?
386898 | CR | 20181117 | CAQ | D | FP-V-127 packing leak | N | Y |  | N | YES | <D> **** Detailed Description **** FP-V-127 has a 4-5 drops per minute packing leak. <I> **** Actions Taken **** Informed MCR & HP | 02-00-FP-V-127
386899 | CR | 20181117 | CAQ | D | RPS-RLY-K4D is noisy | Y | N |  | N | YES | <D> **** Detailed Description **** RPS-RLY-K4D is noisy compared to the adjacent relays. The noise is cyclic in nature and occurring multiple times per second. RPS-PLY-K4D is energized normally. There is no visible movement of the relay contacts and the temperature is roughly the same as the relays adjacent to it. Failure of the relay is unlikely to occur in the immediate future. <I> **** Actions Taken **** Informed CRS and had other operators look and listen to RPS-RLY-K4D. | 02-00-RPS-RLY-K4D
386900 | CR | 20181117 | CAQ | D | FP-V-127 Packing gland broke | N | Y |  | N | YES | <D> **** Detailed Description **** While conducting PM 15.1.19 (02124518) found a packing leak of 4-5 DPM, attempted to adjust packing and packing gland broke, valve is backseated and still functional. Work request has been generated 29145648 to repair replace valve. <I> **** Actions Taken **** notified WWM, Ops and maintenance and generated work doucument to repair/replace valve 29145648 | 02-00-FP-V-127
386901 | CR | 20181117 | CAQ | D | DG4 float voltage high out of spec | N | Y |  | N | YES | <D> **** Detailed Description **** While conducting PMT of DG4 battery replacement, DG-B0 -DG4/A & DG-B0-DG4/B, 02110025 & 02110026, found float voltage high out of spec (26.2 - 27.0) reading was 27.4, per PPM 10.25.5H attachment 9.1, notified engineering to evaluate. <I> **** Actions Taken **** Informed WWM, OPS Maintenance and engineering to evaluate <N> **** Equipment Description **** DG4 south of diesel building | 02-00-DG-B0-DG4/A,02-00-DG-B0-DG4/B
386902 | CR | 20181117 |  | 4 | SP-4 CPS-1000 Sampler Leaking | N | N |  | N | YES | <D> **** Detailed Description **** SP-4 CPS-1000 is leaking water, but the exact source of the leak has not been identified. <N> **** Equipment Description **** TB 441' Sample Room, inside PSR-SR-3 | 02-00-PSR-SR-3
386903 | CR | 20181117 |  | 4 | TDAS-MUX-15 caused lmultiple alarms on PPC-PRN-A1 | N | N |  | N | YES | <D> **** Detailed Description **** TDAS-MUX-15 caused lmultiple alarms on PPC-PRN-A1 and the one in the back of the control control room. Did open the front cover panel for more cooling but issue still exist. Need to investigate and repair. <I> **** Actions Taken **** Turn off both line printers in the control room to save papers printer. CRS/SM informed. | 02-00-TDAS-MUX-15
386904 | CR | 20181117 |  | 4 | E-CP-RBHV/A, Drop 3-2, REA-FN-2A temp irregular operation | N | N |  | N | YES | <D> **** Detailed Description **** Drop 3-2 of E-CP-RHHV/A is operating irregularly. When both light bulbs are installed, neither will illuminate during Annunciator testing. If one light bulb is removed, the other will illuminate very faintly. Both light bulbs were verified to be good by inspecting the filament. See attached EDMS for questionable cameraman work, of irregular operation. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RB 572 | 02-00-E-CP-RBHV/A
386905 | CR | 20181118 |  | 3 | Tagout D-RVP-RV-1-001 Should have tagged Capture closed val |  |  |  | N | NO | <D> **** Detailed Description **** Tagout D-RVP-RV-1-001 Should have tagged Capture closed valve RVP-V-55 as it is a large 90 degree valve. <I> **** Actions Taken **** informed MCR and will annote the tagout as tagging valve captured closed <N> **** Equipment Description **** tagout
386906 | CR | 20181118 |  | 3 | D-MS-ST-5B/6B-001 had two valves shouldnt captured closed |  |  |  | N | NO | <D> **** Detailed Description **** D-MS-ST-5B/6B-001 had two valves that shouldnt have been captured closed. MS-V-171B and MS-V-173 B were large handwheel operated valves. <I> **** Actions Taken **** Discussed with supervision and Decided that we would proceed wioth no capture device. These valves are handwheel operated through a gearbox device and so the potential of bumping and causing a misposition does not exist. This CR is to document this for future clearances. <N> **** Equipment Description **** tagout AED-MEC-M502-2 shows these valves as ball valves. | 02-00-MS-V-171B,02-00-MS-V-173B
386907 | CR | 20181118 |  | 4 | Burning smell coming from Terminal Box in Flocculator Buildi | N | N |  | N | YES | <D> **** Detailed Description **** There is a burning smell coming from inside an unmarked terminal box near the NW door to the flocculator building. No damage was visible inside the terminal box. The smell seems to be coming from the conduit tube. The conduit tubes are labeled â€œCTS2 DIV-Bâ€ and â€œCTS3 DIV-Bâ€ The conduit comes out of the ground to the terminal box and back into the ground. See EDMS for photos. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** Building 33 Water Filtration Building
386908 | CR | 20181118 |  | 4 | CW-P-1B Coupling inspection port safety cover | N | N |  | N | YES | <D> **** Detailed Description **** The coupling inspection port safety cover was not re -installed after CW-P-1B lift. This safety cover should be re-installed. See EDMS for Photos. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** CWPH | 02-00-CW-P-1B
386909 | CR | 20181118 |  | 4 | TMU-CB-TMU1B Overcurrent Relay Found Tripped | N | N |  | N | YES | <D> **** Detailed Description **** TMU-RLY-5051/TMU1B/C was found tripped. TMU-P-1B was not running at the time. With CRS direction the Overcurrent relay was able to be reset. This CR is for Trending only. See EDMS for Photos <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TMU Pumphouse | 02-00-TMU-RLY-5051/TMU1B/C
386910 | CR | 20181118 |  | 4 | Schedule Conflict |  |  |  | N | NO | <D> **** Detailed Description **** Both D-CRD-P-1B-002 and D-CRD-CB-P1B-001 are scheduled to hang at the same time; however the required positions conflict with each other. It appears that this was identified during planning but the clearances were scheduled to hang at the same time anyway. <I> **** Actions Taken **** Informed the WWM of the conflict.
386911 | CR | 20181118 |  | 4 | Conflicting clearances scheduled to be performed at the same |  |  |  | N | NO | <D> **** Detailed Description **** The clearance associated with WO 02108762 (D-CRD-CB-P1B -001) conflicts with the clearance for WO 02104711 (D-CRD -P-1B -002). The conflict is clearly identified in the clearance notes for D-CRD-CB-P1B -001. <I> **** Actions Taken **** Discussed with SM and WWM agreed to not hang both clearances at the same time.
386912 | CR | 20181118 | CAQ | C | SOP-DO-OPS prerequisite not able to be performed as written. |  |  |  | N | NO | <D> **** Detailed Description **** New revision of SOP-FO-OPS requires that the CRS review the most recent copy of CSP-DO-C101. This step was not able to be completed as written as this surveillance is not available for review; it was last completed 7-23-18 and has not been scanned into QAR documents yet. The intent of this step was accomplished by reviewing the sample results in NuclearIQ.
386916 | CR | 20181118 |  | 4 | Orange/Black Nitrogen bottles needed in Railroad Bay |  |  |  | N | NO | <D> **** Detailed Description **** There are currently zero full orange/black nitrogen bottles in the railroad bay which is less than minimum required per logs ( Min: 1). Two empty bottles in storage racks and none in portable racks. <I> **** Actions Taken **** SSS and Operations Coordinator notified <N> **** Equipment Description **** RX BLDG 441 RAILROAD BAY
386917 | CR | 20181118 | CAQ | D | DG4 belts scraping | N | Y |  | N | YES | <D> **** Detailed Description **** While running DG4 for PMT after battery maintenance the belts were heard to intermittently make a distinct scraping noise. <I> **** Actions Taken **** Informed MCR | 02-00-E-GEN-DG4
386918 | CR | 20181118 |  | 4 | CO-P-2B inboard bearing abnormal oil usage | N | N |  | N | YES | <D> **** Detailed Description **** Oil was reqired to be added to CO-P-2B inboard bearing, twice in a 7 day period. Both oil additions were of 2 or 3 ounces. 2 - 3 ounces is equivalent to finding the oil bubbler completely empty. Please investigate/repair/adjust bubbler operation. <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** Aux Boiler room, TG 441 | 02-00-CO-P-2B
386919 | CR | 20181118 |  | 4 | Wasp(s) in TMU pumphouse. |  |  |  | N | YES | <D> **** Detailed Description **** There was a large wasp guarding the stairs going into the basement of the TMU pumphouse. Out of safety concerns logs in the basement were not taken. <I> **** Actions Taken **** Initated AR. Informed MCR. <N> **** Equipment Description **** TMU Pumphouse, Building 51
386921 | CR | 20181119 |  | 3 | Schedule not ready for implementation |  |  |  | N | NO | <D> **** Detailed Description **** FPSI 18-0300 and 18-0302 for SL-61/6N outage have not been evaluated and are still at draft. <I> **** Actions Taken **** Informed WWM and SM.
386922 | CR | 20181119 |  | 3 | Failed HDD on IBMDISK1 for TSM storage | N | N |  | N | YES | <D> **** Detailed Description **** DriveID 14 in slot 13 (a 900GB 10K drive) has failed in IBMDISK1, the IBM storage array used for TSM. There was a spare 900GB drive in the array that took over for the failed drive. The 900GB drives are also in a RAID5 configuration, so no data was lost and we still have the ability to lose 1 drive in the RAID5 array without losing any data. <I> **** Actions Taken **** PMR 68825,227,000 was created with IBM and a replacement drive will be shipped overnight and should arrive Tuesday, 11/20/18. Suggest Non CAQ 3 to track the replacement fo the failed drive. <N> **** Equipment Description **** Corp Computer equipment. No EPN. Not plant-related.
386923 | CR | 20181119 |  | 4 | Contract tech rep discussion with vendor |  |  |  | N | NO | <D> **** Detailed Description **** Contract tech rep asked software vendor for version of software before contract was finalized. <I> **** Actions Taken **** Coaching received. No actions needed. NCAQ 4 for trending.
386925 | CR | 20181119 |  | 3 | UNABLE TO PROCESS DRAWINGS |  |  |  | N | NO | <D> **** Detailed Description **** DESIGN ENGINEERING ORG 54410 SUBMITTED DRAWINGS TO DOCUMENT CONTROL TO BE PROCESSED WITH SOME OF THESE BEING TOP TIER DRAWINGS. DOCUMENT CONTROL IS UNABLE TO PROCESS DUE TO EC BEING AT THE WRONG STATUS. <I> **** Actions Taken **** DOCUMENT CONTROL SUPERVISOR WAS INFORMED OF ERROR, DRAWINGS WILL BE PLACED ON HOLD UNTIL NECESSARY CHANGES ARE MADE. CR WAS ISSUED.
386926 | CR | 20181119 |  | 4 | Lighting under DG 4 is out and needs replaced. | N | N |  | N | NO | <D> **** Detailed Description **** Lighting under DG 4 is out and needs replaced. Contact security at 2185 for details. <I> **** Actions Taken **** CR/WR initiated. Security supervision notified. <N> **** Equipment Description **** DG 4 south of Diesel Generators.
386928 | CR | 20181119 |  | 3 | (QA) At Risk Behaviors Observed During Backfill Work |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) At risk worker behaviors were observed during an observation of Service Water (SW) Pipe Heat Trace Backfill Activities â€“WOT 02094048-09 HT-HTP-FP/7 Backfill A Quality Auditor observed excavation backfill and compaction activities as part of QC continuous monitoring and OF.2 Risk Observation activities including QC inspections, vendor-performed density measurements, heavy equipment operation, backfill and compaction activities as well as supervisory oversight and engagement. The following deltas were noted: â€¢ A worker dropped a large sheet of plywood (shoring) while lifting it out of the excavation and over a red danger tape barrier. The sheet fell to the ground knocking over a plastic barrier stanchion. The observer discussed this with the craft supervisor, who did not see the drop, and coached the worker on the at risk behavior. â€¢ A worker jumped into an excavation approximately 4 feet deep with a long handled shovel in hand which contacted a loader bucket. The worker was coached relative to this behavior and encouraged to step down into the hole or use a ladder. Insights â€¢ In these cases the worker placed themselves or their coworker(s) at risk from their activities from either a falling piece of plywood or a shovel in hand or personal impact with a large loader bucket at head level a few feet away. â€¢ The supervisor observing did not intervene prior to the coaching in the instances noted nor did they elect to stop work to address the dropped plywood sheet once informed by the observer. This would have been a good opportunity to rezero the crew and discuss at risk behaviors which may have caused a different mindset where the worker elected to not jump down into the excavation a few minutes later. <I> **** Actions Taken **** Caoched workers. Notified supervisor of issues. Debriefed supervisor and manager of events. Coached all individuals involved. Notified Quality Manager. <N> Williams Plant Services.
386931 | CR | 20181119 | CAQ | D | TEA Temporary Sample Cart Low Flow | N | Y |  | N | YES | <D> **** Detailed Description **** TEA Temporary Sample Cart cannot achieve desired flow rate of 96 SLPM per procedure 12.5.35B. Able to achieve 85 SLPM with the bypass valed closed and sample line fully opened. <I> **** Actions Taken **** Specialist and Supervisor informed. <N> The lower flow rate through the sample cart can be attributed to the sample nozzles needing cleaning. WO 02134937 is already planned to do the cleaning and should be performed so that higher flow rates can be achieved. AR 386258 noted the sample flow trend and attributed lower flows to smoke contaminants from all the recent fires. Low flows on the sample cart is still an issue when not connected to the plant [ref CR 386765] and the blower and muffler should be looked at. It is possible that the muffler may have some internal resistance due to the smoke contaminants and should be inspected/cleaned or replaced. Additionally, the sample hoses on the cart should be inspected for any buildup and cleaned/replaced if needed. | 02-00-HP-EQ-42808
386932 | CR | 20181119 |  | 4 | Halogenation Peristaltic Pump Hose Ruptured | N | N |  | N | NO | <D> **** Detailed Description **** The halogenation trailer peristaltic pump hose for the CW sodium hypochlorite pump A ruptured during halogenation 11/19/18 (Monday). The Chemistry Technician performing the halogenation found the pump leaking due to the ruptured pump tube and safely shut down the halogenation system and isolated the pump. All the hypochlorite that leaked from the pump was contained in the building and in the designed spill containment. No release to the environment occurred. The building was vented by opening the main and end doors due to the strong chlorine smell. The â€œBâ€ side halogenation line up is available for halogenations while the â€Aâ€ is isolated for repair by Suez. Spill containment is still less than half full and continues to meet spill containment needs. <I> **** Actions Taken **** The trailer is leased from Suez Water Technologies Solution who is responsible for maintaining the systems and the trailer. Suez has been called to perform the repairs and clear the containment area of chemicals. Chemicals from the containment will be used to halogenate the CW as the original intended use. <N> The repairs have been made by Suez Water Technologies Solution. No further action required.
386933 | CR | 20181119 |  | 4 | Late entry in eSOMS for Maintenance - Week of 11/3/18 |  |  |  | N | NO | <D> **** Detailed Description **** An electrician was asked to work a 12-hour overtime shift but only 10 hours were entered into eSOMS. No violation occur when hours were corrected. <I> **** Actions Taken **** Updated eSOMS with correct hours
386934 | CR | 20181119 |  | 4 | Late eSOMS entries for Maintenance - Week of 11/10/18 |  |  |  | N | NO | <D> **** Detailed Description **** Three mechanics had late eSOMS entries the week of 11/10. One was because the mechanic left later than his scheduled PT was to start. The other two had holdover time entered on the wrong day (Thursday instead of Friday). No violations occured when eSOMS was corrected. <I> **** Actions Taken **** eSOMS updated with correct hours
386935 | CR | 20181119 |  | 4 | Computer point L076 found out of tolerance | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of ISP-SW-X305B under WO 02104508 01 computer point L076 was found out of tolerance low at 2 cardinal points. <I> **** Actions Taken **** Per step 7.7.1.b noted on cover sheet and initiating a work request. <N> **** Equipment Description **** 501 MCR
386936 | CR | 20181119 |  | 3 | Emergency stop occurred during LP lobe alteration machining |  |  |  | N | YES | <D> **** Detailed Description **** On 16Nov2018, the vendor provided notification of an unexpected machining event that occurred while performing lobe alterations on the LP rotor removed from MS-DT-1A in R23 [rotor Serial Number TE-44411]. The event was an automatic emergency stop on the side entry mill machine while machining the middle lug of groove 72 on the GEN end L-0 blade groove. The automatic stop is a safety feature of the machine. This condition is isolated to a rotor in the vendor facility and is not currently is service plant equipment. Once refurbishment is complete, this rotor is slated for installation in R24. <I> **** Actions Taken **** The vendor performed the following immediate actions: 1. the vendorâ€™s maintenance team investigated the input signals to the automatic trip, 2. The tool was removed from the machine in order to remove it with the least impact, 3. The vendor charted a small irregularity at the point where the tool stopped, and 4. The vendorâ€™s engineering department evaluated the impact of the irregularity and repair method. <N> **** Equipment Description **** located in vendor facility | 02-00-MS-DT-1A
386937 | CR | 20181119 |  | 4 | No Lighting and water on floor in RB 548' RHR A HX Room | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** When going to perform a pre-job survey in the RB 548' RHR A HX room it was discovered that the lights did not work in the room. A plug in light was retrieve to perform the survey. During the survey water was discovered on the floor which apprears to be coming from the SE side of the room near the Contamninated Area boundary (See Survey 20181117 -1). Due to poor lighting I was unable to determine the location of the leak. The floor and water were <1000dpm/PA-LAS. These issues should be address in a timely manner due to upcoming work in the room. <I> **** Actions Taken **** Noted conditions on survey. Researched if any CRs had been written on either concern in the room. Notified RP Supervision. Initiated CR
386940 | CR | 20181119 |  | 4 | MET-MT-14 Rain Gauge found out of tolerance | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of W/O 02124184-01, ICP-MET-S302, MET-MT-14 was found non-functional. Cleaning and calibration was not successful. CR# 380492 was written 05.23.18 stating the following: â€œDuring the performance of, 02121316-01, ICP-MET-S302 the Rain gauge MET-MT-14 did not have expected number of tilts in step 7.2.11. Cleaning and calibration was not successful.â€ WR# 29142803 was written and is still open. <I> **** Actions Taken **** Contacted CRS, Wrote CR, referenced previous CR & WR. | 02-00-MET-MT-14
386942 | CR | 20181119 | CAQ | C | Minor Inconsistencies in ISFSI Calc CE-02-01-20 |  |  |  | N | NO | <D> **** Detailed Description **** Minor inconsistencies were identified in calculation CE -02-01-20, Calculation For Evaluation Of Underground Utilities For Cask Transportation Path Sargent and Lundy's Calculation SLENW-CALC-02. The calculation indicates the Independent Spent Fuel Storage Installation (ISFSI) duct bank cover is 3 feet. The installed duct banks for the three (3) existing pads and the proposed duct banks for future pads are at 2â€™ 9â€. The calculation indicate the conduit drains have 3â€™ 6â€ cover. Actual conduit drain cover for Pads 1 & 2 is 2â€™ 10â€. . No SSCs are judged to be impacted by these inconsistencies. . Recommend a Category 3 and assignment to AR-CMC for correction to calculation. <I> **** Actions Taken **** Reviewed condition with Civil Design Engineering Supervisor with a judged no impact to buried commodities in the ISFSI facility. <N> All actions completed as per assignment 01. No further actions required. This AR-CR is now closed. .
386947 | CR | 20181119 |  | 4 | Leak on DW piping to SW side of RHR-HX-1A | N | N |  | N | YES | <D> **** Detailed Description **** Leak of approximately 4-6 drops per minute coming from piping at DW-CE-2A. This pipe was DW serving the SW side of the RHR-A heat exchanger but is now deactivated. Leak identified by HP, and investigated by Ops to find the source. <I> **** Actions Taken **** Informed SSS <N> **** Equipment Description **** R548 HX Room south wall | 02-00-DW-CE-2A
386948 | CR | 20181119 |  | 3 | R24 procedure change SOP-ELEC-SM3-MAINT |  |  |  | N | NO | <D> **** Detailed Description **** SOP-ELEC-SM3-MAINT step 5.8.3 and 5.8.4, should just say ENERGIZE E-SM-3 per SOP-ELEC-4160V-OPS, step 5.8.4 should just say ENERGIZE E-SM-8 from E-SM-3 per SOP-ELEC-4160V -OPS, due to source bus availability TRS or TRB maybe being OOS. <I> **** Actions Taken **** wrote CR
386949 | CR | 20181119 |  | 3 | Potential task missing from Model WO's for hi-pot test |  |  |  | N | NO | <D> **** Detailed Description **** AR 178909 initiated on 3/19/2008 to split the 5 NonSeg buses inspection PM's from one PMID-RQ for each bus to 3 PMID-RQ's for each bus. This was to be done to the PM Requirement 01 for the following PMID's 00019475, 00019476, 00019477, 00019478, & 00019479. The 01 PM Requirement was split into 01, 02, & 03 for each PMID. See AR 178909 Attribute - Model W/O-Notes for the details. When the 02 RQ was created for each PMID, the Hi-Pot testing was also included in the model work order and subsequent executable work orders. When the 03 RQ was created for each PMID, the Hi-Pot testing was not added to the Model Work orders. Hi-Pot testing task were added to the executable work orders once generated for last occurance but not for the executable for next occurance. So current state for each PMID RQ 01 and 02 perform a Hi -Pot test of each NonSeg bus and RQ 03 does not. This has the Hi-Pot test being performed on the second and forth year but not the sixth year on each NonSeg bus. There is the potential of missing task from the model wo's on the 03 RQ's for hi-pot testing or added one not needed on the 02 RQ's for doing the hi-pot testing. Need engineering to review which. If the hi-pot is required every outage then the Model WO for the 03 RQ's need a task added to perform. Also an OSCR needs to be submitted to have a tasks added to each of the current executable work orders for R-24 due to the increase in scope. If the HI-Pot is only required every third outage then delete the Hi-Pot tasks from the 02 RQ's Model WO's. Before AR 178909 was submitted the Hi-Pot was only required every 4 years, not every 2. <I> **** Actions Taken **** Researched the issue once it was discovered Hi-Pot testing for NonSeg buses was not in R-24. Contacted the System Engineer to see if needed and initiated this CR for resolution.
386950 | CR | 20181119 | CAQ | D | FP-PI-D58 pressure is at 270 psi. need to be replaced | N | N |  | N | YES | <D> **** Detailed Description **** Working 15.1.19 found FP-PI-D58 header pressure to be reading wrong. pressure was above 300 psi , by tapping on the gauge pressue dropped to 270 psi. needs to be replaced. | 02-00-FP-PI-D58
386951 | CR | 20181119 |  | 4 | CO-P-2B inboard bearing loosing oil | N | N |  | N | YES | <D> **** Detailed Description **** CO-P-2B inboard bearing oil cup has been filled 2 time in the last week and is lowering at a rate of about 1/4 of an inch a shift. <I> **** Actions Taken **** CR/WR was initiated and CRS was informed. | 02-00-CO-P-2B
386952 | CR | 20181119 | CAQ | D | Recommend changing out the High range detector for WEA-SR-25 | N | Y |  | N | YES | <D> **** Detailed Description **** This CR recommends changing out the High range detector for WEA-SR-25 to reduce the number of nuisance alarms due to the following history. The detector that is currently installed is fully capable of performing its Function. . â€¢ Rad Cal WO 02102537 adjusted the HVPS from 1065 to 1080 for the High Range detector on 6/22/2017 as part of the calibration procedure. This increased the sensitivity of the detector (which was expected) and resulted in alarms in the control room [ref CR 368186]. Background subtract was then used to account for the expected increase in readings. (The vendor recommends using this feature to correct the detector activity count rate for static background radiation.) . â€¢ In the following months, more alarms were received in the control room and it was found that the area dose rates had gone up since the calibration was performed. The increase was due to resin fines from EDR-TK-1 and how the spent resin is processed [ref CR 381126]. The spent resin is getting into the ductwork and trapped in the filters of WEA-FU-1A, -1B & -1C. The filters on all 3 filter units were changed out in a span of 10 months. However, the control room continued to receive alarms after the last filter changeout. After reviewing the trend data from HP, it showed that WEA-FU-1C contact dose rate had increased since the filters were changed out in September 2017 [ref CR 382527]. . â€¢ Current dose rate in front of the sample rack is 1 to 5 mR/hr (Survey map #20180929-2, taken 9/29/2018) and floor level dose rates from the overhead duct work near the sample rack is 3.5 to 4 mR/hr (Survey map #20181024-4, taken 10/24/2018). . â€¢ Due to the changing nature of the area dose rates near the sample racking, it is recommended that the High range detector be changed out. The vendor calibration of the spare detector was reviewed and it has a lower HVPS and gain settings which would make it less prone to alarms from the area dose rates constantly changing. It would also remove the need to constantly change the value of the background subtract feature and potentially mask actual conditions in the sample stream. <I> **** Actions Taken **** Discussed with HP, Chemistry and Engineering Supervisor | 02-00-WEA-RE-14A,02-00-WEA-SR-25
386953 | CR | 20181119 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 237 B: 237 C: 237 E-TR-B A: 118 B: 118 C: 118 The following sensors were tripped and are reset: J7 - 500KV Neutral Ground Overcurrent BPA reports the following: a. Cause was Ashe - Slatt 500KV line relayed off and then reclosed b. Relaying involved a single pole c. no damaged equipment d. line reclosed e. no emergent work or line outage required f. did not affect the 230KV or 115KV systems.
386954 | CR | 20181119 | CAQ | D | Received Oscillograph Started, H13-P800.C4.4-3, alarm | N | N |  | N | NO | <D> **** Detailed Description **** Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 237 B: 237 C: 237 E-TR-B A: 118 B: 118 C: 118 The following sensors were tripped and are reset: J7 - 500KV Neutral Ground Overcurrent J12 - SM-8 Undervolatge BPA reports the following: a. Cause was Ashe - Slatt 500KV line relayed off and then reclosed b. Relaying involved a single pole c. no damaged equipment d. line reclosed e. no emergent work or line outage required f. did not affect the 230KV or 115KV systems.
386955 | CR | 20181119 | CAQ | D | TIP-MON-3A and 4 fuses not illuminated during surveillance | Y | Y |  | N | YES | <D> **** Detailed Description **** During performance of WO#02104544-01, ISP-MS-Q942, TIP -MON-3A and TIP-MON-4 fuse 5 were not illuminated during step 7.19.6. <I> **** Actions Taken **** Notified CRS, wrote this CR. | 02-00-TIP-MON-3A,02-00-TIP-MON-4
386956 | CR | 20181119 |  | 3 | Evaluate enhancements for CDA troubleshooting |  |  |  | N | NO | <D> **** Detailed Description **** Review the process for identifying potential cyber attacks on Critical Digital Assets to identify opportunities to increase awareness and alignment between cyber security and other key departments (e.g., Operations, Maintenance, Security, and Licensing). This could incorporate learnings from internal OE, industry benchmarking, procedure review, and EN practices around other regulatory programs (e.g., Emergency Preparedness, Security, etc.) <I> **** Actions Taken **** Initiated industry bencharmking with NEI cyber security taskforce peers & provided interim awareness communication to Operations crews. <N> 18-0145 initiated
386957 | CR | 20181119 | CAQ | D | CCH-PI-3B Low following CCH-CR-1B Start | Y | Y |  | N | YES | <C> Trend to CR 380635 <D> **** Detailed Description **** CCH-PI-3B was LT 5 psig and SW-FIS-35B was indicating stable flow following start of CCH-CR-1B per OSP-CCH/IST -M702 step 7.1.41 c the surge tank level was increased and CCH-PI-3B stabilized out at around 10 psig. Flow indication on SW-FIS-35B was stable and increased about 10 gpm. Per OSP-CCH/IST-M702 step 7.1.4 1e this CR is for trending. This is the same issue as CR 380635 <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RW 525 | 02-00-CCH-CR-1B,02-00-CCH-PI-3B
386958 | CR | 20181120 |  | 3 | FP-CP-ISD/1 Vesda panel fault | N | N |  | N | YES | <D> **** Detailed Description **** In RW 467 vital island, FP-CP-ISD/1 is currently reading Fault Zone 20. There are no logs on this panel, but CR is written for investigation purposes. <I> **** Actions Taken **** Initiated CR. | 02-00-FP-CP-ISD/1
386959 | CR | 20181120 |  | 3 | Evaluate material staging practices, compliance with MI-1.8 |  |  |  | N | NO | <D> **** Detailed Description **** Tours of the plant have revealed numerous areas where material is staged with work-in-progress signs that point to a generic â€œemergent maintenanceâ€ work order. It appears that the â€œemergentâ€ work order is being used as a way to stage materials for extended periods of time. Discussions with operators revealed that they have observed this equipment staged for a long time and they note that the work completion dates on the signs are updated periodically rather than removing the staged material. This practice is contrary to MI-1.8 section 18.5 â€œWork in Progress Postingâ€ which states that the posting is to indicate job duration, â€œnot to exceed 45 days from start date. Job duration may be extended up to an additional 45 days with Supervisor approval, if required.â€ Recommend Maintenance evaluate material staging practices and compliance with MI-1.8. If material staging is necessary, recommend identifying permanent staging areas. Also, recommend NOT using the emergent maintenance work order on work-in -progress signs. See EDMS.
386963 | CR | 20181120 |  | 3 | PCB Oil Spill Reportable to WA State Ecology | N | N |  | N | NO | <D> **** Detailed Description **** A condition report is being issued for an ongoing spill response identified in CR 00383462 for PCB transformer dielectric fluid. The spill was identified in April and PCBâ€™s were recognized in August. Initially it was determined that the spill was non-PCB and the spill was to soil that cannot be quickly controlled and or remediated. The spill is to the side surface of a transformer running to the concrete pad and off to the soil; ~2.5 gallons were released. E&RP discovered that the spill contained 13 ppm Polychlorinated Biphenyl (PCB) that placed it as a dangerous waste spill. This caused the spill to be reportable along with other state and federal clean-up requirements. <I> **** Actions Taken **** The spill was discussed in a meeting with E&RP, Facilities, Work Management, and Engineering. Alignment was reached on a path forward. An outside contractor was contacted for availability to respond and clean-up. Department of Ecology will be notified. <R> This issue has been reviewed by Regulatory Affairs for reportability. Given the low volume of PCBs in the minor spill, which did not impact any nearby sources of water, this issue does not meet the reporting requirements of 10 CFR 50.72(b)(2)(xi). | 02-00-E-TR-6/61
386964 | CR | 20181120 |  | 4 | Late eSOMS entry for Maintenance |  |  |  | N | NO | <D> **** Detailed Description **** An Electrical Supervisor came to work on a day when he was scheduled to be on PT and didn't update his time in eSOMS. No violation occured when hours were entered in eSOMS. <I> **** Actions Taken **** Updated eSOMS with correct hours.
386965 | CR | 20181120 |  | 3 | Potential Trend: Radioactive Material Control |  |  |  | N | NO | <D> **** Detailed Description **** During the October 2018 FAS meeting, a potential trend in Radioactive Material Control was discussed. In October 2018, there were two instances where radiation workers brought items labeled as radioactive material into a clean area. These two events also caused the Improper Radworker Behavior performance indicator to turn yellow in October. In April 2018, there was one event where radioactive material was found outside of the Protected Area. This event caused the â€˜Other Rad Mt Control for RPIâ€™ indicator to turn red in 2Q2018. This condition report is being initiated to validate the potential trend by completing a Trend Validation Worksheet per TM-01, Trending Manual. Recommend a NCAQ, 3/RPOPS.
386966 | CR | 20181120 |  | 3 | Potential Trend: Radiation Protection Document Quality |  |  |  | N | NO | <D> **** Detailed Description **** During the October 2018 FAS meeting, a potential trend in Radiation Protection document quality was discussed. Over the last quarter, there have been condition reports initiated and several observations documenting errors being found in RP documentation. This condition report is being initiated to validate the potential trend by completing a Trend Validation Worksheet per TM-01, Trending Manual. Recommend a NCAQ, 3/RPOPS.
386967 | CR | 20181120 |  | 4 | ASD printers need new ink ribbons | N | N |  | N | YES | <D> **** Detailed Description **** While performing WR 29145331 RRC-IMD-ASD1B/2 noticed the printer needs a new ink ribbon. Walked down the other printers 1A1 and 1A2 need new ribbons too. <I> **** Actions Taken **** Notified Supervisor | 02-00-RRC-IMD-ASD1A/1,02-00-RRC-IMD-ASD1A/2,02-00-RRC-IMD-ASD1B/2
386968 | CR | 20181120 |  | 3 | Asset Suite unavailable |  |  |  | N | NO | <D> **** Detailed Description **** Asset Suite was unavailable from approximately 0300 to 1000 on 11/20/18. The cause has been identified as an unauthorized device plugged into the corporate network. <I> **** Actions Taken **** Removed device from network, restored application to service. Recommend NCAQ 3 to ITMGMT. <N> This is not a reportable cyber secuirty event under 10 CFR. 73.77.
386973 | CR | 20181120 |  | 3 | SOP-FPC-ASSIST-ALT section 5.6 enhancement needed |  |  |  | N | NO | <D> **** Detailed Description **** SOP-FPC-ASSIST-ALT section 5.6 does not have you verify FPC-V-191 open prior to starting RHR-P-2B. FPC-V-191 is normally Locked Open. Section 5.6 has you close all other suction paths and assumes FPC-V-191 is in its normal configuration. This is an infrequently used procedure and we should verify FPC-V -191 open prior to starting a large ECCS pump from an off normal suction path. | 02-00-FPC-V-191
386974 | CR | 20181120 |  | 4 | S-DOOR-S109 install electric opener | N | N |  | N | YES | <D> **** Detailed Description **** S-DOOR-S109 is the most used door on site. it is very hard to open and close. i could see some one getting hurt trying to open or close the door pulling on the chain. THIS IS A SAFTEY ISSUE <N> AR type EVAL needed? | 02-00-S-DOOR-S109
386975 | CR | 20181120 |  | 4 | Minor Leak on HS-V-T2M | N | N |  | N | YES | <D> **** Detailed Description **** There is a very minor steam/water leak coming from the stem of HS-V-T2M. Probably just needs the packing tightened a bit. <I> **** Actions Taken **** Informed MCR | 02-00-HS-V-T2M
386976 | CR | 20181120 | CAQ | D | ISP-RPS-Q906 test box lamp stayed lit. | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of WO 02104545-01 ISP-RPS-Q906, test box stayed illuminated when it was supposed to be cleared. disconnecting the rps test box did not result in a half scram and alarms were clear prior to disconecting the box. this occured on step 7.1.35 <I> **** Actions Taken **** CRS notified of that rps test box did not clear. I&C supervision notified, CR generated. <N> **** Equipment Description **** 501 control room H13 P611 RPS-RLY- k4B
386979 | CR | 20181120 |  | 4 | CO-P-2A has bad packing leak. | N | N |  | N | YES | <D> **** Detailed Description **** CO-P-2A inboard pump packing is leaking bad enough to be running a continuous stream past two different spray shields. Please investigate and adjust / replace pump packing. See video in attributes and EDMS. <I> **** Actions Taken **** Informed supervisor and wrote AR/WR. <N> **** Equipment Description **** T443 G9/4.5 | 02-00-CO-P-2A
386982 | CR | 20181120 |  | 4 | handwheel installed upside down | N | N |  | N | YES | <D> **** Detailed Description **** MS-V-171B hand wheel installed upside down. could cause incorrect positioning of valve. <I> **** Actions Taken **** CRS/SSS notified. <N> **** Equipment Description **** TB441 in "B"steam jet air ejector rm upside down valve, left of unit, near wall | 02-00-MS-V-171B
386984 | CR | 20181120 |  | 3 | (QA) 3 Cyber Security Procedures Point to Nonexistent Docâ€™s |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) 3 Cyber Security Procedures Point to Nonexistent Docâ€™s (QA) Three Cyber Security procedures point to other documents, which do not currently exist. The potential consequence is these three procedures cannot be followed as written, which could cause confusion and a loss of productivity for the users. Factual Basis: â€¢ SWP-CSW-25 â€œCyber Security Incident Handling and Responseâ€ rev 001-001 section 2.0 â€œResponsibilitiesâ€ subsection 2.5 â€œCSIRTâ€ step 2.5.5 states, â€œInitiate in accordance with the Incident Response Plan, SWP-CSW-19â€; however: o SWP-CSW-19 â€œIncident Response Planâ€ does not exist. o SWP-CSW-19 â€œCyber Security Incident Responseâ€ has been reserved, but not yet issued. o SWP-CSW-19 is not listed in References section 9.0 in SWP-CSW-25. â€¢ GBP-IS-37 â€œIncident Response Tabletop Exercise Processâ€ rev 001 step 3.5.5 states, â€œInitiate in accordance with Incident Response Plan, SWP-CSW-19.â€ o SWP-CSW-19 â€œIncident Response Planâ€ does not exist. o SWP-CSW-19 â€œCyber Security Incident Responseâ€ has been reserved, but not yet issued. o SWP-CSW-19 is not listed in References section 9.0 in GBP-IS-37. â€¢ SWP-CSW-27 â€œCyber Security Vulnerability Management and Reportingâ€ rev 002-001 step 2.5.2 states, â€œReference DES -6-8 for guidance on applying patches/updates required to mitigate vulnerabilitiesâ€; however: o DES-6-8 does not exist. o DES-6-8 is not listed in the References section 6.0 within SWP-CSW-27. o DES-2-8 â€œDocument Only Change Process â€œis listed in References section 6.0 in SWP-CSW-27. Insight: â€¢ Initially the Cyber Security group believed SWP-CSW-19 would be required, but later it was determined a separate Incident Response Plan was not needed beyond what is covered in SWP-CSW-25 and SWP-CSW-28 â€œCyber Events Recognition, Response and Reportingâ€. â€¢ The Cyber Security group believes DES-6-8 is a typographical error and should have been DES-2-8. <I> **** Actions Taken **** Contacted the Assistant IS Manager responsible for Cyber Security. . This is a Deficiency identified during the Cyber Security Audit AU-CSQ-18. . Recommend Routing to AR-ITCYBER.
386985 | CR | 20181120 |  | 3 | (QA) GBP-IS-09 Contains Incorrect Document Information |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) GBP-IS-09 â€œCyber Security Programâ€ contains incorrect document information, including two outdated documents, two incorrect procedure titles, eight forms not used in listed procedures, and is missing two forms used in listed procedures. The potential consequence is GBP-IS-09 rev 003-005 (issued 2/20/18) cannot be followed as written, which could cause confusion and a loss of productivity for the users. Factual Basis: (See full CR details in EDMS) Insights: â€¢ Cyber Security group has GBP-IS-09 on their spreadsheet to review and update as a voluntary proactive extent of condition after Quality identified other procedure misalignments in another audit. â€¢ Cyber Security group did not identify the above issues on their spreadsheet tracked under AR 384747; however, the group now plans to add these issues to their list for updates to GBP-IS-09. <I> **** Actions Taken **** Contacted the Assistant IS Manager responsible for Cyber Security. . This is a Deficiency identified during the Cyber Security Audit AU-CSQ-18. . Recommend Routing to AR-ITCYBER.
386986 | CR | 20181120 |  | 3 | (QA) ISDI-CYBER-13 Lists Incorrect Document Information |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) ISDI-CYBER-13 â€œCyber Security Defensive Architectureâ€ lists incorrect document information, including three outdated documents, two incorrect procedure titles, three incorrect titles of forms, seven forms not used in listed procedures, and is missing one form used in listed procedures. The potential consequence is that ISDI-CYBER -13 rev 000-001 (issued 2/28/18) cannot be followed as written, which could cause confusion and a loss of productivity for the users. Factual Basis: â€¢ ISDI-CYBER-13 Section 3.1 â€œCyber Defense Overviewâ€ cites SWP-SEC-13 â€œSabotage Reportingâ€; however, the correct title is â€œSabotage Events Recognition, Response and Reporting North American Electric Reliability Corporation (NERC)â€. â€¢ ISDI-CYBER-13 Section 3.2.1 â€œProgram Monitoring, Audits and Accountabilityâ€ cites SWP-CSW-18 â€œCyber Security Assessmentsâ€ and lists forms used therein, but the following three listed forms are not used in that procedure: o Form 27013 â€œEvaluation Compliance Matrixâ€ o Form 27014 â€œAssessment Compliance Matrixâ€ o Form 27015 â€œ1310 Evaluation Matrixâ€ â€¢ ISDI-CYBER-13 Section 3.2.1 cites SWP-CSW-27 and lists forms used therein, but is missing Form 27149 â€œCyber Security Vulnerability Notificationsâ€ used twice in SWP -CSW-27 section 3.2. â€¢ ISDI-CYBER-13 Section 3.2.1 lists the following three forms with incorrect titles: o Form 26997 â€œCritical Digital Asset Modification Formâ€ (correct is â€œCritical Digital Asset Revisionâ€) o Form 27008 â€œAsset Digital Determinationâ€ (correct is â€œDigital Asset Determinationâ€) o Form 27011 â€œAsset Digital Configurationâ€ (correct is â€œCDA Master Data Sheetâ€) â€¢ ISDI-CYBER-13 Section 3.2.3 â€œConfiguration Management and Change Controlâ€ cites DES-2-18 â€œReplacement Item Equivalencyâ€, which was at â€œHistoryâ€ status on 7/1/17. â€¢ ISDI-CYBER-13 Section 3.2.5 â€œSupply Chainâ€ cites SWP -CSW-24 â€œCyber Security Procurementâ€ and lists forms used therein, but the following two listed forms are not used in that procedure, and were both at â€œHistoryâ€ status since 12/21/17: o Form 27095 â€œCyber Security Trusted Vendor Screeningâ€ o Form 27096 â€œCyber Security Trusted Distribution Path Requirementsâ€ â€¢ ISDI-CYBER-13 Section 3.4.11 â€œMedia Protectionâ€ cites SWP-CSW-15 â€œPortable Media and Digital Device Useâ€ and lists forms used therein, but the following listed form is not used in that procedure: o Form 26973 â€œCritical Digital Asset Security Control Baselineâ€ â€¢ ISDI-CYBER-13 Section 3.4.12 â€œSystem and Information Integrityâ€ cites SWP-CSW-25 â€œCyber Security Incident Handling and Responseâ€ and lists forms used therein, but the following listed form is not used in that procedure: o Form 27100 â€œCyber Security Incident Response Drill Resultsâ€ Insights: â€¢ Cyber Security group has ISDI-CYBER-13 on their spreadsheet to review and update as a voluntary proactive extent of condition after Quality identified other procedure misalignments in another audit. â€¢ Cyber Security group did not identify the above issues on their spreadsheet tracked under AR 384747; however, the group now plans to add these issues to their list for updates to ISDI-CYBER-13. <I> **** Actions Taken **** Contacted the Assistant IS Manager responsible for Cyber Security. . This is a Deficiency identified during the Cyber Security Audit AU-CSQ-18. . Recommend Routing to AR-ITCYBER.
386988 | CR | 20181120 | CAQ | C | (QA) 7 SWP-CSW-xx Procedures Not Meeting SWP-PRO-03 |  |  |  | Y | NO | <C> This CR was changed from non-CAQ 3 to CAQ C still to ITCYBER as per the MRT. <D> **** Detailed Description **** (QA) Seven site-wide Cyber Security procedures do not meet steps in SWP-PRO-03 â€œWriter's Manualâ€ for describing revision changes and identifying regulatory requirements. The potential for not identifying regulatory requirements in a procedure is the risk of the requirements being inadvertently removed from the procedure. This is a procedure use and adherence issue with no known actual consequences. Requirements: â€¢ SWP-PRO-03 rev 023 step 2.2.1c.3) â€œCover Page and Description of Change Informationâ€, which states, â€œ. . . b) INCLUDE a description of changes made to the procedure on the appropriate page relative to the changes made in the revision, regardless of type of revisionâ€ â€¢ SWP-PRO-03 section 2.2.2 â€œRules for Proceduresâ€ includes step 2.2.2l, which states, â€œ. . . 2) IF over 30% of the procedure has changed, THEN no revision bars are required AND ADD a comment on the Description of Changes page.â€ â€¢ SWP-PRO-03 includes step 2.2.2m2) â€œIdentification of Requirements, Commitments . . .â€ states, â€œWHEN a Requirement or Commitment is satisfied by a statement within the body of a procedure, THEN IDENTIFY the statement by placing the number in French brackets { }, immediately following the statement or reference or, if space is a problem, one hard return below the text as follows. a) ANNOTATE steps added as a result of a regulatory requirement in French brackets beginning with an â€œRâ€ followed by the reference number assigned under the reference section (e.g., {R-7.1}). Factual Basis: (see full CR details in EDMS Insights: â€¢ Cyber Security group has all the above procedures on their spreadsheet to review and update as a voluntary proactive extent of condition after Quality identified other procedure misalignments in another audit. â€¢ Cyber Security group did not identify the above issues on their spreadsheet tracked under AR 384747; however, the group plans to add these issues to their list for updates to the above procedures. <I> **** Actions Taken **** Contacted the Assistant IS Manager responsible for Cyber Security. . This is a Deficiency identified during the Cyber Security Audit AU-CSQ-18. . Recommend Routing to AR-ITCYBER.
386989 | CR | 20181120 | CAQ | C | (QA) LDCN 17-024 Record Missing POC Chair and PGM Signatures |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Quality Assurance Record (QAR) for Licensing Document Change Notice (LDCN) 17-024 for the Cyber Security Plan was missing required signatures for the Plant Oversight Committee (POC) Chair and the Plant General Manager (PGM). Other issues were identified on LDCN Form 24341 where blanks or check boxes should have been completed, but were not, and two forms were missing from the package. Upon notification by Quality, Information Services personnel provided the POC 17-23 Meeting Minutes showing LDCN 17-024 was presented to and approved by POC on 12/7/17 and the POC Chair and PGM both signed for approval of these minutes; however, the LDCN record copy in the vault did not document POC and PGM approval on Form 24341, contrary to SWP-LIC-03 â€œLicensing Document Change Processâ€. This is a procedure use and adherence issue with no known consequences. Requirements: (See full CR details in EDMS) Factual Basis: â€¢ The QA Record copy of LDCN 17-024 for changes to CSP-01 â€œCyber Security Planâ€ rev 003 retrieved from the vault for the audit team on 11/7/18 has the following errors on Form 24341: o Section (10) â€œPOC Meeting No.â€ was blank. o Section (10) No approval signature for the POC Chairman. o Section (10) No approval signature for the PGM. o Section (11) â€œIs the LDCN on Hold for approval?â€ â€œYes/Noâ€ boxes were not completed. o Section (12) â€œDo other Change Management actions need to be coordinated with LDCN implementation?â€ â€œYes/Noâ€ boxes were not completed. o Form 26232 â€œPOC Review Criteriaâ€ was not included in the package. o Form 26294 â€œOperability Impact Determination Screeningâ€ was not included in the package. Insights: (See full CR details for more Insights) â€¢ Information Services personnel provided the information that the required signatures were originally obtained and submitted to Records and Information Management (RIM). After it was identified five months later under AR-CR 380206 that the Cyber Security Plan changes in LDCN 17-024 were not submitted to the NRC within 60 days, RIM could not locate the associated QAR for this LDCN in the vault. As part of the Cyber Security group reproducing the LDCN package, inadvertently, not all required signatures were obtained, not all boxes were checked, and two forms were left out. â€¢ On 11/8/18, the QAR for LDCN 17-024 was corrected to resolve the above issues. <I> **** Actions Taken **** Contacted the Assistant IS Manager responsible for Cyber Security. . This is a Deficiency identified during the Cyber Security Audit AU-CSQ-18. . Recommend Routing to AR-ITCYBER.
386991 | CR | 20181120 |  | 3 | (QA) ISDI-CYBER-14 Points to Wrong Step & Wrong Attachment |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) ISDI-CYBER-14 â€œSanitization and Destruction of Electronic Media Storage Devicesâ€ points to an incorrect step number and an incorrect attachment number. The potential consequence is these two procedures cannot be followed as written, which could cause confusion and a loss of productivity for the users. Factual Basis: â€¢ ISDI-CYBER-14 rev 001 step 5.3.2c states, â€œFOLLOW Section6.4 to sanitize the driveâ€, but section 6.4 does not exist within this instruction. â€¢ ISDI-CYBER-14 rev 001 step 5.6.4 states, â€œRECORD identification number of portable media using the Disposal Inventory List Template, Attachment 10.1â€, but Attachment 10.1 does not exist within this instruction. Insight: â€¢ Cyber Security group explained that â€œSection 6.4â€ is a typographical error and it should have been â€œSection 5.4â€ in ISDI-CYBER-14. â€¢ Cyber Security group explained that â€œAttachment 10.1â€ is a typographical error and it should have been â€œAttachment 9.1â€ in ISDI-CYBER-14. <I> **** Actions Taken **** Contacted the Assistant IS Manager responsible for Cyber Security. . This is a Deficiency identified during the Cyber Security Audit AU-CSQ-18. . Recommend Routing to AR-ITCYBER.
386992 | CR | 20181120 |  | 3 | (QA) ISDI-MAINT-44 Does Not Meet a Step in GBP-PRO-03 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) ISDI-MAINT-44 does not meet one step in GBP-PRO-03 â€œPreparation, Review and Approval of Corporate Procedures, Department Instructions and manualsâ€ for describing revision changes. This is a procedure use and adherence issue with no known actual consequences. Requirements: â€¢ GBP-PRO-03 rev 006 step 3.3.3 â€œPreparing the Document Revision and Paperworkâ€ states, â€œe. ENSURE the following elements are updated . . . 1) Description of Changes . . . 4) Revision bars are included if less than 30% of the documents has changed.â€ Factual Basis: â€¢ ISDI-MAINT-44 â€œScanning Station Maintenanceâ€ rev 005 does not provide a description of changes on the Description of Changes page. <I> **** Actions Taken **** Contacted the Assistant IS Manager responsible for Cyber Security. . This is a Deficiency identified during the Cyber Security Audit AU-CSQ-18. . Recommend Routing to AR-ITCYBER.
386993 | CR | 20181120 | CAQ | C | (QA) LBIEâ€™s Not Completed for 5 Cyber Procedure Revâ€™s |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) A Licensing Basis Impact Evaluation (LBIE) was not performed for each of five Cyber Security procedure revisions, contrary to SWP-LIC-02 â€œLicensing Basis Impact Determinationsâ€. Five of six major revisions to â€œSWP-CSW -XXâ€ procedures selected for review by the audit team did not perform a LBIE as required because Applicability Determination (AD) forms were improperly completed thus allowing each LBIE to be waived. The purpose of the LBIE is to determine if the change can be implemented without prior NRC approval. While no instances were identified where prior NRC approval should have been obtained, not conforming to the established process could lead to such an issue and have negative consequences in regulatory space. Requirements: (see full CR details in EDMS) Factual Basis: (see full CR details in EDMS) Insights: â€¢ AD form Section II question #3 should have been checked â€œYesâ€ because each of the five changes were to procedures that implement regulatory requirements that could impact critical digital assets. â€¢ SWP-LIC-02, and the AD form, were revised 03/28/18 to clarify the instructions to help personnel get to the correct determination of the need for a LBIE via a newly developed LBIE Screen form. â€¢ The 10 CFR 50.59 program owner that made the 2018 clarification to the AD process explained that this clarification was not a change in policy or expectations, but was driven by a LBIE not being performed for too many procedure revisions by multiple departments across the station. <I> **** Actions Taken **** Contacted the Assistant IS Manager responsible for Cyber Security. . This is a Deficiency identified during the Cyber Security Audit AU-CSQ-18. . Recommend Routing to AR-ITCYBER.
386994 | CR | 20181120 |  | 3 | (QA) CSDG-01 Contains Incorrect Document Information |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) CSDG-01 â€œCyber Security Design Guideâ€ contains incorrect document information, including three outdated documents, two documents that do not exist, four incorrect procedure titles, one incorrect title of a form, and contains nine documents in the References section that are not cited in the guide, and the References section is missing eight procedures and one form cited that are cited in it. The potential consequence is that CSDG-01 rev 002 (issued 8/29/18) cannot be followed as written, which could cause confusion and a loss of productivity for the users. Factual Basis: (see full CR details of 32 errors in EDMS) <I> **** Actions Taken **** Contacted the Assistant IS Manager responsible for Cyber Security. . This is a Deficiency identified during the Cyber Security Audit AU-CSQ-18. . Recommend Routing to AR-ITCYBER.
386995 | CR | 20181120 |  | 4 | Wasp Infestation, TMU Pumphouse-Roof Flashing Repair Needed | N | N |  | N | NO | <D> **** Detailed Description **** The TMU pumphouse has had numerous CR written due to wasps being found inside the building. Facilities NBU Laborers have killed hundreds over the last year. The latest CR and WR was worked and an area on the roof flashing was discovered to be missing when compared to another area and remnants of caulking suggest that one had been in place in the past. The missing flashing is where the largest amount of wasps were observed and killed during this latest attempt. The flashing needs to be replaced and the building is Plant according to SWP-DES-01 and should be routed to Maintenance for repair. <I> **** Actions Taken **** Provided pictures to SM and explained the jurustictional issues that would need to be resolved if others outside of Maintenance were to perform this work. Wrote this CR and WR <N> **** Equipment Description **** TMU Pumphouse, Building 51 | 02-00-M-BLDG-MISC
386996 | CR | 20181120 | CAQ | C | (QA) Quality-Affecting Information Not in Procedures |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Examples were identified where a manual and two instructions contained Quality-Affecting information that should be contained in plant procedures. This practice introduces a risk where undesirable changes could be made by a single person with no reviews required and it opens the station up to regulatory exposure for a non-compliance with the OQAPD or the ANSI N18.7-1976 standard. These examples were spread across many different groups at the station. At Columbia, department instructions are controlled by GBP-PRO-03, Preparation, Review and Approval of Corporate Procedures, Department Instructions and Manuals, which is not designed or intended to meet ANSI N18.7-1976 â€œAdministrative Controls and Quality Assurance for the Operational Phase of Nuclear Power Plantsâ€ requirements. . The inclusion of Quality-Affecting information in department instructions results in a situation where a revision can take place without receiving the reviews required by ANSI N18.7 or consideration for reduction in commitment, effect on regulatory requirements, 10 CFR 50.59 screening, etc. Requirements: (See full CR details in EDMS) Factual Basis: (See full CR details in EDMS) Insights: â€¢ ISDI-CYBER-17 and ISDI-CYBER-23 were reviewed, but not identified as containing Quality-Affecting information under a corrective action for the Finding AR-CR 380151 â€œ(QA) Quality-Affecting information in Department Instructionsâ€ during the Document Control and Records Management Audit AU-AD-18. â€¢ SWP-CSW-12 â€œCyber Security Defensive Strategyâ€ points to ISDI-CYBER-23, but SWP-CSW-12 does not capture the NEI 08 -09 requirements for training. <I> **** Actions Taken **** Contacted the Assistant IS Manager responsible for Cyber Security. . This is a Deficiency identified during the Cyber Security Audit AU-CSQ-18. . Recommend Routing to AR-ITCYBER.
386997 | CR | 20181120 | CAQ | C | (QA) ARMA - Alt. Cyber Control & Freq. Bases not in Records |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Bases for not implementing the Cyber Security Controls in Appendices D and E of NEI 08-09 â€œCyber Security Plan for Nuclear Power Reactorsâ€ Addendum 1, and for mitigating with alternative controls, countermeasures, and frequencies were not found in Records, contrary to Sections 3.1.1 and 3.2 in NEI 08-09 Addendum 1 Appendix A. Many of the required documented bases, analyses, or justifications missing from Critical Digital Asset (CDA) Assessment Records are based on Benchmarking information, which is kept by the Cyber Security group on an uncontrolled spreadsheet. The Nuclear Regulatory Commission (NRC) endorsed the NEI 08-09 Addendum 1 as meeting the requirements of 10 CFR 73.54 â€œProtection of digital computer and communication systems and networksâ€. Accordingly, a potential consequence of this noncompliance with NEI 08-09 Addendum 1 is the exposure to a loss of regulatory margin. Requirements: (See full CR details in EDMS) Factual Basis: (See more facts in full CR details in EDMS) â€¢ The Cyber Security group sampled a few Records of CDA Assessments developed to meet NEI 08-09 Addendum 1 Appendix A Sections 3.1.3 - 3.1.5, and found no bases, analyses, or justifications therein for alternative controls, countermeasures, and frequencies not as specified in NEI 08-09 Appendices D and E. This is contrary to NEI 08-09 Addendum 1 Appendix A Sections 3.1.6.2 and 3.2. â€¢ Some bases, analyses, or justifications have been filed with Cyber Security Assessment Team (CSAT) records packages. Insights: â€¢ The Cyber Security group explained that approved CDA Assessments meeting NEI 08-09 Addendum 1 Appendix A Sections 3.1.3 - 3.1.5 are currently stored within Records. â€¢ The Cyber Security group has confidence all the information exists to support documenting the bases, analyses, or justifications required by Section 3.1.6.2 in the Assessment Records cited in Section 3.2. <I> **** Actions Taken **** Contacted the Assistant IS Manager responsible for Cyber Security. . This is an Area Requiring Management Attention (ARMA) identified during the Cyber Security Audit AU-CSQ-18. . Recommend Routing to AR-ITCYBER.
386998 | CR | 20181120 | CAQ | C | SW crosstie valve IST Program Compliance | Y | Y |  | N | YES | <D> **** Detailed Description **** During review of recent Ultimate Heat Sink Inspection findings from other stations, it was identified that the manual exercising of SW-V-69A/B and SW-V-70A/B does not meet the full intent of the ASME OM Code for exercising manual valves within the IST Program. The finding stated that in addition to manual exercising of the valves once every two years the verification of obturator (disc) movement must be done. This can be accomplished through indirect means such as the use of lights or changes in system response such a pressure, temperature or flow. The subject SW valves are manually exercised once every two years, but additional indication is not recorded within their associated surveillances to verify obturator movement. These valves are 18â€ gate valves with an internal design configuration that prevents the stem from rotating unless there is a stem disk separation. If stem rotation is observed, this is evidence that a stem to disk separation has occurred. There have been no CRs found identifying stem rotation during previous performance of these surveillances. Due to the size of these valves it is likely that the equipment operator would feel the unseating and reseating of the valve during exercising, providing assurance of the required obturator movement. The surveillance also includes a caution note providing specific guidance to exercise the valves such that valve damage does not occur. Additionally, the likelihood of obturator separation is reduced by a 4 year PM to lube the stem exists in order to ease the exercising of these manual valves. Based on the above information, there is reasonable assurance that the subject valves will be able to perform their intended design function. The non-compliance is in regards to ASME OM Code ISTC-3540 as reflected in step 5.2.10 of LBD-IST-4. <I> **** Actions Taken **** Expanded the team with system engineering and technical support engineering. Discussed with supervisors and contacted the control room. | 02-00-SW-V-69A,02-00-SW-V-69B,02-00-SW-V-70A,02-00-SW-V-70B
386999 | CR | 20181120 | CAQ | D | Benton County EOC dial up phone is not working | N | Y |  | N | YES | <C> reopened and rescreened to CAQ by CAP Supervisor <D> **** Detailed Description **** Benton County EOC identified a problem with their dial up phone as is working on resolving the issue. The CRASH and PIO are available. <I> **** Actions Taken **** Notified: EP, SCC, and the MCR <N> **** Equipment Description **** Benton County EOC
387000 | CR | 20181120 | CAQ | D | Low oil level in the lower sight glass of CCH-CR-1B | Y | Y |  | N | YES | <D> **** Detailed Description **** OPS2 noted on operator rounds that the oil level in the lower sightglass of CCH-CR-1B was 1/4" below the top of the lower sightglass. The log instructions direct that oil be added per PPM 10.2.13. instructions direct that oil be added per PPM 10.2.13. <I> **** Actions Taken **** CRS informed. | 02-00-CCH-CR-1B
387001 | CR | 20181120 |  | 4 | FPC-P-3 | N | N |  | N | YES | <D> **** Detailed Description **** during shift to Supp Pool cleanup, FPC-P-3 exhibited an abnormal "buzzing" noise. pump discharge pressure was normal and steady, and there was no indication of shaft misalignment, noise did not sound like pump cavitation. pump motor vibes were not excessive nor were temps noticably elevated. recommend vibes be taken and evaluated for potential bearing problem or other motor fault. <I> **** Actions Taken **** informed MCR and SSS initiated CR/WR | 02-00-FPC-M-P/3,02-00-FPC-P-3
387002 | CR | 20181121 |  | 4 | TOA-FN-1A | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FN-1A has no apparent power. the disconnect was found closed, with no power indicating lights lit. the breaker was taken to off with CRS direction, and the overload reset pushbutton was depressed, with no change in status. bkr was placed back in on. request electricians in <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-TOA-42-3A6B,02-00-TOA-FN-1A
387003 | CR | 20181121 |  | 4 | TB HVAC hi D/Ps | N | N |  | N | YES | <D> **** Detailed Description **** turbine bldg (TOA) intakes are becoming clogged with ice and causing the HVAC units to run at a high negative pressure. this may? have caused the trip/loss of TOA-FN-1A. request this be evaluated and ice be knocked off to prevent further damage to the TB HVAC system. <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-TOA-HV-1A
387007 | CR | 20181121 | CAQ | C | Ineffective corrective action on CR 381638 | N | Y |  | N | YES | <D> **** Detailed Description **** CR 381638 was written against TEA-FN-93 to address the baseplate being captured and not allowing removal of the unit for replacement or maintenance. This configuration does not allow access to the bolts since it is welded and captured on all four sides and needs an action to fix this before the next scheduled maintenance. As stated in the CR this was identified by FIN in 2016 and again in 2018. <I> **** Actions Taken **** Notified my supervisor and the main control room. Recommend having the base modified to allow for maintenance. <N> **** Equipment Description **** TEA-FN-93 | 02-00-TEA-FN-93,02-00-TEA-SR-26
387008 | CR | 20181121 |  | 4 | TDAS-MUX-15 A B overheating / alarmimg | N | N |  | N | YES | <D> **** Detailed Description **** TDAS-MUX-15 A B overheating / alarmimg As often happens mux overheats causing multilpe pages of alarm to be printed on the alarm timer. Request modification of the unit to amelioriate condition. Drilling more ventillation holes in the front cover or installing power supplies with froced cooling would be options. I believe the forced cooling option may already be an ongoing modification. See EDMS for impact list. <I> **** Actions Taken **** opened covers to cool components per CRS direction Limited access to the area with signage | 02-00-TDAS-MUX-15,02-00-TDAS-MUX-15A
387010 | CR | 20181121 | CAQ | D | TDAS-MUX-12 Failure | N | Y |  | N | YES | <D> **** Detailed Description **** TDAS-MUX-12 has failed. The following are impacted points: X385-02 CSP-V-96 Closed position indication on GDS X385-12 CSP-V-93 Closed position indication on GDS X399 Containment LOCA Rad Monitor Div 2 on GDS X411 Suppression Pool Average Temperature Div 2 on GDS. Other indications for these points are available in the Main Control Room. Additionally, X400 Rx Bldg Elev Release Hi is alos impacted. This point is a required ERDS parameter. Compensatory actions per PPM 13.14.11 require that an alternate indication is available to be transmitted to the NRC via the ENS line. Compensatory actions are in place if needed. EP has been notified. <I> **** Actions Taken **** Wrote CR. Established compensatory actions per PPM 13.14.11. Contacted EP. <N> **** Equipment Description **** MCR | 02-00-TDAS-MUX-12
387011 | CR | 20181121 |  | 3 | Procedure enhancement to SOP-MT-START |  |  |  | N | YES | <D> **** Detailed Description **** During a plant startup in the summer of 2016 post-outage it was discovered that the main turbine turn gear had disengaged itself (this has a chance of happening after the addition of sealing steam). Because there is no indication in the control room, this did not get identified for an unknown period of time and was suspected of causing additional vibration after brought up to speed at the time. This enhancement requests adding a step such as â€˜5.3.3 Locally verify the Main Turbine on the turn gear.â€™ 5.3.3 is a good location for it as the previous step is also a EO step verifying the exciter doors closed. The step is close enough in startup that the time at which the turn gear should automatically disengage is not far away. This allows the MCR to know if the MT came off the turn gear unexpectedly and decide on actions going forth. <N> **** Equipment Description **** procedure enhancement
387012 | CR | 20181121 |  | 4 | TOA-TIS-24A PV failed higher than actual during de-icing | N | N |  | N | YES | <D> **** Detailed Description **** Indicated temp went from 40Â°F to 120Â° during de icing This TIC controls HS to TOA-HVAC-2A suggest split loop at controller on TG-HVAC-2A panel to see if TE or TIC failure. Indication not off scale just high (30Â°F outside air) <I> **** Actions Taken **** CT for use of B/P to control HS to unit | 02-00-TOA-TIS-24A
387013 | CR | 20181121 |  | 4 | Lights are Out in Deschutes Parking Lot |  |  |  | N | YES | <D> **** Detailed Description **** The lights are out in the Deschutes Building (PEC) parking lot. Combined with freezing fog and slick conditions, this is a safety issue. <I> **** Actions Taken **** Contacted Facilities and Comm. Eng. Manager . Lights appear to be coming on after it is already fully dark. <N> **** Equipment Description **** Parking Lot Lights - Deschutes Parking Lot
387014 | CR | 20181121 | CAQ | D | Constant Tamper on SEC MW 01 RBT | N | N |  | N | YES | <D> **** Detailed Description **** Recieved a constant Tamper on MW 01 RBT. <I> **** Actions Taken **** Security Comp in place, contacted electricians, walked down zone and generated CR/WR | 02-00-SEC-MW-1RB
387015 | CR | 20181121 |  | 4 | Poor lighting in TB East end stairwell |  |  |  | N | NO | <D> **** Detailed Description **** Several lights are out in the TB East end stairwell (Stair no. A1) causing it to be poorly lit presenting a possible safety hazard. <N> **** Equipment Description **** TB East side stairwell | 02-00-T-BLDG-MISC
387016 | CR | 20181121 | CAQ | D | Bus SL-83 Ground concurrent with DG2 start. | Y | N |  | N | YES | <D> **** Detailed Description **** Recieved Bus SL-83 ground. OPS 2 reported that Gnd was on MC-8A and reset the ground alarm. Suspect that this may have come in then the air compressor for DG2 started to recharge the air banks. The operator in attendance reports tha DSA-C-1B1 started to recharge air banks. There is no evidence to suggest that this was the equipment that gave the alarm or that it is unable to perform its function. This is really the only piece of equipment to cycle on and off at this time. AR written to document unexected alarm. <I> **** Actions Taken **** Wrote this CR. Informed supervision. Referenced SOP-ELEC -AC-LU | 02-00-DSA-C-1B1,02-00-E-SL-83
387017 | CR | 20181121 |  | 4 | CF-TK-4 level rise during Precoat of COND-DM-1F. | N | N |  | N | YES | <D> **** Detailed Description **** CF-TK-4 level rise continued throughout the Precoat of COND-DM-1F. Initially COND-V-323 was throttled open 1 turn, but had to be throttled open until full open at the end of the Precoat. With COND-V-323 full open, level appeared steady. No drain downs were required, and no resin was lost. This condition in the past eventually degraded to the point of drain downs being required during the Precoat of COND-DM-1F. <I> **** Actions Taken **** Notified supervisor and maintained CF-TK-4 level by throttling COND-V-323. <N> **** Equipment Description **** RW 467 | 02-00-CF-TK-4
387018 | CR | 20181122 |  | 4 | CW-FN-3 Failed to start. | N | N |  | N | YES | <D> **** Detailed Description **** CW-FN-3 Failed to start during deicing evolution. Sent Operator to reset overloads locally, Will reset vibes during the day for safety for CW-FN-3. <I> **** Actions Taken **** Informed CRS/SM | 02-00-CW-42-6L4A,02-00-CW-FN-3
387019 | CR | 20181122 | CAQ | D | SW-V-2B Does not indicate closed from MCR. Valve indicates c | Y | N |  | N | YES | <D> **** Detailed Description **** SW-V-2B Does not indicate closed from the MCR. Valve indicates closed locally. This happened when stopping SW -P-1B following the DG2 monthly run. <I> **** Actions Taken **** Informed CRS/SM With management concurrance SW-P-1B was started IAW SOP-SW -START. SW-P-1B started normally with NO green light indication at all. SW-P-1B was then secured and placed in a standby line up with local valve position for SW-V-2B being closed. | 02-00-SW-RLY-V/2B1,02-00-SW-V-2B
387024 | CR | 20181122 |  | 4 | W-1 sump very heavy oil content, needs pumped to barrels | N | N |  | N | YES | <D> **** Detailed Description **** W-1 sump very heavy oil content, needs pumped to barrels <I> **** Actions Taken **** Follow up to CR #384285 and W/R #29144460, which is still at H/APPR status. The water is currently being pumped into RW processing systems to maintain level below the sump Hi Level alarm. This is causing TOC excursions in the RW processing systems. Staged barrels staged to pump contents of sump into them. | 02-00-FDR-SUMP-W1
387025 | CR | 20181122 | CAQ | D | METB51 not tracking with other signals | N | Y |  | N | YES | <D> **** Detailed Description **** Per OSP-INST-H101, the Met Tower data for 245' wind speed redundant channels do not meet the required channel check. Compared 245' wind speed data displayed on MET-WSR-4 is 8.0mph with METB51 at 0.82mph. | 02-00-MET-WMON-1B
387026 | CR | 20181122 |  | 3 | EDNA search function changed for the worst |  |  |  | N | NO | <D> **** Detailed Description **** EDNA search function is now activating the search after the first character is placed in the field. This is a recent issue (last couple months) that must have come in with an update. Historically the entire input was entered and the return/enter key would execute the search. The new function requires placing the cursor back in the search field and adding characters one at a time. This is not an upgrade but causes the user more keystrokes and wasted time. Please restore the search function to the previous default - no user setting found to correct this issue.
387027 | CR | 20181122 |  | 4 | High TOC's in EDR-TK-4A | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** High TOC's in EDR-TK-4A. This is at least the 3rd High TOC in a sample tank in the past 2 days. Latest failed tank OC levels have been :270 ppb, 580 ppb, and 950 ppb. Unknown source of TOC's <I> **** Actions Taken **** Informed MCR Sent failed tank water to EDR-TK-5. This brings the total volume in EDR-TK-5 to 79% or 55264 gallons <N> **** Equipment Description **** High TOC's in RW processing | 02-00-EDR-TK-4A,02-00-EDR-TK-5
387028 | CR | 20181122 | CAQ | D | MC-8A Ground Fault Light Socket Broken | Y | N |  | N | YES | <D> **** Detailed Description **** While on rounds it was noticed the ground fault light for MC-8A in the SM-8 room was out. Bulb appeared to not to be damaged. A replacement bulb was inserted with no illumination. <I> **** Actions Taken **** Notified CRS <N> **** Equipment Description **** Ground Fault panel in SM-8 room. | 02-00-E-MC-8A
387029 | CR | 20181122 | CAQ | C | ARP Change â€“ 4.672.A9, drop 1-10 |  |  |  | N | NO | <D> **** Detailed Description **** MCR received a Glycol Pump Suction Temperature High Alarm. ARP drop 1-10 step 5 states, â€œIF no refrigeration machines are running, THEN CHECK the response of GY-TIC-17 by lowering the setpoint.â€ GY-TIC-17 has no setpoint adjustment. MCR stated the TIC has been replaced with a different model. ARP needs updating. <I> **** Actions Taken **** Notified CRS <N> **** Equipment Description **** ARP | 02-00-GY-TIC-17
387030 | CR | 20181122 |  | 4 | TOA-FN-1A tripped again | N | N |  | N | YES | <D> **** Detailed Description **** Several days ago TOA-FN-1A was found not running, leaving the TB in a 2/2 lineup and a steam tunnel high temp alarm came in. Since then a 3rd supply fan was started, maintaining a non-idea but usable lineup. Running both TOA-FN-1A and 1B is preferred but could clearly not be done. A (or multiple) fuse was found blown that would have caused the fan to trip. The equipment was worked and fixed. Operations did a fan swap to start TOA-FN-1A and stop TOA -FN-2A. FN-1A did start and building DP was getting less negative (about -0.3" H2O) as expected (and desired). Shortly after, the fan running light was found not lit, bulb appeared to be in good condition, DP was getting more negative (about -0.4" h2o). The operator opened TOA-FN-1A's door and found the fan windmilling slowly, with no DP across the door. The fan had again tripped. It appears the problem is deeper than a random blown fuse. | 02-00-TOA-FN-1A
387031 | CR | 20181122 | CAQ | D | ESOMS H101's recalculated later in shift, and resigned after |  |  |  | N | NO | <D> **** Detailed Description **** Esoms OSP-INST-H101 was originally signed at 10:14 on 11/22/18. A problem was corrected by the OPS Esoms coordinator caused the H101's need to be resigned later in the shift. The original signature time is documented in the attributes tab of the H101's <I> **** Actions Taken **** Wrote CR
387032 | CR | 20181122 |  | 4 | EDR-TK-4B released to CST with high TOC | N | N |  | N | NO | <D> **** Detailed Description **** EDR-TK-4B was authorized to be released to the CSTs, with chemistry concurrence, with high TOC concentration. The limit for TOC is 200 ppb. TOC levels in EDR-TK-4B were 652 ppb. All other analysis were within specification. The tank was released due to a shortage of storage space in radwaste. <I> **** Actions Taken **** Identified source of TOC intrusion and took measures to stop continued intrusion (See CR 387024). Authorized release of EDR-TK-4B to CSTs. | 02-00-EDR-TK-4B
387033 | CR | 20181122 | CAQ | D | OSCILLOGRAPH STARTED alarm received due to 500KV Neutral Gro | N | N |  | N | NO | <D> **** Detailed Description **** SCILLOGRAPH STARTED alarm received due to 500KV Neutral Ground (J7 sensor) and SM-8 Undervoltage (J12 sensor). The sensor has been reset. BPA reports that the LO-MO and Hanford#2 500KV line relayed off and back on. TR-S voltages are 238/238/238 kV and TR-B voltages are 117/117/117 kV respectively. All plant controllers and equipment exhibited normal operation
387034 | CR | 20181122 |  | 4 | WOA-FN-9 (Counting Room Fan) vibrating strongly | N | N |  | N | YES | <D> **** Detailed Description **** WOA-FN-9 motois vibrating very strongly. It is attached at the edge of ducting, and drives a fan through a belt. It appears to be either the motor, or the attached pulley, which is causing this vibration. Note that this vibration has recently gotten worse. Please investigate and repair. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 507 next to basketball court entrance. | 02-00-WOA-FN-9
387035 | CR | 20181123 | CAQ | D | Spurious DG3 Generator RTD High Temperature alarm | Y | N |  | N | YES | <D> **** Detailed Description **** Received GENERATOR RTD HIGH TEMPERATURE (E-CP-DG/RP3 2-1) caused by a spurious high temperature alarm on HPCS-TIS-DG3 for phase B. The alarm is reset / clear at this time with temperature indicating 44 degrees C (alarm setpoint is GE 130 degrees C). DG3 is in a normal Standby Status. This is a repeat occurrence - reference previous WR 29144144 & 29145444 (CR 383533 & 386437) <I> **** Actions Taken **** Submitted CR for trending. Notified CRS and Shift Manager. | 02-00-HPCS-TIS-DG3
387036 | CR | 20181123 |  | 3 | Station not meeting expectations validating eWP |  |  |  | N | NO | <D> **** Detailed Description **** The station is not validating all electronic work packages that are on the new Pre-Approval WO Tasks, which is now part of the daily schedule. This is causing a delay in getting work pre-authorized because the work cannot be pre approved. Specifically this weekend work orders 0212784301, 0202767601, and 0212794301 were not validated. . Reccomend retraining the station in the eWP process now that we have new processes in place and learnings from what we have done so far. <I> **** Actions Taken **** Wrote CR. Contacted Weekend Craft supervisor.
387037 | CR | 20181123 |  | 4 | WOA-V-21 red position light not working | N | N |  | N | YES | <D> **** Detailed Description **** During WO 02098521-06 step 4.4 has the performer verify the red/green indicating lights work. The red indicating light does not work. According to EWD-85E-028, the red lamp is associated with the CLOSED position switch. A mechanic was local at the valve while it was stroking. He confirmed when going open and closed both limit switches made the expected clicking noise at about 80% to the full open/closed position. 2 new replacement bulbs were tried, neight lit up. Possible socket problem or other. To be determined. <I> **** Actions Taken **** Documented in WO. | 02-00-WOA-V-21
387038 | CR | 20181123 |  | 4 | Spurious alarms 4.602.A6 drop 3-4 | N | N |  | N | YES | <D> **** Detailed Description **** 4.602.A6 drop 3-4 "ASD/A INPUT TRANFORMER TROUBLE' alarm came in and cleared several times. Initial investigation showed no abnormal temperatures, pressures or levels. <I> **** Actions Taken **** Directed OPs4 tour the ASD transformers | 02-00-RRC-RLY-K10A
387039 | CR | 20181123 |  | 4 | TG-TE-TBMFF4 failed high (main turbine thrust bearing) | N | N |  | N | YES | <D> **** Detailed Description **** DEH cab 00, chassis 1, slot 4, input 22 indicates 795Â° (and alarm on DEH computer) with corresponding TC on TG-TR-48 pt 41 indicating 122Â°F. see EDMS for data sheets and trend Type T dual unit TE. | 02-00-TG-TE-TBMFF4
387040 | CR | 20181123 |  | 3 | Fire Panel CP-B88/1 generating false alarms | N | N |  | N | YES | <C> This CR is assigned as a 3 to Security for them to write a WR <D> **** Detailed Description **** Fire Panel CP B88/1 MSI-01 has generated a false alarm for the past 3 Fridays around the same time at 1740. Evaluate the cause of these false alarms. <I> **** Actions Taken **** CR Generated WR cross referenced no further action <N> **** Equipment Description **** Building 88 Fire Panel
387041 | CR | 20181123 | CAQ | D | OG-V-95A failed to open | N | N |  | N | YES | <D> **** Detailed Description **** While attempting to swap to the 'A' train per SOP-OG-OPS, section 5.1.2, OG-V-95A failed to open. These are normally slow to open valves but it failed to open after a 5 min wait. Placed 'C' train on service instead. <I> **** Actions Taken **** placed 'C' OG train in service | 02-00-OG-V-95A
387042 | CR | 20181124 |  | 3 | TMU-P-1C tripped. | N | N |  | N | YES | <D> **** Detailed Description **** Received H13-P824 drop 3-4 TMU PUMP C BKR TRIP and drop 6-3 TMU PUNP C PRELUBE FLOW LOW. TMU-P-1C tripped. No flags were tripped at breaker. Drop 6-3 stayed locked in after TMU-P-1C RMS in control room taken to STOP. <I> **** Actions Taken **** Started TMU-P-1B. | 02-00-TMU-M-P/1C,02-00-TMU-P-1C
387047 | CR | 20181124 | CAQ | D | OG-AY-12B reading low | N | Y |  | N | YES | <C> CR reopened to cross reference additional WR 29145793, then taken back to complete <D> **** Detailed Description **** OG-AY-12B is reading lower than usual and lower compared to 12A. It currently fluctuates between 0.03% to 0.11%. There is no operability concern at this moment. <I> **** Actions Taken **** CRS informed and ISP-OG-A302 was referenced. <N> **** Equipment Description **** MCR | 02-00-OG-AY-12B
387048 | CR | 20181124 | CAQ | D | Power lost to TDAS-MUX-1 and 2 | N | Y |  | N | YES | <D> **** Detailed Description **** TDAS-MUX-1 and 2 have no power. Both are powered from E -CB-USPT/22. The CB is shut and fuses do not appear to be blown according to thier BFIs. TDAS-MUX-15 also periodically fails. <I> **** Actions Taken **** WR written. CRS informed. <N> **** Equipment Description **** MCR | 02-00-TDAS-MUX-1,02-00-TDAS-MUX-15,02-00-TDAS-MUX-2
387049 | CR | 20181124 | CAQ | D | IDS 20 (P.I.) | N | N |  | N | YES | <D> **** Detailed Description **** Security IDS 20 is not functioning as designed. Contact Security at extension 2185 for further details. <I> **** Actions Taken **** Compensatory measures posted. Security Supervision notified. CR/WR generated for Electrical Support | 02-00-SEC-IDS-EVAL/20/21
387051 | CR | 20181124 | CAQ | C | PPM 16.11.6 Missed Surveillance per PPM 1.5.1 and SR 1.0.2. | N | Y |  | N | NO | <D> **** Detailed Description **** PPM 16.11.6 is a missed surveillance per PPM 1.5.1 due to not having been documented as reviewed by a CRS/Shift Manager (WO# 02127827). Surveillance was taken to finished on 11/21/18 at 16.11.6 per Portal J records, however Major rev 23 Minor rev 01, effective 11/14/18, does not have a cover page for CRS authorization or close-out (despite this surveillance being a required surveillance per ODCM 6.2.2.1) and was therefore not documented as authorized or reviewed by the CRS. Last valid completion of this surveillance was 11/14/18 at 00:20, exceeding the periodicity allowance of SR 1.0.2. The cover sheet for ops authorization and review was inadvertently deleted when the new revision went into effect. <I> **** Actions Taken **** Informed the Shift Manager. Invoked SR 1.0.3 for missed surveillance. Reviewed the surveillance and verified it to be satisfactory effective 11/24/18 at 13:49. Request procedure change to restore the ops authorization and review cover sheet prior to next performance of PPM 16.11.6.
387052 | CR | 20181125 | CAQ | D | Rods requiring High Dp to move during OSP-CRD-M701. | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02113437, then taken back to complete <D> **** Detailed Description **** During performane of OSP-CRD-M701 22 HCU's required Higher Drive Water Dp to move from their initial position. Details are in the attached EDMS. <I> **** Actions Taken **** Entered ABN-ROD and exited ABN-ROD. | 02-00-CRD-HCU-0235,02-00-CRD-HCU-0623,02-00-CRD-HCU-0643,02-00-CRD-HCU-1015,02-00-CRD-HCU-1023,02-00-CRD-HCU-1455,02-00-CRD-HCU-1811,02-00-CRD-HCU-1835,02-00-CRD-HCU-1839,02-00-CRD-HCU-2619,02-00-CRD-HCU-3003,02-00-CRD-HCU-3007,02-00-CRD-HCU-3019,02-00-CRD-HCU-3055,02-00-CRD-HCU-3411,02-00-CRD-HCU-3855,02-00-CRD-HCU-4227,02-00-CRD-HCU-4655,02-00-CRD-HCU-5011,02-00-CRD-HCU-5435,02-00-CRD-HCU-5443,02-00-CRD-HCU-5839
387053 | CR | 20181125 |  | 3 | ENS Line is Down | N | Y |  | N | YES | <D> **** Detailed Description **** On 11/25/2018 the NRC called the CGS Shift Manager and reported that they were unable to contact the MCR via the ENS line. The ENS line has no dial tone and all associated phone lines were verified plugged in. <I> **** Actions Taken **** EP informed. <N> **** Equipment Description **** MCR ENS phone NRC resolved issue with service provider. See WR 29145756.
387054 | CR | 20181125 | CAQ | C | OG Pretreatment Radiation Level Elevated during OSP-CRD-M701 | Y | Y |  | N | YES | <D> **** Detailed Description **** During the performance of OSP-CRD-M701 (WO 02127656) it was noted that OG pretreatment radiation levels rose sharply from approximately 50 mrem/hr to 68 mrem/hr. This rise in OG pretreatment rad levels started to occur at 2352 on 11/24/2018 per OG-RR-604. There was no change to OG flow rate (constant 47 scfm) during this time. OG pretreatment rad levels slowly lowered back to 50 mrem/hr by 0020 on 11/25/18. Chemistry took an OG sample and results were less than 50% change from previous samples. All control rods that were being exercised at approximately this time were full out with the exception of 50-19 and 18-11. <I> **** Actions Taken **** Wrote CR to document. Note OG pre-treat point X073 and OG post treat point X088 are unavailable due to MUX 2 having lost power (CR 387048). | 02-00-OG-RR-604
387055 | CR | 20181125 |  | 4 | Trend data for 471 heater bay steam leak | N | N |  | N | YES | <D> **** Detailed Description **** The large steam leak in TB 471 heater bay above the 6B heater may be geating bigger. from camera 11 looking south, a waterfall can be seen on the west side of the 2A heater at a rate of 5-10 gpm. This is either from the 6B heater or a new steam leak above the 2A heater. Recommend ensuring this is taken care of during the R24 window. <N> **** Equipment Description **** TB 471 above FW HTR 2A/6B | 02-00-COND-HX-2A,02-00-RFW-HX-6B,02-00-T-BLDG-MISC
387057 | CR | 20181125 | CAQ | D | MS-TR-614 will not wake up/display | N | Y |  | N | YES | <D> **** Detailed Description **** MS-TR-614 is no longer displaying. This is being used to monitor SRV tailpipe temperatures. <I> **** Actions Taken **** Informed CRS/SM./STA | 02-00-MS-TR-614
387058 | CR | 20181125 |  | 4 | Trend - CW Fans spurious alarms | N | N |  | N | YES | <D> **** Detailed Description **** 4.824.M 4-1 (Fans 25 through 30 OL/Vibe High) alarm came in and cleared twice. No fans have tripped and Backpressure is steady. <I> **** Actions Taken **** Verified no fans have tripped. <N> **** Equipment Description **** CW electrical building | 02-00-CW-CT-2B
387060 | CR | 20181125 |  | 4 | Door handle on TGHVAC-2A is broken | N | N |  | N | YES | <D> **** Detailed Description **** Door handle to the east side access door at the 2A Turbine Building HVAC control panel is broken/held on with a nail. <N> **** Equipment Description **** Turbine Building 501' West side TGHVAC-2A | 02-00-T-BLDG-MISC
387061 | CR | 20181125 |  | 4 | Several light bulbs are out or flickering (A1 stairwell) | N | N |  | N | YES | <D> **** Detailed Description **** The A1 stairwell (by the elevator) in the turbine building has several lights that are either out or flickering including emergency light bulbs. <I> This is non-essential lighting. <N> **** Equipment Description **** A1 stairwell in the turbine building | 02-00-T-BLDG-MISC
387062 | CR | 20181125 |  | 4 | Tygon Tubing Used as Berm | N | N |  | N | NO | <D> **** Detailed Description **** Tygon tubing around Mechanical vacuum pumps being used as berm. <I> **** Actions Taken **** Informed SSS and SM | 02-00-T-BLDG-MISC
387063 | CR | 20181125 |  | 4 | Joe Bute and Mesa Paging Sites have leased line outage | N | Y |  | N | NO | <C> This CR found at INPROG and moved forward to APPROVED. This CR Trended to CR 387053 (Severity 3). <D> Frontier Communications experienced an outage on a DS3 transport system which carrys the two DS0 leased lines for Joe Bute and Mesa Paginig Sites respectively. The outage was out of the Frontier Kennewick Main Central Office. Circuit IDs 86.LHXX.509153..FTNC and 86.LHXX.509155..FTNC NCAQ-4 <I> Opened trouble tickets with Frontier Communications, followed up multiple times to escalate tickets to finally get tech dispatched before Monday. <N> Input from IS is this condition has been corrected.
387064 | CR | 20181125 | CAQ | D | Unable to Perform Channel Check of MS-RV-1B | N | Y |  | N | NO | <D> **** Detailed Description **** Due to MS-TR-614 no longer displaying (AR 387057), the Main Control Room is unable to perform CHANNEL CHECK of tailpipe temperature monitoring instrument for affected SRV (MS-RV-1B) as required per LCS 1.3.3.1, B(2). MS-RV-1B has been indicating intermediate since the load reject scram in May. Daily verification of tailpipe temperatures had been used per LCS sheet LCS-18-MS-RV-1B-001 since then, but we are now unable verify tailpipe temperatures. The next LCS action is to write a CR, which has already been completed previously due to inability to comply with LCS 1.3.3.1, B(3), which required closed position indication of MS-RV-1B to be restored within 30 days. <I> **** Actions Taken **** Informed shift manager and wrote this CR. Previous CR has work request to repair MS-TR-614. | 02-00-MS-RV-1B,02-00-MS-TR-614
387065 | CR | 20181125 |  | 4 | Water accumulation on ground from potential ground leak | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Security notified Operations of standing water on ground near a pipe coming up from the ground southwest of NW Remote Air Intake . During investigation, found pooling around what appears to be a capped metal conduit in rocks that leads to an unknown location. Inspection at actual pooling location was not possible without water intrusion into conduit but a similar cap was removed south of the leakage and photos are attached. This could be a due to a leak in the ground from Fire Protection or Potable Water although there is no nearby PW piping (100+ feet away). Pooling did not show any significant leakage that required immediate action. <I> **** Actions Taken **** Investigated with SRO and took photos <N> **** Equipment Description **** West of Transformer Yard near NW Remote Air Intake
387075 | CR | 20181126 |  | 4 | EDR-DPIS-27 continues to operate incorrectly | N | N |  | N | YES | <D> **** Detailed Description **** Recent history of issues with EDR-DPIS-27 spiking high when securing EDR processing through EDR-DM-9. DPIS was worked on recently but the issue still persists. Gives false high D/P which locks out the ability to process forcing the RWCR operator to reset the EDR PLC to restore function. This is putting undue wear on the the PLC and EDR processing system as it sometimes take mulitiple attempts to get EDR processing. <I> **** Actions Taken **** Informed SSS <N> **** Equipment Description **** RWCR | 02-00-EDR-DPIS-27
387077 | CR | 20181126 |  | 3 | VPN cert expiration IEBS-1 |  |  |  | N | YES | <D> **** Detailed Description **** VPN certificate has expired on IEBS-1 laptop. Request computer engineering support to repair. <I> **** Actions Taken **** Notified Computer Engineering and Security Management <N> **** Equipment Description **** IEBS-1
387112 | CR | 20181126 |  | 4 | False SRD Dose Rate Alarm Received During RW Elevator Work |  |  |  | N | NO | <D> **** Detailed Description **** While performing work activities related to the radwaste elevator maintenance, an individual's self-reading dosimeter (SRD) instantaneously alarmed and cleared on a peak dose rate of 3560 mrem/hr. The SRD did not activate an audible alarm prior to clearing. During the RCA logout process, the individual was flagged for restriction due to the alarm and promptly notified Health Physics. Dose rates in the elevator shaft and surrounding areas do not support this being a valid SRD dose rate alarm. The individual had been using a sawzall with the electrical cables near or in direct contact with the SRD. Electrical interference is the most likely cause. During the period in which the SRD was in the alarming state, it registered 1.7 mrem. <I> **** Actions Taken **** Coaching was provided on maintaining SRD distance from electrical sources (including those which have the potential to create EMF intereference). The individual was manually logged out of the RCA. <N> ED alarm investigation, histogram and survey have been uploaded into EDMS. No further action required. | 02-00-MT-ELEV-4,02-00-W-BLDG-MISC
387120 | CR | 20181126 |  | 3 | IMDS for MS-TR-614 needs to be updated | N | Y |  | N | NO | <D> **** Detailed Description **** IMDS for MS-TR-614 needs to be updated to include COlor for Channel 18. under color on page 4 of the IMDS needs to include the following: CH 18 = Black . this is an issue with the IMDS only and does not affect the Recorder. <I> **** Actions Taken **** wrote CR. | 02-00-MS-TR-614
387121 | CR | 20181126 | CAQ | C | TDAS computer malfunction due to system memory full | Y | N |  | N | YES | <D> **** Detailed Description **** Most TDAS processes stopped due to system memory filling up with accumulated log files. This caused a loss of heat balance information on the primary computer. <I> **** Actions Taken **** Shifted heat balance and other monitoring to the PPC computer. Deleted accumulated log files and restarted processes that TDAS had shut down. Verified that 3DMonicore had automatically restarted once heat balance information was available again. Notified computer engineering. Note: a â€œWeekly Computer System Maintenance PMâ€ keeps accumulated log files from leading to a full system memory, but this PM is now done only monthly. This PM should be done at least biweekly to ensure uninterrupted primary computer function. | 02-00-TDAS-CPU-VMS/WS
387123 | CR | 20181126 |  | 3 | VENDOR ERROR MAY CAUSE DELIVERY DELAY FOR R24 MOTORS |  |  |  | N | YES | <D> **** Detailed Description **** PO#00351753 for RFW-M-V/65A and RFW-M-V/65B was issued on 3/28/18 and sent to the vendor with a promised delivery date of 12/28/18. It was discovered on 11/26/2018 when vendor was contacted for getting a status on this PO that the vendor, did not perform the order entry of this PO in March when they received the PO. Per CGS CID, we were asking for aluminum rotors, which have a 38 week lead time. This would not make the R24 outage requirement at this time. The vendor is offering an available motor that would have magnesium rotors at a $70,000.00/per motor discount as a compensation for the error. For a total of $140,000.00 if we can accept the magnesium rotor motor. SCS recommends engineering evaluation to see if the magnesium rotor motors can be accepted. This is the only option that will be delivered in time for R24. This is a issue with the procurement of replacements. <I> **** Actions Taken **** Discussed with supervisor Issued MP-OT-65001902-112618 to Procurement Engineering CR Issued <N> Discussed the issue with the MOV Component Engineer. The replacement aluminum rotor is a contingency part in case RFW-V-65B doesnâ€™t pass the testing during R24. Bill has no reason currently to expect that the RFW-V-65B motor will fail, but he was hedging his bets. The aluminum motor will be used for a scheduled replacement in RFW-V-65A and RFW-V -65B motors in R25. . The replacements are driven by BRWOG recommendations and lots of industry OE. The station has made no commitment to the replacement to any outside agency. There is no PM that will be missed as a result of not having the motor. Additionally, Bill told me he doesnâ€™t want the magnesium rotor motors because that would lead to eventually needing to replace with aluminum anyway. . According to the Buyer, the supplier, Areva will reserve one of the magnesium rotor motors just in case it is needed to support the R24 activity. . Based on what information I got from Bill, I recommend it be a severity level 3 non-CAQ CR classification. | 02-00-RFW-M-V/65A,02-00-RFW-M-V/65B
387126 | CR | 20181126 |  | 4 | Unsecured tritium grab sampler |  |  |  | N | NO | <D> **** Detailed Description **** An NRC representative walking through the plant raised a question about the stability of the chemistry tritium sample collection device. While grab sampling is in progress, the tritium collection device is connected to building exhaust air via plastic tubing and is typically leaned against the wall. The NRC representative recommended the device be secured in some way to prevent the tipping over or disconnection of the device. A safer alternative for positioning the tritium sample collector during use, such as a stand or holder, should be implemented. <I> **** Actions Taken **** Device was secured to wall with adhesive tape. CR was written. <N> Is this tritium grab sampler permanent plant equipment (does it have an EPN?) or just a temporarily installed tool?
387127 | CR | 20181126 |  | 4 | SCBA battery leakage |  |  |  | N | NO | <D> **** Detailed Description **** SCBA unit 67846 was found to be removed from service due to battery leakage discovered in the battery compartment. <I> **** Actions Taken **** The SCBA was green tagged and prepâ€™d for transport to calibration repair facility. RP Supervision notified. This did not affect Fire Brigade response unit inventories. Recommend all respiratory equipment issues be identified and trended when safe operations of units could have been affected. <N> SCBA was transferred to the calibration lab on 11/28/18. Respirator equipment reviewed and inspected on a regular basis. No further action required.
387128 | CR | 20181126 |  | 4 | WO# 02036318-01 (Schedule Code B) will not complete today |  |  |  | N | NO | <D> **** Detailed Description **** WO# 02036318-01 was created to replace the MCC bucket at SW-42-8BB6A (SW-V-188B). The task is coded as a Graded Schedule Code â€œBâ€. The task was started on schedule and the bucket has now been replaced, however the next step in the task is to close the disconnect switch to re-energize the bucket. In discussion with OPS, this is not a good time to perform this, due to the protection scheme currently in place (â€œAâ€ FPC/SW) and the potential for the valve opening (if wired incorrectly). This task will remain open until later this week, when the protection scheme is lifted and the correct plant configuration can be obtained. <I> **** Actions Taken **** Discussed with PSRO and CRS CR written
387130 | CR | 20181126 | CAQ | C | OSP-CONT-M102 Cannot be Performed as Written | Y | N |  | N | NO | <D> **** Detailed Description **** OSP-CONT-M102 cannot be performed as written for steps 7.6.4, 5, and 6. As written these pounded steps verify R -DOOR-R103, the A1, and A2 hatch are closed when R-DOOR -R106 is closed. These doors are not required to be closed when R106 is closed as the secondary containment boundary is established at R106 allowing for the hatches and doors to be opened for equipment ingress and egress. It appears that our interpretation of SR 3.6.4.1.2 and 3.6.4.1.3 was flawed during the implementation of AR 379131. SR 3.6.4.1.2 applies to the HPCS and RHR equipment hatches that are not opened in Modes 1, 2, or 3 (R-DOOR-RS1 and 2 respectively). SR 3.6.4.1.3 applies to R106, R103, A1, and A2. OSP-CONT-M102 needs to be revised and additional information needs to be provided for what constitutes an equipment hatch or door (update EPNs or add information to the TS Bases). This change was performed in Rev 9 on 5/16/18. Late date for completing this surveillance is 11/30/2018. <I> **** Actions Taken **** Marked up procedure attached. | 02-00-MT-DOOR-A1,02-00-MT-DOOR-A2,02-00-R-DOOR-R103,02-00-R-DOOR-R106,02-00-R-DOOR-RS1,02-00-R-DOOR-RS2
387131 | CR | 20181127 |  | 3 | Evaluate protected requirements for FPC in 1.3.83 |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate protected system requirements for FPC in PPM 1.3.83 specifically for FPC-SYS-A or B when time to 200F is greater than 72 hours. Currently there is guidance to protected TSW and RCC, but only a single pump is each system when we take a FPC pump/system out of service for maintenance. This seems overly redundant as both of these systems have redundancy built in to ensure functionality if a running pump has an issue. Additionally if either TSW or RCC has one of their pumps become nonfunctional either per equipment issue or planned maintenance then PPM 1.3.83 directs to protect the remaining components. Protecting a single pump in the TSW and or RCC system will not prevent planned maintenance taking out one of the other pumps in either of these systems. Recommend removing the requirement to protect TSW and RCC components when time to 200F is greater than 72 hours, this will reduce required required manpower to perform a task which is in line with Delivering the Nuclear Promise. <I> **** Actions Taken **** Discussed this with on shift SROs and ROs
387139 | CR | 20181127 |  | 3 | R24 Evaluate impact If E-C1-7 is placed on alternate power |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate impact If E-C1-7 is placed on alternate power from the E-MTS-8A/C1/2B and E-MTS-6B/C1/7. If E-C1-7 is placed on alternate power from the normal power that feeds E-C1-2B but transferred to E-C1-7 from the E-MTS-8A/C1/2B and E-MTS-6B/C1/7 will MC-8A and DG-2 remain operable? E-C1-7 is an additional load that may not be accounted for in the DG-2 loading calculations. Additional loads may require removal as part of this evaluation and limitations placed on when this lineup can be used i.e. Mode 4/5. If part of this evaluation requires additional loads removed for in the DG-2 loading calculations could CAS-C-1B could be removed from service (tagged out) to provide additional margin? If this AR-EVAL is approved SOP-ELEC-125V-START would need additional wording to indicate the limitations on use and removal of additional loads (if any) on when this lineup could be used <I> **** Actions Taken **** AR eval 00387137 written | 02-00-E-C1-7
387146 | CR | 20181127 |  | 4 | WOA-FN-9 broken belt | N | N |  | N | YES | <D> **** Detailed Description **** Drive belts for WOA-FN-9 broke; 2 belts <I> **** Actions Taken **** Informed SSS and MCR <N> **** Equipment Description **** RW 507' North of 1B chiller | 02-00-WOA-FN-9
387149 | CR | 20181127 |  | 3 | SOP-CW-CHEM-MAINT references SWP-ENV-02 which is superseded |  |  |  | N | NO | <D> Prerequisite 3.1 in SOP-CW-CHEM-MAINT states, "REVIEW SWP-ENV-02 Section 4.1, Spill Prevention and Preparedness, prior to commencing any evolution in this procedure. Change SWP-ENV-02 to GBP-ENV-18. The section remains the same. evolution in this procedure. <I> Wrote this CR and notified Supervisor. <N> This CR was found at INPROG and moved forward to APPROVED.
387151 | CR | 20181127 |  | 3 | SOP-HVAC/WCH-FILL steps 5.2.1 and 5.2.2 should be deleted |  |  |  | N | NO | <D> **** Detailed Description **** SOP-HVAC/WCH-FILL steps 5.2.1 and 5.2.2 should be deleted since the oil cooler does not have separate cooling on the new modified WCH-CR-51A. WCH-V-24 is now closed and capped. Reference M550-1 REV 38 | 02-00-WCH-CR-51A,02-00-WCH-V-24
387152 | CR | 20181127 |  | 3 | Step 5.1.1 should be deleted from SOP-HVAC/WCH-START. |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.1.1 should be deleted from SOP-HVAC/WCH/START. This step has you verify a WCH pump running however the pumps are not supposed to be started until step 5.1.6. Reference section 5.2 for WCH-CR-51B.
387153 | CR | 20181127 | CAQ | C | Update R program manual for new ownership by Code Programs |  |  |  | N | NO | <D> **** Detailed Description **** The R program manual for NBIC R Stamp repairs on ASME Vessels has been transferred to Code Programs. In addition to the update required by AR 00384318 Assignment 22 for the organizational changes, the manual needs to include revisions to show the alignment from Quality to Technical Services for new ownership. Additional Items for revision include: Revision to assign responsibility for the R Stamp program from Quality Manager to Technical Services. The complete rewrite of the manual should include to include: â€¢ Remove responsibility for the Maintenance Welding Program from the Manager, Design Engineering. â€¢ Revise the Org Chart to reflect current Plant organization. â€¢ Reformate to improve appearance of the manual. â€¢ Revise section relating to Filler Material Issue and Control to reflect current practice. â€¢ Revise Exhibits to show current examples of plant Records relating to the R Program. â€¢ Review manual against current edition of the NBIC (2017). â€¢ Review manual against current edition of Washington Boiler and Unfired Pressure Vessels Laws (2018
387154 | CR | 20181127 |  | 3 | EDR Sump R5 high level alarm | N | N |  | N | NO | <D> **** Detailed Description **** A temporary sump pump was installed in EDR sump R5 to support an EDR line flush that required disabling EDR-P -5A/B. EDR sump R5 level was to be controlled by pumping R5 to R3. The sump pump was verified installed but was not plugged in when the tags were hung on EDR-P-5A/B. The EDR sump R5 high-high level alarm was received early on day shift 11/27/18. <I> **** Actions Taken **** Plugged in the the sump pump, verified R5 level alarm cleared. No further problems encountered with R5 level control. | 02-00-EDR-SUMP-R5
387157 | CR | 20181127 |  | 3 | MT-CRA-1 Upgrade - Degraded Trolley Motor and Wiring | N | N |  | N | YES | <D> **** Detailed Description **** While installing a jumper to provide temporary power to the turbine crane trolley motor, Whiting Crane personnel found the following degraded conditions: 1) When the motor terminal box was opened, both it and the internal wiring were saturated with oil. In addition, the insulation on the brake leads was completely degraded and flaked-off when handled. 2) The existing trolley motor brake power cord was saturated with oil and is also completely degraded. The source of the oil intrusion is the existing trolley brake solenoid container. This condition is typically the result of overfilling the container and/or long term seeping of the oil along the inside of the cable jacket. <I> **** Actions Taken **** 1) Whiting performed a temp repair to the wiring to enable upgrade work to continue. 2) Requested Whiting provide options and recomendation for trolley motor repairs and have received their report. 3) Requested Whiting validate and provide trolley motor specs to aid in sourcing a potential new motor and have received the motor info. <N> **** Equipment Description **** T 555' A3/15.0 (west of parked position) | 02-00-MT-CRA-1
387163 | CR | 20181127 |  | 4 | Records Submitted without proper Documentation |  |  |  | N | NO | <D> **** Detailed Description **** On 11/27/2018 A Record was submitted to records control without following the records submittal process. There was not a signature or date included on the transmittal form (Form # 26916 R5) . This CR is for trending purposes only. <I> **** Actions Taken **** Notified Supervision. Tried to make contact with sender and senders supervisor. This record is a Confidential Record and Chemistry Department will need to come grab the record and resubmit. <N> Record has been resubmitted by Chemistry. No further action required.
387167 | CR | 20181127 | CAQ | D | FP-P-3 Leaks Water onto Floor | N | N |  | N | YES | <D> **** Detailed Description **** FP-P-3 in the CWPH is spraying a large amount of water on to the floor and has done so for some time. This item has been addressed before with no resolution. A recent QA audit noted that no resolution has occured for this long standing issue. <I> **** Actions Taken **** Repair/Contain the leak. Ensure that the work does not get cancelled as it has been moved several times without resolution. <N> The CR states that no resolution has occurred for this long standing issue. The FP-P-3 leak has been worked on under WO 02075938 (2017) and WR 29145175 (10/23/2018). The work request is the most appropriate method to address the leak and/or issues with the catch basin. . | 02-00-FP-P-3,02-00-P-BLDG-MISC
387169 | CR | 20181127 |  | 3 | Procedure editorial CSP-INST-M201 |  |  |  | N | NO | <D> **** Detailed Description **** In procedure CSP-INST-M201 step 7.8.9 should references step 7.8.2 which is incorrect. Step 7.8.9 should reference step 7.8.3. <I> **** Actions Taken **** CR written, specialist informed
387170 | CR | 20181127 | CAQ | D | TEA-SR-26 High Range Detector Replacement Needed Soon | N | Y |  | N | YES | <D> **** Detailed Description **** The TEA high range detector checksource response has decreased below checksource limit setting of 500 cpm +/- 20%. Today while performing checksource response testing, the instrument failed with a response of 393 cpm. A subsequent retest of the checksource response passed with a response of 435 cpm. This decreasing trend in detector response was first captured in CR 378376, which resulted in WP 02105303 to replace the TEA high range detector. This work is not scheduled until 02/16/2019, however, it does not seem likely that the current detector will continue to function until that date. Recommend that WP 02105303 be completed before the next performance of TEA-RE-13A source check. <I> **** Actions Taken **** Spoke with CRS and wrote CR. | 02-00-TEA-RE-13A,02-00-TEA-SR-26
387172 | CR | 20181127 | CAQ | D | RHR-V-922 assembly pre-fabbed incorrectly. |  |  |  | N | YES | <D> **** Detailed Description **** During a walkdown to verify that the pre-fabbed section of piping would properly fit, it was discovered that the the vertical section between welds XI-5 & XI-6 was approx 12" too long. <I> **** Actions Taken **** Notified CPM and generated CR. | 02-00-RHR-V-922
387173 | CR | 20181127 | CAQ | D | Minor Leakby observed on SLC-V-15 | Y | N |  | N | YES | <D> **** Detailed Description **** During a walkdown minor leakage (slightly less than 1 dpm) was observed going into the SLC floor drain. The leakage appears to be coming from the pipe with the SLC-V-15 upstream indicating that the SLC-V-15 likely has some small amount of internal leakby. The sodium pentaborate crystals were also observed on the outside of the drain pipe exit. Additionally, this leakage may be the cause of the reduced SLC tank boron concentration (ref. CR 00386858). <I> **** Actions Taken **** CR written and supervisor notified. Need a work request to repair SLC-V-15 to eliminate the leakby. <N> **** Equipment Description **** SLC-V-15 - SLC area, Rx Bldg 548' SLC-TK-1 - SLC area, Rx Bldg 548' | 02-00-SLC-TK-1,02-00-SLC-V-15
387174 | CR | 20181127 |  | 3 | Hot Spot Discovered Following EDR/FDR Backwash | N | N |  | N | NO | <D> **** Detailed Description **** Following an EDR/FDR backwash, a new radiological hot spot was discovered in the radwaste 467' "A" valve gallery. The post-backwash survey identified 220 mrem/hr on contact and 18 mrem/hr at 30 cm in close proximity to FDR-V-085. Refer to survey M-20181127-4 (attached in EDMS) for further details. <I> **** Actions Taken **** Hot spot posted and logged in the tracking database. No other posting adjustments were required. Contacted Operations and determined that flushing the line is not an option at this time. <N> FDR-V-085 (FDR-V-85) is not an EPN in Portal J MEL. | 02-00-W-BLDG-MISC
387175 | CR | 20181127 |  | 4 | RWCU-FCV-33 Drawings not available in Portal J |  |  |  | N | YES | <D> **** Detailed Description **** When EC 10907, REPLACE RWCU-FCV-33 INTERNALS was completed, the following drawings were never uploaded into Portal J: CVI DWG 02G33-08,5,1 4.00 IN G110 UP 600# VALVE ASSEMBLY (SPARE TRIM CVI DWG 02G33-08,5,2 4.00 IN G110 UP 600# TRIM ASSEMBLY OMNI SEAL PLUG CVI DWG 02G33-08,5,34.00 IN G110 UP 600# TRIM ASSEMBLY OMNI SEAL PLUG CVI DWG 02G33-08,5,44.00 IN G110 UP 600# TRIM ASSEMBLY OMNI SEAL PLUG <I> There is no issue associated with EC MALT 10907 (i.e., the administrative actions completed by Document Control for its implementation in 2013). Per input from the Mechanical Design & Drafting Lead, the reason there are no images uploaded into Portal J for these particular drawings is that they are proprietary/confidential. <N> From Mechanical/Civil Design lead Scott Payne: The reason no image is loaded into portal J is these drawings are proprietary/confidential. If you need to see these drawings talk to Kim Saenz. This CR should be cancelled or Comp/NA | 02-00-RWCU-FCV-33
387176 | CR | 20181127 |  | 3 | Chemistry Technician Initial Training Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** A Chemistry Technician failed an exam in the initial training program. <I> **** Actions Taken **** Notified training and line management of exam failure.
387177 | CR | 20181127 |  | 3 | Conflicting signage and procedure instructions |  |  |  | N | NO | <D> **** Detailed Description **** During the HPCS floor plug removal PJB it was identified that procedure 10.4.14 step 7.1.5 states to remove the tape and lift out the fire rated penetration seal. The stickers on the floor plug state DO NOT REMOVE. See picture in EDMS. The seals are inspected prior to installation for damage <I> **** Actions Taken **** ecommend making a revision to the procedure to remove step 7.1.5 <N> Procedure uploaded to Maintenance data base . Link provided in EDMS. | 02-00-R-BLDG-MISC
387179 | CR | 20181127 | CAQ | C | RHR-MO-49 Actuator Replacement Limit switch Cover Bolt Hole | Y | N |  | N | YES | <D> **** Detailed Description **** RHR-MO-49 actuator was replaced by WO 02093558. The scope is to use the new actuator with the existing (old) explosion limit switch cover. Installation of the explosion limit switch cover identified 2 of the 4 bolt holes were smaller (misaligned) requiring elongation. It should be noted that the new limit switch cover fit perfectly on the old actuator. The explosion cover shows indications in the bolt holes where it was tight when installed on the old actuator. The old explosion cover was used to ensure the actuator weight remained the same. The new and old limit switch gasket fits both actuators. <I> **** Actions Taken **** Discussed with design supervision and EQ. The slight elongation of the limit switch does not impact the function or environmental qualification of the actuator. Note: The limit switch gasket does not require modification. <N> Installing the old explosion proof limit switch cover (LS) on the new actuator was a tight fit due to the LS cover hole alignment. It was also a tight fit on the old actuator. Maintenance asked for additional support on the LS cover holes. Two of the LS bolt holes were slightly enlarged (within the hole tolerance) to reduce the stress on the LS bolting and for installation (removed the bur). There was no issues with the LS gasket. There was no impact to the actuator design, design fuctions, EQ or siesmic requirements. The CR was initiated was initiated to document the support call question. . Issue was reviewed with Design Engineering, EQ, and seismic and no additional actions are required. Closing this CR | 02-00-RHR-MO-49
387180 | CR | 20181127 | CAQ | D | SPTM-TE-7A failed on CMS-TR-5 (pt 204) | Y | Y |  | N | YES | <D> **** Detailed Description **** SPTM-TE-7A failed on CMS-TR-5 (pt 204) see OSP-INST-H101 for required actions to calculate WW temp ave. Pt is required for calculation and can be substituted. with another element from the same sector. SEE EC 16285 for another element on this same temp recorder. This may require action during an upcoming outage to correct. EDNA attached - fail time 1430 11/27/18. It also appears pt 208 should be the sector replacement TE but it was used when CMS-TE-1A failed (appears pt 205 should be substitute for pt 201 failed and pt 208 should be substitute for pt 204 failed). SPTM-TI-5 also impacted (indicates 43Â°F) <I> **** Actions Taken **** average temp per H101s calculated (71Â°F) even though this is a day shift reading. <N> SPTM-TE-7A substitute is SPTM-TE-6A. SPTM-TE-1A previously failed is appropriately replaced by SPTM-TE- 8A Notes about PT 208 substituted for pt 201 are not correct - that is the appropriate substitution. | 02-00-CMS-TR-5,02-00-SPTM-TE-7A
387185 | CR | 20181128 |  | 3 | WO didnt authorize in dataglance the normal way |  |  |  | N | NO | <D> **** Detailed Description **** Tech Spec surveillance 15.3.16 WO 02127978-01 didnt allow me to authorize it on the ops authorization view. It is a surveillance and should show on that view. It allowed me to authorize it on the supervisor view <I> **** Actions Taken **** Wrote CR. Talked to the craft supervisor that owns the work <N> WO 02127978 - PPM 15.3.16 INSP ANSUL SYSTEM â€“ MONTHLY is a Surveillance with a WO task of â€œNS-Essential PM â€“ OPS review not requiredâ€. It has a â€œControl Room Communication = 3â€ and the Review Required is checked. . The CWO Hold was released on 10-26-18 and the prior surveillance was worked as scheduled. . There is not a clear reason for this not to be on the OPS Authorization panel. The Operator was able to Authorize from the Supervisor Assignment Panel. . Recommend to Trend â€“ A change will be made, prior to the end of 2018, that will not require OPS Authorization on a â€œControl Room Communication = 2 or 3â€ and the code to require OPS to Authorize packages with the Review Required flag is checked will be removed.
387188 | CR | 20181128 |  | 4 | Loss of Control of Personal Vehicle |  |  |  | N | NO | <D> **** Detailed Description **** While turning onto EN Access road individual lost control of personal vehicle when wet road conditions caused the lightweight, rear wheel drive truck to spin out. Vehicle spun out, struck a light pole and slid into an embankment. No injury noted. Seatbelt worked as expected. <I> **** Actions Taken **** Notified the control room and got assistance pulling truck from embankment. Parked truck safely on old access road to Kootenai bldg. Notified Supervisor and Manager.
387189 | CR | 20181128 |  | 3 | Lost information from revision 23 of 01-00,81 |  |  |  | N | NO | <D> **** Detailed Description **** Revision 23 of 01,00,81 only has the page with the item descriptions. The old versions had additional pages that showed the main generator and exciter components with assigned item numbers. It looks like these were mistakenly not included with revision 23 of 01-00,81. These pages provide good information for tagging out the Main Generator and Exciter and should be included.
387191 | CR | 20181128 |  | 3 | SCI-MUX-OCR1A/2 IMDS needs fixed | N | N |  | N | YES | <D> **** Detailed Description **** Channel 3 is inverting output and channel 11 is non -inverting output If a new Supervisory Mux is replaced it could be programed incorrectly. EWD-55E-003 and EWD-45E-014 for reference <I> **** Actions Taken **** Notified Supervisor | 02-00-SCI-MUX-OCR1A/2
387195 | CR | 20181128 |  | 4 | Portal J update RHR-PT-37B | N | N |  | N | NO | <D> **** Detailed Description **** The Portal J noun name for RHR-PT-37B is "RHR-P-2A DISCH PRESS XMTR." This pressure transmitter is for RHR-P-2B. <I> Portal J has been corrected to say "RHR-P-2B DISCH PRESS XMTR" for RHR-PT-37B. no further action required. | 02-00-RHR-PT-37B
387196 | CR | 20181128 | CAQ | D | OG-AY-12B is not indicating properly | N | Y |  | N | YES | <D> **** Detailed Description **** OG-AY-12B is reading zero (0.00) percent hydrogen. This usually indicates that this hydrogen analyzer is not functioning properly. | 02-00-OG-AY-12B
387197 | CR | 20181128 |  |  | Revise MOT-PUMP-1-2 for PMID 970-03, 971-03 | [5 empty] | <D> CMS-P-1401 has item number 9.1. This needs to be evaluated and revised. | 02-00-CMS-P-1401
387198 | CR | 20181128 |  | 3 | OI-9 enhancement |  |  |  | N | NO | <D> **** Detailed Description **** In order to eliminate a potential error trap concerning open procedures that are carried from shift to shift , revise OI-9 to include the following: 7.2.2.d Prior to using a procedure from the open procedure binder in the Field Supervisor office, Main Control Room, or Radwaste Control Room personnel will verify the revision of the procedure to the current revision. If the open procedure is not the current revision, discuss impact of the most recent revision on completing the open procedure with the CRS/SM prior to proceeding with the evolution. See EDMS attachement for justification of the change. <I> **** Actions Taken **** Notified AOM.
387200 | CR | 20181128 | CAQ | D | 2 Pieces of M&TE Suspended/ Lost |  |  |  | N | NO | <D> **** Detailed Description **** 2 Proto Torque Wrenches are Missing from the Clean Tool Crib and can't be located. Calcode #0059688 model 6066A 1000in. No Activity in Met/Track or Portal J. DEF #6778A written. Calcode #0065906 model 6181F 600in. Usage # 1 Per PPM 1.5.4 section 4.4.3 (a-c) Torque Wrench had acceptable post use verification @ +/- .06%. Last c/o 3/7/18 by Mechanic for CW but not reflected as used in Portal J. DEF #6779A written. Bot Suspended/ Lost. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
387202 | CR | 20181128 | CAQ | C | RHR-P-2A new mechanical seal issues identified | Y | N |  | N | NO | <D> **** Detailed Description **** During the performance of WO 02033672-82 to rebuild the mechanical seal it was identified that there was a substance used on the faces of the mechanical seal during the assembly process offsite at the vendor. If this seal from the vendor would have been installed with the pump package the seal would have failed, this would have created a high dose environment and rework. These seals should not have any material used on the faces and should be ultra clean and dry when assembled. There was also 3 small chips on the lower edge of the carbon bushing that were discovered. These will not affect the operation of this bushing. <I> **** Actions Taken **** Notified my supervisor the project manager and the system engineer for direction. | 02-00-RHR-P-2A
387203 | CR | 20181128 |  | 4 | RWCR desk radio not working | N | N |  | N | YES | <D> **** Detailed Description **** Found radio not connecting to radio network. <I> **** Actions Taken **** Found connection to be damaged. Initated AR & WR. Informed MCR. | 02-00-COMM-DSKSET-11A
387204 | CR | 20181128 |  | 4 | CW-CT-1A Access drive missing cement and has exposed rebar. | N | N |  | N | YES | <D> **** Detailed Description **** CW-CT-1A Access drive missing cement and has exposed rebar. Spalling? please evaluate and repair as necessary to preserve columbias assets. Please see attached pictures. <I> **** Actions Taken **** CR Wr <N> Per review of the photo attached to the EDMS of this AR CR: 1) This reinforced concrete degradation is not structurally impacting to the CW-CT-1A cooling tower itself - as is indicated in the AR CR, the degradation is in the access drive slab (i.e., outside the outer perimeter of the cooling tower structure). 2) It appears that insufficient concrete cover over the reinforcement in this access drive slab was provided to protect the encased rebar from degradation (an original construction issue) and led to the concrete and rebar degradation noted in this AR CR. | 02-00-CW-CT-1A
387207 | CR | 20181128 |  | 3 | EWP creating issues with Weld Records |  |  |  | N | NO | <D> **** Detailed Description **** For work Order 02129443 RHR high point vents, in-house welders are using electronic process for prefabrication. WPS is not using electronic work packages so duplicate weld records are resulting, making it difficult for field changes such as cut out and re-weld. It is recommend that following lessons learned be considered: â€¢ Scanned weld records need to be individual PDF files not group scanned. This way if editing is necessary the PDF will not need to be broken down. â€¢ Prefab weld records done electronically need to be printed and made original for WPS craft for the hard copy packages. â€¢ Uniform titles on the Weld Record files are necessary if scanned e.g. weld record number and CODE class B31.1, ASME or AWS. This will assist in closure reviews. â€¢ For Upcoming R24 prefab done by Maintenance craft recommend that the packages be reviewed for proper copies of weld records in the Williams work packages. Recomend that this CR go to maintenance <I> **** Actions Taken **** Contacted WPS and it was determined that the electronic prefab packages are rare and there is no active work impacted. Talked with maintenance supervisor about standardizing the weld records
387209 | CR | 20181128 |  | 4 | Duplicate Revision on Drawing |  |  |  | N | NO | <D> **** Detailed Description **** CVI Drawing was submitted to Document Control for processing by Org 54410 - Design Engineering. Drawing cannot be processed because it is a duplicate revision. <I> **** Actions Taken **** Document Control Supervisor was informed of error. Drawing will be sent back for corrections to be made. CR was issued. <N> This drawing error has been corrected. Portal J has been updated no further action is required. . This AR/CR should be Trended. . Scott Payne Mechanical/Civil Design lead
387212 | CR | 20181128 | CAQ | C | Drawing references incorrect calc for design conditions | N | N |  | N | NO | <D> **** Detailed Description **** Drawing 215-11,81 for the RHR-HX-2A and 2B seal cooler has a note stating that the shell design pressure is 309 psig and the tube design temperature is 480F. This note references calculation ME-02-86-44 for the information. The correct reference for the information is calculation ME-02-85-70. The supply for the shell side of the seal cooler comes from SW (7)-2-2 for Div 1 and SW (6)-2-1 for Div 2, which have a design pressure of 309 psig per specification 1, page 67. The stated shell design pressure of 309 psig is therefore correct. The supply lines for the tube side of the RHR-P-2A/2B seal coolers branch off of RHR (1)-2-1 and RHR (1)-2-2 respectively, just downstream of the pump. The stated tube design temperature of 480F is therefore correct, per specification 1, page 56. What is incorrect is the reference calc. ME-02-86-44 does not exist. ME-02-85-70 analyzed the seal coolers for the higher temperature and pressure and determined them to be acceptable. Therefore, there are no issues with the ability of the seal coolers to perform their design function, as all design information is correct and supported by analysis. <I> **** Actions Taken **** Located the correct analysis for the change in design temperature and pressure. Confirmed that the pressure and temperature used in the analysis are still valid by locating the design pressure and temperature in the ASME design specification, spec 1. | 02-00-RHR-HX-2A,02-00-RHR-HX-2B
387213 | CR | 20181128 |  | 4 | ILC Simulator Interruptions | N | N |  | N | NO | <D> **** Detailed Description **** Two simulator aborts occurred during ILC training on 11/7/18 and 11/13/18. Training was able to be completed and no objectives were missed. The CR is required per TDI-06, Simulator Management, for a simulator interruption. SR 2839 and SR 2834 document resolution of the THOR aborts that caused the simulator interruptions. No further action is required under this CR. The simulator performance indicators have been updated with the information. Recommend assignment to training and closure.
387216 | CR | 20181128 |  | 4 | CO-V-10A, Leaking by seat | N | N |  | N | YES | <D> **** Detailed Description **** CO-V-10A found to be leaking by its seat during the attempted tagout of L-CO-P-2A-001. Leak rate was to much to allow for pump repack. Local isolation valves were checked closed with no change in leak rate. The midas meter was used to confirm that CO-V-10A is leaking by it seat with CO-P-2B in service. <I> **** Actions Taken **** Recommend valve rebuild during next available window when the Deaerator is out of service. | 02-00-CO-V-10A
387217 | CR | 20181128 | CAQ | D | CMS-SR-21 TDAS X413 | N | N |  | N | YES | <C> This CR was found at INPROG and was moved forward to APPROVED. <D> While performing ISP-CMS/PRM-X308 CC per WO#02100673-01 it was discovered that TDAS point X413 is not functioning due to MUX 12 failure. <I> Stopped and placed work in a safe condition, notified the CRS and Maintenance Supervision. After speaking to our supervision we were notified that MUX 1 and Mux 12 had failed and are being replaced making TDAS X413 unavailable for the day. We were instructed to continue with X308 and initiate a CR. <N> CMS-RIS-12B MCR | 02-00-CMS-RIS-12B,02-00-CMS-SR-21,02-00-TDAS-MUX-12
387218 | CR | 20181128 | CAQ | D | DG4 failed to start during vendor investigation. | N | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02134870-01, then taken back to complete <D> **** Detailed Description **** During vendor investigation of DG4 per WR 29142879, the diesel failed to start at step 5.2.5 of SOP-DG4-PM. Further vendor troubleshooting indicated a failure of the motherboard. <I> **** Actions Taken **** Vendor ordered a new board and will be onsite tomorrow to repair. | 02-00-E-GEN-DG4
387219 | CR | 20181128 |  |  | Prohibited Item Declared at Security Checkpoint | [5 empty] | <D> An individual scheduled for an-onsite interview, this date, declared at the Security Checkpoint that he had a taser in his vehicle.
387220 | CR | 20181128 | CAQ | D | Skimmer surge tank B level hi-hi alarm | N | N |  | N | YES | <C> CR reopened to cross reference additional WO 02131807, marked completion required box, then taken back to complete <D> **** Detailed Description **** Received 4.627.FPC2 "SKIMMER SURGE TANK B LEVEL HIGH-HIGH" alarm. FPC-LIS-2 indicates 48% and steady, this alarm comes in at 49% according to the ARP and COND-V-42 is closed. | 02-00-FPC-LIS-1B,02-00-FPC-TK-1B
387221 | CR | 20181128 |  | 3 | SOP-HVAC/WCH-LU will need to be updated |  |  |  | N | NO | <D> **** Detailed Description **** SOP-HVAC/WCH-LU will need to be updated following completion of WO 02085540-01. Currently the lineup procedure just shows all vents and drains as closed, however, M550-01 shows them as closed and capped.
387222 | CR | 20181128 |  | 3 | SOP-TSW-LU will need to be updated |  |  |  | N | NO | <D> **** Detailed Description **** SOP-TSW-LU will need to be updated following completion of wo 02085540-01 for TSW-V-H610 being closed and capped. | 02-00-TSW-V-H610
387224 | CR | 20181128 | CAQ | C | Incorrect Grayboots for RHR-MO-49 Motor Replacement | Y | N |  | N | YES | <C> At the direction of MRT today, CR Severity moved from D/Trend Repair and assigned as a C to AR-MNTPLAN group. <D> **** Detailed Description **** Under W.O. 02093558-01 Replace Motor Operator and Pinion Gear where steps to set up for Reterming the new motor using Grayboot connectors instead of reterming using Raychem to allow for half of the reterm to occur outside of the high radiation area and so that future determ/reterm tasks would be significantly quicker and lower dose. None of the Grayboots ordered to support that work where of the correct type and the correct type is not available in our system. <I> **** Actions Taken **** Initialted C.R., informed Work Week Manager, Electrical Component manager, and Engineering. Material Request added ordering appropriate Raychem materials. NOTE: The grayboot ordered was for the cable size, however the insulation was thicker requiring a different grayboot (no CATID or stocked). This was determined when the wiring was measured in the field. | 02-00-RHR-M-V/49,02-00-RHR-MO-49
387227 | CR | 20181128 |  | 4 | Prohibited Item Declared at Security Checkpoint |  |  |  | N | NO | <D> **** Detailed Description **** An individual scheduled for an on-site interview, declared a taser, at the Security Checkpoint. <I> **** Actions Taken **** Individual was turned away by Security. The individual who made the arrangements was coached, as well as the individual who was scheduled to be interviewed.
387229 | CR | 20181128 |  | 3 | Work orders w/ embedded pmts cause schedule adherence hits |  |  |  | N | NO | <D> **** Detailed Description **** Work orders for starter coil inspections had embedded pmts that caused schedule adherence hits to station metrics. The following "B" adherence work orders could not be completed as scheduled due to a clearance order that was in effect beyond the scheduled completion time: WOs 0211724801, 0211726601, 0211837601. These work orders did not require the clearance but they could not be fully completed until the clearance was lifted and power restored. Recommend planning perform extent of condition on future work orders with embedded pmts. Update model work orders such that a separate pmt task exists for work that the pmt task may be delayed after completion of the main task. <I> **** Actions Taken **** Inititated CR, WWM, RM informed.
387230 | CR | 20181128 |  | 3 | Steam cycle loss of 2 MWe |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Over the course of the October and November 2018, an unidentified steam cycle loss has appeared on the Thermal Performance tracker, gradually growing and fluctuating to around 2 MWe. The loss is known to be steam cycle related because the condenser performance remains steady (accounting for the CW flow issues in CR 380183). Recommend assignment to AR-PPROG for further evaluation and tracking. CIM evaluation and steam trap monitoring should be initiated by BOP and Thermal Performance. There is no immediate impact to station safety or operability. <I> **** Actions Taken **** Initiated CR. Began review of CIM data. Discussed with BOP Engineering.
387233 | CR | 20181128 |  | 3 | AR 00381020 resolution is inadaquate |  |  |  | N | NO | <D> **** Detailed Description **** AR 00381020 was wriiten to document that HT-TS-71/1A/C and HT-TS-71/1A/L are listed in asset suite as reg guide 1.97 instrumentation. the resolution to AR 00381020 closed this AR stating that the heatrace is not required to meet reg guide 1.97 per EC 4789 rev 3A. however the EPNS in asset suite still say they are reg guide 1.97. . An Action to engeneering to update the requirements screen for HT-TS-71/1A/C and HT-TS-71/1A/L is needed. to remove the reg guide 1.97 codes. This is legacy administrative issue. <I> **** Actions Taken **** Wrote CR. | 02-00-HT-TS-71/1A/C,02-00-HT-TS-71/1A/L
387234 | CR | 20181128 | CAQ | D | The DOE EOC radio is not working | N | Y |  | N | YES | <D> **** Detailed Description **** DOE reported the radio at their EOC (Federal building) is not working. The phones are operable. <I> **** Actions Taken **** Telecom expects to have it fixed tomorrow. 11/29/18 Notified: EP and the SCC. <N> **** Equipment Description **** Federal building
387235 | CR | 20181128 | CAQ | C | (QA) RHR-M-P/2A WOT Not Routed to QC |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) WOT 02117218-66 was not routed to Quality Control (QC) for review prior to being taken to Approved and then Ready status. WOT 02117218-66, Rotational Bump Check / Uncoupled Run of RHR-M-P/2A, contains Quality Control Hold Points within the task instructions, multiple QC inspection plans and QC resource hours. QAP-ASU-07, Peer Verification Program Planning, lists types of work requiring QC review. MI-1.22A, Maintenance Planners Guide, requires the addition of a QCI Hold Code on tasks requiring review / approval by Quality Control prior to advancing the task to Approved / status 30. Not routing work tasks to Quality Control for the types of work defined within QAP-ASU-07 could result in missed programmatically required QC inspections, QC hold points with incomplete or inaccurate work instructions, incomplete or inaccurate acceptance criteria as well as QC Inspections that are not necessary or programmatically required. . . <I> **** Actions Taken **** Notified Maintenance Planning Supervisor, Quality Services Supervisor and set the task to Returned status. | 02-00-RHR-M-P/2A
387236 | CR | 20181128 | CAQ | D | Hold pump tripped off following precoat of FDR-FU-19 | N | N |  | N | YES | <D> **** Detailed Description **** Following the Backwash and Precoat of FDR-FU-19 when the timer completed the Hold pump turned on. While verifing other indications the hold pump kicked off and precoat was lost. <I> **** Actions Taken **** Expanded team to MCR, initiated AR. | 02-00-FDR-FU-19,02-00-FDR-P-17
387237 | CR | 20181128 | CAQ | D | Licensing Basis and Procedures out-of-sync |  |  |  | N | NO | <D> **** Detailed Description **** A change to the Operational Quality Assurance Program Document (OQAPD) & the Final Safety Analysis Report (FSAR) via LDCN-18-015 supporting Delivering the Nuclear Promise (DNP) Efficiency Bulletin (EB)16-23 had 4 associated procedure changes which were made active in Asset Suite on 11/28/2018 without the supporting Licensing Basis Documents (LBD), i.e., the OQAPD and the FSAR being made active at the same time. The Licensing Document Change Notice (LDCN) was on hold to be released simultaneously with the procedures however only one of the procedures had an associated hold in Automated Procedure Process Workflow (APPW). Three of the procedures had no hold so when signed by the final approver they were available for release. The 4th procedure had a hold but the hold was not associated with other documents or actions Therefore, the LBDs and the procedures are out of sync. <I> **** Actions Taken **** Notified managers, Quality and Regulatory Affairs. Wrote CR. Quality and Licensing worked with RIM to expedite the release of the OQAPD and the FSAR to support the revised procedures. Recommend Cat 3 Trend to Quality. <N> LDCN-18-015 which changed the OQAPD and the FSAR went live today. The Revision 54 of OQAPD is in asset suite. The FSAR update to the Licensing Tree is complete.
387238 | CR | 20181128 | CAQ | D | FPC-V-152B Leaking by to Scupper | N | N |  | N | YES | <D> **** Detailed Description **** FPC-V-152B is leaking by at about 0.5 gallons per minute. FPC-V-152B is hard piped to a scupper. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** FPC H/X Room | 02-00-FPC-V-152B
387240 | CR | 20181128 |  | 4 | BRE 33 OCA Camera Needs Maintenance | N | N |  | N | NO | <D> **** Detailed Description **** BRE 33 OCA Camera Needs Maintenance <I> **** Actions Taken **** Security Supervision Notified, CR/WR Initiated <N> **** Equipment Description **** NE PA BRE 33
387241 | CR | 20181129 |  | 4 | EDR-P-5A/5B did not start and HI Hi level alarm received | N | N |  | N | YES | <D> **** Detailed Description **** when temporary sump pump turned off after maintenance per W/O 02128871 hi hi level alarm received and EDR-P-5A/B did not start . Suspect level switch issue. Pump did start when temperature switch activated. Suggest checking level switch when area cleaned up after flushes per W/O 02128871-15. area is high rad and high contamination - see W/O for possible ALARA task. <I> **** Actions Taken **** restored temp sump pump to operation and pumped sump down. | 02-00-EDR-P-5A,02-00-EDR-P-5B,02-00-EDR-SUMP-R5
387247 | CR | 20181129 |  | 3 | Revise MOT-PUMP-1-2 for PMID 970-03, 971-03 |  |  |  | N | NO | <D> **** Detailed Description **** CMS-P-1401 has item number 9.1. This needs to be evaluated and revised. This has been discussed with the MOT owner. <I> **** Actions Taken **** Initiate CR | 02-00-CMS-P-1401
387248 | CR | 20181129 |  | 4 | 2 Pieces of M&TE OOT | N | N |  | N | NO | <D> **** Detailed Description **** 2 Pieces of M&TE found OOT & adjusted within specs. Both were NOT used during Calibration cycles. Calcode #45413 HP RMS Voltmeter- model 3400A. DEF #6780A written. Calcode #0065605 Heise Press. Calibrator- model PTE-1. DEF #6781A written. No Action Required. <I> **** Actions Taken **** None Trending purposses only.
387249 | CR | 20181129 |  | 4 | M&TE Rejected | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0063204 Quest Technologies Heat Stress Monitor -model Questemp 32 found OOT & Rejected- wouldn't power on & Contaminated- can't be sent out for repair. Not used during Calibration cycle. DEF #6782A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
387250 | CR | 20181129 |  | 4 | 2 Pieces M&TE OOT | N | N |  | N | NO | <D> **** Detailed Description **** 2 Quest Technology Thermal Environment Monitors- model Questemp 44's wouldn't power on and need repair. Used for personal safety only. No Plant Impact. Calcode #0065561. DEF #6783A written. Calcode #0067089. DEF #6784A written. No Action Required. <I> **** Actions Taken **** None Trending purspoes only.
387251 | CR | 20181129 | CAQ | C | Extent of Condition Findings for Controlled Documents |  |  |  | N | NO | <D> **** Detailed Description **** This CR is not associated with equipment. The purpose of this CR is to document misalignments between controlled documents, identified by extent of condition assignment CR EOC 384482-05. Specifically, the following controlled documents contain misalignments with DES-6-1 or DES-6-3 for design of plant digital SSCs. (FORM FORM 27162 rev 002), (FORM FORM 26345 rev 012) (PPI PPM ENG-DES-50 rev 001) (PPI ENG DES-4-8 rev 005) (PPI SWP SWP-CSW-27 rev 002) (PPI ENG DES-2-8 rev 011) (PPI ENG DES-4-12 rev 012) (PPI ENG DES -4-7 rev 014) (PPI ENG NFM-4-5 rev 002) (PPI DDSI DDSI -DOC-02 rev 008) (MAN SPES SPES-1.6.7 rev 054) (FORM FORM 26108 rev 011) (PPI ENG DES-2-1 rev 057) (PPI ENG DES-6-1 rev 018) (PPI ENG DES-6-3 rev 02). A detailed description is provided on the EDMS.
387252 | CR | 20181129 |  | 3 | R24 02111490 (E-MC-8BB) WIâ€™s changed without RO/SRO review |  |  |  | N | NO | <D> **** Detailed Description **** R24 02111490 (E-MC-8BB) E-CB-8B2D: INSPECT MCCB WIâ€™s changed without RO/SRO review We found WO 02111490 instructions had been changed significantly when doing the clearance order second checks. There wasnâ€™t RO/SRO hold placed on the WO so the new WIâ€™s could not be verified against the current C/O boundary. Attached in the EDMS is the PDF file thatâ€™s contained in the CERT package for 02111490 located in the clearance attachments and the current WO instructions. <I> **** Actions Taken **** RO hold placed on WO and CR written
387255 | CR | 20181129 |  | 4 | RWCU-P-3A seal leakage ( pencil size stream) ALARA | N | N |  | N | YES | <D> **** Detailed Description **** RWCU-P-3A has seal leakage that is being directed into the designed drip tray. Current leak rate is only that of a pencil size stream; however, past occurances of pencil size streams have degraded quickly into full on Spray and ABN -RAD-SPILL. Reference WR# 29108318. This OE showed that in only a matter of 3 days of pencil size stream went by before full on failure of the seal which required isolation. WO 02073789 is being planned for RWCU-DM-1A work (sheduled for mid Janruary). RWCU-P-3A would be isolated to support this work. If possible these repairs should be completed together. Significant Time and Dose savings could be achieved (ALARA). Please See EDMS for snap shot of previous WR detail and video of leakage. RWCU-DM-1A is currently in service and RWCU-P-3A is in standby. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RW 467 | 02-00-RWCU-P-3A
387259 | CR | 20181129 |  | 3 | OPDS CVT heater branch circuit breaker found in OFF position | N | N |  | N | YES | <D> **** Detailed Description **** As part of the Open Phase Detection System monitoring and tuning efforts, a line up discrepancy was identified for the auxiliary branch OPDS CVT Control Panel Box Heater Circuits. Review of line-up procedures for OPDS (SOP-ELEC-AC -LU) and the OPDS physical configuration identified: (1) branch circuit breaker OPDS-CB-PP/B/11 (on OPDS-PP-B located inside OPDS-BLDG-B in the Transformer Yard) is in the OFF position and (2) Branch circuit breaker OPDS-CB-PP/S/11 (on OPDS-PP-S located inside OPDS-BLDG-S in the Transformer Yard) is in the OFF position. The expected configuration per SOP-ELEC -AC-LU for the OPDS-CB-PP/B/11 and OPDS-CB-PP/S/11 are for both of these CBs to be in the ON position. OPDS-CB-PP/B/11 services the OPDS Capacitive Voltage Transformer (OPDS-CP-B1/CVT) Control Panel Box Heater Circuit (which services the OPDS-CVT-B1/A, OPDS-CVT-B1/B, and OPDS-CVT-B1/C Termination Box Heaters). OPDS-CB-PP/S/11 services the OPDS Capacitive Voltage Transformer (OPDS-CP-B1/CVT) Control Panel Box Heater Circuit (which services the OPDS-CVT-S1/A, OPDS-CVT-S1/B, and OPDS-CVT-S1/C Termination Box Heaters). The Control Panel Heater Circuit is a supplemental heater circuit, which functions only to reduce potential condensation (for reducing long term possible oxidation/rusting of terminations/equipment) inside the Control Panel and Termination Panel Boxes for the OPDS CVTs. The OPDS-CP-B1/CVT and OPDS-CP-S1/CVT Control Panel Heater Circuits utilize a thermostat to automatically turn on/off the heaters (between 45ÂºF and 60ÂºF). Per CVI OMM 1262-00,1, once the CVTs are in service it is not recommended to keep the heater on especially when ambient temperature exceeds 40ÂºC (104ÂºF). No significant impact / degradation of the CVT Control Panel and Termination Panel Boxes is expected from having OPDS-CB -PP/B/11 and OPDS-CB-PP/S/11 in the OFF position. This CR (by Work Request) will drive energizing the CVT CP heater circuits; update to SOP-ELEC-AC-LU to include notes on the OPDS CVT Termination Box and Control Panel Heaters and updates to SOP-COLDWEATHER-OPS / SOP-WARMWEATHER-OPS to include line-up of the OPDS CVT Termination Box and Control Panel Heaters. <I> **** Actions Taken **** Spoke with SM Work Request generated as part of CR Confirmed with Vendor (Trench) and BPA that CVT heater circuits are not required for CVT to function correctly (heater circuit is only an electrical good practice for reducing potential condensation and subsequent degradation). <N> **** Equipment Description **** Branch Circuit Breakers located within OPDS TR-B and TR-S relay buildings within Transformer Yard; CVT physically located in Transformer Yard. | 02-00-OPDS-CB-PP/B/11,02-00-OPDS-CB-PP/S/11
387260 | CR | 20181129 |  | 3 | Conditional Release Logs not Found |  |  |  | N | NO | <D> **** Detailed Description **** An HP technician was attempting to document a conditional release of a source when he discovered that the binder for the logs had been emptied, this kept him from knowing the next CRT Number that should be used on the form. <I> **** Actions Taken **** The HP technician contacted his supervisor for help. The suprvisor noticed that there was no DIC number on form #26485, which is the log to be used as per PPM 11.2.15.7, Release of Material from Radiologically Controlled Areas. Section 7.2 of 11.2.15.7, states that the log, form 26485, does not require permanent retention in plant files, but should be retained by RP for reference purposes for a period of one year, after which they may be discarded. The retention file was found to not contain the removed logs from the emptied binder. A search of other possible file locations was then conducted, but the logs have yet to be found.
387261 | CR | 20181129 |  | 4 | SAT-V-17 unable to operate | N | N |  | N | YES | <D> **** Detailed Description **** During the clearance lift for the SAT-TK-2 work 02123672 it was identified that SAT-V-17 a newly replaced vale was unable operate. It is presumed to be clogged with residual gunk the tank. <I> **** Actions Taken **** CR and WR generated. | 02-00-SAT-LG-2,02-00-SAT-TK-2,02-00-SAT-V-17
387264 | CR | 20181129 | CAQ | D | IDS 20 | N | N |  | N | YES | <D> **** Detailed Description **** IDS 20 12/24 false alarms <I> **** Actions Taken **** Compensatory measure put in place. A walkdown of the zone provided no known cause of alarms. | 02-00-SEC-IDS-EVAL/20/21
387265 | CR | 20181129 |  | 4 | EDR-P-5 Discharge Valves Wonâ€™t Open | N | N |  | N | YES | <D> **** Detailed Description **** EDR-V-21 and EDR-V-22 both indicate shut. EDR-TIS-601 controls the position of these valves such that one of the two should always be open, depending upon the temperature of the water in the R-5 sump. Cycled the setpoint of EDR -TIS-601 in order to simulate R-5 sump as having high temperature; EDR-P-5 did start as expected, but both EDR -V-21 and -22 remained shut.. EDR-SPV-21 controls the position of both EDR-V-21 and -22, so it is possible that the solenoid has failed. The instrument rack air supply valve to EDR-SPV-21, IR61-V4, was verified open. Per ABN -CAS, EDR-V-21 and -22 both fail AS-IS, so having both shut is odd. EDR-P-5 has been caution tagged in Pull-to-Lock to prevent pump running with no discharge path. | 02-00-EDR-P-5A,02-00-EDR-P-5B,02-00-EDR-SPV-21,02-00-EDR-SUMP-R5,02-00-EDR-V-21,02-00-EDR-V-22
387266 | CR | 20181129 | CAQ | D | RPS Testbox lamp to RPS-RLY-K12H did not extinguish as expec | Y | N |  | N | YES | <D> **** Detailed Description **** While performing ISP-APRM-S404 per WO#02104724-01 during step 7.4.34 the RPS Test box lamp failed to extinguish. . Condition above noticed during the first operation of the relay with the test box in place; first operation being the test of the Trip Relay in the 'Y' postion of APRM-UPSC and It was noticed that during the second cycling of the relay in the Trip Relay in the 'Y' postion of APRM-UPSC lamp stayed extiguished; this condition is likely due to the cycling of the relay. <I> **** Actions Taken **** initiate CR, inform operations, document in the work order. | 02-00-RPS-RLY-K12H
387267 | CR | 20181129 |  | 3 | Procedural Enhancement OSP-ELEC-W101 |  |  |  | N | NO | <D> **** Detailed Description **** There is a note in OSP-ELEC-W101 which is not correct. The note following step 7.1.12 of OSP-ELEC-W101 states: "H13 -P800.C3.1-7 and H13-P800.C3.2-7 are normally illuminated when E-TR-S is NOT loaded." This statement is no longer true and needs to be removed.
387268 | CR | 20181129 |  | 4 | Mech Boom Ttuck anti-two block needs repair. | N | N |  | N | NO | <D> **** Detailed Description **** No impact to plant equipment. As part of Monthly PM it was determined the anit-two block needs addressed prior to future use. <I> **** Actions Taken **** Facilities contacted, Do not use tag placed as part of maintenance. Truck is being delivered to facilities to support repair. No futher action required. <N> **** Equipment Description **** Mechanical maintenance Boom Truck No WR needed at this point, Facilities will address.
387269 | CR | 20181129 | CAQ | D | FDR-P-17 failed to start after Precoat | N | N |  | N | YES | <D> **** Detailed Description **** FDR-P-17 (hold pump) failed to start at the end of the FDR-FU-19 Precoat cycle. This has been a reoccuring problem in the last month. Reference WR# 29145443, 29145549 and 29145808. FDR-FU-19 had previously reached iths High D/P lockout. Per the ARP the "ON HOLD" pushbutton was pressed and held for 10 seconds, before the Backwash was started. Note, the PLC logic was not reset (cycle power supply breaker) when performing the Backwash, based on previous watch's successful Precoats without performing this reset. During the Precoat of FDR=FU-19, precoat flow was abnormally low (~ 130 gpm). Normal precoat flow should be ~ 300 gpm. Per procedure 190 to 370 gpm is reccommended. This is further evidence of the badly degraded septum on FDR-FU-19. It is likely that these two issues are related. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RW 467 | 02-00-FDR-FU-19,02-00-FDR-P-17
387270 | CR | 20181129 |  | 4 | TB 501 W light fixture vibrating | N | N |  | N | YES | <D> **** Detailed Description **** The high bay light fixture above the 501 TB SW stairwell is vibrating to the point where the light seems to be flickering. It may be that the mounting fixture is coming loose. It does not appear to be in imminent danger of failing or coming off at this time. <I> **** Actions Taken **** Notified FIN and initiated WR | 02-00-T-BLDG-MISC
387272 | CR | 20181129 | CAQ | D | Fire brigade SCBA seals |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Three of the staged Fire Brigade SCBA cases at the TG 441 turnout station were found to have either missing or broken inventory Seals. All three cases were re-inventoried by the Fire Brigade Leader and have been re-sealed with no equipment deficiencies noted. This AR generated for trending purposes. It is of high importance that these SCBAs be in a condition to allow unhindered response during an emergent situation. <I> **** Actions Taken **** Informed MCR/Fire Brigade Leader. Reperformed inventory checks and re-sealed SCBA cases. <N> **** Equipment Description **** TG 441 Fire Brigade Turnout Station
387275 | CR | 20181129 |  | 3 | SOP-REFUEL-OPS needs a new step. |  |  |  | N | NO | <D> **** Detailed Description **** The first step in SOP-REFUEL-OPS section 5.6 should be to ensure the grapple / camera light is turned off. This will allow time for the lights to cool off in the water prior to lifting the mast out of the water. These lights generate a lot of heat and when pulled out of the water while still on or hot causes them to dry out quickly increasing the potential of radiological airborne release. Please add this one step to ensure the lights are off and cooled down. <I> **** Actions Taken **** Wrote this procedure change request.
387276 | CR | 20181129 |  | 4 | SCW-P-1 Cyclical Bearing Noise | N | N |  | N | YES | <D> **** Detailed Description **** SCW-P-1 has a cyclical bearing noise. This bearing noise should be investigated and evaluated for potential bearing failure. At this time it does not sound like failure is imminent but this investigation should be a priority. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TB 441 West | 02-00-SCW-P-1
387277 | CR | 20181129 |  | 4 | RFW-VBI-1A/XS/TE Above Min RPM Light Extinguished | N | N |  | N | YES | <D> **** Detailed Description **** The â€œAbove Min RPMâ€ light on RFW-VBI-1A/XS/TE was found extinguished. Per CVI OMM 660-00,3 page 613 This light extinguishes when rotating speed falls slightly below 1 RPM. On page 618 of the OMM it describes that detected RPM is compared to an oscillator frequency. Looking at EWD -72I-025 seems to show the detected RPM is from RFW-SE -T/1A. This speed keyphasor also provides RPM indication to RFW-VBI-SE/T1A (Vector Filter) which is indicating RPM as expected. If this is correct it may indicate an issue with the oscillator frequency in the timing control circuit. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TB 441' E | 02-00-RFW-VBI-1A/XS/TE
387278 | CR | 20181129 | CAQ | D | Rod Accum Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-3823 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-3823. OPs 2 reports the source of the alarm was high moisture, the alarm is clear. <I> **** Actions Taken **** Drained moisture per SOP-CRD-HCU | 02-00-CRD-HCU-3823
387279 | CR | 20181129 |  | 4 | Elevator craft worker did not have proper PPE |  |  |  | N | NO | <D> **** Detailed Description **** While preforming the RW elevator upgrade, a craft worker did not have safety shields installed on their safety glasses while performing work. Also, the elevator door was open while out of service without a barrier tape across the door opening. <I> **** Actions Taken **** The individual was coached, the project took a stand-down where the entire crew was coached on Industrial safety is a fundamental behavior and should always be adhered too. Safety is not a personal choice itâ€™s a condition of employment. The individual could have sustained an eye injury and someone could have walked into the elevator while work was ongoing putting them in harms way. A Thumbs down write-up for elevator project will be generated.
387280 | CR | 20181129 |  | 3 | Evaluate if chill water pump needed to vent WCH system |  |  |  | N | NO | <D> **** Detailed Description **** SOP-HVAC/WCH-FILL WCH system fill and vent (WCH-CR-51A/B) is not well laid out. Section 5.1 reads as if you do not need a chill water pump running, it never has you verify one running. Instead after you vent it tells you to start WCH-CR-51A/B per the SOP-HVAC/WCH-START. SOP-HVAC/WCH-START has you start a chill water pump. Request evaluating if we can get a good vent on the WCH system including the RW 525 coils and WCH-CR-51A/B without a pump running? If not, SOP-HVAC/WCH-FILL Needs to be updated.
387281 | CR | 20181129 | CAQ | D | HCU 46-31 Scram solenoids making above average noise. | Y | N |  | N | YES | <D> **** Detailed Description **** Found HCU 46-31 making louder than than other HCU vibrational noise. Thermal imaging shows no discernable difference between solenoids. Could not feel difference in vibrations. <I> **** Actions Taken **** Informed MCR, initiated AR/WR. | 02-00-CRD-HCU-4631
387284 | CR | 20181129 |  | 3 | Gap Training not Documented After Identified in SA |  |  |  | N | NO | <D> **** Detailed Description **** During the 2016 Chemistry and Radiation Protection Focused SA, a deficiency was identified that chemistry updates training (JITT) for the new circulating water system chemical addition process was not documented. The intended action out of the SA was to document the revision of the initial lesson material with the GE Halogenation skid and to provide the gap training. Although the initial training material has been updated there is still no record of gap training being completed. Interviews with training instructors and the line SME indicate the training was conducted but they failed to document the completion. Refresher training on this topic is scheduled to be taught in continuing training cycle 19-01. <I> **** Actions Taken **** contacted training management.
387285 | CR | 20181129 |  | 3 | Required M&TE is not available for circuit breaker testing |  |  |  | N | NO | <D> **** Detailed Description **** Both primary injection test sets (PITS) are malfunctioning. This M&TE is required to perform primary injection testing which is used to test circuit breaker overcurrent trip setpoint testing. Recommend immediate turn around as this test equipment is needed for numerous pre-outage bench tests. WO 02126249-02 is on hold until repairs can be completed <I> **** Actions Taken **** Initiated AR, notified M&TE staff.
387286 | CR | 20181129 |  | 3 | Indications of plugging on OLNC injection lines | N | N |  | N | YES | <D> **** Detailed Description **** During review of the data from Online Noble Chem Application in November 2018 and comparison with previous applications, it was noted that the platinum injection lines are indicating signs of plugging. The line pressure normally starts at about 1070 psi and slowly increases up to about 1120 psi over the 10 day application period. During November 2018, the injection line pressure started at about 1120 psi and quickly increased to about 1200 psi. The 10 day platinum application was successfully completed with persistent intervention by the vendor to manipulate the injection flows and keep the lines from completely plugging. OE from other nuclear plants indicates that the platinum injection lines will eventually plug and have to be cleaned out. Recommend assignment to Chemistry. <I> **** Actions Taken **** Consulted with GE-Hitachi regarding injection line plugging and options for resolution. They recommend cleaning the injection lines by removing the injection lines at both the â€œAâ€ and â€œBâ€ feedwater locations and cleaning the injection taps during the next refueling outage or consider installing OLNC Injection Quills. If Injection Quills are not installed, Columbia should plan on injection tap cleaning at all future refueling outages. An opportunity exists to volunteer through the BWROG to be the second Pilot Plant for installation of the OLNC injection Quills. The advantage to Columbia is that the cost of the materials and services would be paid by BWROG. It is believed that all nuclear plants will eventually by required to install the OLNC Injection Quills and have to pay the full cost of materials and installation. The cost could be well over $100K. | 02-00-RFW-V-908A,02-00-RFW-V-908B,02-00-RFW-V-909A,02-00-RFW-V-909B,02-00-RFW-V-910A,02-00-RFW-V-910B,02-00-RFW-V-911A,02-00-RFW-V-911B,02-00-RFW-V-912A,02-00-RFW-V-912B
387287 | CR | 20181129 |  | 3 | 2018 Annual Force on Force engagments |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate the conditions leading to the simulated neutralization of a security response officer during the conduct of the November 28, FOF exercise. <I> **** Actions Taken **** Security Programs Superviser advised. This action is being closed to the cross referenced CR 385670 for addressing simulated engagements in quarterly training. No further action is required.
387288 | CR | 20181129 |  | 3 | 2018 Annual Force on Force neutralization |  |  |  | N | NO | <D> **** Detailed Description **** A friendly fire incident occurred during the conduct of the November 28, 2018 FOF exercise. This resulted in the simulated neutralization of a security response officer. <I> **** Actions Taken **** Security Programs Superviser advised. This action is being closed to the cross referenced CR 385670 for addressing simulated engagements in quarterly training. No further action is required.
387289 | CR | 20181129 | CAQ | C | B5b Pumper Truck Still Won't Prime | N | Y |  | N | YES | <C> At the direction of MRT today, CR Severity moved from D/Trend Repair and assigned as a C to AR-PPROG group. <D> **** Detailed Description **** The B5b pumper truck would not prime using the procedure given. Each time, per procedure, the 30-second time limit would be reached, and attempt to prime would be stopped. At the stop, an odd burning smell was noted. It appears the same problem is still occurring. Please investigate and repair. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** Bldg 600 | 02-00-B5B-P-1
387290 | CR | 20181129 | CAQ | C | B5b truck level gauge broken | N | Y |  | N | YES | <D> **** Detailed Description **** B5b-P-1 level gauge was contacted by corrugated draft hose being removed from left roll up door on rear end of the truck, and was sufficiently brittle that both screw holes broke and it fell off. It was placed inside the left roll up door. Recommend replace with new level gauge, possibly in a less vulnerable location. <I> **** Actions Taken **** Inforrmed CRS, generated AR/WR. | 02-00-B5B-P-1
387291 | CR | 20181129 |  | 3 | Corporate property not in accordance with GBP-IS-36 |  |  |  | N | NO | <D> **** Detailed Description **** Corporate property travelled not in accordance with GBP -IS-36. <I> **** Actions Taken **** Electronic device was taken to IS for evaluation.. <N> Review completed by IS. Virus Scan was completed with no identified issues. Individual was coached on the procedure use for traveling with EN resources. No further action required.
387292 | CR | 20181129 | CAQ | C | Include effects to PRM alarm setpoints in AER |  |  |  | N | NO | <D> **** Detailed Description **** This CR does not affect plant operability, it is being written to track an action for the chemistry effluents specialist: Deliverable: The impacts to the PRM alert/alarm set points due to the events documented in CR 386750 should be included in the 2018 annual effluents report (AER). The applicable time frame for these effects is from 10/26/18 to 11/9/18. This CR should be assigned to the Chemistry Effluents Specialist, and have a due date of May 1st, 2019 to align with the submission of the 2018 annual effluence report.
387293 | CR | 20181129 |  | 4 | MT-CRA-1 Upgrade - Degraded Part Dropped to TG 501 Floor | N | N |  | N | YES | <D> **** Detailed Description **** During operation of the trolley, a degraded collector arm and pieces of plastic insulator material fell from the "B" girder area to the 501' floor below. Due to known degraded buss conditions, a barrier was in place around the overhead crane travel zone IAW ISPM-18 and personnel were briefed to remain clear of the trolley travel path during trolley operations. Note: Trolley buss bars were already de-energized as part of the demolition portion of the crane upgrade work. <I> **** Actions Taken **** Placed crane in safe condition. Requested OEM techs inspect buss collector components and provide recommendations to mitigate further falling debris. Recommend to disposition this CR for trending only. Since the demoilition plan includes steps to remove degraded buss materials that step will be done now rather than when scheduled to prevent any addtional loose debris. The potential of falling debris was part of the crane bridge movement | 02-00-MT-CRA-1
387294 | CR | 20181129 | CAQ | C | (QA) Quality Level 1 Cable Storage in question |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Quality Level 1 Cable Storage Area in Question. Quality Level (QL) one cable storage for 800 feet of QL1 cable, Catalog Identification number (CID) 71802101 issued under Material Request (MR) 236953 shows, in Asset Suit that this cable was stored in area G that is outside and not available for issue to the plant per current controls due to potentially degraded conditions of the material. Quality issued an Area Requiring Management Attention (ARMA) via CR 386673 on 11/12/18 which documents over 100 spools of electrical cabling segregated and stored outdoors (in area G) and many of these were significantly degraded. Additionally, wording in the MR notes field entered by the Storekeeper presents questions as to whether or not the correct material was issued. Quality discussed this issue with the warehouse supervisor who stated that the roll of cable used to supply the 800 feet in question was currently inside of warehouse 5 and the location (G) shown in Passport was incorrect, similar to examples identified in the above ARMA. The notes in the MR questioning the correct material were from the nightshift Storekeeper to have the dayshift personnel verify that the cable was the correct CID, which was performed, however the notes were not updated to reflect this action. Visual inspection of the approximate 180-foot roll and 620-foot roll of cabling by QC, during acceptance inspection for use in the plant, found the cable to be the correct material with no apparent degradation noted on the external layer of the cable spools presented for inspection. This issue is similar to the one identified in the ARMA but with a different CID. AR 386673 assignment 01 issued under the ARMA will verify and validate accurate inventory locations for all current usable spool wire inventory and correct any inaccurate location codes in Passport. This assignment is currently due by 1/10/19. Completion of this assignment will eliminate future questions. Recommend severity 4 assignment to Supply Chain Services. <I> **** Actions Taken **** Discussed with the Warehouse Supervisor and Williams Plant Services Supervisor.
387295 | CR | 20181129 |  | 4 | H2-F-1/2 Pipe union fittings small H2 Leak | N | N |  | N | YES | <D> **** Detailed Description **** There is a small H2 leak on both the inlet and outlet pipe union fittings for H2-F-1/2. See EMDS for Snoop Check video <I> **** Actions Taken **** Informed supervision <N> **** Equipment Description **** TB 471' West H2 Dryer Skid | 02-00-H2-F-1/2
387296 | CR | 20181129 |  | 4 | Uncovered storm drains near sulfuric acid tank cleanout work |  |  |  | N | NO | <D> **** Detailed Description **** During a walk-down, E&RP identified four storm drain locations that are near the sulfuric acid totes (in the vicinity of the cooling towers) and are an environmental pathway should a sulfuric acid spill occur. GBP-ENV-18 section 4.1.13 requires that practical efforts are made utilizing storm drain covers to prevent spills to the environment. <I> **** Actions Taken **** Notified E&RP and Facilities management. Initiated CR. <N> **** Equipment Description **** Cooling towers / sulfuric acid tank vicinity. CR is for trending only; WR is not required--Facilities is covering the appropriate storm drains. 2 drains are covered already, and the other two are projected to be covered before noon on 12/03/18.
387298 | CR | 20181129 |  | 3 | TMU-FIS-5C IMDS needs to be updated. | N | N | N | N | NO | <D> TMU-FIS-5C was replaced Aug 28, 2018 And per the limits on use for CID 11377 A Doc update was created and attached to the installing WO 02131108 to revise the IMDS. . the IMDS is not yet updated. This system for managing changes in not effective. The current system does not make it easy to see that the IMDS has a pending change and in currently inaccurate. <I> Wrote CR to generate a trackable assignment to update IMDS. | 02-00-TMU-FIS-5C
387299 | CR | 20181129 |  | 3 | ESP Generic Training Examination Failures |  |  |  | N | NO | <D> **** Detailed Description **** Four Engineering Personnel did not acheive a passing grade on the examination administered following Generic Cycle Trianing on Instrumentation. Personnel Qualifications are not affected. This CR is being generated as required by TDI-02, Section 4.4.10.p.3). <I> **** Actions Taken **** Reviewed missed questions with individuals. Individual Supervisors were notified regarding the failures. Personnel will take a make up exam to receive credit for the course. following remediation.
387300 | CR | 20181129 |  | 4 | Potable water break at the north valve station. | N | N |  | N | YES | <D> **** Detailed Description **** At 1605 it was reported to the facilities call line that there appeared to be a potable water break at the north valve station located west of B-24 (Sewage treatment plant). Facilities investigated and found that the north valve station was full of water and the leak appaers to be a crack in a 4" coupler up stream of PWC-V519. Estimated leak at this point is 2 to 3 gal/min. <I> **** Actions Taken **** Notified Shift manager. Notified Site one manager that the Cross tie would need to be initiated to feed B-34 and B-35 Flushed Site One cross tie line for 45 min ending at 1915 <N> **** Equipment Description **** North valve station (potable water) | 02-00-PWC-V-519
387301 | CR | 20181130 |  | 3 | ALARA Remote Monitoring Room is Non-Functional |  |  |  | N | I DONT KNOW | <C> ANON CR Generated, moved to CR-SRO APPROVED status. OFM Re-assigned CR 387301 from ITMGMT to AR-RPST on 11.06.2018 <D> **** ANONYMOUS CR - Detailed Description **** The ALARA Remote Monitoring Room is non-functional in it's current state due to inadequate access to the LAN. There are three LAN outlets in the room. Two of the outlets have no live LAN plug-ins. The third outlet has only one live LAN plug-in, but it is currently being used for a Wireless Remote Monitoring (WRM) base station. The base station at the HP PAP will not reliably work, so it was moved to the Remote Monitoring Room. There are two computers in the Remote Monitoring Room, neither of which have LAN drops available to them. That makes access to ALARA Cast, Network Cameras, and the Network unavailable. The Remote Monitoring Room needs to be always available for use to support jobs, whether they are worked with the plant at power, or during a forced or planned outage. Currently, that is not the case. <I> **** Actions Taken **** After not seeing any action being taken after verbally bringing this up, this CR is being initiated. . Telecom would like to move the wall LAN jacks to better suit the current desk and equipment configuration. This work will be conducted under Change hear ticket IR-36078. <N> **** Equipment Description **** Remote Monitoring Room - GSB 441' . Telecom and RP walked the ALARA remote monitor room and verified AlaraCast is fully functional on both computers. The other equipment in the room was also verified to have good network connections. Because all the devices in the room have the required network connection, this ticket is being closed.
387303 | CR | 20181130 |  | 3 | ALARA Cast not displaying ARM's - Nightly Routine Incomplete | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Since the recent upgrade to ALARA Cast, the Telemetry Jobs were lost from the available folder and even though the electronic dosimeters were reportedly added to the recreated "ARM" Telemetry Job, they do not display. The large display monitor still had the ARM's being displayed because it had not been closed out since the upgrade. On all the other computers that were tried in the RP work area, no Electronic Dosimeters were displayed when the ARM Telemetry Job was opened. Tonight, the computer that controls the large monitor at the HP Lead Tech work station, was automatically restarted during a scheduled maintenance activity by Energy Northwest. Once that occured, ALARA Cast performed like it has been on all the other computers. No electronic dosimeters are displayed when the ARM folder is opened. Our nightly routine of recording these readings could not be accomplished. <I> **** Actions Taken **** Initiated this CR.
387315 | CR | 20181130 | CAQ | D | LPCS-P-2 abnormal cyclic noise | Y | N |  | N | YES | <D> **** Detailed Description **** LPCS-P-2 is making an abnormal resonating/cyclic noise. Pump discharge pressure was normal and steady at 130 PSIG. Pump and motor ambient temps were normal, to the touch. Oil level was normal. Reference WR# 29096036 for previous instance of what is seems to be the same issue. Reccomend vibration readings be taken. See EDMS for snap shot of WR 29096036. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RX 422 | 02-00-LPCS-P-2
387316 | CR | 20181130 | CAQ | C | Incorrect connection point for test equipment identified | Y | N |  | N | YES | <C> At the direction of MRT today, CR Severity moved from D/Trend Repair and assigned as a C to AR-ELECM group. <D> **** Detailed Description **** Incorrect connection point for test equipment identified when generating the Determ/Reterm Data Sheet resulting in clearing the control power fuse for RHR-MO-49 at E-MC -8BB7A. <I> **** Actions Taken **** Engineering Informed Component Manager Informed Additional Subject Matter Experts used to review steps taken Incorrect installation identified and corrected through W .R. 29145829 | 02-00-E-MC-8BB,02-00-RHR-MO-49
387317 | CR | 20181130 |  | 3 | Information lost when E537-1VB-2 was updated |  |  |  | N | NO | <D> **** Detailed Description **** On E537-1VB-2 has the power to TG-TR-144/MUX, MS-PR-1C, TG-E/S-1, TG-E/S-2, TG-XR-TSI, TRA-TR-24, TG-TR-144 and TG-TR-144/MUX1 are crosshatched out. A note says that these transitioned to EWD-46E-242A. These components are not shown on EWD-46E-242A. E555-E-CP-H13/P820 says that these components are powered from E-PP-7AZ circuit 3. EWD-46E-242 is the electrical distribution drawing for E -PP-7AZ. EWD-46E-242 does not show that any of these components are powered from E-PP-7AZ circuit 3. It looks like when these components were no longer included in E537-1VB-2 that this information was lost.
387318 | CR | 20181130 | CAQ | C | Acceptance criteria not updated prior to implementation |  |  |  | N | NO | <D> **** Detailed Description **** WO 02093558 â€œRHR-MO-49 - REPLACE MOTOR OPERATOR AND PINION GEARâ€ implemented AR 321015 â€œIssue RIE for RHR-MO-49 Gear Ratio Changeâ€. This changed the stroke time of RHR-MO-49. However, the surveillance used for the PMT (OSP-RHR/IST -Q703) was not updated prior to this change. As written, the valve would have been required to be declared inoperable with the new stroke times. The SRO reviewing the surveillance had to review the AR to determine the proper stroke time in order to call the PMT sat. The surveillance should have been changed, or other guidance provided, prior to requiring the on-shift SRO to determine the proper acceptance criteria. <I> **** Actions Taken **** Validated proper stroke times via AR. Peer check from SM. <N> Changed to CAQ/C from Non-CAQ as allowed by SWP-CAP-01 as a result of Quality feedback. The surveillance testing acceptance criteria was not aligned with plant configuration and should have been considered a condition adverse to quality. | 02-00-RHR-MO-49
387319 | CR | 20181130 |  | 3 | EWD-51E-039 references the wrong component |  |  |  | N | NO | <D> **** Detailed Description **** On EWD-51E-039 for ITEM 97 it says Turbine Generator Exciter. Per 01-00,81 ITEM 97 is on the Main Generator not the Exciter. The components terminated on ITEM 97 are the hydrogen cooler RTD's . The hydrogen coolers are on the main generator.
387320 | CR | 20181130 |  | 4 | Oil Leak from RRC-TR-ASD/A/1 Tap Changer | N | N |  | N | YES | <D> **** Detailed Description **** There is an oil leak coming from around the tap changer which requires a transformer outage to replace the gasket. See EDMS for photos. This oil leak was reported on 3-17 -2015 via WR 29119411, the oil leak was incorrectly determined to be from past work and the WR was closed with no maintenance performed. This same issue was reported in 12-20-2009 and the gasket replaced by WR 29079470 and WO 01183663. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** ASD Transformer | 02-00-RRC-TR-ASD/A/1
387321 | CR | 20181130 |  | 4 | Oil Damage possible cause of RRC-TR-ASD/A/1 alarms | N | N |  | N | YES | <D> **** Detailed Description **** See WR 29144953 and 29145725 for previous alarms. The local oil temperature indicator (RRC-TI-OT/ASD/A/1) and the Winding temperature indicator (RRC-TI-WT/ASD/A/1) have for years been subject to oil from a leak above WR 29145844. The seal around the Temperature indicator has been warped and damaged by constant oil saturation. Along with the temperature indicators the sensing lines have also been constantly oil saturated. See EDMS for Photos. An engineering evaluation is needed to determine if the temperature indicators and sensing lines have been damaged by the oil. The sensing lines should also be tested/replaced to ensure the oil saturation hasnâ€™t degraded insulation resulting in spurious shorts. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** ASD Transformer . | 02-00-RRC-TR-ASD/A/1
387322 | CR | 20181130 | CAQ | D | SEVERLY DAMAGED INSULATION- OG-V-125B | N | N |  | N | YES | <D> **** Detailed Description **** DURING WORK ACTIVITIES IN THE AREA IT WAS IDENTIFIED THAT INSULATION ON OG-V-125B (SJAE RM B) NEEDS TO BE REPLACED. SEE EDMS FOR PICTURES <I> **** Actions Taken **** NOTIFIED SUPERVISION, INITIATED CR, WORK REQUEST <N> **** Equipment Description **** SJAE B RM | 02-00-OG-V-125B
387323 | CR | 20181130 |  | 4 | SEVERLY DAMAGED INSULATION- MS-V-110B | N | N |  | N | YES | <D> **** Detailed Description **** DURING WORK ACTIVITIES IN THE AREA IT WAS IDENTIFIED THAT INSULATION ON MS-V-110B (SJAE RM B) NEEDS TO BE REPLACED. SEE EDMS FOR PICTURES <I> **** Actions Taken **** NOTIFIED SUPERVISION, INITIATED CR, WORK REQUEST <N> **** Equipment Description **** SJAE B RM TG 441 | 02-00-MS-V-110B
387324 | CR | 20181130 |  | 4 | RCC-P-1B outboard bearing hot to the touch | N | N |  | N | YES | <D> **** Detailed Description **** RCC-P-1B outboard bearing is hot to the touch. RCC-P-1B was placed in service on 11-27-18 to support online lubrication, prior to upcoming maintenance (Ref. WO 02131312). The lubrication task fro WO 02131312 is at finished status. It may be that the outboard bearing has been overgreased. The outboard bearing of RCC-P-1B was 148F, with a infrared thermometer. The inboard bearing of RCC-P-1B and the inboard and outboard bearing of RCC-P -1A were all 90 to 95F. <I> **** Actions Taken **** Informed MCR. MCR has secured RCC-P-1B due to hot bearing and to support the upcoming maintenance/confidence run. <N> **** Equipment Description **** RX 548 | 02-00-RCC-P-1B
387325 | CR | 20181130 |  | 4 | COND-V-231A operational issue | N | N |  | N | YES | <D> **** Detailed Description **** On 11/30/2018, during a relax of COND-DM-1E, it was noted that the controller for COND-DM-1A was not controlling as usual. The manual controller is placed at 95%, and the flow through COND-DM-1A was not as high as it should be. Inspection of COND-V-231A showed the valve was approximately half open. Excessive air noise seems to be coming from the black diaphram and the engineered ports on that diaphram. This will negatively impact all other 5 COND-DM's and reduce their life, requiring backwash and precoats earlier than necessary. COND-V-231A valve operator should be investigated as soon as possible. <I> **** Actions Taken **** Initiated CR. Informed MCR. | 02-00-COND-V-231A
387326 | CR | 20181130 |  | 3 | RCC-P-1B outboard bearing is hot to the touch | N | N |  | N | YES | <C> CR Trended to CR 387324 At the direction of MRT today, CR Severity moved from 4//Trend and assigned as a 3 to AR-SENSSS group. <D> **** Detailed Description **** RCC-P-1B Outboard bearing is considerably hot to the touch, especially in comparision to its inboard bearing and the bearings of RCC-P-1A. RCC-P-1B was started on 11-27-18 to support online lubrication for WO 02131312. The lubrication task is at FINISHED status. It seems likely that the outboard bearing has been overgreased. Temperature of the Outboard bearing was 148F, via Infrared Thermometer. RCC-P-1B Inboard bearing temp was 95F. RCC -P-1A Inboard and outboard bearing temps were 91 and 89F. MCR has secured RCC-P-1B due to the outboard bearing temp and to support the upcoming work associated with WO 02131312. See EDMS for snap shot of WO 02131312 status, as of 11-30. <I> **** Actions Taken **** Informed MCR. MCR secured RCC-P-1B <N> **** Equipment Description **** Rx 548 | 02-00-RCC-P-1B
387327 | CR | 20181130 |  | 4 | CW-B Supervisory fault causes manual operation | N | N |  | N | YES | <D> **** Detailed Description **** Several CW Pumphouse parameters were noted to be cycling (listed below) indicating a fault with Supervisory. Manual level control of CW Basin level was established and CW blowdown was secured. Basin CW-C level (TMU-LI-2A) was observed to cycle rapidly (every 2 seconds) from pegged low to the normal reading of 444â€™. The CW basin controller (TMU-LIC-2A) was observed to be rapidly cycling the makeup valve (TMU-LCV-2A) from its normal 30% output to 80% in response to the TMU-LI-2A changes. TMU flow was changing in response to this as well. CW pH indication on F141 was rapidly cycling from 0.1 to 8.4 pH, causing CBD-LCV-1 (the blowdown valve) to cycle rapidly. Manual control of basin level was established and CW blowdown was secured. All four of the Supervisory MUXâ€™s in CW-B cabinet in the MCR were all in alarm and faulted. The MUXâ€™s were reset per the ARP, but within five minutes several of the faults had recurred. Request Maintenance trouble shoot and repair CW supervisory. | 02-00-SCI-MUX-OCWB/1
387328 | CR | 20181130 |  | 4 | TMU-P-1C has packing leak. | N | N |  | N | YES | <D> **** Detailed Description **** When TMU-P-1C was started as part of WR 29145836 investigation the pedestal quickly filled up with water. Further investigation revealed significant packing leakage coming from the shaft seal. The pedestal was found to be plugged, but was eventually cleared and the pedestal drain down. However, after the pump was secured lube water flow never stop and the pump packing leakage decreased significantly but was still greater than the packing leakage of the operating pumps. See EDMS for pictures and video and also AR/CR 387329. <I> **** Actions Taken **** Informed supervision and wrote this AR/WR. <N> **** Equipment Description **** TMU Pumphouse. | 02-00-TMU-P-1C
387329 | CR | 20181130 |  | 4 | TMU-V-18C Solenoid/Control Issue | N | N |  | N | YES | <D> **** Detailed Description **** After opening TMU-V-32C per D-TMU-FIS-5C -002 following WR 29145836 indicated lube water flow was ~7gpm after mechanical agitation the flow reduced to ~3gpm. After the MCR returned TMU-RMS-P1C/7 from PTL to Normal after Stop the MCR received a low lube water flow alarm that cleared shortly after and flow increased to ~7gpm. After starting TMU-P-1C flow dropped to about ~3gpm; 10 minutes later the solenoid was still warm. After the pump was shut down the solenoid remained warm and flow was ~7gpm with the switch for TMU-V-18C in Auto. The MCR took the TMU-V-18C control switch to close and flow reduced to ~4gpm. When TMU-V-18C switch was returned to Auto flow increased to ~7gpm but the solenoid for TMU-V-18C did start to cool down. There seems to be some electrical issue with the alarm, the solenoid remaining energized beyond the 30 second time delay after pump start, and the solenoid valve leaking by. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TMU Pumphouse | 02-00-TMU-V-18C
387330 | CR | 20181130 | CAQ | D | CRD 02-43 high moisture. | Y | N |  | N | YES | <D> **** Detailed Description **** At 2257 on 11-30-2018, crd 02-43 alarmed in the MCR. Upon further investigation, Ops 2 found crd 02-43 to have a high moisture condition. <I> **** Actions Taken **** Moisture drained per SOP-CRD-HCU. | 02-00-CRD-HCU-0243
387331 | CR | 20181201 |  | 4 | Stationary Equipment Source Check Failure |  |  |  | N | NO | <D> **** Detailed Description **** Whole Body Counter failed QA source checks portion of the shiftly source check. <I> **** Actions Taken **** Contacted Rad Support personnel for assistance in adjusting WBC. WBC declared OOS. HP Lead, ROS, and RPM informed. <N> **** Equipment Description **** Fastscan # 0061364
387332 | CR | 20181201 |  | 4 | Untreated wood in turbine building for extended duration |  |  |  | N | NO | <D> **** Detailed Description **** 460 lbs of untreated wood in the form of a cable spool were brought into the turbine building on 11/28/2018. TCP 18 -0178 was opened and then extended on 12/30/2018. The duration limit for this much untreated wood in the plant in modes 1,2,3 is 24 hours per PPM 1.3.10C and the material is to be removed when practical. If the job is not worked on through the weekend, then the wood will sit in the turbine building for several more days before it is removed, forcing Operations to extend the TCP several more times. This constitutes a poor risk mitigation strategy. <I> **** Actions Taken **** Informed the Shift Manager and Work Week manager to expedite removal of the wood. Sent communication to WWM to remove material . <N> Process was followed for 24 hour extensions, Fire Marshall and SM have come to agreement that this can be extended to 12/21/2018. | 02-00-T-BLDG-MISC
387368 | CR | 20181201 |  | 4 | Braided steel rigging cable with out-of-date inspection ring |  |  |  | N | YES | <D> **** Detailed Description **** A braided steel rigging cable is located on the west side of Turbine Building 441â€™ with an out-of-date inspection ring. The cable is currently on the floor next to the large lift. The cable has a brown inspection color code indicating it was inspected in a year that ends in 7. Cable needs to be inspected before use. <I> **** Actions Taken **** Notified CRS <N> **** Equipment Description **** T441' west side near large lift
387369 | CR | 20181201 |  | 4 | THST BRG CNTR 2 FAIL alarm on DEH | N | N |  | N | YES | <D> **** Detailed Description **** THST BRG CNTR 2 FAIL alarm on DEH has returned. This was previously documented by WR 29123869, which has been actioned to WO 02083505, which is at PLAN. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-DEH-MON-2
387370 | CR | 20181201 | CAQ | D | Rod accumulator trouble alarm on CRD-HCU-3839 | Y | N |  | N | YES | <D> **** Detailed Description **** Rod accumulator trouble alarm on CRD-HCU-3839, due to low nitrogen pressure. Previously cocumented by CR 382450, WR 29143659. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. . Per the control room log, CRD-HCU-3839 required an accumulator recharge on 11/3/18, 11/8/18, 11/14/18, 11/20/18, 11/25/18 and today. | 02-00-CRD-HCU-3839
387371 | CR | 20181201 | CAQ | D | Nitrogen makeup pressure to the Wetwell is low. | Y | Y |  | N | YES | <D> **** Detailed Description **** Nitrogen makeup pressure to the Wetwell is low. SOP-CN-OPS Step 5.1.2.b [first bullet] has an Operator verify flow by ensuring CN-PI-13 denotes between 5 to 50 psig. The current pressure is 4 psig. The second bullet allows for verification of flow by monitoring CN-FQ-2 operation. This has been performed to satisfy the requirement. CN-PI-13 may be reading low. <I> **** Actions Taken **** Checked CN-FQ-2 operation. Please evaluate the calibration of CN-PI-13. | 02-00-CN-PCV-5,02-00-CN-PI-13
387372 | CR | 20181201 |  | 4 | The RHR A Floor Plug improperly stored on RCIC Floor Plug. | Y | Y |  | N | YES | <D> **** Detailed Description **** The RHR A Floor Plug improperly stored on RCIC Floor Plug. Sign on the plug states Do Not Stack Floor Plugs. Reference PPM 10.4.14, Miscellaneous Load Handling. PPM 10.4.14 Att. 9.6, Floor Plug Stacking illustrates an Unacceptable Configuration identical to the current method of stacked Floor Plugs. See attached photos. <I> **** Actions Taken **** Notified the SM and CRS. Please restack the RHR A Floor Plug per PPM 10.4.14. Reference WO 02033672-08. <N> **** Equipment Description **** RHR A Floor Plug 471' Reactor Building . Issue was discussed with Mechanical Component Manager and Site Rigging Coordinator. It was determined that the floor plug in question was placed in accordance with the procedure and procedure is in alignment with best practices in rigging. Setting a floor plug on an installed floor plug is an acceptable practice. | 02-00-R-BLDG-MISC
387373 | CR | 20181201 |  | 3 | 216-05,40,10 does not match the plant. |  |  |  | N | NO | <D> **** Detailed Description **** 216-05,40,10 does not match the plant. 216-05,40,10 shows the plant air supply to the TOA manifold coming in at the S1 valve. In the plant the plant air supply comes in at the S15 side of the manifold. 216-05,40,10 shows S1 as the first valve on one side of the manifold. In the plant there is a spare valve before S1. 216-05,40,10 shows 15 supply valves. In the plant there are 18 supply valves. There are other discrepancies. In addition, none of the valves are labeled. In addition, it is difficult to follow the air tubing inside E-CP-TGHV/1 because there are many air lines. This is an error likely situation. 216-05,40,10 needs to be updated and the air valves inside E-CP-TGHV/1 need to be labeled.
387374 | CR | 20181201 |  | 3 | LPCS-P-2 needs vibration monitoring points | Y | N |  | N | YES | <D> **** Detailed Description **** LPCS-P-2 is missing the metal discs necessary for accurate and consistent vibration monitoring. These discs have been installed on all the points on the pump side but the motor is missing them. 5 points total will need to be installed. This does not affect the operation of the pump. <I> **** Actions Taken **** Sent email to system engineer for point location identification. <N> **** Equipment Description **** R-422 NE room | 02-00-LPCS-M-P/2,02-00-LPCS-P-2
387375 | CR | 20181201 |  | 3 | Four Temporary Covers in place GT 90 days. |  |  |  | N | YES | <D> **** Detailed Description **** Four Temporary Covers have been in place GT 90 days. An audit of Temporary Covers per PPM 1.3.81, Maintaining Plant Component Status Control was performed. Reference WO 02083987. During the audit, it was identified that four Temp. Covers have been in place for GT 90 days. Step 6.4.7 states, â€œAtt. 9.5, Temporary Cover Control Log should be reviewed by Operations periodically for the purpose of determining if any temporary covers in place for GT 90 days are still required and whether they should be converted to permanent covers per Att. 9.6, Installation of Permanent Bump Protection.â€ The covers are on the four 24V battery chargers float/equalize switches. The covers were placed on 15 JUN 18. <I> **** Actions Taken **** Please perform the PPM 1.3.81 Att. 9.6 assessment to determine if these four temporary switch covers should be converted to permanent bump protection acrylic covers. This requires AR EVAL per DES-2-9, SRO, Plant Support Engineering, Design Engineering and Classical Fire Protection SME assistance. . Submitted AR EVAL 387376 <N> **** Equipment Description **** Covers on four 24V battery chargers float/equal switches. EPNs?
387377 | CR | 20181201 |  | 3 | Confusion on ISPM-2 temp bottle storage needs clarification |  |  |  | N | NO | <D> **** Detailed Description **** ISPM-2 step 3.2.1.a starts out with describing that when using gas bottles they need to be secured to a structural steel and ends with saying that they can be stored temporarily in carts that are designed for storage or transport. in addition since the bottles in question are in the reactor building they are also subject to PPM 10.2.222. in the attached photos this is what I have witnessed 4 times today twice in the reactor building and twice in the RW building. So I am not sure that the storage transport carts we use here are the ones that we are adressing in the ISPM. Neither carts was marked per PPM 10.2.222. Please see attached word document and pictures for clarification. Please come to a resolution and get the word out on the right way so we all know. <I> **** Actions Taken **** discussed with supervision who were also surprised with the wording and the carts and recommended writing this cr.
387378 | CR | 20181201 |  | 4 | TO-TK-2 Low Level | N | N |  | N | YES | <D> **** Detailed Description **** TO-TK-2 has fallen below the minimum spec of 0". Please add oil. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 441 E | 02-00-TO-TK-2
387379 | CR | 20181201 |  | 4 | TEMPORARY MAN LIFT STUCK IN UPPER POSITION - WILL NOT LOWER |  |  |  | N | NO | <D> **** Detailed Description **** UNITED RENTALS SIZZOR LIFT MODEL GS-5390 (SER. No. 10178287) IS STUCK IN IT EXTENDED UPPER POSITION. SITE SUPPORT CONTRACTOR WAS SUPPORTING THE CRANE MODIFICATION ON THE TURBINE CRANE MT-CRA-1 AND FINISHED PERFORMING THIER WORK WHEN THE LIFT FAILED TO LOWER. OUR SECOND HOIST WAS USED TO LOWER THE CRAFT TO THE 501 ELEVATION. THE STUCK MAN BASKET ELEVATION IS LOCATED AT THE CRANE BRIDGE- THE CRANE IS TAGGED OUT OF SERVICE FOR THE REPAIR WORK UNDER WORK ORDER 02114492. THE LIFT IS STABLE. <I> **** Actions Taken **** OUR SECOND HOIST WAS USED TO LOWER THE CRAFT TO THE 501 ELEVATION. CONTROLS AT THE BASE OF THE LIFT WERE ALSO TRIED WITH NO SUCCESS. NOTIFIED CONTROL ROOM OF PROBLEM. ALSO CONTACTED LOCAL SERVICE REP AND HE WILL BE ON SITE THIS EVENING TO TROUBLE SHOOT THE LIFT. AREA HAS BEEN DANGER TAGED. ALSO CONTACTED THE PROJECT MANAGER. Lift has been restored to the lowered position. <N> **** Equipment Description **** LIFT IS A RENTAL PIECE OF EQUIPMENT BUT IS LOCATED NENT TO THE MT-CRA-1 BRIDGE | 02-00-T-BLDG-MISC
387380 | CR | 20181201 |  | 4 | HT-HTP-FP/6/1 50F Low Temp light flashing | N | N |  | N | YES | <D> **** Detailed Description **** HT-HTP-FP/6/1 50F Low Temp light is flashing. Power On light and Continuity light are both lit. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-HT-HTP-FP/6/1
387381 | CR | 20181201 |  | 4 | SSW B Pumphouse Light Flickering | N | N |  | N | YES | <D> **** Detailed Description **** The light just inside the door of the SSW B Pumphouse is flickering on and off. <I> **** Actions Taken **** Wrote CR. Non-essential lighting <N> **** Equipment Description **** SSW B Pumphouse Lighting | 02-00-B-BLDG-MISC
387402 | CR | 20181202 |  | 4 | Leak Det Turb Bldg Temp Hi-Hi, H13-P601.A3, 3-5 alarm. | N | N |  | N | YES | <D> **** Detailed Description **** Leak Detection Turbine Building Temperature Hi-Hi, H13 -P601.A3, 3-5, alarm. . LD-MON-1A A4-4 for LD-TE-52A denotes 189Â°F. This is for MSL A Turbine Building Ambient. LD-TRS-608 pt. 23 remains in alarm and denotes 191Â°F. CRO 1 continues with their Temporary Log. TOA-FN-1A remains INOP. Reference CR 387030. <I> **** Actions Taken **** Notified the CRS and SM. | 02-00-LD-MON-1A,02-00-LD-TE-52A,02-00-LD-TRS-608
387410 | CR | 20181203 |  | 4 | GSB 441 lunch room ice maker OOS |  |  |  | N | YES | <D> **** Detailed Description **** The ice maker in the GSB lunch room is not producing any ice. <I> **** Actions Taken **** Wrote CR <N> **** Equipment Description **** 441 GSB lunch room | 02-00-GSB-BLDG-MISC
387412 | CR | 20181203 | CAQ | D | SW-V-678 might be plugged (affects SW-FE-17A2 work) | Y | N |  | N | YES | <D> **** Detailed Description **** When hanging D-SW-FE-17A2-001 for WO 02077569, isolation valves SW-V-22A and SW-V-23A were closed, and then SW-V-678 was opened to verify boundary integrity. SW-P-1A is running. When SW-V-678 was opened, about 2 or 3 ounces of water came out, and then drainage stopped. This could be an indication that SW-V-678 is plugged. Recommend trying to clear the drain line to ensure adequate isolation. SW-V-678 is OPEN per D-SW-FE-17A2-001, but has a NO-TAG applied because it could be removed during work. <I> **** Actions Taken **** Informed SM/ CRS, wrote this CR and WR. . Mechanics rodded out SW-V-678 and didn't get any more water. Appears the isolation valves are tight. Not a DNC. | 02-00-SW-V-678
387422 | CR | 20181203 |  | 4 | CM 7/ 11 Calibration expired |  |  |  | N | YES | <D> **** Detailed Description **** The Calibration on HP-EQ-53252 located on the 501' Main Control Room has expired. <I> **** Actions Taken **** Placed a radiological instrument repair tag on it informed HP Supervision and intiated a CR. And a wrote a work request. <N> **** Equipment Description **** 501' Main Control Room | 02-00-HP-EQ-53252
387423 | CR | 20181203 |  | 4 | Security rental light plant failed to start |  |  |  | N | NO | <D> **** Detailed Description **** Security rental light plant failed to start after several attempts. Contacted vendor for repairs. Light plant ID # 991237. <I> **** Actions Taken **** Coordinating with rental agency for repairs or replacement. CR generated for trending.
387427 | CR | 20181203 | CAQ | C | SW-FE-8A orifice flanges are different than in AED SPC 1 | Y | N |  | N | YES | <D> **** Detailed Description **** SW-FE-8A orifice flanges are a different type as call out in AED SPC 1 (ASME Piping Systems). AED SPC 1 calls for a 150 lb. flange while SW-FE-8A is a 300 lb. flange type. CVI ISO 215-00,2884 calls out that the flange is a 300 lb. class. In addition, AED CAL 8.42.0026 evaluated a 300 lb. flange for SW-FE-8A for the piping stress analysis calculation. The 300 lb. flanges installed for SW-FE-8A are conservative as compare to the 150 lb. class flanges called out in AED SPC 1. Recommend that AED SPC 1 be updated to indicate acceptability of the existing installed/evaluated higher (300 lb. vs. 150 lb.) class flanges in this location and suggest resolution to Design Engineering Mechanical Design Basis group. <I> **** Actions Taken **** Dissucessed issue with Shift Manager and Deisng Engineering Supervisors. | 02-00-SW-FE-8A
387428 | CR | 20181203 | CAQ | B | 2018 Annual and Biennial Exam Failure Rates Exceed 20% | N | N |  | N | NO | <C> Removed NRC Name referenced in CR Immediate Action Notes. RISK: Medium. CAUSE: Uncertain and complex. Investigation Template Required. <D> **** Detailed Description **** 51 individuals participated in the 2018 annual operating and bienniel written exams. 2 out of 8 crews failed the 2018 annual operating exam scenarios (10 individual failures). 4 individuals failed the 2018 biennial written exam (one also failed a scenario). No individuals failed the 2018 annual exam JPMs. NRC Inspection Procedure 71111.11 describes how exam results are evaluated in table 03.02-01. The individual failure rate was 25% (13 individuals failed divided by 51). The crew simulator failure rate was 25% (2 crews divided by 8). These failure rates exceed the threshold of 20% for potential NRC enforcement as described in IP 71111.11 03.02.d. There is a total of 52 licenses at Columiba. One individual did not take any portion of the exam for medical reasons. This CR is to document the failure rates from the exam as a whole and is not meant to track individual failures and actions from those failures. <I> **** Actions Taken **** The NRC (.........) has been notified of the failure rates exceeding 20%. . REGE/REP assignments are made when there is evidence that an impacted SSC was or may have been inoperable in the past three years. This CR does not involve any SSC's, however, request Licensing evaluate this CR for reportability or potential violation - see 10 CFR 55.59. <R> This condition has resulted in a self-revealing Green finding for exceeding the 20% exam failure rate identified in Inspection Procedure 71111.11. This performance deficiency challenges the expected knowledge and abilities of licensed operators as demonstrated during the requalification exams required by 10 CFR 55.59(a)(2). This finding has been assigned a cross-cutting aspect of H.1, Resources. In accordance with GBP-LIC-08, the evaluation for this CR should address the performance deficiency identified, and any organizational or programmatic gaps that led to the finding. A REGA assignment has been created for Regulatory Affairs to perform a gap assessment when the finding is documented in the inspection report.
387429 | CR | 20181203 | CAQ | C | Breaker lineup procedure needed on E-TR-M1/2/3/4 N1/2 |  |  |  | N | NO | <D> **** Detailed Description **** Currently no procedure exists to perform a breaker lineup on the main and normal transformers. SOP-ELEC-500KV/TRANS -LU only performs lineup on valves and control switches. PPM 10.25.209 step 7.5.9i and Attachment 9.1 reference generic EPNs. Request circuit breakers be added to lineup procedure or added to ac lineup procedure.
387431 | CR | 20181203 |  | 4 | D-DOOR-D301 | N | N |  | N | YES | <D> **** Detailed Description **** Door D301 needs maintenance. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** security notification made, WR generated | 02-00-D-DOOR-D301
387435 | CR | 20181203 | CAQ | C | Part 21, EDG Fuel Cover Bolt | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02119140-01/02. marked completion required box, then taken back to complete <D> **** Detailed Description **** The part 21 was reviewed and found to be applicable to CGS. DG1 fuel pumps replaced in 2015, DG2 replaced in 2018. DG3 replaced many years ago and is not succeptible. The inventory in the warehouse is also covered by this part 21. A WR has been generated to perform a torque check on DG1 and DG2. At this time there is reasonable assurance that the fuel cover bolts are functioning as designed. The engines have passed all monthly survailences and the engines are monitored daily by operations for leaks. System engineer recommends performing torque check prior to the next monthly survailanece run. This will be a one time check to validate that the proper torque has been applied. <I> **** Actions Taken **** Contacted SM and reviewed Part 21 | 02-00-DG-ENG-1A1,02-00-DG-ENG-1A2,02-00-DG-ENG-1B1,02-00-DG-ENG-1B2,02-00-DG-ENG-1C,02-00-DO-P-4A1,02-00-DO-P-4A2,02-00-DO-P-4B1,02-00-DO-P-4B2
387436 | CR | 20181203 |  | 3 | Assignments not created for procedure changes tied to ECs |  |  |  | N | NO | <D> **** Detailed Description **** While preparing the outage procedure milestone list and verifiying the contents it was found that five ECs did not have assignments to track procedure revisions for the procedures identified that require changes based on the EC. The following ECs do not have assignments cross-referenced EC 16355, 17061, 17107, 17111. 17112. These assignments are used to track procedure revisions on the outage procedure milestone list. Recommend assignment to AR-CEI <I> **** Actions Taken **** Provided question to engineering and received followup that process was not followed. This is an administrative issue only.
387438 | CR | 20181203 |  | 4 | chem lab hood lower storage is getting rusty. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** while checking Cal. gas supply bottles it was noticed the storage area below the hood is getting rusty. it ts rusting the high pressure calibration bottles as well. <I> **** Actions Taken **** made a suggestion to supervisor about the posibility of getting it treated with rust converter before it gets worse. May save the cost of a hood replacment. <N> **** Equipment Description **** Chem lab
387439 | CR | 20181203 | CAQ | D | Document Contol received a procedure without AD. | N | N | N | N | NO | <D> A Major Revision procedure was reviewed, approved and submitted to Document Control for issuance without the Applicability Determination. (AD) <I> The procedure was returned to the originator via the APPW system
387440 | CR | 20181203 |  | 4 | Over on November Monthly Dose Goal |  |  |  | N | NO | <D> **** Detailed Description **** Williams Plant Services went over the Departments November monthly dose goal of 671 MR by 300 MR. The final dose received for the month was 971 MR. This was mainly due to our Craft receiving dose associated to the MT-CRA-1 repair support. We have accumulated 319 MR on this support to date; most of this dose was received the week of 11/26/18. Work order 02114492. Another task that was transferred over to us from Maintenance was PWR-CRA-1 scaffold installation. We received 139 MR on the installation of this scaffold, work order 021228959. An emergent ALARA task was added into the month for insulation removal on HT- HTP-FP/5 CKT 22F. We received 1 MR of an estimate of 7 MR. Work order 02092519. <I> **** Actions Taken **** Contacted Management.
387442 | CR | 20181203 | CAQ | D | Rod accumulator trouble alarm on CRD-HCU-4259. | Y | N |  | N | YES | <D> **** Detailed Description **** Rod accumulator trouble alarm on CRD-HCU-4259 due to moisture. Drained water per SOP and the alarm is clear. <I> **** Actions Taken **** Initiated CR per Night Order | 02-00-CRD-HCU-4259
387444 | CR | 20181203 |  | 4 | Late eSOMS entries for Maintenance - Week of 11/17/18 |  |  |  | N | NO | <D> **** Detailed Description **** 2 I&C supervisors changed their eSOMS end times after they had already worked the hours being entered. 1 Electrician came in 1.25 hours earlier than was communicated to the Maintenance scheduler. 1 Electrician showed up for work on a day he had PT scheduled. No violations occured when eSOMS was updated. <I> **** Actions Taken **** Updated eSOMS with correct hours
387445 | CR | 20181203 |  | 4 | Late eSOMS Entries for Maintenance - Week of 11/24/18 |  |  |  | N | NO | <D> **** Detailed Description **** 1 Electrician, 1 I&C Supervisor, and 1 Night supervisor worked full days on days they were scheduled to be off. There were 6 instances of supervisors changing their time after working the hours they were changing. (5 were I&C & 1 was Mechanical). There was 1 instance of a mechanical supervisor changing the time code in eSOMS after having worked 10.5 hours, which changed his start time after the fact. No violations occured when eSOMS was updated. <I> **** Actions Taken **** Correct hours were entered in eSOMS <N> modified description to denote night supervisor at request of CR originator - JLK
387446 | CR | 20181203 | CAQ | C | Bent tubing between SW-V-771B and SW-FI-17A2 | Y | N |  | N | YES | <D> While preparing to remove RHR-P-2A, a Mechanic noticed the stainless steel tubing between SW-V-771B and SW-FI-17A2 is severely bent. See attached photos in EDMS. <I> Mechanic notified supervisor <N> R 426 K1/8.4 R 426 K1/8.4 . Discussed path forward with OCC Engineering rep. Tubing will be replaced at a later date via the attached WR/WO. No further action needed on this CR. | 02-00-SW-FI-17A2,02-00-SW-V-771B
387447 | CR | 20181203 |  | 4 | Conceptual Design from AE rejected due to quality |  |  |  | N | NO | <D> **** Detailed Description **** The conceptual 30% design for EC 17317 submitted by the AE for EN review was rejected by the Technical Representative due to the amount of open issues and overall design quality of the product being less than expected. Discussed with the AE the concerns and rejection of the EC. The AE will reschedule the submittal of the design product for EN review. <I> **** Actions Taken **** Contacted the Project Manager, discussed with Design Engineering Manager, met with the AE and discussed issues. Initiated CR. Recommend close to track and trending.
387448 | CR | 20181203 |  | 3 | Missing SQA documention for AQ EPNs | N | N |  | N | YES | <D> **** Detailed Description **** The EPNs listed as affected equipment do not have SQA documentation required by DES-6-3. The equipment is listed is as AQ but does not have equipment listed in the relationships panel. The EPNs should have SQA documentation generated, or be evaluated for declassification. <I> **** Actions Taken **** Contacted the Software Owners, contacted IS for verification that the software exists. Initiated CR. | 02-00-NET3-SOFT-OWL/1/MBTS,02-00-NET3-SOFT-OWL/1/OPDS,02-00-NET3-SOFT-OWL/1/RFTS,02-00-NET4-SOFT-OWL/1/MBTS,02-00-NET4-SOFT-OWL/1/OPDS,02-00-NET4-SOFT-OWL/1/RFTS
387449 | CR | 20181203 | CAQ | D | Malfuction SEC-IDS-20 21 | N | N |  | N | YES | <D> **** Detailed Description **** CAS received a malfuction alarm on IDS 20 21. <I> **** Actions Taken **** Compensatory measures were posted. A walk down of the area was conducted and nothing was found that could be causing the zone to alarm. Electical Maintenance was notified. Shift Manager was notified. CR/WR generated. This is not reportable. | 02-00-SEC-IDS-E/S/20/21
387450 | CR | 20181203 |  | 3 | Revise ABN-SGT-TEMP/RAD |  |  |  | N | NO | <D> **** Detailed Description **** The second bullet for entry condition 1.2 needs to be changed from â€œH13-P602.A5-3.5, REACTOR BLDG STACK RAD HIGHâ€ to â€œH13-P602.A5-3.8, REACTOR BLDG STACK RAD ALERT.â€ This changed per EC-11288.
387451 | CR | 20181204 | CAQ | D | Rod Accumulator Trouble Alarm CRD-HCU-3027 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-3027. Alarm is due to high water level. <I> **** Actions Taken **** Drained water, the alarm is clear | 02-00-CRD-HCU-3027
387452 | CR | 20181204 | CAQ | C | Broken set screw on RHR-MO-48A | Y | N |  | N | YES | <D> **** Detailed Description **** During the Mag rotor inspection on RHR-MO-48A it was discovered that the set screw theat held the motor pinion gear tight was broken into two pieces. <I> **** Actions Taken **** Informed OCC, added step to the work order to remove the screw and replace it. Recommend closing to trend. <N> Set screw will be replaced under WO 02113021-01. | 02-00-RHR-MO-48A
387461 | CR | 20181204 |  | 3 | RHR-P-2A Work RWP Requires Revision due to CAM Availability |  |  |  | N | NO | <D> **** Detailed Description **** While preparing for work on RHR-P-2A, it was discovered that no continuous air monitors were available to install in the pump room as specified in the RWP. This required a revision of the RWP, which has been completed. This is being generated to capture as a potential lesson learned. <I> **** Actions Taken **** The team searched the unit for any potential CAMs that could satisfy the requirement. Upon finding none, they stopped and engaged supervision on a path forward. The review determined that the CAM requirement may have been additional based on the plan to use both HEPA ventilation and a gooseneck grab sampler to clean and monitor the airborne conditions. It was determined that the CAM requirement could be removed out of the RWP with a minimal impact to risk. This was discussed with the OCC for concurrence prior to implementation. | 02-00-R-BLDG-MISC,02-00-RHR-P-2A
387462 | CR | 20181204 | CAQ | C | RHR-HX-2A As-found inspection results | Y | N |  | N | YES | <D> **** Detailed Description **** The SSW side of RHR-HX-2A 'RHR-P-2A SEAL INJECTION WATER COOLER' was inspected under WO 02077068 with the following as-found results: Thick dark brown/black slime/silt coating the cooling coil and the shell internals. Multiple tubercles on the carbon steel shell Multiple areas of carbon steel shell showing signs of pitting No immediate signs of damage to the stainless steel coil Recommendations: Take a sample of the silt/slime mixture to be analyzed by Chemistry / Heat Exchanger program owner Perform cleaning as outlined in WO 02077068-01 Engineering inspect cleaned heat exchanger and measure pit depth to ensure heat exchanger shell integrity WO 02077068. Evaluate the need to increase the frequency of the heat exchanger cleaning/inspection Evaluate the need to coat the carbon steel shell to prevent corrosion. <I> **** Actions Taken **** notified EOC/OCC of inspection results <N> Heat Exchanger RHR-HX-2A was cleaned by WO 02077068 to remove the silt/slime from the coil and shell. The as-left condition post cleaning was SAT. The pitting was measured and identified to be greater than minimum wall (CRs 387484, 387539). The areas of low wall thickness were weld repaired by WO 02077068-09. RHR-HX-2A has been returned to an acceptable condition. | 02-00-RHR-HX-2A
387465 | CR | 20181204 | CAQ | C | EWD-15E-010 incorrectly updated per EC 12271 |  |  |  | N | NO | <D> **** Detailed Description **** EWD-15E-010 incorrectly updated per EC 12271 related to SDIV replacement. EC 12271 incorrectly identified MS-LIS -24C SW 1B actuates RPS-RLY-K6B. MS-LIS -24B SW 1B actually actuates RPS-RLY-K6B (as verified by CVI 02C72-05,3,7 in same EC and previous drawings and functionally tested quarterly per ISP-MS-Q902. This is a drawing issue only and does not affect operability of plant equipment. EWD-15E-004 correctly shows MS-LIS-24C actuates RPS-RLY-K6C. <I> **** Actions Taken **** Initiated CR
387468 | CR | 20181204 | CAQ | D | NSSE-EQ-8B camera failed PMT per 02120901-09. | N | N |  | N | YES | <D> **** Detailed Description **** While performing WO 02120901 task 09 for the refuel bridge camera the camera picture is satisfactory with grapple sitting on DUMMY bundle bale handle. Picture focus will not change in either direction nor will the picture zoom in or out therefore when grapple is raised a few inches above bale nothing can be clearly seen because zoom and focus do not work. Don't know if it's the camera or the camera controller. This was recorded as working satisfactorily in task 01 prior to putting the mast back in the water. Please investigate and correct. <I> **** Actions Taken **** Informed craft supervisor, system engineer and work week manager. | 02-00-NSSE-EQ-8B
387469 | CR | 20181204 |  | 3 | Changes required for surveillance authorization |  |  |  | N | NO | <D> **** Detailed Description **** In order to fully capitalize on the efficiencies gained from the DataGlance application suite, several changes to the method of processing work orders should be performed. These changes are outlined in the document attached to edms, but should include the following: Remove the requirement for operations to status work in eWP to authorized for work order tasks with a control room communication of 2. Change work orders with surveillances to comm 2. Remove the CRS/SM signature requirement for authorizing surveillance work order tasks. Revise PPM 1.5.1 to remove the requirement for an SRO to change the status of surveillance work orders to authorized. The requirement to obtain verbal permission from the CRS or designee still remains in effect. Revise PPM 1.5.1 to allow use of the work order audit document attached to the eWP record if the surveillance is performed electronically. Revise all surveillances to remove the authorization signature, and include a note that if performed electronically, signatures will be captured using the audit information.
387471 | CR | 20181204 | CAQ | D | CRD-HCU-1803- Two Water alarms in one month | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02082572 then taken back to complete <D> **** Detailed Description **** CRD-HCU-1803 had two water alarms in one month (10/9/18 and 11/5/18). Three water alarms in one month is a level 5 reactivity event. Recommend cycling the piston per SOP -CRD-HCU to prevent getting a level 5 reactivity event. Discovered during System Engineering monitoring and trending. | 02-00-CRD-HCU-1803
387472 | CR | 20181204 |  | 4 | Need Cold Weather Protection at PWC-LT-100 | N | N |  | N | YES | <D> **** Detailed Description **** Per step 6.1.12 of SOP-COLDWEATHER-OPS, we require a temporary "dog house" installed over PWC-LT-100 to allow installation of freeze protection. <I> **** Actions Taken **** Discussed with PSRO. | 02-00-PWC-LT-100
387473 | CR | 20181204 |  | 4 | Daisy chained power strip found |  |  |  | N | NO | <D> **** Detailed Description **** The State Fire Marshall found a daisy chained power strip in the Simulator Hardware area. This is in conflict with ISPM-6 3.7.3d <I> **** Actions Taken **** Removed daisy chained power strip. Initiated this CR.
387474 | CR | 20181204 | CAQ | C | Overfilled job boxes creates increased fire hazard |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.3.10C Attachment 7.4 states â€œWhere metal containers (such as job boxes) are used to store materials that are combustible, keep the lids closed.â€ The RW 507â€™ Room C404 scaffold storage area southwest corner has three job boxes that are overfilled and the lids cannot fully shut. See pictures in EDMS of the one that was found fully open (says Carpenters on top). The fire protection program credits the lids are shut so the combustible contents do not contribute to the area fire severity and do not require inclusion in the combustible loading calculation. Housekeeping is needed to go through the boxes and eliminate contents so the lids can fully shut. There is no equipment operability issue. This CR is also reminder to all to keep plant job boxes and cabinet doors fully closed when unattended. <I> **** Actions Taken **** Discussed with Fire Marshal and wrote this CR. . Contacted OCC to get the job boxes unloaded and properly closed. Room C404 is not discussed in GO2-16-119, COLUMBIA GENERATING STATION, DOCKET NO. 50-397 LICENSE AMENDMENT REQUEST FOR ONE-TIME 7 DAY EXTENSION OF COMPLETION TIME FOR TS CONDITION 3.5.1.A, 3.6.1.5.A, AND 3.6.2.3.A. <N> **** Equipment Description **** RW 507' Room C404 southwest corner Williams Plant Services Carpenters.
387475 | CR | 20181204 |  | 3 | INPO 15-005 Essential Outcome Negative Trend |  |  |  | N | NO | <D> **** Detailed Description **** The INPO 15-005 Leadership Effectiveness Essential Outcome "Engage Workforce" shows a negative trend for August, September, and October based on the Leadeship Focus Team observations. <I> **** Actions Taken **** Communicated to the Leadership Focus Team, scheduled review with Senior Management, and will brief the site leadership to raise awareness and increase attention to improve performance.
387476 | CR | 20181204 | CAQ | D | Received RX Bldg Stack General Trouble alarm | N | Y |  | N | YES | <D> **** Detailed Description **** Received RX Bldg Stack General Trouble, H13-P851.S2,1-4 alarm. The alarm immediately cleared. The event log denoted NGD-12 AC not valid value. The alarm was activated for 0.16 seconds. <I> **** Actions Taken **** Notified the CRS, SM and Shift Chemistry Technician. Currently, all parameters appear normal. Reference ODCM 6.1.2 and LCS 1.3.3.1. | 02-00-PRM-RIS-1
387479 | CR | 20181204 | CAQ | C | Control of software not maintained |  |  |  | N | NO | <D> **** Detailed Description **** As part of Root Cause for CR 386750, it has been identified that the compact flash card received from the vendor that was believed to be the final version was not properly processed per DES-6-1. Furthermore, the software disk provided to IS for loading of software necessary to support the PRM-SR-1 CPU was not submitted with the appropriate documentation as required by SWP-CSW-01. This issue does not impact any current software or equipment currently used on the system. Recommend assigning to AR-CPMPROJ. <I> **** Actions Taken **** Discussed with root cause team, CPM Manager, IS Supervisor, and initiated CR.
387482 | CR | 20181204 |  | 4 | turbine supervisory rack 2 digital vector filter | N | N |  | N | YES | <D> **** Detailed Description **** Turbine supervisory rack 2 digital vector filter in control room is not functioning. When the selector knob is rotated to the different bearings the display blinks but does not show the selected bearing vibration magintude or phase angle. This display should be repaired to allow monitoring of bearing vibration phase angles. <I> **** Actions Taken **** Discussed with control room operators, initiated CR to document deficiency and to repair. | 02-00-TG-EF-1
387483 | CR | 20181204 |  | 3 | SO-P-H2S, increased noise from hydrogen side seal oil pump |  |  |  | N | YES | <D> **** Detailed Description **** SO-P-H2S, Hydrogen side seal oil pump is developing a cyclic knocking sound. Vibration readings should be taken on the pump and motor to determine if the pump is degrading and should be replaced. The increase in noise is not excessive but is noticable. The seal oil system can operate with the hydrogen side pump out of service so there is no concern of a seal oil system failure. Operation without the hydrogen side pump can result in a deacrease in hydrogen purity. <I> **** Actions Taken **** DIscussed with CRS and Shift manager. | 02-00-SO-P-H2S
387484 | CR | 20181204 | CAQ | C | Pits found on the shell of RHR-HX-2A | Y | N |  | N | YES | <D> **** Detailed Description **** During performing the As-Left inspection on RHR-HX-2A per WO 02077068, several pits were seen on the inner surface of the shell of this heat exchanger. Several pit depth measurements were taken. The range of the pits depths is between 0.2â€ to 0.25â€. The nominal thickness of the shell as shown in the code data report is 3/8â€ (0.375â€). Recommend action to NDE is to UT the shell from the outside and map out the pits and determine the remaining wall thickness in these locations with respect to the measure adjacent wall thickness. <I> **** Actions Taken **** Talked to EOC and System Engineer | 02-00-RHR-HX-2A
387487 | CR | 20181204 |  | 4 | Engineer removed from ESP training to support OCC / EOC |  |  |  | N | NO | <D> **** Detailed Description **** In accordance with GBP-TQS-01, this CR is being written to document removing an individual from Engineering (ESP) Continuing Training on 12/4/18 (within 24 hours of training) to support an emergent modification (replacement of RHR-MO-48A). Specifically, the individual was needed to develope the necessary updates to four electrical calculations to authorize the motor replacement. This work is considered highly specialized. The VP of Engineering was notified of the decision and concurred. <I> **** Actions Taken **** Informed training in advance of 0800 training start time Ensured individual is registered for a subsequent offering of ESP training Informed VP of Engineering; confimed concurrence
387488 | CR | 20181204 |  | 4 | Cabinet fan for C91/P607B noisy needs replacement | N | N |  | N | YES | <D> **** Detailed Description **** During the Computer System functional checks under WO 01103773 01 the cabinet fan for C91/P607B was discovered to be noisy and needs replacement. <I> **** Actions Taken **** writing this CR/WR <N> **** Equipment Description **** 501 MCR C91/P607B
387489 | CR | 20181204 | CAQ | D | RRA-42-7B4B - Amp readings slightly unbalanced during PMT | Y | Y |  | N | YES | <D> **** Detailed Description **** The MCC bucket at RRA-42-7B4B (RRA-FN-2) was replaced per WO# 02035825. Current readings taken during PMT for this work were outside the 10% acceptance criteria for balance between phases. A - 4.1 amps, B - 4.6 amps, C - 4.1 amps. Percent unbalance = 11.9%. All other PMT criteria was met. <I> **** Actions Taken **** Notified EOC, generated CR and WR. Need to re-perform current readings to determine whether or not issue is with test equipment or motor. Review of history for this motor shows closer balance between phases. <N> From: Oaks, Doyle L. <DLOAKS@energy-northwest.com> Sent: Thursday, December 06, 2018 12:01 PM To: Homer, Lawrence P. <LPHOMER@energy-northwest.com> Cc: Twomey, John D. <JDTWOMEY@energy-northwest.com>; Mutumba, Abubaker <amutumba@energy-northwest.com>; McLaen, Trevor W. <twmclaen@energy-northwest.com> Subject: RRA-FN-2 baker test Larry, The electric shop collected Baker data on RRA-M-FN/2 this morning per WO 02072348-01. The current readings were 4.3, 4.5, and 4.5 amp with a calculated imbalance of 4.51%. Doyle | 02-00-RRA-42-7B4B
387490 | CR | 20181204 | CAQ | D | Received the ROD DRIVE CONTROL SYS INOP alarm. | Y | Y |  | N | YES | <D> **** Detailed Description **** Received the ROD DRIVE CONTROL SYS INOP alarm (H13-P603.A7 2-8) and RPIS OR DMM INOP (H13-P603.A7 1-7) alarm. The RWM displays SYSTEM ERROR. No rod movement was in progress. Control Rod 26-43 is selected. <I> **** Actions Taken **** Notifed the CRS, SM and OCC. Reset RDCS per ARP. Reset RWM per SOP-RWM-START. Sent P616 information to applicable engineers. | 02-00-CRD-DMM-1
387491 | CR | 20181204 |  | 3 | ESP Generic Training Examination Failure |  |  |  | N | NO | <D> **** Detailed Description **** An Engineer did not achieve a passing grade on the examination administered following Generic Cycle Training on Instrumentation. Qualifications are not affected. This CR is being generated as required by TDI-02, Section 4.4.10.p.3). <I> **** Actions Taken **** Reviewed missed questions with the individual and notified their supervisor. Individual will take a make up exam to receive credit for the course following remediation.
387493 | CR | 20181204 | CAQ | D | RHR-4720-11 U-Bolt gap out of spec. | Y | N |  | N | NO | <D> **** Detailed Description **** During installation of RHR-V-922, the work group was unable to obtain the maximum allowed gap at the top of the u-bolt for support RHR-4720-11 due to a lack of threads. QC was notified 60 min prior of required inspection. U-bolt had not been installed at time of notification, therefor, when QC arrived to perform the inspection, the u-bolt was in an unacceptable configuration and a resolotion was being discussed with Eng. <I> **** Actions Taken **** Engineering and CPM contacted. <N> **** Equipment Description **** RHR-4720-11 Williams Plant Services | 02-00-RHR-V-922
387494 | CR | 20181204 | CAQ | C | RHR-P-2A Pump did not fit during installation | Y | N |  | N | YES | <C> CR Bring Back (CRBB) - ENG will have more information to bring back tomorrow. Added WP 02033672 to the cross reference panel <D> **** Detailed Description **** During installation, the pump did not sit down on the flange face by 3/8". Two fitups were tried with no success. The bottom guide pin appears to be the issue <I> **** Actions Taken **** Pulled pump and put it on the 471 Talomg measurements of old pump vs. the new pump. <N> **** Equipment Description **** 422 pump room . Response provided in Assignment 01 listed the appropriate immediate corrective action, the believed to be cause, and future corrective actions (for RHR-P-2C). It should be noted that all these pumps are "match marked" from the original installation, thus, making it very challenging for the station to allow the pump rotors be interchangeable. . No further actions are required. The parent AR-CR is now closed. . | 02-00-RHR-P-2A
387496 | CR | 20181204 | CAQ | C | Calc revision needed to support inprogress LDCN | N | Y |  | N | NO | <D> **** Detailed Description **** During review cycle of in progress LDCN under AR 336753 it was identified that ME-02-08-10 requires revision. The calculation did not include the MUR flow chagne and the calculation needs to be updated to reflect the MUR flow condition. This was identified by the Design Engineering reviewer of the LDCN, the calculaton ME-02-08-10 was reviewed to determine the impact, a detailed discussion of the review is in the EDMS and this calculation must be updated prior to approving the LDCN. <I> **** Actions Taken **** Initate this CR, and a assignement to up date the calculaton was created to update the calculation under the LDCN AR.
387498 | CR | 20181204 | CAQ | D | (QA) Work Order Planned without Required PV Inspections |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Work Order task 02113021-17 at approved status was not planned for Peer Verification for torqueing of thermal overall (TOL) in accordance with QAP-ASU-07. The Safety Related seismic 1 work task for ESP-MOVTOL-B301: TESTING OF TOL'S (RHR-MO-48A) was found, upon review by QC, without PV steps, PV resources in the appropriate panel nor ELDL qualifications in the plan. The WOT was reviewed for a QCI soft hold as requested by dayshift OCC mgt. The WOT in fact did not have a QCI hold nor was one required, however the task should have been planned, with peer verification of torqueing on the motor and motor starter leads when terminated/landed. <I> **** Actions Taken **** QC took the task to returned. Notified nightshift planner of the issue. OCC notified of the condition. Notified Quality Manager | 02-00-RHR-MO-48A
387499 | CR | 20181204 |  | 3 | Follow-up actions for org effectiveness |  |  |  | N | NO | <D> **** Detailed Description **** A review of leadership survey data identified opportunities to perform some additional follow-up to activities intended to more accurately determine if additional actions are warranted. <I> **** Actions Taken **** Assign to org effectiveness
387500 | CR | 20181204 |  | 3 | Revise 4.603.A7 |  |  |  | N | NO | <D> **** Detailed Description **** Section 3-8 of 4.603.A7 step 2 states â€œVERIFY CRD-P-1A OR CRD-P-1B running.â€ I recommend removing this step as it requires starting one of these pumps. Pump restart is accomplished by performing step 3.c.
387501 | CR | 20181204 |  | 4 | large amount of water on FW HTR 6B from steam leak. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Large amount of water running down the side of Feed Water Heater 6B visible from camera 13 on TG471. Unable to ge an exact source from cameras available. I talked to Equipment Operators familiar with the leak and they believe the amount of water has increased. It is in the vicinity of the RFW-FCV-10A leak but from using other cameras looks like there may be a second leak north of RFW-FCV-10A above the 6B heater. <I> **** Actions Taken **** CRS and supervision informed. | 02-00-RFW-FCV-10A,02-00-RFW-HX-6B,02-00-T-BLDG-MISC
387502 | CR | 20181204 | CAQ | D | Manual operation of RHR-MO-24A non-functional | Y | N |  | N | YES | <D> **** Detailed Description **** Several attempts were made to operate RHR-MO-24A manually while obtaining the as found testing with no success. <I> **** Actions Taken **** Informed OCC and EOC for resolution and added scope needed for the work. | 02-00-RHR-MO-24A,02-00-RHR-V-24A
387504 | CR | 20181204 |  | 3 | Verification/adjustment cannot be performed on RRC-PS-18B | Y | N |  | N | YES | <D> **** Detailed Description **** Verification/adjustment cannot be performed on RRC-PS-18B per ISP-RRC-Q901 step 7.2.15 due to RRC-PS-18B does not have or require a pointer due to design and only utilizes the switch function of this Barton. P&L step 4.9 (4.9 If the physical condition of the Barton switch is such that the verification/adjustment cannot be performed (i.e. missing stop bracket, snubber(s), pointer, switch vented to atmosphere), the step(s) may be marked N/A and a condition report initiated so that the condition can be evaluated and tracked for resolution) allows craft to N/A the pointer checks if not required and document the N/A of such/these steps with a CR. <I> **** Actions Taken **** N/A'ed step wrote this CR <N> Duplicate of CR-387505 and 370953. An assignment has been placed in the Maintenance enhancement database on Sharepoint. | 02-00-RRC-PS-18B
387505 | CR | 20181204 |  | 4 | RRC-PS-18B has no indicator, fix ISP-RRC-Q901 | Y | N |  | N | I DONT KNOW | <C> Trend to CR 387504 <D> **** Detailed Description **** While performing ISP-RRC-Q901 CC, step 7.2.15 wants you to check pointer stops. RRC-PS-18B has no pointer or indication. P&L 4.9 says this step can be marked N/A and to write a CR for resolution. The pointer check for this switch should be removed from the procedure. <I> **** Actions Taken **** marked appropriate steps of 7.2.15 N/A and wrote this CR | 02-00-RRC-PS-18B
387506 | CR | 20181204 | CAQ | C | Fire Protection Trouble Alarm received | N | N |  | N | YES | <D> **** Detailed Description **** FCP-1 drop 6-2 "RW BLDG 507 MECH EQUIP ROOM" Trouble alarm was received. Ops2 investigated and found nothing odd. The alarm was received coincident with resetting a different Trouble Alarm which was brought in and then cleared per WO 02092492-03 step 4.14 Rev 3. There is not any apparent relationship/connection but a mere coincidence seems unlikely. <N> Upon investigation it was inconclusive that the elevator #4 work created the alarm condition. No further action required. | 02-00-FP-ID-27/1
387507 | CR | 20181204 |  | 4 | ASD transformers need N2 add for Ambient temperatures. | N | N |  | N | YES | <D> **** Detailed Description **** Found RRC-TR-ASD/A/2 at vacuum -0.5# and others close to vacuum. ASD/A/1 0.25#, B/2 0.5#, B/1 0#. This is likely due to the cold winter weather. <I> **** Actions Taken **** Infromed MCR, initiated AR & WR. | 02-00-RRC-TR-ASD/A/1,02-00-RRC-TR-ASD/A/2,02-00-RRC-TR-ASD/B/1,02-00-RRC-TR-ASD/B/2
387508 | CR | 20181205 | CAQ | C | O-Ring found pinched during disassembly of the new RHR-P-2A | Y | N |  | N | YES | <D> **** Detailed Description **** During WO 02117218-73 disassembly of the new RHR-P-2A it was discovered that the O-ring between the suction bowl and the impeller was pinched during the assembly of the pump at the factory. <I> **** Actions Taken **** Notified my supervisor the main control room and the OCC. Recommend replacing O-ring during the reassembly task. <N> **** Equipment Description **** RHR-P-2A | 02-00-RHR-P-2A
387509 | CR | 20181205 |  | 3 | SOP-MT-AOP/TEST requires procedure change |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.1.23 "SEND a copy of the completed attachment 6.1 to the Main Turbine System Engineer" needs removed. The current practice using DataGlance is to upload the entire completed procedure and attach it to the work order or electronically complete the procedure in eWP. The engineer can get this information from DataGlance as the data is immediately available there.
387510 | CR | 20181205 |  | 4 | Shield Package 92-071 Minor Coating Damage. | N | N |  | N | YES | <D> **** Detailed Description **** While performing the bi-annual shielding, noted minor coating damage on Shielding Package 92-071, TG 441Corridor Over-head on 10 inch Condensate Line. Attached pictures in EDMS <I> **** Actions Taken **** Documented in a CR. <N> **** Equipment Description **** TG 441 Corridor
387517 | CR | 20181205 | CAQ | C | RHR-MO-24A pinion gear found loose. | Y | N |  | N | YES | <D> **** Detailed Description **** When the motor was removed from the RHR-MO-24A it was noticed that the pinion gear was loose with the tie wire and set screw still intact. <I> **** Actions Taken **** Notified OCC and EOC. Recommend close to trend, this will be corrected with the installation of the new motor WO# 02136624 | 02-00-RHR-M-V/24A,02-00-RHR-MO-24A
387519 | CR | 20181205 | CAQ | D | R-DOR-R107 found not fully closed | N | N |  | N | YES | <D> **** Detailed Description **** R-DOOR-R107 was found not fully closed. It looks like its catching on its latch. Attempted to open the door and release from 1/3 open to see if it would close and it got stuck on its latch again. This does not meet the criteria per the fire door surveillence. <I> **** Actions Taken **** Attempted to close from 1/3 open. | 02-00-R-DOOR-R107
387520 | CR | 20181205 |  | 4 | Circuit breaker lubrication | N | N |  | N | YES | <D> **** Detailed Description **** The investigation conducted by AR 384701, E-CB-1/500S failed to open, found the failure was due to degraded operating mechanism lubrication. A review of circuit breaker maintenance records found that slow opening times is typically the first indicator of degraded lubrication and that the degradation can be compounded when an interval of greater than six years between inspections occurs. During the inspection, a few drops of light machine oil is applied to the mechanism components which acts to rejuvenate the grease, make it more pliable, and extend its life. Also contributing to the lubrication degradation, E-CB-1/500S is infrequently operated, having accrued only eight operations during a thirteen year service period. Cycling a breaker periodically will remix the lubrication, slowing down the rate of degradation. When the time between their last and next scheduled inspections was reviewed, ten in-service breakers were found that will exceed an interval of six years. Eight of those breakers were already identified by ACE 358027 as likely to have degraded lubrication due to the length of time since their last overhaul and are therefore a priority to be replaced at the earliest opportunities. The other two have been added to the ACE tracking mechanism. E-CB-6/63 is already scheduled to be replaced in R24. E-CB-TR82 is scheduled to be replaced in Nov 2020. If this remains as currently scheduled, the breaker will have a service period of 8 years, 9 months without an inspection. As this breaker is also infrequently operated, engineering will work with Work Control to determine if an earlier opportunity can be found. The purpose of this CR is to document that the list of breakers judged to be of higher risk of failure due to degraded lubrication has been expanded to a total of 41. <N> Monthly stakeholder meetings are being held with Engineering, Operations, Maintenance, and Work Control personnel. This meeting will be used to find the earliest opportunity for replacing E-CB-TR82. | 02-00-E-CB-6/63,02-00-E-CB-TR82
387523 | CR | 20181205 |  | 3 | Rework - Incorrect Liner Cap Installed on Condensate Liner | N | N |  | N | NO | <D> **** Detailed Description **** On Monday, 12/3/18, the wrong liner cap was initially placed on condensate resin liner# 18-052. The liner cap for liner# 18-053 was inadvertently placed on the condensate liner being completed. Liner drying had been completed earlier in the day and the resin processing fill head had been moved to the FDR-TK-22 liner# 18-053 that required completion of its drying cycle. The resin liner vendor was contacted to determine potential impacts to liner integrity. The lid and Poly High Integrity Container (PHIC) are manufactured as an integral unit to ensure a proper fit and seal are maintained. The Vendor stated that there is no impact if damage to cap did not occur. The liner cap was then removed from 18-052 and a visual inspection of the liner cap was performed. No damage was found. The correct liner caps have now been installed on the condensate and floor drain radioactive resin liners. There is no regulatory impact associated with this error. There is no equipment issue associated with this error. <I> **** Actions Taken **** RP Supervision and Management were informed. Issue was properly documented and corrected.
387525 | CR | 20181205 |  | 3 | Enhance SOP-ELEC-SM1-MAINT, 5.5.1 & Attach 7.2. |  |  |  | N | NO | <D> **** Detailed Description **** Enhance SOP-ELEC-SM1-MAINT, section 5.5.1, last bullet about Electrician should be removed. Attach 7.2., PPM 10.25.175 can be deleted as they are controlled by Facilities. Per the Facilities Craft/Maint Supervisor there is no need to remove/restore Facilities EBU's. Add a step after power restoration for Facility Electricians to PM the affected EBU's. This can apply to other SOP-ELEC -XXX-MAINT. <I> **** Actions Taken **** Notified Ops Procedures.
387528 | CR | 20181205 |  | 3 | SOP-HVAC/RW-START step 5.2.13 references WEA-RIS-13 |  |  |  | N | NO | <D> **** Detailed Description **** SOP-HVAC/RW-START step 5.2.13 references WEA-RIS-13, it should read WEA-RIS-14
387529 | CR | 20181205 |  | 3 | Further Review Identifies Two Individual Biennial Simulator |  |  |  | N | NO | <D> **** Detailed Description **** After an additional review of crew results was conducted by the Biennial Evaluation Team, it was determined that two individuals, who were previously identified as being part of the crew failures but passing individually, will be counted as individual failures as well. This changes the overall failure rate to 15 of 51. Crew failure rate remains 2 out of 8 crews. The NRC has been notified. The individuals and crews have been remediated successfully. This should not impact the overall IP 71111.11 results. There will still be a potential NRC enforcement as described in IP 71111.11 03.02.d. Individual failure rate still remains well below 40% which could result in a white finding. <I> **** Actions Taken **** Operations and Training management have been informed. The NRC has been informed. Recommend closure to CR 387428. <N> The OPIT (CR 387428) will address the additional failures identified within this CR. This CR is routed to Training Management for closure. MS 1/2/19
387534 | CR | 20181205 | CAQ | D | Received Rod Accumulator Trouble Alarm | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02082572 then taken back to complete <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-18-03. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-18-03 was due to high water level. <I> **** Actions Taken **** Dispatched OPS-2 to investigate. OPS 2 drained water per SOP-CRD-HCU and alarm is clear. | 02-00-CRD-HCU-1803
387537 | CR | 20181205 |  | 3 | Unable to process IMDS. Missing signatures and/or dates |  |  |  | N | NO | <D> **** Detailed Description **** Document Control received a list of IMDS s to process from Engineering . 18 of them were missing dates and/ or signatures and could not be processed. <I> **** Actions Taken **** Notified my supervision. Wrote CR and notified Engineer who submitted them. Attached list of documents in EDMS.
387539 | CR | 20181205 | CAQ | C | RHR-HX-2A Shell Min wall less than allowed per design | Y | Y |  | N | YES | <C> The owed to group has been changed to AR-CPROG as per the MRT. <D> **** Detailed Description **** NDE inspection of RHR-HX-2A in response to AR 387484 regarding pits found on the shell of RHR-HX-2A resulted in min wall measurements below the required design min wall thickness. Per ME-02-85-70, the minimum wall for circumferential stress (bounding) is 0.125â€. The lowest measured wall thickness from NDE was 0.104â€. NDE results are attached to the EDMS. RHR-HX-2A is the RHR-P-2A seal cooler. The cooling of the seal water is only required during initial entry into shutdown cooling. <I> **** Actions Taken **** Discussed with EOC and SM | 02-00-RHR-HX-2A
387540 | CR | 20181205 |  | 3 | DEH solenoids incorrect amperage on CID 21911 |  |  |  | N | YES | <D> **** Detailed Description **** This CR is a repeat of CR 375437. CAT ID 21911 is incorrect an needs to NOT be used due to an amp rating of .02A . This cat id was ordered for W.O 02135425-01. Cat ID 23993 is correct and is needed. The remaining stock of 21911 needs to be returned to the vendor and not purchased. Currently we do not have the correct amperage CID 23933 to replace the DEH-SV-TRIP/C solenoid in the december downpower unless we remove the correct amperage solenoid from CID 21910 assembly. Maintenance has already been down this path under W.O 02119703-01 <I> **** Actions Taken **** notified supervisor Working with warehouse and Procurement to change status of catid to H/USER. This was completed. Discussed with Control Room. Only two instances of installation have occurred in the past (following the initial installation) and those have since been removed and replaced with the correct model style. This CATID 21911 is currently not installed in the plant. | 02-00-DEH-SV-TRIP/C
387541 | CR | 20181205 |  | 4 | Personal medical condition HFD response |  |  |  | N | NO | <D> **** Detailed Description **** On Tuesday, December 4, 2018, an individual experienced a personal medical condition. The person sought assistance from the Occupational Health Nurses at the Occupational Health Facility at the Willamette Building. The Control Room was contacted for ambulance response. The on-duty RN requested no first responder tone out. The Hanford Fire Department was called at 2:13 p.m. and arrived at the security checkpoint at 2:29 p.m. One HFD ambulance M1923 and one HFD ladder truck L1923 arrived at Occ Health and provided care for the patient. After evaluation by HFD paramedics the individual was not transported off-site to the local hospital. The manager/ supervisor was notified of the condition and drove the individual to their primary care physician. <I> **** Actions Taken **** Documented HFD resonse times in this CR.
387543 | CR | 20181205 |  | 4 | COND-V-208F failed to open during auto Backwash Cycle | N | N |  | N | YES | <D> **** Detailed Description **** while performing a backwash and precoat of COND-DM-1F the Fast Drain valve COND-V-208F failed to open all other component is step 5.11.23 a. and b. occured as expected. After the step timer, timed out, it displayed a down triangle and -0.0 and the sequence would not advance. <I> **** Actions Taken **** Informed CRS and got direction to take the COND-RMS-N12F switch to HAND and initiate a CR/WR. | 02-00-COND-V-208F
387545 | CR | 20181205 |  | 4 | Crane Technician Right Elbow Burn from Light Fixture |  |  |  | N | NO | <D> **** Detailed Description **** While traversing down to the MT-CRA-1 trolley from the temporary overhead hoist above the crane bridge, the technician brushed his exposed right elbow against a light fixture in the TG501 overhead area. <I> **** Actions Taken **** Technician immediately notified his supervisor and the project coordinator on the TG501. Technician went to Occupational Health for evaluation. Technician received first aid and instructions to monitor the wound. Technician and supervisor completed internal safety reporting documents. EN personnel generated Injury Report 18-0026 and notified the Maintenance Department Manager and PGM. This event will be reviewed with all crane technicians at PJB before work continues.
387548 | CR | 20181205 | CAQ | D | Evaluating Extent of Condition for RHR-HX-2A Pitting | Y | Y |  | N | YES | <D> **** Detailed Description **** Based off inspection results from RHR-HX-2A, RHR-HX-2B past inspection was evaluated along with RHR-HX-2C for extent of condition. RHR-HX-2B was last inspected in June 2015 (WO 02041443) and the as-left inspection did not note any significant pitting similar to what was found within RHR -HX-2A. Documented condition of last inspection for RHR -HX-2B was evaluated under CR 329531. There is no indication that RHR-HX-2B would challenge min wall thickness for shell of the heat exchanger. Next planned inspection, WO 02111390, for RHR-HX-2B is currently scheduled for next RHR B online window (October 2019). Contingency to repair/replace the HX Shell should be planned with WO 02111390. . RHR-HX-2C has not been inspected. The cooling of the seal injection water is only required for the high temperature operation of shutdown cooling mode of RHR. Since loop C has no shutdown cooling capabilities, SW is valved out to it. However, due to inspection results from RHR-HX-2A, recommend inspection of RHR-HX-2C at the next available work window to validate material condition. While current condition of RHR-HX-2C is expected SAT, contingency for repair/replace of the HX shell should be planned along with the inspection. With Service Water being valved out, RHR-HX-2C should not see Service Water System Flow or Pressure. <I> **** Actions Taken **** Notified SM | 02-00-RHR-HX-2B,02-00-RHR-HX-2C
387550 | CR | 20181205 |  | 4 | WOA heating coil 'N' steam leak. | N | N |  | N | YES | <D> **** Detailed Description **** A large steam leak was found in WOA heating coil 'N'. Local tags were alreading haning (L-WOA-HC-1/N-001). Appreared FIN had already looked at the coil (WR29141281) and left the local tags aligned with the coil inservice. I signed on to the local tagout and isolated per the tagout. <I> **** Actions Taken **** MCR notified. <N> **** Equipment Description **** Coil 'N' | 02-00-WOA-HC-1
387552 | CR | 20181206 | CAQ | D | Hole in made during weld repair | Y | Y |  | N | YES | <D> **** Detailed Description **** During performance of weld repair on RHR HX 2A per WO 02077068-09 the thin metal on the wall was blown through the I-2 location. This will need to be evaluated by Engineering for repair prior to reinstallation. See pictures in EDMS <I> **** Actions Taken **** Generated CR notified OCC and Main Control Room <N> **** Equipment Description **** RHR-HX-2A Change to the ASME plan was made and weld record to repair OD surface indication. it was not a hole but a weld metal protrusion from excessive heat. This repair will require A VT-2 System Pressure test as a result. WOT has been changed to accomodate these changes
387553 | CR | 20181206 |  | 4 | TOA-FN-1A Peckerhead Leakage | N | N |  | N | YES | <D> **** Detailed Description **** While attempting to shift to TOA-FN-1A on 12/5/18, it was discovered that the conduit box on the fan, colloquially known as a peckerhead, was leaking water. Subsequent investigation could not find any source of water that could be attributed to, and that it was likely coming from the conduit cable. The fan was immediately secured. CR written and video of water is attached. <I> **** Actions Taken **** Informed MCR/SM, initiated CR. | 02-00-TOA-FN-1A
387554 | CR | 20181206 |  | 4 | Abnormal Potable Water usage (PW leak) | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** There is abnormal Potable Water usage, as indicated by PWC-FIT-1. The yokogawa (in the flocculator bldg) is reading ~90 gpm. The trend data shows that the PWC usage has been steady at ~ 90 gpm since 0600 on 12-5-18 . This is an unusually high usage rate for the winter months and is indicitive of a PW leak. OPS 4 conducted a search for the leak. Unfortunately, the leak/rupture remained hidden under the cover of darkness. Further investigation (begin isolating sections of PW ring header) will be required, as manpower/daylight permits. <I> **** Actions Taken **** Informed MCR. Verified Security has not identified any abnormal water accumulations in the PA. <N> **** Equipment Description **** Bldg 33
387555 | CR | 20181206 |  |  | Broken Thermocouple Lead On New RHR-M/P2A | [5 empty] | <D> During performance of a walkdown on the new RHR-M-P/2A, I&C Craft noticed a broken lead on a Thermocouple wire (see EDMS for photos), as well as several other conductors that are "ringed", which could cause a failure or lead to more broken leads on the Thermocouple term block. | 02-00-RHR-M-P/2A
387559 | CR | 20181206 | CAQ | D | M&TE Suspended/ Lost |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0063200 Fluke True RMS Multimeter- model 187 Last c/o by I/C 12/19/17. Can't locate. Suspended/ Lost. EFIN EVAL: Usages #1, 2 & 4 - All have since had Surveillances performed. Usage # 3 Meter was not used. Usage #5 Reading of the 3 Phases matched closely. No Plant Impact. DEF #6776A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
387560 | CR | 20181206 |  | 4 | M&TE Suspended/ Lost |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0068297 Industrial Scientific Gas Monitor- model Ventis MX4 was NOT checked out in Met/Track and can't be located. Suspended/ Lost. DEF #6785A written. Ongoing problem with individuals not following PPM 1.5.4 to check out Calibrated test equipment. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
387561 | CR | 20181206 | CAQ | D | Broken Thermocouple lead on new RHR-M-P/2A | Y | Y |  | N | YES | <D> **** Detailed Description **** During craft walkdown of Thermocouple work, a broken thermocouple lead was noticed. Several other "ringed/nicked" conductors were also noted. this could lead to failure of these thermocouple leads if not corrected. . See photos in cancelled CR 00387555 <I> **** Actions Taken **** Notified OCC and RHR War Room of issue, generated Work Request #29145932 with instructiosn to repair broken lead and inspect/repair other leads if requiured. | 02-00-RHR-M-P/2A
387564 | CR | 20181206 |  | 3 | RP air sample data no reviewed for > 30 days with some resul |  |  |  | N | NO | <D> **** Detailed Description **** While preparing RP air sample report for records it was discovered 13 Air Samples taken in the month of October 2018 had no supervisory approval. Of the 13 Air Samples, 2 had not been completed. PPM 11.2.13.8 step 6.1 states air samples should be reviewed within 7 days of initiation and completed air sample results submitted to records within 30 days when completed. <I> **** Actions Taken **** Completed calculations for Air Sample 913784 and 913785. Deleted sample 915024because there was no data identified. Notified RP-Supervision.Requested RP supervision to complete air sample reviews.
387566 | CR | 20181206 | CAQ | D | Rod accumulator trouble alarm on CRD-HCU-3839. | Y | N |  | N | YES | <D> **** Detailed Description **** Rod accumulator trouble alarm on CRD-HCU-3839, due to low nitrogen pressure. CR written for trending. <I> **** Actions Taken **** Recharged accumulator per SOP-CRD-HCU. | 02-00-CRD-HCU-3839
387567 | CR | 20181206 | CAQ | D | CRD-V-107/1803 quick disconnect leaks. | Y | N |  | N | YES | <D> **** Detailed Description **** While performing accumulator piston sealing per SOP-CRD-HCU section 5.13 water was leaking out of the release collar for the female quick disconnect to the high pressure hose at CRD-V-107/1803. This is a threaded on fitting that can be replaced without a clearance as it is downstream of CRD-V-107/1803. Please obtain a new half inch female quick disconnect fitting and replace the old one. <I> **** Actions Taken **** informed supervisor and wrote this AR/WR. <N> **** Equipment Description **** Rx 522 L5/8.4 | 02-00-CRD-V-107/1803
387569 | CR | 20181206 | CAQ | C | Div. 1 power supply electricl drawings require update |  |  |  | N | NO | <D> **** Detailed Description **** Div. 1 power supply electricl drawings require update. New power supplies installed for EPNs E-E/S-99 (per WO 02059798) and E-E/S-199 (per WO 02059796). Both installing WOs had Attributes panel DOC Update set to YES listing the following drawings as requiring update: EWD-46E-236B, E537-1VA-102, EWD-46E-236C and E537-1VA-100. Note: EWD-46-236C is superseded by EWD-46E-269A. All of the drawings need to have Terminal 3 of the E/S indicated as the +24 VDC terminal. <I> **** Actions Taken **** Initiated this CR including info for updates required. <N> **** Equipment Description **** This is a documentation issue. | 02-00-E-E/S-199,02-00-E-E/S-99
387570 | CR | 20181206 |  | 4 | OG-LIS-8B high | N | N |  | N | YES | <D> **** Detailed Description **** On operations logs OG-LIS-8B was reading 26% level where as the band is 15-25%. While level was fluctuating this was the average. It is known to change with time, historically. CR written for trending. | 02-00-OG-LIS-8B
387571 | CR | 20181206 | CAQ | D | Rod accumulator trouble alarm on CRD-HCU-2211. | Y | N |  | N | YES | <D> **** Detailed Description **** Rod accumulator trouble alarm on CRD-HCU-2211, due to low nitrogen pressure. CR written for trending. <I> **** Actions Taken **** Recharged accumulator per SOP-CRD-HCU. | 02-00-CRD-HCU-2211
387572 | CR | 20181206 |  | 3 | 2 CRO Evaluation Forms Lack Complete Documentation |  |  |  | N | NO | <D> **** Detailed Description **** Two (2) CRO Evaluation Forms (Form #26299) lack complete documentation as required by TDI-23 which states: â€œAll follow-up questions and answers for failures should be documented in the comments section of the individual evaluation form.â€ Whereas the answers to the follow-up question were documented in both cases, two (2) completed CRO Evaluation Forms were found to not document the question that was asked. The evaluation team in both cases asked the question â€œWhat was the status of Condensate and Feed when the SRVâ€™s were open for Emergency Depressurization?â€ This question is missing from the subject 2 evaluation forms. The answer is documented in both cases on Page 2 of the CRO Evaluation Summary in the comments section of â€œUnderstand Plant and System Responseâ€ criteria. The purpose of the CR is to add record of the evaluation team question asked for purposes to complete documentation. A copy of this CR will be added to the record document of the evaluation. Recommend Severity Level 4 TREND. <I> **** Actions Taken **** Wrote this CR Performed an Extent of Condition review over all other applicable evaluations; no additional deficiencies noted.
387573 | CR | 20181206 |  | 3 | Missing EPN Label Plate | N | N |  | N | YES | <D> **** Detailed Description **** Ground Fault Indicating Panel next to E-MC-6BA missing label plate "MC-6BA" <I> **** Actions Taken **** Wrote CR for WR creation. | 02-00-E-MC-6BA
387574 | CR | 20181206 |  | 3 | Missing Label Plates for Ground Fault Indicating Panels | N | N |  | N | YES | <D> **** Detailed Description **** Ground Fault Indicating Panels for E-MC-7CA and E-MC-8CB missing label plate stating "Ground Fault Indicating Panel". <I> **** Actions Taken **** Wrote CR for WR creation. | 02-00-E-MC-7CA,02-00-E-MC-8CB
387575 | CR | 20181206 |  | 4 | Aux boiler overfull with water, coming from N2 layup drain | N | N |  | N | YES | <D> **** Detailed Description **** Last winter this same thing happened. When in heating steam, we have an aux boiler feed pump running. Even though the boiler is shut down, CO-V-12 leakby causes a slow intrusion of water to the boiler. This increases level until it eventually starts pressurizing the boiler. Last year, this caused the breakage of AS-RG-2 due to overpressurizing the outlet gauge, which still has not been replaced. The general solution was to secure the N2 blanket and connect a hose to a top vent on the boiler and leave the valve open to let the slow flow of water go to the sump. This needs to be done sooner than later to prevent the breakage of the usable reg/gauge. Though it already may be compramised as water has already made it to that leg of pipe. Pressure reads 5 psig. | 02-00-AS-BLR-1,02-00-CO-V-12
387576 | CR | 20181206 |  | 4 | BS-T-7B Failure evidenced by downstream leak | N | N |  | N | YES | <D> AR 382829 and 385995 identified a through wall leak downstream of BS-V-54B and which is downstream of BS-T-7B. This large S5 leak has been further degrading as can be seen an camera TG #01. Also the leak appears to be continuous, which would indicate that the trap is no longer trapping steam and has failed. It is also possible that the bypass valve is leaking by, but the location described in planned WO 02135814 suggests trap failure. Closure of trap station isolation valves would validate that it is the trap that has failed. Recommend that this trap station be replaced with thru-wall leak permanent repair WO 02136004. <I> Notified supervisor and FLC. <N> This represents a MWe loss concern if the trap is continuosly blowing down to the condenser. | 02-00-BS-T-7B
387577 | CR | 20181206 | CAQ | C | RHR-P-2A oring does not meet spec | Y | Y |  | N | YES | <D> **** Detailed Description **** The o ring on the RHR-P-2A suction head was discovered to be pinched. Flowserve was contacted and stated that the shipping time would be ~3 days. The commercial part number from Flowserve was AS568-281 EPDM 80 dur. This part can be commercially dedicated therefore CGS procurement engineering started a commercial dedication plan. The original part that was removed from the pump was tested and found to be a 70 dur, and does not meet the Flowserve specification. Flowserve stated that this was due to service time. Engineering does not feel that this is a valid assumption. This could be a part 21 issue with Flowserve and should be investigated. <I> **** Actions Taken **** new orings has been ordered from flowserve and a commercial dedication plan is approved if needed for a commercially purchased roing <N> send to supplier quality | 02-00-RHR-P-2A
387580 | CR | 20181206 |  | 4 | BRE 30 Heater | N | N |  | N | YES | <D> **** Detailed Description **** The BRE 30 wall mounted heater does not work and requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervision notified. CR/WR generated <N> **** Equipment Description **** BRE 30
387581 | CR | 20181206 | CAQ | D | Green Color on Particulate Filter CMS-SR-20 | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Upon removal of the Particulate Filter for CMS-SR-20, it had a slight green color. <I> **** Actions Taken **** Replaced filter with new one per instructions. Informed Supervisor. <N> **** Equipment Description **** 548Rx | 02-00-CMS-SR-20
387583 | CR | 20181206 | CAQ | D | CMS-SR-20 Particulate Filter Holder Handle Broken | Y | N |  | N | I DONT KNOW | <C> CR reopened as the work request was cancelled. The completion required check is now on WO02135078 <D> **** Detailed Description **** During performce of WO# 02128247-01, the Handle of the Particulate Filter Holder assembly was broken making it difficult to remove assembly to change filter and Orings. Needs repair. <I> **** Actions Taken **** Removed assembly and replaced filter and Orings. Informed Supervision. <N> **** Equipment Description **** 548Rx | 02-00-CMS-SR-20
387586 | CR | 20181206 |  | 4 | ASD1A/2 glycol leak on black hose union with copper piping | N | N |  | N | YES | <D> **** Detailed Description **** During a system walk down, a very low volume glycol leak was observed between hose fitting and copper pipe for ASD1A/2. No drips were noticed during the walk down. However, dried leak residue was noted on the floor below the connection. Reference pictures in EDMS of this AR. This leak has been called out in the Operator rounds data in ESOMS referencing AR 00372559 which had been documented as fixed under WO 02124960 in August 2018. Hose clamps were tightened under this WO and the leak was stopped during that time. As of today, this remains a very slow leak and the work performed did not permanently resolve the initial issue. Recommend re-performing steps as detailed in WO 02124960 which could include replacing hose clamps <I> **** Actions Taken **** notified supervisor,discussed with shift manager and wrote CR to document the issue. <N> **** Equipment Description **** VR 441' G0/3.0 (ASD BLDG) | 02-00-RRC-IMD-ASD1A/2
387589 | CR | 20181206 |  | 4 | Nalco Leak CWPH | N | N |  | N | YES | <D> **** Detailed Description **** there is a NALCO leak on the stainless piping (thru wall) leak downstream CF-V-863 the CF inlet to the TSW weir for the 42A/B pumps <I> **** Actions Taken **** isolated area and informed chem/ERP informed MCR initiated CR/WR | 02-00-CF-V-863
387592 | CR | 20181206 |  | 4 | GSB PAP ARGOS Out Of Service | N | N |  | N | YES | <D> **** Detailed Description **** ARGOS HP-EQ-42784 is out of service due to a sensor board fault on foot detector 1a. This is significant due to another ARGOS currently being out of service which leaves only one ARGOS available at the PAP RCA exit point during high RADON levels. <I> **** Actions Taken **** Contacted RP Supervision, placed ARGOS OOS and initiated this CR and WR. <N> **** Equipment Description **** GSB PAP RCA Exit Point | 02-00-HP-EQ-42784
387593 | CR | 20181206 |  | 4 | 'B' RFT turning gear failed to engage. | N | N |  | N | YES | <C> This CR was reopened to add a cross reference. <D> **** Detailed Description **** Know issue with RFT turning gear not engaging. performed SOP-RFT-OPS to wire the turning gear. <I> **** Actions Taken **** Performed SOP-RFT-OPS <N> **** Equipment Description **** turning gear of RFW-DT-1B | 02-00-RFW-DT-1B
387594 | CR | 20181206 | CAQ | B | Trip of COND-P-2A from low suction pressure. | N | N |  | N | I DONT KNOW | <C> RISK: MEDIUM (NRC PI) UNCERTAINTY: CAUSE UNCLEAR "B" WITH AN INVESTIGATION TEMPLATE <D> **** Detailed Description **** COND-P-2A tripped from low suction pressure. Low pressure cause is unknown. All three booster pumps had low pressures. RFT 'B' tripped as a result of the pump trip. Plant responded as expected and RRC Pumps ran back to 30HZ. The crew stablized the plant at 65% power in the OPRM enabled region. COND-V-76 did open. | 02-00-COND-DPIC-5,02-00-COND-P-2A,02-00-COND-V-76
387595 | CR | 20181206 | CAQ | D | HCU-1847 accumulator trouble | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** High water level alarm on HCU-1847 Written for tracking. <I> **** Actions Taken **** drained wtaer. | 02-00-CRD-HCU-1847
387596 | CR | 20181206 |  | 4 | HWC shutdown during condensate transient. | N | N |  | N | YES | <D> **** Detailed Description **** The hydrogen water chemistry system shutdown during the condensate transient experience at ~1930 on 12/6/2018. ABN-HWC was entered and a quick restart was performed per SOP-HWC-START . HWC was restored at 2145 on 12/6/2018. Indications at the panel upon operator arrival were "local shutdown demand" alarm was in, and the "Hydrogen Injector low water flow" alarm was flashing as the condition had cleared. It appears the condensate transient caused the injector low flow which caused the shutdown of the system. <I> **** Actions Taken **** Entered ABN-HWC CR written to document the shutdown. | 02-00-COND-DPIT-107
387597 | CR | 20181207 |  | 4 | COND-HX-2A tripped on high level during condensate transient | N | N |  | N | YES | <D> **** Detailed Description **** During condensate transient, COND-HX-2A tripped on high level at ~1930 on 12/6/2018. ABN-FWH-HILEVEL/TRIP was entered and the heater was recovered and left in an "removed from service" lineup as normal for this power level. CR written to document the trip that occured. <I> **** Actions Taken **** Entered ABN-FWH-HILEVEL/TRIP | 02-00-COND-HX-2A
387598 | CR | 20181207 |  | 4 | COND-DPIC-7 failed closed | N | N |  | N | YES | <D> **** Detailed Description **** COND-HX-8A and 8B bypass controller failed closed causing a low suction trip of COND-P-2A and subsequent runback to 65% power. <I> **** Actions Taken **** stablize the RX plant. | 02-00-COND-DPIC-7
387599 | CR | 20181207 |  | 3 | COND-CP-1 had no indication after booster pump trip | N | N |  | N | YES | <D> **** Detailed Description **** COND-CP-1 is the panel that lights amber indicators if any of the three pressure switches per booster pump reaches its setpoint. During the transient of Decmber 6th, when COND -P-2A tripped on low suction pressure, none of the indicators lit. It is not known whether the lights lock in or not on a pressure switch activation, but if they don't, the usefulness of the panel is drastically degraded. Suggest checking to see if these lights are designed to lock in; if not, suggest changing the design so lights will lock in with a local reset (lights only, not pressure switches). <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 441 W near COND-P-2A. | 02-00-COND-CP-1
387600 | CR | 20181207 |  | 4 | Condensate system High dp alarm did not actuate properly | N | N |  | N | YES | <D> **** Detailed Description **** System High dp alarm on COND-CP-DM/1 did not come in during a large Condensate transient that caused COND-V-76 to open. COND-DPR-205 at time of transient showed overranged dp followed by a dp of ~61#. Relay CR30 did actuate, but the alarm did not come in. Tested annunciator lights & horn and thos functioned as expected. <I> **** Actions Taken **** Informed MCR, SSS. Initiated AR. | 02-00-COND-CP-DM/1,02-00-COND-DPR-205,02-00-COND-V-76
387606 | CR | 20181207 | CAQ | D | Interference removed during RHR-M-P/2A installation | Y | Y |  | N | NO | <D> **** Detailed Description **** A U-bolt was removed and conduit moved from angle support ACOMA 9200-1 to facilitate RHR-M-P/2A installation. See EDMS for Picture <I> **** Actions Taken **** Notified OCC initiated CR and WR <N> **** Equipment Description **** 422 RX RHR "A" pump room | 02-00-RHR-M-P/2A
387607 | CR | 20181207 |  | 3 | RFW-V-106B handwheel configuration discrepancy | N | N |  | N | YES | <D> **** Detailed Description **** During lower dose (ALARA) opportunity walkdown of the RFW B pumproom 12/7/18 AM to look at RFW-V-106B for AR EVAL 376882 (Evaluate installation of handwheel restraints), it was noted that the existing handwheel configuration installed at the valve did not conform to that depicted on CVI DWG 43-00,92. The CVI drawing indicates that an original configuration chainwheel is installed directly to the valve operator shaft at RFW-V-106A and RFW-V-106B and that a regular handwheel is installed on the valve operator shaft for RFW-V-107A and RFW-V-107B. At RFW-V-106B, a regular handwheel is installed on the valve operator shaft and an aftermarket chainwheel adapter is bolted to that. See the photos attached to the EDMS of this AR CR 387607. It appears the original configuration of RFW-V-106B and RFW-V-106A were modified to the configuration observed at RFW-V-106B via WO 01078400 which references AR EVAL 182705 (Evaluate RFW-V-106A & 106B chain wheel). CVI DWG 43-00,92 and CVI OMM 43-00,124 were impacted by the configuration change per WO 01078400. This condition is a configuration management issue only - there is no associated impact upon continued functionality, operation, or qualification of any station SSCs. <N> WOT 01078400-01 appears to indicate that EMS 30034 was implemented on the RFW-V-106A and RFW-V-106B handwheels (this also affects a NOTE on CVI DWG 43-00,92). | 02-00-RFW-V-106A,02-00-RFW-V-106B
387608 | CR | 20181207 | CAQ | D | E-TR-S low oil level, addition needed | Y | N |  | N | YES | <D> **** Detailed Description **** E-TR-S has a low oil level. This generally happens in colder weather as the oil density increases, thus volume decreases. If oil level was a little higher in band it would reduce or eliminate this condition. It is desirable to have more margin and fewer operator work arounds, thus an addition should be performed. Level currently reads 0.1 per the OPS4 logs. <I> **** Actions Taken **** Informed CRS. Monitored level per temp-log. | 02-00-E-TR-S
387609 | CR | 20181207 | CAQ | 3 | Volt/Current imbalance formula |  |  |  | N | NO | <D> **** Detailed Description **** The voltage and current imbalance formula being used in PMT work instructions, such as WO 02035825-04, is incorrect. For the referenced work order, the calculated current imbalance was 11.9% which exceeded the tolerance of LTE 10%. When baker testing was later performed on the same motor, the baker software calculated the imbalance as 2.1%. While there were differences between the currents obtained due to using different equipment, they were not different enough to make that large of a change in the imbalance value. Engineering needs to identify the correct formual so planners can update work instructions.
387610 | CR | 20181207 | CAQ | D | (QA) Unacceptable Inspection Performed by Quality Control | Y | Y |  | Y | NO | <D> **** Detailed Description **** QA) Penetration Seal #C-304-4021 (4â€ diameter penetration) required a minimum seal depth of 12â€ as per Seal Control Form #7368 and Detail Number PS-1. After application of damming material by Craft the QC Inspector performed the required dimensional check inspection, accepted, and documented a depth of 10â€ measurement from the kaowool damming. The SF20 sealant start application/cure time was documented by by Quality Control. The documented 10â€ minimum seal depth recorded by QC does not meet the requirements called out in the Seal Control Form and the PS-1 detail and and PPM 15.4.5 therefore an unacceptable inspection. This was found during a document check in preparation for final inspection with the work order at "Working Status". . At the time of this finding the penetration seal had achieved the 24 hour cure for final inspection by QC and inspection had no been performed. Impairment #18-0204 is open and in place. <I> **** Actions Taken **** Notified QS Supervision, Fire Protection Engineer/Manager, Williams, and Main Control . <N> **** Equipment Description **** This is EC 15891 Seismic System Replacement Project Work per WOT 02115890-09. Williams Plant Services
387611 | CR | 20181207 |  | 3 | Alarm/Computer Label incorrectly for Booster Pump Suction | N | N |  | N | YES | <D> **** Detailed Description **** edna plot points: F518, 522, 526 are labeled incorrectly. Currently labeling states COND PUMP 1A Suction (F518). This point is actually from COND-PS-14A which is COND-P-2A [Booster Pump]. <I> **** Actions Taken **** Notified OCC as this impacted troubleshooting efforts related to COND-P-2A trip. These computer points should be updated to eliminate confusion in the future. | 02-00-COND-PS-14A,02-00-COND-PS-14B,02-00-COND-PS-14C
387613 | CR | 20181207 |  | 3 | Procedure enhancement, step clarity, SOP-H2/CO2-OPS |  |  |  | N | YES | <D> **** Detailed Description **** Add text in red. As this step is originally worded, the trailer shutoff valve should be closed. That is not the intention of the step, as you close the shutoff valve in 5.16.6. See EDMS file. <N> **** Equipment Description **** SOP-H2/CO2-OPS
387616 | CR | 20181207 |  | 4 | OG-LIS-8A level low and erratic | N | N |  | N | YES | <D> **** Detailed Description **** OG-LIS-8A level is low and erratic, and MCR is getting low level alarms. Previously this has been fixed by backfilling the instruments per equipment history. Recommend backfilling instruments to attempt to fix issues. See cross referenced ARs. <I> **** Actions Taken **** Informed MCR, generated AR/WR. See cross referenced ARs. | 02-00-OG-LIC-5A,02-00-OG-LIS-8A,02-00-OG-LT-7A
387620 | CR | 20181208 | CAQ | D | Loose light mounting plate CRA-42-7B2B | Y | Y |  | N | YES | <C> CR reopened after accidental cancellation. <D> **** Detailed Description **** The plate with red and green indicating lights on the front of the disconnect pushed into the disconnect approximately 1/2 inch when trying to replace a light bulb. This same plate is more secure on adjacent disconnects and do not move with similar pressure applied. <I> **** Actions Taken **** Replaced bulb | 02-00-CRA-42-7B2B,02-00-CRA-FN-4A
387621 | CR | 20181208 |  | 4 | COND-DPIC-5 failed to 0% in manual | N | N |  | N | YES | <D> **** Detailed Description **** ROs observed a drop in condensate booster pump suction pressure at approximately 0815. In response, DPIC-5 and COND-DPIC-7 were shifted to manual. ROs began adjusting DPIC-5 to recover booster pump suction pressure when DPIC failed to 0% still in manual. Both DPICs remain in manual. See EDMS for EDNA trace. <I> **** Actions Taken **** DPICs remain in manual. OCC and EOC notified. | 02-00-COND-DPIC-5
387622 | CR | 20181208 |  | 3 | STATE FM-Facility Fire Door Inspections Insufficient | N | N |  | N | YES | <D> **** Detailed Description **** Annual facility building inspection by the State Fire Marshal found that some Facility fire doors do not have an eyes-on and documented annual inspection as required by the Fire Code. This finding will be resolved by revision of the existing fire door inspection procedure, FPP-2.2.12. This finding does not require immediate action. Facility fire doors are continuosly observed to be in working order and corrective actions are taken when necessary. Assign to AR-TEFP for resolution. <N> **** Equipment Description **** Facility Building Fire Doors
387624 | CR | 20181208 |  | 3 | STATE FM-Facility Fire Damper Inspections Incomplete | N | N |  | N | YES | <D> **** Detailed Description **** Annual State Fire Marshal inspection of Facility Buildings found that fire damper inspections are incomplete. Fire dampers are required to be physically drop tested every four years per the Fire Code and NFPA 80. Critical fire dampers at fire walls around high dollar value areas are included in procedure FPP-2.2.11. However, all fire dampers must be tested. This issue affects Facility buildings only. <I> **** Actions Taken **** This issue was previously questioned by the State FM but no Finding was issued. AR 356412 was written and assignments are in process to identify all fire dampers and include them in procedure FPP-2.2.11. <N> **** Equipment Description **** Facility Building Fire Dampers B25, B26, B34, B35, B64 and Richland Buildings B68 and B81
387625 | CR | 20181208 |  | 3 | STATE FM-Fire Alarm Testing Requires NICET Certification | N | N |  | N | NO | <D> **** Detailed Description **** Annual State Fire Marshal review of fire alarm testing procedures finds that the crafts do not have the required NICET certification. A recent Washington State Amendment to the Fire Code requires that all technicians performing testing and maintenance to fire alarm systems must be certified by the National Institute for Certification in Engineering Technologies (NICET) as a Level 2 technologist. The Columbia method to have the craft certified by the fire alarm company (Siemens) and have the testing crew augmented by a Fire Protection Engineer does not meet the requirement. Craft that perform inspection and testing for Facility fire alarm systems include Electricians and Telecomm craft outside the Protected Area. Plant Electricians perform the testing inside the PA. This AR should be assigned to AR-TEFP so that assignments can be made to affected work groups. <I> **** Actions Taken **** The fire alarm system testing for 2018 have been completed.
387626 | CR | 20181208 |  | 3 | STATE FM-Office Lunch Room Cook Stoves Not Properly Vented | N | N |  | N | NO | <D> **** Detailed Description **** State Fire Marshal inspection of Facility buildings finds that some of the residential stoves and ovens are not properly vented to the outside. A recent Washington State ammendment to the Fire Code requires that all domestic type cooking appliances in Office lunch rooms must have a residential Type 2 hood that ventilates to the outside. Any installation that has more than one appliance must upgrade the cooking hood to a Type 1 hood. Note that ISPM-10 does not allow any cooking that produces grease laden vapors. The cooking hood requirement is necessary for basic boiling, steaming and warming of precooked food. This AR should be assigned to the Facilities manager AR-FACIL to design and provide correct type cooking hoods. <I> **** Actions Taken **** The commercial-type cafeterias are shut down so no immediate action required for them. There are several Facility buildings with residential stoves that do not ventilate outside. These should be removed from service in the near future until properly ventilated.
387627 | CR | 20181208 |  | 3 | STATE FM-Wet Chemical Fire System Inspection Deficient | N | N |  | N | NO | <D> **** Detailed Description **** Annual State FM audit of procedures found that there is no monthly inspection of the wet chemical fire suppression system. This system is located in Building 88, in the cafeteria. The monthly inspection is required to document that minimum standards such as cleanliness and clearance around Fire Protection features are upheld. Procedure FPP-2.2.15 performs a 6 month inspection and test of the system.. Assign this AR to AR-TEFP. <I> **** Actions Taken **** There is only one Wet Chemical suppression system on site, located in Building 88 cafeteria. This cafeteria is currently shut down so no immediate action is required.
387628 | CR | 20181208 |  | 4 | STATE FM-Daisy Chain Surge Protectors Found |  |  |  | N | NO | <C> This is a duplicate of CR 387473 <D> **** Detailed Description **** State Fire Marshal inspection of Kootenai Building 34 found a surge protector plugged into another surge protector in the Simulator maintenance room. This was immediately unplugged. <I> **** Actions Taken **** Determined that the desk was unattended and the computers shut down. Unplugged the surge protector and discussed the issue with a Simulator Engineer to pass on to the Supervisor.
387629 | CR | 20181208 |  | 3 | STATE FM-Deficient Fire Wall Visual Inspections | N | N |  | N | NO | <D> **** Detailed Description **** State Fire Marshal annual review of Facility procedures found that there is no specific and documented visual inspection of all fire walls. The Fire Code requires an annual visual inspection be documented to ensure fire wall integrity. The Fire Marshal does not accept the current practice of continually inspecting fire walls through periodic walk throughs and detailed inspections during remodels. Assign this item to AR-TEFP to initiate and develop a Model Work Order or Procedure.
387630 | CR | 20181208 |  | 3 | State FM-Excessive Fire Extinguisher Travel Distance | N | N |  | N | NO | <D> **** Detailed Description **** State Fire Marshal inspection found that the travel distance to a fire extinguisher exceeds the allowable 75 feet. Building 64 Records Storage room 151/158 needs to have a fire extinguisher added to meet the NFPA 10 requirement. <I> **** Actions Taken **** Work Request will add a new fire extinguisher in an acceptable location. <N> **** Equipment Description **** ABC Dry Chemical Fire Extinguisher
387631 | CR | 20181208 |  | 3 | COND-DPIC-5 IMDS should be corrected | N | N |  | N | NO | <D> **** Detailed Description **** The output of COND-DPIC-5 is 4-20mA, and not 1-5VDC as shown on the IMDS. Basis: the E/P wired to the controller's output accepts a 4-20mA input (field verified), also ref. CVI OMM 385 -00,1,1,5 page 63/89 and EWD-69I-011 for additional confirmation. The IMDS should be corrected. <I> **** Actions Taken **** Discussed with I&C shop <N> correction: CVI OMM is 358-00,1,5 | 02-00-COND-DPIC-5
387632 | CR | 20181208 |  | 3 | Unidentified Peak in Exit WBC Initially Identified |  |  |  | N | NO | <D> **** Detailed Description **** On 12/08/18 an individual who has been working on the MT -CR-1 replacement project requested an exit Whole Body Count (WBC). The WBC did not identify any radioisotopes, but did note an unidentified peak at 511 KeV energy was present. Additional WBCs resulted in the same peak. <I> **** Actions Taken **** While this energy is not associated with any activation products associated with Columbiaâ€™s operation, the RP department needed to ensure no licensed material was present. Additional surveys of another project employee also indicated the same peak was present. Air sampling of the work location, including sampling for gaseous activity did not identify any licensed material. However, the gamma isotopic results for the gaseous sample noted an unidentified peak at 511 KeV which it tentatively identified as Tl-208, a radon decay product. This was the likely source of the unidentified peak as the worker received another WBC about 5 hours after the initial count, with no decon measures taken and no peaks were identified. The worker was released with no further action with the concurrence of the RP Manager. | 02-00-MT-CRA-1,02-00-T-BLDG-MISC
387633 | CR | 20181208 |  | 3 | STATE FM-Halon Fire Suppression Missing 6-Month Bottle Check | N | N |  | N | NO | <D> **** Detailed Description **** State Fire Marshal indicated that the Facility building Halon bottles need to be weighed every six months to verify fullness. The Facility Halon bottles are continuously monitored for pressure. The pressure switch is connected to the Halon fire alarm control panel. This is an acceptable method to monitor the container integrity per NFPA 12A 2015 Edition Section 6.1.6. Assign this AR to AR-TEFP to determine if follow up actions are required.
387634 | CR | 20181208 |  | 3 | STATE FM-Facility Emergency Generator Fuel Test In Question | N | N |  | N | NO | <C> CR reopened at departments request to create more actions. See email in the EDMS. <D> **** Detailed Description **** State Fire Marshal review of the Emergency Diesel Fuel Testing procedure found to be deficient. The NFPA 110 criteria is to annually test the fuel to ASTM-975-2018, Standard Specification for Diesel Fuel Oils. Procedure 12.5.40, NonSafety Related Diesel Fuel Test indicates that two criteria are used: Viscosity and Water and Sediment percentage, to determine acceptability. The procedure references ASTM D975-94. Need to determine if the fuel test includes all necessary parameters from the current ASTM D975. Recommend this AR be assigned to AR-TEFP or to Chemistry to provide a comparison between current test method and the ASTM D975 method. <I> **** Actions Taken **** There are four Facility Emergency Diesel Generators that must follow NFPA 110 criteria. At Columbia: Deschutes Bldg 25/26 and Kootenai B34/35. At ENOC: APEL Building 68 and MPF Building 81. All four tanks are currently tested per PPM-12.5.40.
387635 | CR | 20181208 |  | 3 | ESOMS PQ&S running incredibly slowly |  |  |  | N | NO | <D> **** Detailed Description **** The ESOMS PQ&S program is running incredibly slowly. It takes the program approximately 3 minutes to open and run the self check. Then, if you want to change the date or enter new data, it takes another few minutes to run the recalculation of working hours to check for fatigue rule violations. Given that we are scheduling a large amount of overtime to deal with the unplanned downpower and the RHR-A outage, as well as CORC overtime for the outage, this poses an unnecessary burden on the individuals using the program to call out and schedule overtime. Request IS investigate and optimize resources to ensure the program runs in a timely manner. <I> **** Actions Taken **** Discussed with CRS.
387636 | CR | 20181208 |  | 3 | STATE FM-Fire Water Tank Corrosion Testing Not Performed | N | N |  | N | YES | <C> At request of Facilities reopened to add information to EDMS <D> **** Detailed Description **** State Fire Marshal review of the Kootenai fire water tanks re-coating work found that corrosion testing was not performed in accordance with NFPA 25. When steel tanks are drained down due to signs of corrosion then nondestructive ultrasonic testing is supposed to be conducted where there is evidence of pitting or corrosion. The two Kootenai tanks internal inspection report from year 2013, found in AR 280408, indicate the tank coating had "uniform corrosion induced blistering throughout the tank". Both water tanks were sandblasted and recoated without any ultrasonic readings taken to evaluate wall thickness. In addition, Tanks with flat bottoms shall be vacuum-box tested at bottom seams. This AR should be assigned to AR-FACIL to explain why the required testing was not performed or to schedule the required testing. <I> **** Actions Taken **** The two Kootenai water tanks have a weekly exterior inspection. There are no signs of water leaks documented on the procedure. <N> **** Equipment Description **** Kootenai Fire Water Storage Tanks at Building 57 and B58
387637 | CR | 20181208 | CAQ | D | Bus Bar fabricated incorrectly | Y | N |  | N | NO | <D> **** Detailed Description **** During the fabrication of Bus Bars for RHR-P-2A WO 02117218-82 EC000014635R000D.FCR one of the buss bars was not fabricated (drilled to many holes) to the bus bar sketch. . See EDMS for picture <I> **** Actions Taken **** Notified OCC wrote CR and ordered additional material | 02-00-RHR-M-P/2A
387638 | CR | 20181208 |  | 3 | STATE FM-Facility Building Evacuation Drill Record Keeping | N | N |  | N | NO | <D> **** Detailed Description **** State Fire Marshal review of the annual building evacuation drills finds that required drill information is not being recorded. Drills are being performed. The Fire Code requires that records be kept on nine different parameters. The items lacking include: Number of occupants evacuated, time to accomplish evacuation and weather conditions during evacuation. There are two buildings at Columbia that are required to have annual evacuation drills. These two buildings are Deschutes B26 and Kootenai B34. Assign this to AR-TEFP to include necessary information into existing AR 60942 and AR 60943.
387639 | CR | 20181208 |  | 3 | STATE FM-Facility Sprinkler Systems Missing Signs and Spares | N | N |  | N | NO | <D> **** Detailed Description **** State Fire Marshal noted that some fire sprinkler risers are missing their required hydraulic calculation signs. Also some risers do not have spare sprinkler heads with sprinkiler wrench in a boxat the riser in order to restore the system after a sprinkler activation. Assign this item to AR-TEFP to have a list made up for all deficient sprinkler systems. Then to have calculation signs made up and to write WR attach signs and for adding spare sprinkler and wrench boxes where missing. <I> **** Actions Taken **** Hydraulic calculation information is on file. Spare sprinklers are readily available from the Warehouse.
387640 | CR | 20181208 |  | 3 | Replacement controller scale does not match installed | N | N |  | N | NO | <C> Manually moved this CR to APPROVED after the system crashed during CR creation. Discussed the situation with the author and moved it forward. <D> WO 2136717 will be used to replace COND-DPIC-5. The replacement instrument has a 0-100 scale while the installed instrument has a 0-10 scale. The use of the new instrument was evaluated by AR 287256 with an equivalency evaluation. The equivalency evaluation did not identify the use of a new scale. Actions to be evaluated for use with the new controller requires review of the equivalency evaluation for adequacy, identification and revision of impacted procedures (e .g., SOP-COND-FILL), IMDS, and Simulator fidelity concerns, etc. to ensure proper impementation with the new instruments. <I> OCC Emergent issues briefing with Engineering, Ops, Maintenance <N> Uploaded redline of IMDS for COND-DPT-5 to EDMS folder. | 02-00-COND-DPIC-5
387641 | CR | 20181208 | CAQ | D | Indication identified in weld | Y | N |  | N | NO | <D> **** Detailed Description **** During the performance of the MT/PT for weld XI-1 WO 02033672-14 an indication was identified by NDE in the feathering of the weld to flange. Repair to follow. <I> **** Actions Taken **** Generated CR for documentation, notified OCC and planning to start the repair process.
387642 | CR | 20181208 | CAQ | C | OSP-INST-H101 for 7 DEC 18 Days contains an error |  |  |  | N | NO | <D> **** Detailed Description **** OSP-INST-H101, Shift and Daily Instrument Checks [Modes 1, 2, 3], for 7 DEC 18 Dayshift contains errata. Specifically, APRM 3 Level from IRM-LR-603C, the denoted value was 78%. APRMâ€™s 1,2 and 4 denoted values were 68%. This is Seq: 27 and Sta: 18. This caused the APRM Tolerance Evaluation to be Not OK. This is Seq: 29 and Sta: 327. The Acceptance Criteria is LE4% of each other. Most likely an error of transcription. Actual APRM Power at that moment was about 68%. This was reviewed and signed by an SRO. <I> **** Actions Taken **** Please amend the errata. Review Surveillance Requirements 3.3.1.1.1.F2a, 3.3.1.1.1.F2b, 3.3.1.1.1.F2c, 3.3.1.1.1.F2e, 3.3.1.1.1.F2f and LCS 1.3.3.1.1.F7a. <N> **** Equipment Description **** APRM-CHS-3 . coaching provided and information reviewed. No actual specifications were violated. no further action this AR,
387643 | CR | 20181208 |  | 4 | Main Gen Monitor (TG-ID-1) out of paper | N | N |  | N | YES | <D> **** Detailed Description **** The chart recorder on the Main Generator Condition Monitor is out of paper (TG-ID-1). Please refill. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 471 W | 02-00-TG-ID-1
387644 | CR | 20181209 | CAQ | D | RHR-P-2A thermocouple terminations | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** RHR-P-2A thermocouple terminations, work order 02117218-04; Unable to terminate thermocople cables due to termination box space, cable number ACOMA-9200 and ASCAN-9023. <I> **** Actions Taken **** Recommended actions: Planning to completethe following; Have a task for electricians to pull cables back into cable tray approx 35' away in the same room, cable tray covers will have to be removed to suppport cable being pulled back, build scaffold under tray to support cable pull, support task to have I/C technicians there for guidance on how much cable to pull back. Pulling cable's back will reduce the amount of dose taken by I/C to modify cables to fit in the box if not pulled back. | 02-00-RHR-M-P/2A,02-00-RHR-P-2A
387645 | CR | 20181209 |  | 3 | COND-E/P-5 failed bench test |  |  |  | N | NO | <D> **** Detailed Description **** During the bench testing in work order number 02136717-11 CAT ID 060103974 failed its bench test - part ordered not linear during bench test; could not calibrate per spec. <I> **** Actions Taken **** initiate cr, order remaining 2 in stores, inform OCC and document in work history. | 02-00-COND-E/P-5
387646 | CR | 20181209 | CAQ | D | E-TR-7/73 pressure is at a vacuum | Y | N |  | N | YES | <D> **** Detailed Description **** During OPS2 rounds, it was noted that E-TR-7/73 pressure is at a vacuum of .6". Room temperature was significantly lower than the previous tour, however, it is abnormal and out of specification for the Transformer pressure to be at a vacuum. <I> **** Actions Taken **** informed MCR and wrote CR. | 02-00-E-TR-7/73
387647 | CR | 20181209 |  | 4 | COND-FQ-200E indicates 690-750 gpm with CFD offline. | N | N |  | N | YES | <D> **** Detailed Description **** COND-FQ-200E indicates flow with COND-DM-1E off line and after isolation . Past trouble with this totalizer was a drift in the zero adjustment. Suspect same. <I> **** Actions Taken **** Notified MCR/CRS. <N> **** Equipment Description **** RWCR | 02-00-COND-DM-1E,02-00-COND-FQ-200E
387649 | CR | 20181209 | CAQ | D | OSCILLOGRAPH STARTED alarm received | N | N |  | N | NO | <D> **** Detailed Description **** . CRO2 reports it was the (J8 Sensor) 230 KV Neutral Ground Overcurrent, (J9 Sensor) 115 KV Neutral Ground Overcurrent and (J15 Sensor) 230 KV Undervoltage. All sensors are reset. BPA Munro reports Benton-White Bluffs #1 115KV line tripped and closed back in automatically. Control room voltage indications are 238KV, 239KV & 238KV for each phase of Startup power and 118KV, 118KV & 118KV for each phase of Backup power. Containment Vacuum Breakers, Hotwell, RRC, Feedwater Controllers and Plant Inverters exhibit normal operation. <I> **** Actions Taken **** Informed CRS
387650 | CR | 20181209 | CAQ | D | RHR A T/C cable ground wires can not be attached to term blo | Y | N |  | N | YES | <C> Reopened at request of engineering to add notes <D> **** Detailed Description **** During reconnection of the T/C ground wires the 4 ground wires could not be connected per the work instructions. <I> **** Actions Taken **** Informed shop supervisor Developing a repair plan <N> **** Equipment Description **** RX422 RHR pump room - Engineering reviewed the pertinent drawings and determined this is below the level of detail shown on the drawing. Specific location and attachment method for the ground connection is not articulated. Engineering position is that installation adequately fulfills the requirement of grounding the shield. Refer to EDMS for email documentation. | 02-00-RHR-M-P/2A
387651 | CR | 20181210 |  | 3 | Revise ARPs for condensate booster pump low suction pressur |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate and revise the ARPâ€™s for low condensate booster pump pressures. This should include steps to read COND -DPIC-5 and COND-DPIC-7 for fluctuations and take manual control as necessary. See edms. <I> **** Actions Taken **** Initiated CR | 02-00-COND-DPIC-5,02-00-COND-DPIC-7,02-00-COND-P-2A,02-00-COND-P-2B,02-00-COND-P-2C
387652 | CR | 20181210 |  | 3 | Consider performing loop calibration of COND-DPIC-5 in R24 |  |  |  | N | NO | <D> **** Detailed Description **** During the replacement of COND-DPIC-5 online we were unable to verify the operation of the COND-PCV-5 due to plant conditions. Rercommend performing the full loop calibration in R24 to validate proper operation of COND -PCV-5 operation of | 02-00-COND-DPIC-5,02-00-COND-DPT-5,02-00-COND-PCV-5
387653 | CR | 20181210 |  | 3 | 2nd IC tech unavailable. Supervisor used to perform loop cal |  |  |  | N | NO | <D> **** Detailed Description **** Loop cal for PMT of COND-DPT-5 was performed by 1 IC tech and a supervisor as a second IC tech was not available to complete the task. IC manager provided oversight of the evolution. Technician expressed concern over this practice and provided pushback to the OCC and IC manager. <I> **** Actions Taken **** OCC informed, IC manager informed and CR initiated to document use of unqualified individual under direction of supervision. | 02-00-COND-DPT-5
387654 | CR | 20181210 |  | 4 | XD 4 Needs Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** XD 4 Needs Maintenance <I> **** Actions Taken **** CR/WR, Security Supervision Notified | 02-00-SEC-XD-4
387659 | CR | 20181210 |  | 4 | Security Cameras to be cleaned |  |  |  | N | NO | <D> **** Detailed Description **** Security Cameras to be cleaned cctv 01, 16, 17, 22, 25 thermals 4, 7, 16, 17, 21, 22 <I> **** Actions Taken **** CR/WR, Security Supervision Notified | 02-00-SEC-CCTV-1,02-00-SEC-CCTV-16,02-00-SEC-CCTV-16T,02-00-SEC-CCTV-17,02-00-SEC-CCTV-17T,02-00-SEC-CCTV-21T,02-00-SEC-CCTV-22,02-00-SEC-CCTV-22T,02-00-SEC-CCTV-25,02-00-SEC-CCTV-4T,02-00-SEC-CCTV-7T
387660 | CR | 20181210 | CAQ | D | Required Compensatory Actions of LCO 1.6.1.5.A.1 not met |  |  |  | N | NO | <D> **** Detailed Description **** This CR is written per LCS RFO 1.6.1.5.C.1 to document failure to restore Suppression Pool Spray to OPERABLE Status within seven days per RFO 1.6.1.5.A.1. RHR-SYS-A remains inoperable for a 14-day TSAS as approved per GO2-16-119 as a 1-time LAR in support of RHR-P-2A replacement. The OCC remains active to restore RHR-A to operable per the plan.
387662 | CR | 20181210 |  | 4 | E-GEN-1 vibration data unusually low compared to trend | N | N |  | N | YES | <D> **** Detailed Description **** The spectral data for all points indicate a low amplitude step change at 2X Operating Speed (60 Hz). The 1X component has reduced significantly from trend values. This could be caused by the data being collected on the wrong points, plant/loading conditions changed, or that maintenance was performed. It could also be caused by proximity probe adjustments or changes. Continue monitoring. Obtain a follow up data set ensuring proper data collection setup / point location and machine speed / load. <I> **** Actions Taken **** Reviewed data and verified trends. | 02-00-E-GEN-1
387663 | CR | 20181210 |  | 4 | Recieved 4.602.A5 4-7 RWCU PUMP A Trouble | N | N |  | N | YES | <D> **** Detailed Description **** Recieved 4.602.A5 4-7 RWCU PUMP A Trouble. RWCU parameters are normal in the MCR. OPS 2 reposrtd the cause of the alarm is CRD-FS-2A indicates low flow. All other parmerters are normal in the field. I&C support needed to flow adjustment per ARP and SOP <I> **** Actions Taken **** Wrote this CR. Dispatched OPS 2. | 02-00-CRD-FS-2A,02-00-RWCU-P-1A
387664 | CR | 20181210 |  | 3 | Incorrect SQA version number in catalog |  |  |  | N | NO | <C> Closed and reopened CR to remove proper name from Immediate Action notes per SWP-CAP-01. <D> **** Detailed Description **** Catalog show version 1.130 and should read 1.1.30 FW-SOFT-COTS-MFARD21 <I> **** Actions Taken **** Alerted Records / Information Management Manager <N> **** Equipment Description **** Monaco Fire reporting | FW-00-SOFT-COTS-MFARD21
387666 | CR | 20181210 | CAQ | D | Broken thermocouple wire found during terminations | Y | Y |  | N | NO | <D> **** Detailed Description **** During performance of WO 02117218-04, retermination of thermocouple wires on RHR-M-P/2A, it was discovered that currently installed thermocouple wire 3RHR-TE-501-3 (BL) (+) on terminal P3-3, was broken inside junction box. This is a spare thermocouple wire and is not in use. <I> **** Actions Taken **** Contacted supervision and was provided direction to repair broken wire and document with CR. Repaired wire per 10.25.19. <N> **** Equipment Description **** RHR-M-P/2A TERMINAL BOX | 02-00-RHR-M-P/2A
387668 | CR | 20181210 |  | 4 | PPM 10.24.57 requires correction |  |  |  | N | NO | <D> **** Detailed Description **** PPM 10.24.57 - PM CAL/Test - Bailey Basic Controller - should be corrected per the attached markup in the EDMS. Issues with the reference use procedure are as follows: (1) The notes on page 13 and Attachment 9.2 incorrectly refer to output voltage as input voltage â€“ this caused confusion and significant delays during implementation of WO 02136717-02. (2) Step 7.6.10 requires second person verification. It is not clear why step 7.6.15 does not require the same. Recommend changing step 7.6.15 for consistency. (3) Attachment 9.5 Step 1.6 should read â€œâ€¦5 voltsâ€, not â€œSVâ€. (4) Attachment 9.2 includes several instances of â€œ#Div/0!â€ â€“ They should be removed. <N> ***General Notes*** An assignment has been made within the Maint. procedure revision data base. a mark up has been added to the edms of this AR. A link to the Maint. procedure revision data base has been added to the EDMS of this AR> | 02-00-COND-DPIC-5
387669 | CR | 20181210 |  | 3 | Procedure change for 4.602.A5 |  |  |  | N | NO | <D> **** Detailed Description **** Request the following change be made to PPM 4.602.A5, both 4-7 and 4-8 step 3c, to make the step conditional: "IF unable to clear the low flow light, THEN ESTABLISH....". Also need to change "lights" to "light" on both steps 3b (editorial change).
387670 | CR | 20181210 |  | 4 | Replacement controller for COND-DPIC-5 failed bench test/cal | N | N |  | N | NO | <C> Item is obsolete with no vendor for warranty and item is set up for future repair/return only. This is non-safety and recommend a 4 trend <D> **** Detailed Description **** On 12/9/2018 while bench testing the replacement controller for COND-DPIC-5 per PPM 10.24.57 and WO 02136717-02, the controller CID 60111926 failed the section on Deviation Meter Calibration - could not be adjusted within spec. <I> **** Actions Taken **** Informed I&C shop at that time. A replacement controller was pulled from stores and calibrated successfully. | 02-00-COND-DPIC-5
387673 | CR | 20181210 |  | 3 | COND-DPT-7 IMDS requires correction |  |  |  | N | NO | <D> **** Detailed Description **** The IMDS for COND-DPT-7 shows COND-DPIC-7 as indicating 0 -10 psid input whereas in fact it indicates 0-100%. Markup in EDMS. No impact on equipment. | 02-00-COND-DPIC-7,02-00-COND-DPT-7
387675 | CR | 20181210 |  | 4 | STATE FM-B34 Wiring Found Attached to Fire Sprinkler Piping | N | N |  | N | NO | <D> **** Detailed Description **** State Fire Marshal inspection found that wiring has been laid on fire sprinkler piping. Some places the wiring has been tie wrapped to the fire sprinkler piping. ISPM-10 prohibits this practice. The requirement comes directly out of NFPA 13, the Fire Sprinkler Standard. Building 34 Penthouse and B34 Telecom room and B34 HVAC Room 123B. Based on work requests written and included in XREF, this AR can be closed. <I> **** Actions Taken **** B34 Penthouse appears to be HVAC control wiring. WR 29145996 written for Facilities to remove the wiring. B34 Telecom Room 211 appears to be telecom and computer wiring. WR 29145997 written to remove wiring.
387677 | CR | 20181210 |  | 3 | ISPM-18 â€“ Caution Barrier Posting Non-Conformances |  |  |  | N | NO | <D> **** Detailed Description **** Caution Barriers (Signs & Tape) supporting the elevator modification work are not posted in accordance with ISPM-18 Section 3.4.9. See pictures for examples in the EDMS file. . Facts: 1. 487â€™ Radwaste Posting: a. Yellow tape is posted with NO Caution Sign b. A Notice sign is on the elevator door informing personnel the elevator is out of service. We are not allowed to have multiple signs (Caution/Notice) at any work site; it can be confusing to personnel. 2. 467â€™ Radwaste Posting: a. The Caution tape has been twisted in a roll and canâ€™t be read. Three Caution tape streamers are hanging from it. b. The Caution sign is missing the CONTACT name and extension. 3. 441â€™ Main Hallway has no Caution sign postings at all which is inconsistent with the other elevator door locations. It was recommend to the Project Manager that someone evaluate each floor elevation (elevator door location) and ensure postings are in conformance with the ISPM. Requirements: ISPM-18 Section 3.4.9 â€œCaution Barriers â€œstates; a. A Caution barrier is identified as tape, rope, flagging, or physical barricade delineated with caution signs. (If an attendant is present the sign is optional) b. The barrier delineates an area, which has potential hazards. Examples of hazards which would be inside a Caution Barrier are: â€¢ Job site area hazards â€¢ Welding hazards â€¢ Overhead hazards c. A caution barrier with a Caution sign(s) attached shall be placed to warn personnel of possible hazards. (If an attendant is present the sign is optional) {R-6.2} 1) The sign should identify the hazard(s), the required PPE, conditions for entry, and the name(s) and phone number(s) of contact personnel such as project worker or supervisor. (Form 26966) d. IF personnel have a true business need to cross the barrier, understand the identified hazard, have proper PPE donned, and can comply with all other entry requirements, THEN personnel may enter or cross a Caution barrier. <I> **** Actions Taken **** Contacted the responsible CPM Project Manager.
387678 | CR | 20181210 |  | 3 | 2 EDs not updating eDNA real time data viewer | N | N |  | N | NO | <D> **** Detailed Description **** EDs #31440 and 694881 assigned to provide back-up indications for ARM-RIS-20 and ARM-RIS-24 is not updating eDNA real time service. The devices are transmitting to AlaraCast as expected, but data is not being sent to archive file in which the eDNA interface collects data from. <I> **** Actions Taken **** Notified IS support and RP lead desk. If the back-up service is required the EDs may need to be replaced. Notified RP-Ops.
387679 | CR | 20181210 |  | 4 | WMA-FN-6 degraded Filter unit door gasket | N | N |  | N | YES | <D> **** Detailed Description **** During the Preventive Maintenance of WMA-FN-6 WO 02105906 -01 it was discovered that the fans filter unit door gasket is degraded and should be replaced. The gasket is a self adhesive1â€ wide by Â½â€ thick and would need 25 feet to replace it in its entirety. The current gasket still serves its purpose and doesnâ€™t affect the fans operation. <I> **** Actions Taken **** Notified MCR, initiated CR and WR | 02-00-WMA-AH-6,02-00-WMA-FN-6
387680 | CR | 20181210 |  | 3 | Oil leak from E-TR-M2 bus duct. | N | N |  | N | YES | <D> **** Detailed Description **** There is an oil leak of about 6 dpm coming from the bus duct on the SE end of E-TR-M2 in the vicinity of E-DISC -LINK/M2/E. Discovered leak while performing Transformer Yard Inspection IAW WO# 02001147-01. <I> **** Actions Taken **** Notified supervisor and Engineering. <N> **** Equipment Description **** Transformer Yard. | 02-00-E-TR-M2
387681 | CR | 20181210 |  | 3 | Training Records Submitted w/o Flag Sheet |  |  |  | N | NO | <D> **** Detailed Description **** A large Stack of Training records was submitted to records control without following the proper submittal process. They were not flagged appropriately and were not submitted following the confidential process . Please Refer to SWP -REC-02 section 4.3.2 and GBP-REC-04 section 4.7.1 for the submittal process on these types of records. <I> **** Actions Taken **** Notified my supervisor, Notified appropriate personnel in Operations Department for Corrections and re submittal.
387682 | CR | 20181210 |  | 4 | STATE FM-Fire Wall Repair Required B34 Room 134 | N | N |  | N | NO | <D> **** Detailed Description **** State Fire Marshal inspection found a fire wall that needs repair. Building 34, Kootenai, Class Room 134 has a hole in the wall and door frame. Appears that door hardware or locking device was changed and the wall and frame were not restored to one hour fire rating status. <N> **** Equipment Description **** Kootenai B43 Classroom 134 . See EDMS for picture.
387686 | CR | 20181210 | CAQ | C | mathematical Operator missing impacting ME-02-18-01 Appendix |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of copying some expressions from the calculation ME-02-18-01 to be used in eSOMS reports to avoid the use of interpolations, it was found that one variable in an expression term was missing a mathematical operator impacting Appendix A in the calculation. The expression was used on the region for calculation of values with drain time greater than 36 hrs. causing the calculated result to differ slightly for the above region greater than 36 hrs. . This error is considered inconsequential since the calculation developed was being implemented on a document to be used during the RFO 24. This condition will require updating Appendix A in calculation ME-02-18-01. Update Calculation ME-02-18-01 Appendix A <I> **** Actions Taken **** Tables in appendix A were reviewed to determine the error impact, It was found that the impact was minimum since the results from the corrected tables differ slightly for the region where the drain time is around the 36 hrs. zone.
387687 | CR | 20181210 |  | 4 | COND-DPT-5 OOT | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** WHILE PERFORMING WR 29145957, COND-DPT-5 WAS FOUND OOT APROXIMATELY 0.32 MADC BELOW TOLERANCE AT ALL 5 POINTS LINEAR (DESIRED IS 4 MADC THRU 20 MADC +- 0.04). ADJUSTED ALL AS LEFT VALUES ON COND-DPT-5 WITHIN TOLERANCE PER 10.24.32. <I> **** Actions Taken **** CONTACTED SUPERVISION AND CALIBRATED PER 10.24.32 <N> **** Equipment Description **** COND-DPT-5 | 02-00-COND-DPT-5
387688 | CR | 20181210 | CAQ | C | FCP 3 drop 17-4 alarms not expected | N | Y |  | N | NO | <D> **** Detailed Description **** working maintenance PPM's alarm FCP 3 Drop 17-4 would alarm at times when FCP 2 was reset. maintenance procedures need to be revised. <I> **** Actions Taken **** contacted Operations to clear alarms <N> **** Equipment Description **** revise procedure | 02-00-FP-CP-FCP2,02-00-FP-CP-FCP3
387689 | CR | 20181210 |  | 4 | INSTRUMENTS FOUND OOT DURING PMT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** DURING PMT OF COND-DPIC-5 AND COND-E/P-5, WO 02136717-03, COND-DPT-5 WAS FOUND OOT APROXIMATELY 0.24 MADC BELOW TOLERANCE AT ALL 5 POINTS LINEAR (DESIRED IS 4 MADC THRU 20 MADC +- 0.04). ADJUSTED ALL AS LEFT VALUES ON COND-DPT-5 WITHIN TOLERANCE PER 10.24.32. COND-DPT-5 WAS RECENTLY CALIBRATED UNDER WR 29145957. COND-E/P-5 WAS ALSO FOUND OOT APPROXIMATELY 2 PSIG BELOW TOLERANCE AT ALL 5 POINTS LINEAR (DESIRED IS 3 PSIG THRU 15 PSIG +- .6). ADJUSTED ALL AS LEFT VALUES ON COND-E/P-5 WITHIN TOLERANCE PER MFG. INSTRUCTION MANUAL AND IMDS. <I> **** Actions Taken **** CONTACTED SUPERVISION, OPERATIONS, AND CALIBRATED PER 10.24.32, MFG. INSTRUCTION MANUAL AND IMDS. <N> **** Equipment Description **** COND-DPT-5 COND-E/P-5 | 02-00-COND-DPT-5,02-00-COND-E/P-5
387691 | CR | 20181210 |  | 3 | FW Total Iron above Action Level 1 | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** An integrated metals sample was collected on 12/10/18 from Reactor Feedwater. The result was 6.8 ppb. Primary Chemistry Action Level 1 is GT 5.0 ppb per SWP-CHE-02 Table 6.1.15. The sample collection was started on 12/6/18 prior to the downpower and unexpected opening of COND-V-76. This is likely the cause of the elevated sample result. The frequency of measurement is â€œIntegrated 96 hrsâ€. Additional Guidance #8 states â€œCorrective actions for exceeding Action Level 1 for feedwater iron and feedwater zinc apply after 96 hrsâ€. The sample collection was started on 12/10/18 and will end on 12/13/18. <I> **** Actions Taken **** Reviewed sample results. Informed Chemistry supervison. Started next sample collection. Wrote this CR for documentation.
387692 | CR | 20181210 |  |  | Chemistry Technician Initial Training Exam Failure
387693 | CR | 20181210 |  | 4 | Chemistry Technician Initial Training Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** A student in the Chemistry Technician initial training program failed an exam. <I> **** Actions Taken **** The student conducted a review of the examination, and reviewed the objectives. A counseling session was conducted to reinforce the importance of proper exam preparation and exam taking. A subsequent exam resulted in a passing grade. Trend only.
387695 | CR | 20181210 |  | 4 | Waste vendor arrived 4 hours late. |  |  |  | N | NO | <D> **** Detailed Description **** Safety Kleen was four hours late to their committed timeline for a SLC-Water shipment occurring at the 437â€™RW roll-up doors. Coordinated efforts were made over a two -month timeframe with multiple departments including: E&RP, Security, RW Shippers, HP, and RW Labors in order to facilitate the commitment. Safety Kleenâ€™s failure to arrive in timely manner forced committed resources to standby for the shipment and reschedule other priorities. This CR is for trending purposes; no further action required. <I> **** Actions Taken **** Initiated CR and notified E&RP manager. Contacted vendor sales rep and notified company of dissatisfaction. <N> **** Equipment Description **** 437'RW roll-up doors
387696 | CR | 20181210 |  | 4 | TMU-P-1C lube water low flow is locked in again. | N | N |  | N | YES | <D> **** Detailed Description **** It was observed on a panel walk down that the alarm for TMU-P-1C is now locked in. This will impeded the planned start of TMU-P-1C on 12-11-18. <I> **** Actions Taken **** Informed Supervision, Emailed FIN | 02-00-TMU-FIS-5C,02-00-TMU-P-1C
387697 | CR | 20181210 | CAQ | D | Cable 1SM7-0060 train radius is less than the requirement | Y | Y |  | N | YES | <D> **** Detailed Description **** After termination of cable 1SM7-0060 inside the new RHR-P -2A motor terminal box, the electrician found the train radius of the cable 1SM7-0060 is less than 13.5 inches for Type B 4/0 AWG 5KV undergrounded neutral power shielded cable as required per procedure 10.25.54. The train radius measured is approximately 8.5 inches for this cable as measured in the final configuration (see the picture in AR EDMS). Engineering recommends <I> **** Actions Taken **** Contacted management and engineering. Initiated and approved EC EVAL 17511 to evaluate the impact on the cable for the performance and the reduction in life. Although the cable has a bend radius of approximately 8.5 inches, a report published by Watts Bar identified that the manufacturer Okonite allowed a relaxed bend radius up to 4.4 times the diameter of the cable. The EC evaluation documents that there is adequate margin to determine the cables can operate without impacting the mission time for the RHR motor to perform its safety function. Engineering recommends replacing the stress cones to allow the cable to be shortened to alleviate the cable rend radius issue at the next opportune time. | 02-00-RHR-M-P/2A
387698 | CR | 20181210 | CAQ | C | Items on M544 do not have EPN in MEL |  |  |  | N | NO | <D> **** Detailed Description **** While working on License Renewal implementation it was discovered that SGT-ME-3A, 3B 5A and 5B are shown on M544 but EPN in MEL does not exist. <I> **** Actions Taken **** Initiate this CR | 02-00-SGT-MI-3A,02-00-SGT-MI-3B,02-00-SGT-MI-5A,02-00-SGT-MI-5B
387700 | CR | 20181210 | CAQ | B | New RHR-M-P/2A Motor is a Different S/N than EC | Y | Y |  | N | YES | <C> CRG review Risk: High - Bullet 6 SWP-CAP-06 page 21 Cause: Complex/Uncertain Grade: CAQ "A" with a root cause CR Rescreened at OFM/MRT on 02.14.2019 and downgrade approved to Severity B, Investigation Template Required. See CR RESCREEN notes in Attributes. <D> **** Detailed Description **** New Schulz RHR motor removed from the warehouse and installed under WO 02117218 has a serial number that does not match EC 14635. There are three new Schulz RHR motors that are the same model number. <I> **** Actions Taken **** Notified RXMM Supervisor Engineering notified Engineering is commencing writing an FCR for the new RHR motor that represents the serial number of the motor that is currently installed on the new RHR Pump. <N> This CR is CAQ based on attachment 8.1 example 7) a generic break down of a program implementing quality assurance requirements The cause of this event is complex uncertain, and the risk of this event is High. | 02-00-RHR-M-P/2A
387701 | CR | 20181210 |  | 4 | Loose fitting on COND-SPV-17 | N | N |  | N | YES | <D> **** Detailed Description **** During replacement of COND-DPT-5 it was noticed air was leaking from the air inlet to COND-SPV-17. Investigation shows minor thread engagment from teh air tubing to the SPV. <I> **** Actions Taken **** Informed CRS and OCC Wrote CR | 02-00-COND-SPV-17
387702 | CR | 20181211 | CAQ | D | Rod accumulator trouble, HCU 3839, low N2 pressure | Y | N |  | N | YES | <D> **** Detailed Description **** Received rod accumulator trouble alarm on CRD-HCU-3839 due to low nitrogen pressure. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-HCU-3839
387703 | CR | 20181211 |  | 4 | GY-TK-10B1 level trending down | N | N |  | N | YES | <D> **** Detailed Description **** It appears that GY-TK-10B1 level is trending down. Since Oct 2018 level has dropped 2 inches per logs. Hard to confirm but seems that leak has increased in rate. <I> **** Actions Taken **** Informed MCR | 02-00-GY-TK-10B1
387704 | CR | 20181211 |  | 4 | GY-TK-10A1 level trending down | N | N |  | N | YES | <D> **** Detailed Description **** It appears that GY-TK-10A1 level is trending down. Since Oct 2018 level has dropped 2 inches per logs. Hard to confirm but seems that leak has increased in rate. rate <I> **** Actions Taken **** Informed MCR | 02-00-GY-TK-10A1
387712 | CR | 20181211 |  | 3 | GEN-TQS-03 has attachments numbered incorrectly. |  |  |  | N | NO | <D> **** Detailed Description **** GEN-TQS-03 has eight sections. Section 8 is for attachments. The actual attachment is titled 9.1 instead of 8.1 as the table of contents shows and the list of attachments shows on page 24. Please correct the numbers on the actual attachments to read Attachment 8.1. <I> **** Actions Taken **** Wrote this AR/PCR.
387713 | CR | 20181211 |  | 3 | Remove unneeded changes PPM 15.1.16 |  |  |  | N | NO | <C> Per SWP-CAP-01, removed name from immediate action notes, left title for reference. <D> **** Detailed Description **** steps were added that is not needed ,CR 373966 to remove. different stepswere added, still not needed new CR PPM needs to go back to existing , all worked well, the step are duplicating a PM that is performed quarterley ,usually with in 2 weeks <I> **** Actions Taken **** Contacted system engineer to complete a markup <N> **** Equipment Description **** revise 15.1.16 Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications No assignment needed.
387714 | CR | 20181211 |  | 3 | Alarm Printers both out of service during RHR Pump Trip | N | N |  | N | YES | <D> **** Detailed Description **** This impacted operations/engineering ability to analyse the trip. Computer Engineering was called out to recover the data. This caused an 8 hour delay in this data being available for the troubleshooting process. Suggest this CR go to CPM - PPC Project. <I> **** Actions Taken **** Engineering staff called in to recover data. Alarm printer functionality returned. | 02-00-PPC-PRN-A1,02-00-PPC-PRN-A2
387715 | CR | 20181211 | CAQ | D | Wrong type of fuse installed | Y | N |  | N | YES | <D> **** Detailed Description **** During a motor starter inspection PM, the control power fuse was replaced with an incorrect type of fuse. Per drawing E528-18C, the control power fuse of DSA-42-6B4E (DSA-C-1C starter) is to be a type ATM, A6Y, F60C, or KTK fuse with a 3 amp rating. According to the fuse log entry, the craft replaced an ATM-3 fuse with a FNQ-R-3. While the installed fuse has the correct rating, the FNQ is a time delay fuse while the ATM is a fast blow. Recommend replacing the control power fuse with the correct type at earliest opportunity. | 02-00-DSA-42-6B4E
387716 | CR | 20181211 |  | 3 | DSA-V-715 is listed as inactive in passport. |  |  |  | N | NO | <D> **** Detailed Description **** DSA-V-715 shows up in the passport D030 panel as inactive since 07/29/1998 and that it was the PS-19 Root Isolation. SOP-DG3-LU also calls it the PS-19 Root Valve. AED MEC 512-1 shows it as a vent valve and the actual field configuration is that the valve does exist and it is just a vent valve and the EPN tag describes it as a â€œCross Connect Ventâ€. The EPN tag is correct in the EPN per the drawing and the description is correct in its function as seen in the field and on the drawing. Please update passport status as active and change the name to â€œCross Connect Ventâ€ and then correct SOP-DG3-LU description to reflect that it is a cross connect vent. eSoms has already been corrected with this information. See picture and drawing in EDMS. <I> **** Actions Taken **** Updated eSoms and wrote this AR. | 02-00-DSA-V-715
387717 | CR | 20181211 |  |  | NRC request for test CR |  |  |  | N | NO | <D> **** Detailed Description **** NRC wants to see CR
387720 | CR | 20181211 | CAQ | D | PI-EFC-X78B closed during the performance of work order. | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO# 02033672-74 PI-EFC-X78B closed during the performance of section 4.4. <I> **** Actions Taken **** Shift manager informed of condition and drain valve was closed per the direction of the control room, work instructions updated by the dayshift Shift Manager to reflect the N/A condition called out in section 1.0, coaching provided to the technicians and supervisor by the Shift Manager, Technicians involved benched per the direction of PGM and MM. Recovery: work request to be made to open the check vavle via the direction of ISP-EFC-B104 section 7.10.29 and the concurrence from the OCC and Shift Manager. | 02-00-PI-EFC-X78B
387721 | CR | 20181211 |  | 4 | eSOMS late entries for Maintenance 12/3 - 12/9/18 |  |  |  | N | NO | <D> **** Detailed Description **** Maintenance had three instances last week of time being entered in eSOMS after the start time of the hours being worked. One was by a FIN supervisor, one was by the night shift supervisor, and one was by the weekend supervisor. <I> **** Actions Taken **** I will be discussing the particulars of the late entries with the Maintenance Manager.
387722 | CR | 20181211 | CAQ | C | Drawings not updated following component replacement |  |  |  | N | NO | <D> **** Detailed Description **** Drawing E528-42A has not been updated to show the original ITE starter was replaced by a NLI unit per EC 12162 and WO 02036323. Recommend action to engineering to update drawing E528-42A and ensure other drawings related to WMA -42-8F2C were properly updated.
387725 | CR | 20181211 | CAQ | C | RDCS INOP P603-A7-2/8 alarm. unable to reset. | Y | Y |  | N | YES | <D> **** Detailed Description **** RDCS INOP P603-A7-2/8 alarm with RPIS or DMM inop alarm P603-A7-1/7. Whiole resetting per the ARP SCRAM light for rod 50-19 illuminated and RDCS remained inop. Scram valve for 50-19 verified shut. <I> **** Actions Taken **** Entered ABN-ROD and expanding team. | 02-00-CRD-DMM-1
387727 | CR | 20181211 | CAQ | D | Accumulator trouble alarm | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-3451 low nitrogen pressure caused an accumulator trouble alarm. <I> **** Actions Taken **** followed ARP | 02-00-CRD-HCU-3451
387729 | CR | 20181211 |  | 3 | TMU-V-18C issues | N | N |  | N | YES | <D> **** Detailed Description **** 1. When starting TMU-P-1C, TMU-V-18C was warm to the touch, and TMU-FIS-5C indicated 4 gpm flow prior to TMU-V-18C control switch being taken to open. There was no change in flow after the control switch was taken to open. 2. After TMU-P-1C was started, TMU-V-18C solenoid de -energized but TMU-FIS-5C still indicated ~2.5 gpm flow. With CRS direction and Engineering concurrence, TMU-V-32C was shut and TMU-FIS-5C was shown at 0 gpm. When TMU-V-32C was reopened, indicated lube water flow went back up to ~2.5 gpm. It appears that TMU-V-18C is not fully shut when de-energized. <I> **** Actions Taken **** Informed MCR. Wrote CR. <N> The excessive packing leak noted in 388043 is likely due, in part, to the leakage past TMU-V-18C described in this CR. | 02-00-TMU-V-18C
387730 | CR | 20181211 |  | 4 | PPC-COMP-8715 Error | N | N |  | N | YES | <D> **** Detailed Description **** The error light on PPC-COMP-8715 is currently lit. TDAS is currently being used as the primary computer system. Request Computer Engineering investigate and resolve the error so that PPC will be available should it becme necessary to swap primary computer systems. <I> **** Actions Taken **** Notiifed CRS. | 02-00-PPC-COMP-8715
387731 | CR | 20181211 |  | 4 | Wrong type of fuse installed | N | N |  | N | YES | <D> **** Detailed Description **** During a recent motor starter inspection, the control power fuse was replaced with an incorrect type of fuse. Per drawing E528-40B, the control power fuse of REA-42-8CB5C (REA-FN-15 starter) is to be a type ATM, A6Y, F60C, or KTK fuse with a 3 amp rating. According to the fuse log entry, the craft replaced an ATM-3 fuse with a FNQ-R-3. While the installed fuse has the correct rating, the FNQ is a time delay fuse while the ATM is a fast blow. Recommend replacing the control power fuse with the correct type at earliest opportunity. | 02-00-REA-42-8CB5C
387732 | CR | 20181211 |  | 4 | Two different cable numbers and one CAT ID. |  |  |  | N | NO | <D> **** Detailed Description **** Elevator package # 02092492-27 had a MR# for cable G2. When receivng the cable the CAT ID # 20198 was for a different cable which was for a G2A cable. <I> **** Actions Taken **** Contacted planning and engineering to get permission paperwork to use the cable received. <N> recommend Cat . This is a no issue it is common to have more than one part number under one CID. The requester should be looking at the limitation on us and follow them so the Part number issued can be used. this was also confirmed with Procurement Engineering
387733 | CR | 20181211 | CAQ | C | Drawing not updated |  |  |  | N | NO | <D> **** Detailed Description **** Drawing E528-25B was not updated after RHR-42-7BA7B, starter for RHR-FCV-64A, was replaced with a NLI unit. The NLI starters typically require a different type of control power fuse. This information has not been updated. Recommend engineering update E528-24B and ensure other drawings associated with the starter replacement have been updated with correct information. | 02-00-RHR-42-7BA7B,02-00-RHR-FCV-64A
387734 | CR | 20181211 |  | 4 | Vibration noted on DEH-AC-IR/TRIP blower wheel | N | N |  | N | YES | <D> **** Detailed Description **** During performance of PM WO 02132103-01, vibration was noted on the blower wheel and that the cooling coils will require using water on the next cleaning vs. air / brush with a vacuum. Both these conditions require a clearance order to be in place to perform maintenance. <I> **** Actions Taken **** Craft notified Supervisor of this issue <N> **** Equipment Description **** T501 D2/6.1 | 02-00-DEH-AC-IR/TRIP
387735 | CR | 20181211 |  | 3 | Chemistry sample results after refill of RHR-A | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** Samples were collected from the new high point vents in RHR-A following refill of the system. Analyses included pH, Conductivity, Insoluble Iron and Soluble Iron. The results are as follows: RHR-V-922; pH 5.29, Conductivity 10.6 uS/cm, Insoluble Iron 27.5 ppb, Soluble Iron 203 ppb RHR-V-923; pH 5.53, conductivity 2.73 uS/cm, Insoluble Iron 275 ppb, Soluble Iron 13.9 ppb RHR-V-924; pH 5.83, Conductivity 1.15 uS/cm, Insoluble Iron 7,180 ppb, Soluble Iron 45.3 ppb RHR-V-924 resample after 4.5 hours; pH 5.80, Conductivity 1.05 uS/cm, Insoluble Iron 1,272 ppb, Soluble Iron 62.6 ppb Based on the significant amount of Insoluble Iron remaining in the RHR-A system, especially at RHR-V-924, it would be prudent to plan additional flushing activities prior to R24 or at least before placing RHR-A in shutdown cooling. <I> **** Actions Taken **** Discussed with System Engineering and Chemistry Management | 02-00-RHR-V-922,02-00-RHR-V-923,02-00-RHR-V-924
387739 | CR | 20181211 |  | 3 | PPM 18.1.34 Minor Rev 01 Editorial Notes |  |  |  | N | YES | <D> **** Detailed Description **** PPM 18.1.34 was under review for RHR-P-2A pump and motor testing. In review, one finds that Attachment 9.1 and 9.2 footer stated "RHR-P-2B Pump Data Sheet". Whereas the header and procedure cell read " RHR-P-2A Preserve Test and Pump Data Sheet. <I> **** Actions Taken **** 1. Notified the EOC Manager 2. Contacted the Responsible Procedure Owner, Tech Servs - Engineering Programs supervisor. 3. Reviewed what actions to be taken as to pen and ink with initial/date or a revision. 4. Direction given was to pen and ink with intial/date on the procedure when preparing for the testing at the PJB. 5. Initiated this CR/AR to document the finding and to make the formal corrections as requried. | 02-00-RHR-P-2A
387740 | CR | 20181212 | CAQ | D | RHR-42-7BA3B (RHR-V-4A) difficult to operate | Y | Y |  | N | YES | <D> **** Detailed Description **** RHR-42-7BA3B (RHR-V-4A disconnect) was being cycled to support Voltage checks. RHR-42-7BA3B is currently Caution Tagged OFF to support PCIV specs. The disconnect operated normally going to the ON position but was very stiff going back to the OFF position. Additionally, the door interlock mechanism was not operating properly, with the disconnect handle in the OFF position (disconnect door would not open). With CRS permission, an adjustment to the operating rod was attempted; however, the operating rod was already fully inserted. Electricians believe the operating rod is longer than it should be, causing the abnormal operation of the disconnect. They recommend the operating rod that connects the door handle to the actual circuit breaker be cut to the correct size, to allow proper operation. RHR -42-7BA3B was cycled multiple times to verify it will operate, and left in the OFF position, per the Caution Tag. <I> **** Actions Taken **** Informed MCR. Attempted adjustment. Verified that although operation is abnormal, the disconnect does operate. <N> **** Equipment Description **** RX 522 MC-7BA | 02-00-RHR-42-7BA3B
387741 | CR | 20181212 |  | 3 | Condensate Booster Pump suction pressure drop | N | N |  | N | YES | <C> This CR was reopened at the request of engineering. <D> **** Detailed Description **** Condensate Booster Pump suction pressure was steady during the #2 heaters (all three) and #1A heaters being placed in service at 97 psig. At approximately the time the dump valve for the #1B heater was closed Booster pump suction pressure dropped and remained steady at 90 psig. MCR was not able to explain why this happened. <I> **** Actions Taken **** Informed the CRS/SM. Adjusted COND-DPIC-5 open 5% and raised Condensate Booster Pump suction pressure back to 98 psig. Wrote CR for evaluation. | 02-00-COND-DPIC-5
387743 | CR | 20181212 |  | 4 | Camara 21 on TB471 not functioning | N | N |  | N | YES | <D> **** Detailed Description **** Remote monitoring camera #21 on TB471 is not working. <I> **** Actions Taken **** informed MCR <N> **** Equipment Description **** TB 471
387744 | CR | 20181212 |  | 4 | Replace ASD glycol filters | N | N |  | N | YES | <D> **** Detailed Description **** Trend data shows drop in resistivity. Need to replace filters. GY-F-10A2 is approximately 5.0 mohms <I> **** Actions Taken **** monitoring trend data <N> **** Equipment Description **** ASD building | 02-00-GY-F-10A1,02-00-GY-F-10A2,02-00-GY-F-10B1,02-00-GY-F-10B2
387746 | CR | 20181212 | CAQ | C | Excessive Specification Deviations Against Spec 15209 |  |  |  | N | NO | <C> CR changed to CAQ "C" by CAP supervision due to CAQ CR 399263 being trended to it. The assignment has been changed from an ASGN to CA type. <D> **** Detailed Description **** This is a document only issue and does not affect proper function of plant equipment. Procurement Specification 15209 Revision 4 titled, â€œMOTOR CONTROL CENTER REPLACEMENT DRAW OUT COMPARTMENTS, COMPONENTS, AND LOCAL STARTERS, SAFETY RELATED,â€ has 45+ open Procurement Specification Deviations (PSD) listed against the subject document revision (see screen prints EDMS). In addition, the specification has two Minor Plant Design Changes (MPDC) and one Plant Design Change (PDC) listed against it. Most of the deviations have been issued by Design Engineering in support of the NLI MCC bucket replacement project. . Having 45+ PSDs against the subject specification (analogous to having many open CMRs against one calculation) makes any interpretation of the current specification requirements, by CGS or the vendor, error likely. The last major revision (rev 004) to Procurement Specification 15209 was issued in December of 2010 when CGS was still procuring Spectrum Buckets. Recommend that Procurement Specification 15209 be revised (Revision 005) to incorporate all open changes against this document. Recommend assignment to Design Engineering or the MCC bucket replacement project as the majority stake holders for this document. <I> **** Actions Taken **** informed supervision. wrote CR. <N> Assignment 387746-01 (due date 1/3/20) is revising this procurement spec 15209.
387752 | CR | 20181212 |  | 3 | RFT-LOC-1A bump hazards identified | N | N |  | N | NO | <D> **** Detailed Description **** During performance of RFT-LOC-1A PM's, bump hazards were identified during the field walkdown / take 2. 3 of the 5 valves identified were identified on Clearance Orders D -RFT-LOC-1A -010 and D-RFT-LOC-1A -009. The other 2 were identified during the field walkdown. All 5 valves should be listed on the C/OS and these valves should also be zip tied / restrained as part of hanging the C/OS. The valves identified are RFT-V-1A, 4A, 5A, 7A and 8A. <I> **** Actions Taken **** Mechanics identified valves and SSS was contacted to restrain the valves listed above. | 02-00-RFW-LOC-1A
387753 | CR | 20181212 |  | 4 | MTE not available for As-Found. Repeat baseline testing. |  |  |  | N | NO | <D> **** Detailed Description **** MTE 0063577-02 not available for As-Found calibration. Clamp on ammeter. Repeat W/O 0128627 to obtain baseline data. Fan motors on E-TR-M4. <I> **** Actions Taken **** Wrote CR. <N> **** Equipment Description **** TRANSFORMER YARD
387756 | CR | 20181212 |  | 3 | Tightening of Main Transformer Bushings | N | N |  | N | YES | <D> **** Detailed Description **** The purpose of this CR is to document the need re-tighten the new main transformer High/low voltage bushings after they have been in-service based on vendor recommendations. This was recommended as part of the vendor O&M manual and this was not performed in R23 and it is currently not in the scope of the main transformer accessory testing in R24. Based on what is being seen in AR-CR 387680 with the E-TR -M2 bushing oil leak and after talking with the vendor we should perform this check during R24. Performing this check will ensure that the main transformers do not see the same condition as E-TR-M2 is currently seeing with oil leaks and this will potentially repair the leak being seen on E-TR-M2. This AR will generate WRs to perform this work in R24 since all of the main transformer doghouses will be open for isophase bus inspections. | 02-00-E-TR-M1,02-00-E-TR-M2,02-00-E-TR-M3
387757 | CR | 20181212 |  | 3 | Unsat surveillance | N | N |  | N | NO | <D> **** Detailed Description **** Surveillance 15.1.23 (WO 02124561) Protected Area and Warehouse Sprinkler System Testing is completed unsat. Dataglance will update asset suite as completed and it will look sat. <I> **** Actions Taken **** Talked to dataglance IS support and OPS procedure reviewer, and determined that a CR needs to be written to document the problem. The failed components are non-essential fire areas / equipment. No additional action required.
387759 | CR | 20181212 |  | 3 | Increased cycling of TMU-LCV-2A | N | N |  | N | YES | <D> **** Detailed Description **** The cycling frequency of TMU-LCV-2A has gradually increased over the past two months. In the months leading up to the increased cycling, TMU flow has typically cycled once in an eight hour period, but has gradually increased to a rate of one cycle every five hours (see EDMS for plots). The cycling of the TMU-LCV-2A can create frequent changes in head pressure, which can promote torsional fatigue failure of the TMU pump shafts, and should therefore be minimized when possible. It is recommended that TMU-LIC-2A be tuned to reduce TMU-LCV-2A cycling frequency and overshoot. Recommend an assignment to AR-SEBOP to update the IMDS of TMU-LIC-2A with the new tuning parameters when work has been completed. <N> Despite changes in TMU flow fluctation frequency the automatic controller continues to maintain CW basin level within a relatively tight band (within 2-3" of setpoint). This issue does not represent a concern with CW basin level management. | 02-00-TMU-LCV-2A,02-00-TMU-LIC-2A
387761 | CR | 20181212 |  |  | Badge expiration date issue identified in badging computer |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** While conducting our monthly five year badge expiration dates, a delta was discovered on our crystal badge report. Several badges that were replaced this year, did not update (new badge number) to the crystal report. The crystal report is updated by the badging transfer process. <I> **** Actions Taken **** Updated the issue date again in IEBS and completed our transfer process. It was verifed the badge numbers did update on our crystal report. CR written for trending purposes.
387763 | CR | 20181212 | CAQ | D | MS-RV-2c VPI zero voltage out of tolerance | N | Y |  | N | YES | <D> **** Detailed Description **** MS-RV-2c VPI zero voltage out of tolerance during performance of ISP-MS-M201. Found at -0.044 volts. Tolerance is 0.000 +/- 0.040. CR for trending. WO 02128288-01 <I> **** Actions Taken **** Notified supervision and adjusted the voltage to within tolerances per the surveillance. <N> **** Equipment Description **** W-467' | 02-00-MS-VPI-SCU/9
387764 | CR | 20181212 | CAQ | D | Constant Malfunction 20 21 | N | N |  | N | YES | <D> **** Detailed Description **** CAS received a constant malfunction on IDS 20 21 <I> **** Actions Taken **** Security conducted a walk down of the zones and found no cause for the alarm. Security comp in place, contacted plant electricians for support and generated CR/WR. | 02-00-SEC-IDS-E/S/20/21
387766 | CR | 20181212 | CAQ | D | M&TE Suspended/ Lost |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0063577 AEMC Clamp Meter- model 514 Last c/o EN Electrician 6/19/18 . Can't locate. Suspended/ Lost. EFIN EVAL: WO #02128627-01 As Found Data may not be accurate. Repeat test. Notified Electric Shop Manager. Usages #2-5 Meter was not used. DEF #6777A written. <I> **** Actions Taken **** Notiied Electric Shop Manager
387768 | CR | 20181212 | CAQ | D | Small Oil Leak on RHR-M-P/2A | Y | N |  | N | YES | <D> **** Detailed Description **** During RHR Alpha work window during the 5 minute pump run for SOP-RHR-FILL, a small oil leak was identified on the lower bearing oil fill port. Oil is leaking out of the top of the 90 degree ellbow of the threaded fitting Lower operating oil level is at the low mark of the operating range. <I> **** Actions Taken **** Had Mechanical Superviisor notifiy the Control Room Notified Supervision and the Outage Command Center | 02-00-RHR-M-P/2A
387770 | CR | 20181212 |  | 3 | GTR8000 Repeater |  |  |  | N | NO | <D> **** Detailed Description **** This CR is to document that the equipment was purchased under contract #351661 and the vendor shipped on June 6 2018, yet delivery of the equipment did not include one of the GTR8000 Repeaters as identified in the packing slips <I> **** Actions Taken **** A trace has been initiated by the vendor and Energy NW and an ongoing investigation is pending. In order to meet the implementation schedule of January 7-11, 2019 we are requesting approval to purchase a replacement GTR8000 repeater.
387771 | CR | 20181212 | CAQ | C | Shielding Work Order Instructions Not Followed |  |  |  | N | NO | <D> **** Detailed Description **** On 12/12/18 shielding was hung on a FPC line without the required clearance. This line is 4 inch line FPC(16)-1 which drains the dryer separator pit. The work order task (02112149-24) was sequenced such that a clearance order was to be hung prior to the shielding being installed, but the work instructions were not accurately followed. <I> **** Actions Taken **** Notified the shift manager, the Rad Ops Supervisor and the RMC supervisor Operations initiated actions to hand clearance order. <N> Station Stand Down was conducted on 12/13/18 (see EDMS).
387772 | CR | 20181212 |  | 4 | ASD1A/2 glycol leak observed on hex nut above 11A2 elbow | N | N |  | N | YES | <D> **** Detailed Description **** During a system walk down for observing filter replacement work, some moisture was noted around upper portion of hex nut, which is located down below coolant pump strainer and above elbow fitting of glycol pump 11A2. No drips were noticed during the walk down. Reference pictures in EDMS of this AR. Informed maintenance about this leak. No new WR is generated. Per discussion with maintenance, this leak issue will be incorporated in WR 29143954(also associated with AR387586 and AR 383144) and work order will be generated to schedule this work. <I> **** Actions Taken **** Discussed with supervisor, maintenance and notified control room. | 02-00-RRC-IMD-ASD1A/2
387773 | CR | 20181212 |  |  | RFT-LOC-1A, internal coating degraded |  |  |  | N | YES | <D> . <I> Mechanics contacted Supervisor about this issue. <N> T443 E5/9.0 (RFW PUMP ROOM "A", WEST OF TURBINE). | 02-00-RFT-LOC-1A
387774 | CR | 20181212 |  | 4 | STATE FM-Fire Protection Signs Missing |  |  |  | N | NO | <D> **** Detailed Description **** State Fire Marshal inspection found that several fire sprinkler riser rooms, fire alarm panel rooms and the Kootenai fire pump houses do not have identification signs. These room identification signs are required by the Fire Code to provide direction to the fire department during an emergency response call. Areas Identified include: 1. Kootenai Fire Pump Houses B57 and B58. 2. B186 Sprinkler Riser Room. 3. B106 Fire Alarm Control Panel Room <I> **** Actions Taken **** Label Request made for pump houses. Work Request written to install new pump house sign. Standard sprinkler riser and fire alarm sign installed in other two locations. <N> **** Equipment Description **** Kootenai Pump House B57 and B58
387775 | CR | 20181212 | CAQ | C | Incorrect image uploaded for AED EWD EWD-9E-033 |  |  |  | N | YES | <D> **** Detailed Description **** During the in-progress RHR A maintenance outage, EC DEC 17459 was implemented via WO 02103287 for replacement of RHR-M-V/24A. During implementation of the modification, it was discovered that cable leads needed to be swapped (motor initially ran backwards) and an FCR was processed to update Top-Tier AED EWD EWD-9E-033 which was subsequently rolled up into EC DEC 17459 R001. However, the image subsequently uploaded in Portal J for AED EWD EWD-9E-033 (R015) associated with EC DEC 17459 implementation was that for EC DEC 17459 R000, not that for EC DEC 17459 R001. . | 02-00-RHR-M-V/24A
387776 | CR | 20181212 |  | 4 | personal heater found on |  |  |  | N | NO | <D> **** Detailed Description **** Personal Heater found â€œonâ€ in Kootenai Bldg. office space. The individual left site 12/11/18 at the end of shift and the heater was discovered on by facilities staff the morning of 12/12/18. This does not align with ISPM-6 section 3.2.1d requiring all personal use heaters to be turned off at the end of the work shift. <I> **** Actions Taken **** Unplugged heater and Informed supervision. Coaching provided to the individual.
387777 | CR | 20181212 |  | 3 | WBC-2 Top detector HV issue |  |  |  | N | NO | <D> **** Detailed Description **** The Whole Body Counter has been experiencing issues with the MCB properties for the top detector being re-set to factory defaults. The software/hardware provider has indicated that this may be a caused by electronic component failure o the digibase module used to interface the detector with the software. If the issue has not been resolved with the last file update the unit may require the digibase component replacement. The site currently has 2 on site available to be used by another FastScan if deployed. The digibase component could be used as replacement while the in-service digibase module is being repaired. The consequence to the WBC fastscan is it may be out of service for replacement of the component and re -calibration of the detector. The down time would be expected to be less than 72 hours. <I> **** Actions Taken **** Notified RP-ops lead and RP-Support supervisor.
387780 | CR | 20181212 |  | 4 | RFT-LOC-1A, internal coating degraded | N | N |  | N | YES | <D> **** Detailed Description **** During PM maintenance, Mechanics noted internal coating of lube oil conditioner shows signs of flaking and degradation. Some parts also show signs of overheating. See attached photos in EDMS. <I> **** Actions Taken **** Mechanics contacted Supervision <N> **** Equipment Description **** T443 E5/9.0 (RFW PUMP ROOM "A", WEST OF TURBINE). | 02-00-RFT-LOC-1A
387781 | CR | 20181212 |  | 4 | FPC-FIC-15B indicating 425gpm while isolated | N | N |  | N | YES | <D> **** Detailed Description **** FPC-FIC-15B is indicating 425gpm when the inlet and outlet isolation valves are closed and FPC-DM-1A on the suppression pool. This issue was previously worked per WR 29142284 to drain the flow transmitter without lasting success. The alarm for â€œEffluent B Low Flowâ€ on FPC-CP-1 drop 3-3 is not illuminated. However when one of the two bulbs is removed the remaining bulb does glow very dimly. This light behavior does not occur with the â€œEffluent A low Flowâ€ alarm with FPC-FIC-15A reading 560gpm. Both alarms clear at 300 gpm see 4.FPC.DM drops 3-1 and 3-3. With this odd light behavior recommend investigating a possible electrical issue. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** RWCR | 02-00-FPC-FIC-15B
387782 | CR | 20181212 |  | 4 | EDR-DM-9 high D/P spikes when securing operation | N | N |  | N | YES | <D> **** Detailed Description **** DR-DM-9 D/P spikes to GT 50 psid when the stop push button is depressed and the filter is placed in hold. This issue was not resolved by the steps performed in WR 29140974 and WR 29145507. When EDR-DM-9 is returned to service after a short time on hold a loud banging water hammer like noise can be heard following opening of EDR-V-58 and subsequent lowering on d/P. Please investigate further and do not close WR/WO without performing a PMT with RWCR operator. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** RWCR | 02-00-EDR-DM-9,02-00-EDR-FC-14
387783 | CR | 20181212 |  | 4 | CW Dispersant Pump CF-P-41A not Pumping | N | N |  | N | YES | <D> **** Detailed Description **** Based on inventory trending and a drop in chemical dispersant residual, CF-P-41A is not pumping. Chemical feed pumps were switched on 12/6/18 from CF-P-42A to CF-P -41A when a tubing wall leak was found on CF-P-42A to the TSW Weir injection point - CR 387589. CW ortho-phosphate residuals are now below target point of 5.0 mg/L. Test result for 12/11/18 was 4.6 mg/L. Adequate dispersant residual is required to prevent scaling of the Main Condenser. <I> **** Actions Taken **** Chemical feed pumps were switched to CF-P-41B (new pump). Chemical injection rate was increased. If inventory trend indicates that this pump is not pumping, a request to Operations will be made to perform a manual chemical addition from TK-41. Repairing the leak on the CF-P-42 side should be made a priority to prevent having to manually add dispersant to the TSW Weir and CW System each shift. <N> **** Equipment Description **** CW System - CF-P-41A | 02-00-CF-P-41A
387784 | CR | 20181212 |  | 4 | Monthly Chemical Storage area inspection discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** The monthly inspection of Mechanical Maintenance chemical storage areas discovered the following discrepancies: Chemicals found outside of flammable liquid storage cabinet in GSB shop. <I> **** Actions Taken **** Notified appropriate personnel to resolve. All discrepancies resolved, no further action required.
387786 | CR | 20181212 |  | 3 | (2018 Heat Sink)(NRC) Surplus detail for commitment |  |  |  | N | NO | <D> **** Detailed Description **** During the 2018 Triennial Heat Sink Inspection, the NRC provided an observation regarding regulatory commitments for Generic Letter 89-13. In the commitment tracking log, a few of the commitments contained surplus detail and the station should consider cleaning up the details contained in the log. Recommend assigning this CR as a non-CAQ 3 to AR-LIC. <I> **** Actions Taken **** Discussed with inspection team and Compliance supervisor. <N> Line items in the Commitment Tracking Log for commitments that were made by Columbia in response to GL 89-13 have been revised to remove unnecessary detail. Specifically, C -10983, C-11047, C-12838, C-12840, C-12842, C-12926, C -21513, C-21514, C-21515, C-21516, C-21517, C-21518, and C -21519 were edited to remove outdated information such as references to old CRs, and revision history. No additional actions are required for this issue.
387787 | CR | 20181212 |  | 3 | (2018 Heat Sink)(NRC) Revision to DBD |  |  |  | N | NO | <D> **** Detailed Description **** During the 2018 Triennial Heat Sink Inspection, the NRC provided an observation regarding DBD 309, Design Basis Document for Standby Service Water. Specifically, page 309-34A contains a quote from an NRC response to a disputed non-cited violation. The station should consider revising the DBD to include the technical basis that supports the quote. <I> **** Actions Taken **** Discussed with inspection team and Compliance supervisor.
387788 | CR | 20181212 |  | 4 | Declared firearm at the roadblock |  |  |  | N | NO | <D> **** Detailed Description **** At 1525 a third party vendor arived at the checkpoint and declared he had a concealed firearm with a permit. the firearm and contacted Security supervision. <I> **** Actions Taken **** Security Supervision, Shift Manager, and Benton County were contacted. The vendor was denied access.
387790 | CR | 20181212 |  | 4 | STATE FM-Extension Cord and Surge Protection Problems |  |  |  | N | NO | <D> **** Detailed Description **** Annual inspection by State Fire Marshal found several issues with extension cords and surge protectors as follows: 1. B189 Firing Range: 3-way WYE plugged into extension cord 2. B189 Firing Range: Damaged Extension Cord. 3. B64 Red Cross blood drive with daisy chain power taps. 4. B64 Red Cross power tap plugged into extension cord. 5. B34 Simulator Craft Room with daisy chain surge prot. 6. B35 I&C Lab extension cord in use 7. B13 SCBA area extension cord in use. . All of these items are prohibited by ISPM-6. Individuals were coached where they were present. All items were corrected immediately or same day. <I> **** Actions Taken **** All found issues were corrected immediately or same day.
387791 | CR | 20181212 |  | 4 | STATE FM-Portable Space Heater Plugged Into Surge Protector |  |  |  | N | NO | <D> **** Detailed Description **** State Fire Marshal inspection found a portable space heater plugged into a surge protector in B26 Office 1-299. This was unplugged immediately and discussed with the area Supervisor. No further actions. This AR for tracking and trending. <I> **** Actions Taken **** Unplugged heater immediately. No further actions.
387793 | CR | 20181212 |  | 3 | EPN placards do not identify if valves are in the correct ro |  |  |  | N | NO | <D> **** Detailed Description **** Placard outside of the Tip Mezzanine and the North side pipe chase room is outdated and needs to have the valves updated to reduce searching for valves and wasting dose. RHR-V-922 is not on the list for the Tip Mezzanine room and is in the room, and RHR-V-923 is not on the list for the North Side Pipe Chase room and is in the room. These high -rad areas need to be properly identified to fix an error likely situation. <I> **** Actions Taken **** Suggest doing an extent of condition and updating signs to reflect the correct valves to minimize looking for locations in higher dose areas. Notified the main control room and my supervisor of this condition. <N> WR 29146067 written to update and replace EPN placards. Two label requests have been submitted with a need by date of 1/31/19 . FIN has agreed to install the new labels. | 02-00-R-BLDG-MISC,02-00-R-DOOR-R309,02-00-R-DOOR-R404,02-00-RHR-V-922,02-00-RHR-V-923
387794 | CR | 20181212 | CAQ | D | RHR-V-244 packing leak (pencil size stream) | Y | Y |  | N | YES | <D> **** Detailed Description **** RHR-V-244 (RHR-P-2A discharge pressure test connection isolation) was noted to have a pencil size stream packing leak, when in the OPEN position. No leakage existed while the valve was CLOSED. RHR-V-244 is a normally closed valve and only opened while obtaining test data. A small catch waa put in place to prevent the spread of contaminated water as test data was obtained for PPM 18.1.34. RHR-V-244 is located in the RHR-P-2A pump room, 422 elevation, directly off of the pump discharge piping. Note: this room is normally a High Rad Area. <I> **** Actions Taken **** Informed MCR and HP. Catch installed to direct packing leakage to floor drain. <N> **** Equipment Description **** Rx 422, directly off of RHR-P-2A discharge piping | 02-00-RHR-V-244
387795 | CR | 20181212 | CAQ | C | RHR-V-73A failed in the open position. | Y | N |  | N | YES | <D> **** Detailed Description **** While stroking RHR-V-73A per OSP-RHR/IST-Q701 step 7.2.11 valve position initially was 95% open. When the RMS was taken to Close through Stop indication went full upscale. Approximatly 1 min later placed the RMS in Stop. Approx. 5 min later a Ground on SL-71 alarm recieved with RHR out of service and BISI for MOV network power loss. Ground relay E-RLY-50N/T7/71 indicated a ground. <I> **** Actions Taken **** All valves with MCR indication were verified enerigzed. OPS 2 investigated gound and verified MC-7BB had ground. No abnormal indications or smells in MC-7BB. OPS 2 opened Disconnect for RHR-V-73A. Generated Clearance for RHR-V -74A for PCIV and Clearance for RHR-V-73A for equipment damage. OPS 2 reset ground on MC-7B, ground on MC-7BB did not clear. | 02-00-RHR-42-7BB5D,02-00-RHR-MO-73A,02-00-RHR-V-73A
387796 | CR | 20181212 | CAQ | C | PRM-SR-1 froze during rest | N | Y |  | N | YES | <D> **** Detailed Description **** During reset of PRM-SR-1 the system froze requiring downloading software and restarting the system <I> **** Actions Taken **** Informed MCR and OCC Wrote CRE | 02-00-PRM-SR-1
387797 | CR | 20181212 |  | 4 | No numbered lights lit for Turbine Vibration Monitor(repeat) | N | N |  | N | YES | <D> **** Detailed Description **** See WR 29140176 for previous occurrence. Currently there are no lit BVMS number lights when it is expected to have number 4 light lit. This previously occurred and then changed to having number 3 light lit for several consistent months. See attached photo. This CR is for trending. <I> **** Actions Taken **** Notified CRS. <N> **** Equipment Description **** MT-BLADE-VIB-MON, TB 501
387798 | CR | 20181212 |  | 4 | Lighting Very Poor in RW487 Women's Decon Room. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Lighting is Very Poor, needs to be re lamped. Can not read the Ludlum 177 Frisker. <I> **** Actions Taken **** Notified HP Lead Technician. Initiate CR <N> **** Equipment Description **** RW 487 Women's Decon Room. | 02-00-W-BLDG-MISC
387799 | CR | 20181212 | CAQ | D | RHR-M-P/2A lower bearing oil level low while running | Y | Y |  | N | YES | <D> **** Detailed Description **** RHR-M-P/2A lower motor bearing oil level is low while running. Per OSP-RHR/IST-Q702, oil level is required to be between the MIN and MAX marks while operating. Oil level was apporximately 1/8" Less Than the lower "Operating range" mark. Oil level was SAT while in standby; however, there was still margin to raise oil level and be withing band. Per OSP-RHR/IST-Q702, Standby oil level can be established "no higher than 1/4" above standstill level when the motor is cold." Please add oil to 1/4" above standstill mark once RHR-P-2A has been shutdown and reached ambient temp. Note: RHR-P-2A pump room is a High Rad Area. <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** Rx 422, RHR-P-2A room | 02-00-RHR-M-P/2A
387800 | CR | 20181213 |  | 3 | MS-PI-20B Listed in Wrong Location in PPM 9.3.1 |  |  |  | N | NO | <D> **** Detailed Description **** Step 13 of Attachment 7.1 in PPM 9.3.1, Manual Core Heat Balance, lists the location of MS-PI-20B as H13-P603. The location of MS-PI-20B is actually H13-P820 (Board-B). <I> **** Actions Taken **** Recommend Severity Level 3 to Reactor Engineering as the Procedure Sponsor to update the procedure. | 02-00-MS-PI-20B
387801 | CR | 20181213 | CAQ | D | Control Rod 26-19 moved two notches | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02111975, then taken back to complete <D> **** Detailed Description **** Control rod 26-19 moved from 00 to 04 when the withdraw button was pushed. Final intended postion was 06. The system had normal drive header pressure. <I> **** Actions Taken **** Notified CRS and reactivity manager, moved control rod to final position 06. | 02-00-CRD-HCU-2619
387802 | CR | 20181213 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0063550 Dresser Sensor- model HQS-2 15psia found OOT & adjusted to specs. Not used during Calibration cycle. DEF #006786A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only
387810 | CR | 20181213 | CAQ | D | Temp gauge fittings loose during 18.1.34 RHR-P-2A run | Y | N |  | N | NO | <D> **** Detailed Description **** During performance of 18.1.34 I&C installed a temp gauge at RHR-PI-2A. The upstream valve is RHR-V-260A and (normally closed). At step 7.3.17 operations opened RHR-V-260A to take two pressure readings and the fittings instantly leaked on the floor. Within about 10 seconds the valve was closed; a small puddle developed on the floor roughly 7-8â€ in diameter. The fitting tightness was checked, one fitting was threaded but actively loose, as in not even hand tight. Another connection was likely hand tight but came loose while trying to tighten the clearly loose connection. The data was taken again following tightening the connections, readings remained unchanged and the leakage went away. HP and the MCR were contacted. The water on the floor was deemed not contaminated by HP. This is not the first time this issue has happened. This can impact data collected and create contaminated areas. <I> **** Actions Taken **** Informed MCR and HP. <N> **** Equipment Description **** I&C installation. | 02-00-RHR-PI-2A,02-00-RHR-V-260A
387813 | CR | 20181213 | CAQ | D | OG-RIS-601B failed downscale | N | Y |  | N | YES | <D> **** Detailed Description **** OG-RIS-601B has failed downscale. OG-RIS-601A is reading 5.09E-4 and steady. OG-RIS-601B has "Loss of RM-2000 Comm" on the display. <I> **** Actions Taken **** Protected OG-RIS-601A. WR written. <N> **** Equipment Description **** RW 501. | 02-00-OG-RIS-601B,02-00-OG-SR-11B
387816 | CR | 20181213 | CAQ | D | CRD-HCU-1807 Rod Accumulator Trouble | Y | N |  | N | YES | <D> **** Detailed Description **** Received "Rod Accumulator Trouble" alarm on CRD-HCU-1807. Ops2 reports the alarm is due to water; that he has drained the water and the alarm is clear. | 02-00-CRD-HCU-1807
387817 | CR | 20181213 |  | 4 | CW Dispersant Pump CF-P-41B Not Pumping | N | N |  | N | YES | <D> **** Detailed Description **** Based on no drop in inventory overnight, CF-P-41B is not pumping. CF-P-41A was found not pumping on 12/12/18 (CR 387783). No pumps are now available on the TK-41 side. The TK-42 side is tagged due to a leak in the feed line to the TSW weir - CR 387589. This is the dispersant that prevents scaling of the main condenser. <I> **** Actions Taken **** Instruction have been sent to the Control Room to perform a manual chemical feed per the procedure. While the chemical feed systems is out, first add of 120 gals then 80 gals per shift until the pumps are confirmed back in service or Chemistry provides instructions otherwise. <N> **** Equipment Description **** CWPH - CF-P-41B | 02-00-CF-P-41B
387820 | CR | 20181213 | CAQ | D | RDCS lockup on 12/12/2018 @2309 | Y | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02138999. marked completion required box, then taken back to complete <D> **** Detailed Description **** The RDCS system engineer was contacted around midnight last night by the EOC about a RDCS lockup that was subsequently reset. Computer Point A515 shows the lockup to have occurred at 2309. No CR was written and there is no reflection of this lockup in the Control Room log or the OCC log. According to the EOC which was soon after disbanded the lockup related to rod 42-03 (supposedly similar to the lockup on 12/11/2018 â€“ ref. CR 387725). In addition, no fault map sheet was received by the system engineer as directed by the ARP (PPM 4.603.A7). <I> **** Actions Taken **** Discussed with dayshift CRS. They had not received any turn over on another lockup. | 02-00-CRD-HCU-4203,02-00-CRD-RDCC-1
387821 | CR | 20181213 | CAQ | D | Keyswitch for OG-AY-12B not working correctly | N | Y |  | N | YES | <D> **** Detailed Description **** During performance of ISP-OG-A302, WO 02136575-01, the keylock switch for OG-AY-12B would not smoothly operate and required eccesive effort to remove the key. Keylock switch will be replaced by WO 02136585-04 and PMT will be Performed by WO 02136585-05 to perform a partial ISP-OG -A301 following replacement of switch <I> **** Actions Taken **** Wrote CR to document. Work will be performed by WO 02136585-04 and 05 | 02-00-OG-AY-12B
387822 | CR | 20181213 |  | 4 | Trending - Coaching provided for using red duct over opening |  |  |  | N | NO | <D> **** Detailed Description **** During performance of W.O. 02117218-64 Cut hole in term box red duct tape was used to cover the top of the motor lead box when the plate having a 4 inch hole cut into it was removed. Individuals coached by supervisor on correct methods and information verified in 10.1.13. Component Manager was informed. <I> **** Actions Taken **** CR generated for trending per direction, no further action required.
387823 | CR | 20181213 | CAQ | D | Cable 1SM7-0060 train radius less than the requirement | Y | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02137241, marked completion required box, then taken back to complete <D> **** Detailed Description **** CR 387697 documented cable 1SM7-0060 was less than the requirement. This was not repaired during the RHR-A outage, so this CR documents the OBDN condition per PPM 1.3.66. <I> **** Actions Taken **** EC 17511 was completed to evaluate the existing condition and determined that adequate margin exists with the existing bend radius. | 02-00-RHR-M-P/2A,02-00-RHR-P-2A
387824 | CR | 20181213 |  | 3 | Concerns with HVAC lines for MT-ELEV-4 |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** This CR is being written to address the concerns that the HVAC mechanics have with the construction and potential functionality of the HVAC lines that were ran for the MT -ELEV-4 machine room AC units. Attached to the EDMS are concerns and photos. This is to document the concerns prior to it being turned over to maintenance following testing. <I> **** Actions Taken **** CR generated for documentation <N> **** Equipment Description **** not currently an issue but has the potential based upon the concerns documented. . FCR EC12277R005A issued to allow installation of appropriate fittings (brazed, soldered, or flared) to replace the compression type fittings (Swagelok) and to reduce the number of bends per each refrigerant line (no more than 15). . | 02-00-MT-ELEV-4,02-00-W-BLDG-MISC
387825 | CR | 20181213 | CAQ | C | (2018 Heat Sink) (NRC) Evaluate SW Sediment Sampling Method |  |  |  | N | NO | <D> **** Detailed Description **** During the 2018 Triennial Heat Sink Inspection, The NRC provided an observation regarding if the method in which we currently gather sediment samples from the Standby Service Water Spray Ponds is adequate in detecting potential for clams. Recommend re-evaluate whether the method to gather sediment from the spray ponds can be enhanced to better identify any potential for the presence of clams within the spray ponds. AR 384628-01 is still open to fully evaluate the clams that were found in Spray Pond B from divers during the pond dredging. <I> **** Actions Taken **** Discussed with Licensing and Supervisor.
387826 | CR | 20181213 |  | 3 | (QA) Fire Brigade Pre-Fire Plans remain out-of-date |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Printed Pre-Fire Plans (PFP) located in the Turbine Building 441 fire brigade turn-out room are not the current revision and are out-of-date. This is a repeat issue previously identified by Quality in July 2018 (AR-CR 382815). These PFPs are used by the Columbia Fire Brigade and Hanford Fire Department when responding to a fire at Columbia Generating Station. Out-of-date PFPs can lead to untimely or ineffective firefighting strategies. Factual Basis: â€¢ PPM 1.3.10, Plant Fire Protection Program Implementation, states â€œPre-Fire Plans for fighting fires in specific areas of the plant shall be available for FB and Hanford Fire Department use.â€ â€¢ An unlabeled binder in the fire brigade turn-out room contains 18 Pre-Fire Plans, all of them out-of-date. The versions currently in the binder are the same versions observed in July 2018. See EDMS in AR 382815 for details. Insights: â€¢ An assignment to update pre-fire plans in the fire brigade turn-out room was extended 3 times, currently due 12/20/18 (AS 382815-01). The plant Fire Marshall stated that many pre-fire plans were updated recently and he expects to meet the current due date. â€¢ There is currently no requirement or defined method to ensure that printed PFPs in the fire brigade turn-out room remain current. <I> **** Actions Taken **** This issue is considered a Deficiency identified during Quality continuous monitoring activities. <N> **** Equipment Description **** N/A
387831 | CR | 20181213 |  | 4 | PI accessible in shared regions of SharePoint |  |  |  | N | NO | <D> **** Detailed Description **** On 12/13/2018, during a search in SharePoint IS staff noticed documentation on an IS SharePoint team site that included Personal Information (SSN). This documentation was immediately removed. A preliminary extent of condition review was performed and 1 additional form was found that contained the same information. IS staff notified the affected department supervision about the additional FORM and requested removal of the documentation. This documentation is also being reviewed and removed. <I> **** Actions Taken **** Please assign this CR to ITMGMT as a NCAQ Severity 4 All actions have been taken.
387832 | CR | 20181213 |  | 4 | Damaged flex for RFT-M-LOC/1A | N | N |  | N | YES | <D> **** Detailed Description **** Two sections of FLex for RFT-M-LOC/1A damaged. One has the seal tight outer coating missing. The other has the seal tight outer coating missing and the metalic flex is split. The damage on both is near mid flex run near a clamp securing the flex to the skids unistrut. <I> **** Actions Taken **** Generated C.R. when mechanics working on 02109746-01 informed the electrical shop. Electrical Component Manager informed. | 02-00-RFT-M-LOC/1A
387833 | CR | 20181213 | CAQ | B | RCIC-42-S21A/5C Tripped on thermal overload | Y | N |  | N | YES | <C> Risk: Medium Cause: Unclear/complex Grade "B" with investigation template required. <D> **** Detailed Description **** RCIC-42-S21A/5C supplies RCIC-V-19, RCIC-P-1 min flow valve. During performance of OSP-RCIC/IST-Q701 step 7.2.80 the MOV NETWORK PWR LOSS/OL flickered in/out at least once and then lit and stayed in and light indication for RCIC -V19 was lost. Operator locally checked RCIC-42-S21A/5C, noted that it was closed and then reset the overloads. Upon resetting the overloads, the valveâ€™s light indication restored and the valve went shut. <N> This is an MRule failure of a Safety Related and MSPI component. Direct cause if opening of the Thermal Overloads (TOL) it is unclear at this time why the TOLs opened. . This CR screens as a Severity "B" with an EQIT. | 02-00-RCIC-42-S21A5C,02-00-RCIC-V-19
387835 | CR | 20181213 |  | 3 | Unsuccessful post-training evaluation TREQ 17-0074 |  |  |  | N | NO | <D> **** Detailed Description **** TREQ 17-0074 PTE success criteria not met for vibration monitoring. See "PTE Results" tab of TREQ for specifics. IAW TDI-04, analysis of remaining performance gap and consideration of traniing and non-training solutions to be completed. <I> **** Actions Taken **** Initiated CR. Notified Training management. Recommend Severity 3 owed to AR-TRNMT.
387836 | CR | 20181213 |  | 4 | 437'RW desk phone (x2546) is in-operable. |  |  |  | N | YES | <D> **** Detailed Description **** 437â€™RW desk phone (x2546) is in-operable: no dial-tone and ambient sound is amplified and transmitted through the earpiece. <I> **** Actions Taken **** Notified E&RP Manager, annotated on weekly inspection form, initiated CR/WR. <N> **** Equipment Description **** 437'RW Desk Phone | 02-00-W-BLDG-MISC
387839 | CR | 20181213 | CAQ | C | DCW valve's field configuration does not match Asset Suite | Y | N |  | N | NO | <D> **** Detailed Description **** Documentation and Asset Suite information does not match the current field configuration for the following valves: DCW-V-8A1, 8A2, 8B1 & 8B2. CR 00379390 initially identified this issue, stating that the valves that are installed in the field are 1â€ ball valves and not Borg Warner model #76700 1â€ gate valves. While researching CR 00379390 it was discovered that these valves were changed from gate valves to ball valves on the flow diagram by BDC 55-0371-0A, in 1988. The DCW system is a safety-related QC I, seismic 1, B31.1 system. The valves have the passive safety function of pressure integrity. Despite the DCW system being safety-related QC 1 and seismic 1, during investigation no documentation was located for the installed valves that would identify the valves approved as QC 1. Currently as installed in the field, valves DCW-V-8A1, 8A2 and 8B2 are PBM (Pittsburg Brass Manufacturing) SP 14 B1 bronze body ball valves. According to what is written on the valve handle for the above valves, they are rated for 400 psi. Meanwhile DCW-V-8B1 is installed as a NIBCO 590 or 595 series bronze body ball valve and these valves also have a pressure rating of 400 psi. This is important because these valves form part of the pressure boundary for the DCW reservoir tanks which have a pressure rating of 7 psi. Because of their small compact design, the valves are considered as strong as or stronger than the attached pipe per the evaluation in QID 800800-01. The ball valves were seismically qualified in QID 800800-01 This is a legacy documentation issue only and will not have any impact on the ability of the valve to maintain its pressure integrity. This is because the valves have been seismically qualified in AED QID 800800-01 and are stronger than the pipe to which they are attached (QID 800800-01). Therefore, these valves are fully capable of performing their design function of pressure integrity. Recommend Severity level C and assign to Design Engineering. <I> **** Actions Taken **** Notified my supervisor, manager and the control room
387840 | CR | 20181213 | CAQ | C | Use of Loctite 5772 instead of Teflon Tape on CRD-HCUs | Y | N |  | N | YES | <D> **** Detailed Description **** Maintenance has been using Loctite 5772 on threaded gas connections on the CRD HCUs. This is different than the OEM recommendation to use Teflon tape on these connections. See WO 01180556, 02015727, 02034468, 02062639, 02083963. Example location is on the bottom of the nitrogen tank pipe thread. Per GE Drawing 731E947 this joint uses Teflon tape. There are likely other locations that have used Loctite, but WO history is not adequate to determine for sure. LOCTITE 5772 is allowed for use on stainless steel and is an approved thread sealant. The manufacturer recommends it for use under 300 psi in gas systems. The nitrogen system is over 300 psi, but these joints have not leaked and it is not a pressure integrity issue, since the joints are threaded connections. This is a non-conformance (not IAW drawing). Since the N2 accumulators maintain pressure there should be no impact on the function of the HCU with Loctite instead of Teflon tape. | 02-00-CRD-HCU-0231,02-00-CRD-HCU-1031,02-00-CRD-HCU-2203,02-00-CRD-HCU-2255,02-00-CRD-HCU-4203
387841 | CR | 20181213 |  | 3 | DES-4-7 / DES-4-12 process for CCER revisions |  |  |  | N | NO | <D> **** Detailed Description **** Per conversation with Technical Services personnel (i.e., the sponsor for PPI ENG DES-4-7), the existing DES-4-7 / DES-4-12 process for CCER revisions and superseding CCERs needs to direct adding the affected CCER (AED CER CXX-XXXX) to the ADL listing for the EC type EDB being processed. Please assign to the DES-4-7 sponsor for resolution. . <N> This issue was noted while processing EC EDB 17507.
387842 | CR | 20181213 |  | 4 | SAM 12 Display Failure |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** SAM 12, HP-EQ-42712, display has failed. Monitor still functions and pass / fail lights do illuminate but the display is blank. Display should be repaired as soon as possible. <I> **** Actions Taken **** Initiated CR / WR and notified HP supervision. <N> **** Equipment Description **** HP-EQ-42712 outside of the Main Control Room
387843 | CR | 20181213 |  | 3 | Error in drawing EWD-69I-011 Rev 8 |  |  |  | N | NO | <D> **** Detailed Description **** While walking down WO# 02136717-01 an error was found in drawing EWD-69I-011 Rev8. E-CP-H13/P894 TERM CAB TCG1 should read BAY B not BAY F. <I> **** Actions Taken **** Informed supervisor and wrote CR. <N> This CR was cancelled and reopend in order to unprotect the description. The title was also changed. Instead of "EWD -691-011" it now reads "EWD-69I-011.
387844 | CR | 20181214 |  | 3 | CN-PCV-2 (CN-TK-1 pressure reducing valve) control issues |  |  |  | N | YES | <D> **** Detailed Description **** CN-PCV-2 historically has issues maintaining CN-TK-1 pressure, due to severe ice buildup in the winter months [reference AR 374628 (2017), 321856 (2015), 301678 (2014)]. AR Eval 374653 was completed in 2017 and approved the installation of heat lamps and heat tape around CN-PCV-1 and 2. Recommend we take advantage of this lull in the harsh winter weather and establish these comp-measures once again, before the severe icing begins. Note: failure to maintain CN-TK-1 pressure in band can result in an unplanned plant Shutdown due to Closure of Inboard MSIVs. Additionally, this comp measure should be incorporated into SOP-COLDWEATHER-OPS. The installation of this comp -measure should occur every winter. CN-PCV-2 is not having pressure control issues at this time. This AR/WR written in an attempt to be proactive, in regards to known equipment issues that could cause a plant transient. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** CN-TK-1 skid | 02-00-CN-PCV-2
387849 | CR | 20181214 | CAQ | C | RRC pump 1B Stator temperature variation | Y | N |  | N | YES | <D> **** Detailed Description **** On 12-14-18 approximately 0240, shortly after pulling 2 control rods 1 notch each for rod line maintenance RRC-P-1B stator temperatures for all three phases had cyclic temperature change swings recorded on RRC-TRS-601. This occurred concurrently with slightly higher than normal bi -stable flow in the core. B Motor Stator A phase point 17 had the lowest cyclic temperature swings of 131F to 136F, B Motor Stator B phase point 18 had the highest temperature swings of 128F to 142F, and B Motor Stator C phase point 19 had a temperature swing of 127F to 135F. Scrolling back through the trend history there was a similar occurrence around 2200 on 12-13-18 as the next most recent, a handful of other similar occurrences scrolling back to 11/20/18 on RRC-TRS-601 with variable durations but similar temperature swings. This doesnâ€™t appear to have any immediate impact to the operation of RRC-P-1B. The RRC-P-1A did not have these same indications. Attached picture in EDMS. <I> **** Actions Taken **** Informed MCR | 02-00-RRC-P-1B
387850 | CR | 20181214 |  | 4 | TR-N1 control power transfer relay test issue | N | N |  | N | YES | <D> **** Detailed Description **** When performing model work order #01172150 task #01, the 83E alarm is not received and the local amber alarm light is not illuminated during Step 4.5.2. The Control Room does not receive the alarm for XFMR TR-N1 Trouble as required for Step 4.6.1. There may be a problem with E -RLY-83/TRN1 not always functioning as required to bring in the local alarm light and the annunciator in the Control Room. The power transfer switch sounds and appears to be working as it should, it is just the alarms are not coming in as they should. <I> **** Actions Taken **** informed Shift Supervision <N> **** Equipment Description **** TR-N1 transfromer | 02-00-E-RLY-83/TRN1
387851 | CR | 20181214 |  | 3 | 10.2.93 need changes |  |  |  | N | NO | <D> **** Detailed Description **** 10.2.93 step 7.7.1 note and attachment 9.2 , Different number of pumps per cu. in. of grease , With same model 500 alemite grease gun <N> An assignment has been made within the Maint. Procedure revision data base. No Procedure revision assignment is needed under this AR due to the creation of this assigment.
387852 | CR | 20181214 |  | 3 | PPM 12.14.10 needs enhancement |  |  |  | N | NO | <D> **** Detailed Description **** PPM 12.14.10 needs enhancement to allow for the operator and/or chemistry technician to operate the Service Building Chiller and or Heater pumps for sampling and chemical addition. The pumps operate in a cyclic manner during seasonal changes, but are needed as the mode of force for sampling or chemical addition.This could be accomplished by adjusting temperature set points or moving the pump switch from the auto position to the on position. A note should also be added to ensure that a pump is verified running <I> **** Actions Taken **** Wrote CR
387853 | CR | 20181214 |  | 3 | REA-FN-1A Precautions & limitations not clear. |  |  |  | N | NO | <D> **** Detailed Description **** working WO# 02105316-01 REA-FN-1A Precautions & limitations 2.3 Although unlikely due to Fan discharge Damper REA-AD-1A being closed, Removal and Reinstallation of the Fan/Duct access cover may affect Reactor Building (RB) Differential Pressure (DP). It is vital that this be coordinated with Operations due to the possibility of momentarily exceeding the RB DP limit. Operations should enter the applicable T .S. LCO as required. This should be a sign off step in the worl steps.
387854 | CR | 20181214 |  | 4 | NRC Identified - SW PH A 4 of 8 overhead lights are out | N | N |  | N | YES | <D> **** Detailed Description **** During a walkdown, the NRC informed the MCR that about 4 of 8 overhead lights in the SW A PH are not lit - all lights should be on in the SW pumphouse. <I> Non-essential lighting. <N> **** Equipment Description **** Lighting in Service Water A Pump House.
387855 | CR | 20181214 | CAQ | D | SW-P-1A lower bearing oil level is 1/16â€ below standstill ma | Y | N |  | N | YES | <D> **** Detailed Description **** Need to add oil to SW-P-1A due to the oil level is currently 1/16â€ below the Stand-Still or Standby mark. <I> **** Actions Taken **** informed CRS | 02-00-SW-P-1A
387856 | CR | 20181214 |  | 4 | Outdoor GFI outlet at SW-POND-B keeps tripping | N | N |  | N | NO | <D> **** Detailed Description **** The outdoor GFI protected ac outlet at SW-POND-B keeps tripping. The Cold-Weather OPS water mixer required for pond freezing protection is plugged into this outlet. Need to determine the cause of the problem; the outlet needs replaced, the heavy-duty extension cord needs replaced, the mixer needs to be replaced or a combination of everything. <N> **** Equipment Description **** SW-POND-B GFI protected outlet
387857 | CR | 20181214 |  | 3 | STATE FM-Facility Emergency Generator Annual Oil Change |  |  |  | N | NO | <D> **** Detailed Description **** State Fire Marshal review of the Facility (non-Power Block) emergency diesel generator maintenance finds that the annual or 50 hour run time oil change is not being performed. The NFPA 110 criteria is required to be followed by the International Fire Code, 2015 edition, Section 604.4. This affects the diesel generators for Building 25, 34, and the two in Richland for B68 and B81. . See AR 387634 for deficient annual fuel testing.
387858 | CR | 20181214 |  | 4 | STATE FM-B34 Fire Door Unauthorized Modifications Found | N | N |  | N | NO | <D> **** Detailed Description **** State Fire Marshal inspection found several fire doors in Koottenai, B34 where a mirror or smoked film has been added to the fire rated window for several classrooms . This is an unauthorized modification to the fire door glazing material and must be removed. Includes classroom 138, 120 and Simulator 235 where paper or cardboard has been adhered to the glass. Work Request written to remove this material from the glass. <N> **** Equipment Description **** Kootenai Building 34
387859 | CR | 20181214 |  | 3 | STATE FM-B189 Excessive Travel Distance to Exit |  |  |  | N | NO | <D> **** Detailed Description **** State Fire Marshal inspection of the Security Firing Range in Building 189 observed that the travel distance from the North end to the nearest exit exceeds the allowable maximum. Review of the International Fire Code 2015 edition indicates that maximum allowed exit access travel distance is 200 feet. It is about 300 feet to reach the West side double doors that have a required exit sign. A letter from MEIR Architects justifying the deviation was presented to Fire Protection on Feb 5, 2018, but this letter needs to be submitted to EFSEC or State Fire Marshal for a variance. This AR needs to be assigned to Facilities to evaluate why this condition was allowed and approved by the third party Plans reviewer without further variance request. <I> **** Actions Taken **** MEIER letter in EDMS
387860 | CR | 20181214 |  | 4 | Overhead light prevented hanging of clearance order. |  |  |  | N | YES | <D> **** Detailed Description **** Attempted to hang tags inside TB-R463 located in MC-7BB room NW corner above light fixture. The door could not be fully opened to to interferance with lighting fixture. This light does not move or sway and is fixed in place. Temporary removal of this light or alteration of how light is fixed is needed to safely access TB-R463. Clearance orders affected: C-RHR-V-73A-003A & C-RHR-V-73A-002A. <I> **** Actions Taken **** Informed MCR & SSS. Did not hang tags. | 02-00-E-TB-R463
387861 | CR | 20181214 |  | 4 | STATE FM-Facility Buildings have fire sprinkler deficiencies | N | N |  | N | YES | <D> **** Detailed Description **** State Fire Marshal inspection found fire sprinkler deficiencies that need correction. All items are classified as minor and do not impair fire sprinkler sytem operation. Work requests written to correct. This AR could be closed and the WR/WO work control process will ensure completion. <I> non-essential fire systems <N> **** Equipment Description **** Various Facility Buildings
387862 | CR | 20181214 |  | 4 | Increase Setpoint of HHW-RV-51 | N | N |  | N | YES | <D> **** Detailed Description **** HHW-RV-51 is lifting this issue was previously evaluated per AR Eval 11584 and the relief valve setpoint was not increased. This issue drains water from the system causing a loss of system corrosion inhibitor and a constant drainage to the floor drain system. Evaluate setting this relief to 40 psig or higher to ensure normal process pressures do not cause a premature lift. See AR EVAL 11584 for additional details. Note SHHW-P-51A/B run intermittently this issue should be observed with a pump running. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** SB Basement | 02-00-HHW-RV-51
387863 | CR | 20181214 | CAQ | C | DO-TK-3 and DO-TK-7 Min Fuel Oil Level Evaluation | N | Y |  | N | NO | <D> **** Detailed Description **** Facilities has a weekly PM to check level in DO-TK-3 and DO-TK-7 and fill if below the level listed in their PM. The level in the PM for DO-TK-3 to prompt filling of the tank is 180 gallons. This is also the minimum level required for B5B. Please evaluate the action levels for the facilities PM to meet OSP-INST-H101 log requirements. <I> **** Actions Taken **** informed Supervision
387864 | CR | 20181214 | CAQ | D | IDS 9&10 Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** IDS 9&10 Malfunction. <I> **** Actions Taken **** Compensatory measure put into place and a walkdown of zones completed. | 02-00-SEC-IDS-E/S/9/10
387865 | CR | 20181215 |  | 4 | AIM Video not functioning as intended | N | N |  | N | YES | <D> **** Detailed Description **** The AIM Video System in CAS and SAS is not functioning as intended. Please call Security at x2185 for more details. <I> **** Actions Taken **** Generated CR/WR | 02-00-SEC-SOFT-AIM
387866 | CR | 20181215 |  | 4 | Recieved 4.602.A5 4-7 RWCU PUMP A Trouble | N | N |  | N | YES | <D> **** Detailed Description **** Recieved 4.602.A5 4-7 RWCU PUMP A Trouble. All RWCU parameters look normal in the MCR. OPS2 reports low purge flow alarm illuminated in the field. I & C support necessary to correct flow. <I> **** Actions Taken **** Followed applicable ARP. | 02-00-RWCU-P-1A
387867 | CR | 20181215 | CAQ | D | FDR-P-17 trip | N | N |  | N | YES | <D> **** Detailed Description **** during the first drain step of the BW procedure from the normal hold condition (5.3.8 a) the hold pump tripped off. this occured early. it should have happened several steps later during 5.3.8 b. i performed a second BW on FDR-FU-19 and during this process from the same hold condition start the hold pump tripped off on the proper step 5.3.8 b. <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-FDR-P-17
387879 | CR | 20181215 | CAQ | D | CRD-HCU-1823 Accumulator alarm | Y | N |  | N | YES | <C> CR was reopened in order to add another cross reference -29146138 <D> **** Detailed Description **** CRD-HCU-1823 high water level. <I> **** Actions Taken **** OPS 2 cleared alarm. | 02-00-CRD-HCU-1823
387880 | CR | 20181215 | CAQ | D | Accumulator alarm on CRD-HCU-1823. | Y | N |  | N | NO | <C> CR reopened to cross reference additional CR 387879 and WR 29146111, then taken back to complete <D> **** Detailed Description **** Recieved an Accumulator alarm on CRD-HCU-1823. This CR is to support monitoring the CRD system.
387881 | CR | 20181215 | CAQ | D | Rod Accumulator Trouble Alarm for CRD-HCU-3459 | Y | N |  | N | NO | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-3459 was due to high water level.
387882 | CR | 20181215 |  | 4 | MS-V-115B lost power while stroking closed. | N | N |  | N | YES | <D> **** Detailed Description **** MS-V-115B was cycled to identify the steam leak in WR 29141905. The leak is from the valve packing, however while closing to reisolate the leak, it appears the mov fuses cleared. All indication was lost right after dual indication was observed , and the leak remains. Attempted to reset overloads with no success. Recommending checking/replacing fuses. If unsuccessful, manually close the valve to isolate the leak. <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** OG Preheater room | 02-00-MS-MO-115B
387883 | CR | 20181215 | CAQ | D | alarms on CRD-HCU-5823 and 3803 during scram time testing | Y | N |  | N | NO | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-5823 and 3803 during scram time testing.. Dispatched OPS-2 to investigate. <N> Alarms on both CRD-HCU-5823 and CRD-HCU-3803 were due to high moisture level. Ops 2 drained moisture per SOP-CRD -HCU.
387884 | CR | 20181215 |  | 4 | TOA-FL-1B is at end of roll | N | N |  | N | YES | <D> **** Detailed Description **** While performing opertator rounds it was observed that TOA-FL-1B was at end of roll. <I> **** Actions Taken **** Informed CRS and wrote CR. | 02-00-TOA-FL-1B
387885 | CR | 20181215 | CAQ | D | Rod Accumulator Trouble Alarm for CRD-HCU-0235 | Y | N |  | N | NO | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm for CRD-HCU-0235. The alarm is due to high water level.
387886 | CR | 20181215 |  | 4 | FLM steam leak walkdown at 65% power | N | N |  | N | YES | <D> **** Detailed Description **** During the TG walkdown per WO 02134901, the following leaks were found: --BS-V-717A body-to-bonnet leak, S5 --HD-V-3D27 packing leak, S5 --Identified leak on WR 29143740 as crossunder pipe manway --Backseated MS-V-170A, reducing from S5 to S2 --Identfied leak on WR 29141905 as MS-V-115B packing --Verified waterfall down the side of COND-HX-6B is from HD-V-18D. <I> **** Actions Taken **** Backseated HD-V-3D27, leak is now S2. Updated FLM maps. | 02-00-BS-V-717A,02-00-HD-V-3D27
387887 | CR | 20181215 | CAQ | D | IDS 20 21 Not Functioning as Designed | N | N |  | N | YES | <D> **** Detailed Description **** IDS 20 21 are not functioning as designed. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervision notified. Initiated CR/WR. Contact WWM. Compensatory measure put in place. | 02-00-SEC-IDS-E/S/20/21
387888 | CR | 20181215 |  | 3 | D LL I&C resouce task not identified for SOP-COND-FILL | N | N |  | N | NO | <D> **** Detailed Description **** Downpower lessons learned SOP-COND-FILL for COND-P-2B requires support for I&C to fill Condesate pressure switches asociated with COND-PS-14B 1(2)(3) to support refill for WO 02134436. Work order did not have the required support task. I&C resources were not identified as needed on swingshift to support fill. <I> **** Actions Taken **** WO 02134436 task 06 created to support SOP-COND-FILL. I&C resources contacted to support fill.
387889 | CR | 20181215 | CAQ | D | OSP-MS-S701 issues encountered for IV/RV section. | N | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02080035 then taken back to complete <D> WO 02122413 OSP-MS-S701 was perfomred with the following noted isses. MS-V-166B and MS-V-165B failed to automatically close IAW step 7.16.18. Actions to cycle these valves was taken multiple times and additionally the opposite side valves we cycled to attempt to clear a permissive with MS-V-165B ,166B. After cycling the opposite side valves we again tried to cycle MS-V-163B,164B without success. EO was dispatched to perform attachment 9.1 which worked. . Open indication for MS-V-163C and MS-V-166C did not return to open automatically. This also required EO intervention to locally verifry these valves open. Valve indication was verified open and checking the limit switch . Cycling MS-V-166C required to test steps to be performed twice which was when the indication for MS-V-165C failed to indicate correctly. ADDITIONALLY 10mrem of occupational exposure was recieved by operations for this surviellance. Request the this be corrected. <I> Consulted supervision. Worked through procedure. | 02-00-DEH-LMS-3RL,02-00-DEH-LMS-3RR,02-00-DEH-SV-2IR,02-00-DEH-SV-2RL
387890 | CR | 20181216 |  | 4 | No Lighting RW 467 A Valve Gallery - Pipe Space Room |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** NO Lighting in the RW 467 Pipe Space Room. This room is inside the A Valve Gallery. Room C230. Door C228. <I> **** Actions Taken **** Notify HP Lead. Initiate CR/WR <N> **** Equipment Description **** RW 467 Pipe Space Room
387891 | CR | 20181216 | CAQ | D | Rod Accumlator Trouble CRD-HCU-3839 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble for CRD-HCU-3839. Alarm was due to Low Nitrogen pressure. Local pressure was reading 980#. OPS 2 recharged CRD-HCU-3839 and alarm is clear. <I> **** Actions Taken **** Informed CRS/SM | 02-00-CRD-HCU-3839
387892 | CR | 20181216 |  | 3 | BOLTED TERMINATION IN COND-M-P/2B TERM BOX LOOSE | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of work order 02134725 (INSPECT AND REPAIR BOLTED TERMS IN COND-M-P/2B TERM BOX) the as found condition of "A" phase termination at the common bus connection was very loose. At the time of the finding, plant electricians notified operations and the WWM of the loose connection. The cables were brought to the OCC for inspection by engineering personnel. It was determined the cable lugs and common bus connection point could be cleaned to remove corrosion/oxidation, and then re -installed back into the motor terminal box. <I> **** Actions Taken **** Generated this CR to document issue found with loose connection. Contacted OCC with CR number. | 02-00-COND-M-P/2B
387893 | CR | 20181216 |  | 3 | There is no link to SOP-RFT-OPS in T:\User Applications\PDIS |  |  |  | N | NO | <D> **** Detailed Description **** Section 5.17 and 5.19 of SOP-RFT-OPS directs establishing a Real Time Plot per SOP-COMPUTER-OPS. SOP-COMPUTER-OPS provides direction to navigate to T :\User Applications\PDIS\HSD1 or HSD2 (depending on whether TDAS or PPC are primary) and double click on the referenced procedure to run a Real Time plot. The referenced procedure, SOP-RFT-OPS, does not exist at that location. <I> **** Actions Taken **** Plot was created manually in eDNA Trend.
387898 | CR | 20181216 |  | 3 | Lower stab misaligment found on COND-P-2B breaker | N | N |  | N | YES | <D> **** Detailed Description **** The lower center load side stab on COND-CB-CB2B does not aligned properly with the the switchgear. This improperly impacts the rosette and prevents the breaker from racking in properly. This is not a breaker issue, this is a switchgear issue. Recommend adjusting the switchgear side breaker connection. | 02-00-COND-CB-CB2B
387899 | CR | 20181216 |  | 4 | COND-CB-CB2B misalignment | N | N |  | N | YES | <D> **** Detailed Description **** COND-CB-CB2B is not aligned when racking in the middle load side rosebud was damaged. This is a repeat issue with multiple instances of the same rosebud damaged. AR EVAL 286424 documented the middle stab bottle is 1/16 to 1/8 inch higher than the other two. The problem existed last refueling outage too. <I> **** Actions Taken **** Informed supervision and the OCC another attempt to rack in the breaker was tried with the same result. <N> This is a duplicate CR to #387898 | 02-00-COND-CB-CB2B
387900 | CR | 20181216 |  | 4 | Dataglance and eWP problems |  |  |  | N | NO | <C> This CR is a duplicate of #387906. <D> **** Detailed Description **** Dataglance is unable to validate packages. See EDMS for screenshot. When attempting to download a package to a tablet an error called "Checkout error 500 Document metadata taking too long to validate." is present. <I> **** Actions Taken **** Manually validated that the revision of the procedure is the current one, Contacted the Duty IS person for help. <N> This CR can be closed as NCAQ4. The same issue is identified in more detail in 387906. Actions will be tracked in 387906. 387906 has been cross-referenced.
387901 | CR | 20181216 |  | 3 | Repairs to Switchgear in SM2 should be Top 10 Safety Issue | N | N |  | N | YES | <D> **** Detailed Description **** The load side stabs in the cubical for COND-CB-CB2B are misaligned due to inadequately supported cabling in the back of this SM2 switchgear cubical. This condition results in an inability to rack in this breaker without performing high risk work near energized 4160 VAC conductors to temporarily align the load side stabs. This degraded condition has been previously documented in CR 367817, and WO 02114719. <I> **** Actions Taken **** The purpose of this CR is to highlight this safety concern, and drive the planning, scheduling and required corrective maintenance to adequately support the cables. This item should be added to the stations top 10 Safety Issues list and scoped into R24. | 02-00-COND-CB-CB2B,02-00-E-SM-2
387902 | CR | 20181216 | CAQ | D | Rod Accumulator Trouble Alarm for CRD-HCU-22-07 | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-2207 was due to high water level. <I> **** Actions Taken **** OPS 2 drained water per SOP -CRD-HCU and alarm is clear. | 02-00-CRD-HCU-2207
387903 | CR | 20181216 |  | 4 | LP-HTR-1C level low alarm not clearing with normal level | N | N |  | N | YES | <D> **** Detailed Description **** HD-LS-1CL remains locked in with level at normal setpoint of -1.00 inches. <I> **** Actions Taken **** Informed CRS. | 02-00-HD-LS-1CL
387904 | CR | 20181216 | CAQ | D | TIP-MON-4 FUSE 5 IS NOT ILLUMINATED | Y | Y |  | N | YES | <D> **** Detailed Description **** While doing the task preview for ISP-RPS-Q907 (WO# 02105334-01), we noticed that Fuse 5 on TIP-MON-4 was not illuminated. This is a long standing problem. Investigate the reason Fuse 5 is not illuminated <I> **** Actions Taken **** we informed our supervisor and operations and documented on our procedure | 02-00-TIP-MON-4
387905 | CR | 20181216 |  | 4 | CCTVs Need Cleaning | N | N |  | N | YES | <D> **** Detailed Description **** CCTV 01/12/13/14 require cleaning. <I> **** Actions Taken **** Initiate weekly camera cleaning list. Initiate CR/WR. <N> **** Equipment Description **** Perimeter Cameras CCTV 01/12/13/14
387906 | CR | 20181216 |  | 3 | DataGlance application issue |  |  |  | N | NO | <D> **** Detailed Description **** The DataGlance application experienced various issues with generating and processing electronic work packages. A review of the log files showed the application to be experiencing numerous 'numeric overflow' errors. <I> **** Actions Taken **** Contacted database administrator who determined that the issues were related to the application, not the database. Contacted supervisor. Initiated support ticket with vendor. Worked with vendor developer to create a patch to the application. Patch was applied to the Development environment and tested. Patch was applied to the QA environment and tested. Contacted Control Room to request a time to apply the patch to the Production environment. Received permission to go ahead and apply the patch. Applied the patch to the Production environment. Restarted the application. Monitored application processing jobs to verify they were functional. Initiated this CR to document the issue.
387907 | CR | 20181216 |  | 4 | CM-11 Hand Monitor is OOS @ HP PAP |  |  |  | N | NO | <D> **** Detailed Description **** HP-EQ-53253 goes into "ALARM MODE" when lifted off the cradle and moved around. Possible short in the Cord. <I> **** Actions Taken **** -Took CM-11 OOS and initiated CR/WR. -Notified HP Supervision via e-mail. <N> **** Equipment Description **** HP-EQ-53253
387908 | CR | 20181216 |  | 4 | Camera Cleaning |  |  |  | N | YES | <C> This CR was reopened to add notes. . This CR is being trended as it is a duplicate of 387905 <D> **** Detailed Description **** CCTV 1, 12, 13, 14 need to be cleaned. | 02-00-SEC-CCTV-1,02-00-SEC-CCTV-12,02-00-SEC-CCTV-13,02-00-SEC-CCTV-14
387909 | CR | 20181216 | CAQ | D | High accumulator water level. | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-26-47 was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear. Trending CR. <I> **** Actions Taken **** Drained water. <N> **** Equipment Description **** RB 522 | 02-00-CRD-HCU-2647
387910 | CR | 20181217 |  | 3 | Plant water usage rate increase | N | N |  | N | NO | <D> **** Detailed Description **** Over the last 5 days plant water usage rate has increased form 11.9 gpm to 27.8 GPM.
387911 | CR | 20181217 | CAQ | D | Step change in RCIC-P-3 cycle time after run on 12/13/18 | Y | N |  | N | YES | <D> **** Detailed Description **** After performance of OSP-RCIC/IST-Q701 under WO 02105341 there is an obsevable change in RCIC-P-3 run time. Prior to this RCIC run the 24 hour cycle time was about 15 times. After our RCIC run the 24 hour cycle time increaced to about 25 times in a 24 hour period. WR 29140056 give an excellent guide for possible leakage paths. This does not appear to impact the current availiblity of the RCIC system. Suggest that this continue to be monitored especially as that the current retest for RCIC-MO-19 called out as OSP-RCIC/IST-Q701. <I> **** Actions Taken **** Informed supervision of observed changes. Plots attached to EDMS. This CR was written | 02-00-RCIC-P-3
387917 | CR | 20181217 |  | 4 | PROHIBITED ARTICLE DECLARED AT CHECKPOINT |  |  |  | N | NO | <D> **** Detailed Description **** On 12-17-18 at approx 0700 hours, a contractor arrived at the checkpoint. When asked by Security if there were any articles to declare, the contractor declared there was alcohol in the truck. <I> **** Actions Taken **** Shift Manager, Benton County and Security Management was notified. IS Management notified.
387919 | CR | 20181217 | CAQ | C | AED CAL 6.19.53-SV-95 Conservative Unit Conversion Error | Y | N |  | N | NO | <D> **** Detailed Description **** The original calculation for barrier panel design (AED CAL 6.19.53-SV-95) has incorrect unit conversion from psi to ksf (kips/sq. ft.). The ksf value used in analysis is equivalent to a HELB pressure of 18 psig. The original design HELB (high energy line break) pressure was 1.8 psig, and current HELB design pressure is 2.7 psig. These HELB pressures are an order of magnitude lower than the design pressure, so the error was conservative. The calculation only includes HELB and jet impingement loads, because Seismic loads were considered insignificant. . Recommended Actions: AED CAL 6.19.53 SV 95 should be revised (CMR) to reflect the current HELB loading and note that the previous design was bounding. The calculation has no impact of personnel or plant safety and equipment. <I> **** Actions Taken **** None <N> See â€œCR 387919 Additional Info.docxâ€ in the EDMS folder for AR/CR 387919 for more details concerning the removable block wall steel panel for the south side of the RWCU Heat Exchanger Room (R510). . As per assignment 01, there is no need to update the calculations as it is a conservative error and there is another calculation which adequately addresses this concern. Therefore, no further actions are required. The parent AR is closed. .
387921 | CR | 20181217 | CAQ | C | CAS compressor drawings show EPNs not in Passport. | N | N |  | N | NO | <D> **** Detailed Description **** The EPNs CAS-CP-C/1A/2, CAS-CP-C/1B/2, CAS-CP-C/1C/2 are not listed in Passport, but they are shown in E546-1, E546-1A, E546-2, EWD-78E-001A, EWD-78E-003A & EWD-78E-005A. CAS-CP-C/1A, CAS-CP-C/1B & CAS-CP-C/1C are listed in Passport, but do not show up on any of these drawings. The three EPNs not in Passport are out in the field. This appears to be a Passport issue. Please investigate and bring everything into alignment. See drawings in EDMS. <I> **** Actions Taken **** Wrote this AR/CR.
387931 | CR | 20181217 |  | 3 | Procedure enhancement ABN-RRC-LOSS. |  |  |  | N | NO | <D> **** Detailed Description **** On page 14 of ABN-RRC-LOSS in the NOTE above step 4.3.5 it should indicate Jet Pump Loop "A". In step 4.3.5 it should read RRC Loop "A" and Jet Pump Loop "A". They all currently read "B".
387932 | CR | 20181217 | CAQ | D | Notification of certification form issue |  |  |  | N | NO | <D> **** Detailed Description **** Site was notified by US Ecology of an issue with the Radioactive Waste Shipment Certification form (DOH RHF-31D) for shipment 18-71 shipped to US Ecology on 11/16/18. Shipment 18-71 was an EDR/FDR resin liner shipped in a Type A cask as a LSA-II shipment. The volume listed in Section A (Generator) of the form did not match the volume listed in Section C (Carrier) of the form. The correct volume was listed in Section A of the form. The volume on the NRC Form 540 and Form 541 was correct. A corrected form was provided to the burial site. <I> **** Actions Taken **** RPM and Shipping supervisor notified. Corrected form provided to burial site.
387934 | CR | 20181217 |  | 3 | Incomplete Information on MOT Document |  |  |  | N | NO | <D> **** Detailed Description **** On 12/13/18 Eng. Tecnical Services (org.54122) submitted document MOT-RELAY-1 for processing to Document Control. Document Control is unable to process document due to information within the document being cut off. <I> **** Actions Taken **** CR initiated, MOT was returned for corrections.
387935 | CR | 20181217 | CAQ | D | CRD 2211 accumulator trouble alarm | Y | N |  | N | YES | <D> **** Detailed Description **** Low N2 pressure / repressurized. <I> **** Actions Taken **** dispatched OPS 2 and cleared alarm wrote WR as directed | 02-00-CRD-TK-125/2211
387936 | CR | 20181217 | CAQ | D | CRD HCU 2203 accumulator alarm | Y | N |  | N | YES | <D> **** Detailed Description **** water alarm / drained and clear <I> **** Actions Taken **** notified OPS2 wrote WR as directed | 02-00-CRD-TK-125/2203
387939 | CR | 20181217 |  | 4 | RWCU-SPV-234B- exhaust port air leak | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WO 02088852-01 RWCU-AO-210B for suspected air leakage through actuator seal(s), the actual leak was discovered to be at the exhaust port of RWCU-SPV -234B. <I> **** Actions Taken **** Mechanics notified supervisor. <N> **** Equipment Description **** W 475 Q4/11.7 | 02-00-RWCU-SPV-234B
387943 | CR | 20181217 |  | 4 | Extermely Low Oil Levels Found in MT-CRA-1 Main & Aux Hoist | N | N |  | N | YES | <D> **** Detailed Description **** During main hoist upgrade activities, the turbine crane OEM drained oil from the main and aux hoist reducers. Approximately 10 gals was drained from the aux and 7 gals from the main. Expected volumes are 16 gals and 26 gals respectively, indicating extremely low oil levels at the time of draining. Depending on how long the oil levels have been this low, and with the high temperatures of the operating environment, the OEM warns that seals may begin leaking once oil is placed in the reducers at the specified levels. <I> **** Actions Taken **** Initiated this CR to document the as-found condition. <N> **** Equipment Description **** T 555' A3/15.0 (PARK POSITION) | 02-00-MT-CRA-1
387944 | CR | 20181217 |  | 3 | No Eng support task for RRA-CC-17 inspection |  |  |  | N | NO | <D> **** Detailed Description **** There was no engineering support task for WO 02112149 for RRA-CC-17 water-side inspection. The engineering support task is used to properly plan for when engineering support will be required in order to complete the planned work to ensure that engineering is properly planned and ready. This also facilitates proper communication with maintenance and the Work Week Manager along with HP to notify engineer of any High Rad briefs that are being conducted. Discussed with planning and got a support task created for this work, however, moving forward, future cooling coil inspections requiring an engineer in the field to support need to have an engineering support task. See CR 386475 for similar incident. <I> **** Actions Taken **** Discussed with Planning and Supervisor <N> Discussed with Lead scheduler. Support tasks were directed to planning to be cancelled per change management several months ago. If resources were needed in a particular WO in the "support" function, the resources were added to under the 01 task. Engineering resources were on the 01 task for these CR's (387945). WC will communicate change to engineering. WC discussed change with engineering and provided tools for them to be successful. No other actions needed on this CR per WC manager. CR is complete.
387945 | CR | 20181217 |  | 4 | No Eng support task for RCC-V-23B inspection |  |  |  | N | NO | <D> **** Detailed Description **** There was not an engineering support task for WO 02114922, to perform internal inspection of RCC-V-23B. The engineering support task is used to properly plan for when engineering support will be required in order to complete the planned work as scheduled. <I> **** Actions Taken **** Discussed with fellow engineering supervisor, who informed me that planning requested that we document a similar issue in a CR (reference 387944). Completed the task of generating a CR with diligence. <N> Discussed with Lead scheduler. Support tasks were directed to planning to be cancelled per change management several months ago. If resources were needed in a particular WO in the "support" function, the resources were added to under the 01 task. Engineering resources were on the 01 task for these CR's (387944). WC will communicate change to engineering.
387946 | CR | 20181217 |  | 3 | COND-P-2C TSW flow | N | N |  | N | YES | <D> **** Detailed Description **** during rounds i noted oil temps at the high spec with a step jump in temps from the previous shift. during investigation i found no TSW flow was going thru the cooler. the throttle valve was cracked open, but zero flow indicated on the flowmeter. i throttled the outlet valve open to flush the cooler and then reset flow approx 2.5 gpm after LO temps returned to band. suspect valve fouling led to this condition as the outlet valve is barely throttled open to maintain temps in band <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-COND-P-2C
387947 | CR | 20181217 |  | 4 | TSW leak COND-P-2C | N | N |  | N | YES | <D> **** Detailed Description **** there is a TSW leak above TSW-FG-2C (left flow gage for oil cooler flow) approx 15 dpm. the leak is coming from a union above the gage before the 90 degree piping bend. <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-TSW-FG-2C
387948 | CR | 20181218 | CAQ | D | unrepeatable event during calibration of SW-MO-PCV/15B | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During the calibration of SW-MO-PCV/15B electricians performed steps in PPM 10.25.137 as written. The task is to apply 4-20mA signal to position the 90 degree valve in three separate positions. at 12mA the valve is to be at midstroke, and it functioned properly. The 20mA signal is applied and the valve moves to the closed position as expected. However, per step 7.2.18, when 4mA was applied, the valve functioned properly, but the motor that drives the actuator gears kept running (free wheeling). The actuator stopped at the OPEN (thru flow) position as expected, but the motor should have cut-off. We notified supervision and reperformed our calibration steps with supervisor oversight. We could not get the unexpected event to repeat again. Per step 7.2.20 of 10.25.137, calibration is satisfactory. This CR is for trending purpose <I> **** Actions Taken **** Notified Supervisor and CRS. Write CR. <N> **** Equipment Description **** W530 L5/13.4 SW-MO-PCV/15B | 02-00-SW-MO-PCV/15B
387955 | CR | 20181218 |  | 3 | TSI-6.3.5 Incorrect Revision Number |  |  |  | N | NO | <D> **** Detailed Description **** For TSI-6.3.5, the correct revision number is Major Rev. 000, Minor Rev. 001. However, the native document shows Minor Rev. N/A. This is an administrative error only. The procedure content is correct. <I> **** Actions Taken **** Generated CR.
387956 | CR | 20181218 | CAQ | D | Receiving FPC SURGE TK LEVEL HI-HI alarm | N | N |  | N | YES | <D> **** Detailed Description **** Control room has been receiving the skimmer surge tank A and B high-high level alarms following COND-V-42 filling the SST. FPC-LIS-2A and or FPC-LIS-2B should close COND-V-42 prior to actuating FPC-LIS-1A and FPC-LIS-1B which causes the HI-HI level alarm to come in. The Skimmer surge tanks achieve 49% on FPC-LIS-2B and 50% on FPC-LIS -1B as seen from the camera on Security Desk. Please adjust FPC-LIS-2A and FPC-LIS-2B to close COND-V-42 prior to receiving the FPC-LIS-1A and FPC-LIS-1B hi-hi alarms. | 02-00-FPC-LIS-2A,02-00-FPC-LIS-2B
387957 | CR | 20181218 |  | 3 | SWP-IRP-01 and FORM 26232 Discrepancy |  |  |  | N | NO | <D> **** Detailed Description **** Form 26232, POC Review Criteria, states that POC review is required if the proposed activity "results in a configuration with an ORANGE or RED plant operational or shutdown risk level". Procedure SWP-IRP-01 2.9.17 requires a POC review for "Plant Risk Level ORANGE". <I> **** Actions Taken **** Discussed this discrepancy with POC chair.
387958 | CR | 20181218 |  | 4 | PI accessible in Asset Suite |  |  |  | Y | NO | <D> **** Detailed Description **** On 12/17/18 it was discovered that an Asset Suite document contained Personal Information (PI) (SSN). Information Management Supervisor was notified and the document was removed from Asset Suite and identified as containing confidential information per GBP-REC-04. A preliminary extent of condition reviewed 122 audit within the Records Management in Asset Suite and no additional PI were found that contained the same information. See EDMS for documents reviewed. <I> **** Actions Taken **** notified Quality management and Information Management Supervisor.
387959 | CR | 20181218 |  | 4 | COND-P-2B needs cribbing installed prior to racking in | N | N |  | N | YES | <D> **** Detailed Description **** During restoration from the scheduled down power to repair a leak to COND-P-2B discharge drain valve there were issues with racking in COND-CB-CB2B; see CRs 387898/387899. Every time this specific breaker is racked in, we absolutely need electrical to install the necessary cribbing inside the back of the breaker cubicle due to electrode misalignment (performed under WO 02134725). This is a cubicle problem due to cable tension on the electrodes and it cannot be easily resolved. Finding a way to control this current need will assist in reducing the chance of equipment damage and can prevent unexpected power ascension delays in the future when COND-CB-CB2B is racked out. | 02-00-COND-CB-CB2B
387961 | CR | 20181218 |  | 3 | SOP-ELEC-SM1-MAINT improvement to page 28 |  |  |  | N | NO | <D> **** Detailed Description **** See EDMS, changes in red. To improve the quality of the section. <I> **** Actions Taken **** Proc change request. <N> **** Equipment Description **** SOP-ELEC-SM1-MAINT
387964 | CR | 20181218 |  | 4 | COND-V-120B loose handwheel gearbox mating surfaces | N | N |  | N | YES | <D> **** Detailed Description **** During operation of COND-V-120B movement was observed between the mating connection of the handwheel gearbox and the gear assembly housing directly above the yoke. By holding on to the handwheel gearbox you can wiggle it by hand. A little under a 1/16" gap can be observed between the mating surfaces. The are no visible bolts or nuts that can be tightened, though the bolts/studs are visible in the small gap, so the tightening of them must be internal on one side or the other. See EDMS for photo of the location. | 02-00-COND-V-120B
387965 | CR | 20181218 | CAQ | D | CRD-FI-4A LOOS | Y | N |  | N | YES | <D> **** Detailed Description **** On rounds it was discovered CRD-FI-4A was reading <0.12 gph.Gauge doesn't indicate below 0.12 gph. Band is 0.12 - 0.42 gph. <I> **** Actions Taken **** Informed CRS | 02-00-CRD-FI-4A
387967 | CR | 20181218 |  | 4 | RCC-V-23B internal inspection results | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02114922-01 RCC-V-23B Inspect internals. The Check Valve Reliability Program Engineer performed the inspection with mechanical craft and identified the backstop area of the bonnet shows signs of impacting the disc stud as the valve flutters in the full open position. This is expected in this application so close to the pump. The woodruff keyway area on the hanger arm has become widened which allows the hanger arm to move before the shaft starts to move. Due to the turbulent application this wear would be expected to continue, but would not affect the valveâ€™s ability to stroke by flow, the woodruff key is only there to be able to cycle the valve externally. The disc has also been rotating in flow, as indicated by the wear on the hanger arm face where the disc washer rubs. The currently installed disc to hanger arm gap is approximately .125â€. On a new disc / arm assembly this gap is measured at .080â€. Freedom of motion and seat contact checks (.002â€ feeler gauge) were Satisfactory. Inspection results were documented on attachment 9.3 of PPM 10.2.99 in the work order. Valve is acceptable to reassemble. . Check Valve Reliability Program Engineer Recommendations: . Rotate bonnet to undamaged backstop location-Maintenance replaced with a new bonnet. Measurements should be verified / trended during next performance of the PM by the Check Valve Reliability Program Engineer. A work request was generated to have a package planned for disc / hanger arm / disc shaft sub assembly assembled / welded prior to the next scheduled performance of this PM (or the PM on sister valves RCC-V-23A and RCC-V-23C) which would prevent any scheduled preventative maintenance tasks from going long should additional wear be observed, and a decision to replace parts made. <I> **** Actions Taken **** Notified MCR, initiated CR and WR to have a package planned for disc / hanger arm / disc shaft sub assembly assembled / welded prior to the next scheduled performance of this PM (or the PM on sister valves RCC-V-23A and RCC-V-23C) | 02-00-RCC-V-23B
387968 | CR | 20181218 |  | 3 | NET3-COMP-IPS1 not passing traffic | N | N |  | N | YES | <D> **** Detailed Description **** NET3-COMP-IPS1 was found to not be passing traffic on most of its interfaces. This is part of a redundant pair of IPS devices. NET3-COMP-IPS2 appears unaffected and is functioning normally. Initial review of the log files does not indicate source of the problem. Recommend to Computer Engineering to investigate. . This is not a reportable condition. This does not currently impact Operations due to the redundant pair being fully functional. <I> **** Actions Taken **** Notified SM and generated CR. | 02-00-NET3-COMP-IPS1
387975 | CR | 20181218 | CAQ | D | Scope change for RRA-CC-17 and RRA-CC-15 |  |  |  | N | NO | <D> **** Detailed Description **** During performance of the water side inspection of RRA-CC -17 WO 02112149-02 it was discovered that the coil housing did not have an anode plug inspection hatch. And due to the location and proximity of the associated piping to the wall the flanges could not be separated to perform the boroscope inspection. Piping will have to be cut to remove the return and supply flanges for inspection. RRA-CC-15 was walked down and found to be similar in design without an anode access hatch. The piping can be unbolted and separated to perform the boroscope inspection. Piping will have to be cut if a backflush is required. <I> **** Actions Taken **** Generated CR for documentation and notified planning for necessary required changes.
387976 | CR | 20181218 |  | 4 | Late eSOMS Entries for Maintenance - 12/9 - 12/13 |  |  |  | N | NO | <D> **** Detailed Description **** There were 7 instances last week of eSOMS time being changed after hours were worked. 4 were by Mechanics, 1 was an Electrician, 1 was an I&C Tech, and 1 was a FIN Supervisor. <I> **** Actions Taken **** Updated eSOMS with correct hours
387979 | CR | 20181218 |  | 4 | SA-RV-265 lifting with water coming out | N | N |  | N | YES | <D> **** Detailed Description **** During the RWCU-V-210B work, mechanics noticed an increased noise in the room that has been getting progressively worse over the last 30 hours. The noise appears to be coming from SA-RV-265 which is now rapidly cycling with water coming out of the outlet piping and draining into the scupper. The RV may need to be reviewed for replacement and figure out why it's lifting at this time. This may impact the RWCU-DM clearance lift. <I> **** Actions Taken **** notified supervisor and RW control room | 02-00-SA-RV-265
387980 | CR | 20181218 | CAQ | D | IDS 20/21 Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** IDS 20/21 Malfunction <I> **** Actions Taken **** Compensatory Measures Initiated, CR/WR, Electrical Supervisor Notified. This failuer is non-reportable. | 02-00-SEC-IDS-EVAL/20/21
387982 | CR | 20181218 |  | 3 | TASK TAKEN TO FINSHED BY OTHER WORK GROUP. |  |  |  | N | NO | <D> **** Detailed Description **** Work order package 02050986-93 was taken to finished by another work group without the owner of the work orders knowledge. Work steps were not completed and transient combustible permit was not closed per work order instructions. <I> **** Actions Taken **** Had to close transient combustible permit and sign off work steps.
387983 | CR | 20181218 |  | 4 | TSW-FS-39B REQUIRED CALIBRATION | N | N |  | N | YES | <D> **** Detailed Description **** TSW-FS-39B required calibration during scheduled PM (WO# 02104505-01). The desired value was 5 PSID +/- 0.15. The as found value was 5.74 PSID. We adjusted it to the as left value of 4.96 PSID, SAT <I> **** Actions Taken **** adjusted switch, SAT. Wrote this CR | 02-00-TSW-FS-39B
387987 | CR | 20181218 | CAQ | D | CCH Purge Unit Coating Degradation | Y | Y |  | N | YES | <C> CR reopened to cross reference additional WP 02142516, marked completion required box, then taken back to complete <D> **** Detailed Description **** This CR is for trending purposes only. Based on engineering review the condition described below does not prevent the CCH system from performing its design function. During inspection of the CCH-CR-1B purge unit under WO 02106603 (CCH-CR-1B, REPLACE OIL/ FILTER), coating degradation was identified. The borescope inspection revealed small pieces of internal coating on the bottom of the purge unit. Small pieces of foreign material can potentially hinder operation of the purge unit and other components in the oil system. Pictures of the loose coating were shared with the craft. Engineering recommended to the craft that loose coating be removed from purge unit. It was also recommended that the WO completion notes document the successful removal of the loose coating. During this work the oil filters were inspected and no coating flakes were found. Purge unit epoxy degradation was also noted during a recent inspection of CCH-CR-1A performed under WO 02100874-01 (CCH-CR-1A, REPLACE OIL/ FILTER) in November, 2018. In this case the foreign material was successfully removed. The oil filter was inspected and no epoxy flaking was found. The CCH purge unit coating degradation is a known deficiency. Multiple CRâ€™s have been written documenting this condition. AR 358871 is currently tracking the replacement of the CCH purge units. | 02-00-CCH-CR-1A,02-00-CCH-CR-1B
387988 | CR | 20181218 |  | 4 | ILC-23 candidate failed simulator evaluation LO001883E1 |  |  |  | N | NO | <D> **** Detailed Description **** One student failed simulator evaluation LO001883E1 on 12/14/2018. Remediation is IAW TDI-02 and documented on Form 26430. Recommend closing this AR to "trend." <I> **** Actions Taken **** Notified Training management and AOM of Training, generated this AR.
387989 | CR | 20181218 | CAQ | D | DO-V-58 leak during Fuel Oil Delivery | Y | N |  | N | YES | <C> CR reopened at the request of Environmental to add additional notes. <D> **** Detailed Description **** DO-V-58 was found to be leaking during a Fuel Oil Delivery. DO-V-57 was also covered in Fuel Oil, however there was no visible leak coming from the valve. The FO transfer was stopped isolating the leak and the FO that was spilled was confined to the bermed are of the FO Polisher Building structure. An unknown quantity of FO drained into the Floor Drain Sump outside the FO Polisher Building. FO-V-38 was closed per the procedure which prevented the FO from being discharged to the environment. The contents of the Sump will be sampled by Chemistry and emptied by laborers. <I> **** Actions Taken **** Notified SM, CRS, Maintenance Supervisor. CR/WR generated. Correction: FD-V-38 was isolated vs. FO-V-38. This isolated the sump from manhole S4. The leakage was collected. This was evaluated and is not reportable. <N> See E&RP write-up in EDMS docs. | 02-00-DO-V-57,02-00-DO-V-58
387990 | CR | 20181219 | CAQ | C | Loose nut adaptor found loose on RCIC-V-19 | Y | N |  | N | YES | <D> **** Detailed Description **** After the completion of the diagnostic testing on RCIC-V-19 it was discovered that the nut adaptor was loose during the stroke. See video @ S:\Engineering\Technical Services Engineering\Plant Programs\MOV Program\MOVData\ALBUM\RCIC\RCIC19 <I> **** Actions Taken **** Informed Supervision and Shift Manager. <R> The REP/REGE assignments were extended with concurrence from the Compliance Supervisor. | 02-00-RCIC-V-19
388001 | CR | 20181219 |  | 3 | Revise PPM 10.2.251 Temporary Flood Barrier Installation |  |  |  | N | NO | <D> **** Detailed Description **** During the RHR-P-2A safety system window there was confusion during temporary flood barrier installation per PPM 10.2.251 that the rubber berm material was required. The procedure does not list this material as required in Section 5.0 MATERIALS, TOOLS, AND TEST EQUIPMENT; however Attachment 9.1, Typical Temporary Flood Berm in the procedure with a picture depicts that the rubber is used. . Discussed issue with E-Fin and Fire Protection Engineering for clarification and it was confirmed that the rubber berm material is not required. Revise PPM 10.2.251 Temporary Flood Barrier Installation to change the picture and possibly add a note that clarifies that the rubber berm material is not required. Assign AR CR to AR MECHSHOP. <I> **** Actions Taken **** Discussed the clarification with the Mechanical shop and Site Support contractor. Had EN scaffold group take new pictures for incorporation into procedure revision. Initiated CR
388003 | CR | 20181219 | CAQ | D | Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-30-27 <I> **** Actions Taken **** Dispatched OPS-2 to investigate. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-30-27 was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear. | 02-00-CRD-HCU-3027
388005 | CR | 20181219 |  | 4 | Atmospheric monitoring alarmed during initial measurement |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO 02106600-01, atmospheric monitoring is required for the inside of main generator hatch area. Access is required to take physical measurements of generator thermocouples. During initial monitoring, the south side of the main generator alarmed on CO. Instrument was zeroed outside TG building before initial measurement was taken and measured again after re -zeroing the instrument with identical results. Measurements were taken on the north side of main generator and no alarms were generated. <I> **** Actions Taken **** Contacted supervision, operations, and system engineer <N> **** Equipment Description **** Main Generator
388009 | CR | 20181219 | CAQ | D | DO-V-58 Not locking in full closed position | Y | N |  | N | YES | <D> **** Detailed Description **** The locking handle on DO-V-58 over travels when the valve is in the full closed position. This over travel allows the valve to be bumped or blown open without squeezing the handle. Possibly missing pin in handle see EDMS for Photos. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** Diesel Polisher Bldg | 02-00-DO-V-58
388011 | CR | 20181219 |  | 4 | GSB 441' Ice Machine Not Producing Ice |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The ice machine located in the GSB luchroom on the 441' elevation is not producing ice following a scheduled power outage starting last week and finishing this past tuesday morning (12-18-18). There is obvious power to the ice machine at this time and ice was being produced as normal prior to the scheduled power outage. <I> **** Actions Taken **** Initiated WR <N> **** Equipment Description **** GSB 441' Lunchroom ice machine
388012 | CR | 20181219 |  | 4 | B26 Cooking Problem caused smoke in break room |  |  |  | N | NO | <D> **** Detailed Description **** Fire Protection Engineer called to investigate burning smell in B26 Deschutes 2nd floor break room. Individual had put tortillas wrapped in aluminum foil and then paper towel in the microwave. The tin foil sparked and caused the paper to smoke. The individual was watching the microwave and stopped the process immediatelyl. No further action.
388013 | CR | 20181219 | CAQ | D | Calculations for EC 12277 not processed per DES-4-1 |  |  |  | N | NO | <C> CR changed to Priority CAQ; and from Severity 4 to D at the request of OFM on 12.27.2018. <D> **** Detailed Description **** Design calculations supporting EC 12277 were not submitted to Records & Information Management, as required per DES-4 -1, Sec. 4.3.17. As EC 12277 was being revised over time, the calculations were also revised, and no previous revisions were submitted to RIM. <I> **** Actions Taken **** All revisions of the following calculations tied to EC 12277 were placed in the appropriate RIM folder on the S drive: CE-02-14-17, CE-02-15-19, CE-02-15-21, and ME-02-15 -11. No further action is necessary.
388014 | CR | 20181219 | CAQ | C | ISP-HPCS-X302 Procedure Update |  |  |  | N | NO | <D> **** Detailed Description **** ISP-HPCS-X302, HPCS Flow Rate Low (Minimum Flow) â€“ CC, Major Revision 7, Minor Revision 1 (PCN-17-0029) inserted steps to maintain availability of HPCS (AR 368884). The PSA group and Maintenance Rule Coordinator reviewed the steps and determined that they do not meet the requirements for availability. The minor revision should be removed from the procedure. . The procedure steps use a dedicated operator to maintain availability of HCPS-SYS-1. In the event of an auto start of HPCS-P-1 the operator must operate the HPCS-P-1 minimum flow valve (HPCS-V-12) to open and close the valve as required. In accordance with NUMARC 93-01 and NEI 99-02 a dedicated operator may be credited for uncomplicated restoration actions that are virtually certain to be successful. The procedure steps use ongoing manual operations of a system designed to operate automatically. It was determined that the steps do not meet the guidance of a few simple actions to restore function. . The following guidance is from NEI 99-02: . Unavailability of a monitored function during testing, operational alignment or return to service need not be included if the test or operational alignment configuration is automatically overridden by a valid starting signal, or the function can be promptly restored either by an operator in the control room or by a designated operator stationed locally for that purpose. Restoration actions must be contained in a written procedure, must be uncomplicated (a single action or a few actions), must be capable of being restored in time to satisfy PRA success criteria, and must not require diagnosis or repair. Credit for a designated local operator can be taken only if the operator is positioned at the proper location throughout the duration of the test or operational alignment for the purpose of restoration of the train should a valid demand occur. The intent of this paragraph is to allow licensees to take credit for restoration actions that are virtually certain to be successful (i.e., probability nearly equal to 1) during accident conditions. . The individual performing the restoration function can be the person conducting the test or operational alignment and must be in communication with the control room. Credit can also be taken for an operator in the main control room provided the operator is in close proximity to restore the equipment when needed. Normal staffing for the test or operational alignment may satisfy the requirement for a designated operator, depending on work assignments. In all cases, the staffing must be considered in advance and an operator identified to perform the restoration actions independent of other control room actions that may be required. . Under stressful, chaotic conditions, otherwise simple multiple actions may not be accomplished with the virtual certainty called for by the guidance (e.g., lifting test leads and landing wires; or clearing tags). In addition, some manual operations of systems designed to operate automatically, such as manually controlling HPCI turbine to establish and control injection flow, are not virtually certain to be successful. These situations should be resolved on a case-by-case basis through the FAQ process. <I> **** Actions Taken **** Discussed the issue with the Work Week Manager and PSRO.
388018 | CR | 20181219 | CAQ | D | GFIP for SL-71 has 2 lights out and it won't accept new bulb | Y | N |  | N | YES | <D> **** Detailed Description **** Ground fault indicator panel for SL-71 has two lights out and it wont accept new bulbs. Bulbs were both labeled 24e. stopped tring to put bulbs in when i determined it was boardering on excessive force. <I> **** Actions Taken **** discussed with FIN whe mentioned there might be an alternative bulb. wrote cr to track lights. | 02-00-E-SL-71
388019 | CR | 20181219 |  | 4 | HS-27 RRC-V-98 needs to be flushed |  |  |  | N | YES | <D> **** Detailed Description **** HS-27 RRC-V-98 R506 J2/7.2 needs to be flushed. The hot spot is currently reading 2150 mrem/hr on contact and 220 mrem/hr at 30 cms. HS-27 is located near the normal Drywell undressing area increasing dose rates from 1 to 3 mrem/hr in June 2017 to 2 to 20 mrem/hr Dec 2018. This change in dose rates, if no action is taken, will result in an increase in dose for individuals exiting the Drywell or supporting exiting the Drywell. Surveys M-20181205-6 and Surveys M-20170615-20 were placed in EDMS. Recommend evaluation to determine best method (flush or shield) to reduce dose rates from HS-27 to the Drywell Undress area. <I> **** Actions Taken **** Initiated CR <N> **** Equipment Description **** R506 J2/7.2 | 02-00-RRC-V-98
388021 | CR | 20181219 |  | 3 | R24 SOP-HVAC/TB-START procedure change |  |  |  | N | NO | <D> **** Detailed Description **** SOP-HVAC/TB-START references TEA-FN-93 (Blower for SR 38) to be placed in service, this has been removed and replaced with the new sample TEA-SR-26. SOP-HVAC/TB-SHUTDOWN does references the new TEA-SR-26. <I> **** Actions Taken **** wrote cr
388023 | CR | 20181219 |  | 4 | High Risk work plan milestone missed for SW A maint window |  |  |  | N | NO | <D> **** Detailed Description **** It was identified at the T-3 meeting on 12/18 that the high risk work plan for SW A had not been challenged which does not meet the requirements of PPM 1.3.76. There was a breakdown in communication between the new WWM and CMPM for the upcoming window that resulted in the meeting not getting scheduled. Additionally the extension of the RHR A maintenance window into the following week presented additional challenges. This was discussed in detail at the T-3 and the high risk challenge meeting has been scheduled to ensure the work will be prepared for implementation and prior to the T-2 meeting. No further actions are recommended and this CR is for trending purposes only. <I> **** Actions Taken **** Discussed with PSO manager, CMPM, and WWMâ€™s. Scheduled High Risk Challenge meeting
388024 | CR | 20181219 |  | 4 | Fire Alarm at APEL |  |  |  | N | NO | <D> **** Detailed Description **** Fire alarm activated at approximately 0800 hours on october 24, 2018. Manual pull station 1:003 near the West exit door was inadvertantly pulled while an employee was putting on their jacket. Employee notified APEL Property Managers immediately. <I> **** Actions Taken **** Appropriate EN chain of command were notified. Richland Fire department responded and reset the fire panel. APEL Building staff evacuated to the assembly area and appropriate emergency procedures were followed by the APEL Facilitiy Property Managers. Employee was coached by EN Supervision. No further actions required.
388025 | CR | 20181219 | CAQ | C | VSDS Radiological Survey Viewer error |  |  |  | N | NO | <D> **** Detailed Description **** While accessing the VSDS survey viewer on the Current, the monthly radiological survey for RB 501' displayed is the monthly survey from August 2018. This could potentially have incorrrect radiological data for individuals using the self-briefing method using the VSDS survey viewer on the Current. <I> **** Actions Taken **** Discussed with HP Supervision, initiated CR.
388026 | CR | 20181219 | CAQ | D | Franklin county siren C2 reporting a partial alarm | N | Y |  | N | NO | <D> **** Detailed Description **** While poling the alerting sirens C2 responded with a partial amplifier alarm. This indicates one or more of the 10 amplifiers is not working. The siren will sound but may be slightly lower in volume. Adjacent sirens are fully functional. <I> **** Actions Taken **** Notified: EP, IS leadership. Dispached techinsicans for repair. <N> **** Equipment Description **** Frankin County Close to WR.
388027 | CR | 20181219 | CAQ | C | ICP-CIA-X101 (WO 02105018) two gauges needed replaced. | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of ICP-CIA-X101 (WO 02105018) two gauges were required to be replaced because they were out tolerance when compared to a calibrated gauge. Gauges were replaced per procedure: CIA-TK-1A and CIA-TK-14B. <I> **** Actions Taken **** Gauges were replaced per procedure. CR generated for tracking purposes. <N> **** Equipment Description **** 441 Truck bay | 02-00-CIA-TK-14B,02-00-CIA-TK-1A
388028 | CR | 20181219 |  | 4 | R24 Outage Milestone PO.12 Scope Freeze turned RED |  |  |  | N | NO | <D> **** Detailed Description **** Outage Management has turned the R24 outage milestone PO .12, Scope Freeze, RED (milestone not met) retroactively on 12/19/18. PO.12 was closed as meeting the criteria; however, in fact electrical resources were well over actual productivity curves from R23. Therefore, PO.12 Scope Freeze did not meet the criteria with quality. An evaluation has been completed under CR 386062 and actions to drive improvement are tracked under that CR as well. Recommend 4/Trend. <I> **** Actions Taken **** Discussed at the Outage Meeting
388031 | CR | 20181219 | CAQ | D | Leak by on valve at WEA-SR-25 | N | Y |  | N | YES | <D> **** Detailed Description **** While performing surveillance 16.11.1, valve WEA-V-SR25/V22 was discovered to no longer function. This valve is necessary for chemistry to take ODCM tritium samples. Summary: The tritium collection apparatus was connected to the WEA system via quick disconnects. When the flow outlet valve WEA-V-SR25/V28 was opened, the flow indicator immediately read 3000 cc/min, despite the flow inlet valve WEA-V-SR25/V22 not yet being opened. V22 is used to throttle the desired flow (300-1000 cc/min) through the tritium collector, but personnel were unable to stop or control flow via V22. WEA-SR25/V22 is no longer functioning and air leakage from or into this system is being prevented instead by the quick disconnect, WEA-QDC-SR25/14A. Recommend replace/repair of WEA-SR25/V22 before the next performance of 16.11.1 to prevent issue with collection of monthly tritium sample. <I> **** Actions Taken **** Contacted supervisor. Wrote CR. | 02-00-WEA-V-SR25/V22
388032 | CR | 20181219 |  | 3 | HPI-0.19 does not aligned with PPM 11.2.15.13 |  |  |  | N | NO | <C> This CR was found at INPROG and after review was moved to approved. <D> 11.2.15.13 gives direction that a CR should be generated if a PCE is determined to a level 2 or level 3. This is inconsistent with direction given in HPI-0.19, which is to generate a CR for all PCEs. <I> Discussed the discrepancy with HP Supervision
388035 | CR | 20181219 |  | 3 | ABN-TSW Procedure Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** ABN-TSW step 4.4.3 directs opening the main condenser vacuum breakers if a main turbine trip is required due to high vibration or temperature. This action is not conservative (closes the MSIVs/BPVs) and does not align with the high vibration or high temperature ARPs. The high vibration ARP (4.820.B1 drop 7-6) directs tripping the MT at 14mils if load reduction does not reduce vibration and opening main condenser vacuum breakers at 18 mils while coasting down; ABN-TSW should mimic the ARP direction. The high bearing temperature ARPs (4.820.B2 drops 2-6 and 3-1) do not direct opening main condenser vacuum breakers at all; ABN-TSW should mimic the ARP direction. Opening the main condenser vacuum breakers will not improve generator/SCW high temperatures after the main turbine has tripped.
388036 | CR | 20181219 |  | 3 | PPM 10.25.227 section 8.8.1 needs enhancement |  |  |  | N | NO | <D> **** Detailed Description **** During performance of section 8.8.1 of 10.25.227 it was discovered that there is no direction in the procedure to remove the braided stainless steel hose from the sample cart to AR-V-1 OUT sample point after all valve alignments are completed. <I> **** Actions Taken **** Discussed with HP and SM and notified supervisor.
388037 | CR | 20181219 | CAQ | B | (QA) Recurring theme â€“ Gaps in PU&A - ARMA |  |  |  | Y | NO | <C> SWP-CAP-06 Matrix Risk: Medium Cause: Unclear CAQ B/PERFIMP with investigation template(s) <D> **** Detailed Description **** (QA) Area Requiring Management Attention - ARMA. Quality identified a recurring theme with regards to gaps in procedure use and adherence across the station that had not been recognized. This theme has continued throughout the recent two year audit period. This period included 19 audits and multiple surveillances. In every case, Quality identified examples of procedure non-compliances. These shortfalls resulted in multiple Quality Findings, ARMAs and deficiencies and are pre-curser behaviors that could place the station in jeopardy for potential regulatory findings. Some examples identified by Quality over the period include: â€¢ January 2018: Special Nuclear Materials related CAPRs not performed as written (Quality Finding, AR-CR 377024) â€¢ January 2018: Second Verifications not performed for Special Nuclear Materials (SNM) (ARMA, AR-CR 377003) â€¢ January 2018: Main Control Room Temporary Modification Log Index not updated (ARMA, AR-CR 377029) â€¢ May 2018: Incorrectly processing of work order tasks resulting in lost Quality Assurance records (Quality Finding, AR-CR 380144) . While the examples above are associated with administrative procedures, it is an indication that behavior shortfalls exist specific to following procedures as written. Additionally, these shortfalls have manifested themselves into more recent significant issues. Some examples include: â€¢ Performing steps that should have been marked NA for current plant conditions causing equipment isolations. (AR-CR 387720) â€¢ Not signing onto a clearance order prior to performing work (AR-CR 387771) . Factual Basis - Examples Listed Above . Insights - â€¢ Personnel are not effectively reviewing procedures prior to work â€¢ Personnel are not ensuring procedures are updated to reflect current practices â€¢ Procedures and work instructions could not be performed as written, yet work continued This ARMA was identifed during the 2018 Corrective Action Program Audit AU-CA-18. For full details on this ARMA see the EDMS. - To Performance Improvement
388038 | CR | 20181219 | CAQ | D | (QA) CR Not Categorized as CAQ - Deficiency |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) AR-CR 387318 was incorrectly categorized as Severity 3 during CRG and Management Review. The condition of a surveillance testing acceptance criteria not aligned with current plant configuration is a Condition Adverse to Quality. Should it be used for emergent issue, incorrect criteria could be used to determine operability. . Factual Basis: â€¢ SWP-CAP-06, Condition Report Review, Attachment 8.1, definition for Condition Adverse To Quality in part states â€œdeficiencies in characteristic, documentation, or procedure that reduce the quality of an item or activity due to factors such as improper design, testing..â€ [italics added] â€¢ AR-CR 387318 categorized as a 3 under GBP-CAP-01. . â€¢ OSP-RHR/IST-Q703 was last revised 11/13/18, and this Surveillance does not match current configuration of RHR -MO-49. Should it be used for emergent issue, incorrect criteria could be used to determine operability. . used to determine operability. . used to determine operability. . used to determine operability. Insights: â€¢ Both CRG and Management Review recognized the need to revise surveillance OSP-RHR/IST-Q703 but failed to recognize that inaccurate acceptance criteria was a Condition Adverse To Quality . â€¢ AR-CR 387318 was subsequently changed from a Severity 3 to CAQ Severity C. This deficiency was identifed during the 2018 Corrective Action Program Audit - AU-CA-18. - Corrective Action Program <I> **** Actions Taken **** Initaited CR and Notified Corrective Action Supervisor <N> The priority has been corrected on the CR in question. No further action is required.
388039 | CR | 20181219 | CAQ | C | (QA) CAPR Not Annotated in Procedure - Deficiency |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Corrective Action to Preclude Repetition (CAPR) action was completed with the generation of PPM 11.2.23.45 however there is no annotation in the procedures sections or steps. . Factual Basis: â€¢ SWP-CAP-01, Corrective Action Program, Revision 36 Minor 2 in effect at the time, section 4.4 Note states â€œCAPRs MUST be annotated in their implementing documents as internal commitments, per the guidance in SWP-PRO-03.â€ â€¢ SWP-PRO-03, Writerâ€™s Manual, Revision 22 in effect at the time: o Section 2.2.3.m.2.d states â€œAnnotated steps added as a result of a Corrective Action to Preclude Repetition (CAPR) with reference number in French bracketsâ€ . o Section 2.2.3.M requires CAPRs to be listed in the references including French bracket â€œCAPR-â€œ designator â€¢ PPM 11.2.23.45, â€œManagement of Spent Fuel Pool Filters, Irradiated, and Non-Irradiated Items to Support Packaging, Transportation, and Disposal as Low-Level Radwaste,â€ Revision 0 issued on 3/15/17 to meet CAPR assignment 360236-05, contains no annotated steps or sections to AR-CR 360236. Additionally the reference to AR-CR 360236 is missing the French bracket designator to complete the cross-reference. . Insights: â€¢ The other CAPR assignments contained a cue to annotate CAPRs per SWP-PRO-03, however CAPR assignment 360236-05 did not include this cue to reinforce procedure compliance . This deficiency was identifed duriing the 2018 Corrective Action Program Audit - AU-CA-18. - Radiation Protection <I> **** Actions Taken **** Initiated CR and contacted Radiation Protection <N> Revision 000.001 to PPM 11.2.23.45 was issued on 12/31/18. The CAPR annotation was added into the purpose section of the procedure. No further action required.
388041 | CR | 20181219 |  | 3 | Update model WO PM for RHR-HX-2A based on work performed |  |  |  | N | NO | <D> **** Detailed Description **** No impact to plant. Enhancement only. This is to support future planning/maintenance. As part of the recent RHR -P-2A replacement, the torque value on the RHR-HX-2A (shell head to shell flange fasteners) was questioned for defaulting to the .5 of the PPM 10.2.10 value for a "generic" Composition gasket. (Step 4.28.7 of WOT 02033672-10). Engineering reviewed the actual Gasket being installed (CATID 5359) and supported going to a higher torque value based on the actual gasket being used and the bolting (still within the allowed torque value of the 5/8" 193 Gr B7 bolting within the design temp.) <I> **** Actions Taken **** Generated CR to track a revision to the model WO 01077381 (Step 4.16) under PMID 10161-01. Work step 4.28.7 of 02033672-10 initially had 70 ft-lbs resulting from the 140 ft-lbs of the bolting at the (480 Deg F) used 500 Deg F design temp for conservatism, then taking a .5 reduction due a "composition" gasket. This initially put the final torque value at 70 ft-lbs. Discussion with Engineering and review of CATID 5359 supported the gasket material and bolted connection to be torqued to a 140 ft-lb value. An assignment should also be to Engineering to review Model WO 01189957-01for RHR-HX-2B (PMID 10162-01) and adjust final torque value to allow for torquing bolting for the shell head to shell flange fastners under step 4.16 using CATID 5359 to 140 Ft-lbs. Recommend the specifics get added to both work orders that CATID 5359 model used was shown as a Garlock 3122TC, and that the 3122TC model should be referenced in the step such that if a 3122TC model is ever replaced by a different Garlock Part # that the torque value gets reviewed based on the gasket composition. <N> 140 ft-lbs is the maximum do not exceed torque value provided by Engineering for these fasteners at RHR-HX-2A for a 2018 RHR-A WOT. A better torque value to specify in the PM WOTs for RHR-HX-2A(B) and for WOTs associated with RHR-HX-2C probably should be the 110-116 ft-lbs range currently indicated in the CVI OMM 02E12-08,10 General Torque Procedure for 5/8â€ A193 B7 fasteners.
388042 | CR | 20181219 |  | 3 | DST-TEC-2 Chassis failure | N | N |  | N | YES | <D> **** Detailed Description **** recommend Non-CAQ 4 DST-TEC-2 which is the second chassis in a virtual pair failed to reload its supervisor module. Corporate Service to Rattlesnake was the only service affected by the outage. <I> **** Actions Taken **** Restored services after migrating link over to DC-TEC, opeing TAC case with Cisco for further troubleshooting, and possible RMA of DST-TEC-2 chassis. <N> **** Equipment Description **** N/A
388043 | CR | 20181220 |  | 4 | TMB-P-1C excessive seal leakage | N | N |  | N | YES | <D> **** Detailed Description **** TMU-P-1C's has excessive leakage. It cannot be quantified, it is spraying all over. Recommend packing adjustment if possible or plan maintenance during the outage. See EDMS for videos. | 02-00-TMU-P-1C
388044 | CR | 20181220 |  | 3 | TMU-CB-TMU1B breaker unexpected trip flags present | N | N |  | N | YES | <D> **** Detailed Description **** TMU-CB-TMU1B breaker unexpected trip flags present. Specifically on TMU-RLY-5051/TMU1B/C. See EDMS for photos. The pump was not running, the breaker was racked in and the lights indicated open. Two of three flags were in on the relay. <I> **** Actions Taken **** Informed CRS and reset the flags per CRS. Remained clear. | 02-00-TMU-CB-TMU1B
388050 | CR | 20181220 |  | 3 | Individual removed from training less than 24 hour notice |  |  |  | N | NO | <D> **** Detailed Description **** Mechanical maintenance removed a trainee from Leak Path Sealing (ME000796) with less than a 24 hour notice. This is the second time the individual has been removed and the last offering of the trainee. Make-up training will need to be scheduled. No documentation of PGM concurrence was provided. <I> **** Actions Taken **** Sent communication to PGM requesting concurrence per GBP -TQS-01. Notified Maintenance. Initiated CR. Recommend Severity 3 owed to AR-TRNMT.
388054 | CR | 20181220 |  | 3 | (QA) Pre-NRC inspection SA not scheduled - Deficiency |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Preparation for and scheduling of a pre-NRC Design Basis Assurance inspection self-assessment does not meet procedure requirements to ensure the station is ready for the inspection. Milestone preparation assignments are not entered into Asset Suite or reflected in the self -assessment schedule, contrary to GBP-LIC-08 â€œPreparation and Conduct of NRC Inspectionsâ€ and GBP-ASU-03 â€œSelf -Assessment and Benchmark Processâ€. Late self-assessment preparation and scheduling could challenge readiness for a major baseline inspection. Factual Basis: â€¢ The Design Basis Assurance (DBA) inspection is biennial with the next inspection scheduled in August 2019. â€¢ GBP-LIC-08, Preparation and Conduct of NRC Inspections, requires a focused self-assessment approximately 5-6 months prior to major baseline inspections. â€¢ The following focused self-assessment milestones from GBP-ASU-03, Self-Assessment and Benchmark Process, were missed: o Focused or Peer assessments should be entered into Asset Suite as an AR-SA at least one to two years before the activity is to be performed. o The responsible department manager should designate the team leader at least 180 days prior to the self-assessment. â€¢ The Design Basis Assurance inspection schedule is included with the annual self-assessment call letter submitted to department managers. Insights: â€¢ The Self-Assessment Coordinator issued a CY 2019 Self -Assessment and Benchmark Call Letter to department managers on 10/10/18. The due date to submit planned 2019 self-assessments was 11/19/18, however, many managers missed the due date. A third reminder to provide responses was sent to several managers on 11/28/18. Late submittal of planned self-assessments challenges the stationâ€™s ability to coordinate, prioritize and schedule these activities to ensure sufficient resources are available. Upon notification by Quality, the responsible line organization initiated AR-SA 387497 â€œFOCUSED SELF ASSESSMENT for 2019 NRC DBAI Inspectionâ€ on 12/4/18. This deficiency was identifed during the 2018 Corrective Action Program Audit - AU-CA-18. - Design Engineering <I> **** Actions Taken **** Initiated CR
388056 | CR | 20181220 |  | 3 | (QA) SA approvals and justifi not documented - Deficiency |  |  |  | N | NO | <D> **** Detailed Description **** (QA) Department manager approval for some focused self -assessment plans and due date extensions are not documented, contrary to GBP-ASU-03 â€œSelf-Assessment and Benchmark Processâ€. Justification is also not documented for some self-assessment due date extensions. This is a procedure compliance issue with no known adverse consequences, however, these behaviors could lead to a misalignment between management expectations and actual focused self-assessment conduct. Factual Basis: â€¢ GBP-ASU-03, Self-Assessment and Benchmark Process, requires the following: o Document the department manager/sponsor approval of the focused self-assessment plan in the SAPL assignment. o Department manager approval for focused self-assessment assignment due date extensions. o Document the justification for focused self-assessment assignment due date extensions in the assignment notes. o Document the justification for rescheduling focused self-assessments. â€¢ Department manager approval of the following focused self-assessment plans was not documented: o AR-SA 340139, Inspection Management o AR-SA 358034, Clearance Order o AR-SA 378159, Radioactive Waste Processing and RAM Handling â€¢ Department manager approval and justification is not documented on four due date extensions for the Inspection Management focused self-assessment plan (AS-SAPL 340139-01) This deficiency was identifed during the 2018 Corrective Action Program Audit - AU-CA-18. - Performance Improvement <I> **** Actions Taken **** Initiated CR
388057 | CR | 20181220 |  | 3 | (QA) Incomplete revision to GBP-ASU-03 - Deficiency |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The requirements to approve focused self-assessment rescheduling are internally inconsistent in GBP-ASU-03, Self-Assessment and Benchmark Process. Steps in the procedure were revised to remove the requirement for PARB approval to reschedule focused self-assessments to a different calendar year but the same requirement was not removed from an attachment to the procedure. Factual Basis: â€¢ GBP-ASU-03 step 4.3.5 requires SA Program owner concurrence if rescheduling within the calendar year or department manager if rescheduling outside of the calendar year. â€¢ GBP-ASU-03 Attachment 8.5 (d) states that all schedule changes for focused activities requires PARB chairman concurrence. . This deficiency was identifed during the 2018 Corrective Action Program Audit - AU-CA-18. - Performance Improvement <I> **** Actions Taken **** Initiated CR
388058 | CR | 20181220 |  | 3 | (QA) SWP-OPX-01 and OPEX-01 Non-Compliant - Deficiency |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Contrary to SWP-PRO-03 â€œWriter's Manualâ€, SWP-OPX-01 "Operating Experience Program" and OPEX-01 "Operating Experience Program Implementation Manual" did not use French Brackets to identify steps that meet all regulatory requirements committed. This is a procedure compliance issue. While no known regulatory requirements were missed, failure to identify regulatory requirements with-in procedures and manuals could result in the inadvertent removal of the requirement from these documents resulting in possible regulatory violation. Factual Basis: â€¢ SWP-PRO-03 step 2.2.3 m. 2) states, " WHEN a Requirement or Commitment is satisfied by a statement within the body of a procedure, THEN IDENTIFY the statement by placing the number in French brackets { }, immediately following the statement or referenceâ€¦." â€¢ The following sections or steps of SWP-OPX-01 "Operating Experience Program" were not identified with French Brackets per SWP-PRO-03 for regulatory commitments per NUREG 0737. o Section 4.6 o Steps; 3.4.6, 3.6.2, 3.6.4, and 3.7.5 â€¢ The following sections or steps of OPEX-01 "Operating Experience Program Implementation Manual" were not identified with French Brackets per SWP-PRO-03 for regulatory commitments per NUREG 0737. o Sections; 3.6 and 3.12 o Steps; 3.6.1, 3.6.2, 3.6.4, 3.6.5, 3.6.6 <I> **** Actions Taken **** Initiated CR
388060 | CR | 20181220 |  | 4 | Steam Leak at HCO-T-W54 | N | N |  | N | YES | <D> **** Detailed Description **** Steam leak discovered on 507RW on HCO-T-W54 <I> **** Actions Taken **** OPS notified | 02-00-HCO-T-W54
388061 | CR | 20181220 |  | 3 | (QA) Two OE Leads not meeting Requirements - Deficiency |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The audit team identified two OE Leads with no record of completing the Computer Based Training (CBT) requirement per SWP-OPX-01, Operating Experience Program and OPEX-01 Operating Experience Program Implementation Manual. Additionally, for one of the individuals identified, the team did not find a completed record for the required Job Familiarization Guide (JFG).The audit team reviewed screening committee attendance records from January 2018 through November 2018. Factual Basis: â€¢ One screening committee member attended 8 meetings and no record of satisfying the CBT requirement or having a signed JFG in the Screening Meetings Completed JFGs in SharePoint. . . â€¢ Another screening committee member attended 4 meetings and had not viewed the CBT, however, does have a signed JFG dating prior to the CBT requirement which was implemented September 8, 2017 Rev. 9. Insights: This is similar to previous issues identified in the two previous Corrective Action Audits. â€¢ AR-CR 360415 â€œ(QA) Two Departmental OE Leads Orientation Incompleteâ€ from AU-CA-17 Corrective Action Audit. â€¢ AR-CR 322939 â€œ(QA) Use of JFG for OE Screening Teamâ€ from AU-CA-15 Corrective Action Audit. <I> **** Actions Taken **** Initiated CR
388063 | CR | 20181220 |  | 3 | (QA) Station response to IER17-5 had no AR nbrs - Deficiency |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) While reviewing the station response to IER 17-5, the team identified a deficiency where the AR and assignment numbers were not listed. Factual Basis: â€¢ Response to IER 17-5 did not have AR and assignment numbers listed â€¢ SWP-OPX-01 4.1.5 g.3 requires that IERA assignment numbers are to be included in the IER response to INPO. â€¢ INPO 10-006 Appendix E also states â€œat a minimumâ€, â€œactions (including corrective action number and due date) to close any identified gaps. This deficiency was identifed during the 2018 Corrective Action Program Audit - AU-CA-18. - Performance Improvement <I> **** Actions Taken **** Initiated CR <N> coaching accepted by department. Information to INPO will not be updated based on the determination the station is fully implemented during the 2018 WANO evaluation. future IER implementations will include this lesson learned. no further action this AR
388068 | CR | 20181220 |  | 4 | Flickering Light on SEA-SMD-53 |  |  |  | N | YES | <D> **** Detailed Description **** SEA-SMD-53, the smoke detector for SEA-FN-52, has a flickering power lamp. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** GSB 456 HVAC room | 02-00-SEA-SMD-53
388069 | CR | 20181220 |  | 4 | Right flag dropped on RRC-RLY-5051/RRA/B | N | N |  | N | YES | <D> **** Detailed Description **** Right flag dropped on RRC-RLY-5051/RRA/B. control room informed and flag was succesfully reset. recommend trend. <I> **** Actions Taken **** reset flag | 02-00-RRC-RLY-5051/RRA/B
388070 | CR | 20181220 |  | 4 | turbin building 441 screen is partially obstructed w/debris | N | N |  | N | YES | <D> **** Detailed Description **** turbine building 441 ventilation screen by COND-P-2A is partially obstructed w/debris. please see picture attached. several of the other screens by the booster pumps have debris in them. please see pictures attached <I> **** Actions Taken **** wrote WR CR <N> **** Equipment Description **** TOA discharge plenums by the booster pumps
388071 | CR | 20181220 | CAQ | C | Benton County Dial up INOP | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** Call from Benton County stated thet DIal up Circuit INOP <I> **** Actions Taken **** created ticket with Carrier #2353629 Frontier - 3/OSNA/97149//GTNW
388072 | CR | 20181220 |  | 4 | B26 Deschutes Conf Rooms Occupied without Fire Alarm |  |  |  | N | NO | <D> **** Detailed Description **** The two new conference rooms in Deschutes 2-244 and 2-243 do not have the required fire alarm horn/strobes installed yet in accordance with the Fire Code. As a compromise to allow occupancy, Notice signs were installed to keep the doors open when meetings are in progress, so occupants would hear the other building fire alarm devices. I have personally coached people to open the doors, and I have had others tell me that the doors were closed and the room occupied. Since the signs are not working, I must remove my conditional occupancy approval and request that you post the rooms with construction signs to prevent occupancy until the required fire alarm devices are installed. <I> **** Actions Taken **** EMail and phone call to Facility Manager and Project Manager to close off the conference rooms until the required fire alarm devices are installed. . Signs installed to prevent conference room use until new fire alarm horn/strobes are installed and tested.
388073 | CR | 20181220 |  | 4 | Sounds like a steam leak in the Off gas preheater room. | N | N |  | N | YES | <D> **** Detailed Description **** Earlier we had a steam leak in the offgass preheater room the steam leak was identified and the room was quite again. today I heard what I believe is a steam leak in the room again. please evaluate if an entry is desired to investigate to include the necessary alara planning. <I> **** Actions Taken **** discussed with SM and srote WR/CR <N> **** Equipment Description **** T441 | 02-00-T-BLDG-MISC
388074 | CR | 20181220 | CAQ | D | Rod accumulator trouble alarm on CRD-HCU-1807 due to water. | Y | N |  | N | YES | <D> **** Detailed Description **** Rod accumulator trouble alarm on CRD-HCU-1807 due to water. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-HCU-1807
388075 | CR | 20181220 |  | 4 | HT-HTP-FP/8 ckt 44F Loss of Continuity Light Blinking | N | N |  | N | YES | <D> **** Detailed Description **** The yellow loss of continuity light is blinking for ckt 44F (4â€ Anti-Siphon Vent). The Red Power light is not illuminated. Inside the panel the circuit breaker 9 is labeled (via Sharpe marker) as the breaker for 44F and is closed. See EDMS for Photos. Please investigate and repair. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** Outside Building 33 (Flocculator building) | 02-00-HT-HTP-FP/8
388076 | CR | 20181220 |  | 3 | E-ATS-ASD/1 Displaying Odd Symbols | N | N |  | N | YES | <D> **** Detailed Description **** The small screen on the front of E-ATS-ASD/1 is displaying odd symbols. All other indications are normal. See EDMS for Photos. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** ASD Building | 02-00-E-ATS-ASD/1
388083 | CR | 20181220 |  | 3 | DES-2-5 is out-of-date for preparation and revision of EMS |  |  |  | N | NO | <D> **** Detailed Description **** PPI ENG DES-2-5 is out-of-date for preparation, revision, and approval of Equipment Modification Specifications (EMS). DES-2-5 continues to call out use of the DES-2-1 (PDC), DES-2-7 (MPDC), and DES-2-10 (MALT) legacy processes and needs to be updated for untilization of the current Standard Design Process (SPP) modification and substitution processes. . This is an administrative process issue only.
388087 | CR | 20181220 |  | 3 | Condensate Transient â€“ 12/6/18 - Lessons Learned |  |  |  | N | NO | <D> **** Detailed Description **** When CFD system D/P reaches 50# relay CR30 in the RWCR engerizes which prevents closure of COND-V-76 until reset. This relay is very loud and was incorrectly thought to be an issue, but it de-energized properly upon reset of the high D/P condition per the ARP. A note describing this should be added to the ARP. . Also, in the ARP for booster pump suction there needs to be an added enhancement to check for proper operation of COND -PCV-5 and COND-PCV-7. <I> **** Actions Taken **** Wrote CR
388088 | CR | 20181220 | CAQ | C | Update IMDS TEA-RIT-13 for new detector |  |  |  | N | NO | <D> **** Detailed Description **** The TEA-RE-13A detector was replaced per WO-02128865, and PMT was performed successfully. The detector settings were adjusted for the new detector, so the Window Calibration Items for Channel 2: High Range Gross on IMDS TEA-RIT-13 needs to be updated. The new values are; Modify Lower Level: 0.200 Modify Select: Inputx1 Modify Noise Rej Cnt: 3 Modify Smoothing FC: 6.000* Modify Gain: 7.59 Modify HVPS: 1776 <S> Item No. 024 of the Configuration Database-Channel Items for Channel 2: High Range was also changed to 2.50E+01 per the WO instructions. This is the background subtract feature for the detector channel item, and the IMDS should be updated.
388089 | CR | 20181220 |  | 4 | Dose overrun for Electrical Maintenance for November, 2018. |  |  |  | N | NO | <D> **** Detailed Description **** Electrical Maintenance receved 1855 mrem for the month with an estimated goal of 1016 mrem. The dose overrun was mainly atributed to work on RHR-MO-49 for an acuator replacement and MOV testing. Monthly dose loaded in the EDMS of this CR. <I> **** Actions Taken **** Generated CR per GEN-RPP-16. Maintenance Manager Notified Electrical Componenet Manager, Maintenance CIC, and Radiological Support Supervisor.
388092 | CR | 20181220 | CAQ | C | FLEX Inventory Issues | N | Y |  | N | YES | <C> CRBB (CR Bring Back) - Engineering to Gather More Information for Severity/Allocation. <D> **** Detailed Description **** While performing the first of six periodic inventory verifiications of FLEX Buildings 82 and 600 per AR-CR -384345 there were multiple issues identified. In Building 600 it was identified that three cables for DG-5 were missing. FLEX-CONN-E/4A4, FLEX-CONN-E/4A5, and FLEX-CONN -E/4A6 were found in Building 82 with the other similar cables. These need to be moved to Building 600. In both buildings there was supposed to be three air filters each for FLEX-VEH-3 and FLEX-VEH-4 (International Model 2602212C1) . Facilities was notified and has ordered four new filters. These filters are used during an ash fall event for the FLEX tow vehicles. There is no forecasted volcanic eruptions or indications of abnormal volcanic activity. Therefore not having all filters at this time does not put the FLEX mitigation strategies at risk. Some components were found in the wrong compartments and restored to their assigned location. All procedural improvements have been documented and are being sent to the Operations Procedure Writers. <I> **** Actions Taken **** Notified Supervisor. Notified facilities. <N> **** Equipment Description **** Buildings 82 and 600. | 02-CM-FLEX-CONN-E/4A6
388094 | CR | 20181220 | CAQ | D | E-DG-4 failed to shutdown when it was supposed to | N | Y |  | N | YES | <D> **** Detailed Description **** E-DG-4 failed to shutdown when it was supposed to. Several attempts were made with the emergency pushbutton. the fuel line was eventually crimped to starve the DG <I> **** Actions Taken **** DG survellance was good untill that point where the diesel was supposed to turnoff. ther was a noise or sound like it was going to stop but never did. <N> The correct EPN is E-GEN-DG4. E-DG-4 is status NONEQUIP (duplicate of E-GEN-DG4). | 02-00-E-DG-4,02-00-E-GEN-DG4
388096 | CR | 20181220 | CAQ | D | Rod accumulator trouble alarm on CRD-HCU-5427 due to water. | Y | N |  | N | YES | <C> CR reopened to cross reference additional WP 02082590. marked completion required box, then taken back to complete <D> **** Detailed Description **** Rod accumulator trouble alarm on CRD-HCU-5427 due to water. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-HCU-5427
388097 | CR | 20181220 |  | 4 | Multiple Leaks at CWPH Chemical Feed SKID | N | N |  | N | YES | <D> **** Detailed Description **** Evidence of Leaks were noted at CF-RV-821B; CF-V-824; CF -FG-41; CF-PCV-42; CF-FG-42; CF-V-833; and CF-V-825. As none of the CF pumps are currently running it is hard to tell if these leaks would be active or have sealed due to chemical buildup. See EDMS for detailed pictures. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** CWPH | 02-00-CF-FG-41,02-00-CF-FG-42,02-00-CF-PCV-42,02-00-CF-RV-821B,02-00-CF-V-824,02-00-CF-V-825,02-00-CF-V-833
388098 | CR | 20181220 |  | 3 | Change to OPS-2 Logs |  |  |  | N | NO | <D> **** Detailed Description **** This is a request to change FORM 27154, OPS-2 LOG. CCH -CR-1A Status Checks please remove from the long instructions to â€œVERIFY WCH-V-51AI CLOSED (WMA-TCV-12A Bypass).â€ And CCH-CR-1B Status Checks please remove from the long instructions to â€œVERIFY WCH-V-51BI CLOSED (WMA -TCV-12B Bypass).â€ See attached email with Engineering in EDMS.
388099 | CR | 20181220 |  | 3 | Quick Card, Repower SM-4 |  |  |  | N | NO | <D> **** Detailed Description **** Recommend a new quick card be created to support repowering SM-4 under certain circumstances. Currently under the conditions of E-CB-S2 failure to auto close on the unit lockout bus transfer and a failure of DG-3 to start the reactor operator will manually close E-CB-S2. This will repower SM-2 but SM-4 will remain de-energized until ABN -ELEC-SM2/SM4 is referenced which directs repowering SM-4 per the system operating procedure. In circumstances when HPCS is needed to support adequate core cooling a quick card would be beneficial to expedite repowering SM-4 from SM-2 and allow HPCS to provide adequate core cooling.
388101 | CR | 20181221 | CAQ | D | 83E emergency power alarm failed to come in (E-TR-B) | Y | N |  | N | YES | <D> **** Detailed Description **** While testing E-RLY-83/TRB, Exercise Transfer switch, Model WO 0206244 task 01, 83E emergency power alarm failed to come in (E-TR-B) per step 4.5.2 of same WO. Transfer switch worked satisfacorily. <I> **** Actions Taken **** Contact MCR and obtained permissioin to continue with the procedure. the switch was taken to test to verify the light did work. | 02-00-E-RLY-83/TRB
388102 | CR | 20181221 |  | 4 | temporary carboys staged/left at CWPH labeling challenged |  |  |  | N | YES | <D> **** Detailed Description **** temporary carboys of sulphiric acid that is staged/left at CWPH is having its labeling challenged. the plate with the label was found off on one carboy and was reattached with tie wraps since the clasp were broken. Please evaluate what we are going to do with theses and move them to a more suitable environment. Please see pictures attached. <I> **** Actions Taken **** reattached placard holder. . This is reminiscent of the issue where acid was inadvertently added to the ASD glycol system. <N> **** Equipment Description **** CWPH
388103 | CR | 20181221 | CAQ | C | CCH-CR-1B Condenser head shows signs of corrosion | Y | Y |  | N | YES | <D> **** Detailed Description **** This CR is to document the as-left condition of chiller CCH-CR-1B Inlet (south) condenser head during performance of WOT 02109572 (CCH-CR-1B - INSPECT/CLEAN CONDENSER TUBES). The condenser head is showing signs of corrosion. See pictures in EDMS folder of this CR which show the location of the degradation. One notable area of crevice corrosion is occurring on the inside corner of the gasket channel. The degradation area is the size of a quarter and ~ 5/16â€ deep. The CCH engineer reviewed this condition with the Materials Engineer, the Heat Exchanger Component Engineer and the SW engineer. There is adequate seating surface for the gasket to maintain pressure integrity of Service Water. Additionally, there is no history of leaks at this location providing further evidence to support its ability to perform its intended function of pressure integrity. Mechanics suggested that a contingency task be added to the next condenser head inspection to perform weld build-up on the affected areas. Currently there is adequate channel depth to keep gasket in place. Based on engineering review the condition described below does not prevent the CCH system from performing its design function. There exists a 2 year PM to clean and inspect the condenser. There is reasonable assurance that this issue will not prevent the chiller from performing its design function until the next inspection. Extent of Condition: The CCH-CR-1A Condenser is subject to the same conditions as seen in this CR . Recommend that a contingency task for weld buildup be added to next CCH-CR-1A Condenser Cleanup / Inspection PM. <I> **** Actions Taken **** Informed Shift Manager. | 02-00-CCH-CR-1B
388104 | CR | 20181221 | CAQ | D | Charger E-C1-2A tripped on OV during ESP-C12A-B101 | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of WO 02105557-01, charger E-C!-2A tripped on overvoltage. Approximately 60 minutes into the 90 minute test when the current was raised from 60 amps to 200 amps, a small perturbation was seen in voltage and current that resulted in the charger tripping on overvoltage. Test results have been recorded to help diagonose cause. The redundant charger is still operating normally as validated by Operations. Test equipment has been removed from the charger and stored. <I> **** Actions Taken **** Notified CRS, recorded test results for evaluation, secured from the load test. <N> **** Equipment Description **** W467 charger room | 02-00-E-C1-2A
388105 | CR | 20181221 | CAQ | D | RCIC-DT-1 inboard and thrust bearing oil level low | Y | N |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was observed that RCIC-DT-1 inboard oil level was 1/8 inch below the low level mark and the thrust bearing oil level was 1/4 inch below the low level mark. <I> **** Actions Taken **** Informed CRS and wrote CR | 02-00-RCIC-DT-1
388106 | CR | 20181221 |  | 3 | (NRC) Transient Combustible Permit Required for E-TR-M2 Oil | N | N |  | N | NO | <D> **** Detailed Description **** Cross referenced CR's document oil leakage from bushings on E-TR-M2. Actions being performed include draining the leakage into barrels staged in the transformer yard. The transformer yard is considered a plant area in PPM 1.3.10C. Per PPM 1.3.10.C Attachments 7.2 and 7.3, a transient combustible permit is required with a duration of 7 days for storage of more than 5 gallons of oil in MODES 1, 2 or 3. Currently there are two empty drums and one drum nearly half full of oil drained from E-TR-M2 (there is greater than 5 gallons of oil in this drum). Leak rate is estimated at one quart per hour (6 gallons per day). This makes maintaining less than 5 gallons of drained oil in the transformer yard challenging. Request the Fire Marshal evaluate for Special Combustible Storage Circumstances per 1.10.3C Section 3.6. <I> **** Actions Taken **** Informed control room.
388107 | CR | 20181222 |  | 4 | Received â€œH2 WTR CHEM TROUBLEâ€ | N | N |  | N | NO | <D> **** Detailed Description **** Received â€œH2 WTR CHEM TROUBLEâ€ P840-A3 drop 7-6 Due to Supply Facility trouble. No alarm exist at the computer in the Chemistry lab to explain the Supply Facility Trouble. Alarm cleared and stayed cleared. <I> **** Actions Taken **** Informed CRS
388109 | CR | 20181222 | CAQ | D | MS-RIS-610C screen unreadable | N | Y |  | N | YES | <C> CR reopened to cross reference additional WP 02137365. marked completion required box, then taken back to complete <D> **** Detailed Description **** MS-RIS-610C screen is on, unresponsive and unreadable. <I> **** Actions Taken **** Wrote CR | 02-00-MS-RIS-610C
388110 | CR | 20181222 | CAQ | D | CMS-TR-6 lost voltage to MUX for approx 5min. | N | Y |  | N | YES | <D> **** Detailed Description **** CMS-TR-6 lost voltage to MUX for approx 5min. All temperature readings were lost during that time and everything read "error", with the exception of point 001 reading "0 MUX V". After approx 5 minutes readings returned to normal and point 001 read "26 MUX V" <I> **** Actions Taken **** Monitored all parameter to verify indications and informed supervision. <N> CMS-TR-6 failed again following the writing of this CR and did not return. CMS-TR-6 is currently not available. | 02-00-CMS-TR-6
388111 | CR | 20181222 |  | 4 | SEC-BRE-35 Door Latch not funtioning as designed | N | N |  | N | YES | <D> **** Detailed Description **** SEC-BRE-35 Door Latch not funtioning as designed. For information contact Security 2185. <I> **** Actions Taken **** Security Supervision notified. CR/WR generated for mechanical support. <N> **** Equipment Description **** BRE South West of Radwaste Roll up door.
388112 | CR | 20181223 |  | 4 | Dataglance failed to make automatic log entry |  |  |  | N | NO | <D> **** Detailed Description **** While completing WO 02136477 Dataglance did not make automatic eSOMS narrative log entries. The surveillance was performed on paper and scanned and attached electronically. The work order was progressed using the dataglance desktop software vice the tablet. <I> **** Actions Taken **** Closed it out in esoms manually.
388113 | CR | 20181223 | CAQ | D | CCTV 22/22T Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** CAS received a Video Loss on NVR1P/1B and NVR2B for CCTV22 and CCTV22T. Maintenance required. <I> **** Actions Taken **** CR/WR generated. Security Supervision notified. Compensatory measures initiated. | 02-00-SEC-CCTV-22,02-00-SEC-CCTV-22T
388114 | CR | 20181223 | CAQ | D | CCH-CR-1B Oil Level High | Y | Y |  | N | YES | <C> CR reopened to cross reference additional AR 395968 WP 02124750, marked completion required box, then taken back to complete <D> **** Detailed Description **** During OSP-CCH/IST-M702 logs (CCH-CR-1B operability) compressor oil level was found high out of spec. the level is supposed to be below half in the upper sight glass; actual oil level is full in upper sight glass. Step 7.1.50.b says that it is preferred to lower oil level while it is running, but if a refrigerant qualified mechanic is not available, it can be shut down and lowered via the Aux Oil Pump. <I> **** Actions Taken **** Informed MCR, logged out of spec in OSP-CCH/IST-M702. <N> This CR will be taking credit for high oil level upon machine shutdown per OSP-CCH/IST-M702. Oil was lowered by using the Aux Oil Pump due to the unavailabilitiy of a refrigerant mechanic. | 02-00-CCH-CR-1B
388118 | CR | 20181223 | CAQ | D | Recieved P603.A8 5-8 "SLC TANK LEVEL HIGH/LOW" | Y | Y |  | N | YES | <D> **** Detailed Description **** Recieved SLC Tank high level alarm, level by SLC-LI-601 is ~5100 gal, TDAS x077 is 5045 gal, and 5050 gal locally. Tank temperature has not changed. <I> **** Actions Taken **** Unable to identify any inleakage to the system. | 02-00-SLC-TK-1
388119 | CR | 20181223 | CAQ | D | SW-TE-2A reading erratically. | Y | N |  | N | YES | <D> **** Detailed Description **** SW-TE-2A reading swinging from 40F to 120F. <I> **** Actions Taken **** CRS informed. logged inop in logs. | 02-00-SW-TE-2A
388120 | CR | 20181223 |  | 4 | Main Control Room ARGOS Out Of Service | N | N |  | N | YES | <D> **** Detailed Description **** Main Control Room ARGOS HP-EQ-42803 is out of service with what seems like a power supply or CPU issue. Both the main screen and main control panel have no power. The CPU has a green light and seems to be running as normal (no loud or uncommon noise). Restart of the CPU yielded no results. The red foot and hand detector beams can be seen visually, but they trigger nothing when entering the machine. <I> **** Actions Taken **** Placed monitor out of service, notified MCR staff, RP Supervision and initiated WR <N> **** Equipment Description **** TG 501 Main Hallway MCR Entrance | 02-00-HP-EQ-42803
388121 | CR | 20181223 |  | 4 | Transformer 1/11 at a vacuum | N | N |  | N | YES | <D> **** Detailed Description **** Found Transformer 1/11 at a vacuum, Turbine Building was colder than normal. Transformer was at -0.3, acceptable range is GTE 0 & LTE 4 psig. <I> **** Actions Taken **** Informed MCR, initated AR. | 02-00-E-TR-1/11
388122 | CR | 20181223 | CAQ | D | E-Lite failure E-BU-SWA8/1 | N | N |  | N | YES | <D> **** Detailed Description **** During quarterly inspection 02132096-01, E-BU-SWA8/1 had low battery capacity and unit failed <I> **** Actions Taken **** Informed ops, maintenance and WWM <N> **** Equipment Description **** Rad WST 454 | 02-00-E-BU-SWA8/1
388123 | CR | 20181223 | CAQ | D | FDR-V-92 showing intermediate with RMS in 'CLOSE' | N | N |  | N | YES | <D> **** Detailed Description **** During performance of SOP-RW-CROSSCONNECT, FDR-V-92 (FDR -TK-6 Influent) is closed; during this performance, FDR-V -92 indicates intermediate. The valve was cycled a few times to verify proper RMS contact made, and the valve showed intermediate with every CLOSE. The valve opens fully with switch in OPEN. During the period of this valve indicating intermediate, there has been a slight and steady increase in the level of FDR-TK-6, which leads me to believe the valve is actually in an intermediate position, and is not an indication error. Cause should be investigated. <I> **** Actions Taken **** Write CR. | 02-00-FDR-V-92
388124 | CR | 20181223 |  | 3 | Procedure Change OPS 4 Logs |  |  |  | N | NO | <D> **** Detailed Description **** A change is needed for the Short Instructions for on the FLEX Comm Batteries log in Building 600 taken on Sunday Dayshift per OPS 4 Logs FORM 27156. The instructions say to verify radio batteries charging. There are no radios or radio batteries in building 600, only satellite phone batteries per OSP-FLEX-A106. This was likely a copy and paste error from the building 82 log. Building 82 does have both radios and satellite phones staged. <I> **** Actions Taken **** Informed MCR
388125 | CR | 20181223 | CAQ | D | Evidence of coolant leak on DG-4 | N | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02135840 then taken back to complete <D> **** Detailed Description **** There is evidence of a coolant leak on DG-4 at a hose connection between the engine block and the coolant heater DG-H-DG4/ENG. The leak is not currently active but there is buildup up of dried coolant. See EDMS for photos. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** Outside Diesel Building | 02-00-E-DG-4
388126 | CR | 20181223 |  | 4 | FDR-SUMP-W1 Sample required | N | N |  | N | YES | <D> **** Detailed Description **** FDR-SUMP-W1 was identified to have high TOCs and was pumped out by laboreres (ref. WR # 29144460). W1 Sump is currently still Caution Tagged in PTL. Please obtain a sample from W1 sump, for Chemistry to analyze for TOCs. If sample results show normal TOC levels, W1 sump pump should be returned to service, and CT removed. <I> **** Actions Taken **** Informed MCR. Verified chemistry has not taken a sample of W1, since it was initially reported to have high TOCs under WR 29144460. <N> **** Equipment Description **** RW 437 | 02-00-FDR-SUMP-W1
388127 | CR | 20181223 |  | 3 | COND-V-178 | N | N |  | N | YES | <D> **** Detailed Description **** Amp readings taken for the PMT 02071388-02 were, A-1.62, B-1.55, C-1.81. This put the calculated unbalance at 15.66%. This is over the less than 10% acceptance value. <I> **** Actions Taken **** initiated CR. Notified supervision and Control room staff <N> **** Equipment Description **** COND-V-178 / COND-42-2R10D . The formula being used in the maintenance work instructions is wrong; refer to CR 387609. Per a formula in Managing Motors (2nd Edition), the current imbalance is calculated by dividing the maximum deviation from the average current by the average current. When this formula and the current values listed are used, the imbalance would be 9.04%. | 02-00-COND-V-178
388128 | CR | 20181223 |  | 4 | Handheld Contamination Monitor CM-11 at HP PAP Quit Working | N | N |  | N | YES | <D> **** Detailed Description **** HP-EQ-53254 (CM-11) at HP PAP quit working and makes a clicking sound when plugged in. The display screen shows no indication of being powered up. <I> **** Actions Taken **** Tagged OOS, unplugged, and initiated this CR and Work Request. <N> **** Equipment Description **** HP PAP on wall, just inside the RCA.
388129 | CR | 20181223 | CAQ | C | (NRC) CRD pump oil bubblers have different configurations | Y | N |  | N | YES | <D> **** Detailed Description **** NRC resident identified that the inboard oil bubblers of the CRD pumps have different piping configurations. CRD -P-1B has a straight piping connection off the side of the bubbler to the bearing housing. CRD-P-1A has a piping configuration that looks similar to a drain trap under a sink. A review of the OMM manual (CVI OMM 02C12-09,11) on page 75 shows a bubbler piping configuration that matches the field configuration of CRD-P-1B. Oil level is visible in the sight glasses of the bearing housings on both pumps and there is visible oil in the bubblers, so lubrication to the bearings is not a concern. See EDMS for pictures. <I> **** Actions Taken **** Wrote this CR. | 02-00-CRD-P-1A,02-00-CRD-P-1B
388130 | CR | 20181223 |  | 3 | (NRC) Capture devices used on diesel generator air receivers |  |  |  | N | NO | <D> **** Detailed Description **** NRC resident inspector identified that there are capture devices (red Panduit straps) on ball valves associated with DG-1 and DG-2 air receiver flasks, but not on valves associated with DG-3 air receiver flasks. SOP-DG3-LU does not require these valves to be locked open (LO), so there is no plant component status control issue. There are also no equipment issue identified in this CR. Evaluate whether a similar requirement to capture valves associated with the DG-3 starting air system similar to that of DG-1 and DG-2 should be adopted. <I> **** Actions Taken **** Wrote this CR.
388131 | CR | 20181224 |  | 4 | ROA-FL-1 at End of Roll since 8-25-2018 | N | N |  | N | YES | <D> **** Detailed Description **** ROA-FL-1 has been at End of Roll since 8-25-2018 Also, 1 of the upper level filter spools has fallen off and is laying on the upper deck. It goes against our Excellence Model to allow the ROA filter to go this long without being properly addressed/ changed out <I> **** Actions Taken **** Had to make an entry into ROA unit to pull blocked filter media out of the way to allow air flow to RB HVAC. <N> **** Equipment Description **** ROA-FL-1 RB 572 | 02-00-ROA-FL-1A
388132 | CR | 20181224 |  | 4 | Only 2 of the 4 OG dryer regen trains are functional | N | N |  | N | YES | <D> **** Detailed Description **** Only 2 of the 4 OG dryer regen trains are functional. This causes constant swapping from 'C' to 'D' and back. Any failure in either of these trains will cause severe limitations for the operability of the OG Regen syatem. <I> **** Actions Taken **** Informed MCR | 02-00-OG-DY-30A,02-00-OG-DY-30B
388133 | CR | 20181224 |  | 3 | MET Tower and RB obstruction lights not registered with FAA |  |  |  | N | NO | <D> **** Detailed Description **** When calling to issue a Notice to Airman with washington state the process is complicated considering the MET tower and RB are not rigistered with the FAA. Recommend rigistering the MET tower and RB obstruction lighting with the FAA, this would make the NOTAM process easier for the contol room personnel and improve the accuracy of the process. <I> **** Actions Taken **** Wrote CR. <N> CR (388133) Subject and Description word changed from FCC to FAA at the request of OPS.
388134 | CR | 20181224 |  | 4 | WO 02120096-05 MET tower preoutage notificaiton |  |  |  | N | NO | <D> **** Detailed Description **** The WO task listed above was not able to be completed as scheduled. The FAA does not accept planned NOTAMs more that 72 hrs ahead of time. <I> **** Actions Taken **** Wrote CR
388135 | CR | 20181224 |  | 4 | Alarm sender/Events/Printer are not working on TDAS and PPCV | N | N |  | N | YES | <D> **** Detailed Description **** Alarm sender/Events/Printer are not working on TDAS and PPCV. Did try to "stop" and "initiate" but issue still exist. Need to investigate and resolve the issue. <I> **** Actions Taken **** CRS/SM informed. <N> CR (388135) Subject and Description word changed from Sander to Sender at the request of OPS. | 02-00-TDAS-COMP-8715
388136 | CR | 20181224 |  | 3 | Dataglance not making log entry |  |  |  | N | NO | <D> **** Detailed Description **** When I set a task to working in Dataglance the automatic log entry in eSOMS didnt occur. WO 02130308-01 <I> **** Actions Taken **** Worte CR
388137 | CR | 20181224 | CAQ | D | CRD-TK-125/4623 hi water lvl alarm | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-TK-125/4623 hi water lvl alarm OPS 2 drained water / alarm clear <I> **** Actions Taken **** OPS 2 drained water / alarm clear | 02-00-CRD-TK-125/4623
388141 | CR | 20181225 |  | 3 | Revise multiple 10.4 series Rigging procedures |  |  |  | N | NO | <D> **** Detailed Description **** Revise the following procedures: â€¢ PPM 10.4.1 Pendant Controlled Crane Inspection, Maintenance, and Testing â€¢ PPM 10.4.2 Chain and Lever Operated Manual Hoist Inspection, Maintenance, and Testing â€¢ PPM 10.4.4 Mobile Crane Operation, inspection, Testing, and Maintenance â€¢ PPM 10.4.5 Reactor (MT-CRA-2) and Turbine Building (MT -CRA-1) Overhead Traveling Crane Inspection, Maintenance, and Testing â€¢ PPM 10.4.10 JIB Cranes and Electrically Operated Hoists Inspection, Maintenance, and Inspection â€¢ PPM 10.4.11 Design, Fabrication, Testing, and Control of Below the Hook Lifting Devices â€¢ PPM 10.4.13 Storage/Retrieval Machines Inspection, Maintenance, and Testing . Purpose of the revisions is to remove redundant Site Rigging Coordinator signatures, minor editorial additions, additions of Hoists returned to service and placed in the PM program and removal of Hoists that have been retired and no longer used. . Recommend assignment to AR-MNTPROG/AR- MNTPROC <I> **** Actions Taken **** Initiated CR and provided mark-ups of the procedures to the procedure writer
388142 | CR | 20181225 | CAQ | D | MCR ENS phone | N | Y |  | N | YES | <C> CR Trend to 388145 <D> **** Detailed Description **** The ENS phone at the CRO3 desk in the MCR rings partially on occasion. The phone test performed each night provides assurance that the NRC can still contact the MCR if needed. <I> **** Actions Taken **** Wrote CR. <N> **** Equipment Description **** ENS phone located at the CRO3 desk.
388143 | CR | 20181225 |  | 4 | COND-V-42 cuases SST high level alarms. | N | N |  | N | YES | <D> **** Detailed Description **** When COND-V-42 automatically opens to fill the FPC skimmer surge tanks, it does not close early enough to prevent the skimmer surge tank high- high level alarms. COND-V-42 needs to be adjusted so that it will close a little earlier so that the skimmer surge tank high-high level alarms do not come in after normal make-up. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-COND-V-42
388144 | CR | 20181225 |  | 4 | Dialing TMU Pump House at 2516 causes Fire Alarm. | N | N |  | N | YES | <D> **** Detailed Description **** Dialing the TMU Pump House at 2516 with the plant phone line causes the reception of a TMU Pump House, 4.FCP.1, 8 -2, Fire Alarm. This is repeatable. OPS 4 was in the TMU Pump House. When we attempted to call him by dialing 2516, the MCR received the Fire alarm. There is no fire or smoke in the TMU Pump House. <I> **** Actions Taken **** CRS and SM notified and witnessed this event. <N> **** Equipment Description **** FCP.1, 8-2
388145 | CR | 20181225 | CAQ | C | NRC "Red Phone" in MCR sporadic ring tone | N | Y |  | N | YES | <D> **** Detailed Description **** The NRC "Red Phone" / Emergency Notification System Phone in the Main Control Room is ringing (for ~ 1/4 second) at random times. This is the phone that the NRC calls on nightly to verify unit status and provide threat authentication code. There has been no issue with receiving these nightly calls. <I> **** Actions Taken **** Notified the CRS / Shift Manager and submitted CR and WR. This is same issue as 388142. See other CR for IOD. <N> **** Equipment Description **** NRC Red Phone in the Main Control Room by lead RO desk
388146 | CR | 20181226 | CAQ | D | Received Oscillograph Started, H13-P800.C4.4-3, alarm | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm at 00:27 on 12/26/18. Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 239kV B: 240kV C: 239kV; E-TR-B A: 119kV B: 118kV C: 118kV. The following sensors were tripped and are reset: J7 Sensor - 500kV Neutral Ground Overcurrent and J12 Sensor - SM-8 Undervoltage. BPA Dittmer reports the cause was a momentary single phase fault to ground on the Ashe - Slatt 500kV #1 line (B phase) with auto re-closure. No equipment damage or emergent outage needed. The 230 kV and 115 kV systems were not involved. Ashe 500 kV voltage is 539 kV <I> **** Actions Taken **** Notified the CRS and Shift Manager. Submitted CR. Fault was on Ashe-Slatt 500Kv Line - lines supporting TR-S and TR-B were not impacted.
388148 | CR | 20181226 | CAQ | D | Rod Accumulator Trouble Alarm for CRD-HCU-2603. The alarm i | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm for CRD-HCU-2603. The alarm is due to high water and OPS 2 has drained the H20. <I> **** Actions Taken **** followed ARP. Wrote this CR. | 02-00-CRD-HCU-2603
388149 | CR | 20181226 |  | 3 | PCR ENG-DES-50 Att 7.2 DES-6-1 interface |  |  |  | N | NO | <D> **** Detailed Description **** ENG-DES-50 p. 37 requires listing affected Software Requirements Specifications on the ADL, which conflicts with DES-6-1 and DES-6-3. Recommend removing excessive detail from ENG-DES-50. <I> **** Actions Taken **** E-mail procedure sponsor.
388153 | CR | 20181226 |  | 3 | Procedure revision for 16.9.1 needed |  |  |  | N | NO | <D> **** Detailed Description **** WO 02105880-01 16.9.1 needs procedure revision. MTE needs updated due to invalid range and MTE (Vakudtbe OS309 is no longer supported 0-20 in H20) Also Step 7.5.14 needs to be moved inbetween step 7.5.8 and step 7.5.9. Performing the procedure as written will leave air in the transmitter. Fixing the order of the work steps will eliminate this issue. <I> **** Actions Taken **** Supervision notified. WR was generated to do proper venting at the end of the procedure. <N> **** Equipment Description **** CW pump house
388155 | CR | 20181226 |  | 3 | GEN-RPP-14 Procedure Issue |  |  |  | N | NO | <D> **** Detailed Description **** GEN-RPP-14, Control of Temporary Shielding, implements Procedure Control Temporary Changes in regards to the installation of Temporary Shielding. It was noted that current practice in regards to 50.59 reviews is more conservative than suggested by GEN-RPP-14. This Condition Report is to resolve the issue. <I> **** Actions Taken **** Informed Supervision
388156 | CR | 20181226 |  | 3 | MI-1.35 Credit Work Order Process doesnâ€™t work |  |  |  | N | NO | <D> **** Detailed Description **** MI-1.35 Credit Work Order Process-section 3.6 Shop Coordinator Responsibilities 3.6.1 When the Crediting Work Order has been completed, perform the following steps: a. Take the Credited Work Order to FINISHED status . NOTE: After the finished date is added to the 300 panel, the ENTER key must be pressed to save the date. . b. For PM Work Orders, ensure the FINISHED date on the Crediting Work Order is entered on the M300 panel of the Credited Work Order. c. Take the Credited Work Order to COMPLETE status. . Most Asset Suite rights have been taken away from supervisors. This process cannot be worked as written. Procedure needs to be re-written and the process changed or Asset Suite rights given back to supervisors to allow the process to be worked as written. Recommend CR assignment to AR-MNTPROG. <I> **** Actions Taken **** initiated CR
388158 | CR | 20181226 |  | 3 | Reinforcement of Chemistry Fundamentals/Standards |  |  |  | N | NO | <D> **** Detailed Description **** During a recent independent evaluation it was noted that reinforcement of Chemistry fundamentals/standards is needed to improve performance. <I> **** Actions Taken **** CR is being initiated to create actions to drive performance improvement. Recommend disposition as a NCAQ Severity 3 to AR-CHEM.
388160 | CR | 20181226 |  | 4 | DW-DWS-4 is still leaking when DW-V-170 is open | N | N |  | Y | YES | <D> **** Detailed Description **** DW-DWS-4 is still leaking when DW-V-170 is open. After clearing the caution tag that was on DW-V-170 for the shower leaking, as soon as the valve was cracked open, the shower started leaking again. I proceeded to open the valve approx 3/4 full open and attempted to re-seat the shower control valve, but it would not re-seat and continued to leak. Recommend replacing DW-DWS-4 control valve. <I> **** Actions Taken **** Re-shut DW-V-170 and informed MCR and wrote CR. | 02-00-DW-DWS-4
388162 | CR | 20181226 |  | 3 | Editorial revision required for ISP-WEA/PRM-X301 |  |  |  | N | NO | <D> **** Detailed Description **** An editorial revision is required for ISP-WEA/PRM-X301. <I> **** Actions Taken **** Recommend implementing change with the next revision. Markup is provided in EDMS documents.
388164 | CR | 20181226 |  | 3 | Procedure enhacement on 15.2.3 |  |  |  | N | NO | <D> **** Detailed Description **** PPM 15.2.3 does not have a note stating that the craft can use a test cart for testing fire alarm heads sensitivity. On step 7.2.3 reference attachment 9.1 and it should be 9.2 for this is a 2 yr test not a 1 yr test. <I> **** Actions Taken **** Craft stop, notified supervision and PSRO that a note needed to be added. The note should state the following as per other fire alarm procedures. Note: The removed detector may be tested using an alternate detector base, such as another base in the zone being tested or on a test cart. The placement of this not should be added at the begining of step 7.2 of PPM 15.2.3 <N> **** Equipment Description **** PPM15.2.3
388165 | CR | 20181226 | CAQ | D | CSP-V-800/26 yoke started backing out whilst operating. | Y | N |  | N | YES | <D> **** Detailed Description **** CSP-V-800/26 yoke started backing out whilst operating during OSP-CONT/IST/Q701. Stopped and infromed MCR. Recieved direction to close CSP-V-800/25 and write WR/CR. Observed LT 1/64th of a turn before stopping. <I> **** Actions Taken **** Informed MCR. Closed CSP-V-800/25. Engaged to WC org. | 02-00-CSP-V-800/25
388166 | CR | 20181226 |  | 3 | EWP data/signatures lost RRA-CC-17 work |  |  |  | N | NO | <D> **** Detailed Description **** After completing the final signatures for weld acceptance and as found component positions WO 02112149-02. Craft returned from the field and all data/signatures had somehow been lost. EWP help line contacted and currently there is no one on site that can look into retrieving the lost data (All on vacation). Operations was notified of the issue and that all work is complete and the clearance D-RRA-CC-17 -002 can be lifted, Work Week Manager, and Shop Manager notified of the issue. Notes were put into ESOMâ€™s clearance order identifying the issue as well. <I> **** Actions Taken **** Notified MCR, WWM of the issue and initiated CR <N> Current Process: After a Validate is performed and a Document has been identified as changed it will request the user to either Replace, Append or Reject the changes. Replace: When a replace is selected the software will delete the current document and replace it with the new document. Append: When an Append is selected the software will add another revision of the document. On 12/26/18 @ 8:27 am, Validate was performed on WO Package 02112149-02 and during the validate process the Master5 and Material Request documents showed that they had been updated. The action by the Supervisor was to replace the Master5 and the Material Request documents, therefore the previous documents were deleted and replaced by the new ones. . User has been coached on the difference between Append, Replace and Reject and what should have happened in this reported case.
388167 | CR | 20181226 | CAQ | D | Both GDS valve status display screen wonky | N | N |  | N | YES | <D> **** Detailed Description **** GDS valve status display screen wonky. Please see attached video in EDMS docs. This screen is currently unusabe and not reliable for indication. Please return this valuable tool back to functional. <I> **** Actions Taken **** Wrote the AR at supervision behest. Contated maintenance org. | 02-00-PDIS-MON-GDS1,02-00-PDIS-MON-GDS2
388169 | CR | 20181226 |  | 3 | AED SPC 15B.1 Table 1 update for RWCU(20)-3 piping needed |  |  |  | N | NO | <D> **** Detailed Description **** Design Specification AED SPC 15B.1 (Non-ASME Piping) Table 1 (Design Conditions) currently contains two entries for RWCU(20)-3 piping with differing information - on page 15B.1-134 and on page 15B.1-136a. The Design Condition information for RWCU(20)-3 piping on page 15B.1-134 appears to be incorrect and the Design Condition information for RWCU(20)-3 piping on page 15B.1-136a appears to be correct. Please update AED SPC 15B.1 Table 1 for RWCU(20)-3 piping. This is a legacy administrative issue. Suggest resolution by Design Engineering - O&M Mechanical.
388170 | CR | 20181226 |  | 3 | Alber BCT test equipment not reliable during ESP-C12A-B101 |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Electrical craft performed 2-year load test on E-C1/2A per work order 02105557-01. On Friday CR#388104 was generated because The charger tripped off while testing was in progress. Electricians resumed testing on 12/26/2018. Testing was set up in automatic mode with Alber BCT test equipment. However, once the test began, within the first four minutes, the voltage displayed on the computer changed from 130vdc to 250vdc. Within the next two minutes the voltage changed back to 130vdc. Then again, at about 22 minutes into the test, the display showed 250vdc again. the analog meter on the charger and fluke meter never showed the fluctuations. So, with supervisor approval, and per guidance of ESP-C12A-B101, step 7.1.12, craft changed testing to manual control and made data collection using digital multimeters and clamp-on meter. Test acceptance criteria are met per section 6.0 of ESP-C12A-B101. <I> **** Actions Taken **** notfied engineering, Supervision and resumed testing in manual mode. Generated CR <N> **** Equipment Description **** e-c1/2a
388171 | CR | 20181226 |  | 3 | AED SPC 1 does not contain information for RWCU(20)-3 piping |  |  |  | N | NO | <D> **** Detailed Description **** Design Specification AED SPC 1 (ASME Piping) does not appear to contain Table 1 (Design Conditions) or Table 2 (Piping Material Specifications) information for Code Group C (ASME III/3) RWCU(20)-3 piping. It appears that some information for this RWCU piping is currently in AED SPC 15B.1 (Non-ASME Piping). This is an administrative issue only (possibly associated with EC PDC 12061). Suggest resolution by Design Engineering (O&M Mechanical).
388172 | CR | 20181226 | CAQ | D | Rod accumulator trouble alarm on CRD-HCU-3839, low pressure | Y | N |  | N | YES | <D> **** Detailed Description **** Rod accumulator trouble alarm on CRD-HCU-3839 due to low nitrogen pressure. CRD-HCU-3839 was recently worked per WO 02136289. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-HCU-3839
388173 | CR | 20181227 | CAQ | B | Unposted Radiation Area found on RX 522 North Pipe Space | N | N |  | N | YES | <C> RISK: Medium. CAUSE: Uncertain. Investigation Template Required <D> **** Detailed Description **** Unposted Radiation Area found on RX 522 N. Pipe Space. At RX522 North Pipe Space HRA boundary a dose rate of 5.8 mRem/hr was found. The area affected by this radiation is not within a posted Radiation Area. This condition is not in compliance with ENW procedure PPM 11.2.7.1 <I> **** Actions Taken **** Identified the dose rates, posted the affected area as a Radiation Area, two different radiation meters were used to perform the survey. The dose rate was verified by a second HP Technician. The area was posted as a Radiation Area, and independently verified by a second HP Technician. HP Supervision was notified in accordance with HPI 0.19, and a log book entry was made. The Main Control Room CRS/SM was notified. See survey map 20181216-3 for documentation. Verified this was not a violation of Technical Specification 5.7. <N> **** Equipment Description **** RX 522 North Pipe Space
388174 | CR | 20181227 |  | 4 | TOA-HC-1B coil KILO leaking | N | N |  | N | YES | <D> **** Detailed Description **** TOA-HC-1B coil KILO leaking was shooting cold water out the end of a tube. cold water too! <I> **** Actions Taken **** isoalted coil <N> Changed wording on CR subject line and description fields from TO-HC-1B to TOA-HC-1B at the request of Initiator. | 02-00-TOA-HC-1B
388175 | CR | 20181227 |  | 4 | toa-HC-1B coil LIMA leaking | N | N |  | N | YES | <D> **** Detailed Description **** TOA-HC-1B coil LIMA leaking. coil was spraying cold water out of the end of the coil. <I> **** Actions Taken **** wr/ cr isolated coil | 02-00-TOA-HC-1B
388183 | CR | 20181227 |  | 3 | Electronic reinvestigation PHQ's are not functioning in SSIS |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Access Authorization is currently unable to send electronic reinvestigation PHQ's. <I> **** Actions Taken **** Contacted Information Services and the Vendor regarding the issue. Access Authorization will be using paper reinvestigation PHQ forms until the issue is resolved. <N> This CR will close with no Actions - See Note below - Issue Resolved. CW made a change to their firewall that blocked us from creating ePHQs. They have now resolved the issue. This problem did not involve any of our servers but was a problem on Curtiss-Wrights end. - CSKADO Email from CW 12/31/18
388184 | CR | 20181227 |  | 3 | fields in Impact Statements should not be blank |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During task previews, craft use the Impact Statement to better understand how the job impacts personnel and the plant. At times, some of the lines (or entire sections) are left blank. See the CORC and RP/ALARA sections of WO# 02104721-01 for an example. This leads us to question if it was reviewed or not. To better align with documentation practices and procedures, shouldnâ€™t these sections/lines be marked N/A? <I> **** Actions Taken **** brought it up in our D15 and wrote this CR <N> in the example given the CORC Review section was blank because a CORC review was not required. This is indicated by the designation C/NR in the Requirements section of the work order task. Similarly the ALARA review section was not filled out for the same reason. It is not required to fill out forms that are not required. This is similar to the practice of volume 10 procedures that only include appliocable sections or attachments without specifically identifying which ones don't apply.
388186 | CR | 20181227 |  | 4 | Green OK lights for RRC-VBI-P1A/PXY flashing a 1 time/sec | N | N |  | N | YES | <D> **** Detailed Description **** Green OK lights for RRC-VBI-P1A/PXY are flashing a 1 Hz. OMM 719-00,3 pg 508 says this means that "transducer has not been ok since last re-set". ARP says "This condition is noted by either a Flashing Green or an extinguished OK LED at the Panel Device. These are advisory alarms indicating sensor failure or device malfunction.". Vibration levels appear to be noraml as observed on camera. Investigate and correct or reset as needed. There are no corresponding alarms for RRC-P-1A in currently. <I> **** Actions Taken **** Wrote this CR. Generated WR. | 02-00-RRC-VBI-P1A/PXY
388188 | CR | 20181227 | CAQ | D | DEH fluid â€“ OEM recommended limits exceeded (x3) | Y | Y |  | N | YES | <D> **** Detailed Description **** Lab results for a DEH fluid sample taken on 12Dec2018 returned three values that exceeded a DEH fluid OEM recommended limits. Each of the three were related to high particulate count for the given size range. Particle count for a 100ml sample should be: 5-10 Micron - LT 9700 10-25 Micron â€“ LT 2680 25-50 Micron - 380 The sample for these particle sizes returned counts of 14680, 7676*, and 448 particles, respectively. Section 4.4.3.8 and the following [Table 4-24] provide Turbine OEM particle count recommendations. For a Siemens/Westinghouse unit such as CGS the limits for 5-10 micron particles is 24,000 and a count of 5,360 for the 10-25 micron sized particles. [See document in EDMS.] Trend information: This should be considered the first occurrence this cycle. The prior report showed elevated numbers, but was well within normal band. This latest report confirms a trend. Last cycle saw multiple occurrences. The cause was determined to be failed insulation in vicinity of DEH lines, as well as steam leaks blowing near DEH lines, such that the DEH lines were exposed to excessive heat. The condition is reemerging. The leak on the HP Turbine West end appears large and may be contributing to this condition. (See CR AR 385656 and OSCR AR 387690 ) Additionally, the Resistivity value has dropped to 19 G-Ohm-cm. The preferred value is GE 20. This condition signals that DEH-F-9 filter media should be replaced. Continue to monitor, write CRs on filters with high dP and replace. *This value is above the turbine OEM recommended limit <I> **** Actions Taken **** discussed with supervisor | 02-00-DEH-F-9,02-00-DEH-TK-2
388190 | CR | 20181227 | CAQ | D | SJAE Cond Outlet Rad high alarm. | N | Y |  | N | YES | <D> **** Detailed Description **** Following draining the moisture trap, 4.602.A5 4-3 (SJAE Cond Outlet Rad High) was received. Level rose from 31mR/hr to 52mR/hr and started to decay slowly. Trending CR <I> **** Actions Taken **** Chemistry contacted to investigate. Ops Log entry made. <N> **** Equipment Description **** mcr | 02-00-OG-RIS-612
388192 | CR | 20181227 |  | 4 | BWRVIA Model failed to run |  |  |  | N | NO | <D> **** Detailed Description **** The BWRVIA Radiolysis and ECP Model has failed to successfully run on a EN Corporate network computer. The software repeatedly produces an error when trying to run a Case for the current operating cycle. Attempted troubleshooting with EPRI and the IS Call Center with no success. The BWRVIA Model is required to be run by BWRVIP-62 and BWRVIP-190 to verify sufficient hydrogen is being injected to maintain proper molar ratios of hydrogen to oxidants. Recommend category D closure to ITSR 388191. <I> **** Actions Taken **** Contacted EPRI for troubleshooting assistance. Contacted the IS Call Center for Adminstrator help. Sent EN data to EPRI for testing. Initiated AR-ITSR 388191 for additional help in resolving the error.
388195 | CR | 20181227 |  | 3 | ATWS Strategy Improvement |  |  |  | N | NO | <D> **** Detailed Description **** The PPM 5.5.11 strategy, to mitigate an ATWS, lists steps not directly related to driving control rods prior to the steps to individually insert them. Performance of those steps allows excessive time to transpire before mitigating actions are taken. During a hydraulic ATWS, this includes direction to repower RPS-B, removal of two fuses, turning a key lock bypass switch, installation of jumpers in 4 panels between 8 relays and resetting the scram. During an electric ATWS, removal of 10 fuses in 2 panels on 8 different terminals. Since control rods can be inserted, even with a scram inserted, as long as drive header pressure can be established, our process should allow operators to commence control rod insertion without delay in parallel with these separate actions to mitigate the ATWS. <I> **** Actions Taken **** See EDMS for 5.5.11 recommended changes to page 5 and 6 which separate the actions and allows entry to insert rods for timely response. CRO1 should have the ability to insert control rods while CRO2 performs the rest of PPM 5.5.11. Additional clarification in OI-15 may be needed.
388196 | CR | 20181227 |  | 3 | Negative Trend in Investigation Template Completion Times |  |  |  | N | NO | <D> **** Detailed Description **** A negative trend for completing Investigation Template assignments in the Engineering Department has been identified after review of OPIT and HUIT assignments since 6/18. This performance trend is visible on the "RCE, CCE, EQIT, HUIT, OPIT - Timeliness" KPI in sharepoint. See timeliness spreadsheet in EDMS. This performance does not meet the 14-day completion time expectation in SWP-CAP-01. <I> **** Actions Taken **** Reviewed performance for the Engineering Dept. in this area and initiated CR to analyze the negative trend.
388200 | CR | 20181227 |  | 3 | MS-PIC-18A setpoint does not match IMDS | N | N |  | N | YES | <D> **** Detailed Description **** The setpoint displayed on MS-PIC-18A is at approximately 310 psig. According to the IMDS for this component, the setpoint should be 200 psig. Currently, the indicated pressure is reading 395 psig with output pressure of 0 (zero), which means the valve is in the appropriate position at full shut. This is not the first time that this PIC has been found with a setting other than that listed in the IMDS. Earlier this cycle the setting was at 200 psig; however, it has since been changed. Recommended actions: 1) make the setting match the IMDS for configuration management integrity, and 2) conduct data collection during the next shutdown to validate 200 psig value or determine if new setpoint is required. [Ensure setpoint does not impact calc as in CR AR 375853] <I> **** Actions Taken **** discussed with supervisor discussed with main control room <N> **** Equipment Description **** TG471 east | 02-00-MS-PIC-18A
388202 | CR | 20181227 |  | 3 | Main Turbine Lube Oil appearance is degrading | N | N |  | N | YES | <D> **** Detailed Description **** Visual inspection of Main Turbine Lube Oil shows the oil is degrading. The oil appears frothy and entrained with bubbles and/or moisture. Sources of moisture are typically from steam leaks IVO oil seals to the bearing pedestals. The S5 leak on the west end of the HP Turbine (CR AR 385656) is the most likely contributor. Results from oil sample analysis for Dec2018 are not currently available in AMS. Actions needed: 1. Complete oil analysis for water in the oil to provide indication if intrusion [if found, determine if it is Main Steam/Sealing Steam or TSW], and 2. If moisture content is GE 400 ppm, then increase the frequency of oil samples from monthly to at least every two weeks to allow for better monitoring of the. <I> **** Actions Taken **** Sent email to lubrication engineer, discussed with Main Control Room | 02-00-TO-TK-2
388203 | CR | 20181227 |  | 3 | greater than two year work order on the schedule for T-12 |  |  |  | N | NO | <D> **** Detailed Description **** A work order that was planned in 2015 was placed on the schedule to be worked in March of 2019. The planning procedure requires that work orders two years and older be returned and replanned to current standards. Recommend this go to Maintenance Planning to perform further reviews to ensure no other old work orders are at approved status <I> **** Actions Taken **** 1- Notified the unit coordinator and the planning supervisor. 2- Returned the work order to planning to replan. 3- Changed the planners name to a current planner. 4- searched for other work orders with the old planners name, no other work orders were found with this issue.
388204 | CR | 20181227 |  | 3 | Procedure revision required for ISP-RWCU-B301 |  |  |  | N | NO | <D> **** Detailed Description **** ISP-RWCU-B301 needs to be revised to change computer point. The computer point currently in the procedure reads out in lbm/hr and the procedure requires gpm. Change computer point being monitored from "B009" to "B009GPM" <I> **** Actions Taken **** Discussed procedure change with IC component group manager and initiated CR to revise procedure.
388205 | CR | 20181227 |  | 4 | SEA-FN-51 | N | N |  | N | YES | <D> **** Detailed Description **** When performing WO #02122287-01 on PPM 15.2.11 2 yr sensitivity check craft noticed low flow alarm on OBHV-1 for Fan SEA-FN-51. <I> **** Actions Taken **** Craft stop work , notified supervision and control room of low flow alarm. Initiated CR. | 02-00-SEA-FN-51
388206 | CR | 20181227 |  | 3 | Small bore RWCU pipe calculations |  |  |  | N | NO | <D> **** Detailed Description **** In the Building 64 (B64) hardcopy calculation file, small bore Gilbert Commonwealth RWCU pipe calculations before RWCU-1778-1 do not physically exist in the file hardcopies. Additionally, small bore Gilbert Commonwealth RWCU pipe calculations before AED CAL RWCU-1796-5 do not exist in Asset Suite / Portal J. Hard copies for calculations RWCU-1778-1 through RWCU-1796-4 physically exist in the hard copy calculation file but do not exist as AED CAL documents in Asset Suite / Portal J. Suggest resolution by Design Engineering (O&M Mechanical). This is an administrative issue only.
388207 | CR | 20181227 |  | 3 | Computer in EO area has large X across sign in (50BKFB2) |  |  |  | N | YES | <D> **** Detailed Description **** almost all of the sign in blocks have this X across the block see attached screen grab. service number for the computer is 50BKFB2 <I> **** Actions Taken **** wr/cr <N> **** Equipment Description **** Equipment Operator area.
388208 | CR | 20181227 |  | 3 | Desktop in Equipment Operator center webpage display issues |  |  |  | N | YES | <D> **** Detailed Description **** Desktop computer Dell Optiplex 7040 service tag 4HCTJB2 doesn't display webpages properly in Internet Explorer. See attached example of peoplesoft login page. Recommend repair/replace as necessary. <I> **** Actions Taken **** Generated AR/WR. <N> **** Equipment Description **** Equipment Operator center, Yakima/GSB 1st floor. 4HCTJB2
388209 | CR | 20181227 |  | 4 | Loose positioner cover found on TMU-LCV-2A | N | N |  | N | YES | <D> **** Detailed Description **** Loose positioner cover found on TMU-LCV-2A <I> **** Actions Taken **** Wrote this CR to document as found and as left condition, Tightened thumb screws on positioner cover Â¼ turn past finger tight. Cover appears to be tight no further issues discovered, work complete R.Cooper 12/17/18 <N> **** Equipment Description **** tmu-lcv-2a positioner cover | 02-00-TMU-LCV-2A
388210 | CR | 20181227 | CAQ | D | HPCS-LS-1A DID not reset as expected | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** during perfomance of ISP-HPCS-Q901 WOT 0210587201, the AF reset value of HPCS-LS-1A was not captured due to switch not reseting in the expected band from previous performance of ISP. Possible internal sticking of switch is causing this issue <I> **** Actions Taken **** Talked with CRS/Supervisor, and *1 the AF reset values and continued with the calibration attachment 9.1 of procedure. Calibrated HPCS-LS-1A into CC tolerance SAT. Created CR for trending | 02-00-HPCS-LS-1A
388211 | CR | 20181227 |  | 3 | Conduit access cover left removed on Open Phase equipment | N | N |  | N | YES | <D> **** Detailed Description **** two conduit cables in the 525 comm room have access covers removed. Conduits are labeled ABPAI-0011-001 and go top the open phase detection system. I think this work is done and covers should be installed. see pictures attached. additionally there is some drywall that can be repaired/replaced. <I> **** Actions Taken **** wrote CR <N> **** Equipment Description **** RW 525 comm room Williams Plant Services and CPM Work.
388212 | CR | 20181228 |  | 4 | CWPH Electrical vault has about 4â€™ to 5â€™ feet of standing wa | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** CWPH Electrical vault has about 4â€™ to 5â€™ feet of water in it, craft were unable to see if the sump pump was working or not but, it appears we will need to place an additional pump in the vault to more water. <I> **** Actions Taken **** Wrote this CR and contacted the CRS <N> **** Equipment Description **** CWPH electrical vault | 02-00-P-BLDG-MISC
388213 | CR | 20181228 | CAQ | D | Received TG BLDG 501 WEST END ULTRAVIOLET fire alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received TG BLDG 501 WEST END ULTRAVIOLET fire alarm, FCP-1 drop 14-3. There were no indications of fire, nor were there any indications on FP-UVD-11. FCP-1 alarm was able to be reset. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-FP-UVD-11
388214 | CR | 20181228 |  | 4 | RFW-P-1A speed is at maximum allowed bias | N | N |  | N | NO | <D> **** Detailed Description **** RFW-P-1A speed (bias) was raised slightly as directed by the ODMI for RFW-P-1B Pump Axial Thrust Displacement. (RFW-VBI-XE/P1B channel A indicates 16 mils - which is the action level in the ODMI for bias adjustment). Procedural guidance in ARP 4.840.A1 (7-5) step 4 and in SOP-RFT-START allows a maximum speed deviation of 350 rpm with flowrate not to exceed 19,000 gpm. RFW-P-1A speed was raised by only 10 rpm (total bias is now 110 rpm above RFW-P-1B) but RFW-P-1A flowrate is at its maximum of 19,000 gpm as indicated on RFW-FI-2A. No change in RFW-P-1B pump axial thrust was noted. Also, RFW-P-1B axial thrust has been steady at ~ 16 mils (i.e. not degrading). The above referenced ODMI was issued on 12/27/18 with new guidance for action at 16 mils. Previous action was to notify the CRS at 18 mils. Further actions to adjust bias will require additional procedural guidance or lowering RX power <I> **** Actions Taken **** Notified the CRS and Shift Manager.
388215 | CR | 20181228 | CAQ | D | Rod accumulator trouble on CRD-HCU-1807 due to high moisture | Y | N |  | N | YES | <D> **** Detailed Description **** Rod accumulator trouble on CRD-HCU-1807 due to high moisture <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR | 02-00-CRD-HCU-1807
388220 | CR | 20181228 |  | 3 | Unable to locate tarp for WR 29145818 | N | N |  | N | YES | <D> **** Detailed Description **** WR 29145818 requires use of a tarp below the temporary pond for PMT of the FLEX pumper truck. Operators were unable to locate the tarp. Warehouse personnel also were unable to locate the tarp that should be staged with the temporary pond. The temporary pond will be used without the tarp and operators will take care to remove any debris from the area before filliing the temporary pond. Request a new tarp be purchased or the existing tarp be located and staged with the temporary pond for future use in annual testing of the FLEX pumper truck. <I> **** Actions Taken **** Notified MCR. | 02-00-B5B-P-1
388221 | CR | 20181228 |  | 3 | Cannot authorize WO 02128980 in DataGlance |  |  |  | N | NO | <D> **** Detailed Description **** Work order 02128980 scheduled for today 12/28/2018 cannot be authorized in DataGlance, there are no holds in passport and DataGlance shows only 1 hold which shows released. <I> **** Actions Taken **** Contacted supervision and the maintenance supervisors authorized maintenance to perform the work since we had circ water blow down secured just to perform this maintenance activity. <N> There was a CWO Hold (â€œHold for PM Current Occurrence Creditingâ€) on 02128980 that was not released on until 12/31/18. The previous PM WO, 02127977, was COMPLETED on 12/31/18, therefore releasing the Hold on the next PM WO Occurrence which was 02128980. . The CWO hold is on the Parent WO, not at the Task level, so unless you look at the WO in Asset Suite you do not know the CWO Hold has not been released. The CWO hold will prevent the next WO from being worked, this way PM WO cannot be worked out of sequence.
388222 | CR | 20181228 | CAQ | D | B5B-P-1 one tire pressure at 90 psig | N | Y |  | N | YES | <D> **** Detailed Description **** Per WO 01148474-01 the B5B-P-1 truck tires are to be kept at 100-110 psig. One tire on the passenger side was found at 90 psig while several others were at about 100 psig (bottom of band). Note that it was in the 30's outside (truck was in building 600). At least 1 tire needs air. This CR is for facilities to add air as required. <I> **** Actions Taken **** Informed SSS. | 02-00-B5B-P-1
388223 | CR | 20181228 | CAQ | D | relamping of essential fluorescent fixtures in control room | N | Y |  | N | YES | <D> **** Detailed Description **** Per Work order 02128987 and PPM 15.2.39, electricians performed monthly inspection of 34 control room fixtures. Seven fixtures require new lamps, but all fixtures on attachment 9.9 of 15.2.39 meet criteria of having at least one lamp lit, which is a $ sub-step of step 7.1.10. A work request will be generated to have fixtures relamped. Reference 15.2.39 attachment 9.9 item numbers 1,6,9,11,12,13 and 21 for fixtures requiring lamps. <I> **** Actions Taken **** Write CR and generated work request to relamp fixtures <N> **** Equipment Description **** control room L.9/12.8
388224 | CR | 20181228 |  | 3 | WO 01148474-01 needs updating (B5B-P-1) |  |  |  | N | YES | <D> **** Detailed Description **** The monthly B5B-P-1 run per WO 01148474-01 needs updating in regards to the air compressor. It is not normally plugged in due to the lack of additional extention cords and the truck has an engine driven air compressor; so it is simply not needed. This is a request to update the WO to allow 'if needed' or similar wording or just remove it. After started, the engine take between 30 and 60 seconds to build up sufficient air pressure per the procedure. Steps 4.4 and 4.24 mention the compressor. <N> **** Equipment Description **** WO update | 02-00-B5B-P-1
388225 | CR | 20181228 | CAQ | D | B5B-P-1 generator fuel gauge not working | N | Y |  | N | YES | <D> **** Detailed Description **** Per WO 01148474-01the B5B-P-1 fuel gauges in the cab (2 of them) are to read full. The generator gauge does not work, reads empty (low). A previous CR for braking a level gauge may be the contributor: CR 387290. Visually verified the three upper tanks full. It will also be recommended that the upper fuel tanks be repaired; they have lots of corrosion at the fill nozzle. | 02-00-B5B-P-1
388226 | CR | 20181228 |  |  | SLC tank level is becoming deviant from expected behavior. |  |  |  | N | YES | <D> SLC tank level is becoming deviant from expected behavior. The level has slowly increased from an expceted level of ~4995 gal to a peak of 5070 indicated (step change from 5040) then dropped to 5020 and finally settled out at ~5030 gal. The level indications were recently checked in tolerance under WR 29145341 with no other action taken. Further DW supply to tank was checked closed. Air flow to hte tank bubbler was verified to be correct. EO operator recommended "rodding out" the bubbler to allow more unrestricted air flow as that it is possible to has crystals for boron form and restrict air flow. This seems to be consistant with the obeserved indications. Please correct this issue. There is a blue DOT on SLC-LI-601 indicaton and X077 is utilized for OSP-INST-H101 daily. Followed ARP for high level alarm in MCR. <I> Had operator investigate as much as reasonable possible. informed supervivion. Responed to ARP. Informed SM/CRS. | 02-00-SLC-FIC-4,02-00-SLC-LI-1,02-00-SLC-LI-601,02-00-SLC-LT-1
388227 | CR | 20181228 | CAQ | C | SLC tank level is becoming deviant from expected behavior.. | Y | Y |  | N | YES | <D> **** Detailed Description **** SLC tank level is becoming deviant from expected behavior. The level has slowly increased from an expceted level of ~4995 gal to a peak of 5070 indicated (step change from 5040) then dropped to 5020 and finally settled out at ~5030 gal. The level indications were recently checked in tolerance under WR 29145341 with no other action taken. Further DW supply to tank was checked closed. Air flow to hte tank bubbler was verified to be correct. EO operator recommended "rodding out" the bubbler to allow more unrestricted air flow as that it is possible to has crystals for boron form and restrict air flow. This seems to be consistant with the obeserved indications. Please correct this issue. There is a blue DOT on SLC-LI-601 indicaton and X077 is utilized for OSP-INST-H101 daily. Followed ARP for high level alarm in MCR. <I> **** Actions Taken **** Had operator investigate as much as reasonable possible. informed supervivion. Responed to ARP. Informed SM/CRS. <N> Reopened CR to correct notes in assignment #1. | 02-00-SLC-FIC-4,02-00-SLC-LI-1,02-00-SLC-LI-601,02-00-SLC-LT-1
388228 | CR | 20181228 | CAQ | D | SEC - CCTV 22 and CCTV 22T | N | N |  | N | YES | <D> **** Detailed Description **** SEC - CCTV 22 and CCTV 22T Not funtioning as designed. <I> **** Actions Taken **** Comp measure initiated, Security Supervision notified and CR/WR generated. | 02-00-SEC-CCTV-22,02-00-SEC-CCTV-22T
388229 | CR | 20181229 |  | 3 | PPM 1.5.18 requires changes |  |  |  | N | NO | <D> **** Detailed Description **** Now that the FLEX equipment is covered under LCS 1.11.1; step 6.1.3.d of PPM 1.5.18 needs to read "CLOSE the LCS tracking sheet" vice "CLOSE the Admin tracking sheet on -the-fly action" <I> **** Actions Taken **** CR written
388230 | CR | 20181229 |  | 4 | Action Required to prevent oily spill to the environment. | N | N |  | N | NO | <D> **** Detailed Description **** MCR recieved "Fuel Oil Polish Building Trouble" alarm (H13-P800.C2.10-3). Cause of the alarm is a high sump level on the Fuel Oil Polishing Bldg sump. This sump presently is awaiting clean-out following a fuel oil spill which ocurred on 12/18/18 due to a leaking valve, DO-V-58 per WR 29146193. This sump must be cleaned out in order to prevent a oily spill to the environment. Per the ARP, the sump must be pumped into barrels and these must be disposed of per SWP-ENV-02. The sump must then be wiped down and cleaned since it normally directs outflow to storm drains. <N> **** Equipment Description **** Sump outside of Fuel Oil Polishing Bldg
388239 | CR | 20181229 |  | 4 | Received ASD/A input transformer trouble alarm 4.602.A6 3-4. | N | N |  | N | YES | <D> **** Detailed Description **** Received ASD/A input transformer trouble alarm 4.602.A6 3 -4. Dispatched Equipment Operator to investigate. All local indications are normal. Liquid temperature 40 C, alarm set point 90 C. Winding temperature 47 C alarm set point 120 C. Transformer pressure 1 psig, high pressure alarm set point 10 psig. Oil level 0.3 this is within the normal band. Alarm is locked in. Outside temperature is 49 F. <I> **** Actions Taken **** Informed MCR and generated a WR | 02-00-RRC-RLY-K10A
388240 | CR | 20181229 |  | 4 | eSoms work hour discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** 2 craft were not in eSoms for their normally scheduled shifts, 12/26/18 and 12/27/18. Discrepancy was identified while verifying eSoms when calling out OT. <I> **** Actions Taken **** Discussed issue with maintenance scheduler and maintenance manager. Scheduler identified that both discrepancies were caused by improperly entering PT into eSoms. See initiator or scheduler for details.
388241 | CR | 20181229 |  | 3 | Demin Trailer silica analyzer not working | N | N |  | N | YES | <D> **** Detailed Description **** The demin trailer was found to be rejecting water to the waste line. This occurs when the silica is reading too high. It was initially thought that the resin bed was exhausted but on further investigation, it was found that the silica analyzer was not working properly. <I> **** Actions Taken **** Contacted the vendor to inform of the issue. He is enroute to the plant for repair. Security and the shift manager have been notified. This is vendor owned and maintained equipment. <N> **** Equipment Description **** MUD trailer outside of BLDG 33.
388242 | CR | 20181229 | CAQ | D | Received H13-P800.C5 drop 6-7 125 VDC B1-7 GROUND alarm. | Y | N |  | N | YES | <D> **** Detailed Description **** Received H13-P800.C5 drop 6-7 125 VDC BATTERY B1-7 GROUND alarm. Ground is approximately 20K ohms. No abnormalities on bus S1-7 voltage or current. After 13 minutes ground returned to infinity and alarm was reset. Operators were dispatched to investigate with nothing abnormal noted. <I> **** Actions Taken **** Reset alarm after ground returned to normal. | 02-00-E-B1-7
388243 | CR | 20181229 | CAQ | C | TS Bases Correction |  |  |  | N | NO | <D> **** Detailed Description **** Technical Specification Bases B.3.3.6.1, Primary Containment Isolation Instrumentation, â€œBACKGROUND â€“ Paragraph 2. Primary Containment Isolationâ€ and â€œAPPLICABLE SAFETY ANALYSES, LCO, and APPLICABILITY - Paragraph 2.c. Drywell Pressure â€“ Highâ€ state that high dry well pressure (F = 1.68 psig) isolates Group 2, 3, 4, and 5 valves. High dry well pressure isolating Group 2 is contrary to information in ABN-FAZ, Top Tier Drawing EWD-1E-060, System Manual SD000173, and CCER C91-0498 (RRC-V-19 and 20). <I> **** Actions Taken **** Notified Shift Manager and prepared Condition Report. Recommend Severity Level 3 to Licensing to review finding for accuracy and update the bases as appropriate.
388244 | CR | 20181229 | CAQ | D | emergency lighting failed quarterly inspection | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of WO#02132109-01, electricians identified four emergency (flourescent style) fixtures that have blinking red indicating lights. Per 10.25.175, this condition is considered a failure and a WR must be generated to repair/replace as required. <I> **** Actions Taken **** Notify Supervisor, Write CR/WR and generate appropriate Impairment to stage with portable lanterns. <N> **** Equipment Description **** TSC emergency lighting
388245 | CR | 20181229 | CAQ | D | emergency lighting failed quarterly inspection | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO#02132086-01, electricians found two fixtures on attachment 9.22 (10.25.175) that failed inspection criteria. Per step 7.1.2, both fixtures indicate that there is a battery fault with an indicating light (two blinks). Work Request will repair/replace fixtures. <I> **** Actions Taken **** Notify Supervisor, Write CR/WR, generate appropriate Impairments to stage with portable lanterns <N> **** Equipment Description **** CWPH and SWPH-A
388246 | CR | 20181229 |  | 4 | CRD-FU-7A and 7B both have high DP. | N | N |  | N | YES | <D> **** Detailed Description **** While swapping CRD purge filters (CRD-FU-7A/B) it was discovered that the on-coming filter had differential pressure high at 21psid and the off going filter had 23PSID. CRD-FU-7A is in service with 21psid and CRD-FU-7B is in standby with 23psid. Both filters need to be replaced. <I> **** Actions Taken **** management informed. | 02-00-CRD-FU-7A,02-00-CRD-FU-7B
388247 | CR | 20181229 |  | 4 | RWCU Low Purge flow after adjustment | N | N |  | N | YES | <D> **** Detailed Description **** Received â€œReactor Water Cleanup Pump A Troubleâ€ (H13-P602 .A5.4-7). Ops 2 reports the alarm is due to low purge flow. Adjusted purge flow for RWCU-P-1A per ARP 4.602.A5 .4-7 to the maximum allowed 2.0 gpm using the temporary installed ultrasonic flowmeter. The purge low flow Trouble alarm cleared for several minutes and then alarmed again. | 02-00-CRD-FS-2A
388248 | CR | 20181230 |  | 4 | AR-P-1A West Bearing Oil Level Low | N | N |  | N | YES | <D> **** Detailed Description **** The Oil level in AR-P-1A west bearing is below the red line while in standby but still visible in the sight glass. Please add oil to return oil level to above the red line. See EDMS for photos <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** TB 441' | 02-00-AR-P-1A
388249 | CR | 20181230 |  | 4 | MWR-V-314A closed indication does not come on. | N | N |  | N | YES | <D> **** Detailed Description **** MWR-V-314A closed indication does not come on. this was previously identified on WR 29142150.29142171, and 29142864. WR 29142150 also discusses it being an obsolete valve and how hard it is to get too. It reference a WO 02127725 which is also at cancel. This appears to be a bit of a shell game with the WO having us test it with the "cylce seldom used radwaste valves", identify it doesnt indicate closed, write it up with a CR and then its canceled because there is a WR written. the WR is cancelled because its obsolete or we are working to make it that way. mean time I have a procedure that directs me to test it and document with a CR/wr. <I> **** Actions Taken **** Discussion with the CRS has found that there is a AR eval 379267 but is not yet implemnted to deactivate this. Please make this the CR the one that gets the AR eval done and cycling the valve removed from the "Cycle seldom used valves" so we can stop the "rinse and repeat" on WR/CR's . | 02-00-MWR-V-314A
388250 | CR | 20181230 |  | 3 | TSP-RHR/ISI-G801 procedure change. |  |  |  | N | NO | <D> **** Detailed Description **** TSP-RHR/ISI-G801 is an RHR 'A' leakage test procedure. The first NOTE on page 6 references coordination with RHR 'B' system procederes. Looks like a copy paste error. Found during T-5 review.
388251 | CR | 20181230 | CAQ | D | Security IDS 22 | N | N |  | N | YES | <D> **** Detailed Description **** Security IDS 22 is not functioning as designed, and requires Electrical maintenance. Contact Security at extension 2185 for further details. <I> **** Actions Taken **** Compensatory measures posted. Security Supervision notified. CR/WR generated for Electrical support. | 02-00-SEC-IDS-E/S/22/23
388263 | CR | 20181230 | CAQ | D | Accumulator trouble CRD-HCU-2259 | Y | N |  | N | YES | <D> **** Detailed Description **** Accumulator trouble alarm H13-P603.A7 drop 6-7 for HCU-CRD -2259 due to water level. <I> **** Actions Taken **** OPS2 drained water to clear alarm. | 02-00-CRD-HCU-2259
388264 | CR | 20181230 |  | 3 | SOP-ELEC-LP-LU requiers change to support MT-ELEV-4. |  |  |  | N | NO | <D> **** Detailed Description **** SOP-ELEC-LP-LU requiers change to support MT-ELEV-4. E-CB-LP7EA/29 was combined with circut 31 per EC-12277. SOP-ELEC-LP-LU has a required position of off for E-CB-LP7EA/29/31. This prevents the elevator AC units from functioning and lifting of C-E-CB -LP7EA/29-001.
388265 | CR | 20181230 |  | 4 | quarterly emergency lite inspection, lamp failure | N | N |  | N | YES | <D> **** Detailed Description **** During Emergency lite QTR inspection, 02132109-01, lite E -BU-AHP441/2 failed <I> **** Actions Taken **** wrote cr informe ops WWM & maintenance <N> **** Equipment Description **** AHP 441 | 02-00-E-BU-AHP441/2
388266 | CR | 20181230 |  | 3 | protected system verification removal from logs |  |  |  | N | NO | <D> **** Detailed Description **** Now that the protected schemes are being tracked in ESOMS, there is no need to do a shiftly verification in operator logs. Due to redundency, remove from logs. <I> **** Actions Taken **** CRS,SM notified <N> **** Equipment Description **** main control room
388267 | CR | 20181230 |  | 4 | Support unavailable due to no qualified workers on site |  |  |  | N | YES | <D> **** Detailed Description **** Security initiated compensatory measures on 12/28/2018 at 2144 hours due to CCTV 22/22T becoming INOP. Weekend maintenance supervisor and work week manager were notified. Due to a lack of resources and qualified workers on site, the cameras have not been repaired and PI hours are being accumulated. The maintenance supervisor and WWM tried to call out support. <I> **** Actions Taken **** compensatory measures initiated. security supervision and shift manager notified <N> **** Equipment Description **** CCTV 22/22T located in IDS zone 23
388268 | CR | 20181230 |  | 3 | Minor change to OSP-SW/IST-Q703 for efficiency |  |  |  | N | NO | <D> **** Detailed Description **** Step 7.3.14.G and H could be moved to improve efficiency. As written the actual testing of HPCS-P-2 cannot be completed until I&C remove a 0-100 psig fluke module installed down stream of SW-V-703. Evaluate if there is a need to have HPCS-P-2 running to remove this 0-100 psig fluke module, if there is not a need to have HPCS-P-2 running then recommend moving the steps to remove the 0-100 psig fluke module to section 7.5 system restorations. Then combine step 7.3.14 H with step 7.5.10 as most of these steps are identical. This would allow the system to be restored to a normal line up more expeditiously and release dedicated operators. <I> **** Actions Taken **** Generated CR for procedure enhancement
388269 | CR | 20181230 | CAQ | D | IDS 5 6 are not functioning as designed | N | N |  | N | YES | <D> **** Detailed Description **** IDS 5 6 are not functioning as designed. Contact security at ext. 2185 for further details <I> **** Actions Taken **** Posted Compensatory measures, security notification made. | 02-00-SEC-IDS-E/S/5/6
388270 | CR | 20181230 |  | 4 | Silica in DW Storage Tank | N | N |  | N | YES | <D> **** Detailed Description **** The mud trailer had the silica trip bypassed yesterday due to the belief that it was tripping the mud trailer off in error. When the Chemistry Tech sampled the mud trailer effluent today it had high levels of silica. We have secured the mud trailer and CST makeup but the DW storage tank has 40 ppb silica. Per SWP-CHE-02 the normal range for DWST silica is 10 ppb with an action level of 100 ppb. CST silica is LT 5 ppb. New deep bed resin is expected on site 12/31/18 from the vendor. <I> **** Actions Taken **** Secured CST Makeup, contacted mud trailer vendor for repairs. <N> **** Equipment Description **** Near Flocculator | 02-00-DW-TK-1
388271 | CR | 20181230 | CAQ | D | HCU high water trouble CRD-HCU-0223 | Y | N |  | N | YES | <D> **** Detailed Description **** HCU high water trouble CRD-HCU-0223 <I> **** Actions Taken **** followed arp | 02-00-CRD-HCU-0223
388272 | CR | 20181230 |  | 4 | TSW-PCV-H51 is leaking | N | N |  | N | YES | <D> **** Detailed Description **** TSW-PCV-H51 is leaking and the bucket under is was found full. there is a WR 29125671 that identifies this as leaking but only describes a minotr leak with moisture present. please see current pic. <I> **** Actions Taken **** wr wrote will add a note to check bucket and empty to the roof if tsw is free releasable | 02-00-TSW-PCV-H51
388273 | CR | 20181231 | CAQ | D | NRC Identified: DG2 Electrical Cabling Missing Rubber Sheath | Y | N |  | N | YES | <D> **** Detailed Description **** There are two electrical cables on the South West side of the generator on DG-2 in which the rubber protective sheath has been removed or fallen off leaving the protective metal conduit exposed. Engineering evaluation needed to determine if the rubber sheath is required to be repaired, replaced, or is only for aesthetic purposes. Repair or replace via Work Request if required. See EDMS for Photos <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** DG-2 The rubber sheath on the flexible conduit is not required in non-HELB areas. These conduits have no HELB markings based on the pictures and the location of the installation inside of the DG2 room. Reference CR 2-06-07522 and PPM 10.25.57 section 7.10. T. Mclaen 12/31/18 | 02-00-DG-GEN-DG2
388274 | CR | 20181231 |  | 4 | NRC Identified: Degraded Caution Tape on Steps in DG3 Room | N | N |  | N | NO | <D> **** Detailed Description **** The doors leading to the DG3 Day tank room and the three DG Storage tank Rooms have caution tape to alert workers to the existence of a step. This tape is degraded and worn or peeling off. Recommend considering to permanently painting these on or replacing the tape. See EDMS for Photos <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** DG3 Room
388275 | CR | 20181231 |  | 3 | Inadequate communication of changes to HELB barriers | Y | N |  | N | NO | <C> CR downgraded from a Severity C to 3 and Priority CAQ Removed at the direction of OFM on 01.03.2019. (Communication issue) <D> **** Detailed Description **** R-DOOR-R516 is labeled as a flood barrier. It is apparently now also to be treated as a HELB barrier, however this has neither been effectively communicated to station personnel nor have any signs been affixed in the field. About 50 doors in the plant are being upgraded to HELB barriers, and are expected to be treated as such, but the only communication provided thus far has been an email to some supervisors. This creates a significant potential for leaving HELB barriers propped open and unattended, including R-DOOR-R516 that was open and unattended for about 30 minutes before it was realized that it is a HELB barrier. Recommend labeling as HELB barriers all doors that are to be treated as HELB barriers promptly. <I> **** Actions Taken **** Generated AR. A label request was submitted on 12/20/18.
388289 | CR | 20181231 |  | 4 | Received Oscillograph Started alarm at 0428 12/31/18 | N | N |  | N | NO | <D> **** Detailed Description **** The alarm was due to the J7 sensor [500KV Neutral Ground]. The J7 sensor has been reset. E-TR-S and E-TR-B voltages as indicated on H13-P800 are 237/239/238 kV and 118/118/117 kV respectively. BPA Dittmer reports that a single phase of Ashe-Marion #2 500 KV line relayed off and back on. No RAS initiated. All plant controllers and equipment exhibited normal operation.
388290 | CR | 20181231 |  | 4 | MT-CRA-2 hook not left in full up position | Y | Y |  | N | YES | <D> **** Detailed Description **** See pictures in EDMS. PPM 10.4.5 requires that the reactor building crane hook be left in the full up position "to prevent possible safety related equipment damage caused by swinging load blocks in a seismic event." Contrary to this requirement, the hook was not left in the correct position. Note that FSAR Table 3.2-1 indicates the reactor building crane is designed to seismic category I requirements. FSAR 3.5.1.4.1 states that the equipment on the refueling floor is not required for safe shutdown. FSAR 3.8.4 indicates that the reactor building structural analysis considers "live loads" which includes movable equipment loads "such as crane loads". <I> **** Actions Taken **** Wrote CR. | 02-00-MT-CRA-2
388291 | CR | 20181231 | CAQ | C | HELB Door list from AR 381212 overly conservative |  |  |  | N | NO | <D> **** Detailed Description **** AR 381212 provided a list of doors credited with being a HELB barrier. The spreadsheet in the AR notes that conservative assumptions were made in generating the list. For instance, R-DOOR-R516 is the door to the FPC pump and HX room (Room R506). The door is identified as a HELB barrier with the reasoning that "Door R516 prevents the effects of the HELBs in Room R510 from impacting this room." Room R510 contains RWCU lines; however, Room R506 is located on the west side of the reactor building while Room R510 is located on the east side of the reactor building. The rooms are separated by the drywell structure. Additionally, the equipment in the Room R506 is located behind a concrete wall and does not communicate directly with the general area on RB 548. The labeling of the door as HELB prevented completing tagging and draining RRA-CC-19. Request AR-DMC to reevaluate the list of HELB doors as it is anticipated that work in the field will be negatively impacted with no commensurate increase in safety.
388292 | CR | 20181231 |  | 3 | Wrong type of fuse installed | N | N |  | N | YES | <D> **** Detailed Description **** During a recent starter inspection PM, the control power fuse was replaced with an incorrect type of fuse. Per drawing E528-50A, the control power fuse of COND-42-1D4A, COND-H-AH3/1 starter, is to be a type ATM, A6Y, F60C, or KTK fuse with a 3 amp rating. Per the fuse log entry, the craft replaced an ATM-3 fuse with a FNQ-R-3. While the fuse has the correct rating, the FNQ is a time delay fuse while the ATM is a fast blow. Recommend replacing the control power fuse with the correct type at the earliest opportunity. | 02-00-COND-42-1D4A
388299 | CR | 20181231 |  | 4 | Records Submitted to Records Control without transmittal |  |  |  | N | NO | <D> **** Detailed Description **** Recorder Charts were submitted to Records Control without following the proper submittal process, Please refer to SWP-REC-02. Section 4.3.2. <I> **** Actions Taken **** Notified my supervisor. Emailed a Supervisor in I&C Maintenance to notify them of the issue and have them come rectify them by filling out a transmittal form.
388300 | CR | 20181231 |  | 4 | PPCRS Alarm Printer A2 Not Functioning Correctly | N | N |  | N | YES | <D> **** Detailed Description **** PPCRS Alarm Printer A2 (EPN: PPC-PRN-A2) is not in agreement with TDAS R6 screen and PPCRS Alarm Printer A1, is printing inaccurate alarms, and is printing many blank pages and pages with the words â€œPORT 1â€. Additionally, it appears to be running out of ink. <I> **** Actions Taken **** Notified Shift Manager and prepared Condition Report and Work Request. <N> **** Equipment Description **** Main Control Room. | 02-00-PPC-PRN-A2
388301 | CR | 20181231 |  | 4 | Main Transformer sudden pressure relay PMs need generated |  |  |  | N | YES | <D> **** Detailed Description **** The purpose of this CR is to document the need to perform additional testing and calibration of the main transformer sudden pressure relays. In May 2018 the sudden pressure relays for the new main transformers were cut into service as a protective trip due to the issues with the buchholz relay. Currently testing is performed on these relays under the accessory checks for each main transformer. After researching the sudden pressure relays installed for each main transformer there are additional tests that the vendor recommends being performed on a 6 year basis for the sudden pressure relays that meet NERC PRC-005 requirements. The purpose of this CR is to document the need to perform additional PMs on the sudden pressure relays for each main transformer which were installed in 2015. <I> **** Actions Taken **** Initiated AR-SMS 387758 to create new PMs for the sudden pressure relays to test them on a 6 year basis. This is not scope for R24 since the transformers were installed in 2015 and the installation of these units is still within the 6Y frequency recommended by the vendor\ for calibratioon. | 02-00-E-MON-M1/63S,02-00-E-MON-M2/63S,02-00-E-MON-M3/63S
388302 | CR | 20181231 |  | 4 | SMA-42-5B2D failed to cycle during clearance hang | N | N |  | N | YES | <D> **** Detailed Description **** SMA-42-5B2D failed to cycle during clearance hang. When attempting to cycle to verify operation prior to hanging a danger tag on it in the OFF position, it failed to close again. Recommend investigating/fixing. <I> **** Actions Taken **** attempteed to cycle the disconnect. | 02-00-SMA-42-5B2D
388303 | CR | 20181231 | CAQ | D | CRD-HCU-1807- 3 alarms in 30 day period |  |  |  | N | YES | <D> **** Detailed Description **** The subject HCU has experienced 3 alarms for high moisture in the last 30 days, which constitutes a Level 5 Reactivity Management Concern per PPM 1.3.79, Reactivity Management Administration. <I> **** Actions Taken **** Initiated WR to investigate/ repair <N> **** Equipment Description **** R522 L5/8.4 Alarms occurred on 12/13/18, 12/20/18 and 12/28/18 | 02-00-CRD-HCU-1807
388305 | CR | 20181231 |  | 4 | Repaired WMA-TT-53B returned damaged from vendor |  |  |  | N | NO | <D> **** Detailed Description **** I was assigned a bench cal for WMA-TT-53B (WO# 02122080 -02). When I took the cover off to inspect the transmitter, I found all the hoses to be extremely brittle and some were broken. I was told we had just received this repaired from the vendor. The original problem was a broken screwâ€¦I am guessing they may have just sent us back a replacement without inspecting it. <I> **** Actions Taken **** informed supervisor and wrote this AR. This should be sent back to the vendor and all hoses should be replaced and functionality verified
388306 | CR | 20181231 |  | 3 | CVI 220-01,1950,11 dimensions inaccurate. |  |  |  | N | NO | <D> **** Detailed Description **** During prefabrication activities of Dehalogenation WOT 02119508-09 it was discovered that various dimensions on CVI 220-01,1950,11 were incorrect. Need drawing correct to reflect correct dimensions. See attached marked up copy. <I> **** Actions Taken **** Notified CPM and Engineering. <N> THE DIMENSIONS FOR CVI 220-01,1950,11 HAVE BEEN CORRECTED AND ISSUED IN EC16616R000K.FCR. No further actions are required. This AR is now closed. .
388308 | CR | 20181231 |  | 4 | Camera Cleaning inside PA | N | N |  | N | NO | <D> **** Detailed Description **** Cameras Listed Need of cleaning inside the protected area. CCTV: 01/04/07/13/14/17/23/25/32/42/43/61 PTZ: 28/29/30/39 <I> **** Actions Taken **** CAS issued list of cameras to be cleaned, notified supervision. CR/WR generated <N> **** Equipment Description **** Varias CCTV cameras inside protected area
388309 | CR | 20181231 |  | 3 | Water found in CCTV cabinet 22/22T | N | N |  | N | YES | <D> **** Detailed Description **** While investigating a loss of picture from cameras 22/22T, it was discovered that the video transmitter had failed. While replacing the transmitter craft noticed a puddle of water in the bottom of the cabinet, water along the edge of the failed transmitter, and condensation inside the top of the cabinet. Suggest engineering evaluation for the need of cabinet heating and/or dessicant at this location <I> **** Actions Taken **** Informed supervision and security <N> **** Equipment Description **** CCTV 22/22T Cabinet south of Bldg 9
388310 | CR | 20181231 | CAQ | D | CRD-HCU 2211 alarmed due to low pressure | Y | N |  | N | YES | <D> **** Detailed Description **** HCU 22-11 recieved a trouble alarm due to low nitorgen pressure. <I> **** Actions Taken **** Followeed ARP and repressurized HCU to normal pressure. | 02-00-CRD-HCU-2211
388311 | CR | 20181231 |  | 4 | SEA-FN-4 Missing Shaft inspection cover | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02103587-01 SVBLDGLUBE02: Inspect & Lube Non-Critical Components. Mechanics discovered the shaft inspection cover was missing. This does not affect the operation of the fan. See EDMS for picture. <I> **** Actions Taken **** Notified Operations, initiated CR and WR | 02-00-SEA-FN-4
388312 | CR | 20181231 |  | 3 | Clearance order with no closure mechanism |  |  |  | N | YES | <D> **** Detailed Description **** During review of clearance orders greater than one year old it was identified that all WR and WOs against C -COND-P-2CÂ Â Â Â -001 are all closed/cancelled. No closure mechanism for this CO currently exists. WO 02094677 is cancelled. <I> **** Actions Taken **** Generated WR and CR <N> **** Equipment Description **** COND-P-2C
388313 | CR | 20181231 |  | 4 | SAFTEY: SW pumphouse A lighting issues | N | N |  | N | NO | <D> **** Detailed Description **** SWPH A has 4 working lights in the crane bay. This is a safety concern and should be fixed as soon as reasonably possible. A WO (02060051) exists to fix the lights scheduled in November of 2020. This should be moved forward so itâ€™s safe to work in SWPH A <I> **** Actions Taken **** Supervision notfied and CR written. <N> **** Equipment Description **** SW pump house A
388314 | CR | 20181231 |  | 3 | Clearance order with no closure mechanism |  |  |  | N | YES | <D> **** Detailed Description **** During review of clearance orders greater than one year old it was identified that all WRs and WOs against C-FP-DISC -3C7CL-001 are closed. No closure mechanism for this CO currently exists. <I> **** Actions Taken **** Generated WR and CR | 02-00-FP-DISC-3C7CL
388315 | CR | 20181231 |  | 3 | Clearance order with no closure mechanism |  |  |  | N | YES | <D> **** Detailed Description **** During review of clearance orders greater than one year old it was identified that all WRs and WOs against C-HPCS-V-10 Â &11-001 are closed. No closure mechanism for this CO currently exists. EC16302 <I> **** Actions Taken **** Generated WR and CR | 02-00-HPCS-V-10,02-00-HPCS-V-11
388316 | CR | 20181231 |  | 3 | Environmental TLD ST-12 found missing |  |  |  | N | NO | <D> **** Detailed Description **** During the 4th quarter 2018 environmental TLD exchange, the TLD at ST-12 (6.7 miles NNW of CGS) was discovered missing. The area around the station was searched but the TLD was not located and declared lost. Probable cause is animal predation. Investigation determined that a TLD at this location is an EFSEC 332 requirement but not an ODCM requirement. This CR written to assure event is reported as a sample deviation in the annual REMP report in accordance with EFSEC 332 section D.5. <I> **** Actions Taken **** Searched for TLD, reviewed EFSEC 332 and ODCM requirements, wrote CR.
388317 | CR | 20181231 |  | 3 | Clearance order with no closure mechanism |  |  |  | N | YES | <D> **** Detailed Description **** During review of clearance orders greater than one year old it was identified that all WRs and WOs against C-HV-V-30HÂ Â Â Â Â -001 are closed. No closure mechanism for this CO currently exists. <I> **** Actions Taken **** Generated WR and CR | 02-00-HV-V-30H
388318 | CR | 20181231 |  | 3 | Clearance order with no closure mechanism |  |  |  | N | YES | <D> **** Detailed Description **** During review of clearance orders greater than one year old it was identified that all WRs and WOs against C-HV-V-31B -001 are closed. No closure mechanism for this CO currently exists. <I> **** Actions Taken **** Generated WR and CR | 02-00-HV-V-31B
388319 | CR | 20181231 |  | 3 | Clearance order with no closure mechanism |  |  |  | N | YES | <D> **** Detailed Description **** During review of clearance orders greater than one year old it was identified that all WRs and WOs against C-HV-V-31EÂ Â Â Â Â -001 are closed. No closure mechanism for this CO currently exists. <I> **** Actions Taken **** Generated WR and CR | 02-00-HV-V-31E
388320 | CR | 20181231 |  | 4 | Hot Spot located |  |  |  | N | NO | <D> **** Detailed Description **** Hot Spot (HS) was identified upon surveying 4â€FPC(16)-1 line in the overhead next to RRA-CC-17 located on the RX 548â€™. <I> **** Actions Taken **** HS-089 has been properly labeled and all requirements of procedure 11.2.24.2 have been satisfied.
388321 | CR | 20181231 |  | 3 | Clearance order with no closure mechanism |  |  |  | N | YES | <D> **** Detailed Description **** During review of clearance orders greater than one year old it was identified that all WRs and WOs against C-ROA-RMS -V/31Â -006 are closed. No closure mechanism for this CO currently exists. <I> **** Actions Taken **** Generated WR and CR | 02-00-ROA-RMS-V/31
388322 | CR | 20181231 |  | 3 | Clearance order with no closure mechanism |  |  |  | N | YES | <D> **** Detailed Description **** During review of clearance orders greater than one year old it was identified that all WRs and WOs against C-TG-TR-144 Â Â Â Â -001 are closed. No closure mechanism for this CO currently exists. <I> **** Actions Taken **** Generated WR and CR | 02-00-TG-TR-144
388323 | CR | 20181231 |  | 3 | Clearance order with no closure mechanism |  |  |  | N | YES | <D> **** Detailed Description **** During review of clearance orders greater than one year old it was identified that all WRs and WOs against C-TMU-V-19A Â Â Â Â -002 are closed. No closure mechanism for this CO currently exists. <I> **** Actions Taken **** Generated WR and CR | 02-00-TMU-V-19A
388324 | CR | 20181231 |  |  | Clearance order with no closure mechanism |  |  |  | N | NO | <D> **** Detailed Description **** During review of clearance orders greater than one year old it was identified that all WRs and WOs against are closed. No closure mechanism for this CO currently exists. <I> **** Actions Taken **** Generated WR and CR
388325 | CR | 20181231 |  | 4 | HOT SPOT TRENDING |  |  |  | N | NO | <D> **** Detailed Description **** Hot Spot (HS-088) was identified upon surveying EDR-1 piping located on the east side of the Rx 471 elevation. This is part of the Quarterly EDR-1 piping survey. requirements of procedure 11.2.24.2 have been satisfied <I> **** Actions Taken **** Attached a HOT SPOT Label and initiated a CR. <N> **** Equipment Description **** RX 471 east side located in a HRA
388326 | CR | 20181231 |  | 4 | RX 548 A Heat Exchanger Room - NO LIGHTS |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** There is NO Lighting in this room. It is a Posted High Radiation Area. This room needs lighting, as per OSHA Regulations. <I> **** Actions Taken **** Notified HP Supervisor and HP Lead Technician. Initiate CR/WR Esoms Log Entry. <N> **** Equipment Description **** RX 548 A RHR Heat Exchanger Room.
388327 | CR | 20181231 |  | 3 | torque value in vendor manual was not correct |  |  |  | N | NO | <D> **** Detailed Description **** torque value in, vendor manual (02-01,491) had the wrong conversion from Nm to ft-lbs for the terminal screws for replacement transmitter for PSR-FIT-SR49/3. the torque value in the vendor manual is 1.5 Nm. this had 11 ft-lbs in parentheses next to it. The correct vaule for ft-lbs is 1.1 ft-lbs or 13 in-lbs. . recommend CVI manual be updated with correct torque conversion. . this is not an equipment issue. CVI needs to be updated. <I> **** Actions Taken **** Wrote CR | 02-00-PSR-FIT-SR49/3
388328 | CR | 20190101 | CAQ | D | DG3 GEN RTD HIGH TEMPERATURE | Y | N |  | N | YES | <D> **** Detailed Description **** On 1/1/2019, a DG3 GEN RTD HIGH TEMPERATURE alarm was received. HPCS-TIS-DG3 was checked per 4.DG3 2-1 ARP, and B channel indicated the trip. The channels were checked, and A and C channel were reading higher than B, at 51 and 56 respectively, and B was reading approximately 45; all well below the 130 listed in the ARP. B channel was 'bouncing' from approximately 41-49, and this could have potentially caused a spurious alarm. All other parameters for DG3 listed in the ARP were normal. CR written for investigation and trending purposes. <I> **** Actions Taken **** Initiated CR. | 02-00-HPCS-TIS-DG3
388402 | CR | 20190101 | CAQ | D | Security PAAP door 12 not operating correctly | N | N |  | N | YES | <D> **** Detailed Description **** Security PAAP door 12 mag switch is not operating correctly and needs maintenance. <I> **** Actions Taken **** CR/WR initiated. Security supervision notified. Comp measures initiated. | 02-00-AAP-DOOR-AAP12
388403 | CR | 20190101 | CAQ | D | CW Blowdown flow rate is less than actual. | N | Y |  | N | YES | <D> **** Detailed Description **** Local indication is 10 gpm vice 1850 gpm actual. Samples are not representatvie of the actual blowdown rate and may not meet our REMP requirements. CBD-FI-1A in the MCR is also downscale. This suggests that CBD-FT-1 may have failed. Find and fix. <I> **** Actions Taken **** Placed CBD-SR-1 and 2 in timed IAW with MCR direction. Caution tags to be placed when they are written. | 02-00-CBD-CP-1,02-00-CBD-FT-1
388404 | CR | 20190101 |  | 4 | WOA-HC-1 O coil steam leak with N coil created large puddle. | N | N |  | N | YES | <D> **** Detailed Description **** WOA-HC-1 O coil steam leak with N coil created large puddle that spread from HV enclosure to the Hot machine shop. This was exacerbated by the drain being mostly occluded and only passing a pencil stream of water. Fix coils. Fix drain. <I> **** Actions Taken **** Wrote this CR. Signed on clearance for N coil. N and O coils closed. | 02-00-WOA-HC-1
388405 | CR | 20190102 | CAQ | D | SW-FI-41 ultrasonic has fallen off | Y | Y |  | N | YES | <D> **** Detailed Description **** SW-FI-41 ultrasonic has fallen off and is unable to measure flow due to installed flow instrument is broke. <I> **** Actions Taken **** Contacted MCR and CRS. Wrote this CR. <N> Temporary Ultrasonic Flowmeter for SW-FI-41 disturbed (CR388405) It appears the ultrasonic flow instrument sensors were inadvertently disturbed while building scaffold to repair the permanently installed flow indicator SW-FI-41. The temporary ultrasonic sensors were inspected and reinstalled under work request 29146386. The unit is back in service and functioning properly Nicholas LaBella 01/02/2019 Williams Carpenters were interviewed regarding the issue documented in this CR. The General Superintendent found that one carpenter had found the instruments laying on the floor upon arrival at the work site but said nothing to his supervisor/foreman because he was not sure there was a problem based on the way the instrument would have been secured to the piping with band clamps. I have observed these Carpenters on several occasions and found them to have a high level of integrity and when they do something that impacts the plant they immediately stop what they are doing and report the issue to their supervisor. . Coaching was provided to the carpenter to inform his foreman/supervisor anythime he knows or thinks something is not right or is a risk to personnel and the plant. | 02-00-SW-FI-41
388406 | CR | 20190102 |  | 4 | RW 487' Broken Light Switch Toggle | N | N |  | N | NO | <D> **** Detailed Description **** Light switch toggle in the RMC Laborers closet is broken. The closet is located on RW 487'. (Door C-325). This is the 4th Condition Report/Work Request initiated since 2011 on this same toggle switch. Reference Work Request #'s :29092931 (2011) 29127958 (2016) 29139995 (2017). <I> **** Actions Taken **** Initiated CR & WR. Notified HP Supervision via e-mail <N> **** Equipment Description **** RW 487' Door C-325
388407 | CR | 20190102 |  | 3 | Unable to rack out E-CB-61/6M per WO 02084635-02 | N | N |  | N | NO | <D> **** Detailed Description **** Unable to rack out E-CB-61/6M as scheduled with the new remote breaker racking tools. <I> **** Actions Taken **** Supervision informed <N> this information will be covered during cycle 19-1. Also coached that lack of proficiency needs to be raised prior to the day of implemenation. Information was provided and could have been reviewed ahead of time to ensure understanding of equipment. No further action this AR.
388439 | CR | 20190102 |  | 3 | Removal of admin hold requires HGU re-enrollment |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** After removing the admin hold on an employees green badge, the individuals badge did not work when presented at the PAAP turnstyles, until their hand geometry was updated (contact access for info regarding troubleshooting). Once the HGU was updated the indivdual was able to enter the PA without delay. The AIM and IEBS showed the individual had an active HGU template and once any hold is removed, it should not require another HGU enrollment. <I> **** Actions Taken **** Completed CR to document the issue and notified Security Services Manager Please assign to org #54211 <N> **** Equipment Description **** AIM (in CAS)
388441 | CR | 20190102 |  | 4 | Received momentary BUS 61/62 MCC OL TRIP alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received momentary BUS 61/62 MCC OL TRIP alarm - H13-P800 .C2 drop 6-6. The alarm was in for approximately 1 second and then cleared. Process computer point E682 (SL-61 CKT BKR TO MC-6N OL TRIP) displayed tripped and then normal. Local investigation at SL-61 and the CWPH / electrical buildings revealed all SL-61 circuit breakers were closed with associated loads in service. No known equipment manipulations or evolutions were in progress at the time of the alarm. <I> **** Actions Taken **** Notified the CRS and SM. Initiated CR and Work Reqest. | 02-00-E-CB-61/6N
388445 | CR | 20190102 |  | 3 | SOP-CRD-FILTERS uses an incorrect EPN. |  |  |  | N | NO | <D> **** Detailed Description **** SOP-CRD-FILTERS sections 5.5 and 5.6 use CRD-FU-7A and CRD-FU-7B in steps 5.5.8 and 5.6.8. These EPNâ€™s refer to the filters in the CRD stabilizing valves. The filters being referred to in this SOP are the RWCU pump CRD purge filters. The correct EPNâ€™s for these filters are CRD-F-7A and CRD-F-7B. All other references to these filters in this procedure are correct. Only the last step of these two sections uses the incorrect EPN. See EDMS for marked up copy. <I> **** Actions Taken **** Called OPS procedure lead and wrote this PCR.
388448 | CR | 20190102 | CAQ | D | Low Specific Gravity E-B0-1B and E-B0-1A | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** average specific gravity was found to be to low on both batteries. Acceptance was to be 1.207 and both were found to be in the 1.206 range. see WO # 02106308-01 <I> **** Actions Taken **** CR, WR, reported issue to supervision. <N> **** Equipment Description **** E-B0-1B E-B0-1A 467 VI
388450 | CR | 20190102 |  | 3 | 12/15/18 Offgas Tracer Gas Testing Results | N | N |  | N | YES | <D> **** Detailed Description **** This CR is to document the findings of the tracer gas testing performed on 12/15/18. The findings characterize existing in-leakage and does not represent any new leaks or failed equipment. There are no new equipment functionality issues identified in this CR. The vendor supplied a report of their findings (with photos) and it is included in the EDMS of this CR. Portions of the report are summarized below. On December 15, 2018, Conco Services conducted a condenser air inleakage inspection on the steam turbine and its condenser. The inspection was performed utilizing helium as a tracer gas and the gas was detected with a helium mass spectrometer analyzer. . Continuws The inspection identified 21 leaks. T501â€™ Main Turbine: 10 â€“ Shaft seal Case Joint/Housing areas 6 â€“ Rupture Disc inner bolted ring flanges 3 â€“ Jacking-bolt holes, 1st open hole next to shaft on horizontal joint T 471â€™ Condenser: 1 â€“ B Manway flange 1 â€“ C Manway flange Recommend assign to BOP to evaluate actions going forward. <I> **** Actions Taken **** Discussed with supervisor and SM after testing was complete. <N> **** Equipment Description **** Main Turbine T501' Main Condenser T471' | 02-00-COND-HX-9,02-00-MS-DT-1A,02-00-MS-DT-1B,02-00-MS-DT-1C
388451 | CR | 20190102 |  | 3 | EC DEC 16655 cannot be installed as designed |  |  |  | N | NO | <D> **** Detailed Description **** During field walkdown of WO 02115413 installation of drain leg for CMS-PT-3 it was discovered that the installation could not be performed as designed. There were obstacles in the proposed piping path and the final tie in could not be welded as designed. Craft met with Engineering and discussed proposed changes. <I> **** Actions Taken **** Generated CR for documentation, notified planner, returned WO and placed an EC hold on the 01 task
388453 | CR | 20190102 | CAQ | C | CRA-42-7B5B did not start CRA-FN-2A2 | Y | Y |  | N | YES | <D> **** Detailed Description **** during testing of CRA-FN-2A1/2A2 - CRA-FN-2A2 failed to start until the 3rd attempt. The green lamp was noted to dim when the switch was taken to start but the green lamp stayed on until the 3rd attempt - the fan then started normally. Suspect mechanical binding of the contactor since the dimming of the lamp indicates the starting coil was likely energizing with the operation of the switch. <N> CRA-42-7B5B (CRA-FN-2A2) is scheduled for replacement on 1/15/19 per WO# 02035819 (new NLI MCC bucket) CRA-42-7B5C (CRA-FN-2A1) is scheduled for replacement on 1/22/19 per WO# 02035821 (new NLI MCC bucket) | 02-00-CRA-42-7B5B
388454 | CR | 20190102 |  | 4 | CMS-RE-27B Connectors need repair | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02123814-01, when disconnecting the High Voltage cable, it was discovered that the BNC connectors were loose/spinning on the housing. Needs to be repaired. <I> **** Actions Taken **** Stopped work. Contacted Supervision. Supervisor came to work location and determined that connectors should be repaired before continuing. Informed CRS that we were backing out of WO at this time. Getting work instructions to repair connectors. <N> **** Equipment Description **** 522RX
388457 | CR | 20190102 |  | 4 | APPW revisions included Form 26232 when not applicable |  |  |  | N | NO | <D> **** Detailed Description **** Some revisions created in APPW between 12/26/18 and 1/2/19 included Form 26232, POC Review Criteria, when POC review was not applicable to the revision. The cause of the issue has been determined and fixed. Individuals with procedure revision affected by this issue will be notified. Form 26232 is only required for some procedure revisions. The complete list of POC Review requirements is listed in SWP -IRP-01. <I> **** Actions Taken **** IS Supervision was notified. The cause was determined and fixed. CR written.
388458 | CR | 20190102 | CAQ | D | attepted to replace SW-TE-1BR WO 02109506-01 probe was stuck | Y | Y |  | N | YES | <D> **** Detailed Description **** Probes SW-TE-1BR & SW-TE-1BR are stuck in the well in the floor. used a bore scope and found huge lumps of rust on the walls preventing removal of probes. Had the mechanics remove the top flange on the well, to remove the well for inspection. the well appears to be attached below the floor near the water. <I> **** Actions Taken **** notified supervisor. used bore scope to inspect. Restored back to the way it was found. <N> **** Equipment Description **** SWPH B | 02-00-SW-TE-1BR
388459 | CR | 20190102 |  | 4 | Late eSOMS Entries for Maintenance |  |  |  | N | NO | <D> **** Detailed Description **** On 12/18, an I&C tech returned from PT 1.25 hours early than scheduled and eSOMS was not updated to reflect the earlier start time. On 12/26 an electrician left after working for an hour, and the wrong electrician's time was updated by mistake, causing him to work without having time entered in eSOMS. <I> **** Actions Taken **** eSOMS was updated with the correct hours <N> No violations occurred when correct time was added in eSOMS.
388460 | CR | 20190102 | CAQ | D | DMA-TIS-11/1 Temp. Indication Deviating from Norm | Y | Y |  | N | YES | <D> **** Detailed Description **** On 01/02/19 while performing system performance monitoring and trending, the system engineer noted that DMA-TIS-11/1 indications are deviating from the other five remaining DMA temperature indicating switches in the DMA inlet air plenums of all 3 diesel generator HVAC systems. DMA-TIS -11/1 should be checked for proper calibration. DMA-TIS -11/1 is a temperature indicating switch in the Emergency Diesel Generator 1 Building Ventilation system. Motor operated face and bypass dampers on the air handling unit (DMA-AH-11) water cooling coils are controlled by the subject temperature switches located in the fresh air intakes. The water cooling coils provide additional cooling during high outdoor air temperatures. Temperatures greater than the maximums could result in premature failure of components which are required for safe shutdown of the plant. When the fresh air temperature falls below 70Â° F, the air is bypassed, by action of the subject temperature switches, over the cooling coil (bypass of the cooling coil) to prevent the supply air temperature from dropping below approximately 70Â° F. DMA-TIS-11/1 appears to be reading approximately 6 deg higher than DMA-TIS-11/2. DMA-TIS-11/2 is reading closer to the current readings of the remaining DMA temperature indicating switches on the other diesel generators and therefore, DMA-TIS-11/1 is suspected of being out of calibration. The fact that DMA -TIS-11/1 is reading higher than the actual supply temperature may result in the coil face/bypass dampers actuating at a lower actual temperature than the 70 deg. F setpoint. This would send air flow across the cooling coils when temperatures are below 70 deg. Room temperature calculation ME-02-92-43 uses peak summer temperatures and takes the cooling of the air via the service water cooling coil into account. Therefore this identified condition does not impact the DG-1 HVAC system from performing its design function in support of DG-1 operation and room temperatures would not exceed limits. <I> **** Actions Taken **** Discussed with my supervision and called the shift manager to discuss the ability of the DG HVAC to perform its design function. | 02-00-DMA-TIS-11/1
388461 | CR | 20190102 | CAQ | D | BATTJBT Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** BATT JBT requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Officer presence/walkdowns completed. Compensatory measures posted. Contacted electrical maintenance for additional support. Initiate CR/WR. <N> **** Equipment Description **** CENTRAL ALARM STATION BATTJBT
388462 | CR | 20190102 |  | 3 | Universal Refresher training not completed. |  |  |  | N | NO | <C> OFM change request from Severity 4 to 3 and assigned to ELECM to document completed training - 1/8/2019. <D> **** Detailed Description **** Universal refresher training was not completed by the due date of 12/31/2018. Organazation 52235 has 6 individuals that have not completed the trainig at the time of this CR. 2 of the individuals are supporting USA and will complete the training upon arrival back to CGS, the other 4 will complete the training once back on site following PT/return to work. <I> **** Actions Taken **** Generated CR to document training not completed. Notified Emergency Preparedness Manager, and responsable Component Manager. <N> This action will be tracked with the Training report that is used by the Maintenance department. this issue is being tracked by the electrical shop and the Maint. Training program owner to ensure that the training deltas are addressed.
388463 | CR | 20190103 |  | 4 | CAS-C-1B low oil level when in standby | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1B has a low oil level when the compressor is in standby. <I> **** Actions Taken **** Informed CR | 02-00-CAS-C-1B
388482 | CR | 20190103 |  | 3 | Request for a switch development for E-MTS-8A/CAS1B/DPSS. |  |  |  | N | NO | <D> **** Detailed Description **** This is a request for a device / switch development be placed on EWD-78E-003A for E-MTS-8A/CAS1B/DPSS to better understand its operation. This will allow all users of this drawing to know and understand that CAS-C-1B cannot be directly powered from E-DP-SS/SL81 and that it only allows for backfeed of E-MC-8A from E-DP-SS/SL81 or powering of CAS-C-1B from E-MC-8A. A switch development showing which contacts can be closed at any one time would enable the end user to know without a doubt that E-DP-SS/SL81 cannot feed CAS-C-1B. Notes 3 & 4 do not provide absolute clarity on this. Please see EDMS. <I> **** Actions Taken **** Wrote this AR-CR.
388484 | CR | 20190103 |  | 4 | Steam leak on WOA-HV-1 | N | N |  | N | YES | <D> **** Detailed Description **** Steam leak on WOA-HV-1 <I> **** Actions Taken **** Isolated steam coil, opened drain valve and requested MCR write a Local Control tag | 02-00-WOA-HV-1
388485 | CR | 20190103 | CAQ | D | RX BLDG STACK GENERAL TROUBLE ALARM in and clear. | N | Y |  | N | YES | <D> **** Detailed Description **** Received RX BLDG STACK GENERAL TROUBLE ALARM in and clear. PRM-RIS-1 showed that NGD-12 AC NOT VALID VALUE came in for several seconds and cleared. There was no change in flow, temperatrue, or count change noted. | 02-00-PRM-SR-1
388487 | CR | 20190103 |  | 4 | PPC ERROR lamp illuminated | N | N |  | N | YES | <D> **** Detailed Description **** PPC error lamp illuminated. Checked u1/u2 screens and see all rods in monitor and events functions are red along with multtiple MUX inputs. Currently TDAS is primary. | 02-00-PPC-COMP-8715
388489 | CR | 20190103 | CAQ | D | Seismic System not returned to functional status within LCS | N | Y |  | N | YES | <D> **** Detailed Description **** The seismic system was removed from service on 12/4/18 for a planned replacement of the entire system per EC 15891. The replacement of the system was expected to exceed the LCS 1.3.7.2.A.1 completion time of 30 days. The seismic system replacement is on track and is expected to be declared functional on 1/10/19 following site acceptance testing and operability testing. <I> **** Actions Taken **** Initiated this CR. | 02-00-SEIS-COMP-NCC,02-00-SEIS-E/S-MR,02-00-SEIS-E/S-NCC
388490 | CR | 20190103 |  | 3 | CSP-ISOTOPIC-M101 Needs Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Step 8.2.4 would be improved if it included a line to write down the power corrected gross gamma activity rate for reviewers to visually verify the formula was used appropriately. <I> **** Actions Taken **** Spoke with chemistry management and specialist, both agreed. Wrote CR to document
388492 | CR | 20190103 |  | 4 | Unable to perform 02095007-11 as scheduled DW-FI-1 wiring | N | N |  | N | YES | <D> **** Detailed Description **** Unable to perform 02095007-11 Install Signal Cables and Term for DW-FI-1 as scheduled due to the instrument being removed from the field. The bench calibration shop task, that is in progress and includes a 24 hour burn in, needs to be complete and the instrument reinstalled in the field for this work to commence. <I> **** Actions Taken **** Electrical Supervison informer. Work Week Manager Informed. | 02-00-DW-FI-1
388493 | CR | 20190103 |  | 4 | I&C Exceeded Dose Goal for December 2018 |  |  |  | N | NO | <D> **** Detailed Description **** I&C exceeded dose goal for December 2018, actual dose received was 797 mrem, dose goal was 775 mrem (23 mrem over for the month) . The majority of the overage was due to emergent work on HCU, OG-AY-12A work was performed by FIN and accounted for 35 mrem for the month that was not budgeted
388499 | CR | 20190103 |  | 3 | ROA-HV-1, small through holes identified | N | N |  | N | YES | <D> **** Detailed Description **** During roll filter replacement of ROA-FL-1A and 1B it was noticed that light could be seen from a small ~1/2" hole between the filter access door and ROA-HV-1. Further inspection identified another hole / screw missing. See EDMS for pictures. Recommend Engineering evaluate repair options. <I> **** Actions Taken **** Notified the shift manager and system engineer. | 02-00-ROA-HV-1
388501 | CR | 20190103 |  | 3 | Evaporation Pond Sludge Levels | N | N |  | N | YES | <D> **** Detailed Description **** The Evaporation Pond sludge levels have reached a point where planning action is required to remove the sludge to maintain adequate operational volume. The upper ponds (1A, 1B and pond #2) utilized for evaporation of the potable water system back wash water has the highest sludge accumulation. Evaporation ponds #3 and #4, which receive potentially contaminated water, have smaller accumulation of sludge. In addition to the cleaning and disposal of the sludge, all the ponds suffer from intrusion of tumble weeds and other debris that must be addressed. Currently, no maintenance budget, responsible party, or disposal plan has been developed for the accumulated debris and sludge. If the sludge in Ponds #3 and #4 is determined to be radioactively contaminated this will present a very challenging issue for disposal. <I> **** Actions Taken **** Recommend assigning tasks under this CR/AR for evaluating and developing the necessary budget, assign responsibility for testing and disposal of all the debris and sludge, and any other identified plans to facilitate maintaining the evaporation ponds. Recommend assignment to Facilities to coordinate the planning, budgeting and activities. <N> **** Equipment Description **** Wastewater Evaporation Ponds
388502 | CR | 20190103 |  | 4 | Late entry into eSOMS for HP Technician |  |  |  | N | NO | <D> **** Detailed Description **** A Health Physics Technician was held over for 2 hours on 12/26/2018 to support dayshift shift coverage. eSOMS PQ&S was not updated to reflect the additional hours. This did not result in a violation of work hour rules. <I> **** Actions Taken **** Updated PQ&S and verified that no work hour rules were exceeded.
388507 | CR | 20190103 | CAQ | C | HPCS-TIS-DG3 wiring and drawing issues | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing WR 29144144 for investigation of spurious alarms we found that the wiring for HPCS-GEN-DG3 Stator RTD and HTR term box did not match EWD-7I-004. The red and black wires from each RTD cable 3hpcs-383 are swapped Also the shield on cable 3HPCS-383 should be grounded and is not. <I> **** Actions Taken **** Notified supervision and agreed that these descreprancies should not affect indication or alarms. Took picture and included edms.
388508 | CR | 20190103 | CAQ | B | Portable media maintenance cabinet found unlocked. |  |  |  | N | NO | <C> RISK - Medium. CAUSE - Cause is Clear. The Cause was HU in that the individual became distracted with their next task and rushed to complete the task without ensuring the cabinet was locked. <D> **** Detailed Description **** Portable media maintenance cabinet was found unlocked. Cabinet is used to hold media out of service for maintenance. Cabinet is in a locked room that was not accessed since being found unlocked. This is not a reportable event under 10.CFR 73.77. <I> **** Actions Taken **** Notified cyber security program manager. Secured Cabinet Ran report to validate only delegated custodians had accessed the area since it was left unattended. Disqualified the Delegate Custodian that left cabinet opened. Please assign Cat C to ITMGMT
388509 | CR | 20190103 |  | 3 | Chiller WCH-CR-51B tubing missing permanent restraints | N | N |  | N | YES | <D> **** Detailed Description **** During a closeout walkdown of modification EC 17099 for replacement of radwaste chiller WCH-CR-51A, it was noted that the newly rerouted tubing track for the supply and control air lines to WCH-CR-51B condensor cooling water control valve TSW-PCV-H52, have tubing clamps (ty-wraps and tape - see EDMS folder) that are not in accordance with EC 17099 referenced restraint drawing CVI 220-01-809,1. The correct tube restraints should be a banded metal cover over the associated tube track. Note that this tubing, tube track and associated control valve and Radwaste Chiller is non-safety equipment so this condition does not affect operation or operability of any safety related equipment. Additionally, the current temporary restraints are adequate in the support of the associated tubing runs, pending installation of the correct restraints. <I> **** Actions Taken **** Notified the installer SSC (Williams) of this condition. Initiated WR 29146421 to replace all temporary tubing restraints with the correct permanent restraints, which can be performed one-at-a-time, with no clearance order or need to take either Radwaste chiller out-of-service. <N> **** Equipment Description **** Radwaste W507' at south end of Radwaste chiller WCH-CR-51B | 02-00-TSW-PCV-H52,02-00-WCH-CR-51B
388510 | CR | 20190103 |  | 3 | PCR for 4.800.c2 drop 6-6 Bus 61/62 MCC OL trip |  |  |  | N | NO | <D> **** Detailed Description **** see EDMS for mark up
388511 | CR | 20190103 |  | 4 | CAS-C-1B unexpected oil level change | N | N |  | N | YES | <D> **** Detailed Description **** While clearing tags on CAS-C-1B there was an unexpected oil level change. Before clearing tags under clearance D-CAS -C-1B-010 on CAS-C-1B the oil level was verified to be 7/16 full. After clearing the first three tags and pressing the reset button the oil level had decreased to 1/8 full, which is the minimum required by logs. <I> **** Actions Taken **** Informed CRS and wrote CR | 02-00-CAS-C-1B
388513 | CR | 20190103 |  | 4 | 61/61 MCC OL TRIP alarm remains in with CB closed. | N | N |  | N | YES | <D> **** Detailed Description **** WO 02084635 E-CB-61/6M: DETAILED VISUAL INSPECTION OF SWITCHGEAR BREAKER. Following the completion of WO 02084635 E-CB-61/6M was racked in and local resets were depressed and the breaker was closed in the alarm on H13-P800 drop 6/6 (61/61 MCC OL TRIP) stayed locked in. Currently the (61/61 MCC OL TRIP) alarm has come in and cleared several times with on actions. | 02-00-E-CB-61/6M
388516 | CR | 20190103 |  | 4 | OG-RF-20C Compressor D/P low of out spec | N | N |  | N | YES | <D> **** Detailed Description **** OG-RF-20C compressor D/P between suction and discharge pressure when unit is running is low out of spec | 02-00-OG-RF-20C
388517 | CR | 20190103 | CAQ | D | Rod accumulator trouble alarm CRD-HCU-5415. | Y | N |  | N | YES | <D> **** Detailed Description **** Received rod accumulator trouble alarm for CRD-HCU-5415 due to high water level. <I> **** Actions Taken **** Drained water, alarm cleared. | 02-00-CRD-HCU-5415
388518 | CR | 20190104 |  | 4 | Lenel system | N | N |  | N | YES | <D> **** Detailed Description **** The Lenel system in SCC needs maintenance. Contact security at ext 2185 for further details. <I> **** Actions Taken **** help ticket #IR- 0036954 generated, security notification made. <N> **** Equipment Description **** Lenel system in the Security Communication Center
388519 | CR | 20190104 |  | 4 | Dept Mgr Approval Not Documented for FSA Assign. Extensions |  |  |  | Y | NO | <D> **** Detailed Description **** Multiple Assignments for Focused Self-Assessment 376427 were extended without documenting Department Manager approval which is required by GBP-ASU-03. Upon self -identification of the issue, the Department Manager was briefed on the non-compliance with procedures and concurred with the extensions. The FSA Planning remains on track for sucessful performance in March and there was no negative effect on the quality of the product due to the non -compliance. Personnel involved were coached and lessons learned were shared with the entire department. No further actions required. Recommend SL 4 trend to Quality. <I> **** Actions Taken **** Debriefed Dept Mgr and obtained concurrence for extensions. Documented concurrence in assignments.
388520 | CR | 20190104 |  | 3 | 10.24.57 requires enhancement |  |  |  | N | NO | <D> **** Detailed Description **** During the bench calibration of COND-DPIC-5 replacement controller under WO 02136717-02 the procedure was found to need clarification in both the body and attachment 9.1 <I> **** Actions Taken **** Notified supervision and writing this CR <N> Revision request has been added to the procedure database. See EDMS for link.
388523 | CR | 20190104 |  | 3 | Request change of SOP-ELEC-125V-SHUTDOWN section 5.6 |  |  |  | N | NO | <D> **** Detailed Description **** SOP-ELEC-125V-SHUTDOWN section 5.6 removing 125VDC battery charger E-C1-2B from service needs a step fixed. 5.6.1 states PERFORM the following prior to removing Battery Charger "E-C1-2A" from service, it should be E-C1-2B.
388525 | CR | 20190104 | CAQ | D | IRM F unexpected INOP & downscale lamps | Y | Y |  | N | YES | <D> **** Detailed Description **** While performing W/O 02118368-01, after completion of Section 7.9 but before starting Section 7.10 Restoration noticed that downscale and INOP lamps were still illuminated with mode switch in operate. <I> **** Actions Taken **** Stopped work, notified CRS & Supervision. CRS opted to leave IRM F in bypass. Wrote CR & W/R to document. | 02-00-IRM-EMSQ-601F
388526 | CR | 20190104 | CAQ | D | IRM-F Voltages Out of Tolerance | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02118368-01, voltages on step 7.5.42 was found out of tolerance at 10.51VDC (9.7-10.3), step 7.7.4 was found at 9.54VDC (9.99-10.01), and INOP Trip voltage in step 7.9.9 was found at 76VDC (78-82) <I> **** Actions Taken **** Informed Supervisor. Adjusted within tolerances and continued with surveillance.
388527 | CR | 20190104 | CAQ | D | Received SLC high level alarm in MCR | Y | Y |  | N | YES | <C> CR TREND TO CR 388557 <D> **** Detailed Description **** 4.603.A8 drop 5-8 alarm came in unexpectadly and trend shows a spike in level. Local level indication 5080 gal. Control room indication shows GT 5050 gal. Tank temperature is 83Â°F. see EDMS for trend | 02-00-SLC-LI-601
388528 | CR | 20190104 | CAQ | D | Rod Accumulator Trouble Alarm P603-A7 for CRD-HCU-30-27. | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-30-27. OPS 2 reported alarm was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear. <I> **** Actions Taken **** Informed CRS/SM. | 02-00-CRD-HCU-3027
388529 | CR | 20190104 | CAQ | D | IRM-LR-603D reads different than IRM on P633 | Y | Y |  | N | YES | <D> **** Detailed Description **** Channel B on IRM-LR-603D reads approximately 6 less than IRM-B and has a variable level. IRM-LR0603D was consistently reading approximately 24 in range 1 for the last several days around 2 pm on 1/4/19 the Yokogawa recorder started to have variance and the output appeared more wave like vice a straight line on the recorder. IRM channel B on H13-P633 reads approximately 23 which is consistent with the previously indicated value on the Yokogawa recorder. This appears to be an issue with the signal from the IRM-B to the Yokogawa recorder. IRM B provides the automatic safety action, however IRM-LR-603D does have PAM indications. Attached picture in EDMS. <I> **** Actions Taken **** Generated WR | 02-00-IRM-LR-603D
388530 | CR | 20190105 |  | 3 | WO 02136034 Missing Task to Stage Barrels |  |  |  | N | NO | <D> **** Detailed Description **** WO 02136034 is missing a task to stage barrels for the tag hang in task 10. Barrels are needed to be staged on the RB 522 to support draining RHR-HX-1A. <I> **** Actions Taken **** Informed laborers to stage barrels.
388531 | CR | 20190105 | CAQ | D | Received Rod Accumulator Trouble Alarm for CRD-HCU-1807. | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-1807. Dispatched OPS-2 to investigate. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-1807 was due to high water level. OPS 2 drained water per SOP -CRD-HCU and alarm is clear <I> **** Actions Taken **** Informed CRS/SM. | 02-00-CRD-HCU-1807
388550 | CR | 20190105 | CAQ | D | Received Oscillograph Started (H13-P800.C4.4-3) alarm. | Y | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started (H13-P800.C4.4-3) alarm. The alarm was due to the sensor J15 (230 kV Undervoltage). Sensor has been reset. E-TR-S and E-TR-B voltages are 239/239/239kV and 118/118/117 kV respectively. BPA Munro reports the cause of the grid disturbance was momentary trip and automatic re-closure of Wine Country/Midway#1 230 kV line. It is not known what caused the line to cycle off and on. No RAS was initiated. <I> **** Actions Taken **** No action required
388551 | CR | 20190105 |  | 4 | GSB 441â€™ kitchen sink hot water filter has a leak | N | N |  | N | NO | <D> **** Detailed Description **** The hot-water filter under the kitchen sink has a leaking plastic fitting; need to replace the fitting or simply replace the old filter cartridge with a new one which typically includes new fittings. The isolation to the hot water filter is currently closed, so the leaking has stopped. See pictures on EDMS screen. <I> **** Actions Taken **** closed hot water filter to stop leak - hung manilla tag to identfy where leak is coming from on the bad fittings <N> **** Equipment Description **** GSB 441 kitchen - under sink area
388552 | CR | 20190105 | CAQ | D | Received Rod Accumulator Trouble Alarm for CRD-HCU-2651 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-2651. Dispatched OPS-2 to investigate. Rod Accumulator Trouble Alarm P603-A7 for CRD-HCU-2651 was due to high water level. OPS 2 drained water per SOP -CRD-HCU and alarm is clear | 02-00-CRD-HCU-2651
388553 | CR | 20190106 |  | 4 | Poor Lighting in RW 452 B Off-Gas Pre-Filter Room | N | N |  | N | NO | <D> **** Detailed Description **** While performing a Quarterly Radiological Survey the lighting in the Room with the B Off Gas Pre-Filter in it is very poor. Some light shines in from the corridor but the room itself is dim. <I> **** Actions Taken **** Documented this CR, documented it in turnover, made a loogbook entry and email HP Supervision. <N> **** Equipment Description **** B Off Gas Pre-Filter Room
388554 | CR | 20190106 | CAQ | D | Recieved accumlator trouble alarm for 34-31. | Y | N |  | N | YES | <D> **** Detailed Description **** Recieved accumlator trouble alarm for HCU 34-31 this was due to high water. <I> **** Actions Taken **** Followed ARP, drained water and cleared alarm. | 02-00-CRD-HCU-3431
388555 | CR | 20190106 |  | 4 | Flocculator would not perform manual backwash | N | N |  | N | YES | <D> **** Detailed Description **** Flocculator would not perform manual backwash. Flocculator was found tripped with high turbidity. Tried to commence backwash and after taking PWC-SS-4 to off the manual backwash initiation button was pushed. The amber backwash light did not come on even after holding for greater than 60 seconds. COntacted CRS and tried to manually move timer motor assembly and all functions performed as they should have. Placed the timer motor back in position as found and tried to initiate a manual backwash, while watching the roll timer assembly. No movement was noted during this time. Believe the timer motor is not working or a relay is/has not made up like it should. <I> **** Actions Taken **** Performed actions above and discussed at length with the CRS. Wrote this CR/WR <N> **** Equipment Description **** floccculater
388557 | CR | 20190106 | CAQ | C | Received SLC tank high level alarm | Y | Y |  | N | YES | <D> **** Detailed Description **** Received SLC tank high level alarm, 4.603.A8 5-8. SLC tank level took a prompt level increase to greater than 5100 gallons local indication is also elevated to approximately 5050 gallons, the bubbler flow rate is 1 scfm. <I> **** Actions Taken **** Followed ARP | 02-00-SLC-LI-601
388558 | CR | 20190106 | CAQ | D | C240 | N | N |  | N | YES | <D> **** Detailed Description **** Tamper alarm, bouncing <I> Contact security for more details. Non-reportable. compensatory measures put in place. | 02-00-SEC-TAS-BC240T
388559 | CR | 20190106 |  | 4 | RX 522' Broken Light Switch Toggle (N.Pipe Space) | N | N |  | N | NO | <D> **** Detailed Description **** Light switch toggle just inside the RX 522' N Pipe Space Door is broken.(outside HRA) <I> **** Actions Taken **** -Initiated CR & WR. -Notified Supervision via e-mail. Non-essential lighting. <N> **** Equipment Description **** RX 522' N Pipe Space Room
388560 | CR | 20190106 |  | 4 | Received LP HTR 1C level high alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received LP heater 1C level high alarm. HD-LIC-1C is controlling at setpoint and normal. | 02-00-HD-LS-1CH
388561 | CR | 20190106 |  | 3 | Plateau CBT system unavailable |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The Plateau CBT system was unavailable on 1/6/19 from ~6 AM to ~ 11 AM due to an Oracle database connection issue. Plateau Application Analyst contacted Orace DBA to investigate. Application Analyst verified the Plateau CBT system is working now but root cause is unknown. Recommend NON CAQ 3 to research root cause. Issue is simliar to incident on 9/30/18 documented in CR 385070. <I> **** Actions Taken **** Notified IS Duty Officer and System owner.
388562 | CR | 20190106 |  | 4 | Error message on the MMS Durability Monitor | N | N |  | N | YES | <D> **** Detailed Description **** MMS Durability Monitor PC has an error, "The Chem/ECP file size is greater than 4 megabytes." This error prevents chemistry personnel from being able to obtain daily ECP readings which could potentially impact CEI. According to SWP-CHE-02, ECP readings are a good practice with no required actions. Notified chemistry specialist. specialist has been contacted. <I> **** Actions Taken **** Attempted to re-start the program in accordance with CI -15.2, but the error message remained. Notified chemistry specialist. <N> **** Equipment Description **** 548' Rx Bldg northside. | 02-00-PSR-CAB-1
388563 | CR | 20190106 |  | 4 | REA-FT-3 Failed Calibration | N | N |  | N | YES | <D> **** Detailed Description **** WO# 02130000-01 while performing this WO task REA-FT-3 failed calibration. While adjusting transmitter SPAN at 100% output, the SPAN pot was only able to achieve 13.15 mA until we ran out of adjustment. As found values were grossly low and out of tolerance. REA-FT-3 needs replacement. <I> **** Actions Taken **** Notified CRS, Notified Supervison, SSS was on station durring calibration, and notified Mike Holle(Engineer) <N> **** Equipment Description **** RX 572' M9/7.8 near | 02-00-REA-FT-3
388565 | CR | 20190106 |  | 3 | E-B0-1A & E-B0-1B chargers in equalize position |  |  |  | N | YES | <D> **** Detailed Description **** When starting ESP-BAT-W101, 02129588, weekly battery test, found E-B0-1A & E-B0-1B in the equalize position, determined that on 1/2/19 W/O 02106308-01 was conducted to check specific gravities in the batteries, specific gravities were low which generated Cr388448 & WR 29146395 and placed the chargers in the equalize position. <I> **** Actions Taken **** Informed WWM, Ops, Maintenace management, completed weekly battery checks and WR 29146395 <N> **** Equipment Description **** RW 467 vital island | 02-00-E-B0-1A,02-00-E-B0-1B
388566 | CR | 20190106 |  | 3 | MCR microwave doesn't work | N | N |  | N | YES | <D> **** Detailed Description **** The MCR microwave works intermittently. <I> **** Actions Taken **** Heated lunch using the oven. <N> **** Equipment Description **** MCR kitchen. . New microwave purchased and placed in MCR kitchen. no further actions needed.
388567 | CR | 20190106 | CAQ | C | HELB door evaluations |  |  |  | N | NO | <D> **** Detailed Description **** Doors being indentified as HELB barriers in PPM 1.3.57 rev 37 need evaluated for comp actions. Current process does not allow impairing doors without engineering input. The need for this can occur at any time. This is very cumbersome activity and may actually prevent action that is required to control the plant. Additionaly this may lead to inoperability of essential equipment and entering a short duration LCO due to the location of these doors. While conservativly identifed as HELB barriers this is not the least risk option for the plant and any capable of being removed should be. Any others need defined comp actions that can be referenced at any time.
388568 | CR | 20190107 | CAQ | C | Received Rx bldg. Stack critical failure | N | Y |  | N | YES | <D> **** Detailed Description **** Received the Reactor building stack critical failure 4.851.S2 drop 2-4. PRM-RIS-1 display reads â€œUnable to connect socket, trying to re-connect.â€ PRM-CP-2 display also reads â€œUnable to connect socket, trying to reconnectâ€ <I> **** Actions Taken **** Informed CRS | 02-00-PRM-RIS-1
388569 | CR | 20190107 |  | 3 | WO task 02136058-12 unable to set to finished |  |  |  | N | NO | <C> OFM change request from group MNTPROG and assigned to OPSWC to provide training to Ops Staff - 1/8/2019. <D> **** Detailed Description **** WO task 02136058-12 is a support task and as such EWP should allow the task to be set to finished, however the set to finish option was greyed out and was unable to be performed. The CRS had to manual process the entire workflow for this work order task vice being able to set the task to finished. This created inefficiencies in the work order process. Recommend training to the responsible group to ensure proper coding is assigned to support task Work Orders in the EWP process. <I> **** Actions Taken **** Asked the CRS to process the WO to allow the task to be taken to finished <N> WO 02136058-12 job Type is â€˜SPâ€™ (Support) and in DataGlance the user would normally be able to set the WO straight to FINISHED, but this option is not allowed if the Control Room Communication, on the Asset Suite Nuclear Panel, is set to â€˜1â€™ or â€˜2â€™. . This WO task 02136058-12, although it is a support task, has the Control Room Communication set to â€˜1â€™, meaning that it is â€œHIGH IMPACT â€“ Only PSRO/OPS may take to 48â€. The software is working as designed. . Operations has the ability to change the value during their Ops (CORC/WC) review.
388570 | CR | 20190107 |  | 4 | Poor Lighting RHR-P-2C Room | N | N |  | N | YES | <D> **** Detailed Description **** There is poor lighting in the RHR-P-2C room, only two light fixtures are working. Relamp as soon as possible. <I> **** Actions Taken **** Wrote CR/WR <N> **** Equipment Description **** Lighting in RHR-P-2C room
388573 | CR | 20190107 |  | 3 | WO 02136058 for FDR-FU-19 has Redundant OPS Authorizations |  |  |  | N | NO | <D> **** Detailed Description **** WO 02136058 has 7 OPS authorization tasks for a septa replacement on FDR-FU-19. This is excessive and wasting SRO time. Tasks that are hang and or lift should not be OPS authorization since no one other then an SRO can authorize tag hangs or lifts. Additionally, scaffolding support as necessary, HP tasks, and PMT tasks for non-TS equipment should not have OPS authorization. If there is not a standard way to code WOs as OPS authorization, one needs to be created to avoid excess work. <I> **** Actions Taken **** Discussed wtih SM.
388574 | CR | 20190107 |  | 3 | WO task 02116386-02 unable to set to finished |  |  |  | N | NO | <D> **** Detailed Description **** WO task 02116386-02 is a support task and as such EWP should allow the task to be set to finished, however the set to finish option was greyed out and was unable to be performed. The CRS had to manual process the entire workflow for this work order task vice being able to set the task to finished. This created inefficiencies in the work order process. Recommend training to the responsible group to ensure proper coding is assigned to support task WO in the EWP process. <I> **** Actions Taken **** Asked the CRS to process the WO to allow the task to be taken to finished <N> In DataGlance the user would normally be able to set the WO task 02116386-02 to finished, but this option is not allowed if the Control Room Communication on the Asset Suite Nuclear Panel, is set to '1' or '2'. WO task 02116386-02-03, although it is a support task, the Control Room has communication set to '1', meaning that it is a "HIGH IMPACT - Only PSRO/OPS may to to 48". The software is working as designed. Operations have the ability to change the value during their Ops (CORC/WC) review. Recommend Maintenance to provide Operation awareness of populating applicable fields. An assignment is being created for maintenance to provide awareness. . Tony Pace created and distributed night order 426 to the operating crews.
388575 | CR | 20190107 |  | 3 | WO task 02114331-02 unable to set to finished |  |  |  | N | NO | <D> **** Detailed Description **** WO task 02114331-02 is a support task and as such EWP should allow the task to be set to finished, however the set to finish option was greyed out and was unable to be performed. The CRS had to manual process the entire workflow for this work order task vice being able to set the task to finished. This created inefficiencies in the work order process. Recommend training to the responsible group to ensure proper coding is assigned to support task WO in the EWP process. <I> **** Actions Taken **** Asked the CRS to process the WO to allow the task to be taken to finished <N> In DataGlance the user would normally be able to set the WO Task 02114331-02 to FINISHED, but this option is not allowed if the Control Room Communication, on Asset Suite Nuclear Panel, is set to '1' or '2'. This WO 02114331-02, although it is a support task, the Control Room Communication has it set to '1', meaning that is is a "HIGH IMPACT - Only PSRO/OPS may take to 48". The software is working as designed. Operations have the ability to change the value during thier Ops (CORC/WC) review. Recommend Maintenance to provide Operations awarness of populating applicable fields. An assignement is being created for Maintenance to provide awareness. Note: Please have
388576 | CR | 20190107 |  | 3 | WO task 02114328-02 unable to set to finished |  |  |  | N | NO | <D> **** Detailed Description **** WO task 02114328-02 is a hang clearance task and as such EWP should allow the task to be set to finished, however the set to finish option was greyed out and was unable to be performed. The CRS had to manual process the entire workflow for this work order task vice being able to set the task to finished. This created inefficiencies in the work order process. Recommend training to the responsible group to ensure proper coding is assigned to support task WO in the EWP process. <I> **** Actions Taken **** Asked the CRS to process the WO to allow the task to be taken to finished <N> WO 02114328-02 job Type is â€˜COâ€™ (CLEARANCE ORDER: HANG OR LIFT) and in DataGlance the user would normally be able to set the WO straight to FINISHED, but this option is not allowed if the Control Room Communication, on the Asset Suite Nuclear Panel, is set to â€˜1â€™ or â€˜2â€™. . This WO task 02114328-02, although it is a support task, has the Control Room Communication set to â€˜1â€™, meaning that it is â€œHIGH IMPACT â€“ Only PSRO/OPS may take to 48â€. The software is working as designed. . Operations has the ability to change the value during their Ops (CORC/WC) review. Recommend Maintenance to provide Operation awareness of populating applicable fields. An assignment is being created for maintenance to provide awareness.
388577 | CR | 20190107 |  | 3 | WO task 02136058-03 unable to set to finished |  |  |  | N | NO | <D> **** Detailed Description **** WO task 02136058-03 is a hang clearance task and as such EWP should allow the task to be set to finished, however the set to finish option was greyed out and was unable to be performed. The CRS had to manual process the entire workflow for this work order task vice being able to set the task to finished. This created inefficiencies in the work order process. Recommend training to the responsible group to ensure proper coding is assigned to support task WO in the EWP process. <I> **** Actions Taken **** Asked the CRS to process the WO to allow the task to be taken to finished <N> WO 02136058-03 job Type is â€˜COâ€™ (CLEARANCE ORDER: HANG OR LIFT) and in DataGlance the user would normally be able to set the WO straight to FINISHED, but this option is not allowed if the Control Room Communication, on the Asset Suite Nuclear Panel, is set to â€˜1â€™ or â€˜2â€™. . This WO task 02136058-03, although it is a support task, has the Control Room Communication set to â€˜1â€™, meaning that it is â€œHIGH IMPACT â€“ Only PSRO/OPS may take to 48â€. The software is working as designed. . Operations has the ability to change the value during their Ops (CORC/WC) review. Recommend Maintenance to provide Operation awareness of populating applicable fields. An assignment is being created for maintenance to provide awareness.
388578 | CR | 20190107 | CAQ | D | 16.11.2 received in records w/o Assigned Reviewer Signature |  |  |  | N | NO | <C> OFM change - Priority from NON CAQ to CAQ, Severity Changed from 4 to D. 1/10/2019 <D> **** Detailed Description **** 16.11.2 Grab Gas Samnples work order manual was received in records without the Assigned Reviewer Signature. <I> **** Actions Taken **** Identified the missing signature and notified supervisor. Wrote CR and returned to Chemistry Department.
388580 | CR | 20190107 |  | 4 | ARGOS (HP-EQ-42782) Possible Sensor Issue | N | N |  | N | NO | <D> **** Detailed Description **** The ARGOS (HP-EQ-42782) Located @ the HP PAP regularly tells the monitored individual "Clean, Please Exit." but after the monitored individual steps out to be monitored by the GEM-5, the ARGOS will be stuck in the "Clean, Please Exit" mode as if it thinks a person is still standing in the monitor. This could be a possible sensor issue. ARGOS is to be left in service as it still passes all functional checks and the ARGOS will eventually clear. <I> **** Actions Taken **** -Initiated CR/WR. -Notified HP Supervision. <N> **** Equipment Description **** HP PAP (HP-EQ-42782)
388590 | CR | 20190107 | CAQ | D | M&TE OOT | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0059932 Alber Battery Discharge Test Set- model BCT-2000/256 found OOT & adjusted within specs. EFIN Eval: The unit was OOT low. Thus the battery performance was better than the data indicated. No Impact. DEF #6787A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only
388592 | CR | 20190107 |  | 3 | DG4 operating procedures need alternate shutdown instruction |  |  |  | N | NO | <D> **** Detailed Description **** The DG4 procedures, SOP-DG4-SHUTDOWN, SOP-DG4-SHUTDOWN-QC & OSP-FLEX-M704 need guidance for shutting down DG4 when all other methods of shutdown fail as did on 12/20/2018 recorded in AR 388094 and WR 29146245. Per technicians from Cummins-Northwest, the knurled knob on the fuel stop solenoid will need to be turned fully clockwise to stop fuel flow to the engine and thereby shutdown the engine. The fuel stop solenoid is located on top of the fuel pump which is on the port side of the engine. Once the engine is at a complete stop the knurled knob needs to be returned to the full counter clockwise position. This same issue and solution was recorded in AR 213249 and its resolution. According to the condition evaluation, operators were informed of this method of shutdown. This was not incorporated in any of the DG4 operating procedures and no operators recall being given this information. Please place guidance in the above procedures for shutting down DG4. See EDMS for picture of knob.
388593 | CR | 20190107 |  | 3 | MT-ELV-4 RW elevator needs protection pads to protect walls |  |  |  | N | NO | <D> **** Detailed Description **** The RW elevator has a brand new interior. Due to cargo movement that will begin soon in preparation for Refueling outage the walls are going to be damaged/scratched. Padding is readily available made to protect the interior of the elevator during such traffic. I would like to see ENW obtain and install this padding from now until post outage cleanup is complete. <I> **** Actions Taken **** No Work Request written as this is not an equipment deficiency.
388597 | CR | 20190107 |  | 3 | Dose savings opportunity for lighting |  |  |  | N | NO | <D> **** Detailed Description **** ENW Electricians replaced incandescent light bulbs in Rx 548â€™ RHR â€˜Aâ€™ HX Room to support upcoming Service Water window work. There was 2 p-mrem expended. In September 2012 WO 02030619 was created to â€˜REPLACE TYPE V8 LIGHTING IN RHR HEAT EXCHANGER ROOM Aâ€™. This WO was cancelled on 04/18/18 with the work not started. WO 02130025, â€˜RX 548' "A" RHR HX ROOM HAS NO LIGHTING - DON'T CANCELâ€™, was approved on 11/20/18 so there would be adequate lighting to support RHR Motor Operator work (02113021) in that room on 12/04/18. The lighting was not replaced and temporary lights were used instead. WO 02130025 is still at APPROVED Status and is scheduled for 11/22/2020. Dose rates in the R548â€™ RHR HX Room are at the lowest level that has been seen in many years, and it is an ideal opportunity to change those lights to LED fixtures, as has been done is several other HRA & LHRA rooms. If this conversion to LED lights is not completed between now and the start of R24, there is a high probability that the dose rates will return to an elevated level after RHR â€˜Aâ€™ system is used during R24. <I> **** Actions Taken **** Documented CR. Notified RP Manager.
388599 | CR | 20190107 | CAQ | D | SW-V-171A Difficult to operate | Y | N |  | N | YES | <D> **** Detailed Description **** While performing WO 02076391 (SW-V-171A, Difficult to operate) Mechanics were able to operate valve, lubricated stem threads, but still found it very difficult to operate. This valve should be repacked and possibly replace the stem bushing. <I> **** Actions Taken **** Mechanics notified supervisor <N> **** Equipment Description **** SW B pond | 02-00-SW-V-171A
388605 | CR | 20190107 |  | 4 | RW elevator OOS | N | N |  | N | YES | <D> **** Detailed Description **** The RW elevator cannot be called. The display says it is on the RW 467 elevation but it doesn't open any doors there. <I> **** Actions Taken **** WR written <N> **** Equipment Description **** RW building | 02-00-MT-ELEV-4
388606 | CR | 20190107 |  | 3 | TSP-FPC/ISI-G802 does not test all ASME Piping as required |  |  |  | N | NO | <D> **** Detailed Description **** TSP-FPC/ISI-G802 is written to perform a leak test on the RHR/FPC cross tie piping and can be performed either on -line with external pressurization or during an outage when the cross tie piping is in operation. If performed on -line the procedure only addresses the suction piping and does not adress pressurizing the discharge piping between RHR-V-104 to FPC-V-119. When performed during an outage under SOP-FPC-ASSIST-ALT or ABN-RHR-SDC-ALT all piping is adequately tested, however W/O 02090235 is currently scheduled to be performed on-line so additional steps will need to be added to the procedure to isolate and pressurize the discharge piping or otherwise verify that that portion of the system is operating prior to inspection. <I> **** Actions Taken **** Discussed procedure with the System engineer and discussed the issue with the Procedure Sponsor. Recommend assignment to OPSPROC to revise the procedure. Verified that this is the first scheduled performance of this procedure since installation of the cross-tie. This PM has not yet been completed and is due 3/1/19. There is currently no DNC as no requiements have been missed.
388608 | CR | 20190107 |  | 4 | 2 o-rings out of 52 misplaced/location not known |  |  |  | N | NO | <D> **** Detailed Description **** CATID 58408042 is the CATID for the filter assemblies for FDR-FU-19. Replacement of the filter unit requires 52 filter assemblies. The o-rings are supplied with the Filter Assembly CATID. As part of the job walkdown prior to removal of the WD hold it was verified that each of the 52 filters contained an o-ring that was attached to each filter in preps for staging at 75/in plant. During pre-assembly of the replacement tubesheet and filters on the RW 507', it was identified that only 50 o-rings could be located (were in the bag that was supplied to meet the MR demand) as opposed to the 52 originally accounted for. Contacted Warehouse who looked for the two additional o-rings however they were not located at the original storage location. No Impact to installed plant equipment. CR for information regarding 2 o-rings that for some reason could not be accounted for. <I> **** Actions Taken **** Contacted Procurement and created a separate CATID (38457) and MR for procurement of the O-rings as a stand alone item. Generated CR for information only. It is not known where/when the potential misplacement/litems going astray occurred.
388609 | CR | 20190107 |  | 4 | turbine bldg door T-134 won't open | N | N |  | N | YES | <D> **** Detailed Description **** turbine bldg door T-134 will not open elactrically or manually. Manual chain operator off its track. <I> **** Actions Taken **** CRS notified. <N> **** Equipment Description **** Turbine bldg 441 west side
388610 | CR | 20190107 |  | 3 | WO task 02114042-03 unable to set to finished |  |  |  | N | NO | <D> **** Detailed Description **** WO task 02114042-03 is a lift clearance task and as such EWP should allow the task to be set to finished, however the set to finish option was greyed out and was unable to be performed. The CRS had to manual process the entire workflow for this work order task vice being able to set the task to finished. This created inefficiencies in the work order process. Recommend training to the responsible group to ensure proper coding is assigned to support task WO in the EWP process. <I> **** Actions Taken **** Asked the CRS to process the WO to allow the task to be taken to finished <N> WO task 02114042-03 job Type is â€˜COâ€™ (CLEARANCE ORDER: HANG OR LIFT) and in DataGlance the user would normally be able to set the WO straight to FINISHED, but this option is not allowed if the Control Room Communication, on the Asset Suite Nuclear Panel, is set to â€˜1â€™ or â€˜2â€™. This WO task 02136058-03, although it is a support task, has the Control Room Communication set to â€˜1â€™, meaning that it is â€œHIGH IMPACT â€“ Only PSRO/OPS may take to 48â€. The software is working as designed. Operations have the ability to change the value during their Ops (CORC/WC) review. Recommend Maintenance to provide Operation awareness of populating applicable fields. An assignment is being created for maintenance to provide awareness.
388611 | CR | 20190107 |  | 4 | No water when draining CRD-FU-7B for maintenance | N | N |  | N | YES | <D> **** Detailed Description **** While draining CRD-FU-7B per SOP-CRD-FILTERS it was noted that when CRD-V-533B was opened no water was observed draining. The equipment operators were expecting water to drain and this may be indication of a clogged drain line. <I> **** Actions Taken **** Informed CRS | 02-00-CRD-V-533B
388612 | CR | 20190108 | CAQ | D | SW-MO-2A-3/8â€ Lock washer missing from limit switch Cover | Y | N |  | N | YES | <D> **** Detailed Description **** SW-MO-2A-3/8â€ Lock washer missing from limit switch enclosure cover found during PM inspection (0208794701 SW -MO-2A LUBE/INSPECT, FULL PM) . Maintenance when trough the BOM for SW-MO-2A and was unable to find a like for like lock washer. The 3/8â€ Lock washer located is of the same I.D., material and quality class as the â€œmissing washerâ€ the only discrepancy is the purchased washer has a wider shoulder (larger O.D.). The lager O.D. isnâ€™t an issue for installation purposes (there are no interferences making the part unusable) and only adds a larger barring surface for the 3/8â€™ fastener. <I> **** Actions Taken **** Wrote CR, contacted OCC and Engineering <N> Electricians installed lock washer CID 0025314660 3/8" NOMINAL BOLT SIZE FOR LIMITORQUE MODELS SMB-000 THRU SMB-3 MOTOR. The lock washer is not a Critical component listed in the Limitorque Critical Components List (PDF in CVI Manual 999-00,12,2 rev. 3). There are 2 different Limitorque Part numbers for the LS Compartment cover lock washer: 1. Limitorque Part # HS8-3/8 is for an alum cover (CATID's 25314660) and 2. Limitorque Part # HT8-3/8 is for ductlile iron (CATID's 25314751 & 25318020)). The BOM lists CATID 25318020. The limit switch cover is ductile iron. HS8-3/8 has a larger OD than HT8-3/8. It is preferred to use HT8 -3/8 per design but will not impact the design function of LS cover. The installation of the lockwasher is nonconforming based on the parts listed in the OMM. The lockwasher should be replaced with the correct lockwasher in the future as the currently installed lockwasher is non conforming to the desgin. | 02-00-SW-MO-2A
388620 | CR | 20190108 |  | 4 | COND-P-1C vibe points show increase | N | N |  | N | YES | <D> **** Detailed Description **** The spectral data for most points indicate an increase at 1X Operating Speed. Amplitudes are still low at 0.23 IPS -Pk. The increase is seen in both the radial and axial directions indicating a potential minor change in alignment or coupling condition. Since levels are still low, additional trending is needed is to confirm an issue. Continue monitoring. No maintenance action needed at this time. Additional trending, via current PM frequency (M03), will be used to monitor and trend the increase. If levels continue to increase over future data sets then further recommendations will be provided. <I> **** Actions Taken **** Vibration data reviewed. Notified systems engineer, BOP supervisor, large motor/pump engineer, and components supervisor. | 02-00-COND-P-1C
388621 | CR | 20190108 |  | 4 | Missed scheduling logic tie SW-A Lesson Learned |  |  |  | N | NO | <D> **** Detailed Description **** During performance of the SW maintenance window it was identified that a logic tie was missed between a PMT task and a lift clearance. WO 02116386 PMT task 03 should have been logic tied to both the SW-Drain and SW-P-1A clearance. However it was only tied to the breaker rack in not the clearance lift. The result was a missed task in the schedule. There was no impact on the overall SW window <I> **** Actions Taken **** Resolved issue Discussed with maintenance and operations
388624 | CR | 20190108 |  | 3 | SCS maintenance unexpectently higher than previous year |  |  |  | N | NO | <D> **** Detailed Description **** On January 7th Energy Northwest received a quote for the annual maintenance for the security computer system (SCS) cost in which the minimum coverage was approximately 50% higher than previous year (2018 ~ 60k & 2019 ~90k). In addition, the options for vendor provided patch testing and warranties has also increased 25% to 40%. The quote is being evaluated by a multi-discipline team including Computer Engineering, Security, and Cyber Security to ensure the correct decision is made. <I> **** Actions Taken **** Assign to ITMGMT as NCAQ 3. <N> Met with Engineering and Security to create a plan forward. This will be over the normal budgeted amount.
388630 | CR | 20190108 |  | 3 | Unable to validate an issued badge |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** When attempting to validate an active badge (in CAS) for a contractor, the CAS operator was automatically logged off work station# 2 by the AIM system. The CAS operator restarted the work station, and then attempted the same task on work station #1 and experienced the same result. Access Authorization restarted IEBS 1, ensured all badge tables were correct and issued a new badge. The CAS operator experienced the same result. No other issued badges experienced this same issue today. <I> **** Actions Taken **** Contacted Security Services Manager and Computer Engineering for the AIM system. Please assign to org #54211 <N> **** Equipment Description **** AIM system in CAS
388631 | CR | 20190108 |  | 4 | Simulator Interruption - eDNA GDS Screens Sluggish |  |  |  | N | NO | <D> **** Detailed Description **** The simulator eDNA based GDS screens were slow to respond to input on 1/7/2018 during the setup for an evaluated scenario. In order to allow time to fix the problem the evaluated scenario was rescheduled to the afternoon. Waiting for the problem to be resolved caused a loss of 60 minutes of training time and is considered a simulator interruption. The simulator evaluation and all other scheduled training was able to be completed on 1/7/2018. See SR 2855 for further details. <I> **** Actions Taken **** The problem was fixed under SR 2855 by rebooting eDNA servers and restarting eDNA processes and resetting the simulator interface PC. See SR 2855 for further details.
388632 | CR | 20190108 |  | 3 | Secured documents were open to searching in theCurrent. |  |  |  | N | NO | <D> **** Detailed Description **** Secured documents were open to searching in theCurrent. <I> **** Actions Taken **** Immediate action â€“ known locations with limited access files were updated to ensure documents would not show up in a search. Notified IS Analyst and IS Supervisor. <S> Worked with IS to ensure all locations with unique permissions were identified and that they were locked down so that files were not available by search. Identified all fiiles that were opened during the time the files were available by search. Provided list to each department identifying the files that were opened and by whom.
388633 | CR | 20190108 | CAQ | D | Original ASME XI Work Plan 2-2981 not found |  |  |  | N | NO | <D> **** Detailed Description **** After an extensive search the original ASME XI Work Plan 2-2981 and it could not be found at package prep after QC and ANII reviews were completed. No plant impact. <I> **** Actions Taken **** Notified QC, ANII, and planning to recreate documents and initiated CR
388637 | CR | 20190108 | CAQ | D | SW-V-612 may not be full closed. | Y | N |  | N | YES | <D> **** Detailed Description **** Equipment operator reported that SW-V-612 was difficult to close he was uncertain that the valve is fully shut and did not want to break the valve. <I> **** Actions Taken **** He informed supervision and the OCC was contacted to have a mechanic provide assistance. This is a normally closed and capped valve. | 02-00-SW-V-612
388640 | CR | 20190108 |  | 3 | R24 Yellow Planning Milestone |  |  |  | N | NO | <D> **** Detailed Description **** In accordance with PPM 1.20.1, section 3.2.3 the outage planning milestone is declared Yellow by the Milestone owner ( Maint Dept Planning) Total scope milestone has dropped below Green and will require a recovery plan to recover and get back to green. Assign this to ARMNTPLN
388641 | CR | 20190108 |  | 3 | Determine if enhancement to ABN-CAS is warranted. |  |  |  | N | NO | <D> **** Detailed Description **** ABN-CAS step 4.2 directs scramming the reactor when air header pressure reaches 75 psig. However that pressure is the setpoint of CAS-PCV-1, which bypasses the dessicant dryers in a last effort to save the CAS system. It would be prudent to allow this action to occur before scramming the reactor. Here are a few (there may be more) options for correcting this condition: 1. Raise the setpoint of CAS-PCV-1. 2. Lower the pressure at which a scram is required. 3. Make step 4.2 conditional if it's expected that opening CAS-PCV-1 would correct the low pressure condition. Recommend assigning to System Engineer and Ops Management. <I> **** Actions Taken **** Informed Ops Training
388642 | CR | 20190108 |  | 3 | (QA) Radioactive material labels not current |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Five 55-gallon drums containing service water were incorrectly labeled with out-of-date radioactive material labels that indicated the drums were empty. The drums are currently used to store water drained from the service water system and are staged outside of the RHR-A heat exchanger room on the Reactor Building 548â€™ elevation. . Actual and Potential Consequences: Workers are not informed of current radiological hazards if radioactive material labels are out-of-date. Service water is non -contaminated so the contents did not introduce an actual radiological hazard to workers. . Factual Basis: PPM 11.2.14.9, Control and Labeling of Radioactive Material, step 4.2.2 requires updated radioactive material labels when the label does not properly communicate the contents of a container. . Insights: The drums were correctly labeled as empty when staged to support service water system maintenance, but the radioactive material labels were not updated when the drums were filled. . This issue is considered a deficiency identified during Continuous Monitoring activities. <I> **** Actions Taken **** An HP Technician surveyed the drums, verified the contents, and applied updated radioactive material labels after prompting from the Quality Auditor. <N> **** Equipment Description **** N/A
388643 | CR | 20190108 |  | 3 | Wire found terminated at point identified as SPARE. | N | N |  | N | YES | <D> **** Detailed Description **** While Performing W.O.# 02095007-11 to implement EC 12510 it was found that the termination point identified under the Cable Termination Instruction (12510-114) at E-LP-1CF to land lead at CKT 1 already has an unidentified wire terminated at this point. Based on inspection of the panel by craft personnel it would be better to use spare CKT 24 which does not have a wire already terminated at that location. Engineering to disposition EC change. L-DW-FI-1-001 has tag 903 hung on E-CB-LP1CF/1. Once new location identified and EC updated the clearance order needs to be changed. <I> **** Actions Taken **** Electrical Supervision informed. Work Week Manager Informed. Engineering Informed. EFIN Supervisor informed. | 02-00-E-CB-LP1CF/1
388647 | CR | 20190108 |  | 3 | Outage PI Yellow for Maintenance Walkdowns Completed |  |  |  | N | NO | <D> **** Detailed Description **** This CR is written in accordance for the maintenance walkdown PI going yellow, in accordance with PPM 1.20.1. Actions to recover this metric include use of targeted overtime by I&C, Mechanics and Electricians. Target to recover this metric to green status is 2/18/19. <I> **** Actions Taken **** Documented performance and recovery action in this CR. Discussed with Maintenance Manager, and all Maintenance Componant Managers.
388648 | CR | 20190108 |  | 4 | HSSF nitrogen tank low pressure alarm received |  |  |  | N | YES | <D> **** Detailed Description **** Alarm NT PIT300-PRES STAT LOW was received on the HSSF -CAB-CHEM/LAB HMI computer. This is the Nitrogen tank low pressure alarm. The alarm cleared when acknowledged, and the tank pressure is currently indicating 106.5 psig. Notified CRS who informed chemistry that the vendor was delivering Nitrogen at the time. This CR is written for documentation only. <I> **** Actions Taken **** Notified CRS and wrote a CR per CI-14.4 required actions. | 02-00-HSSF-CAB-CHEM/LAB
388649 | CR | 20190108 |  | 4 | 10.25.86 procedure clarity & new test equipment |  |  |  | N | NO | <D> **** Detailed Description **** Precedure steps clarity & new test equipment . Use of new test equipment needs added. Steps need cleaned up for clarity & work flow. <I> **** Actions Taken **** Notified supervisor, procedure writer. added marked up procedure to EDMS. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
388650 | CR | 20190108 |  | 4 | Repeat actuation of TMU-RLY-5051/TMU1B/C | N | N |  | N | YES | <D> **** Detailed Description **** After reviewing recent trends and work history on TMU-RLY -5051/TMU1B/C it was identified that this component may be degraded and susceptible to unanticipated actuation, as occurred in CRs 386909 and 388044. TMU-RLY-5051/TMU1B/C provides overcurrent protection for TMU-M-P/1B and will generate a pump trip in the case of inadvertent actuation. There is no concern of a TMU pump trip at this time, as TMU-P-1B is currently out of service. Prior to returning TMU-P-1B to service it is recommended that TMU-RLY -5051/TMU1B/C be replaced with a calibrated spare and the currently installed relay provided to Engineering for further analysis. <I> **** Actions Taken **** Informed supervisor of condition. | 02-00-TMU-RLY-5051/TMU1B/C
388651 | CR | 20190108 | CAQ | D | Low flow indicated for RRA-CC-12 | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of OSP-SW-M101 SW-A Flow Balance, Ops 2 reported that the ultrasonic flow instrument for RRA-CC-12 was stuck at 4.1 gpm. Normal flow is 20 â€“ 25 gpm. The installed SW-FI-41 indicated LT 5 gpm. NDE readjusted and reset the UT meter which then began tracking with a full strength signal at 2-3 gpm. With direction from the CRS the operators then cycled SW-V-98 from the as found position to full open. Indicated flow went upscale. SW-V-98 was then returned to the as found position and both indications are now reading ~ 20 gpm. SW-SYS-A is currently inoperable for annual safety system maintenance window. OSP-SW-M101 is being performed as final Operability testing following the window. Note that SW-FE-41 orifice flanges were upgraded during this window under EC17446. <I> **** Actions Taken **** In response to the indication, OCC was informed, NDE readjusted the UT meter and Operations cycled SW-V-98. Flow indications appear normal. | 02-00-RRA-CC-12,02-00-SW-FE-41,02-00-SW-FI-41,02-00-SW-V-98
388652 | CR | 20190109 | CAQ | D | Small leak found on Annubar at ferrule connection SW-FE-12 | Y | N |  | N | YES | <D> **** Detailed Description **** Small leak found on Annubar at ferrule connection. Leak found while performing PMT 0208442806 TT (M) - SW-FE-12 PMT LEAK CHECK. <I> **** Actions Taken **** Craft tightened ferrule nut 1/8 turn leak stowed down to 1 to 2 drops an hour. Mechanics do not suggest to try to tighten nut, further tightening may cause damage. | 02-00-SW-FE-12
388659 | CR | 20190109 |  | 3 | Drawing E848-1A not updated | N | N |  | N | YES | <D> **** Detailed Description **** Drawing E848-1A was not updated when EC 13492 relocated the EPN's listed below to the main control room and W525. The location information in MEL for the EPN's was also not updated. <I> **** Actions Taken **** Recommend correcting MEL and revising E848-1A. Recommend adding the drawings associated with the current location of the EPN's to their Doc/Journal panel and removing E848-1A . | 02-00-PDIS-CPU-DATA1,02-00-PDIS-CPU-DATA2,02-00-PDIS-CPU-HIST1,02-00-PDIS-CPU-HIST2
388660 | CR | 20190109 |  | 4 | 3 Exhaust Fans Inoperable at the security checkpoint | N | N |  | N | YES | <D> **** Detailed Description **** 3 exhaust fans inoperable at the security checkpoint: Menâ€™s restroom, womenâ€™s restroom, and mechanical/janitorial room. <I> **** Actions Taken **** Initiated CR/WR and informed supervision. <N> **** Equipment Description **** security checkpoint
388661 | CR | 20190109 |  | 4 | Restroom door lock inoperable | N | N |  | N | YES | <D> **** Detailed Description **** The menâ€™s restroom door lock at the security checkpoint is inoperable and requires maintenance. <I> **** Actions Taken **** Initiated CR/WR and informed supervision. <N> **** Equipment Description **** menâ€™s restroom door, security checkpoint
388663 | CR | 20190109 |  | 3 | Model WO 00BXM4 requires update |  |  |  | N | NO | <D> **** Detailed Description **** Model work order 00BXM4 for spray pond sediment checks requires an update to remove the ops review required flag from support task 10. <N> 00BXM4 has been updated to remove the ops review flag on task 10. see cross refs panel.
388666 | CR | 20190109 |  | 3 | Alarms on H13-P840.A2 are a major nuisance post-scram. |  |  |  | N | YES | <D> **** Detailed Description **** Following a reactor scram, feed water heater level alarms on H13-P840.A2 continuously alarm and clear, becoming a major nuisance to the reactor operators while they are responding to the scram. All the alarms on this panel provide no useful indication in this condition. This annunciator panel should be silenced after a scram so that the reactor operators can focus on more important things. I recommend a silence button similar to the one at H13-P851, Board S. However, the time delay that would enable the alarms to sound should be at least 30 minutes, if not longer, instead of the 10 minutes that the button on Board S provides. <I> **** Actions Taken **** Wrote this CR and WR. | 02-00-ANN-ANN-A/A2
388672 | CR | 20190109 | CAQ | C | LEFM paths 1A1, 1B8, 2A2 | N | Y |  | N | YES | <D> **** Detailed Description **** Based on the results of maintenance performed on 1/3/2019 (WO 02125629-01 â€“ LEFM acoustic waveform capture) the 1A1D transducer was recorded as exhibiting abnormally high random noise preceding the signal. For this reason replacement of both 1A1 transducers is recommended at the next opportunity. Due to efficiencies that can be gained it is recommended that the transducers for paths 1B8 and 2A2 also be replaced based on their performance this cycle (1B8U gain spiking CR 372596 and an increasing trend in intermittent 2A2 path rejects). The 6 transducers of these 3 paths are among the 14 (of a total of 32) that were not replaced during R23 â€“ but are exhibiting signs that may be precursors to premature failure. Current system performance remains satisfactory and is expected to allow for operation in check-plus until R24, but continued check-plus operation during cycle 25 is of concern. AR OSCR 388671 has been initiated to request adding this scope to R24. <I> **** Actions Taken **** Discussed with Supervisor. | 02-00-RFW-FE-3/A,02-00-RFW-FE-3/E,02-00-RFW-FE-3/M,02-00-RFW-FE-3/R,02-00-RFW-FE-4/B,02-00-RFW-FE-4/F
388673 | CR | 20190109 |  | 3 | Breaker rating doesn't agree with drawings | N | N |  | N | NO | <D> **** Detailed Description **** Print EWD-46E-374 shows that the main breaker for E-LP-5BA has a rating of 100 amps. Field observations have determined the installed breaker has a rating of 150 amps. Breaker has failed (won't open, refer to AR 366936) and will be replaced. The type of breaker installed is also obsolete. Recommend assignment to design engineering to determine what breaker rating is actually required so that a replacement breaker can be purchased and installed.
388674 | CR | 20190109 | CAQ | C | Drawing M501 Note 9 needs to be updated |  |  |  | N | NO | <D> **** Detailed Description **** Drawing M501 Note 9 needs to be updated. This note states, "System and component abbreviations can be found in the master equipment list (MEL) or in section 1.2 of the FSAR which is updated annually." This section of the FSAR is updated on an as-needed basis rather than on a fixed time frame. Recommend deleting the frequency from the note. <I> **** Actions Taken **** Discussed with Licensing Supervisor.
388677 | CR | 20190109 |  | 4 | Model WO needs task added for Refuel Bridge PM |  |  |  | N | NO | <D> **** Detailed Description **** PM WO 02105447 to perform REFUEL PLATFORM ELEC. PM's should have had a task for RP to appropriately plan to have a zone established for lifting the mast out of the water with the bridge positioned outside of the SFP. However no task was in the model WO. Model WO 00CE38 has been updated with task 10 to include this support. This CR is for trending purposes only. <I> **** Actions Taken **** Notified planning generated CR Added to T+1 critique for the 1/7/19 report
388687 | CR | 20190109 | CAQ | C | SQA documentation error in 2012 |  |  |  | N | NO | <D> **** Detailed Description **** It was identified that during the Radio Obsolescence Project in 2012-2014 their was software installed on the Network Managment Client that was not submitted to SQA for documentation. No CD/DVDs were found with this software to validate the software in the Project folder. <I> **** Actions Taken **** Notified IS Supervisor and created SQA documentation. Initiated CR to document the missing SQA documentation.
388688 | CR | 20190109 |  | 3 | PPM 1.10.1 references superceded FAA Advisory Circular |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.10.1 references a superceded FAA Advisory Circular. AC/70/7460-1K has been superceded by AC/70/7460-1L. 1.10.1 needs to be revised to reference the current FAA Advisory Circular.
388691 | CR | 20190109 |  | 4 | DG4 load bank tripped. | N | Y |  | N | YES | <D> **** Detailed Description **** During run of DG4 per OSP-FLEX-M704. After loading the bank to 350KW the door was partially closed, before 1 min had passed and load verified at the diesel the load bank had tripped all loads and turned its fan off. <I> **** Actions Taken **** Informed MCR & SSS, load bank brought back online slowing to complete testing. | 02-00-E-RES-DG4/1
388693 | CR | 20190109 |  | 3 | BS-V-33, Temporary leak enclosure is leaking | N | N |  | N | YES | <D> **** Detailed Description **** The enclosure installed on BS-V-33 is currently leaking and needs to be reinjected to stop leak. WO#02120281-16 has been generated for reinjection. | 02-00-BS-V-33
388694 | CR | 20190109 | CAQ | C | Increase in foreign material floaters identified in E-B2-1 | Y | Y |  | N | I DONT KNOW | <C> CR reopened to add cross reference to AR 391749, then taken back to complete <D> **** Detailed Description **** During performance of Monthly battery surveillance of E-B2-1, WO#02129627-01, electricians inspected battery cells to determine if demineralized water additions were required. During the inspection, it was noted that several dozen cells have foreign material floaters within the cell jars. The material is similar to floaters that have been previously identified in CR numbers 368625 and 378757. there are approximately 62 cells that have floaters. Previous attempts to retrieve floaters have been unsuccessful and determined to not affect the operability of the Battery string. Engineering and Electrical will maintain an active list of cells that have floaters. <I> **** Actions Taken **** Notified Supervisor, Engineering and CRS. Write CR and WR to attempt retrieval of Floater material. <N> **** Equipment Description **** E-B2-1 Battery Room #1 Vital Island
388695 | CR | 20190109 | CAQ | D | E-B2-1 Cell Leakage Identified | Y | Y |  | N | YES | <D> **** Detailed Description **** During the performance of ESP-B21-M101, cells were identified as possibly starting to leak around where the tops attach to the cell body . In order of severity, they were cells 16, 69,97-100, 63-66, 45-46. <I> **** Actions Taken **** Informed supervision of the finding and contacted engineering. Engineering came to Battery Room 1 to do a visual inspection. Pictures were taken. AR/CR generated to document the condition. CRS informed of the finding and that engineering was evaluating the condition. <N> No impact on operations, electrolyte level is acceptable in all cells. No concern with meeting LCS/Tech spec requirments. R. Roman | 02-00-E-B2-1
388698 | CR | 20190109 |  | 4 | OG Analyzer N2 Calibration Gas Bottle LOW | N | N |  | N | YES | <D> **** Detailed Description **** RIGHT OG Analyzer N2 bottle LT 300 psig. Bottle needs to be changed. <I> **** Actions Taken **** Informed CRS <N> **** Equipment Description **** OG Analyzer Nitrogen
388699 | CR | 20190110 | CAQ | C | High vibe value obtained on point SEH for DG1 WO 0212909401 | Y | N |  | N | YES | <D> **** Detailed Description **** Only one point was found to be high and will need to be analyzed by engineering. This may not be an issue as a similar collection was made in 2014. In previous months the data shows this point averages around ?.4 this month DG1 we collected SEH point at 1.663. all other point on DG1 were trending the same. <I> **** Actions Taken **** Wrote this CR, emailed engineering and contacted CRS | 02-00-DG-GEN-DG1
388700 | CR | 20190110 |  | 4 | Need scaffold to relamp and test fixture identified in 02132 | N | N |  | N | NO | <D> **** Detailed Description **** .Need scaffold to relamp and test fixture identified in 02132100-01 Need scaffold to relamp and test fixture identified in 02132100-01 IN 10.25.64 ATTACHMENT 9.7 ON 467â€™ Lamps LP-6BA-19 need to be tested and new lamps and LP-3DA-27 need new lamps and we will need a scaffold to access the fixtures. <I> **** Actions Taken **** .Wrote this CR emailed Maintenance carpenters <N> **** Equipment Description **** .see page 36 of 10.25.64 for lamp 8 and 9 locations(on map) | 02-00-E-LP-3DA,02-00-E-LP-6BA
388701 | CR | 20190110 |  | 4 | RW Elevator Controller Faults (MT-ELEV-4) | N | N |  | N | YES | <D> **** Detailed Description **** The radwaste elevator has stopped working, with reasons unknown. Inside the equipment cabinet (MT-ELEV-4 machine room on 467) the Pixel Controller had a System Fault red light lit and a EQ (earthquake) fault light lit. The cpu reset button was pressed, and the faults initially cleared but came back within a minute with the same faulted appearance as before. <I> **** Actions Taken **** Attempted reset. Roped off elevator. PA for the elevator OOS announced. | 02-00-MT-ELEV-4
388702 | CR | 20190110 | CAQ | D | eSOMS H101's recalculated later in shift, and resigned after |  |  |  | N | NO | <D> **** Detailed Description **** OSP-INST-H101 in eSOMS was originally signed at 10:23:16 PM on 01/09/19. A calculation error needed to be corrected and the H101's needed to be resigned later in the shift. Re-calculation was performed and the error was corrected. <I> **** Actions Taken **** Wrote CR. Deleted OSP-INST-H101 entry, then recreated the entry, re-calculated readings, and resigned H101â€™s.
388703 | CR | 20190110 |  | 4 | Scaffolds needed for lamp replacemnt of emergency lighting | N | N |  | N | YES | <D> **** Detailed Description **** While performing 02132092-01 HID lighting fixture number 4 circuit ELP-8FC-6 quartz lamp was found burnt out. A scaffold needs to be erected to access this fixture. <I> **** Actions Taken **** Contacted Supervision <N> **** Equipment Description **** . | 02-00-E-ELP-8FC
388704 | CR | 20190110 |  | 4 | ERB light fixture needs replaced | N | N |  | N | YES | <D> **** Detailed Description **** While performing 02132092-01 ERB lighting fixture number W487/2 circuit LP-7EA-35 was found broken. The fixture needs to be replaced. Currently a F16 fixture is installed. <I> **** Actions Taken **** Contacted Supervision <N> **** Equipment Description **** . | 02-00-E-LP-7EA
388705 | CR | 20190110 | CAQ | D | Rod Accumulator Trouble Alarm for CRD-HCU-5843. | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-5843. Dispatched OPS-2 to investigate. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-5843 was due to high water level. OPS 2 drained water per SOP -CRD-HCU and alarm is clear. <I> **** Actions Taken **** Informed CRS | 02-00-CRD-HCU-5843
388710 | CR | 20190110 |  | 4 | Small washout area near trash fence |  |  |  | N | NO | <D> **** Detailed Description **** THere is a small washout area near a trash fence. See originator for specific location. Request facliiites support to repair. <I> **** Actions Taken **** Coordinated with facilities to repair as needed. <N> **** Equipment Description **** Security trash fence
388714 | CR | 20190110 |  | 4 | CW-VBE-P1C/PSY may not be working properly | N | N |  | N | YES | <D> **** Detailed Description **** The vibration point PSY shows a large ski slope at the beginning of the spectrum. The ski slope phenomenon is indicative of an instrumentation issue. Other points on pump and motor do not have a ski slope. This could be due to a faulty connection, cable, or probe. The recommendation is to have I/C techs investigate the instrumentation for the point PSY. <I> **** Actions Taken **** Reviewed vibration data. All other parameters on CW-P-1C and CW-M-P/1C are normal. CW-PNL-P1C is also normal. | 02-00-CW-P-1C,02-00-CW-VBE-P1C/PSY
388717 | CR | 20190110 |  | 4 | DEH-42-1A17C "off" indication, bulb base stuck in socket. | N | N |  | N | YES | <D> **** Detailed Description **** DEH-42-1A17C "off" indication bulb base is stuck in the socket. Bulb came apart while attempting to replace. Copious amounts of rust product also came out with the bulb. This ITE Gould bucket is for DEH-P-2 ( tranfer pump ). <I> **** Actions Taken **** Attempted to remove bulb base ( slightly mangled ), and initiated this AR/WR. <N> **** Equipment Description **** TG 471E | 02-00-DEH-42-1A17C
388718 | CR | 20190110 |  | 3 | Outage sub-indicators no longer linked to parent indicators |  |  |  | N | NO | <D> **** Detailed Description **** All of the sub-indicators associated with outage performance indicators are no longer linked to their parent indicator in the Performance Indicator application. The software must have experienced an issue overnight that caused this to occur because the indicators contained the correct information yesterday. Customers use the indicators daily to track status of outage walkdowns, planning, scope variance, contracts, etc. The software glitch was reported this morning by one of these customers. A priority needs to be placed on restoring the indicator information ASAP to support outage milestones. <I> **** Actions Taken **** Discussed w/Outage Manager, emailed and left voicemail with IS
388720 | CR | 20190110 |  | 4 | Multiple individuals incorrectly removed from training. |  |  |  | N | NO | <D> **** Detailed Description **** On 01/10/19, between 1330 and 1400, approximately 40 managers and supervisors were incorrectly removed from the OT Management continuing training classes on 01/23/19 (ID 50625) and 02/20/19 (ID 50627). The individual who performed the work was tasked with removing a set group from each class and re-enrolling them (to make sure the room location showed up in their Outlook calendar) but instead removed everyone and only re-enrolled the set group. <I> **** Actions Taken **** Once alerted to the event, called the individual tasked with performing the work to verify what had been done. Enlisted the aid of Plateau administrator, IS and one very helpful admin to compile a list of those incorrectly removed. Emailed the Admin staff to let them know what was in progress and ask for their help, re-enrolled those not already re-enrolled by the Admin staff, and sent emails to all effected to explain the situation.
388724 | CR | 20190110 |  | 3 | ABN-AIRBORN-ATTACK needs revision |  |  |  | N | NO | <D> **** Detailed Description **** Note 3 â€œCommunications should be terminated with all agencies except the NRC.â€ This is confusing as this procedure also requires the main control room (MCR) to contact the SCC, who then contacts local authorities. Also, this procedure requires the MCR to make emergency notifications, which doesnâ€™t really line up with terminating all communications with all agencies except the NRC. A phrase like "execpt as directed my this procedure" might be better. Additionally, step M-1 â€œProtected Area Impactâ€ starts with steps to be performed after an impact has occurred, this step should be shaped like a stop sign to align with EOP convention. <I> **** Actions Taken **** Wrote CR.
388726 | CR | 20190110 |  | 3 | TEC battery in the backup system shows degradation. | N | N |  | N | YES | <D> **** Detailed Description **** Battery shows a 24% (TSI-6.3.1 states to notify if >20% increase in internal resistance) increase in internal resistance. System is still operational, and the battery in question will be monitored. <I> **** Actions Taken **** Notified Telecom Supervisor <N> **** Equipment Description **** TEC first floor
388727 | CR | 20190110 |  | 3 | Repair/Return instructions need to be in separate task |  |  |  | N | NO | <D> **** Detailed Description **** When planning work instructions, instructions for inititing the repair data sheet and returning parts to the warehouse for repair need to be in their own task. These instructions are currently included in the main replacement tasks and have recently lead to the main task not able to be closed out in a timely fashion. <I> **** Actions Taken **** initiate CR to document condition. Discussed with planning supervisor.
388728 | CR | 20190110 | CAQ | D | Improper completion of CAQ Assignment 384508-02 |  |  |  | N | NO | <D> **** Detailed Description **** The corrective action program (CAP) reviewed the completion of assignment 02 on CR 384508 and determined that it unsuccessfully met SWP-CAP-01 requirements. The action was to revise SWP-LIC-03 as explained in the OPIT Evaluation write-up and on assignment 2. This assignment (384508-02) went complete on 12/31/2018 and the Procedure was not updated until 1/07/2019. The completion of this assignment preceded the intent of the action, which was to update the procedure accordingly and the assignment should not have been completed until the procedure was issued; this is considered a â€œpromise to payâ€. <I> **** Actions Taken **** Both departments that were responsible for the completion and approval were contacted. Thumbs down was taken and coaching was provided to both Regulatory Affairs and Operations groups. <N> Recommend D/Trend
388736 | CR | 20190110 |  | 3 | FDR-FU-19 missing U-bolt discovered during re-assembly | N | N |  | N | YES | <D> **** Detailed Description **** During re-assembly of FDR-FU-19 WO 02136058-01 it was discovered that a U-bolt for pipe at N4 nozzle and hanger FDR-2497-11 on FDR-FU-19 tank was found missing. . See EDMS for picture <I> **** Actions Taken **** Notified engineering, planning, MCR and initiated CR | 02-00-FDR-FU-19
388739 | CR | 20190110 |  | 4 | Coffee Spill on Security X-Ray Machine | N | N |  | N | NO | <D> **** Detailed Description **** On 1/10/2019 a sizeable amount of coffee was spilled inside one of the x-ray machines at the PAAP. The owner of the coffee is unknown since the spill occurred inside the machine and wasn't visible externally until a short time later. <I> **** Actions Taken **** Security Supervision was notified and the unit was powered off. I&C was notified regarding the spill and potential damage to the x-ray machine. CR was generated. <N> **** Equipment Description **** SEC-XR-4 located in the PAAP
388740 | CR | 20190110 |  | 3 | Field Team Respirator Availability |  |  |  | N | NO | <D> **** Detailed Description **** Need to evaluate current ERO stance on Field Team members not having respirators readily available. ISPM-17 Section 3.3.1 states â€œIn an emergency situation, a positive -pressure self-contained breathing apparatus (SCBA) SHALL BE ISSUED to persons requiring entry into the hazardous atmosphere.â€ In emergency situations, the Field Teams are sent into locations with potential airborne contamination to perform air samples outside the vehicle. Recommend benchmarking other sites on their practices to ensure adequate safety measures are in place to protect the Field Team members. <I> **** Actions Taken **** Discussed with Supervisor and intiated CR. <N> Issue was discussed with the originator on 3-11-19. Action is complete. CR Forrester 3-11-19
388741 | CR | 20190110 |  | 3 | ABN-Earthquake enhancements identified |  |  |  | N | NO | <D> **** Detailed Description **** During training on the new seismic monitoring system an enhancement to the new revision of ABN-EARTHQUAKE was identified. Step 4.4 uses the System activity RB422', RW437', or Free Field lighst as inditication. This step should say Seismic Activity (Red or Yellow) Lights for these locations are illuminated. Also, the procedure does not relate which motion recorder (MR1-6) corresponds with which location. An enhancement could be made which informs the operators which location corresponds with which motion recorder. The installed equipment has the motion recorders listed by location not MR number. Bases Step 4.4 does provide this information for MR1 and MR4.
388743 | CR | 20190110 |  | 4 | B107-Observed Cooking Practice That Violates ISPM-10 |  |  |  | N | NO | <D> **** Detailed Description **** Fire Marshal inspection of Building 107 today found employees cooking backon on the stove top. This is a direct violation of ISPM-10 which prohibits open frying of foods that produce grease vapors. This building is occupied by Org Code 52622. There is a sign adjacent to the stove that states the ISPM-10 requirement that open frying that cooking practices that produce grease laden vapors shall not be used on this equipment. All employees in the area were coached on the requirement. The cooking practice was halted immediately. Discussions with the personnel indicated that a breakfast was prepared at regular intervals at this location, like every friday or perhaps prior to long change. My attention was drawn to this activity in part because both exterior doors were propped open and the grease vapors were easily detected. <I> **** Actions Taken **** Coached the employees in the area on ISPM-10 cooking requirements. Open frying was immediatelj stopped.
388744 | CR | 20190110 | CAQ | D | CSP-INST-H201 Chem Shift Check missing Reviewer Signature | N | N |  | N | NO | <D> **** Detailed Description **** Missing Assigned Reviewer Signature on Chemistry Shift Cannel Check turned into Records for processing. <I> **** Actions Taken **** Identified missing signature, notified supervisor, wrote CR and returned to Chemistry.
388745 | CR | 20190110 | CAQ | D | ISP-APRM-B301 As Found OPRM values not correct. | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of ISP-APRM-B301 ( WO# 0209571901) OPRM parameters in table 7.12b did not match newly revised values. <I> **** Actions Taken **** Corrected values per procedure.
388746 | CR | 20190110 | CAQ | C | Fuses are installed not per E555 | N | N |  | N | NO | <D> **** Detailed Description **** E555 documents are Top Tier listings of all the fuses installed in the plant. E555-E-CP-H13/P823 lists fuses E-FUSE-H13P823/BBF3 and E-FUSE-H13P823/BBF4 and E -FUSE-H13P823/FBL1F3 as being spared. In fact there are fuses installed in these fuse slots.
388747 | CR | 20190110 |  | 3 | Potential degradation of HD-LS-1CHT | N | N |  | N | YES | <D> **** Detailed Description **** Recent CRs have been initiated for COND-HX-1C high and low level switches, HD-LS-1CH and HD-LS-1CL. Degradation of these level switches is likely caused by steam and condensation from a large leak downstream of BS-V-54B. HD-LS-1CHT may also be degraded and has more significant consequences upon failure. Recommend replacement of level switch HD-LS-1CHT at first opportunity or bypassing of the trip function via jumper installation. <I> **** Actions Taken **** Discussed with supervisor. <N> **** Equipment Description **** T 477' B2/12.0 (Heater Bay north side of condenser) | 02-00-HD-LS-1CHT
388748 | CR | 20190110 |  | 4 | Turnstile At The AAP Is Out Of Service | N | N |  | N | NO | <D> **** Detailed Description **** One of the two RWP turnstiles at the AAP RCA entrance is out of service due to what seems like a computer malfunction. <I> **** Actions Taken **** Placed turnstile OOS, Contacted RP Supervision and RAD Support and initiated WR. <N> **** Equipment Description **** AAP RCA Entrance
388749 | CR | 20190110 | CAQ | D | SW-V-790B Packing leak | Y | N |  | N | YES | <D> **** Detailed Description **** There is a small (3-5 drop per minute) leak from the packing of SW-V-790B this is the root valve for SW-FIS-41 which measures flow to RRA-CC-12. Scaffold or ladder will be required to reach this valve. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** Rx 471 NW above the airlock doors | 02-00-SW-V-790B
388750 | CR | 20190110 |  | 4 | Generator Condition Monitor out of paper | N | N |  | N | YES | <D> **** Detailed Description **** Generator Condition Monitor, TG-ID-1, is out of paper. Request paper roll changeout. <I> **** Actions Taken **** Informed CRS. Wrote CR. | 02-00-TG-ID-1
388751 | CR | 20190111 |  | 3 | Dataglance issue approving WO to work |  |  |  | N | NO | <D> **** Detailed Description **** Craft supervisor unable to take support task 0212973902 SP (ELEC) SUPPORT OSP-ELEC-W102 to approved in Dataglance. WO doesnâ€™t have any holds and everything is grayed out to move forward. This is a weekly surveillance and the craft supervisor should be able to take it to approved. <I> **** Actions Taken **** Contacted CRS to see if they could approve WO unsuccessfully, checked PortalJ for holds wrote this CR. <N> Supervisor did not have the ability to authorize the pacakage due to Operations authorization required. The package was completed successfully.
388756 | CR | 20190111 | CAQ | C | CVI OMM 358-00,1,22 in Asset Suite is not the same manual |  |  |  | N | NO | <D> **** Detailed Description **** While an I&C instructor was doing research for IC000760 Bailey Summer training it was discovered that the CVI OMM 358-00,1,22 in Asset Suite is not the same manual that is in stores for the Signal Limiter Type 746 Cards Cat ID# 0063900704. The instructions in the CVI are used in PPI PPM 10.24.124 PM CAL/TEST - BAILEY MODEL 746 SIGNAL LIMITER changes to the PPI PPM may need to be made to reflect what is currently installed in the plant. Contacted SGT system engineer and recommend assign CR to SGT system engineer for further investigation. <I> **** Actions Taken **** Contacted Supervisor and SGT system engineer
388757 | CR | 20190111 |  | 3 | EC MALT 13970 not being tracked due to administrative errors | N | N |  | N | YES | <D> **** Detailed Description **** Minor Alteration EC MALT 13970 (INSTALLATION OF ENTRY/EXIT CARDREADER DOOR AAP12) was prepared by AR-COMPENG and approved/issued through AR-MODS on 08/11/18. Prior to completion of the associated MALT assignment under AR EVAL 266066, the AR-COMPENG Responsible Engineer failed to initiate an ENG assignment under AR EVAL 266066 per DES-2-10 (then rev 32 mnr rev 3) step 5.3.8 e for implementation tracking and closeout of the modification. In part because this ENG assignment had not been created per process, AR EVAL 266066 was subsequently inappropriately advanced to COMPLETE status on 08/16/18 by AR-COMPENG. These administrative errors left EC MALT 13970 without the intended Asset Suite vehicle for tracking, implementation support, or to drive completion of actions for turnover or closeout. It appears that EC MALT 13970 implementation is currently in-progress under WO 02103750. At this time, WOT 02103750-01 (IMPLEMENT EC 13970 - CARD READERS ON DOOR PAAP12) and WOT 02103750-13 (CABLE TERMINATIONS / WPS ELEC) are FINISHED but WOT 02103750-07 (I&C PERFORM TERMINATION PER EC 13970) and WOT 02103750-14 (I&C PERFORM PROBABILITY TESTING ON HAND GEOMETRY 10.28.52) remain at APPROVED status and WOT 02103750-03 (PMT-SECURITY DOOR TEST OF CARD READER) remains at READY status. Suggest resolution assignment to AR-COMPENG. If possible, AR EVAL 266066 should be re-opened for addition of the DES-2-10 process directed ENG assignement for the AR-COMPENG Responsible Engineer. | 02-00-AAP-DOOR-AAP12
388758 | CR | 20190111 |  | 3 | Directory label in new elevator to prevent defacing. |  |  |  | N | YES | <D> **** Detailed Description **** Prior to installation of the new MT-ELEV-4 (RW) Sharpie marker had been used on the surfaces of the elevator to indicate services on each floor ( ie. toolcrib-467). Having some form of labeling inside the new elevator may preclude this activity during the outage. | 02-00-MT-ELEV-4
388759 | CR | 20190111 |  | 4 | GOA-FN-1 expansion joint | N | N |  | N | YES | <D> **** Detailed Description **** Expansion joint on upstream side of GOA-FN-1 was found ripped on the bottom 1/3 of the DUct work. See pictures attached in EDMS. <I> **** Actions Taken **** Notified supervision and initiated this CR <N> **** Equipment Description **** G428 D4/2.4 | 02-00-GOA-FN-1
388760 | CR | 20190111 |  |  | Created in error. |  |  |  | N | NO | <D> **** Detailed Description **** . . . . .
388763 | CR | 20190111 | CAQ | D | MW 67 XTMR JB TAMPER | N | N |  | N | YES | <D> **** Detailed Description **** MW 67 XTMR JB TAMPER went into to alarm multiple times and eventually was stuck in alarm. <I> **** Actions Taken **** Comped the MW 67, contacted plant electricians and genertated CR/WR | 02-00-SEC-MW-ISFSI/67AR
388764 | CR | 20190111 | CAQ | D | Low pressure CRD-HCU-2211 | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-2211. Low pressure 980#. <I> **** Actions Taken **** Followed ARP to repressurize. | 02-00-CRD-HCU-2211
388765 | CR | 20190111 | CAQ | D | ENS Line is Down | N | Y |  | N | YES | <D> **** Detailed Description **** On 01/11/2019 the ENS phone in the control room began spuriously ringing, then continuously ringing, then failed to have a dial tone. <I> **** Actions Taken **** The NRC Operations Center was contacted on the main line telephone. The NRC also contacted the control room via the commercial telephone line. Additionally, cell phones and satellite phones remian available. As such, this condition is not reportable as a major loss of offiste communications capability per PPM 1.10.1 Attachment 7.5. <N> **** Equipment Description **** ENS phone line
388766 | CR | 20190111 | CAQ | C | Portal J MEL discrepancies for EDR-SUMP-R5 discharge EPNs | N | N |  | N | YES | <D> **** Detailed Description **** FSAR Figure AED MEC M537 Note 1 indicates that EDR-SUMP-R5 discharge EPNs (e.g., EDR-P-5A(B), EDR-V-24A(B), EDR-V-23A(B), EDR-V-21, EDR-AO-21, EDR-V-22, and EDR-AO-22) should be designated as Quality Class II+ and Seismic Category 1M (Augmented Quality). Asset Suite/Portal J MEL contrarily indicates these EPNs are Safety Class NSR (should be AQ), Seismic 2 (should be 1M), and Quality Group 2 (should be A). This is a legacy administrative issue only (no effect upon continued SSC functionality, operation, or qualification) - just need to correct Asset Suite/Portal J MEL. These SSCs are evaluated for the applicable Augment Quality Seismic Category 1M requirements - reference existing AQ SC 1M pipe stress analysis AED CAL 8.42.0167. Suggest that this legacy discrepancy (noted while screening AR EVAL 388761 for modification type) be resolved by Design Engineering O&M Mechanical group. | 02-00-EDR-AO-21,02-00-EDR-AO-22,02-00-EDR-P-5A,02-00-EDR-P-5B,02-00-EDR-V-21,02-00-EDR-V-22,02-00-EDR-V-23A,02-00-EDR-V-23B,02-00-EDR-V-24A,02-00-EDR-V-24B
388767 | CR | 20190111 |  | 3 | Possibly obsolete operator round in eSOMS |  |  |  | N | NO | <D> **** Detailed Description **** Cumulative time in suppression pool cooling is tracked using the CRO1 operator rounds. This was used to verify compliance with an assumption made in a past operability assessment that RHR remains Operable in suppression pool cooling mode due to the low probability of a LOOP/LOCA while in suppression pool cooling. We now declare RHR inoperable any time it is in suppression pool cooling or test return so the reading should be deleted. <I> **** Actions Taken **** None.
388768 | CR | 20190111 | CAQ | C | More FLEX components are not qualified for temperatures | N | Y |  | N | YES | <D> **** Detailed Description **** It has been determined that there are more FLEX components that are not qualified for the site extreme temperatures of -27Â°F to +115Â°F based on the extent of condition review. The lay flat hoses (FLEX-ASM-DISCHARGE/D01, DISCHARGE/D02, DISCHARGE/GAS1 and DISCHARGE/GAS2) used on the discharge of the fuel pumps during refuel activities have a lower design limit of -20Â°F. The rigid hoses (FLEX-ASM -SUCTION/D03, SUCTION /D04, SUCTION/GAS1 and SUCTION/GAS2) used on the suction of the fuel pumps during refuel activities have a lower design limit of -20Â°F. The knife valves that are integral to the 6â€ PVC suction wyes (FLEX -ASM-SUCTION/B5B-WYE and FLEX-ASM-SUCTION/HHP-WYE) that are installed on the FLEX water supply pumps have a lower design limit of 32Â°F. No other FLEX components related to the fuel or water addition have been found to be unqualified in this current review . . The suction and discharge hoses remain capable of performing their FLEX design function since the outside ambient temperatures have not been less than -20Â°F and are not forecasted to be less than their design limit. New suction and discharge fuel equipment have been identified and will replace the existing equipment within the next month. Temperatures are forecasted to remain well above -20F in that timeframe. . The 6â€ PVC suction wyes with integral knife valves which are used at the pump suction are not functional for outside ambient temperatures less 32Â°F. These wyes and integral knife valves allow for the online swapping of suction strainers should either suction strainer become fouled while installed in the spray pond. The long-term forecast shows that the daily low over the next 60 days is 25Â°F which means that these components cannot be relied upon to perform their function even though there is reasonable expectation that it would function according to the vendor. The fence that surrounds the ponds helps to minimize the potential for introduction of debris into the ponds. The Ops 4 Equipment Operator inspects the Service Water Ponds each shift for any debris which reduces the likelihood of debris. Form 27156 Ops 4 Log instructs, when possible, to remove any debris using the staged reach rods. If unable to reach the debris with the reach rod, then initiate a Work Request to have CMS remove the debris. Since the debris could go undetected or could get blown into the pond between EO inspections, it is conservative to call the suction hose nonfunctional for both FLEX water addition capabilities (FLEX-P-1 and B5B-P-1) as these wyes are common to both suction configurations. According to LCS 1.11.1 states that if both water addition capabilities for the SFP inoperable, action must be taken to initiate actions to restore one of the inoperable capabilities to OPERABLE within 24 hours and to implement compensatory measures to restore an equivalent to the inoperable capability for the water addition capability to the Spent Fuel Pool (SFP) within 72 hours. . New brass wyes with integral ball valves that can be attached directly to the suction of the pumps and are qualified for the site extreme temperatures have been identified and ordered. These valves will take approximately 6 weeks to arrive at CGS. Compensatory actions of specifying an interim suction configuration excluding the use of uninterrupted swapping of the suction strainers has been saved to the EDMS of the CR. These actions include the additional instructions required to swap suction strainers while momentarily taking the pump offline to install a redundant strainer that has been staged in the immediate vicinity next to the pond. These actions will make both water addition capabilities operable. . In the CGS FLEX MAAP analysis, SFP makeup and subsequent flow to the Suppression Pool start 12 hours after loss of power. MAAP Case 3 (our design limit case) has been run with a 30 minute interruption (stoppage) in flow from 14 to 14.5 hours after loss of power. This results in a maximum Suppression Pool temperature of 239.95 Â°F. Since that meets the 240 Â°F limit established for reliable RCIC operation, a 30 minute interruption during cold weather would be acceptable to change suction strainers. . These results include the assumption that the spray pond water being pumped into the SFP is 60 Â°F. In our vent design case we used 81 Â°F. It is quite conservative to assume the Spray Pond water is 60 Â°F with the cool winter conditions we are experiencing. Using the instructions in the compensatory action the compensatory action the suction strainer could be replaced and flow could be re-established within five minutes. <I> **** Actions Taken **** Discussed with Supervisor. Discussed with HCV project team. <N> **** Equipment Description **** Buildings 82 and 600 | 02-CM-FLEX-ASM-SUCTION/B5B-WYE,02-CM-FLEX-ASM-SUCTION/HHP-WYE
388769 | CR | 20190111 |  | 4 | W-DOOR-C208 - door hangs up and upper hinge needs tightened | N | N |  | N | YES | <D> **** Detailed Description **** When closing, W-DOOR-C208 sometimes hangs up before fully latching. The fasteners for the upper hinge are visibly loose. Please check and tighten any/all loose hinge fasteners and lubricate the latch mechanism for this W467' door. <I> This is not an essential fire door. | 02-00-W-DOOR-C208
388770 | CR | 20190111 | CAQ | D | CRD-HCU-1807 accumulator trouble high water. | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-1807 was due to high water level. <I> **** Actions Taken **** ARP | 02-00-CRD-HCU-1807
388771 | CR | 20190111 |  | 3 | Contamination Detected while loading Open Top Liner |  |  |  | N | NO | <D> **** Detailed Description **** On January 11th 2019, while loading radioactive material into an open top liner on RW 437, loose contamination was detected in the work area. <I> **** Actions Taken **** Work activity was stopped. Controlled and posted the area as a contaminated area. The area was also posted as a high radiation area due to dose rate on the open top liner. There were no personnel contaminations. Notified the Shift Manager and Radiation Protection Manager.
388772 | CR | 20190111 | CAQ | D | CRD-HCU-5819 | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-5819 was due to high water level. <I> **** Actions Taken **** ARP | 02-00-CRD-HCU-5819
388773 | CR | 20190111 |  | 3 | Issues logging into eSOMS application |  |  |  | N | NO | <D> **** Detailed Description **** After upgrading the eSOMS application to version 6.03, many users reported having issues logging into eSOMS. <I> **** Actions Taken **** Opened a critical case with the vendor (ABB). Issue was resolved and the application was put back into normal service.
388774 | CR | 20190112 |  | 3 | Procedure enhancement to SOP-LO-FILL |  |  |  | N | YES | <D> **** Detailed Description **** Request to add a step in sections 5.2, 5.3, 5.4 at the end to document the oil addition per OI-11. See EDMS, pages 17, 21, 25, changes in RED. <N> **** Equipment Description **** SOP-LO-FILL
388775 | CR | 20190112 | CAQ | D | MW 67 JBT | N | N |  | N | YES | <D> **** Detailed Description **** High alarm rate on MW 67 Junction Box tamper transmitter. <I> **** Actions Taken **** Compensatory Measure put in place. <N> **** Equipment Description **** MW 67TJBT XMTR JB Tamper | 02-00-SEC-MW-ISFSI/67AT
388776 | CR | 20190112 | CAQ | D | MW 67 JB tamper | N | N |  | N | YES | <D> **** Detailed Description **** High alarm rate on MW 67 JB tamper <I> **** Actions Taken **** Compensatory Measure put in place. CR/WR generated. <N> **** Equipment Description **** MW 67T JBT XMTR JB Tamper | 02-00-SEC-MW-ISFSI/67AT
388779 | CR | 20190112 |  | 4 | COND-HX-1C level alarms are not working properly. | N | N |  | N | YES | <D> **** Detailed Description **** When removing COND-HX-1C from service per SOP-FWH-SHUTDOWN to support reactor downpower on 1-12-19, the level alarms did not work properly. Prior to removing COND-HX-1C from service, the LP HEATER 1C LEVEL HIGH alarm, from HD-LS-1CH, was locked in with normal heater level. This was previously documented by WR 29146443. When removing COND -HX-1C from service, LP HEATER 1C LEVEL HIGH alarm did not clear, nor did LP HEATER 1C LEVEL LOW alarm come in as expected. This alarm comes from HD-LS-1CL, which was previously documented as being locked in with normal heater level per WR 29146128. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR's. | 02-00-HD-LS-1CH,02-00-HD-LS-1CL
388780 | CR | 20190112 |  | 4 | STM DUMP VLVS NOT FULL CLOSED alarm did not come in. | N | N |  | N | YES | <D> **** Detailed Description **** When removing COND-HX-1A/1B/1C from service to support reactor downpower on 1-12-19, the STM DUMP VLVS NOT FULL CLOSED alarm, P840.A2.9-6, did not come in. This alarm should have come in when BS-DV-1A was opened. BS-DV-1A was the first dump valve to be opened. This alarm should come in when a single dump valve is not full closed. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR; with CRS permission removed alarm card and rubbed an eraser on the card contacts, but condition didn't change. | 02-00-ANN-ANN-A/A2
388781 | CR | 20190112 |  | 4 | E-AY-TR/M3 has a caution light lit. | N | N |  | N | YES | <D> **** Detailed Description **** E-AY-TR/M3 has a caution light lit. scrolling thru last sample gases were; ethylene 4.8 ppm, acetylene 0.6 ppm, TDCG 637.9 PPM, water 2.0ppm, carbon monoxide 485.6 ppm, carbon dioxide 3907.2 -, oxygen 828.8 ppm. Plant was in the process of down powering. <I> **** Actions Taken **** WR,CR Informed Infield supervisor. | 02-00-E-AY-TR/M3
388782 | CR | 20190112 | CAQ | C | RHR A discharge pressure high and is rising. | Y | Y |  | N | YES | <D> **** Detailed Description **** RHR A discharge pressure high and is rising. RHR-PI-612A denotes 450 psig and trend is rising. Potential to affect the operability of RHR-P-2A. Alarm at GE 455 psig <I> **** Actions Taken **** Notified CRS and SM. RHR A, SPC and Containment Sprays TS Operabilities. RHR HX vent valves are degraded. | 02-00-RHR-P-2A
388783 | CR | 20190112 |  | 4 | SS-PCV-39 WO# 02130432-01 | N | N |  | N | YES | <D> **** Detailed Description **** WO# 02130432-01 instructs repair to SS-PCV-39; during the field inspection technicians found positioner leaking beyond repair. <I> **** Actions Taken **** Informed operations, initiate cr, returned package to planning for instructions on replacement in the future, uploaded video and pictures to the S: drive I/C folder for SS-PCV-39. | 02-00-SS-PCV-39
388785 | CR | 20190112 | CAQ | D | MW 67 JB Tamper | N | N |  | N | YES | <D> **** Detailed Description **** Not operating as intended <I> **** Actions Taken **** Comp put is place. WR CR generated | 02-00-SEC-MW-ISFSI/67AT
388786 | CR | 20190113 |  | 4 | Poor Lighting in the Vital Island | N | N |  | N | YES | <D> **** Detailed Description **** Poor Lighting in the vestibule area just outside the Remote Shutdown Room. When you enter the Vital Island from the RW Stairwell entrance and you walk into the vestibule area right outside the Remote Shutdown Room, there is a light fixture that needs the fluorescent tubes changed out to increase visibility. <I> **** Actions Taken **** CR/WR written. Supervision Notified This is non-essential lighting. The lamps have been changed. WR cancelled. <N> **** Equipment Description **** Vital Island Lighting
388787 | CR | 20190113 |  | 4 | Tie Back on Scaffolding loose | N | N |  | N | YES | <D> **** Detailed Description **** While walking throught the Vital Island with a supervisor, we noticed that a tie back attached to an erected scaffold beweet the remote shutdown room and SM-8 was loose. It was obvious due to the fact that the scaffold pole used is to short and not up against the wall in a perpendicular manner. The tie back does not meet requirements in 10.2.53. <I> **** Actions Taken **** CR/WR written Supervision Notified . The scaffold in question is in the hallway between the SM-7 and SM-8 rooms. The scaffold is situated several feet from any vertical walls. It is rigidly clamped to support steel for electrical cable tray supports, per PPM 10.2.53 Step 7.4.3.h. The RSD, SM-7 and SM-8 rooms are adequately protected from any motion of this scaffold. <N> **** Equipment Description **** Tie Back on Scaffolding loose in vital island | 02-00-W-BLDG-MISC
388788 | CR | 20190113 | CAQ | D | Door C-408 is not functioning as intended. | Y | Y |  | N | YES | <D> **** Detailed Description **** Door C-408 is not functioning as intended. Call 2185 for details. <I> **** Actions Taken **** Posted compensatory measures. Notified Electrical Maintenance. Notified S/M. Generated CR/WR. This is security issue only and the barrier function of the door is not impacted. <N> **** Equipment Description **** Control Room Door | 02-00-W-DOOR-C408
388789 | CR | 20190113 | CAQ | C | Fluctuating amps on E-C1-7 | Y | N |  | N | YES | <D> **** Detailed Description **** E-C1-7 amps in the Control room fluctuate between 32 and 42 amps during power ascention as indicated in the control room and locally. The oscillations reduced to 4 amp swings when closer to full power. The data point for it (X274) plotted against Feed Turbine RPMs indicate the oscillations are related. A look at previous downpowers shows the same kind of response. See the EDMS file for an eDNA trend profile. <I> **** Actions Taken **** Investigated feed turbines locally. Nothing found of note. <N> **** Equipment Description **** RW 467 | 02-00-E-C1-7
388794 | CR | 20190113 |  | 4 | Received momentary BUS 61/62 MCC OL TRIP alarm. | N | N |  | N | YES | <D> **** Detailed Description **** Received momentary BUS 61/62 MCC OL TRIP alarm - H13-P800 .C2 drop 6-6. The alarm was in for approximately 0.5 seconds and then cleared. Process computer point E681 [SL -61 CKT BKR TO MC-6M OL TRIP] displayed tripped and then normal. Local investigation at SL-61 and the CWPH / electrical buildings revealed all SL-61 circuit breakers were closed with associated loads in service. No known equipment manipulations or evolutions were in progress at the time of the alarm <I> **** Actions Taken **** Notified the CRS. This is similar to CR 388441 for MC-6N on 2 JAN 19. | 02-00-E-CB-61/6M
388795 | CR | 20190113 | CAQ | D | Blue dot light fixture out in RB 422 NE stairwell | N | N |  | N | YES | <D> **** Detailed Description **** The light fixture in the RB 422 NE stairwell (RCIC and RHR A vestibule) is failing. Please replace. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RB 422 NE stairwell
388796 | CR | 20190113 |  | 4 | Light in IR22/P027 room is out | N | N |  | N | YES | <D> **** Detailed Description **** The light fixture in the IR22/P027 room is out. Please replace. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RB 522 IR22/P027 room.
388797 | CR | 20190113 |  | 4 | Lighting replacement need in RHR-P-2C room | N | N |  | N | YES | <D> **** Detailed Description **** Several lights are out in the RHR-P-2C room and need to be relamped. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RB 422 RHR-P-2C room.
388798 | CR | 20190113 | CAQ | D | OPS Fire brigade truck service indication | N | Y |  | N | YES | <D> **** Detailed Description **** OPS Fire brigade F-250 tag 92975C display indicates the engine oil should be changed, most likely based on elapsed time since last service rather than mileage, as it's still almost 3000 miles from due per sticker. Recommend evaluate whether oil change periodicity can be extended to 12months to minimize disposal of practically brand new oil, and either reset oil life in onboard computer, or perform oil change. Factory recommended interval is 12 months or 7500 miles using SAE 5W20. Removing this truck from service for maintenance requires an entry into LCS 1.10.4 and compensatory actions; performing excess maintenance requires entry into this spec more frequently than may be necessary. <I> **** Actions Taken **** Discussed with CRS, generated AR/WR. <N> **** Equipment Description **** OPS Fire Brigade truck 2010 Ford F-250 single cab, standard bed, 2wd, gas V8, white, tag 92975C
388799 | CR | 20190113 |  | 4 | CAS-AR-1A will not stop â€œdrainingâ€ when isolated | N | N |  | N | YES | <D> **** Detailed Description **** While isolating and tagging out CAS-AR-1A for maintenance, it is evident CAS-V-102A and/or CAS-V-126A are leaking past seat when both valves are closed due to air is still slightly coming out of the receiver via drain valve CAS-V -122A, which is open. When isolating the receiver, CAS-V -102A operated just fine; CAS-V-126A sounded â€œgrittyâ€ when closing the valve. <I> **** Actions Taken **** informed Shift Supervision | 02-00-CAS-AR-1A
388800 | CR | 20190113 | CAQ | D | Reports of phantom crash calls to Washington State | N | Y |  | N | YES | <D> **** Detailed Description **** The SCC received reports that the ENW Main Control Room CRASH line has made several phantom calls to the Washington State Emergence Management Center. All attempted return calls were met with a busy signal. <I> **** Actions Taken **** Informed the Shift Manager the SCC. Contacted the EP organization to investigate this matter further. Made an entry into the Operations log. <N> **** Equipment Description **** ENW Crash line
388801 | CR | 20190114 |  | 4 | Yakima Building kitchen floor drain does not drain properly | N | N |  | N | NO | <D> **** Detailed Description **** The floor drain in the Yakima Building kitchen, which is located behind the ice machine, needs to be â€œsnaked-outâ€ because it does not drain properly. When both sink faucets are on and both sinks are draining, the floor drain will overflow and make a large, dirty water puddle mess on the kitchen floor. This is a very unsanitary condition to have occurring all the time in a kitchen where employees are dinning in. Please schedule the Facilities Dept to repair this drain so it will perform its function properly. <N> **** Equipment Description **** Yakima Building kitchen floor drainYakima Building kitchen
388804 | CR | 20190114 |  | 4 | New Hot Spot (HS-90) detected during RW 437' Monthly Survey | N | N |  | N | NO | <D> **** Detailed Description **** A new Hot Spot was detected while performing the RW 437' Monthly Routine Survey. The Hot Spot is located on the EDR-TK-5 Waste Surge Tank Drain. The dose rate on HS-90, taken with a Victoreen (Ion Chamber) is *200 mRem/hr contact, 30 mRem/hr @ 30 cm. The nearest Radiation Area boundary is 2.0 mRem/hr. <I> **** Actions Taken **** -Created HS-90 in the Hot Spot Log. -Notified Supervision <N> **** Equipment Description **** EDR-TK-5 Waste Surge Tank Drain Boundaries have been verified. Current postings are adequate. No further action required.
388814 | CR | 20190114 |  | 3 | Cathodic protection system doesn't meet criteria | N | N |  | N | YES | <D> **** Detailed Description **** Upon completion of the annual pipe to soil readings of the Cathodic protection system, only 9 of the 71 test points meet the criteria of -850 mvDC. W.O.#02109484-01 <I> **** Actions Taken **** Notified supervision, notified engineering | 02-00-CP-RECT-3,02-00-CP-RECT-5,02-00-CP-RECT-9,02-00-CP-RECT-DW1/A/B,02-00-CP-RECT-DW2,02-00-CP-RECT-DW3,02-00-CP-RECT-DW4,02-00-CP-RECT-DW5
388815 | CR | 20190114 |  | 4 | Security explosive detector XD 5 compressor warning | N | N |  | N | YES | <D> **** Detailed Description **** Security XD 5 explosive detector in the PAAP initiated a compressor warning and needs maintenance. Equipment is not operating by design. <I> **** Actions Taken **** CR/WR generated. Security supervision notified. Equipment taken out of service. | 02-00-SEC-XD-5
388816 | CR | 20190114 | CAQ | C | Box 17034 D-100 sent to the state, potential Appendix B Gap |  |  |  | N | NO | <D> **** Detailed Description **** While searching for soil velocity profiles in support of the seismic PRA a potential gap in 10 CFR 50 Appendix B Quality Assurance Criteria for Nuclear Power Plants, Criterions IV. Procurement Document Control and VI. Document Control requirements was identified. The FSAR and other data uses the summary (averaged) values of the bore hole samples from a Shannon and Wilson (S&W) report. The S&W report was identified as doing the soils report; however, they subcontracted out to Weston Geophysical Engineers to do the actual data collection. The Weston Geophysical Engineers reports was found in Box 17034 D-100. This box has not been processed by Records. Engineering needs to review the box to identify any gaps in the Appendix B program and properly submit the applicable records. Recommend C to AR-DMC. <I> **** Actions Taken **** initiated CR
388817 | CR | 20190114 |  | 4 | Cathodic Protection test stations degraded | N | N |  | N | YES | <D> **** Detailed Description **** Cathodic protection test stations CP-RECT-10 test stations #3 and #4 were found with approximately 2 inches of water in the inner termination box. The 2 test stations along the east edge of the GSB (CP-RECT-6/3 test station #6) and an unidentified test station further south have inner termination boxes with the lids rusted through. See attached pictures. <I> **** Actions Taken **** Notified supervision, removed water from test stations <N> **** Equipment Description **** CP-RECT-10 TS #3 east edge of spray pond 1B CP-RECT-10 TS #4 South side of SWPH 1A CP-RECT-6/3 TS #6 east edge of GSB north of dbl doors Unidentifed TS east edge of GSB north of Single door
388821 | CR | 20190114 |  | 3 | PPM 5.5.5 requires new keys currently not staged. |  |  |  | N | YES | <D> **** Detailed Description **** PPM 5.5.5, Overriding RCIC Isolation and Trip Signals, requires two new keys that currently not staged. New Revision of PPM 5.5.5 is Rev. 008. In Section 2.0, Required Equipment now includes the following keys: 117/2-632 and 127/2-642. Please make these new keys and place them in the MCR EOP Cabinet. <I> **** Actions Taken **** CRS, SM and OPS Procedure Writers Group notified. Keys have been moved from PPM 5.6.2 to PPM 5.5.5, CR can be closed or cancelled thanks Steve Stead | 02-00-LD-RMS-S02A,02-00-LD-RMS-S02B
388822 | CR | 20190114 |  | 4 | PPM 10.4.5 needs procudure revision. |  |  |  | N | NO | <D> **** Detailed Description **** Mt-CRA-1 is in the process of being upgraded by the crane vendor. New componenets are being installed as a result of the upgrade. This affects both the mechanical and electrical maintenance scope of the PM. PPM 10.4.5 needs a revision to the procedure in order to perform work order 02127521 (MT-CRA-1 INSPECT MAINTAIN & TEST (CRHOI-1-1 -12.1). <I> **** Actions Taken **** Generated CR to document the need to revise PPM 10.4.5. Informed Mechanical and Electrical Component Managers, and acting Maintenance Services Manager. <N> Procedure revision is being tracked under AR-370262-19. No further actions required under this AR.
388826 | CR | 20190114 |  | 3 | Incomplete information on MOT Document |  |  |  | N | NO | <D> **** Detailed Description **** On 01/09/19 Eng. Technical Services (org.54122) submitted doument MOT-AOV-1-1 for processing to Document Control. Document Control is unable to process document due to information within the document being cut off. <I> **** Actions Taken **** CR initiated, MOT was returned for corrections.
388827 | CR | 20190114 |  | 3 | E-PP-7BC panel schedule incorrect | N | N |  | N | YES | <D> **** Detailed Description **** The "panel schedule" currently attached to E-PP-7BC (RX 522') is incorrect. A older laminated copy of Attachment 7.6 from SOP-ELEC-AC-LU is attached, which shows five circuits used for the old Stack Monitor equipment (now spared). These circuits show as spares in the current procedure. The panel schedule needs to be updated to match the current procedure. <I> **** Actions Taken **** Discussed with FIN Team and wrote CR | 02-00-E-PP-7BC
388829 | CR | 20190114 |  | 4 | PWR-CRA-2 | N | N |  | N | YES | <D> PWR-CRA-2 crane in the 437' RW truck bay stop working. Trolley will not travel East/West, up or down or North/Southall movement stopped.None of the controls would work. <I> Wrote Condition Report and generated work request. <N> (PWR-CRA-2) 437' RW processing area truck bay crane. | 02-00-PWR-CRA-2
388832 | CR | 20190114 | CAQ | C | Lost many indications on TDAS, including CTP. | Y | N |  | N | YES | <D> **** Detailed Description **** Lost many indications on TDAS, including CTP. Entered ABN -COMPUTER after 15 minutes. Designated PPC as primary computer. Core Thermal Power indication restored. Exited ABN-COMPUTER. <I> **** Actions Taken **** Wrote this CR and WR. | 02-00-TDAS-COMP-8715
388833 | CR | 20190114 |  | 3 | Unexpected Software version mismatch |  |  |  | N | NO | <D> **** Detailed Description **** During the AW Radio Project at Rattlesnake Mountain, while trying to validate the Site Controller configuration files remotely, the remote system would not download the file due to software mismatch. Version PSC R07.D8.033 V3 was the furthest back the vendor supported for the software, and the remote equipment expected to download Version PSC R07 .B8.018 V3. <I> **** Actions Taken **** Stopped and notified IS Supervisor, IS Cyber Manager & IS Assistant Manager of software mismatch when remotely downloading the Site Controller configuration file. Waited for instruction <N> **** Equipment Description **** 02-COMM-SOFT-RPTR1 REPEATER SITE CONTROLLER
388834 | CR | 20190114 |  | 3 | Late eSOMS entries for Maintenance |  |  |  | N | NO | <C> At the direction of OFM â€“ CR 388834 changed from 4/Trend to 3 and assigned to AR-MECSHOP (1/17/2019) <D> **** Detailed Description **** 2 Painters worked on days when they had PT scheduled, and the night shift supervisor worked on the New Years holiday without having time entered in eSOMS. No violations occured when eSOMS was updated. <I> **** Actions Taken **** Updated eSOMS with correct hours.
388835 | CR | 20190114 |  | 3 | Fire Brigade keys for new Radwaste Elevator MT-ELEV-4 | N | N |  | N | YES | <D> **** Detailed Description **** Due to the replacement of the Radwaste Elevator, MT-ELEV-4, the Fire Brigade no longer has a key that will operate this elevator. A new elevator key needs to be distrubuted to all EOs currently on the Fire Brigade and should be included with the initial set of EO keys given to new EOs in the future. Having elevator keys can greatly reduce response times of the Fire Brigade when responding to fires or medical emergencies. <I> **** Actions Taken **** Initiated this CR and informed Ops management. | 02-00-MT-ELEV-4
388840 | CR | 20190114 |  | 4 | NET4-COMP-EPO hung on logout | N | N |  | N | YES | <D> **** Detailed Description **** NET4-COMP-EPO is hung on logout for multiple accounts. To restore login capabilities the system will need to be rebooted. AR-Eval 376954 reviews a permanent fix. Services on this devices are still functioning normally and as designed. This issue only affects Computer Engineering's ability to manage the device. . This is not a reportable condition and does not impact Operations. Recommend Trend to Computer Engineering. <I> **** Actions Taken **** Notified SM and generated CR/WR. | 02-00-NET4-COMP-EPO
388841 | CR | 20190114 |  | 4 | og-rf-20A cycling on and off rapidly. | N | N |  | N | YES | <D> **** Detailed Description **** OG-RF-20A cycles on then shuts off immediately as though it is getting a start signal followed by a stop signal. This happens irregularly, sometimes as often as 3 starts in 3 seconds, and 15 starts over 10 minutes. <I> **** Actions Taken **** WR written. <N> **** Equipment Description **** RW 452. | 02-00-GY-TIC-17,02-00-OG-RF-20A
388842 | CR | 20190114 |  | 3 | Transformer M2 Fast Pressure alarm | N | N |  | N | YES | <D> **** Detailed Description **** Transformer M2 Fast Pressure or Power Status alarm was locked in. <I> **** Actions Taken **** Informed CRS and SSS, reset alarm per ABN-TRANSFORMER Following action of ABN-TRANSFORMER, held management phonecall to discuss operating with the fast pressure trip bypassed - decision made to stay in the current condition overnight (1 hour monitoring implemented) and continue with investigations at 0615 on dayshift. <N> **** Equipment Description **** Transformer yard | 02-00-E-TR-M2
388843 | CR | 20190115 |  | 3 | ABN-TRANSFORMER assumes wrong TR-M trip configuration |  |  |  | N | NO | <D> **** Detailed Description **** ABN-TRANSFORMER step 7.4.14 for the main transformer sudden pressure alarm assumes that the sudden pressure monitor trip function is deactivtade using the local cut-off switch. This feature was enabled per EC-17224. As a result, the ABN directs verifying the trip is deactivated which may be undesirable when since ther is no other sudden pressure trip capability. | 02-00-E-TR-M1,02-00-E-TR-M2,02-00-E-TR-M3
388851 | CR | 20190115 |  |  | Tamper Seals for WO 02112285 | [5 empty] | <N> For work order 02112285, the tech noted that currently there are red tamper seals in place
388852 | CR | 20190115 |  | 4 | Unacceptable Housekeeping around WCH-CR-51A |  |  |  | N | NO | <D> **** Detailed Description **** An unacceptable housekeeping condition was found around WCH-CR-51A. The condition was a result of modification work on WCH-CR-51A. Work Order instructions in multiple tasks for WO 02125913 instructed personnel to ensure work area is clean and housekeeping standards have been maintained in accordance with MI-1.8, Conduct of Maintenance, prior to taking this task to FINISHED (50). The work step was signedâ€“off and the work order is at COMPLETE (99). <I> **** Actions Taken **** Completed a walkdown of the area by WPS management. Area has been cleaned and left in an acceptable condition. An additional walkdown is being performed to verify compliance with MI-1.8. <N> This CR was canceled, reopened and edited at the request of the originator to correct the system and component listed. Also re-routed back to the control room for review. Williams Plant Services.
388859 | CR | 20190115 | CAQ | C | Received Drywell Temperature High alarm. | Y | Y |  | N | YES | <D> **** Detailed Description **** Received Drywell Temperature High, H13-P601.A11, 1-3 alarm shortly after securing CRA-FN-2A2 per SOP-CRA-OPS. Reference WO 02035819. CMS-TR-6 pt. 102 denotes CMS-TE -24, the RPV Head area AZ-325, indicated 151Â°F. The CRS directed restarting CRA-FN-2A2. When that fan was restarted, the Drywell Temperature High alarm cleared. <I> **** Actions Taken **** Notified the CRS. Reference T.S. 3.6.1.4 and LCS 1.7.1. Reference previously written CR 379822 and WR 29142398 from a 7 MAY 18 similar event. CMS-TR-6 pt. 102 inputs to the Post Accident Drywell Average Temperature calculation, CMS-TR-6, pt. 128. | 02-00-CRA-FN-2A2
388862 | CR | 20190115 |  | 3 | Manager/Supervisor missed training 2018 Q4 |  |  |  | N | NO | <D> **** Detailed Description **** During 2018 Q4 continuing trainingthere were 6 classes offered as well as the pilot session. There were 15 with a manager, supervisor or temporary supervisor qualification who did not attend one of the sessions. <I> **** Actions Taken **** Ran Data Access Desktop Leadership Members Who Did NOt Attend report to gather the data. See attached in EDMS.
388863 | CR | 20190115 | CAQ | C | Tamper Seals for CIA-PCV-2A | Y | N |  | N | YES | <D> **** Detailed Description **** For work order 02112285, the tech noted that currently there are red tamper seals in place. The the work instructions state that per drawing M556-1 A seal wire shall be run through the adjusting screw, spiraled down around the valve body and fixed with a lead seal. Can red tamper seals be used or do wire seals need to go back in? Is there a procedure that addresses this? <N> **** Equipment Description **** D N9/8.0 (DG CORRIDOR) | 02-00-CIA-PCV-2A
388866 | CR | 20190115 |  | 3 | Oversight of Long-term Supplemental Continuing Training |  |  |  | N | NO | <D> **** Detailed Description **** The Maintenance TAG has not been discussing the applicability of continuing training for long-term supplemental personnel as outlined in TPD-6. This has resulted in missed opportunities to include the small population of long-term Williams Plant Services electricians and pipe fitters in training applicable to their job scope. <I> **** Actions Taken **** Notified management. Initiated CR. Recommend Severity 3 to AR-TRNMT.
388868 | CR | 20190115 | CAQ | D | FP-V-D55/415 cap leaking | N | N |  | N | YES | <D> **** Detailed Description **** working 15.1.1, found cap and nipple with corrision from leak. | 02-00-FP-V-D55/415
388869 | CR | 20190115 | CAQ | D | FP-V-W6/127 leak upstream | N | N |  | N | YES | <D> **** Detailed Description **** While working 15.1.1 found a leak and corrosion upstream of FP-V-W6/127 . also FP-V-52 needs to be repacked. | 02-00-FP-V-52,02-00-FP-V-W6/127
388870 | CR | 20190115 |  | 4 | Maintenance Planner Error Returns over threshold |  |  |  | N | NO | <D> **** Detailed Description **** Maintenance Planning six month average from returns caused by planner errors has increased about the established threshold. This performance shift will be evaluated and actions will be developed as needed. Recommend 3/MNTPLAN. <I> **** Actions Taken **** Generated condition report.
388872 | CR | 20190115 |  | 4 | Moving personal vehicle contact with parked personal vehicle |  |  |  | N | NO | <D> **** Detailed Description **** On the morning of 1/15/19, and individual was attempting to park a personal vehicle when contact was made with a parked personal vehicle. Minor damage was sustained by the bumper flare of the parked vehicle. No personnel injuries occurred. As the Supervisor, I received this report at approximately 1125 am. <I> **** Actions Taken **** IAW ISPM-1: 1. Initiated CR. 2. Additional notifications performed for respective management chains. 3. Industrial Safety notified. 4. Form 23174 initiated.
388873 | CR | 20190115 | CAQ | D | CRD-GB-P1A/1A + P1B/1B lubricant shows signs of degradation | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02140595-01, marked completion required box, then taken back to complete <D> **** Detailed Description **** CRD-GB-P1A/1A and P1B/1B lubricant shows signs of degradation per latest oil analysis results. Total acid number (TAN) is elevated at 0.8 (P1A/1A) and 0.7 (P1B/1B). TAN is a measure of acidity of the lubricant and it is recommended to keep it less than 1. High TAN is indicative of oil oxidation. Recommendation is to change oil at the next maintenance window. Based on oil analysis results, lubricant condition is low risk of equipment damage or failure. <I> **** Actions Taken **** Data reviewed. | 02-00-CRD-GB-P1A/1A,02-00-CRD-GB-P1B/1B
388876 | CR | 20190115 |  | 4 | Personnel Contamination Monitor fails on High Background cou | N | N |  | N | YES | <D> **** Detailed Description **** RB 606 IPM-8 is found out of tolerance for acceptable background counts on one detector. Detector 14 found with GT 50% of average similar detectors. A reasonable search for possible radioactive contamination resulted in conclusion that the â€œHead Ampâ€ in the electronics is at fault. The source counts are as expected. The IPM is currently Out of Service. <I> **** Actions Taken **** Notified RPS, Rad Support, and I&C | 02-00-HP-EQ-42663
388877 | CR | 20190115 |  | D | Add WO 02114719 to R24 |  |  |  | N |  | <C> *** CRG Review Comments *** CRG Comment = ref. CR 2-05-03538 and PCN 05-0236 <D> *** Originator Subject *** Add WO 02114719 (COND-M-P/2B cables inadequately supported in E-SM-2 ) to R24 *** Detailed Description *** The lower center load side stab on COND-CB-CB2B does not aligned properly with the switchgear. This improperly impacts the rosette and prevents the breaker from racking in properly. This is not a breaker issue, this is a switchgear issue. Recommend adjusting the switchgear side breaker connection. Therefore add WO 02114719 (COND-M-P/2B cables inadequately supported in E-SM-2) to R24 scope to correct the breaker/switchgear stub alignment issue. <I> *** Actions Taken *** Established drain path via MS-V-16, 17, 18 to EDR for R17 <N> *** Equipment Description *** Lower center load side stabs on COND-P-2B breaker found misaligned during inspection. *** Comments/Assessment *** <O> *** OPS Review Comments *** | 02-00-COND-CB-CB2B
388880 | CR | 20190115 | CAQ | D | CRD-V-107/1807 leaks by 20 dpm. | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-V-107/1807 leaks by at 20 dpm. The leakrate was originally worse (a steady pulsing dribble/stream), but after flushing the valve, the leak has been reduced. Valve seat was found loose and replaced in 2017. Recommend removing bonnet and checking the seat. <I> **** Actions Taken **** Installed temp mod hose to direct leakage to drain. | 02-00-CRD-V-107/1807
388881 | CR | 20190115 |  | 4 | Data error on March 2016 NPDES discharge monitoring report |  |  |  | N | NO | <D> **** Detailed Description **** While compiling CW data for the NPDES permit application it was discovered that an error of units resulted in an incorrect zinc concentration result. A concentration of 0.013 ug/L was recorded in the laboratory data management system but should have been 0.013 mg/L. The erroneous data was used in the March 2016 NPDES discharge monitoring report and reported as less than the practical quantitation limit, â€œ<2 mg/L.â€ <I> **** Actions Taken **** Pulled raw data from files to verify correct value. Checked 36 months of data and determined that this was a singular incident. Audit trail in LIMS does not indicate how error occurred. Notified laboratory supervisor and E&RP. Wrote CR and revised DMR for March 2016 (Agency communication GO2 -19-020). <N> Correction on the CR description: The erroneous data was used in March 2016 NPDES DMR and reported as less than the practical quantitation limit, "<2 ug/L". It was originally reported as less than 2 mg/L in the CR description.
388882 | CR | 20190115 |  | 4 | MT-CRA-1 Dead Spot on Runway Conductor System / Bus Bar | N | N |  | N | YES | <D> **** Detailed Description **** A WPS electrician crane operator reported a long standing "dead spot" on the crane bridge runway conductor at/near the location of the bus bar fire in R-20. While operating the crane, the operator has observed a momentary loss of power as the bridge conductors pass over the affected area. <I> **** Actions Taken **** Reviewed CR 240596 to validate location of previous bus bar fire. Searched for previous CRs documenting this condition and found CR 365025 regarding MT-CRA-1 Remote Control issues. Discussed report with my supervisor before generating this CR. <N> **** Equipment Description **** T 555' A3/15.0 (PARK POSITION) | 02-00-MT-CRA-1
388883 | CR | 20190115 |  | 3 | MT-HOI-186 and 187 need replaced. | N | N |  | N | YES | <D> **** Detailed Description **** MT-HOI-186 and 187 need to be replaced with a larger hoists. The cable on both hoists is severly crushed, and cannot pass the annual inspection. Both hoists also get hot to the touch, and smell like the clutch or the brake assembly is burning when in use. These hoists are for raising and lowering the fish baskets in the TMU pumphouse. The next time they are scheduled for use is in March. This issue needs to be addressed before then. <I> **** Actions Taken **** Wrothe this CR, and informed my supervisor. . An AR EVAL is required if replacements are not like for like (e.g., 'larger' as described in this AR CR text). <N> **** Equipment Description **** Lowest level of TMU pumphouse. | 02-00-M-BLDG-MISC,02-00-MT-HOI-186,02-00-MT-HOI-187
388884 | CR | 20190115 |  | 4 | PDIS-CPU-DATA1 log collector service stopped unexpectedly | N | N |  | N | YES | <D> **** Detailed Description **** PDIS-CPU-DATA1 was found to have the McAfee log collection service in a stopped state. This service forwards Windows logs to the level 3 SIEM for review and storage. With this service stopped, logs are only stored locally on the device and not forwarded to the SIEM. Review of the event log found this service had terminated unexpectedly at approx. 7:30 PM on 1/14/19. . This issue has been discussed with Cyber Security and the resolution is a restart of the service and then a manual log review for the timeframe where the service was stopped. . This does not impact Operations. . This is not a reportable condition. <I> **** Actions Taken **** Notified SM, Cyber Security, and generated CR/WR | 02-00-PDIS-CPU-DATA1
388885 | CR | 20190115 |  | 4 | Received Oscillograph Started | N | N |  | N | NO | <D> **** Detailed Description **** The following sensors were tripped and are reset: J7 500kv Neutral Ground Overcurrent BPA reports the following: a. Cause was Trip of Ashe Marion 2 b. Relaying involved a multiphase pole <I> **** Actions Taken **** ARP
388886 | CR | 20190115 |  | 3 | Discrepancies found when taking Vibes for RRC-P-1A, need eng | N | N |  | N | NO | <D> **** Detailed Description **** Found discrepancies when taking point 3 and 4 (PSX and PSY). When you look-up the trending history this point(s) is taken and other times it is not. The WO 0213262201 RRC -P-1A & 1B CONDUCT VIBRATION MONITORING doesnâ€™t direct craft to ignore points. Please contact Rodney Cooper and/or Levi Dunlap for further information. Due to the discrepancies and no engineering support on Swing shift this â€œBâ€™ grade activity will go delinquent. <I> **** Actions Taken **** Wrote this CR, contacted MCR and WWM <N> **** Equipment Description **** RRC-P-1A | 02-00-RRC-P-1A
388887 | CR | 20190116 |  | 4 | Packing Leak on GY-V-216A1 | N | N |  | N | YES | <D> **** Detailed Description **** Small packing leak on GY-V-216A1. Undetermined leak rate, glycol is pooled on valve bonnet. See pictures. This was originally written up in WR 29140554 (dated 1-5-2018) this packing is still leaking. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** RRC-HX-ADS1A/1 Outlet valve | 02-00-GY-V-216A1
388888 | CR | 20190116 | CAQ | D | High moisture alarm CRD-HCU-3043 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-3043 due to high water level. <I> **** Actions Taken **** Refered to SOP-CRD-HCU and removed the moisture. alarm is clear. | 02-00-CRD-HCU-3043
388889 | CR | 20190116 |  | 4 | CAS-DISC-2P6C (CAS-C-1C disc.) needs lubrication/adjustment | N | N |  | N | YES | <D> **** Detailed Description **** CAS-DISC-2P6C (the CAS-C-1C disconnect) was very difficult to operate in both the ON and OFF direction. The disconnect was being cycled, per OI-12, during a Danger Tag hang. Pressure was applied to the cubicle door (as allowed per PPM 1.3.1) but the disconnect remained difficult to operate. Please investigate/repair while CAS-C-1C is Out of Service for 1000hr maintenance. Note: Danger Tag was hung on cubicle door to allow access to cubicle internals. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TG 441 | 02-00-CAS-DISC-2P6C
388891 | CR | 20190116 |  | 4 | Monthly Chemical Storage area inspection discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** The monthly inspection of Mechanical Maintenance chemical storage areas discovered the following discrepancies: Chemicals found outside of flammable liquid storage cabinet on W 507'. <I> **** Actions Taken **** Notified appropriate personnel to resolve. All discrepancies resolved, no further action required.
388899 | CR | 20190116 |  | 4 | E-AY-TR/N1 has service light illuminated. | N | N |  | N | YES | <D> **** Detailed Description **** During a review of the Kelman DGA logs for E-TR-N1 it was discovered that the blue service light on E-TR-N1 was illuminated. This was verified during a walkdown of the transformer. Currently based on the Kelman software this light is not illuminated. This CR is being prepared to document that the kelman for E-TR-N1 may require maintenance sooner than the currently scheduled PM (service) date. Currently the service for all of the Kelman DGAs is scheduled for the week of 7/8/19 under WO 02125574. Currently the Kelman is taking and analyzing oil samples with no service light and this has no impact on the operation of E-TR-N1. | 02-00-E-AY-TR/N1
388901 | CR | 20190116 |  | 4 | ISP-SEIS-X308 Procedure Enhancements |  |  |  | N | NO | <D> **** Detailed Description **** During performance of ISP-SEIS-X308 for new seismic monitoring system, changes/enhancements were documented that will need to be incorporated into the next revision. <I> **** Actions Taken **** Contacted Supervision & Shift Manager, Provided a redlined marked up copy of ISP-SEIS-X308 to procedure writer for revision. Wrote CR for Tracking <N> The redlined markup comments have been incorporated into ISP-SEIS-X308 revision 2 and are currently in the approval process for implementation. procedure has been revised, No further actions required.
388903 | CR | 20190116 |  | 3 | Need to create shut down flow chart |  |  |  | N | NO | <D> **** Detailed Description **** We need to create a shutdown flow chart to go with PPM 3.2.1. This has been discussed with the SROs in Operations. Mike Shoup has marked up copy of a flow chart. <I> **** Actions Taken **** Copy of previous flow chart marked up.
388908 | CR | 20190116 | CAQ | D | DMA-RLY-TK22 Master Equipment List revision needed |  |  |  | N | NO | <A> The D030 Name field is an administrative field and the DMA-RLY-TK22 name has been corrected as directed by this CR. <D> **** Detailed Description **** DMA-RLY-TK22 Master Equipment List description reads DMA -FN-22 LOW DP TIME DELAY ALARM RELAY. Top Tier drawings EWD-88E-020 and EWD-88E-034 show that this relay is only assoicated with the low differential pressure alarm for DMA -FN-21. <I> **** Actions Taken **** Notified System Engineer and initiated this CR. | 02-00-DMA-RLY-TK22
388911 | CR | 20190116 |  | 3 | FORM 22355 Return to Work form neds deactivated |  |  |  | N | NO | <D> **** Detailed Description **** FORM 22355 ATTENDING PHYSICIANS RETURN TO WORK RECORD still shows active in Portal. documents. This form was superceeded by FORM 25004. The form 22355 has innaccurate format and contact/fax numbers and should not be used. HR and OCC Health contacted. <I> **** Actions Taken **** HR is removing the form from active status.
388913 | CR | 20190116 |  | 4 | DEH-42-1A17C will not close in. | N | N |  | N | YES | <D> **** Detailed Description **** When cycling disconnect DEH-42-1A17C during clearance hang, it would not close back in. Request repair while clearance L-DEH-F-9-002 is hanging. Recommend also repairing OFF indicating light per WR 29146550. <N> **** Equipment Description **** TG 471 East | 02-00-DEH-42-1A17C
388916 | CR | 20190116 |  | 4 | Turbine bldg door T-134 will not open | N | N |  | N | YES | <D> **** Detailed Description **** Turbine bldg door T-134 will not open electrically or manually. Manual chain operator was on its track, but did not work either. | 02-00-T-DOOR-T134
388917 | CR | 20190116 |  | 3 | Procedure revision required to complete scheduled work |  |  |  | N | NO | <D> **** Detailed Description **** An ODCM surveillance was not able to be completed the day it was scheduled because the procedure was not revised prior to the day of implementation. The craft supervisor knew the procedure needed to be changed, and was planning to get it revised during the T-week process, but missed it in his schedule reviews. <I> **** Actions Taken **** The procedure was revised, and work completed the next day. The schedule was reviewed through T-7 to ensure no other procedures were in the same situation. No further action required.
388918 | CR | 20190116 |  | 4 | GSB Heater Leak | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Observed a fluid leak in the GSB basement on heater system. Persistant drip rate with water pooling on floor. On pipe beneath valve HCO-V-S5C <I> **** Actions Taken **** Call HP. | 02-00-HCO-V-S5C
388919 | CR | 20190116 | CAQ | C | Component CER Correction |  |  |  | N | YES | <D> **** Detailed Description **** Component Classification Evaluation Record (CCER) C92-0476 specifies the Reactor Protection System (RPS) relays for Turbine Throttle Valve Closure (RPS-RLY-K10A, K10B, K10C, K10D, K10E, K10F, K10G, & K10H) must function (de-energize) upon receiving the power loss signal by the position switches opening when the closure of the Turbine Stop Valves position is < 90% OPEN. The Licensee Controlled Specifications in Table 1.3.1.1-2, Function 8 lists the required set point to support OPERABILITY for Turbine Throttle Valve Closure as LE 5% closed. <I> **** Actions Taken **** Notified Control Room Supervisor and prepared Condition Report. Recommend Severity Level 3 to System Engineering to review the finding and update the CCER as appropriate. | 02-00-RPS-RLY-K10A,02-00-RPS-RLY-K10B,02-00-RPS-RLY-K10C,02-00-RPS-RLY-K10D,02-00-RPS-RLY-K10E,02-00-RPS-RLY-K10F,02-00-RPS-RLY-K10G,02-00-RPS-RLY-K10H
388920 | CR | 20190116 |  | 4 | Water Leak on GSB Water Heater | N | N |  | N | YES | <D> **** Detailed Description **** Water leak was reported on GSB Water Heater. Upon investigation, there was water on the floor and a leak (fast drip) was found on HCO-T-S5. The exact location of the leak is unknown due to installed pipe lagging. <I> **** Actions Taken **** Notified CRS and Laborer. Set up catch to maintain area housekeeping. | 02-00-HCO-T-S5
388921 | CR | 20190116 |  | 4 | Simulator Interuption due to THOR abort |  |  |  | N | NO | <D> **** Detailed Description **** On 1/9/2019 in the ILC program, a THOR abort occurred. The simulator instructors stopped and backtracked and then the THOR abort did NOT occur again. The simulator instructors used the time required to backtrack to brief students and the scenario was able to be completed. Per TDI-06, this is an interruption, but training was able to be completed. SR 2860 documents the resolution. <I> **** Actions Taken **** SR written, CR written
388922 | CR | 20190116 |  | 4 | Missing nut on COND-V-121C chainwheel collar | N | N |  | N | YES | <D> **** Detailed Description **** During a review of pictures taken for development of a design change it was noted that there was a missing nut on COND-V-121C chainwheel collar. Specific bolting details are not provided on any known drawing (such as CVI DWG 43 -00,107). It is possible this is a threaded connection into the bottom collar, but it is not like the other 5 valves in the area (COND-V-121A, COND-V-121B, COND-V-121C, COND -V-122A, COND-V-122B, COND-V-122C). Upon closer inspection of these other valves, it was also noticed that the bottom half of the collar (with chain wheel guide) is slightly thicker than the top half of the collar. Due to this, it appears the heavy hex nuts that were used are contacting the side of the thicker collar and are causing some of the bolting to bend. Therefore, it is suggested that all 6 of these valves have their bolting inspected and corrected if necessary. If the bolting on any of these valves were to fail, it would allow for the chainwheel chain guide to detach from the valve chainwheel and it could then slide down the existing chain. The entire handwheel with chainwheel attached does not appear to be at risk of falling. These valves are located on either side of each condensate booster pump in the overhead. There does not appear to be an immediate concern for becoming a falling object (safety issue) or missile, but maintenance should investigate/repair soon. A potential solution to the nut interference with the collar would be to install a locker washer under the nut and/or change any heavy hex nuts to hex nuts. Another solution might be to install the nuts on the opposite (thinner) side of the collar. Pictures of several valves are attached to EDMS of this AR CR. <I> **** Actions Taken **** Discussed issue with my immediate supervisor and called on-shift Shift Manager to notify him of issue. | 02-00-COND-V-121A,02-00-COND-V-121B,02-00-COND-V-121C,02-00-COND-V-122A,02-00-COND-V-122B,02-00-COND-V-122C
388923 | CR | 20190116 |  | 4 | CJW-V-132 leak by and CJW-V-131 very tight | N | N |  | N | YES | <D> **** Detailed Description **** While taking the monthly CJW samples chemistry discovered a slow leak from CJW-V-132. There is a quick disconnect on this valve and it looked like some chemical buildup had accumulated on the opening. When opening and closing CJW -V-131, it was very tight and hard to open. When closing CJW-V-132 and CJW-V-131 was still open the slow leak increased to 6 drips a minute. After closing CJW-V-131 the leak from CJW-V-132 diminished. It was very difficult to close CJW-V-131 to full close. It took two people. Chemistry suspects that CJW-V-131 packing may be compromised and that CJW-V-132 leaks and needs repair. As the expansion tank for CJW makes up the jacket should not drain out, but corrsion inhibitor will slowly reduce. <I> **** Actions Taken **** Notified CRS, Chemistry Supervision and Chemistry specialist.Initiated WR. <N> **** Equipment Description **** These valves are located on the Turbine Building 441' next to the CAS Compressors. CJW-V-131 CJW-V-132 | 02-00-CJW-V-131,02-00-CJW-V-132
388924 | CR | 20190116 |  | 4 | Simulator I/O issue causes switching of audit exam schedule |  |  |  | N | NO | <D> **** Detailed Description **** On 1/14/19, a simulator I/O issue prevented proper simulator reset after a scenario was completed. Because the simulator could not be reset, audit exam activities were rescheduled while the simulator staff were called for support. The simulator was repaired by resetting the I/O in panel 820. SR 2869 documents actions taken. This is not considered an interruption, but does count as lost time due to the schedule change. <I> **** Actions Taken **** SR and CR written.
388926 | CR | 20190116 | CAQ | C | Red Plastic Seals Installed on CIA-PCV-2A & 2B Not Per DWG | Y | N |  | N | YES | <D> **** Detailed Description **** Condition Report 00388863 reported that red plastic tamper seals were installed on CIA-PCV-2A instead of the wire and lead seal specified on drawing M556-1. A picture of the valve is attached to the EDMS folder. An inspection by the system engineer revealed that CIA-PCV-2B also has the plastic seals installed. Both of these valves were replaced in 2011 under Work Order 01179155 and 01179156. Both of these work orders repeat the drawing requirement in their respective precaution and limitation sections. The work histories for task 01 of both procedures, however, state that â€œred sealsâ€ had been installed instead. No explanation was given for the substitution, and no equivalency evaluation could be found. Although the use of the red plastic seals instead of wire and lead seals doesnâ€™t adversely affect the valvesâ€™ function, it does represent a configuration control issue. Itâ€™s recommended that maintenance investigate the cause of the unauthorized substitution and develop corrective actions. If lead seals are no longer desired, them maintenance should initiate an AR-EVAL per DES-2-9 to determine an adequate substitution and modify the drawing as appropriate. A possible substitution was reported in AR 00132063. <I> **** Actions Taken **** The seal on CIA-PCV-2A will be replaced under WO 02112285. Work Request 29146691 will replace the CIA-PCV-2B seal. | 02-00-CIA-PCV-2A,02-00-CIA-PCV-2B
388927 | CR | 20190116 |  | 4 | Late entry into eSOMS for HP Technician | N | N |  | N | NO | <D> **** Detailed Description **** An HP Technician was requested to report to FFD at end or near end of shift. The required time to complete FFD appointment caused the need for extension of work hours. This was not reported by the technician until the next day. <I> **** Actions Taken **** Upon notification the next day, hours worked were entered into eSOMS. There were no violations as a result of this late entry.
388928 | CR | 20190116 |  | 4 | Pipe protruding out of the ground to a height restricting ac |  |  |  | N | NO | <D> **** Detailed Description **** There is a pipe sticking out of the ground higher than others in the area of the isolation zone south of building 17. This pipe restricts access to the security cameras and ES for maintenance. If possible cutting the pipe lower and capping it would allow easier access to the area for maintenance. <I> **** Actions Taken **** Initiated this CR, discussed the issue with security supervision. Cutting the pipe down and capping it seems to be the best solution. <N> **** Equipment Description **** Isolation zone south of building 17.
388929 | CR | 20190116 | CAQ | D | Pressure Regulator P1 Set to Incorrect Pressure | Y | Y |  | N | YES | <D> **** Detailed Description **** During the evaluation of a replacement flowmeter for use in SLC-FIC-4, under AR-OBS 388879, it was discovered that the pressure regulator upstream from SLC-FIC-4 is currently set at approximately 10 psig, whereas CVI/DWG 02H22-05,65 specifies that this pressure regulator identified as P1 (no EPN) should be set at 20 psig. System Engineer confirmed that the pressure regulator has been set at approximately 10 psig for at least 12 years. Recommend maintenance adjust regulator pressure to 20 psig to align with CVI/DWG 02H22-05,65. See supporting information in AR-CR EDMS. <I> **** Actions Taken **** Expanded team to System Engineer and Design Engineering to confirm that the pressure regulator should be set at 20 psig. Discussed with Procurement Engineering Supervisor. Wrote CR. <N> **** Equipment Description **** Pressure Regulator P1, Upstream of SLC-FIC-4 | 02-00-SLC-FIC-4
388932 | CR | 20190116 |  | 3 | Component labeling in E-MC-2D doesn't match drawings |  |  |  | N | NO | <D> **** Detailed Description **** There are EPNs shown in EWDs: EWD-69E-045 and EWD-69E-048 that are not in assets suite. Labeling in the field of E-MC-2D compartment 4B for the associated components agree with drawing E535-9C component designation. Recommend re-labeling the field to match design drawings and create EPNs in passport. <I> **** Actions Taken **** Discussed issue with design engineer supervisor and initiated CR. <N> **** Equipment Description **** E-MC-2D compartment 4B: Relay compartment | 02-00-E-MC-2D
388934 | CR | 20190116 | CAQ | B | Received 4.601.A11 drop 3-3 NS4 ISOLATION RPV LEVEL LOW. | Y | N |  | N | YES | <C> RISK: Medium. CAUSES: Cause is Uncertain or Complex. Investigation Template Required Reopened CR to add cross reference for WO 02150139 for required work being conducted for cancelled WO 02139793. <D> **** Detailed Description **** Received 4.601.A11 drop 3-3 NS4 ISOLATION RPV LEVEL LOW. Observed MS-LIS-200C pegged low then high several times then steadied at normal level. Gross failure trip lights were illuminated for MS-LIS-200C and 300C. Also received 4.603.A7 5-1 SDV or GROUP 1,2,3,4,7 TROUBLE, 4.601.A11 2-2 RELAY CABINET 2 HALF TRIP and 4.601.A12 MSIV DIV 1 TRIP. WO 02118830 Rotate housing cover for CRD-LT-13C was being performed while this happened. <I> **** Actions Taken **** reset gross failure lights, NS4 and RC-2 trip. <N> CR Bring Back - Maint to bring back more information on this. . Cause known - Wiring was disturbed during maintenance activity under WO 02118830-02. Corrrective action known - Wiring was restored to normal configuration and the 1/2 trip was reset. . (ref: POD attached to EDMS) | 02-00-CRD-LT-13C,02-00-MS-LS-300C
388936 | CR | 20190116 |  | 3 | Service Building Heater Chemical Addition Necessary | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** pH chemistry results were low, they were measured at 8.15 with a low limit of 8.5, also Nitrite level well below limit <I> **** Actions Taken **** Discussed with specialist Wrote CR per specialist request
388937 | CR | 20190116 |  | 4 | Vehicle trap gate | N | N |  | N | YES | <D> **** Detailed Description **** The inner most motorized gate for the vehicle trap needs maintenance. Contact security at ext 2185 for further details. . <I> **** Actions Taken **** Security notification made. WR generated <N> **** Equipment Description **** Inner most motorized gate for the vehicle trap.
388938 | CR | 20190116 |  | 4 | (Non EN/CGS) CC-163 Certificate Incorrect |  |  |  | N | NO | <C> OFM change request â€“ Change Facility to 09 (01.21.2019) <D> **** Detailed Description **** Non EN/CGS Commercial Customer called to request correction to certificate of calibration. Date calibration due was incorrectly listed on certificate. Recommend assign to AR -CALSERV Category 4 <I> **** Actions Taken **** Initiated customer complaint CC-163, this CR and corrected the certificate and sent back to the customer.
388939 | CR | 20190116 |  |  | New relief valve not procured as ASME sec VIII (CAS-RV-118C) |  |  |  | N | YES | <D> **** Detailed Description **** During the process of replacing CAS-RV-118C it was discovered that the Relief Valve Data Sheet requires an ASME section VIII valve to be installed and the purchased valve (CID 19559) was not procured as an ASME section VIII valve. <I> **** Actions Taken **** Notified Manager and Relief Valve Program Owner and Procurement Engineering . <N> **** Equipment Description **** T 441 G5/6.5 | 02-00-CAS-RV-118C
388940 | CR | 20190116 | CAQ | D | Door R109 Verticle Clip broke | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** When walking into the airlock from the hallway there is a broken clip on the floor next to the threshold. <I> **** Actions Taken **** Contacted Security <N> **** Equipment Description **** Door R109
388941 | CR | 20190116 | CAQ | B | PMDD requirements in SWP-CSW-15 not followed |  |  |  | N | NO | <C> RISK - Med. CAUSE - Clear. Document the cause and corrective actions in the notes and create corrective actions. OFM change request â€“ 01.21.2019 RISK: Medium. CAUSES: Unclear/Complex. Investigation Template needed (01.21.2019) <D> **** Detailed Description **** On 1-16-2019 @ approx. 1100 as part of the ongoing review of Portable Media Digital Device (PMDD) it was identified that a Green Laptop and corresponding Green USB had been checked out to an individual greater than 14 days outside the requirement in SWP-CSW-15. The Cyber Specialist began his investigation to see why the laptop had exceeded the procedure requirements for being checked out. During the investigation it was identified through the electronic check-out log that the individual did not have the qualification (CSAI â€“ Use of PMDD) which is required prior to the delegated custodian checking out the media to the individual. In addition, the user admitted to not having scanned the laptop prior to use as required in SWP-CSW-15 and did not check the laptop back into the PMDD cabinet after use. Gaps identified include Delegated Custodian failed to verify CSAI qualification prior to providing GREEN PMDD to individual as per SWP -CSW-15. Individual failed to maintain positive control of GREEN PMDD as per SWP-CSW-15. Individual failed to virus scan GREEN PMDD as per SWP -CSW-15. Individual failed to check GREEN PMDD before 14 day time restriction as per SWP-CSW-15. Delegated Custodian failed to check-in GREEN PMDD and maintained device in unapproved storage failing to maintain positive control as per SWP-CSW-15 <I> **** Actions Taken **** Cyber Specialist notified supervisor and manager of events. Cyber Specialist confiscated the Green Laptop and Green USB and scanned the laptop and USB which scanned clean. Delegated Custodian was disqualified and PMDD Cabinet key confiscated Notified VP Corp, CIO and Security of issue Confirmed that the device was connected to a system that has no ability to be exploited. Non-reportable under 10CFR73.77 <N> Risk is medium, this is not a reoccuring issue. This is an isolated issue. Causes are known and not complex. The cause is that a supervisor issued a lap top with out validating qualifications against the distributed list. Corrective actions are known. The corrective actions have been created as assignments within this AR.
388942 | CR | 20190116 |  | 3 | Calculation E/I-02-91-03 - GT 5 CMRs |  |  |  | N | NO | <D> **** Detailed Description **** In accordance with Design Procedure DES-4-1, the intent of this CR is to document that calculation E/I-02-91-03 has greater than 5 Calculation Modification Records (CMRs) at â€˜Modifiedâ€™ status. There is no impact to the day-to-day operation of CGS. This assignment should be given to Electrical Design (AR-DEI) to revise the calculation and incorporate the â€˜Modifiedâ€™ status CMRs into the next revision.
388944 | CR | 20190116 |  | 3 | E/I-02-92-14 - GT 5 CMRs |  |  |  | N | NO | <D> **** Detailed Description **** In accordance with Design Procedure DES-4-1, the intent of this CR is to document that calculation E/I-02-92-14 has greater than 5 Calculation Modification Records (CMRs) at â€˜Modifiedâ€™ status. There is no impact to the day-to-day operation of CGS. This assignment should be given to Electrical Design (AR-DEI) to revise the calculation and incorporate the â€˜Modifiedâ€™ status CMRs into the next revision.
388945 | CR | 20190116 |  | 4 | CL-LI-4 not accurate below ~1000 gallons | N | N |  | N | YES | <D> **** Detailed Description **** CL-LI-4 does not read accurately below ~1000 gallons. This issue was previously written up in March 2018 on AR #378070. This is indicated by lowering tank level, followed by increasing tank level between 800-1000 gallons with continued use (see attached Chemistry records for trend). Today CL-LI-4 indicated 986 gallons but actual tank level (via inch marks on side of tank) indicated ~300 gallons. The level is very difficult to see by looking at the tank markings when at low levels. <I> **** Actions Taken **** Informed CRS, Wrote CR. | 02-00-CL-LI-4
388946 | CR | 20190116 |  | 4 | TMU phone needs repair, hard to hear. Noisy and static | N | N |  | N | NO | <D> **** Detailed Description **** TMU phone needs repair, hard to hear. Noisy and static <N> **** Equipment Description **** TMU phonr
388947 | CR | 20190116 |  | 3 | E/I-02-90-01 Working Copy - GT 20 CMRs |  |  |  | N | NO | <D> **** Detailed Description **** In accordance with Design Procedure DES-4-1, the intent of this CR is to document that the working copy of calculation E/I-02-90-01 has greater than 20 Calculation Modification Records (CMRs) at â€˜Modifiedâ€™ status. There is no impact to the day-to-day operation of CGS. This assignment should be given to Electrical Design (AR-DEI) to revise the calculation and incorporate the â€˜Modifiedâ€™ status CMRs into the next revision.
388948 | CR | 20190116 |  | 3 | ARP not cleared of mark up during ILC-23 Audit | N | N |  | N | NO | <D> **** Detailed Description **** An ARP was marked up during the second of three scenarios conducted on 1/15/17 for the ILC-23 Audit Examination. The instructors cleaning up between scenarios allowed distractions and a lack of overall ownership of the process to prevent them from cleaning the procedure before it was put away. During the third scenario, an ILC student noted that the ARP was marked prior to his use. The student gained no additional information from the marked up ARP and cleaned off the marks prior to use. Verification/validation and Supervisory Oversight were the enablers of excellence missed in this event. Recommend assignment to the Simulator Group. <I> **** Actions Taken **** Informed Training management, conducted a stand down with the ILC Audit exam team.
388949 | CR | 20190116 |  | 4 | RW 487 Mens Room IPM-8 Out Of Service | N | N |  | N | YES | <D> **** Detailed Description **** IPM-8 HP-EQ-C015124, located in the RW 487 Mens Room is out of service due to "Low Beta Counts" on the head detector. Visual inspection of the detector showed the physical properties to be immaculate. <I> **** Actions Taken **** Placed the IPM-8 OOS, initiated whole body frisking required prior to entering the restroom, contacted RP Supervision and initiated this CR and WR. <N> **** Equipment Description **** RW 487 Mens Room | 02-00-HP-EQ-C015124
388950 | CR | 20190116 |  | 3 | Need referenced warm-up time(SST-9203)noted in ISP-RCIC-Q903 |  |  |  | N | NO | <D> **** Detailed Description **** Need referenced warm-up time for SST-9203 Solid-State noted in ISP-RCIC-Q903. ISP-RCIC-Q903 PRECAUTIONS AND LIMITATIONS, 4.5 â€œAny warm-up periods for test equipment are to be observed before opening breakerâ€. Craft and Supervisor assume this and the note after 7.1 are in reference to Megger Solid-state digital timer â€Multi Amp SST-9203â€ and if so attachment 9.2 should have a reference warm-up time. the Manual for the timer only references the battery life (6 hours continues use) and that Recharge time is twice the time used on battery power with built-in battery charger but, no warm-up time. <I> **** Actions Taken **** Wrote CR, Started warm-up 8 hours before start of ISP -RCIC-Q903 . <N> **** Equipment Description **** MTE Megger Solid-state digital timer â€Multi Amp SST-9203â€ ***General Notes*** An assignment has been added to the maint. procedure revision data base. a link has been added to the EDMS of this AR.
388951 | CR | 20190117 |  | 3 | ISP-CRD-X303,X304,X307,X308 NEEDS FIXED |  |  |  | N | YES | <D> **** Detailed Description **** WHILE PERFORMING ISP-CRD-X304 W/O # 02118830-01 STEP 5.2.9 ELECTROFILM LUBRI-BOND OR EQUIVALENT CAT ID # 32280 COULD NOT BE PURCHASED. THIS IS NEEDED IN STEP 7.1.51. STEP 7.1.47 SHOULD BE DELETED TO INSPECT THE OLD O-RING FOR CLEANLINESS SINCE ITS REQUIRED TO PUT A NEW O-RING IN STEP 7.1.50. STEP 7.1.53 REMOVE METAL-TO-METAL AND THE NOTE ABOVE IT.STEP 7.3.4 ADD & TABLE 7.1a. ALSO SAME FIXES TO X304,X307, AND X308 <I> **** Actions Taken **** talked with supervisor and wrote this cr. <N> **** Equipment Description **** REACTOR 522' ***General Notes*** An assignment has been added to the Maint. procedure revision data base. a link to the data base has been added to the EDMS of this AR | 02-00-CRD-LT-13C
388959 | CR | 20190117 | CAQ | C | New relief valve not procured as ASME sec VIII (CAS-RV-118C) |  |  |  | N | NO | <D> **** Detailed Description **** During the process of replacing CAS-RV-118C it was discovered that the Relief Valve Data Sheet requires an ASME section VIII valve to be installed and the purchased valve (CID 19559) was not procured as an ASME section VIII valve. <I> **** Actions Taken **** Notified Manager, Relief Valve Program Owner and Procurement Engineering. <N> Parent reopened with permission from CAP Supervisor to re -route assignment 01 for supervisor review.
388960 | CR | 20190117 |  | 3 | Relay K8 Setpoint Correction |  |  |  | N | NO | <D> **** Detailed Description **** Annunciator Response Procedures (ARPs) 4.603.A7 and 4.603 .A8 incorrectly identify the setpoint which initiates a scram for Relay K8 as LE 1252 psig and should be corrected to LE 1250 psig. The Licensee Controlled Specifications in Table 1.3.1.1-2, Function 9 lists the required trip setpoint to support OPERABILITY for Turbine Governor Valve Fast Closure, Trip Oil Pressure - Low as GE 1250 psig. <I> **** Actions Taken **** Notified Control Room Supervisor and prepared Condition Report. Recommend Severity Level 3 to Operations Procedures (AR-OPSPROC) to review the finding and update the ARPs as appropriate.
388963 | CR | 20190117 |  | 3 | Archive clearance shows blanks for verification |  |  |  | N | NO | <D> **** Detailed Description **** D-COND-V-79/80-002A in the eSOMS DANGER 01 folder shows blanks for tags 75008 (RWCU-V-236A) and 75009 (RWCU-V -236B). This is due to a data modification that was performed to improve application performance. During this data modification, the clearance D-COND-V-79/80-002 was moved to a different folder in the application. Due to limitations with eSOMS, tag sharing across folders is not allowed. Since the 002A and 002 clearances exist in different folders, they no longer show that they are tag shared. This was an unforseen consequence of the data modification as this instance is unique to these clearances (D-COND-V-79//80-XXX is a permently hanging clearance). Recommended action: Perform another data modification to move the D-COND-V -79/80-002 clearance back to the DANGER 01 folder. <I> **** Actions Taken **** CORC Reactor Operator added a note on the actively hanging clearance explaining the blank verifications.
388964 | CR | 20190117 |  | 4 | Simulator Interruption from THOR Abort During Audit |  |  |  | N | NO | <D> **** Detailed Description **** A simulator interruption occurred during the audit exam on 1/15/2019 due to a THOR abort. The interruption occurred near the end of the scenario. SR 2876 was written to document the interruption. Previous validations and earlier runs of the same scenario on the same day did not result in an abort. <I> **** Actions Taken **** SR 2842 and CR 386862 document an interruption in a similar location in November of 2018. A fix has been obtained from the vendor and is in testing status.
388968 | CR | 20190117 |  | 4 | RWCU UT flow indication installation stopped due to paint |  |  |  | N | NO | <D> **** Detailed Description **** RWCU UT flow instrumentation was being installed per WO 02135031. When the piping insulation was removed from the north pipe space on R522 and the south pipe space in R548, paint was found on the piping under the insulation. The paint was not anticipated since typically we do not paint under insulation. The exact paint and/or a sample analysis was not available to confirm that it was not lead containing paint. Therefore, the removal of paint for preparation to install the UT was stopped. The UT probes could not be installed as planned and the work will have to be replanned. This work was supporting troubleshooting of RWCU Delta flow mismatch. The design spec allows paint, so this is not a non-conforming condition. This CR documents the impact on the station due to not being able to complete work and does not identify any adverse or non -conforming condition with plant equipment.
388969 | CR | 20190117 |  | 4 | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065228 Ashcroft Gauge- model 1490 3psig As Found Data was good- but needle would not return to zero. Gauge does not function properly. Rejected. Not Used during Calibration cycle. DEF #6789A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
388970 | CR | 20190117 |  | 3 | SOP-SW-LU positon for SW-V-736B |  |  |  | N | YES | <D> **** Detailed Description **** SOP-SW-LU says the position for SW-V-736B is closed. This valve is closed and capped in the plant. These need to be the same. | 02-00-SW-V-736B
388972 | CR | 20190117 |  | 4 | RW 507 POOR LIGHTING | N | N |  | N | YES | <D> **** Detailed Description **** On the rad waste 507 above the scaffold stock pile there is a burnt out light making it difficult to see. This is an industrial safety concern. <I> **** Actions Taken **** Contacted SSC manager and CR was written. <N> **** Equipment Description **** Rad waste 507 above scaffold stockpile
388973 | CR | 20190117 |  | 4 | Auto Scram Timer Locked Up | N | N |  | N | YES | <D> **** Detailed Description **** The Auto Scram Timer (AST) locked up on 1/17/19, noticed via red ice cubes on TDAS. Stopped and then restarted the data acquistion, AST was then reset and waiting for a full scram. CR written for trend. <I> **** Actions Taken **** Stopped and started data acquistion. | 02-00-TDAS-CRT-AST
388974 | CR | 20190117 |  | 4 | MT-ELEV-4 OOS | N | N |  | N | YES | <D> **** Detailed Description **** MCR received report from maintenance that MT-ELEV-4 was not responding to calls from different elevations. OPS-2 reset the elevator computer in the RW 467 elevator equipment room and the elevator is now working properly. CR for trend. <I> **** Actions Taken **** Reset elevator. | 02-00-MT-ELEV-4
388975 | CR | 20190117 |  | 4 | PWR-CRA-2 not operating | N | N |  | N | YES | <D> **** Detailed Description **** PWR-CRA-2 had a blown fuse replaced yesterday and it was working correctly after fuse replacement. Today just prior to picking up a liner it became non functional. We need to troubleshoot and correct this issue ASAP to minimize the impact to radwaste shipping. <I> **** Actions Taken **** Wrote CR, informed supervision and WWM. | 02-00-PWR-CRA-2
388978 | CR | 20190117 |  | 3 | ISPM 23 clarification recommended |  |  |  | N | NO | <D> **** Detailed Description **** During implementation of WO 02135031, ULTRASONIC FLOW MEASUREMENT OF RWCU SYSTEM- DELTA FLOW TS, a question came up regarding coating on RWCU piping potentially containing lead. Design spec AED-SPC-15A.3 states that lead paint should not be used in NSSS systems. ISPM 23 does not specifically call out utilizing design basis information to satisfy the determination if lead is contained within the coating. Recommend evaluation of the acceptability of using design basis information to satisfy the intent of ISPM 23 and enhancing the procedure as necessary. Reference AR-CR -388968 <N> At this time design basis documents are not adequate for determining lead containing material. ISPM-23 does not require clarification.
388979 | CR | 20190117 |  | 4 | Thermal losses attributed to MSR 1B degradation | N | N |  | N | YES | <C> Trend to CR 385027-01 <D> **** Detailed Description **** The 2 MWe generation loss tracked under CR 387230 is attributable to MSR 1B degradation from CR 385027. Strong correlations exist between degrading efficiency parameters and MSR 1B outlet temperature. Parameters include turbine first stage pressure, final feedwater temperature, and corrected gross generation. Indications point to a tube leak on the west end of the 2nd stage reheat of MSR 1B. The MSR degradation issue is currently tracked under 385027. Recommend trending this CR. <I> **** Actions Taken **** Initiated CR. Discussed with HX Engineer and MS System Engineer. Communicated to engineering. Assignment made to HX Engineer to evaluate MSR 1B scope. | 02-00-MS-HX-1B
388981 | CR | 20190117 |  | 4 | MT-ELEV-4 Malfunctioning | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-4 was reset and functioning for a few hours when a passenger rode the elevator from the 441 elevation to the 501 elevation. The doors would not open on the 501 elevation and the car returned to the 441 elevation where it jumped on the passenger then the doors opened. <I> **** Actions Taken **** Took the elevator out of service for investigation. | 02-00-MT-ELEV-4
388982 | CR | 20190117 |  | 3 | Unable to perform task due to poor planning/no walkdown |  |  |  | N | NO | <D> **** Detailed Description **** A task to rotate the housing for CRD-LT-13A was added to the surveillance work order 02118829, and a like task was added to 02118830 for CRD-LT-13C. One of these tasks was not given a WD hold, and the other had it's WD hold improperly released. As a result, the tasks made it to implementation week without having been walked down, and were not workable. <I> **** Actions Taken **** The work oder tasks were fixed, and 02118830 was completed. 02118829-02 was cancel requested, and a new WO needs to be created to complete the work with the next occurence of the PM. Likewise, 02132604-02 and 02113295-02 are being planned for CRD-LT-13D and -13B, and need to be split to stand alone work orders.
388983 | CR | 20190117 |  | 3 | ALARA Suggestion: New Fuel Receipt - Sliding Door Shielding |  |  |  | N | YES | <D> **** Detailed Description **** Elevated dose rates exist in the opening and on the 441' floor level adjacent to R-DOOR-RS2 (Railroad air lock sliding door to RHR B mezzanine). This area is in very close proximity to the crane bay hatch and the concrete foyer is a popular place to store tooling and equipment. Unnecessary dose is taken by individuals performing rigging/lifting and crane activities. The New Fuel Receipt project will start on 2/4/19 and the possibilty of an estimated 15-25 mrem could be taken if individuals spend more time in this area than needed. <I> **** Actions Taken **** Discussed with ALARA planning and requested that the sliding door be shielded prior to the staging activities of new fuel receipt. The door is currently bolted to the wall inside the RHR B mezzanine and is not functional. This area should be considered for permanent shielding. | 02-00-R-DOOR-RS2
388984 | CR | 20190117 | CAQ | D | FP-V-39 Needs to be Replaced. | N | N |  | N | YES | <D> **** Detailed Description **** FP-V-39 operates extremely hard. noticed the valve getting harder to operated each time it is cycled. Its time to Replace. | 02-00-FP-V-39
388985 | CR | 20190117 | CAQ | C | Reactor core flow change on computer pt B018 | Y | N |  | N | YES | <D> **** Detailed Description **** Noted a change on core flow following an actual RRC flow change. About 20 minutes after a RRC flow adjustment the trace on B018 Rx Core Flow Total spiked down and up. Then the flow drifted lower for 20 minutes. Then flow on B018 came back up to where it started causing indicated power to rise. Reduced RRC back the 0.1 HZ to lower power. 10 minutes later A longer lower spike was noted on the core flow trace. attached a copy of the trace. Reference CR 372469 and 371412 | 02-00-MS-SUM-606
388988 | CR | 20190117 |  | 3 | Drawing needs updated. |  |  |  | N | NO | <D> **** Detailed Description **** In order to perform troubleshooting on PWR-CRA-2 the craft needed to utilize CVI-DWG-19-01,5. This drawing needs to be updated in the data base so it is readable and of better quality. <I> **** Actions Taken **** Recommend Engineering or Doc Control to update print with a new, clean print <N> The hard copy drawing is in poor condition but it was rescanned to get a better image and then attached in Asset Suite / SharePoint. No further actions required.
388989 | CR | 20190117 |  | 4 | Bus SL-61 motor control center overload trip alarm | N | N |  | N | YES | <D> **** Detailed Description **** BUS SL-61 motor control center overload trip alarm 4.800.C2 drop 6-6 was received in the main control room. The alarm came in and reset and locked in. The alarm typer indicates that MC-6M is the cause of the alarm however there is no indication that there is any fault on MC-6M and no loads were lost. This happened previously as documented by AR 388513. WR 29146423 is at H/APPR. <I> **** Actions Taken **** Informed the CRS | 02-00-E-CB-61/6M
388990 | CR | 20190117 | CAQ | D | in ISP-MS-X306 found MS-LT-26A out of tolerance. | Y | Y |  | N | YES | <D> **** Detailed Description **** in ISP-MS-X306, WO#02106548-01, found MS-LT-26A Out of tolerance. Table 7. 1a the ma output of, MS-LT-26A, was found out of tolerance, in Step 7.1.17 pg.9 <I> **** Actions Taken **** adjusted to within desired tolerance in table 7.3a pg.13. | 02-00-MS-LT-26A
388991 | CR | 20190117 | CAQ | C | IMPROPER CR CLASSIFICATION & CLOSURE |  |  |  | N | NO | <C> The original CR was characterized as a recommendation to review and, if needed, revise PPM 10.1.26. It was not characterized as a procedure that could not be performed as written or did not properly implement a regulatory requirement. While the CRG could have failed conservative at the time, the decision was made to make this CR Non-CAQ until it was determined that the procedure was deficient. Assignment-01 has been created to follow the procedure revision as it moves through the Maintenance Procedure Process. If the procedure is deficient, CAP will take the lead to rescreen CR 368694 to CAQ in accordance with SWP -CAP-01 <D> **** Detailed Description **** QA generated CR 368694 pertaining to a non-compliant Furmanite repair and pressure test to ASME valve MS-V-707C was reviewed (WO 02090150) and appears to have been miscategorized and was closed without addressing the issue. Assignment 01 provided a procedure markup for PPM 10.1.26 (Temporary Leak Sealing) in EDMS, but the procedure was never revised to incorporate the changes. It appears that the reported non-compliances were never addressed: 1.) performing an ASME repair while the plant was shut down, and 2.) performing the non-Code PMT pressure test with the system unpressurized. The QA recommendation was for Maintenance to review procedure guidance and determine if the procedure requires revision. Maintenance provided a procedure markup which was uploaded into EDMS, but the procedure was never revised. Additionally, the marked up Section 4.5 appears to be contradictory and may not align with NRC requirements to repair/replace ASME items during plant shutdowns. MS-V-707C was successfully replaced and PMT tested in R23 (WO 02079104-01) following this Furmanite repair activity. This condition does not impact safety or operations at CGS. <I> **** Actions Taken **** Notified the ISI Program Engineer, Engineering Management, and the original CR personnel in Quality and Maintenance. Recommend assignment to QA or Maintenance.
388992 | CR | 20190117 |  | 3 | WO task 02128862-05 unable to set to finished |  |  |  | N | NO | <D> **** Detailed Description **** WO task 02128862-05 is a support task and as such EWP should allow the task to be set to finished, however the set to finish option was greyed out and was unable to be performed. The CRS had to manual process the entire workflow for this work order task vice being able to set the task to finished. This created inefficiencies in the work order process. Recommend training to the responsible group to ensure proper coding is assigned to support task WO in the EWP process. <I> **** Actions Taken **** Asked the CRS to process the WO to allow the task to be taken to finished <N> DataGlance Set to Finished supports taking support tasks directly to FINISHED status in Asset Suite from the Supervisorâ€™s Assign panel. This activity is only available when the Asset Suite Task status is APPROVED 30 or READY 45 and the JOB-TYPE (table TIDWOTSK) is equal the following: AD-ADMINISTRATIVE CO-CLEARANCE ORDER: HANG OR LIFT NH-SHOP PM - OPS REVIEW NOT REQUIRED NP-PM - OPS REVIEW NOT REQUIRED NO-OTHR PM- OPS REVIEW NOT REQUIRED NS-ESSENTIAL PM - OPS REVIEW NOT REQUIRED OS-OPERATIONS SUPPORT SC-SCAFFOLDING ERECTION/REMOVAL SH-SHOP WORK SP-SUPPORT TASK XX-ADMINISTRATIVE SUPPORT WORK ORDER TASK . In the case of WO task 02128862-05 the Job-Type = â€˜OTâ€™ (operations testing), so the tasks does not qualify for Set to Finished.
388993 | CR | 20190117 |  | 4 | DEH-F-18A needs to be changed out | N | N |  | N | YES | <D> **** Detailed Description **** Differential pressure across DEH-F-18A is currently at 24 psid. Administrative limit is 30 psid, with an alarm set point of 50 psid . dP spiked (from 4 to 19# in one shift )after replacement of DEH-F-9, and it is suspected that debris from the filter replacement is collecting in the downstream DEH-F-18A. Differential pressure may approach its dP limit sooner than normal due to the recent work. Recommend changing out soon. <I> **** Actions Taken **** Informed CRS | 02-00-DEH-F-18A
388994 | CR | 20190117 |  | 4 | Contamination Found Outside RWCU Hold up Pump Rm 'A' | N | N |  | N | YES | <D> **** Detailed Description **** While trying to make entry into the RW 467' RWCU Hold up Pump room 'A' for housekeeping the HP Technician noticed water on the floor and a spray of water coming from inside the room, the source being RWCU-P-3A. Smears revealed 5k dpm/100cm2. <I> **** Actions Taken **** The HP Technician contacted the RWCR about the situation and informed them that he was going to post the walk way infront of the LHRA accordian gate as a Contaminated Area. Dry mop heads were put in place to keep water inside the newly posted Contaminated area. HP Supervision was also informed. <N> **** Equipment Description **** RW 467' RWCU Hold up Pump Room A Survey 20190118-2. | 02-00-RWCU-P-3A
388995 | CR | 20190117 |  | 4 | Vehicle running and unattended; south Deschutes parking lot |  |  |  | N | NO | <D> **** Detailed Description **** A vehicle was identified running and left unattended in the south Deschutes parking lot at approx. 1715 hours. <I> **** Actions Taken **** Notified Security and initiated CR.
388996 | CR | 20190117 |  | 3 | PPC-COMP-8715 unavailable due to failures during backups | N | N |  | N | YES | <D> **** Detailed Description **** While performing WO 02106586-01 to backup PPC-COMP-8715 I&C techs encountered errors during the backup. Backups would error and fail before completion on all three CPUs. Computer Engineering supported troubleshooting that involved adjusting SCSI speeds per the WO instructions, but were not successful. Additionally during troubleshooting, SCSI parity errors and hdd sector errors were observed on su113. . This does affect Operations, only TDAS is available over the weekend. All signals are available. . This is not a reportable condition. . Even though it has a WR, recommend assigning to Computer Engineering to document resolution for trending purposes. <I> **** Actions Taken **** Contacted the vendor who is putting together some troubleshooting instructions for Monday (1/21). Notified CRS and SM of the situation and that PPC will be unavailable over the weekend. TDAS is currently primary and functioning normally. | 02-00-PPC-COMP-8715
388997 | CR | 20190117 |  | 3 | Recommended change to LCS 1.7.1.B.1 action statement |  |  |  | N | NO | <D> **** Detailed Description **** LCS 1.7.1.B.1 action statement is to â€œinitiate actions to restore area or room temperature to be within the Condition B limits of Table 1.7.1-1 Immediately.â€ This action statement appears to be overly restrictive without a technical basis to support the immediate timeframe. Due to this action statement, some work is not able to be performed online solely due to compliance to this action statement. Per the LCS basis, the Condition B temperature limits are in place to minimize aging effects on the equipment. The basis goes on to state that (for primary containment air spaces) no immediate impact to equipment OPERABILITY is expected above this limit for a short time (a few days). Initial assessments conclude that a change to the LCS action statement would have little impact to station risk, and no impact to operability of equipment. See EDMS for recommended working to change LCS 1.7.1.B. <I> **** Actions Taken **** Initiated CR. Discussed with Licensing on the feasibility for an LCS change.
388998 | CR | 20190117 |  | 4 | Received 820.B3.2-2 "GEN SEAL OIL BACKUP PRESS LOW" alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received alarm momentarily, OPS 3 reports SO-PI-279 indicates 130#, normal and steady. <I> **** Actions Taken **** recommend trending | 02-00-SO-PRV-291
388999 | CR | 20190117 |  | 3 | Notification to BPA regarding diabled trip on TR-M2 |  |  |  | N | NO | <D> **** Detailed Description **** The Main 2 Transformer sudden pressure relay logic was bypassed on 1/14/19 due to an alarm condition (Ref. CR 388842). There is a requirement to notify BPA that this protective feature has been disabled per NERC standard PRC-001-1.1. This requirement was not immediately understood. Recommend applicable procedures get updated with this requirement (ABN-TRANSFORMER, PPM 1.10.1). <I> **** Actions Taken **** Wrote CR.
389000 | CR | 20190118 |  | 4 | Data Wireless Reader Not Functioning as Designed |  |  |  | N | YES | <D> **** Detailed Description **** Data Wireless Reader Y2 (DSV11SCAK070501769) located at the Security Checkpoint is not functioning as designed and requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security supervision notified. Initiated CR/WR. DWR taken out of service. <N> **** Equipment Description **** DWR at security checkpoint
389001 | CR | 20190118 |  | 3 | Enterprise Vault email archive not working after patching |  |  |  | N | NO | <D> **** Detailed Description **** EV email archiving is not functioning properly after monthly patching and reboots. Users still have access to their e'mail data within outlook, but are unable to access messages in their email vault. <I> **** Actions Taken **** Several troubleshooting tasks were attempted. Case opened with vendor Veritas. Awaiting Veritas response. <N> **** Equipment Description **** Corp Computer Equipment - No EPN
389002 | CR | 20190118 |  | 4 | COND-V-221 throttled position during RWCU demin backwash | N | N |  | N | YES | <D> **** Detailed Description **** During the first Backwash of RWCU-DM-1A on step 5.3.7 supstep L. COND-V-22A stayed in the throttled position during the 3 minuite Fill and Wash step. Water flow was verified at 55gpm @ 21# when it was supposed to vary from 75-100gpm ~18#. The valve fully opened during the subsequent substep m. On the second Backwash of the demin proper operation was observed. This is a prior documented problem under AR# 296931 & 325569. <I> **** Actions Taken **** Informed MCR, initated AR. | 02-00-COND-V-221
389004 | CR | 20190118 | CAQ | D | OSP-MT-W701 performed with A solenoid GT .4 msec. | N | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02112562, marked completion required box, then taken back to complete <D> **** Detailed Description **** Performed Quad Voter Solenoid test OSP-MT-W701 WO 02130107 and solenoid A was greater than 400 milliseconds at 401 milliseconds. <I> **** Actions Taken **** Performed test 2 more times per procedure and fowarded results to engineering. | 02-00-DEH-SV-TRIP/A
389005 | CR | 20190118 | CAQ | C | SW-TE-2D reading is unstable on SW-TI-2A | Y | Y |  | N | YES | <D> **** Detailed Description **** SW-TE-2D reading is unstable on SW-TI-2A, field operator had to jiggle the switch delicately back and forth within the 2D position to get an reading and the reading with the highest temperature value attained was 36F. This reading is 6 degrees lower than the other 3 reading on SW-TI-2A, the previous shift SW-TE-2D indicated approximately the same value as the other 3 readings on SW-TI-2A. Suspect that either SW-TE-2D is failing or the contact for the SW -TE-2D on SW-TI-2A is becoming lose and dosent properly display accurate temperature. <I> **** Actions Taken **** Informed CRS <N> See EDMS for explanation behind assignment 06 being cancelled. it was also noted that no corrective action was created for the condition adverse to quality. Please note that the condition was resolved via the work management system and cross-referenced WRs. | 02-00-SW-TE-2D
389008 | CR | 20190118 |  | 4 | OG-RF-20A Oil Level HIGH | N | N |  | N | YES | <D> **** Detailed Description **** OG-RF-20A oil level was approximately 3/4 in sightglass while not running. Rounds state the level should be between 1/3 and 1/2. Oil level needs to be lowered. <I> **** Actions Taken **** Notified CRS | 02-00-OG-RF-20A
389009 | CR | 20190118 |  | 4 | Very Poor Lighting in RW 467 "A" and "B" Valve Galleries | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Very Poor Lighting Conditions in RW 467 "A" and "B" Valve Galleries. Extremely Poor Lighting Conditions for upcoming work on RWCU-P-3A, in the RWCU "A" Hold Up Pump Room. These Poor Lighting Condtions are a Safety Concern, for upcoming work and normal access through these spaces. <I> **** Actions Taken **** Notified HP Supervisor. Notified HP Lead Technician. Initiated CR/WR. <N> **** Equipment Description **** RW 467 "A" and "B" Valve Galleries.
389011 | CR | 20190118 |  | 4 | Auro Scram Timer error | N | N |  | N | YES | <D> **** Detailed Description **** Auto Scram Timer appeared to lock up as noticed by red ice cubes on TDAS and red indicator on U1 screen. <I> **** Actions Taken **** Terminated and restarted data acquisition. Reset the AST computer and verified it is waiting for scram. N15 screen on TDAS still shows an error bad data message, but status shows waiting for scram and AST clock matches TDAS clock. | 02-00-TDAS-CRT-AST
389012 | CR | 20190118 |  | 4 | TG-ID-1 step change from likely inadvertant bump | N | N |  | N | YES | <D> On rounds, the chart recorder Date/Time label was obstructing the chart window. When the label was moved to see the window, it is believed that an inadvertant bump occurred causing a step change on the recorder. The recorder was indicating a steady value of approx. 0.77mA DC, but began displaying a steady value of approx. 0.8 mA DC. Instrument may need calibration. <I> Notified the MCR. Was told to write CR to see if calibration is needed. | 02-00-TG-ID-1
389014 | CR | 20190118 |  | 4 | Poor Lighting in RB 422" C RHR Pump Room | N | N |  | N | NO | <D> **** Detailed Description **** When accessing RB 422' C RHR-Pump Room it was noticed that there are multiple lights out on the 422 level. The room is not dark just dimly lit. <I> **** Actions Taken **** Initiated CR <N> **** Equipment Description **** RB 422 RHR C Pump Room
389015 | CR | 20190118 | CAQ | C | Received RCIC Turbine Oil Filter D/P high alarm | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02149597, marked completion required box, then taken back to complete <D> **** Detailed Description **** During performance of OSP-RCIC/IST-Q701 4.601.A4 drop 6-6 RCIC TURBINE OIL FILTER D/P HIGH alarm was received. Local D/P was 3 psid when the alarm was received and the set point for RCIC-DPS-14 is GE 6 PSID to actuate the alarm. RCIC-F-1 was shifted from R to L per the ARP and D/P remained 3 psid. As the RCIC pump quarterly testing continued the D/P was checked and slowly increased to 5 psid. 3 psid is below the alarm set point and potential causes are RCIC-DPS-14 not at the correct set point or RCIC-PI-6 and or RCIC-PI-7 being out of calibration and providing inaccurate information to the filed operators. If RCIC-DPS-6 is calibrated correctly then recommend changing out both filters on RCIC-F-1. <I> **** Actions Taken **** Followed ARP and informed CRS | 02-00-RCIC-DPS-14
389016 | CR | 20190118 | CAQ | D | butt splice on shield wire in E-IR-P005 need repair | Y | N |  | N | YES | <D> **** Detailed Description **** During investigation of wiring in E-IR-P005 under WO 02138131-01 it was dicovered that the but splice for the shield for twisted pair 2 in cable 5RPS-0175 did not capture all the strands of the shield in the crimp. only 5 strands of the shiled are in the butts splice the shield wire is terminated in E-IR-P005 at CC-18. . Discussed with enginnering and engineering concurred that the shiled is connected but that this butt splice needs replaced. Wrote CR to document and generated a WR to repair. . This shiled is for the twisted pair for the current loop associated with CRD-LT-13C. <I> **** Actions Taken **** Notified engineering and operations and generated AR/CR and WR | 02-00-CRD-LT-13C,02-00-E-IR-P005
389017 | CR | 20190118 |  | 3 | PASSPROD database upgrade unsuccessful. |  |  |  | N | NO | <D> **** Detailed Description **** The planned recreation and upgrade (to Oracle ver 12.2) of the PASSPROD database could not be completed during the scheduled maintenance period due to unexpected problems with Oracle's datapump utility. <I> **** Actions Taken **** The original version of the database was restored using Oracle's recovery tools and returned to service.
389018 | CR | 20190118 |  | 4 | Simulator error during scenario |  |  |  | N | NO | <D> **** Detailed Description **** The simulator transferred the electric plant during an evaluated scenario with no instructor input. This transfer was not part of the scenario and distracted the training crew. SR 2879 generated to capture the data. This error was not able to be reproduced by the simulator group. <I> **** Actions Taken **** SR generated to capture the data. informed training management.
389019 | CR | 20190118 |  | 4 | Transformer yard N2 bottle replacement | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-N2 N2 bottle has been replaced, there is now 1 full and 1 empty bottle in the XFMR yard storage rack. IAW ABN -TRANSFORMER, a WR is to be written to have the empty bottle replaced. This AR is to create the WR as required. <I> **** Actions Taken **** Informed MCR, generated AR/WR. <N> **** Equipment Description **** Transformer yard spare N2 bottle storage - empty bottle
389020 | CR | 20190119 | CAQ | D | Two blue dot lights out SM-8 SWGR room | N | N |  | N | YES | <D> **** Detailed Description **** Two blue dot lights are out in the SM-8 swgr room. Please replace. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 467 SM-8 SWGR room.
389021 | CR | 20190119 | CAQ | D | Several lights out RHR-P-2C room, incl. blue dot. | N | N |  | N | YES | <D> **** Detailed Description **** Several light fixtures in RHR-P-2C room need relamping. This includes blue dot fixtures. Please re-lamp. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RB 422 RHR-P-2C room
389024 | CR | 20190119 |  | 3 | E-AY-TR/M1 gas analyzer caution light lit. | N | N |  | N | YES | <D> **** Detailed Description **** Transfiix DGA E-AY-TR/M! yellow caution light is lit. The Caution light remained lit after a second gas sample. An intermitent blue light ( not present at this time ) has been previously identified. This light had been identified on a previous AR/WR but had cleared and the WR cancelled. The only potential error code was TCP-502 which appears on the screen with the XXX. <I> **** Actions Taken **** Notified supervisor and initiated this AR/WR. | 02-00-E-AY-TR/M1
389025 | CR | 20190119 |  | 4 | RWCU-SPV-210B leaking air | N | N |  | N | YES | <D> **** Detailed Description **** During PMT of RWCU-AO-210B 02088852-04, observed air leakage from the solinoid valve, RWCU-SPV-210B, RWCU-V-210B functoned as designed but had slow stroke times. <I> **** Actions Taken **** Notified ops, Mainenance and WWM and generated WR to repair solinoid valve RWCU-SPV-210B <N> **** Equipment Description **** RW 467 B valve gallery Q9/11.8 | 02-00-RWCU-SPV-210B
389026 | CR | 20190119 | CAQ | D | RCIC-DPIS-13B | Y | N |  | N | YES | <D> **** Detailed Description **** While performing ISP-RCIC-Q903(02106575), RCIC-DPIS-13B was found OOT high at 238". The CFT desired tolerance is 210 -230". Considering to switch came in at 238" and was under the allowable tech spec value of 241", I/C informed Ops and adjusted switch back into desired range. <I> **** Actions Taken **** Informed ops, adjusted switch back into desired range, wrote cr <N> **** Equipment Description **** RCIC-DPIS-13B, rx471
389027 | CR | 20190119 | CAQ | D | RCIC-DPIS-13A | Y | N |  | N | YES | <D> **** Detailed Description **** While performing ISP-RCIC-Q901(02106563) RCIC-DPIS-13A Low switch was found OOT at -219". The desired CFT range is -190 to -210". Technicians made adjustment and left switch at its desired setpoint of -205" <I> **** Actions Taken **** Notified Ops, made adjustments, wrote CR <N> **** Equipment Description **** RCIC-DPIS-13A Rx471
389028 | CR | 20190119 |  | 4 | CW East electrical bldg. north entrance not accessible. | N | N |  | N | YES | <D> **** Detailed Description **** CW East electrical Bldg #1 ( Bldg 38 ) north door, door knob, will not turn from the outside. Accessed the East elctrical bldg from the south side double doors. <I> **** Actions Taken **** Checked door lock, and verified that the inner door knob would turn, but the outer door knob would not. Appears that the locking mechanism has failed. Notified supervisor. <N> **** Equipment Description **** CW East Electrical Building.
389029 | CR | 20190119 | CAQ | D | High Alarm Rate SEC-MW-ISFSI/67AT |  |  |  | N | YES | <D> **** Detailed Description **** CAS received a high alarm rate on MW67 TJBT. Compensatory measures were put in place. | 02-00-SEC-MW-ISFSI/67AT
389031 | CR | 20190120 | CAQ | D | Security door C408 dog latch needs maintenance | Y | Y |  | N | YES | <D> **** Detailed Description **** Security door C408 dog latch needs maintenance. The latch on the inside of the control room is inoperable. Appears the pin is broken and latch detached from the door. <I> **** Actions Taken **** CR/WR initiated. Security supervision notified. Shift manager notified. | 02-00-W-DOOR-C408
389032 | CR | 20190120 |  | 4 | Received red ice cube on ALPHA PROCESSOR P605 | N | N |  | N | YES | <D> **** Detailed Description **** Received red ice cube on ALPHA PROCESSOR P605 for 8715 to VMS result in momemtary lost AVG PERIOD of 1 MIN. Need to investigate and resolve the issue. <I> **** Actions Taken **** Terminate DATA ACQ (8715 to ALPHA then re-initiate clear the red ice cube indication. CRS/SOM informed. | 02-00-TDAS-COMP-8715
389033 | CR | 20190120 |  | 4 | Unable to wipe up oil under TO-HX-1A/1B due to scaffolding | N | N |  | N | YES | <D> **** Detailed Description **** Unable to wipe up oil under TO-HX-1A/1B due to scaffolding installed for the outage. scaffold was installed for WO 02111477 task 04 and 07. Area was tight enough to crawl in and clean up scaffolding makes it impossible until it leaks out side the area. <I> **** Actions Taken **** Discussed with supervisor. <N> **** Equipment Description **** t-471
389034 | CR | 20190120 |  | 3 | Evaluate installing a temporary deflector A RFW steamleak | N | N |  | N | YES | <D> **** Detailed Description **** Evaluate installing a temporary deflector for the A RFW turbine steam leak. Leak has eaten a hole thru the lagging it is impinging on and it is unknown if there is further damage under neath. Leak was discovered and discussed in WR 29145190, 29146533, WO 02125690 and CR 385834. <I> **** Actions Taken **** wrote WR CR <N> AR type EVAL needed. | 02-00-MS-V-172A
389035 | CR | 20190120 |  | 4 | CAS-C-1B | N | N |  | N | YES | <D> **** Detailed Description **** Compressor oil level is low and requires filling <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-CAS-C-1B
389036 | CR | 20190120 |  | 4 | RFT-LOC-1B | N | N |  | N | YES | <D> **** Detailed Description **** conditioner was found running with heaters de-energized and no flow going through the bowl. no level was visible at bowl sightglass and the flow meter was pegged low. attempted to vent the skid with no oil issuing from vents. bowl/motor was exhibiting increased vibration/grinding noise. there is a video on the OPS-3 ipad documenting as found condition. checked the suction and discharge paths without going into the HRA on the feed pump skid, but everything looked to be aligned correctly on visual inspection <I> **** Actions Taken **** initiated CR/WR informed MCR secured RFT-LOC-1B and placed in shutdown lineup | 02-00-RFT-LOC-1B
389037 | CR | 20190120 |  | 3 | SOP-COMPUTER-OPS Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Add a section to SOP-COMPUTER-OPS on how to set control rod operability status for the Auto-Scram Timer to reflect slow or inoperable control rods. Create new section 5.18 titled "Setting Control Rod Operability Status for the AST." Copy and paste Section 7.6 of TSP-CRD-C101 as the new section of SOP-COMPUTER-OPS and renumber as appropriate. See EDMS file for email discussion and copy of Section 7.6 of TSP-CRD -C101. <I> **** Actions Taken **** Discussed with OPS supervisors and SNEs.
389038 | CR | 20190120 | CAQ | D | RCIC turbine oil level low | Y | N |  | N | YES | <D> **** Detailed Description **** RCIC-P-1 turbine oil level low, restore oil level between the low and high marks. <I> **** Actions Taken **** Contacted weekend craft supervisor to have oil added. | 02-00-RCIC-P-1
389039 | CR | 20190120 |  | 3 | OI-12 procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Add a section to mechanical standards (recommend new section 3.13) for clearances associated with HCUs. Wording to be included to the effect that when tagging out HCUs which will remain inoperable for greater than one shift, provide direction in the clearance order notes to perform the applicable section of SOP-COMPUTER-OPS to set control rod operability status for the AST analysis program. <I> **** Actions Taken **** Discussed with Ops supervisors and SNEs.
389040 | CR | 20190120 |  | 3 | No Full Black N2 bottles in railroad bay | N | N |  | N | NO | <D> **** Detailed Description **** No Full Black N2 bottles in railroad bay. The minimum per OPS-2 logs is one full black N2 bottle. This is second week in a row that we have not had the required number of bottles in rail road bay. <I> **** Actions Taken **** Contacted CRS/SSS and initiated this CR-
389041 | CR | 20190120 |  | 4 | CW-PHITS-1 has a FAIL/S4 LED lit | N | Y |  | N | YES | <D> **** Detailed Description **** CW-PHITS-1 Yokogawa display has a fail message at the top right of the screen and the FAIL/S4 LED is lit under 'CONTACTS'. Lower left display reads E5.1 Picture included | 02-00-CW-PHITS-1
389042 | CR | 20190120 |  | 4 | DO-TK-3 Diesel storage room B104 light is out |  |  |  | N | YES | <D> **** Detailed Description **** At the CWPH, the diesel storage room (B104) lighting is out. <I> This is NOT essential lighting per LCS 1.10.7, but this light has been out over two months. This is a safety issue and must be fixed. Two WR's are still at H/APPR for this. <N> **** Equipment Description **** CWPH south entrance. Room B104
389043 | CR | 20190120 | CAQ | C | During performance of WO 02106860 deficiencies were noted | N | Y |  | N | YES | <D> During performance of WO 01152144, the trailer inspection had a deficiency. Both the Hydrant Connect bags were missing. Additionally the tools contained in the bag were located in the front left cabinet of the trailer. <I> Informed CR. . This is a repeat DNC, refer to cross-referenced CR's. Create an action to resolve by either revising the inventory list or ensuring existing inventory is fully stocked. <N> Bldg 600 B.5.b trailer
389044 | CR | 20190120 | CAQ | D | Received BUS 73 GROUND alarm H13-P800.C1 6-6 | Y | Y |  | N | YES | <D> **** Detailed Description **** Received BUS 73 GROUND alarm H13-P800.C1 6-6. Investigation revealed the white ground indication lights extinguished for E-MC-7A and E-TR-7/73 Neutral Ground. The ground alarms will not reset. Also, the ground resistor is warm. <I> **** Actions Taken **** Notified the CRS and SM. Submitted CR and WR. | 02-00-E-MC-7A
389045 | CR | 20190121 |  | 4 | MT-ELEV-4 needs its fan turned on | N | N |  | N | YES | <D> **** Detailed Description **** The MT-ELEV-4 (RW elevator) fan is not running. This is controlled by a keylock switch on the elevator panel. Ops does not have these keys. Please turn the fan on. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW Bldg MT-ELEV-4 | 02-00-MT-ELEV-4
389046 | CR | 20190121 |  | 3 | Operations needs keys to MT-ELEV-4 | N | N |  | N | YES | <D> **** Detailed Description **** Operations needs keys for emergency operation of MT-ELEV-4, as required for fire brigade. Issue keys to be kept in RWCR. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW Elevator | 02-00-MT-ELEV-4
389048 | CR | 20190121 | CAQ | D | Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-3027. Alarm was due to high water level. Ref WO 02109735 | 02-00-CRD-HCU-3027
389049 | CR | 20190121 |  | 4 | Received 4.800.C2 7-7 Bus SL-63 GND. | N | N |  | N | YES | <D> **** Detailed Description **** Received 4.800.C2 7-7 Bus SL-63 GND. OPS3 reports the GND ins MC-6B. Ground was reset and is being investigated for source. <I> **** Actions Taken **** Followed ARP. | 02-00-E-MC-6B
389055 | CR | 20190121 |  | 4 | pwr-cra-2 festoon cable needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WR#29146704 â€œPWR-CRA-2 not operatingâ€, it was identified that several sections of its festoon cable were missing their jack chain (cable restraint device). The cables were stretched very tight in certain sections which may have caused the intermittent shorts and cleared the control fuse. The jack chain will have to be repaired at a minimum and the festoon cable will need inspected or repaired/replaced to prevent future failures during a high-RAD lift. <I> **** Actions Taken **** This AR/CR written to rectify and/or document this issue. Contacted HP & Laborers about these issues and actions to take in order to preclude future failures until repairs can be completed. <N> **** Equipment Description **** RW 437 Truck bay | 02-00-PWR-CRA-2
389059 | CR | 20190121 | CAQ | D | Received OFF GAS POST TREAT TROUBLE alarm | N | Y |  | N | YES | <D> **** Detailed Description **** Received OFF GAS POST TREAT TROUBLE alarm (H13-P602.A5, drop 5-2). Dispatched Chemistry to investigate.Chemistry reports that OFF GAS POST TREAT TROUBLE alarm (H13-P602.A5, drop 5-2) was due to the sample pump being off on OG-RIS -601A . The pump has been restarted. | 02-00-OG-RIS-601A
389061 | CR | 20190121 | CAQ | D | Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-1807 . Alarm was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear. | 02-00-CRD-HCU-1807
389063 | CR | 20190121 | CAQ | C | E528-47 drawing needs update per EC 17207 |  |  |  | N | NO | <D> **** Detailed Description **** Per 10.25.116 and WO#02134381-02 bench test of replacement motor for DLO-M-P/6, section 7.4 of 10.25.116 has steps to verify that E528 drawings match motor nameplate HP, FLA and Overload settings. Per EC 17207, pages 4-5, there are are some subtle differences in the new replacement motor that require updating on E528-47 drawing. Per the EC, the current fuse and overload protection installed is adequate for the new motor. <I> **** Actions Taken **** Notified Supervisor and Generate this CR per step 7.4 of 10.25.116 <N> **** Equipment Description **** DLO-M-P/6 replacement motor UTC 524314
389069 | CR | 20190121 | CAQ | C | (QA) Approval for CA due extensions not documented |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The due dates for two severity C AR-CR corrective actions were extended without documented supervisor approval. These assignments implement corrective actions to address issues identified during the 2018 NRC Triennial Fire Protection inspection. Extending corrective action due dates without approval challenges the supervisorâ€™s ability to ensure alignment on plant and department priorities and could lead to unpredictable performance. Factual Basis: 1. The following assignments were extended without documented supervisor approval in Asset Suite: o AS-CA 376281-01, Revise ABN-FIRE o AS-CA 379349-01, Revise pre-fire plan PFP-MN-XFMR-YD-MISC 2. SWP-CAP-01, Corrective Action Program, states the following for corrective action extensions: DOCUMENT the approval. IF the corrective action assignment is for a severity C AR-CR, THEN DOCUMENT the justification and the responsible group Supervisorâ€™s approval. <I> **** Actions Taken **** This issue is considered a deficiency identified during Quality surveillance SR-19-08. Recommend assignment to AR -TEFP. <N> **** Equipment Description **** N/A
389074 | CR | 20190121 |  | 4 | Steam leaks on WOA-HV-1 "K" and "P" coils | N | N |  | N | YES | <D> **** Detailed Description **** Steam leaks identified on WOA-HV-1 at "K" and "P' coils. <I> **** Actions Taken **** Notified PSRO | 02-00-WOA-HV-1
389076 | CR | 20190121 |  | 3 | WO tasks improperly requiring Operations authorizatioin |  |  |  | N | NO | <D> **** Detailed Description **** Two WO tasks on today's 'Pre-approval WO Tasks' list incorrectly require Ops authorization. One is WO 02115185 -14 and is a task to manufacture a gag device for a valve. The other is WO 02102710-02 which is a taks to build a container to transport equipment. It is common to get these and it holds up work for the involved craft and is a waste of time for the SRO having to authorize the work. This issue occurs regularly. <N> Both work orders identified as control communication = 1, which required operations to authorize the package. Recommend re-assigning to operations as a learning opportunity. WO 02115185-14 & 02102710-02, although they are support task, the Control Room Communication is set to '1', meaning that it is "HIgh Impact - Only PSRO/OPS may take to 48". The sofware is working as designed. Operations have the ability change the value during their Ops (CORC/WC) review.
389077 | CR | 20190121 |  | 3 | Spent Fuel Pool Chemistry sample results high | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** A sample of the Spent Fuel Pool was collected on 1/21/19 at 1110. The sample was taken 1 hour after starting RHR-B per SOP-FPC-ASSIST-ALT section 5.6 for spool piece flushes. This was performed as a proactive strategy to prevent issues with new fuel receipt. Sample results were as follows: Conductivity- 2.4 uS/cm, Normal Range LE 1.3 uS/cm; pH - 5.73, Normal Range 5.3 - 7.5; Chloride - 0.62 ppb, Normal Range LE 100 ppb; Sulfate - 1.61 ppb, Normal Range LE 100 ppb; TOC 75 ppb, Normal Range LE 400 ppb; Isotopic Co-60 1.03E-3 uCi/mL (Diagnostic) Isotopic activity GT 1E-3 requires monitoring for Iodine. There were no Iodine isotopes identified. All Normal Range values are per SWP-CHE-02 Table 6.5.12. The high conductivity is consistent with the Iron concentration and not a result of anions in the water. The Fuel Pool Cleanup has been started with FPC-DM-1A placed in at 14:20 on 1/21/19. Additional samples will be colllected to monitor the cleanup progress. Conductivity and Total Metals are in the Action Level per SWP-CHE-02 Table 6.5.12. This is not a Primary Chemistry Action Level, but instead a Diagnostic Parameter per BWRVIP-190 Table 3-4. <I> **** Actions Taken **** Informed Chemistry Supervision, Chemistry Manager and System Engineering.
389078 | CR | 20190121 | CAQ | C | Trend E-SL-73 ground alarms | Y | Y |  | N | YES | <D> **** Detailed Description **** On 1/21/2019 at about 1815 received bus 73 trouble, cause was a ground on MC-7A in and clear, 50gx relay reset. No other discrepencies found. <I> **** Actions Taken **** Performed cursory investigation, reset ground. Generated AR. | 02-00-E-MC-7A,02-00-E-SL-73
389079 | CR | 20190121 | CAQ | B | COND-V-119C - Change in Leakage Rate and Characteristics | N | N |  | N | YES | <C> RISK - Medium. CAUSE - Known. . As per the MRT, the causes are NOT known and are complex. Therefore, an investigation template is required. <D> **** Detailed Description **** The leak on COND-V-119C has changed over an hour period from a leak measured in GPM into a catch, to a spray that is almost reaching COND-P-2B. The leak is currently being captured by dams on the floor and directed into floor drains. The SM has initiated a management text and conference call to discuss the change in the leak. Videos are in EDMS showing the â€˜beforeâ€™ and â€˜after.â€™ <I> **** Actions Taken **** Management text and conference call. MCR is reviewing PPM 3.2.6 Power Maneuvering. . Reduce power to 65%, shutdown and isolated COND-P-2C. <N> Cause is Uncertain/Complex. Severity "B" with EQIT <R> This issue resulted in a Green Finding for failure to follow station proceddure, PPM 10.2.79, "Valve Packing and Live Loading," for maintiaining proper clearances of Chesterton packing. CCA [H.11 - Challenge the Unknown], as documented in IR 2019- 002. | 02-00-COND-V-119C
389080 | CR | 20190121 |  | 4 | WOA-HV-1 heating steam coil leak | N | N |  | N | YES | <C> Trend to CR 389074 <D> **** Detailed Description **** There is a heating steam coil leak in WOA-HV-1, with a plume of approximately 1ft. Recommend investigate and repair. <I> **** Actions Taken **** Informed MCR, generated AR/WR. | 02-00-WOA-HV-1
389081 | CR | 20190122 |  | 4 | XD-4 needs maintenance |  |  |  | N | YES | <D> **** Detailed Description **** SEC-XD-04 is not functioning as designed. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** unit removed from service, security notification made | 02-00-SEC-XD-4
389082 | CR | 20190122 |  | 4 | Camera TG21 not working |  |  |  | N | YES | <D> **** Detailed Description **** The STA/IA has a temp log to monitor the RFW-FCV-10 steam leak once per night shift with camera TG21. TG21 is failing to conect. | 02-00-RFW-FCV-10
389086 | CR | 20190122 | CAQ | D | M&TE Suspended/ Lost | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0063541 Monarch Portable Stroboscope- model Nova -Strobe last c/o 6/19/18 for job #02100668-02 by Elect's. Can't locate- Suspended/ Lost. EFIN Eval: Surveillance subsequetnly re-performed. No issue. DEF #6788A written. No Action Required <I> **** Actions Taken **** None Trending purposes only.
389087 | CR | 20190122 |  | 4 | COND-V-164C handwheel does not engage stem and operate valve | N | N |  | N | YES | <D> **** Detailed Description **** COND-V-164C handwheel does not engage stem and operate valve. Operation of this valve will be required in order to return COND-P-2C to service per SOP-COND-FILL section 5.12. | 02-00-COND-V-164C
389088 | CR | 20190122 |  | 3 | Lack of High Rad RWP for WO 02114493 |  |  |  | N | NO | <D> **** Detailed Description **** On 1/21/2019, Operations department performed WO 02114493 -05 to flush the FPC spoolpiece per SOP-FPC-ASSIST-ALT to support new fuel receipt inspections. This task requires entry into HRAs, LHRAs, and c-zones. THe majority of the procedure takes place in the RHR-B pump room and on the R548 in areas with elevated dose rates. There was no high radiation RWP specifically assigned for this work. Operations personnel utilized the Operations Department HRA RWP 30004389. A total of 61.5 mrem was received for performance of this job. Recommend future performance of this evolution, which will potentially be done again prior to the outage, be evaluated per the HRA RWP process. <I> **** Actions Taken **** Discussed with HP Lead Technician and SM.
389089 | CR | 20190122 |  | 3 | CBT for Hazardous an dmixed waste HZ000035 |  |  |  | N | NO | <D> **** Detailed Description **** The CBT references SWP-ENV-03 for obtaining information about universal waste labeling and storage. SWP-ENV-03 has been superseded by GBP-ENV-17. CBT should be updated to the current documents.
389093 | CR | 20190122 |  | 4 | TOA-FL-2B is near EOR with clean media. | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FL-2B is near EOR with clean media on the take up spool. Please replace/recycle media. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 501W | 02-00-TOA-FL-2B
389094 | CR | 20190122 | CAQ | D | OG-SR-3 gages readings low | Y | Y |  | N | YES | <D> **** Detailed Description **** While performing CI-15.2 Daily Chemistry Monitor checks. On OG-SR-3 ( Off Gas Pre Treatment Sample Rack) found OG -FIC-3/2 flow @ 25 mm. Required to be between 51- 93 mm. Found OG-PI-3/10 @ 2" HG Vac. Normally ~20" Hg Vacuum.. <I> **** Actions Taken **** Per CI-15.2 tried to adjust flow of OG-FI-3/2 to between 51 - 93 mm, but would not respond to adjustment. Did not notice any moisture obstructing the flow in gage. OG-PI -3/10 was reading 2" HG Vac and should be ~20"Hg Vac. Verified line-up of OG pre-treatment system per PPM 12.5.23A Valve Line-up was correct.as well as valve line-up on OG-SR-4. Verified OG-RIS-612 was reading normal (20 mr/hr) for Rx @ 70% power. Contacted Chemistry Specialist. . <N> **** Equipment Description **** OG-SR-3. TG 441' Chemistry Sample Room. | 02-00-OG-FI-3/2,02-00-OG-PI-3/10,02-00-OG-SR-3
389096 | CR | 20190122 | CAQ | D | RHR-V-104 difficult to operate. | Y | Y |  | Y | YES | <D> **** Detailed Description **** During the performance of SOP-FPC-ASSIST-ALT on 1/21/19, RHR-V-104 was very difficult to operate. 2 operators were required and 1/4 of the total dose received by the operators for the entire job resulted trom operating this valve. ( Total dose 63 mrem ). Recommend packing adjustment and/or lubricate stem. This is an important ALARA consideration as pointed out by the SSS. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** Rx 548 | 02-00-RHR-V-104
389098 | CR | 20190122 |  | 3 | High temperature in glycol system with no refrigeration on | N | N |  | N | YES | <D> **** Detailed Description **** High temperature in glycol system and no glycol refrigeration machines will start in auto or from the main control room. GY-TRS-630 indicated 39F and up slow. OG-RF -20A and OG-RF-20C failed to auto start. Attempted to start OG-RF-20A and OG-RF-20C per ARP however neither will turn on. OPS 2 reports that OG-RF-20C was making sounds like it was attempting to start however will not turn on. Locally GY-TI-18 indicates 40F and OG-TIC-17 reads 35.5F. OG-RF-20B is danger tagged off. H13.P672.A9 drop 1-10 is locked in in the MCR. Several CRâ€™s are written on the system for various issues. WR 29144927/WR29146628/AR377420 | 02-00-OG-RF-20A
389100 | CR | 20190122 |  | 3 | PPM 1.5.18 additional required changes |  |  |  | N | NO | <D> **** Detailed Description **** The current revision of PPM 1.5.18 has steps to take once the equipment is restored to a functional status or returned to its normal staging area (step 6.1.3) that were never directed to be taken when the equipment was made non-functional or removed from its normal staging area. Some actions that were in step 6.1.5 of the last revision could be removed based on now having LCS 1.11.1 but the new revisions 6.1.3 would need to parallel those actions. Also, CR 388229 should be looked at and addressed at the same time as this CR.
389101 | CR | 20190122 |  | 4 | OG-TR-640A shows E200 error and has stoped recording data | N | N |  | N | YES | <D> **** Detailed Description **** OG-TR-640A shows E200 error and has stoped recording data for channels A&C. Channel A&C are still displaying data. Please investigate and correct. <I> **** Actions Taken **** Wrote this CR to attempt to drive resoloution. | 02-00-OG-TR-640A
389102 | CR | 20190122 |  | 3 | work steps not created to install fuse DW-FI-1 | N | N |  | N | NO | <D> **** Detailed Description **** During the performance of WO#02095007-11, electricians terminated wiring associated with new ultrasonic flow transmitter (DW-FI-1). The conduit wire-ways and junction boxes were installed in a separate task. Junction box E -TB-GSB/1 was installed to splice 120volt power fed from E-LP-1CF. Within E-TB-GSB/1, there is a Fused term block (F1) and an unfused term block (TB1-1). Wiring was terminated per work instructions, but there does not appear to be a task, or clearance order step, to close in the fused link at Term block (F1). <I> **** Actions Taken **** notified Supervisor, write CR and WR to close in fusible link at Term Block (F1) at E-TB-GSB/1 <N> **** Equipment Description **** S 420 GSB 420 within Radiation Area.
389103 | CR | 20190122 |  | 4 | WO 02116147-05 not completed as scheduled - adherence hit | N | N |  | N | NO | <D> **** Detailed Description **** WO 02116147-05 - Configure factory refurbished breaker for E-CB-S/6 did not complete as scheduled due to failed as found testing. WR 29146623 was generated to provide troubleshooting direction. <I> **** Actions Taken **** Notified WWM, RM and Eng. Contacted vendor. Troubleshooting has not revealed direct cause of failure. <N> **** Equipment Description **** RW487 breaker shop
389105 | CR | 20190122 | CAQ | D | FP-V-39 Requires Replacement | N | N |  | N | YES | <D> **** Detailed Description **** During performance of a Fire Protection System Vulnerability evaluation during the 1-14-19 work week, it was identified through interviews with several Equipment Operators that FP-V-39 is extremely difficult to operate. . Equipment Operators involved with lifting clearance C-FP -CP-FSP-7-001, WO 02089265, EC 13537 identified FP-V-39 was extremely difficult to operate. Upon further investigation the FP System Vulnerability Evaluation assessment group was able to determine that this is a difficult valve for different equipment operators to operate. . This CR is to create a WR/WO to replace FP-V-39. . FP-V-39, although difficult to operate (degraded), can still perform itâ€™s design function of providing isolation of Pre-Action 65 suppression system. FP-V-39 is currently functional. <I> **** Actions Taken **** Initiated CR to create WR/WO. <N> **** Equipment Description **** Cable Spread Sprinkler Supply(P65 Supply) Location - W 504 J0/14.8 | 02-00-FP-V-39
389106 | CR | 20190122 |  | 3 | RWCU-V-213A NEW PLUG NOT LIKE FOR LIKE | N | N |  | N | NO | <D> **** Detailed Description **** While performing repair activities on RWCU-V-213A it was discovered that the new plug did not match the plug that was removed from the valve. The new plug has a divider in the center creating 2 orifices. The plug removed from the valve is full bore with no divider. The plug removed from the valve is scored and pitted on the sealing surface. The other new plug in stock has the same divider in it (CID 19472). See attached pictures in EDMS. <I> **** Actions Taken **** Informed Work Week Manager of potential delay.
389109 | CR | 20190122 | CAQ | D | CRA-42-7B5B control power terminal block disconnected | Y | Y |  | N | YES | <D> **** Detailed Description **** During replacement of MCC bucket CRA-42-7B5C (CRA-FN-2A1), the bottom segment of the control power terminal block (terminal points 12, 13 & 14) in MCC bucket CRA-42-7B5B (CRA-FN-2A2) was found to be disconnected. This bucket is the old ITE style with a â€œpull apartâ€ type terminal block; each section of 3 terminal points can be disconnected separately (see attached picture in EDMS). CRA-42-7B5B (CRA-FN-2A2) is currently in service. CRA-42-7B5C (CRA-FN-2A1) is currently OOS for replacement. Some of the existing power wiring for the bucket, routed in the MCC wire way, is also being replaced. Per drawings EWD-23E-009 and EWD-11E-025, this wiring affects annununciator H1, 1-1 (CRA-FC-2A TRIP) and RCC-V-72A fan interlock circuitry. <I> **** Actions Taken **** Contacted Production SRO and wrote CR. | 02-00-CRA-42-7B5B
389110 | CR | 20190122 |  | 3 | boundaries at RX 501 elevation need clarification |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** While recently walking through the Reactor building at the 501' elevation, I noticed two separate areas that have red/white striped tape adhered to the floor. It appears to be somewhat new installation and has no signage as to what the boundary is/protects. The red/white stripes are consistent with sensitive areas, such as instrument racks, but there aren't any signage associated. the first area is just inside the RX building from the main corridor at J/8 and the second area is in front of MC-8C at L/4. It appears that either the wrong boundary color has been used, or the proper signage is missing. see pictures. I will attach a picture of typical signage for "sensitive equipment' areas. the other two pictures are the actual affected areas. <I> **** Actions Taken **** notified Supervision and write CR <N> **** Equipment Description **** RX 501 J/8 and L/4
389111 | CR | 20190122 | CAQ | C | CRD-LT-13C cover not tightened metal to metal as required | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of ISP-CRD-X304 per WO # 02118830, step 7.1.53 that states cover is tightened metal to metal was not followed. See WO closure notes and CR-388951. This issue is documented in CR-384850-01 closure notes, 3150 series transmitters installed in EQ applications, the Rosemount specified torque requirements must be met to maintain the qualification of the transmitter. <I> **** Actions Taken **** Informed supervision. See attached e-mail in EDMS. | 02-00-CRD-LT-13C
389115 | CR | 20190122 | CAQ | B | Unexpected alarms during ISP-MS-X315 | Y | N |  | N | YES | <C> RISK - MEDIUM CAUSE - Uncertain or Complex. The issue in this CR will be addressed in CR 388934 <D> **** Detailed Description **** During performance of ISP-MS-X315, at step 7.1.18 during DMM installation, MS-LS-300D and MS-LIS-200D gross fail tripped unexpectedly. H13-P603.A8-5.1 SDV OR GROUP 1, 2, 3, 4, 7 ISOLATION TRIP UNIT TROUBLE along with H13-P601.A11 -5.3 MSIV HALF TRIP SYSTEM B was tripped at the same time along with associated MSIV SYSTEM B inboard and outboard bus B lamps extinguished. Operations and supervision were contacted and permission was given to reset gross fail on MS-LIS-200D and MS-LS-300D and operations reset NS4 logic. All annunciators cleared and reset accordingly. The procedure was N/Aed with SM and supervisor concurrence and used to back out and restore the system. <I> **** Actions Taken **** Contacted supervision, operations, used restoration steps in ISP-MS-X315, wrote CR. <N> **** Equipment Description **** RX 522 E-IR-H22-P027 . Due to the correlation (unexpected RC-2 Half Trip) between the event described in this CR and CR 388934, the evaluation for this CR will be bounded by the EQIT performed in CR 388934 and this CR will be resolved by CR 388934. POD is documented and attached to EDMS under 388934. No additional acitons required. | 02-00-MS-LT-61D
389116 | CR | 20190122 |  | 3 | Energy Northwest Work Trailer Damage |  |  |  | N | NO | <D> **** Detailed Description **** Trailer tongue a-frame was bent following the loading of scaffold materials (Pictures in EDMS). Shortly after loading the material and during vehicle movement (approximately 10â€™) the trailer A-frame bent at the trailer/A-frame connection location. Scaffold materials were off-loaded and the trailer was move up to building 32 vehicle yard. Approximately 8,700 LBS. (calculated after loading) of scaffold material was loaded onto the trailer with a GVW Rating of 9,990 LBS. The tire load capacity of the trailer is 7,170 LBS. which is the max load capacity of the trailer. Each axle is rated at 4,995 LBS. According to Great Northern Trailer, the manufacturer of the trailer, the trailer should only have been loaded not exceed the 7,170 load capacity. They also stated the tongue weight should not exceed 10-15% of the load being hauled. . Based on the information gatherd, it appears this is a Knowledge based error as opposed to Human Performance related. <I> **** Actions Taken **** Off-loaded trailer and moved it to the yard at building #32. Tagged trailer â€œDO NOT USEâ€. Notified the Plant General Manager, Maintenance Manager, Reactor and Major Maintenance Manager, Industrial Safety Manager, Facilities Department Manager and Operations (OI-34 screening). Initiated Form 23174 per ISPM-1 and routed per ISPM-1. Looked in ISPMâ€™s to see if they contained information regarding trailer use; nothing found. Benched personnel associated with this event. <N> Williams Plant Services
389118 | CR | 20190122 |  | 4 | CW-CT-1B Fans | N | N |  | N | YES | <D> **** Detailed Description **** CW fans on CT-1B may be having an oil contamination issue Fan 10 has very black oil as opposed to the normal yellow color and two others are darker than normal. <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-CW-FN-10
389119 | CR | 20190122 | CAQ | D | HT-HTP-FP/7 | Y | Y |  | N | YES | <D> **** Detailed Description **** low temperature light blinking on ckt 1F <I> **** Actions Taken **** initiated CR/WR informed MCR | 02-00-HT-HTP-FP/7
389120 | CR | 20190122 |  | 4 | RFT-SE-99T2/1A2 behaving erratically at speeds LT 4200 RPM | N | N |  | N | YES | <D> **** Detailed Description **** The signal from RFT-SE-99T2/1A2, one of the four RFT A speed probes, is noted to deviate considerably from the other three probe signals when RFT speed is less than 4200 RPM. The delta between RFT speed and RFT-SE-99T2/1A2 signal appears to grow as RFT speed lowers â€“ the signal has been observed as low as 400 RPM lower than RFT speed (see EDMS for eDNA plot). The erratic signal currently has no impact on RFT speed control because the RFT governor control system selects the second highest signal from all four probe signals. Recommend replacing the probe at the next opportunity. | 02-00-RFT-SE-99T2/1A2
389122 | CR | 20190122 |  | 4 | SA-C-1 Compressor and Fan Wire Termination Label Issue | N | N |  | N | YES | <D> **** Detailed Description **** In performance of WO# 02091976-01, It was discovered that the the load side of the compressor starter and fan starter were labeled backwards. 1T1, 1T2,1T3 should be labeled under the larger compressor starter. 2T1, 2T2, 2T3 should be labeled under the smaller fan starter. Verfied against the plant print, and the print on the inside of the door. This is just a labeling issue, and not an operability issue. <I> **** Actions Taken **** Notified supervision of the discrepancy, and re-validated the findings with him. Informed Engineering that a CR was going to be written. Took pictures (attaching to this CR). Validated the wires coming off the small starter went to the fan, and the wires off the larger starter went to the compressor. Wrote a AR/CR to document the finding. <N> **** Equipment Description **** Electrical cabinet inside SA-C-1 | 02-00-SA-M-C/1,02-00-SA-M-FN/2
389124 | CR | 20190122 | CAQ | D | HIgh water level HCU 2603. | Y | N |  | N | YES | <D> **** Detailed Description **** Recieved HIgh water level HCU 2603. OPS 2 corrected this issue. <I> **** Actions Taken **** Followed ARP | 02-00-CRD-HCU-2603
389125 | CR | 20190122 | CAQ | D | FLEX Building 82 has roof leak above FLEX-GEN-B82 | N | Y |  | N | YES | <D> **** Detailed Description **** While performing an inventory verification of FLEX components in FLEX Building 82 it was noted that there is a leak around the exhaust pipe that extends from FLEX-GEN-B82 house generator through the roof. This leak is active and is onto the top of the generator cabinet. Some droplets are collecting on the floor around the generator. The generator cabinet was opened and it was verified that no water is presently getting into the cabinet and onto energized equipment. This leak need to be repaired before it does become a problem with the generator. Corrosion staining of the pipe suggests the leak has existed for a while. <I> **** Actions Taken **** Discussed with Supervisor, Manager and Shift Manager. <N> **** Equipment Description **** FLEX Building 82 | 02-CM-FLEX-GEN-B-82
389127 | CR | 20190123 |  | 4 | Oil in RW Elevator South Door Track | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** There is an oil build up in the tracks of the south door of the RW Elevator. There is also oil on the wall below the control panel inside the elevator. Possibly coming from behind the door wall. It is not on the floor causing a slipping hazard but may if the track fills up. <I> **** Actions Taken **** Initiated CR Verified it was not a slipping hazard at this time
389130 | CR | 20190123 |  | 3 | Provide training for Seal Steam Pneumatic controllers |  |  |  | N | NO | <D> **** Detailed Description **** Provide training for Seal Steam Pneumatic controllers: Fisher C1, 4160, 4150 and 1348H series (i.e. SS-PC-4E). These controllers are infrequently worked on and are unusual in their configuration. Also, they use a reverse regulator on the input that usually causes confusion during maintenance. Traditionally, we struggle with these during power ascension. Clarification of calibration, system interface, and adjustments during power ascension is needed. Also, 10.24.121 should be revised, during training, to assure we have the procedural steps needed to efficiently work on this device during a bench calibration OR field tuning adjustment. <I> **** Actions Taken **** wrote this AR
389131 | CR | 20190123 |  | 4 | Sealing compound not in inventory |  |  |  | N | NO | <D> **** Detailed Description **** Sealing compound CID 17216 was not inventory when potentially needed for repairs of COND-V-119C. When notified of the need, SCS located material in WA and arranged for delivery within one day. Recommend category 4 to AR-SCS <I> **** Actions Taken **** material was procured and will be stocked. discussed with Purchaing material specialists who took actions needed to expedite delivery
389132 | CR | 20190123 |  | 4 | Leakage past COND-V-120C | N | N |  | N | YES | <D> **** Detailed Description **** During maintenance on COND-V-119C it was identified that there is leakage past either COND-V-120C or COND-V-601C. Most likely the leakage is past COND-V-120C. The leakage is approximately 5-10 gpm. <I> **** Actions Taken **** Initiated CR. | 02-00-COND-V-120C
389137 | CR | 20190123 |  | 3 | PPM 10.25.60 requires revision |  |  |  | N | NO | <D> **** Detailed Description **** E-PP-ASD-1/2 supplies power to RRC-IMD-ASD-1A/2 and RRC -IMD-ASD-1B/2. E-PP-ASD-1/1 supplies power to RRC-IMD -ASD-1A/1 and RRC-IMD-ASD-1B/1. Please correct. <I> **** Actions Taken **** Checked change against ABN-INV-ASD. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
389140 | CR | 20190123 |  | 3 | Mobile cranes running without operator |  |  |  | N | NO | <D> **** Detailed Description **** On 01/22/19, Training observed two mobile cranes left running with no operators in sight next to Building 238. See EDMS for pictures. After looking around the job site, the crew (one ENW employee and Lampson personnel) were found in the adjacent Building 186 on a break. In discussion, rationale for why the practice was okay included the need to maintain the cranesâ€™ hydraulic system pressure, outriggers were in place, work being performed outside the owner controlled area. While no specific standard in ISPM-5 or 19 appears to prohibit this practice, it begs the question if this is the safest way to work and if site standards & expectations need to be clarified. This CR is being written to drive such evaluation/clarification. <I> **** Actions Taken **** Training rep notified Facilities, Site Rigging Coordinator, and Maintenance Training Superivsor. CR initiated. <N> ISPM-19 contains guidance that "Vehicles should not be left unattended while the motor is running", section 3.7.5. By definition a mobile crane is a vehicle. Additionally WAC 296-155-53401(7)(w) Says that the engine shall be stopped before leaving a crane unattended. There is an exception, limited to line of sight. Deviations from our ISPM-19 standard must be approved via ISPM-14. See EDMS.
389153 | CR | 20190123 | CAQ | D | E-RLY-RHRB/62/2 as-found out of tolerance per LCS req. | Y | Y |  | N | YES | <D> **** Detailed Description **** While performing ESP-RLYRHRB622-B301 E-RLY-RHRB/62/2 was as-found out of tolerance for the LCS requirement( 19.74 to 20.03 seconds) at 21.40 seconds. Relay operated but was out of tolerance. Adjusted the time dial and brought the timing within tolerance. As left time is now 19.05 seconds. <I> **** Actions Taken **** Notified CRS and supervision <N> **** Equipment Description **** sm8 | 02-00-E-RLY-RHRB/62/2
389160 | CR | 20190123 |  | 3 | DataGlance Training Region Unavailability Delayed Training |  |  |  | N | NO | <D> **** Detailed Description **** Unavailability of the training region of DataGlance resulted in a 1 hour delay of scheduled non-accredited Instructor training pilot session. <I> **** Actions Taken **** Informed IS training region of DataGlance was unavailable. <N> During the IS maintenance outage on 1/17, work had been performed which impacted the database schemas associated with the DataGlance training environment. A backup copy of the schemas was restored to the database, Tomcat was restarted, and the application was available again.
389161 | CR | 20190123 |  | 3 | SOP-CST-DRAIN requires further enhancment |  |  |  | N | NO | <D> **** Detailed Description **** AR 375199 appears to have intended that rain water be directed to the storm drains. P&L 4.9 as well as the first note in section 5.1 still discuss sending a small amount of water to T-4 to prevent slip hazards. Rain water is generally a small amount of water. This procedure needs better alignment with the intended use of the lined evaporation ponds.
389163 | CR | 20190123 | CAQ | C | FSAR 2.2.2.5 revision |  |  |  | N | NO | <D> **** Detailed Description **** FSAR section 2.2.2.5 describes Vista Field as an airport operated by the Port of Kennewick. Vista Field is no longer an active airport. Recommend revising FSAR 2.2.2.5 to remove references to Vista Field. <I> **** Actions Taken **** Contacted Licensing regarding the recommended revision.
389165 | CR | 20190123 |  | 3 | CVI DCR 1215-00,2 information outdated, needs revised |  |  |  | N | NO | <D> **** Detailed Description **** CVI DCR 1215-00,2 includes an outdated revision (Rev. 0) of the LEFM Uncertainty Analysis (dated 3/6/2014) and does not include the latest revision (Rev. 3 dated 12/23/2015). The Vendor Design Criteria document should be updated with the correct revision of ER-1049 â€œBounding Uncertainty Analysis for Thermal Power Determination at Columbia Nuclear Generating Station Using the LEFM Check +M Systemâ€ which is part of the basis for the stationâ€™s MUR uprate. This is a documentation issue only and has no impact on LEFM operation.
389166 | CR | 20190123 |  | 3 | Found unattached ground cable | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Noticed a ground cable exposed and unattched near the South side of the Alpha Service Water pumphouse. One end is attached to the metal stairase/walkover. The other side is unattched with a fitting crimped to the end. See pictures <I> **** Actions Taken **** Took pictures, cleared the area, notifiied supervisor Appears to be a temporary ground cable. Not associated with permanent ground on any SW / safety related components.
389169 | CR | 20190123 |  | 3 | IS: Possible data corruption on Server122. |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Discovered possible data corruption on Server122's filesystem "/ora-prod-misc". Reliable diagnosing of the problem requires all databases on this server to be shutdown. If corruption is found, then fixing also requires all databases to be shutdown. <I> **** Actions Taken **** Users have been notified and approved shutdown. Work plan written.
389170 | CR | 20190123 | CAQ | C | RHR-M-V/73A motor is classified as AQ in Portal J |  |  |  | N | NO | <D> **** Detailed Description **** Portal J identifies RHR-M-V/73A motor safety classif ias AQ. However the actautor, valve, and electrical components (including cable and supply) are safety related. The motor's spare parts are identified as safety related. The actuator is a Limitorque SMC, which means the motor is intergal to the actuator. The motor can be replaced in piece parts. <I> **** Actions Taken **** This issue is related to the classification of the motor and is not related to installed plant equipment. <N> The same condition also exists for RHR-M-V/73B. . Per Asset Suite and CERs C91-0293 and C91-0369, RHR-M-V/73A, B, 74A and B (motor) is nonsafety related even though both the associated valves and operators are safety related. This is because the safety function of the valves is to stay closed (they are normally closed) and to ensure pressure integrity. The operators are not required to perform any safety function during or following a design basis accident but do support operator information and system status monitoring. The motors therefore do not perform a safety function; they are however powered from safety related MCCs E-MC-7BB and E-MC-8BB but have 3 pole disconnect switches normally open which provide circuit isolation and electrical integrity. Based on this information and discussion/concurrence with design engineers and design supervisor, Asset Suite information is correct as is.
389172 | CR | 20190123 |  | 3 | New Procedure Request for HCU Trouble Alarm Response |  |  |  | N | NO | <D> **** Detailed Description **** Attached to EDMS is a draft for a new Quick Card to be used by operators in response to an HCU trouble alarm <I> **** Actions Taken **** Informed Supervision
389173 | CR | 20190123 |  | 3 | New Procedure Request for HCU N2 Bottles |  |  |  | N | NO | <D> **** Detailed Description **** Attached to EDMS is a draft for a new Quick Card to be used by operators to change out HCU Nitrogen Bottles <I> **** Actions Taken **** Informed Supervision
389174 | CR | 20190123 | CAQ | D | Unaccounted voltages in TB-SW1541 in SWPHA | N | Y |  | N | YES | <D> **** Detailed Description **** TB-SW1541 ground to shield in cable TB-SW1540 there is 0.3vdc. Found approximately 0.5vdc on SW-TE-2A and SW-TE -2D to ground on incoming leads to SW-RMS-TI/2A <I> **** Actions Taken **** Notified Engineering and Supervisor | 02-00-SW-TE-2A,02-00-SW-TE-2D
389175 | CR | 20190123 | CAQ | D | MW 67 XTMR JB Tamper | N | N |  | N | YES | <D> **** Detailed Description **** High alarm rate on MW 67 jb tamper <I> **** Actions Taken **** Compensatory measure put in place. Not reportable. | 02-00-SEC-MW-ISFSI/67AT
389176 | CR | 20190123 |  | 4 | Heat Trace CST 3F | N | N |  | N | NO | <D> **** Detailed Description **** While perfoming WO 02098263-01 four year pm on Heat Trace HT-HTP-FP/5 Zone 3F the heat cable wire insulation was found cracked and brittle while performing Step 7.1.4 of 10.25.213. <I> **** Actions Taken **** Repaired with Raychem per Supervision on 1-23-19 and performed the applicable section of 10.24.213. All SAT. <N> **** Equipment Description **** HT-HTP-FP/5 Zone 3F CST pit
389177 | CR | 20190123 |  | 3 | SAM Calibration source has decayed below recommended value |  |  |  | N | NO | <D> **** Detailed Description **** The SAM (Small Article Monitors) Calibration source (ID 10 -195E) activity has decayed below the low value recommended in HPI-12.100, SAM-12 Calibration. The source strength is currently 0.26 uCi ( 0.3 uCi when rounded), however HPI 012.100 states the source should be greater than 0.3 but no more than 1.0 uCi. The source is therefore not greater than 0.3 uCi currently stated in procedure. This slight difference does not affect the SAM calibration, as it is only a recommendation to maintain optimum activity for good measurement statistics over a useful activity range. This range is due to relatively short halflife of Co60 (5.2 years) and useful lifespan of only about 7-10 years between replacements. <I> **** Actions Taken **** Contacted RP Supervision and discussed. Replaced source used for calibration with a more desirable higher activity (0.65 uCi) Co60 calibration source from inventory, 16-301E, that is also used for GEM-5 Gamma Portal Monitor calibrations. Initiated procedure changes in APPW for HPI -12.100 and HPI-12.63 to add clarification to guidance. A review of data following the most recent SAM calibration with the new source 16-301E compare to previous 10-195E source was about 1%, or less, deviation from previous calibrations/source.
389179 | CR | 20190123 | CAQ | C | Discrepancy in RSM title in the FSAR |  |  |  | N | NO | <D> **** Detailed Description **** LDCN-17-001 changed the the Chemistry/Radiological Safety Manager title to Chemistry/Radiological Services Manager. The change was missed in one location on page 12.5-1. <I> **** Actions Taken **** CR written. The correction will be included in LDCN-18-030 AR 00384463.
389180 | CR | 20190123 |  | 4 | HD-LIC-5B21 found with no level and zero demand at 75% power | N | N |  | N | YES | <D> **** Detailed Description **** During system walkdown HD-LIC-5B21 was found offscale low with zero valve demand. HD-LIC-5A21 was level was noted to be near setpoint with ~15% demand as expected. Previous december walkdown at 100% power noted both of these controllers to be maintaining level with a 14-18% demand. Loop calibration may be needed for HD-LIC -5B21. <I> **** Actions Taken **** Informed CRS. <N> **** Equipment Description **** W 501' K0/10.5 (E-CP-H13/P835) Control Room | 02-00-HD-LIC-5B21
389181 | CR | 20190123 |  | 4 | Esoms clearance order causing work delays. |  |  |  | N | NO | <D> **** Detailed Description **** Both Electrical and Mechanical Maintenance experienced delays in signing on clearance orders which caused delays to starting work. ESOMs module lead was contacted with the issues associated with accepting clearance order, and in both cases, the passwords were reset and access to ESOMs became avialalbe for maintenance personnel. <I> **** Actions Taken **** Generated CR to document delays in work due to ESOMS.
389182 | CR | 20190123 | CAQ | C | Extent of Condition For RC-2 Trips and Isolations | Y | N |  | N | YES | <C> This CR to be closed under AR-CR 388934 <D> **** Detailed Description **** Based on events or Operating Experience associated with RC-2 half trips during surveillances or field work in proximity to these circuits (AR 00365352 on 5/16/17, AR 00388934 on 1/16/19 and AR 00389115 on 01/22/19) there is reasonable assurance that a common sensitivity issue exists within the cable/termination scheme (Ref WO 02138131). These problems started shortly during and after the implementation of EC 12271. Condition Report history search supports the EC relation of RC-2 trips coming in, in relation to the circuit chain. Surveillances and Calibrations of all components within the Extent of Condition have been proven to perform their functions. This issue is cable/termination associated. Detailed evaluation attached to EDMS <I> **** Actions Taken **** Extent of Condition CR was requested Notified SM, EFIN Supervisor and Systems Engineering Manager <N> Due to the correlation (unexpected RC-2 Half Trip) between the extent of condition described in this CR and CR 388934, the evaluation for this CR will be bounded by the EQIT performed in CR388934 and this CR will be resolved by CR 388934. Extent of condition write up is attached to EDMS. | 02-00-E-IR-P004,02-00-E-IR-P026,02-00-E-IR-P027
389183 | CR | 20190123 |  | 3 | Maintenance found no graphite bushing in the COND-V-119C | N | N |  | N | YES | <D> **** Detailed Description **** Maintenance found no graphite bushing in the COND-V-119C stuffing box. The valve packing datasheet for this valve from WO 02072877-01 (performed in R23) directed the use of a 0.188 (3/16â€) carbon bushing below 5 rings of packing. After contacting the packing vendor Chesterton, they recommended the lower carbon bushing to be 1.5 times the height of the packing rings, which would be a carbon bushing that is ~0.468â€ thick. The thinner bushing either failed or was never installed (this is a potential cause of the packing leakage increase). The depth of the stuffing box would not allow the use of a 0.468â€ thick carbon bushing and 5 rings of packing. Instead, the vendor approved the use of one ring of braided Chesterton 1601 packing (CID 17802) to replace the carbon bushing and the normal 5 rings of packing (2 rings of CID 37137 and 3 rings of CID 56306306). The torque was increased on the gland nuts to from 10 to 13 ft-lbs which was also approved by the vendor. This value is the midpoint between the preferred torque of 10 ft-lbs and the maximum torque of 16 ft-lbs. The packing set used did not meet the tolerance specified in PPM 10.2.79 Step 4.13. This was also discussed with the vendor and while not preferred was deemed to be acceptable based on performance since R23 with the same packing set. The vendor provided part numbers for the correct packing set. Recommend updating the packing datasheet in seal pro and in WO 02042797 for the valve rebuild. <I> **** Actions Taken **** contacted vendor, OCC, EOC Amended packing data sheet for repacking wo 02138264 | 02-00-COND-V-119C
389185 | CR | 20190123 |  | 4 | Packing Leak from COND-FCV-15C | N | N |  | N | YES | <D> **** Detailed Description **** While starting COND-P-2C for PMT, a packing leak was noted on COND-FCV-15C. While a leak was already documented in CR 370397 as being ~1 drop/second, the leak has progressed to about 2.5 drops/sec (video loaded to EDMS). This CR is being generated to document the leak rate for trending purposes. <I> **** Actions Taken **** Notified SM. | 02-00-COND-FCV-15C
389186 | CR | 20190124 |  | 4 | 1A FWH not responding as expected when placing in service | N | N |  | N | YES | <D> **** Detailed Description **** While recovering the 1A FWH on 1/23/2019 the heaterâ€™s response was not as expected. Per SOP-FWH-START placing HD-LIC-1A to 1-2% less than the recorded value from when the heater was removed from service should give adequate level rise. The logged value when the 1A FWH was removed was a demand signal of 95% when removed per SOP-FWH -SHUTDOWN. Demand on HD-LIC-1A was at 70% when hotwell level began slowly lowering, an indication that the FWH was filling up. After the controller was placed in automatic control per SOP-FWH-START the level swings displayed by the FWH was significantly more pronounced that the 1B or 1C FWHs when they were placed online shortly after. Once HD -LIC-1A established the level set point of -1â€ the level stabilized and appeared to be operating normally with the exception that demand was roughly 30% more than the 1B and1C FWHs. The normal demand for HD-LIC-1A is 90-95% open where as both HD-LIC-1B and HD-LIC-1C operate around 60% open to maintain level. <I> **** Actions Taken **** Informed MCR | 02-00-HD-LIC-1A
389187 | CR | 20190124 |  | 4 | Poor Lighting in Reactor Buiding 422' RCIC Room. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Poor lighting in RX422' RCIC Room. <I> **** Actions Taken **** Notified HP Lead Technician. Esoms Log Entry. Initiate CR/WR. <N> **** Equipment Description **** RX422' RCIC
389192 | CR | 20190124 | CAQ | D | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #C003954 Shopmade ARM Power Supply passed Calibration and now Rejected- No Longer Needed. No plant Impact. DEF #6790A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
389193 | CR | 20190124 |  | 3 | Evaluate removing the old main xfmrs from the yard |  |  |  | N | NO | <D> **** Detailed Description **** A decision with funding needs to be made on removing the old main transformers from the staging pads in the transformer yard. Currently there is no funding for this activity and it will require quite a bit of money to move these transformers out of the yard. This currently represents additional costs on projects for future transformer replacements and it will impact those budgets to remove these transformers.
389198 | CR | 20190124 |  | 4 | 4th Qtr 2018 Security Training |  |  |  | N | NO | <D> **** Detailed Description **** There were zero failures on the Security Annual Written Tests conducted during 4th Quarter 2018 Training. This CR is for trending purposes only. <I> **** Actions Taken **** CR Submitted. Specific data placed into 4th Quarter End of Cycle Review.
389199 | CR | 20190124 |  | 4 | EWP library with incorrect Procedure Revision |  |  |  | N | NO | <D> **** Detailed Description **** Craft noticed while pulling ISPM-20 into a work order from EPP to the tablet that the procedure was two revisions old. The metadata was downloaded back in march of 2018. The file name on the procedure when pulled up on EWP is â€œELECTRICAL SAFETY, ARC PROTECTION WORK PRACTICESâ€ not â€œISPM-20â€. When the validation was checked with the tablet it said â€œ All documents validâ€. When the task was validated on Dataglance the procedure was not able to validate and work was not started until the document was removed. <I> **** Actions Taken **** Contacted supervion(Craft MNT Supervisor) and EWP support (Project Manager Maintenance). When the task was validated on Dataglance the procedure was not able to validate and work was not started until the document was removed. See EDMS for pictures. IAW SWP-CAP-01 - Removed names. <N> **** Equipment Description **** .
389204 | CR | 20190124 | CAQ | C | Offgas valves found out of expected position | Y | Y |  | N | NO | <D> **** Detailed Description **** During a check of offgas sample flow Chemistry found two offgas sample rack trap drain valves OG-V-3/7 and OG-V-3/8 open. These are normally closed valves that are opened manually to drain excess water when needed. <I> **** Actions Taken **** Directed the Shift Chemistry Technician to close the two trap drain valves per SOP-OG-LU.
389206 | CR | 20190124 |  | 4 | Unable to process IMDS. Revision already in Asset Suite |  |  |  | N | NO | <D> **** Detailed Description **** Document Control received an IMDS to process from HP. The paperwork says it was revision 35 but there is already a revision 35 in the system. <I> **** Actions Taken **** Notified my Supervision. Wrote CR and notified Org 52212. Returned document to sender with CR attached.
389208 | CR | 20190124 |  | 3 | Environmental Stewardship Program Cost Savings NALCO |  |  |  | N | YES | <D> **** Detailed Description **** WO 02126440 needs to be modified prior to DG2 window to prevent release of NALCO. As a cost savings and to align with our ESP the DCW engine coolant shall no longer be free released as it has for the past 30 years . Coolant shall be reused as long as chemistry parameters are in spec. This is applicable for DG1/2/3 and will result in a significant savings for the station. System engineer will work with chemistry in determining the limits on reuse. Reused coolant needs to be filtered prior to addtion back into the expansion tank. <I> **** Actions Taken **** Contacted Environmental | 02-00-DCW-TK-1A1,02-00-DCW-TK-1B1,02-00-DCW-TK-1C
389212 | CR | 20190124 | CAQ | D | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0068202 Heise Pressure Calibrator- model PTE-1/XT was found OOT & adjusted within specs. Not used in the OOT Range of 10.000 V. DEF #6793A writtten. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
389214 | CR | 20190124 | CAQ | D | RWCU-MO-40 Grease Inspection (correct grease) | Y | N |  | N | NO | <D> **** Detailed Description **** CR 366847 identified RWCU-MO-40 actuator grease had the wrong grease installed (ref WO 02079206-01). WO 02113799 -24 reperformed the actuator grease inspection and identified the correct grease was installed (MOV Long Life Grade 0). A sample was provided to engineering for additional verification. <I> **** Actions Taken **** No action is required. This CR is to document RWCU-MO-40 had the correct grease installed contrary to the results of CR 366847. Recommend CR for Trending There is no DNC for this CR.
389218 | CR | 20190124 |  | 3 | Security Badge Observation |  |  |  | N | NO | <D> **** Detailed Description **** During an observation at the security checkpoint there were 6 instances of the security officers coaching individuals on the condition of their security badge. The photo either needed updated or the badge was faded to the point of needing replaced. In each case postive identification occured. Recommend an assignment be generated to each department ensuring badges are up to date and in good condition. Badge replacements should be scheduled with Access Authorization. Recommend non-CAQ 3 to Security. <I> **** Actions Taken **** Notified Security Management. <N> During OFM and MSM it was briefed by security to have department heads review and discuss with their staff to maintain accurate photos, maintenance of badges and to update as needed.
389221 | CR | 20190124 |  | 4 | Vendor broke tool when performing Hot Tap in CWPH | N | N |  | N | NO | <D> **** Detailed Description **** Vendor was performing hot tap on CBD(1)-1 through newly installed valve CBD-V-101 when the cutting tool sheared and became stuck in the 24" CBD(1)-1 pipe. Vendor attempted to reattach tool but when he removed extension, the tool was completely sheared from the drill shaft. The CBD-V-101 valve was able to be closed and prevent leakage. <I> **** Actions Taken **** Removed hot tap assembly from valve CBD-V-101, called PSRO and notified CPM supervision and engineering. Also notified work control. Work is stopped and in a safe condition. <N> **** Equipment Description **** CBD-V-101 is a 1" valve located on north end of 24"CBD(!)-1 pipe located close to north side rollup door in CWPH . EPN CBD-V-101 does not currently exist in Portal J / MEL. Looking at EC DC 16616, the likely EPNs are either CL-V-101 or CBD-V-10 (both tap off of the 24"CBD(1)-1 line per EC DC 16616 pg 13.2). Most likely EPN associate with this AR CR is CL-V-101 (appears to be closest to the CWPH roll up door) .
389223 | CR | 20190124 | CAQ | D | ISP-CIA-Q902 | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of ISP-CIA-Q902, as found trip for CIA -PS-22B was found OOT low at 153 psig (Calibration limits 155 psig to 157 psig) at step 7.1.13. Adjusted CIA-PS-22B per the procedure and as left trip to within tolerance at 156 psig. CIA-V-39B time response (Step 7.3.15) as found was outside desired range at 3 minutes and 14 seconds (Desired is 2 Min 50 Sec to 3 Min 10 Sec). Recorded value is for trending purposes only. <I> **** Actions Taken **** Notified operations, supervision, adjusted CIA-PS-22B, wrote CR <N> **** Equipment Description **** RX 548
389224 | CR | 20190124 |  | 3 | Packing installed in COND-V-119C out of PPM tolerance | N | N |  | N | NO | <D> **** Detailed Description **** While performing maintenance activities on COND-V-119C it was discovered that the packing that was ordered for the task does not meet the tolerances provided by PPM 10.2.79 . The Valve Packing Data Sheet (VPDS) calls for a packing size that is 1.250â€ X 1.906â€. Field measurement confirmed the packing dimensions of the VPDS. The packing that was ordered is 1.250 X 1.875. Install the packing due to not having the correct size on site. The same incorrect size packing was installed in R23 in the same valve on WO# 02072877. <I> **** Actions Taken **** Notified Engineering and OCC.
389227 | CR | 20190124 |  | 3 | Trailer 124 Refrigerators plugged into Power Tap |  |  |  | N | NO | <D> **** Detailed Description **** Fire Protection Engineer inspection of Trailer 124 today found two full sized refrigerators plugged into a single power strip. This is a direct violation of ISPM-6 which does not allow high amperage appliances like this to be plugged into a surge protector or power tap. This trailer is not currently occupied. The two refrigerators are empty. This CR needs to be directed to whomever is responsible for setting up these trailers. Unless the people responsible can be coached, this problem is likely to recur. <I> **** Actions Taken **** Unplugged the refrigerators and the power tap.
389229 | CR | 20190124 |  | 4 | Heat trace failed resistance test | N | N |  | N | YES | <D> **** Detailed Description **** While performing section 7.1 of 10.25.213 the 6F zone of heat trace in the CST pit failed the megger test at 2500vdc with a value of 535 mega ohms. The acceptance criteria is GT 1000 mega ohms or 1 gig ohms. <I> **** Actions Taken **** Craft informed supervisor and place the heat trace back to its as found condition. Wrote CR. <N> **** Equipment Description **** HT-HTP-FP/5 Zone 6F in CST pit
389230 | CR | 20190124 |  | 4 | Simulator Interruption unexpected TR-N to TR-S shift |  |  |  | N | NO | <D> **** Detailed Description **** On 1/17/2019, a simulator interruption occurred when the simulator electric plant unexpectedly shift lineup from the TR-N to TR-S breakers. This could not reproduced and the scenario was re-run successfully. SR 2879 documents this interruption.
389231 | CR | 20190124 | CAQ | C | PRM-SR-1 Vendor Backup Copy |  |  |  | N | NO | <D> **** Detailed Description **** CF Card backup copy recieved from vendor on 1/21/19 does not contain the latest configuration and parameters. This copy can not be used as a backup unti lit's updated. This is an administrative issue only, not equipment. <I> **** Actions Taken **** Talked with maintenance supervisor CR Written | 02-00-PRM-CPU-1,02-00-PRM-SR-1
389232 | CR | 20190124 |  | 4 | SA-F-69 appears to be plugged up with corrosion products | N | N |  | N | YES | <D> **** Detailed Description **** Air not depressurizing from the filter at its normal rate when drain valve SA-V-23 is opened two turns, IAW SOP -RWCU-DEMIN, Step 5.3.7y. SA-F-69 has had RWCU demineralizer water draining out its drain valve for several months, therefore it is probably now plugged with corrosion. The filter is depressurizing at a very slow rate as evident on SA-PI-71. Air filter needs to be replaced, however this could re-occur on its replacement filter as well. <I> **** Actions Taken **** inform Shift Supervision <N> **** Equipment Description **** RW467 | 02-00-SA-F-69
389235 | CR | 20190124 | CAQ | B | (QA) Fire Detection LCS SVs Not Completed By Due Date | N | Y |  | Y | YES | <C> At the direction of OFM, CR changed from C to B RISK - Medium. CAUSE - Uncertain. Investigation Template Required. (Repetitive (trend) and could lead to a green finding). 1/29/2019 Reopened Assignments 06 and 07 at customers request for a major revision on product before PARB <D> **** Detailed Description **** (QA) Surveillance Requirements SR 1.10.6.1 and SR 1.10.6.3 for Essential Fire Protection Zone 13 were not completed within the required frequency due to a Preventive Maintenance deferral, causing the station to meet the requirements to enter RFO 1.10.6 Condition A, however entry was not recognized due to the deferral. SR 1.10.6.1 is now met by WO 02100739-01 (Finish 1/23/19) and SR 1.10.6.3 is now met by WO 02102188-01 (Finish 1/23/19). See EDMS for full Details, including initial potential extent of condition. <I> **** Actions Taken **** Initiating CR, Notified QA Management, Notifying Control Room, Maintenance Management. This is a Finding identified during the Maintenance Audit AU-MN-19. Recommend an Extent of Condition review of all Essential Fire Protection surveillances for interval issues. <N> **** Equipment Description **** Essential Fire Protection, See EDMS <R> REP/REGE assignments are not required. Both assignments have been cancelled with Compliance Supervisor concurrence.
389236 | CR | 20190124 |  | 4 | Poor Lighting Reactor 501 West Side | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Poor Lighting Reactor 501 West Side. Needs Bulb Replacements. <I> **** Actions Taken **** Notified HP Lead Technician Initiated CR/WR ESOMS log entry <N> **** Equipment Description **** Reactor 501 West Side
389237 | CR | 20190125 |  | 4 | CW-P-1C excessive leakoff from shaft | N | N |  | N | YES | <D> **** Detailed Description **** CW-P-1C has excessive leakoff from shaft overflowing basin and running onto floor after CW-P-1B shutdown <I> **** Actions Taken **** MCR notified <N> **** Equipment Description **** CWPH | 02-00-CW-P-1C
389241 | CR | 20190125 |  | 4 | RWCU-V-232A open indication bullb stuck in socket | N | N |  | N | YES | <D> **** Detailed Description **** while restoring RWCU-DM-1A the open indicating light blew, while trying to remove the bulb by pulling the bulb straight out, the base of the bulb came off and stayed stuck inside the socket. <I> **** Actions Taken **** intorm the CRS and initiate a CR/WR | 02-00-RWCU-V-232A
389242 | CR | 20190125 |  | 4 | TMU-LCV-2A unexpectedly went closed | N | N |  | N | YES | <D> **** Detailed Description **** At 0611 on 1-25-19, Received board M trouble. TMU-LIC-2A output went to 0%, with the controller being ed. Operators took manual control of TMU-LIC-2A and reopened the TMU-LCV-2A. TMU flow went from 14000 gpm to 5000 gpm. After verifying TMU parameters were normal, Operators placed TMU-LIC-2A back in automatic. | 02-00-TMU-LIC-2A
389243 | CR | 20190125 |  | 3 | Change design procedures require ball valves have locking |  |  |  | N | NO | <D> **** Detailed Description **** Operations procedures require locking devices be installed on all "bump hazard" valves (90 degree ball valves). New systems being installed in the plant are still using 90 degree ball valves with no installed locking devices. Significant time and resources are spent ensuring applicable ball valves are "locked" using temporary devices (tie-wraps, chains, brady locking devices, many Ops man -hours). This CR is requesting Design Engineering update applicable procedures to require all 90 degree ball valves called for in new designs have locking mechanisms permanently installed on the valves (locking plate/pins). This CR is for new designs going forward only and is not requesting a change to already installed equipment or new designs too far through the design process to reasonably change at this point.
389245 | CR | 20190125 | CAQ | D | TREND ONLY AR - CCH-CR-1B high oil level | Y | Y |  | N | YES | <D> **** Detailed Description **** CCH-CR-1B, Upper sightglass, oil level was at the high limit of 1/2 full. Per PPM 3.1.10 (Operator Logs), the Aux Oil pump was manually ran to bring oil level down to 1/8 full. This AR generated per the directions in PPM 3.1.10 (OPS 2 Logs). Note that CCH-CR-1B was ran for monthly testing and secured on 1/24/19 at ~ 1330. A high oil level following the monthly run is not unusual. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RW 525 | 02-00-CCH-CR-1B
389247 | CR | 20190125 |  | 4 | while testing found SA-MON-1 out of tolerance | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** SA-MON-1 out of tolerance while performing 02106870-01 <I> **** Actions Taken **** adjusted to within tolerance <N> **** Equipment Description **** RW467
389248 | CR | 20190125 |  | 3 | CW suspended solids GT 125 PPM | N | N |  | N | NO | <D> **** Detailed Description **** CW suspended solids were analyzed due to appearance of the sample taken. The initial sample was 158 PPM. A backup sample was taken and analyzed at 175 PPM suspended solids. SWP-CHE-02 action level is LT125 PPM. PPM 12.14.3 stated to increase CW blowdown by 1000 GPM for GE 24 hours. Blowdown is currently secured due to halogenation, but will be increased by 1000 GPM over the calculated blowdown rate when it is started. Suspended solids will then be resampled. CW-P-1B was secured at 0303. This CR is for trending. <I> **** Actions Taken **** Notified CRS and supervision.
389251 | CR | 20190125 |  | 4 | Heat Trace Zone 13F | N | N |  | N | YES | <D> **** Detailed Description **** While performing WO 02098263-01 Zone 13F failed to meet acceptance criteria of GT 1000 megohms at 500VDC and GT 1000 megohms at 2500VDC. Results of test are as follows 27.0meg at 500VDC and 92.0meg at 2500VDC. <I> **** Actions Taken **** Informed supervisor of our results and documented with CR. <N> **** Equipment Description **** HT-HTP-FP/5 Zone 13F CST PIT.
389252 | CR | 20190125 |  | 4 | HT-HTP-FP/6 ckt 24F ( PWC-SEW-10 ) no continuity. | N | N |  | N | YES | <D> **** Detailed Description **** Found HT-HTP-FP/6 ckt. 24F no continuity light flashing and the power light for this ckt. off. Reset tripped free breaker for PWC-SEW-10 but the condition did not change. (breaker remiained shut) Pease T/S and repair as necessary. <I> **** Actions Taken **** Notified supervisor and obtained permission to reset tripped free breaker. <N> **** Equipment Description **** CWPH west end. | 02-00-HT-HTP-FP/6
389253 | CR | 20190125 |  | 4 | TMU pump house mid level needs relamping. | N | N |  | N | NO | <D> **** Detailed Description **** TMU pump house mid level has at least 8 burned out light bulbs. They are 100W 130V incandescent bulbs. Please relamp or provide bulbs for relamping. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TMU pump house area lighting. ( Mid level )
389254 | CR | 20190126 | CAQ | D | Accumulator Trouble Alarm for CRD-HCU-42-55 | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-42-55 was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear <I> **** Actions Taken **** Followed ARP. | 02-00-CRD-HCU-4255
389257 | CR | 20190126 | CAQ | D | HCU 18-07 accumulator trouble | Y | N |  | N | YES | <D> **** Detailed Description **** HCU 18-07 accumulator trouble due to high water. <I> **** Actions Taken **** Followed ARP and drained water. | 02-00-CRD-HCU-1807
389258 | CR | 20190126 | CAQ | D | Received Oscillograph start alarm | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph start due to a Lower Monumental -McNary single phase fault which automatically reclosed. B/U voltages 118/118/118 kv. S/U voltages 236/236/235 kv.
389259 | CR | 20190126 |  | 3 | GBP-ENG-01 and/or Job Code AP073 correction needed |  |  |  | N | NO | <D> **** Detailed Description **** For the Principal Engineer position, minor disconnects exist between the Principal Engineer column in GBP-ENG-01 Table 1 (Engineer Qualifications) and the Postition Description Form for Job Code AP073 (Principal Engineer). Examples: The AP073 Position Description indicates 1 Diverse Assignment is Required while GBP-ENG-01 Table 1 indicates 1 Diverse Assignment is Desired for Principal Engineer. The AP073 Position Description indicates 2 Diverse Assignments are Preferred (not indicated for Principal Engineer in GBP-ENG-01). The AP073 Position Descripton indicates SRO or Plant Certification is Desired (SRO Desired is not indicated for Principal Engineer in GBP-ENG-01). One or the other or both of these documents should be corrected to make them match. Also for GBP-ENG-01, the distiction between 'preferred' and 'desired' should be clarified.
389260 | CR | 20190126 |  | 3 | OSP-INST-H101 Rev 092 needs enhancement. |  |  |  | N | NO | <D> **** Detailed Description **** OSP-INST-H101 Rev 092 needs enhancement. Step 9.8.5 first bullet currently says, Log these values on Step 33. This step is not as clear as it could be. The following information should be added to Step 9.8.5 first bullet in parentheses: (SW-TE-2B/ SW-TE-2C for SW-TI-2A, SW-TE-2F/ SW-TE-2G for SW-TI-2B). <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR.
389261 | CR | 20190126 |  | 3 | Procedure enhancement for OSP-RHR/IST-Q704 |  |  |  | N | NO | <D> **** Detailed Description **** in OSP-RHR/IST-Q704 please make a note that allows step 7.2.11 prestart checks to be accomplished any time before the pump start. . also include a note that step 7.2.55 to remove the fluke can be performed any time after step 7.2.54 <I> **** Actions Taken **** Informed CRS, wrote CR
389262 | CR | 20190126 | CAQ | D | while performing ISP-MS-X315 unable to complete step 7.22.26 | Y | Y |  | N | I DONT KNOW | <D> *1 unable to complete step 7.22.26 to confirm Fuse F5 on TIP-MON-4 was illuminated has WR # 29142205 <I> created cr to track the *! <N> CR found at INPROG. APPROVED CR for OPS review.
389263 | CR | 20190126 | CAQ | D | SLC tank high level alarm | Y | Y |  | N | YES | <D> **** Detailed Description **** The SLC tank high level alarm was received. Investigation showed that SLC-LI-601 was reading high. . Request I&C ream out SLC-FIC-4 <I> **** Actions Taken **** Wrote CR Rodded out SLC bubbler by using PM scheduled for two weeks from today: work order 02137798. The initial adjustment of air flow to 1.0 cfm returned the control room instrument to the expected reading, the rod out PM restored the TDAS reading to the pre event reading. | 02-00-SLC-FIC-4
389264 | CR | 20190126 |  | 4 | Heat Trace failed to meet resistance criteria | N | N |  | N | YES | <D> **** Detailed Description **** While performing WO 02098263-01 section 7.1.4 Zone 2F failed to meet acceptance criteria of GT1000 megohms at 500VDC and GT1000 megohms at 2500VDC. Test results are 276 megohms at 500VDC and 7.9 megohms at 2500VDC. Craft also discovered that the junction box at the ground level was extremely corroded. And needs replaced. <I> **** Actions Taken **** Informed supervision and wrote CR. <N> **** Equipment Description **** HT-HTP-FP/5 Zone 2F | 02-00-HT-HTP-FP/5
389265 | CR | 20190126 |  | 4 | Heat Trace failed to meet acceptance criteria | N | N |  | N | YES | <D> **** Detailed Description **** While performing WO 02098263-01 section 7.1.4 Zone 16F failed to meet the acceptance criteria of GT 1000 megohms at 500VDC and GT 1000 megohms at 2500VDC. The results are 6.9 megohms at 500VDC and .19 megohms at 2500VDC. <I> **** Actions Taken **** Informed supervision and wrote CR. <N> **** Equipment Description **** HT-HTP-FP/5 Zone 16F CST Pit | 02-00-HT-HTP-FP/5
389266 | CR | 20190126 | CAQ | D | RHR-DPIS-29B Missing Indicator Stop Snubber | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02106825-01, the Indicator Pointer Stop steps could not be completed because there is no Stop Snubber on the right (positive side) of RHR-DPIS -29B <I> **** Actions Taken **** Contacted Supervision. Continued with procedure and wrote CR to document condition per 10.24.34. <N> **** Equipment Description **** 501Rx
389267 | CR | 20190126 | CAQ | D | RHR-DPIS-29B found Out of Tolerance | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of WO# 02106825-01, both annunciator switches were found out of tolerance. SW #1,2 was found at -3.60 (-3.75 to -3.85) and SW#9,10 was found at +3.50 (+3 .75 to +3.85) <I> **** Actions Taken **** Contacted Supervision. Informed CRS. Calibrated to within tolerance per 10.24.34 and IMDS. As left were SW#1,2 -3.81 and SW#9,10 +3.80
389268 | CR | 20190126 |  | 3 | OSP-RHR/IST-Q704 wastes ECCS INOP time and dose |  |  |  | N | NO | <D> **** Detailed Description **** Procedure steps to have I&C remove test gage (which is valved out) is required to be completed before stopping RHR-P-2C. This is during a time when the pump is INOP during the surveillance. This is holding up 2 operators and 2 electricians unnecessarily. The gage removal can be done in closing out the surveillance (like the other ECCS operabilities. Other procedures should be reviewed for similar issues causing unnecessary INOP time and dose. In addition time is wasted during set up to walkdown the system before establishing test conditions. The walkdown should be after the test conditions are set so W/D and vibes etc can be performed in parallel. This same basic principal should be verified to be part of all the ECCS operability surveillances. <I> **** Actions Taken **** suggest this procedure be suspended until fixed and fixed ASAP - this has been an issue for awhile
389269 | CR | 20190126 | CAQ | D | DEH valves leak by | Y | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02112562, then taken back to complete <D> **** Detailed Description **** During performance of WR 29146712 to change out DEH-F-18A it was discovered that DEH-V-66 & DEH-V-67 leak by making it difficult to change out the filter. Please repair or replace these valves in the outage. <I> **** Actions Taken **** Supervision was informed. | 02-00-DEH-V-66,02-00-DEH-V-67
389270 | CR | 20190126 | CAQ | C | Moisture in OG process flow to OG-SR-3 | Y | Y |  | N | YES | <D> **** Detailed Description **** The moisture making it to OG-SR-3 is causing operator to drain OG-T-3/1 and OG-T-3/2 when requested by chemistry. This should normally be performed as direct by OPS 3 tour once per week. There are numerous documented issuse of flow, moisture, and vacuum/pressure abnormalities. It appears that the only current active WO's against this is 02136729 which is to address the degraded operation of OG -FIC-3/2. It appears that as a station we are utilizing FIN,Chem, and OPS resources to correct this on a case by case basis. An investigation seems warranted into the issue of how/why moisture is causing so many issues at this point. OG-SR-3 taps off of this system after OG-MS-6 and typically the weekly blowdown has been sufficient to preclude the issues we are having. Please evaluate and investigate this issue. <I> **** Actions Taken **** Discussed with supervision. Wrote this AR. | 02-00-OG-SR-3
389271 | CR | 20190126 | CAQ | C | OG-V-811 is shown as a normally open gate valve on M535-1 | N | N |  | N | YES | <D> **** Detailed Description **** OG-V-811 (also refered to PS-V-11) is a sample line drain to EDR on the OG line to OG-SR-3. CVI 317-00,2039 shows this line as a normally open globe valve. SOP-OG-LU lists this valve as normally closed. Please evalutate if this valve could be opened to act as a loop seal and drain excess moisture for the OG line going to OG-SR-3 without causing issue with dose rates. M671 shows this line draining to an EDR scupper with a welded cap suggesting that contamination should not be an issue. It is shown on 317-00,2039 as being a 4in loop seal. Please evaluate if this valve can be open during normal operation. Regardless M535 should be updated to show closed or SOP-OG-LU should be changed to open for this valve. <I> **** Actions Taken **** Discussed with supervision. Referenced SOP-OG-OPS (and hsitorical versions of SOP-OG-START, and PPM 2.6.4) and found that this valve has a normally closed position since at lease 1999. <N> AR EVAL needed vs AR CR? | 02-00-OG-V-811
389272 | CR | 20190126 |  | 3 | Fuel pool high risk plan not approved by T-3 | N | N |  | N | NO | <D> **** Detailed Description **** Fuel pool high risk plan not approved by T-3 and available for Operation review as required per WCI-4. WO 02112795 and 02112796.
389273 | CR | 20190127 | CAQ | D | Rods required High DP to move during OSP-CRD-M701. | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02113437, then taken back to complete <D> During performance of OSP-CRD-M701, 9 HCU's required High Drive water DP to move from their initial position. <I> Informed CRS. Entered ABN-ROD | 02-00-CRD-HCU-0235,02-00-CRD-HCU-1015,02-00-CRD-HCU-1455,02-00-CRD-HCU-2619,02-00-CRD-HCU-3003,02-00-CRD-HCU-3019,02-00-CRD-HCU-3411,02-00-CRD-HCU-4655,02-00-CRD-HCU-5443
389274 | CR | 20190127 | CAQ | C | Recieved 4.603.A7 drops 1-7 and 2-8 For RDCS | Y | Y |  | N | YES | <D> **** Detailed Description **** Recieved 4.603.A7 drops 1-7 ROD POSITION INDICATION SYSTEM OR DISPLAY MEMORY MODULE INOPERABLE and 2-8 ROD DRIVE CONTROL SYSTEM INOPERABLE while with drawling rod 42-03. Followed ARP and RESET alarm. <I> **** Actions Taken **** Took pictures and forwarded information to system engineer. | 02-00-CRD-DMM-1
389281 | CR | 20190127 | CAQ | C | ISFSI printout can not be used for OSP-INST-H101 data | Y | N |  | N | NO | <D> **** Detailed Description **** printout is at 0700 and H101 data collection is to begin no earlier than 0730. Contacted project personnel about the issue and they indicated it is too hard to fix. Suggest OPS take ISFSI temp monitoring (OSP-SFS-D101) out of H101s and make a stand alone procedure to be completed by OPS 3 each day. OPS 3 selected since the printout is black and white and one of the checks is to monitor the screen for yellow or red indications.
389282 | CR | 20190127 | CAQ | D | DSA-DY-1A through wall leak | Y | N |  | N | YES | <D> **** Detailed Description **** There is evidence of a through-wall leak on DSA-DY-1A. There is no effect currently on Air Pressure. See attached picture. <I> **** Actions Taken **** Informed MCR, wrote CR. | 02-00-DSA-DY-1A
389283 | CR | 20190127 |  | 4 | OG-LIS-8B reading high and trending higher. | N | N |  | N | YES | <D> **** Detailed Description **** OG-LIS-8B is currently high out of band reading 29 (high of 25) it has trended up from 25 to 29 from 1/20/19 to 1/25/19. Still reading 29 on 1/27/19. Last CR was cancelled for trending AR#00387570. <I> **** Actions Taken **** Logged and informed supervision. | 02-00-OG-LIS-8B
389284 | CR | 20190127 | CAQ | D | water leak from MS-LIS-37D | Y | N |  | N | YES | <D> **** Detailed Description **** water leak from MS-LIS-37D approx 1 drop/min coming from stem leakage on the instrument equalizing vlave <I> **** Actions Taken **** Informed MCR Placed absorbent material underneath | 02-00-MS-LIS-37D
389285 | CR | 20190127 | CAQ | D | MS-PS-413D As Found Out of Tolerance | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02106834-01, MS-PS-413D As Found Trip was found out of tolerance low at 490psi (491-502). <I> **** Actions Taken **** Informed Supervisor nd Operations. Adjusted to within tolerance at 492psi per procedure.
389286 | CR | 20190127 | CAQ | D | MS-LIS-37D Equalize Valve has small leak. | Y | N |  | N | I DONT KNOW | <C> Closed, Trended to CR 389284 <D> **** Detailed Description **** While performing work at E-IR-PO27, it was noticed that MS-LIS-37D Equalize Valve 44 had a small leak. <I> **** Actions Taken **** Informed Supervisor and CRS. See picture in EDMS <N> **** Equipment Description **** 522Rx PO27
389287 | CR | 20190127 |  | 4 | TSW-FI-P/1B flow element stuck | N | N |  | N | YES | <D> **** Detailed Description **** While starting CW-P-1B, it was discovered that TSW-FI-P/1B float was stuck. Debris was noticed contacting the float assembly. The debris was partially cleared with high water flow and lightly tapping flow indicator. This caused the float to move slightly, but the float still didnâ€™t indicate accurate flow (didnâ€™t move after increasing flow or isolating meter). Flow to CW-P-1B motor cooler was determined (with CRS permission) by fully opening TSW-V -127B, throttling TSW-V-96B and looking at flow on TSW -FIS-33B with TSW-V-95B closed. Meter needs to be cleaned/recalibrated <I> **** Actions Taken **** Notified CRS | 02-00-TSW-FI-P/1B
389288 | CR | 20190127 |  | 3 | WO task 02092634-02 unable to set to finished |  |  |  | N | NO | <D> **** Detailed Description **** WO task 02092634-02 is a hang clearance task and as such EWP should allow the task to be set to finished, however the set to finish option was greyed out and was unable to be performed. The CRS had to manual process the entire workflow for this work order task vice being able to set the task to finished. This created inefficiencies in the work order process. Recommend training to the responsible group to ensure proper coding is assigned to support task WO in the EWP process. <I> **** Actions Taken **** The CRS had to process the WO to allow the task to be taken to finished <N> Normanlly, in DataGlance the user woulld be able to set the WO task 02092634-02 straight to FINISHED, but this option is not allowed if the Control Room Communication on the Asset Sutie Nuclear Panel is set to '1' or '2'. This Wo Task 02092634-02, although it is a support task, has the Control Room Communication set to '1', meaning that it is "HIGH IMPACT -Only PSRO/OPS may take to 48". The software is wokring as desiged. Operations have the ability to change the value during Ops CORC/WC review. ) Recommend Maintenance to provide Operation awareness of populating applicable fields. An assignment is being created for maintenance to provide awareness.
389289 | CR | 20190127 |  | 3 | Work process 02092634-02 task |  |  |  | N | NO | <D> **** Detailed Description **** 02092634-02 task was set as ops authorization required, so instead of being able to take the task directly to finished it had to be authorized, taken to working, set to finished, and finally work complete a waste of time. This is happening fairly frequently and with the larger amount of tag outs which will be happening as we get closer to the outage it will waste even more time. <I> **** Actions Taken **** Informed supervsion. <N> Using DataGlance user is unable to set WO 02092634-02 to FINISHED, but this option is not allowed if the Control Room Communicaiton on the Asset Suit Nuclear Panel is set to "1' or '2'. Although, WO 02092634-02 is a support task, the Control Room Communicaiton is set to '1', meaning that it is "HIGH IMPACT - only PSRO/OPS may take to 48". The software is working as designed. Operations have the ability to change the value during thier Ops (CORC/WC) review. Recommend Maintenance to provide Operation awareness of populating applicable fields. An assignment is being created for maintenance to provide awareness.
389290 | CR | 20190127 |  | 4 | AR/WR cancelled with no action taken to address issue |  |  |  | N | YES | <D> **** Detailed Description **** AR 374389/WR 29140105 was written to address low total REA air flow. WR 29140105 was cancelled to WO 02130000. Actions to correct the original reported condition are at status CXCL/REQ with no follow on work item to address the condition. In the meantime, Operations continues to log the condition low out of specification. Engineering evaluation of the condition recommended no change in log specifications and to actually fix the low flow condition. Continuing to log out of specification conditions with no corrective action planned desensitizes operators to out of specification conditions and does nothing to addresss the issue. <I> **** Actions Taken **** Discussed with CRS. <N> **** Equipment Description **** R572 | 02-00-REA-FI-3
389291 | CR | 20190128 | CAQ | C | B5B quartelry and annual cabinet inventories do not match | N | Y |  | N | NO | <D> **** Detailed Description **** Quarterly B5B Cabinet Inventory was scheduled 1/21/19 (WO 02106860) and the annual one was scheduled 1/28/19 (WO 02107151). The two inventories were compared to each other and they do not match. Specifically the locker locations are labeled different from one to the other and location of equipment is different from one to the other. Additionally, these inventories should be scheduled on the same day.
389292 | CR | 20190128 | CAQ | C | B5B Inventory Missing Adapter | N | Y |  | N | NO | <D> **** Detailed Description **** During performance of B5b Bldg 600 Cabinets Inventory Check, could not locate '6 INCH NF Female threaded to 5" Storz adapters to provide 5 INCH storz inlets to pump suction' item. Two are requested in the entire inventory: one in pumper truck which was located and the other should be stored in Trailer Gang Box. Item could not be located in Building 600. <I> **** Actions Taken **** Notified SSS and initiated CR <N> **** Equipment Description **** B5b Adapter - 6" NF female threaded to 5" Storz in Bldg 600
389297 | CR | 20190128 | CAQ | D | Received 4.812.R2 4-2 FUEL POOL COOLING ROOM COOLER FLOW LOW | N | Y |  | N | YES | <D> **** Detailed Description **** Received 4.812.R2 4-2 FUEL POOL COOLING ROOM COOLER FLOW LOW. Dispatched OPS 2 to perform OSP-SW-C102. Alarm is clear now. As founf 34.5 GPM. As lest 47 GpM. <I> **** Actions Taken **** Wrote CR. Sent out OPS2 to make it fixed. | 02-00-RRA-CC-19
389298 | CR | 20190128 | CAQ | D | Rod accumulator trouble alarm HCU 2203 (water level) | Y | N |  | N | YES | <D> **** Detailed Description **** received high water level alarm HCU 2203 <I> **** Actions Taken **** dispatched OPS 2 to drain water / alarm clear | 02-00-CRD-TK-125/2203
389299 | CR | 20190128 |  | 3 | COND-P-2C has no spare parts for the upgaded seals | N | N |  | N | NO | <D> **** Detailed Description **** The B.O.M. for COND-P-2C is exactly the same as the other two pumps. The B.O.M should include the different seals and shaft. If we have a seal failure it appears we would have no spare parts. <I> **** Actions Taken **** Wrote AR and contacted supervisor.
389309 | CR | 20190128 | CAQ | D | IR-V-H22P004/V24 packing leak | Y | N |  | N | YES | <D> **** Detailed Description **** while performing WR#29139018, it was noticed that IR-V -H22P004/V24 was leaking form the packing gland at 1 to 3 drops per minute. <I> **** Actions Taken **** wrote CR and Notified supervisor and PSRO <N> **** Equipment Description **** RX 522 | 02-00-IR-V-H22P004/V24
389311 | CR | 20190128 |  | 4 | TOA-FL-2A is at End of Roll | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FL-2A is at the End of Roll. Please replace filter media. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TG 501W | 02-00-TOA-FL-2A
389312 | CR | 20190128 |  | 4 | CAS-C-1C maintaining header pressure abnormally low | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1C is maintaining the CAS header pressure abnormally low. Header pressure is normally ~ 112 to 114 PSIG with one CAS compressor running. Currently, with only CAS-C-1C running, the CAS header pressure is ~104PSIG and steady. Verified with the MCR that no unusual CAS usage was in progress. Suspect an adjustment to the inlet valve may be needed. Note: a CAS header pressure of 104PSIG is not low out of spec, and the standby CAS compressors do not auto start until 100 PSIG. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TG 441 | 02-00-CAS-C-1C
389313 | CR | 20190128 | CAQ | D | 6 Pieces of M&TE Rejected | N | N |  | N | NO | <D> **** Detailed Description **** 6 Pieces of M&TE were Suspended for several years and are Now Rejected- No Longer Needed. DEF #6794A thru #6799A were written for each piece. See EDMS for Calcodes, MFR, Models and associated DEF numbers that reflect the original Suspensions. No Action Required. <I> **** Actions Taken **** None rending purposes only.
389314 | CR | 20190128 | CAQ | C | Drawing not updated |  |  |  | N | NO | <D> **** Detailed Description **** Motor starter RRA-42-8BA11A was replaced in 2014 and drawing E528-36B has not been updated to show the change in acceptable control power fuse type. Recommend assignment to ensure all applicable drawings have been updated.
389315 | CR | 20190128 | CAQ | C | CAT ID 60111506 not configured as per sub eval 2756 | N | N |  | N | YES | <D> **** Detailed Description **** Sub eval 2756 shows single pole double throw contacts. Both switches pulled from the warehouse did not have this configuration. Both switches had a fourth connection that could possibly be used.. However, this connection point not shown on vendor supplied documents. Unknown contact rating. W/O 02109182-02 CAT ID 60111506 ENGINE SYSTEMS INC MODEL 9544841 <I> **** Actions Taken **** Wrote CR. . --Update 1-28-19- - initial Procurement Engineering investigation documentation uploaded to EDMS. Tcroyl 1-28-19 . | 02-00-DCW-TS-8
389317 | CR | 20190128 |  | 3 | Change to PPM 10.19.7 to enhance procedure |  |  |  | N | NO | <D> **** Detailed Description **** Change PPM 10.19.7 sections 7.2.12 and 7.2.14 c to allow any non-contaminated water source to be used to clean the condernser tubes
389319 | CR | 20190128 |  | 4 | TDAS X413 found out of tolerance | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02130381-01, the af found data for TDAS X413 was found out of tolerance high. <I> **** Actions Taken **** Informed Supervision and Operations. Wrote CR to document. <N> **** Equipment Description **** 548Rx
389320 | CR | 20190128 |  | 4 | (QA) Housekeeping Issues - CWPH |  |  |  | N | NO | <D> **** Detailed Description **** Housekeeping Issues - CWPH A Wolf Creek Nuclear Station employee supporting the Mechanical Maintenance audit informed Industrial Safety of several housekeeping and potential safety issues observed at the Circulating Water Pump House. (CWPH). 1) A Delxo lightweight aluminum 4 foot step ladder was observed inside the pump house. The ladder did not have an OSHA rating and is not allowed per ISPM-9, section 3.2.4 & 3.2.5. The ladder was removed from service. 2) A 10 ft step ladder was observed inside the pump house, staged for a work activity. The ladder was rusted at the steel rivet connections and all labels were illegible. The ladder did not meet the requirements of ISPM-9, section 3.2.2. The ladder was removed from service. 3) Rigging wire rope slings are stored outside the NE corner of the CWPH on a pallet. The rigging is degraded and some had yellow rings attached that indicated they had not been inspection since 2016. The Maintenance Manager and Site Rigging Coordinator (SRC) was notified to have the pallet moved and the rigging inspected and/or taken out of service. <I> **** Actions Taken **** Actions: the two ladders were taken out of service and the Maintenance Manager and SRC notified to take care of the rigging. (WR 29146877) The assigned area owner of the CWPH (Chemistry) was informed of the issues found per SWP-MAI-02, section 5.1.7. A Condition Report was initiated per SWP-MAI-02, seciton 5.1.7. http ://thecurrent/sites/HMC/Shared %20Documents/Plant %20Housekeeping%20Area%20Owners.xls <N> This is a Deficiency identified during the Maintenance Audit, AU-MN-19.
389321 | CR | 20190128 |  | 3 | SOP-ELEC-DIV2-TEMPPOWER HAS ERRORS FOR R-24 WORK |  |  |  | N | NO | <D> **** Detailed Description **** SOP-ELEC-DIV2-TEMPPOWER section 5.27 & 5.28 for temp power to guardhouse need to be cleaned up. The new revision does not require any determs /reterms but still requires clearances to be hung. Clearances should not be required to perform procedure. All steps for hanging and lifting clearances need to be removed. This creates unessecary work and manpower. SOP needs to be ready by R-24.
389322 | CR | 20190128 |  | 4 | Corroded Ground Cable in East CW Electrical Building | N | N |  | N | YES | <D> **** Detailed Description **** There is corroded ground cable along the floor on the North wall of Building 38 (East CW Electrical Building). This level of corrosion should be evaluated by engineering to determine if the cause is stray current or galvanic corrosion due to contact with steel. See photos attached in EDMS <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** Building 38 (East CW Electrical Building) . Engineering recommends that the cablecleaned and the corrosion removed. If the ground cable has signs of material degradation, to replace it as needed.
389323 | CR | 20190128 |  | 3 | Flush Sample for COND-P-2 Oil Coolers | N | N |  | N | NO | <D> **** Detailed Description **** Procedure SOP-TSW-FLUSH added steps to obtain samples of the flush water for analysis for biologic and debris. The procedure should be enhanced to include a statement for NA this step if it is not possible or practicable to obtain the sample. Currently WO 02107101-02 cannot be completed as written due to it not being possible or practicable to obtain the sample. <I> **** Actions Taken **** Assign enhancement revision to Sponsor for action.
389325 | CR | 20190128 | CAQ | C | (FP) Ignition Source Permits expired |  |  |  | N | NO | <D> **** Detailed Description **** ISP 19-0008 and ISP 19-0009 have been expired and not been requested for extension or closure. Work order 02135031-06 is listed on the permit for the initiating document. Factual basis: PPM 1.3.10A â€œControl of Ignition Sourcesâ€ revision 17-001 states the following: Section 2.5 Work Supervisor responsibilities states: â€¢ 2.5.5 Tracks ISP termination dates/times and completes actual hot work within the allotted time limit or contacts the Evaluator where extensions are required. Section 3.1 Ignition Source Permit Requirements states: â€¢ 3.1.5 Where hot work cannot be completed within the ISP maximum duration limit, ISP extensions of equal duration to the original ISP can be made by contacting the Evaluator/Approver and recording approval on the ISP form. <I> **** Actions Taken **** Emailed the issue to Supervisor and initiated CR.
389329 | CR | 20190128 |  | 3 | Dose distribution anomalies |  |  |  | N | NO | <C> Per MRT review, this was reprioritized as NCAQ <D> **** Detailed Description **** In review of data for the 1/18-12/18 Dosimeter of Legal Record read it was noted that significant deltas exist in some work groups between higher and lower dose individuals in the group. These variances are explained by qualifications and job assignments for continuity. See EDMS for more detail. This CR written to document Rad support review of individual dose as part of the DLR cycle review. <I> **** Actions Taken **** Wrote this CR.
389330 | CR | 20190128 |  | 3 | Dataglance problem closing work order tasks |  |  |  | N | NO | <D> **** Detailed Description **** I have had a problem closing work order tasks in dataglance. they are grayed out and wont let me set them to finish. 02108170-02, 02109182-03, 02135427-05 02115300-02 02134381-04 These problems persist since we started using eWP and will become a problem during the outage if we have to call someone to close numerous tasks every day. . please fix this problem before the outage <I> **** Actions Taken **** Contacted eWP help line <N> In DataGlance users would normally be able to set the WO taks 08170-02, 02109182-03, 02135427-05 02115300-02 to FINISHED, but this option is not allowed if the Control Room Communication on Asset Suit Nuclear Panel is set to '1' or '2'. Although, these WO tasks are support tasks, the Control Room Communication is set to '1', meaning that it is "HIGH IMPACT - Only PSRO/OPS may take to 48". Operations have the ability to change the value during their Ops (CORC/WC) review. Recommend Maintenance to provide Operation awareness of populating applicable fields. An assignment is being created for maintenance to provide awareness.
389331 | CR | 20190128 | CAQ | D | DMA-RLY-TK32 as found timing out of tolerance | Y | N |  | N | YES | <D> **** Detailed Description **** DMA-RLY-TK32 as found timing out of tolerance. After adjusting time dial timing still was not constantly in tolerance (9.5-10.5sec). as found time 11.13sec. <I> **** Actions Taken **** Craft notified supervision and CRS. Relay replacement is being planned per supervision under WO# 02106776-01. <N> **** Equipment Description **** E-CP-DGHV/3 | 02-00-DMA-RLY-TK32
389332 | CR | 20190128 |  | 4 | Outlets have no power in CMS-SR-21 Room | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While setting up test equipment for WO# 02130381-01, there was no power at the two power outlets labeled 6BA-C-22 in the CMS-SR-21 room or the outlet labeled 6BA-C-12 just outside the room at Door R-511 on the 548Rx. <I> **** Actions Taken **** Contacted Supervision and directed to write CR and WR. Found outlet with power aand ran extension cord to power test equipment. Continued with surveillance. <N> **** Equipment Description **** 548Rx
389335 | CR | 20190128 |  | 4 | RP000001 CBT BROKE |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** WHILE TAKING RP000001 CBT FOR RESPIRATORY PROTECTION WHEN I WAS ON PAGE 91 OF 103 THE COMPUTER KICKED WE OUT. I WAS ABLE TO LOG BACK IN AND START ON PAGE 91. THEN AFTER TAKING THE TEST I WAS STOPPED DUE TO A CONTECT ERROR WITH A MESSAGE TO CONTACT MY SUPERVISOR. <I> **** Actions Taken **** CONTACTED SUPERVISOR AND MANAGER WROTE THIS CR <N> **** Equipment Description **** COMPUTER 525 RADWASTE ADDITIONAL NOTES: The â€œValidation Errorâ€ message upon completion of an exam in Plateau (CBT) is a hard coded message within Plateau that is displayed when a student completes an exam and attempts to â€œReturn to Contentâ€ vs closing the training module. The intended purpose of the message is to let the student know they completed the exam and do not a access to the exam for addition attempts.
389336 | CR | 20190128 | CAQ | C | PMs performed after late date. | N | Y |  | N | NO | <D> **** Detailed Description **** During the extent of condition review for CR-00389235, it was identified that in June of 2018, two PM deferral requests were dispositioned as denying the request for deferral. However, both PMs (WO 02094444, 02098603) were performed after their late dates. PMs were associated with non-critical and non-safety related components. Recommend category 3 to ELECM. <I> **** Actions Taken **** Discussed issue with management and generated condition report. <N> This AR will be resovled by action under AR-389235 which is a B w/ investigation template. <R> The REP/REGE assignments for this CR are not required and are being cancelled. This condition is not reportable to the NRC and does not challenge past operability of plant equipment. Concurrence for cancellation has been obtained from Regulatory Affairs Management.
389337 | CR | 20190128 |  | 3 | De-Vitalization of DG-3 was not well coordinated |  |  |  | N | NO | <C> Per MRT review, this item was dispositioned as a 3 - AR-WC <D> **** ANONYMOUS CR - Detailed Description **** The de-vitalization of DG-3 was not well coordinated this morning. Normally, the selected DG room is surveyed by Radiation Protection on Sunday during the dayshift. A frisker is set up so that the DG can remain a "Clean Island" within the RCA until de-vitalization. Normally, security contacts RP and the de-vitalization occurs just before nightshift ends, between 0400 and 0500. This time it was decided that the de-vitalization would occur at 0600, which conflicts with turnovers, start times, and some D-15's. It would have been much smoother to have had it de-vitalized just before dayshift started. It has been working well that way for many years without incident. <I> **** Actions Taken **** Discussed with various participants. Initiated this AR/CR. <N> ANON CR generated, moved to CR-SRO for OPS review.
389339 | CR | 20190128 | CAQ | C | Top Tier Drawing E503-5 Is Wrong |  |  |  | N | NO | <D> **** Detailed Description **** Top Tier Drawing E503-5 Rev 70 (TEA-FN-93) needs to be revised to reflect changes in EC 4789 <I> **** Actions Taken **** Informed the design group before CR was initiated
389340 | CR | 20190128 |  | 4 | Lower than expected flow while flushing TSW-HX-6F | N | N |  | N | YES | <D> **** Detailed Description **** Per WO 01092495-01 TSW-HX-6F was flushed per SOP-TSW-FLUSH section 5.5. The full open flushing flow was much lower than anticipated; TSW-FG-2C read 6-7 gpm while flushing. The outlet valve (TSW-V-4F) was cycled several times in an attempt to flush potential debris from the piping/hx, there was no change. The supply pressure from TSW-PI-2C1 was initially ~98 psi but while flushing dropped by ~25-30 psi. To compare to COND-P-2A, the HX flow test had a ~10 psig pressure drop and flush flow was >20gpm. Pumps 2A/B TSW piping was completely changed, 2C had the instrument/valve tree changed out but there is a lot of old, unchanged TSW piping, 20-40 ft perhaps that may be contributing to the noted pressure drop. Although reduced flow is evidence of heat exchanger plugging, normally it wouldnâ€™t create such a high pressure drop. This is all assuming the flow instrument is accurate; this could also be a problem. | 02-00-TSW-HX-6F
389344 | CR | 20190128 | CAQ | D | DMA-RLY-42X/FN31 As found pickup out of tolerance | Y | N |  | N | YES | <D> **** Detailed Description **** During testing of DMA-RLY-42X/FN31 per PPM 10.25.138 and WO#02107952-01 the As found pickup voltage was at out tolerance at 95.54 VAC with a tolerance range of 96-98 VAC. The dropout voltage was in tolerance at 92.93 VAC. The settings and ranges are listed on E514-32 and the relay data sheet. Relay operated as designed but slightly out of tolerance. <I> **** Actions Taken **** Notified supervisor and PSRO. Adjusted relay per PPM 10.25.138. As left pickup is 97.07 VAC and dropout is 93.00 VAC which are in tolerance. <N> **** Equipment Description **** E-MC-4A/5A | 02-00-DMA-RLY-42X/FN31
389346 | CR | 20190128 |  | 3 | Email phishing attempt | N | N |  | N | NO | <D> **** Detailed Description **** Multiple users received a phishing attempt via email <I> **** Actions Taken **** User notified IS of suspicious email. Cyber security performed investigation. All suspicious emails removed. Users account passwords have been changed. No further actions necessary. Not reportable via 10CFR 73.54, SWP -CSW-28. <N> User notified IS of suspicious email. Cyber security performed investigation. All suspicious emails removed. Users account passwords have been changed. No further actions necessary.
389347 | CR | 20190128 |  | 3 | Internet unavailable |  |  |  | N | NO | <D> **** Detailed Description **** WSA issue resulted in the internet becoming unavailable for the site. <I> **** Actions Taken **** Troubleshooting resulted in WSA reboot. Internet became available upon restart. No further actions required. Not reportable under 10 CFR 73.54, SWP-CSW-28. <N> Troubleshooting resulted in WSA reboot. Internet became available upon restart. No further actions required. Tracking purposes only
389348 | CR | 20190128 |  | 3 | RRA-FN-8 Vibration data indicates motor bearing degradation | N | N |  | N | YES | <C> Per MRT review, reopened and dispositioned as a 3 - AR -SYSENG <D> **** Detailed Description **** Recent vibration data collected on RRA-FN-8 indicates that the rolling element bearings in the motor are degraded. The vibration spectrums on the motor points show bearing fault frequencies have developed. Also the time waveform data for this bearing have increased from 3 G-s Pk-Pk to 14 G-s Pk-Pk. These values indicate that the bearing has degraded to a stage 4 condition where failure would be expected in the next 30 day to 60 days. Therefore, it is recommended to remove RRA-FN-8 from service as soon as possible and utilized it for emergency use only. <I> **** Actions Taken **** Notified CRS/SM Discussed condition with System Engineer <N> **** Equipment Description **** ST501 H3/5.4 Additional Info: RRA-FC-9 has degraded performance as documented in AR CR 351946. Work orders 02106152 and 02106151 exist to replace RRA-CC-9 piping with stainless steel pipe and to replace RRA-CC-9. The generated WR should be considered for R24 Scope for repair. | 02-00-RRA-FN-8
389349 | CR | 20190128 |  | 3 | NET4-COMP-EPO iLO web interface not responding | N | N |  | N | YES | <D> **** Detailed Description **** NET4-COMP-EPO iLO web interface would not load. iLO is still up, responded to ping. This prevented completion of WR 29146206. . This does not affect Operations, the iLO is used by Computer Engineering for system administration. This is not a reportable condition. . Recommend to Computer Engineering as a 3. <I> **** Actions Taken **** Discussed with Cyber, notified SM and wrote CR. | 02-00-NET4-COMP-EPO
389350 | CR | 20190128 |  | 3 | Factory refurbished breaker for AR-CB-P1 failed bench test | N | N |  | N | NO | <D> **** Detailed Description **** WO 02120617-02 to configure factory refurbished breaker failed bench test on 24 Jan 2019 and requires return to factory for repair. The system Engineer contacted the vendor for troubleshooting recommendation but after hearing the symptoms the vendor recommends return for repair. This is the third factory refurbished breaker in two months that has failed bench testing. All three are R24 pre-outage tasks. Breaker UTC is 350136, Cat ID 68307953. Pre -outage task that will not complete as scheduled. <I> **** Actions Taken **** Contacted Engineering and vendor. <N> **** Equipment Description **** RW 487 breaker shop
389353 | CR | 20190128 |  | 3 | NET3-COMP-EPO EICAR test issue | N | N |  | N | YES | <D> **** Detailed Description **** Quarterly Cyber EICAR testing was partially successful on NET3. Expected alerting was observed on PDIS-CPU-DATA1, however when the file was checked on NET3-COMP-EPO, no alerting was observed. File was removed automatically as expected. . This does not affect Operations. This is not a reportable condition. . Recommend to Computer Engineering as a 3. <I> **** Actions Taken **** Discussed with Cyber and notified SM | 02-00-NET3-COMP-EPO
389354 | CR | 20190128 |  | 3 | Findings following dismantling of LP Turbine Rotor (TE44411) | N | N |  | N | YES | <D> **** Detailed Description **** On 25Jan2019, the vendor provided notification of findings discovered following partial dismantle of LP Turbine Rotor (Serial Number: TE44411). This rotor has completed the refurbishment process including High Speed Balancing with good results. The findings occurred while the rotor was being prepared for shipping which includes removal of the last two blade rows on each end of the turbine (L-1 and L-0 rows, both Governor and Generator ends). There were three primary findings which are as follows: 1. Coupling hole marks â€“ There was one hole in the Generator end coupling that was found to have minor marks on the interior surface. 2. Rotor overhang â€“ There were a handful of marks discovered on the Generator end overhang. The marks were declared to not reside on a critical surface. Vibrometer lands and journal surfaces were not affected. 3. Last stage blade roots and blade grooves â€“ There were blade grooves, and corresponding blade roots, that were identified as having received some level of damage during the L-0 blade removal process. [Locations have been initially identified as: Gov 37, 62, 64 and Gen 13, 40, 71]. Affected blades are being evaluated for use. The conditions described in this CR relate to a piece of equipment in the vendorâ€™s facility and is not current plant operating equipment. <I> **** Actions Taken **** Item 1 â€“ The vendorâ€™s engineering department reviewed the finding, recommend a repair method, and accepted results of the repair. Item 2 - The vendorâ€™s engineering department reviewed the finding, recommend a repair method, and accepted results of the repair. Item 3 â€“ The vendorâ€™s engineering department reviewed the finding and recommend a repair method. The repair has been implemented on the rotor steeples and â€œblue checksâ€ have been performed and accepted. Final engineering acceptance is pending. <N> **** Equipment Description **** Serial Number TE44411 was removed from MS-DT-1A and will be placed in MS-DT-1C in R24 (2019). | 02-00-MS-DT-1C
389355 | CR | 20190128 | CAQ | C | HPCS-EHO-1C new sight glass shows incorrect level | Y | N |  | N | NO | <D> **** Detailed Description **** After installation of new sight glass for HPCS-EHO-1C a question arose as to where the oil level should be filled to. Upon receiving pictures from Engineering regarding where the level should be, it was noticed by the Mechanics that their newly installed sight glass had the level fill line in the upper half of the glass and the ones in the pictures from Engineering had the fill line in the lower half of the sight glass. The new sight glass was installed as received from the vendor. Engineering communicated to the Mechanical Supervisor that the sight glass is upside down and needs to be flipped over. No further action is required. <I> **** Actions Taken **** Supervisor, Component Manager and OCC engineering was notified to resolve this issue.
389356 | CR | 20190128 |  | 4 | Steam leak (S-1) on 471 TG htr. bay NW corner. | N | N |  | N | YES | <D> **** Detailed Description **** There is a large steam leak (S1) with a plume of about 2 to 3 ft. in all directions at B1-12.9 near the vicinity of the NW condensor vacuum breaker. Exact source is unknown. Visible on camera # 1 , TG 471. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 471 B1-12.9.
389357 | CR | 20190129 | CAQ | C | E528-47 needs updated |  |  |  | N | NO | <D> **** Detailed Description **** While performing 02134381-03 it was documented that the FLA listed on the drawing is incorrect. The drawing needs to read FLA 1.7. <I> **** Actions Taken **** contacted supervision <N> **** Equipment Description **** .
389358 | CR | 20190129 | CAQ | D | Rod Accumulator Trouble Alarm P603-A7 drop 6-7 | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-0619 was clear prior to OPS 2 arriving at the HCU. With CRS concurrence drained water per SOP-CRD-HCU and alarm is clear. Nitrogen Pressure was 1100#. <I> **** Actions Taken **** Drained Water. | 02-00-CRD-HCU-0619,02-00-CRD-LS-129/0619
389359 | CR | 20190129 |  | 4 | PWC-FU-1 | N | N |  | N | YES | <D> **** Detailed Description **** flocculator has developed a leak from the shaft seal of the paddle wheel where it penetrates the flocculator. this is creating a potential slip hazard <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-PWC-FU-1
389360 | CR | 20190129 |  | 4 | CF-P-41A/B | N | N |  | N | YES | <D> **** Detailed Description **** during swapping from the CF-TK-42 to CF-TK-41, the 41A/B pumps failed to pump fluid/develop discharge pressure. no fluid was being discharged to the TSW weir. verified the suction path was aligned and full/vented, but neither pump would move fluid. recommend work order to jumper the suction line drains from CF-TK-41 and 42 to allow the use of the 42A/B pumps and the 41 tank. system still aligned to use CF-P-42B <I> **** Actions Taken **** secured the CF-P-41A/B informed MCR initiated CR/WR | 02-00-CF-P-41A
389361 | CR | 20190129 | CAQ | C | As-Found time out of tolerance range DMA-RLY-TK31/1 | Y | N |  | N | YES | <D> **** Detailed Description **** DMA-RLY-TK31/1 As-Found time out of tolerance range. AS-FOUND WAS 1648.6 SECONDS THE RANGE IS 1732.2 TO 1980.0 SECONDS. Relay operated as design but was before the min tolerance range. This relay was removed from service & tested on the bench to limit Mrule time on the desiel .A new relay was installed in its place per Task 01. <I> **** Actions Taken **** Notified supervisor & Ops | 02-00-DMA-RLY-TK31/1
389362 | CR | 20190129 |  | 3 | Workorder instructions and 10.23.7 do not match scope descri |  |  |  | N | NO | <D> **** Detailed Description **** Craft was delayed 5 hours due to a conflicting description of required inspection and replacement criteria. The work order 02109317-01 and 10.23.7 the WO described swivel replacement criteria as â€œas requiredâ€ and the P&Lâ€™s in 10.23.7 step 4.13 as â€œInspect crank arms and ball joints (swivels) for degradation and replace parts as required.â€ The MOT criteria only identifies to replace swivel like for like (regardless of their condition). This discrepancy were discussed with available engineering and with the OCC and a conservative decision was made to replace the swivels per the MOT. The work was stopped the WO was revised. <I> **** Actions Taken **** The work was stopped the WO was revised.
389363 | CR | 20190129 | CAQ | D | IDS 20/21 Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** IDS 20/21 Malfunction. Wire disconnected in IDS 21 on pole 202. <I> **** Actions Taken **** Compensatory Measure Posted. | 02-00-SEC-IDS-E/S/20/21
389375 | CR | 20190129 |  | 4 | EC: 17317 ¦ 30% Design Milestone Missed |  |  |  | N | NO | <D> **** Detailed Description **** The 30% Design Contract Technical Statement of Work is insufficient to ensure adequate protection of the Main Generator. <I> **** Actions Taken **** Previous scope changes have been incorporated into the 30% Design in an effort to ensure adequate Main Generator Protection. However, during the 30% Design review several concerns regarding the HMI and SPV solutions have been raised. Design Engineering is pursuing additional outside support to ensure that the 30% design meets the NERC/FERC and IEEE requirements for protection schemes for the Main Generator OEM. Recommend Trend-Only
389380 | CR | 20190129 |  | 4 | Late eSOMS entries for Maintenance |  |  |  | N | NO | <D> **** Detailed Description **** 2 Electricians and 1 Electricial Supervisor worked over their scheduled hours without updating eSOMS, and an I&C tech was entered in eSOMS as being on PT all day instead of for 1/2 day as listed on the PT slip. No violations occurred when eSOMS was updated. <I> **** Actions Taken **** Updated eSOMS with the correct hours and notified component group managers of errors.
389382 | CR | 20190129 | CAQ | C | Ineffective closure of CR 387202 | Y | N |  | N | NO | <D> **** Detailed Description **** CR 387202 was written to document the findings of the new mechanical seal that was sent with the new RHR-P-2A pump from Flowserve. It was identified that the long term storage of the pump warranted the rebuild of the mechanical seal (WO 02033672-82) With (CID 0056511322) before installation of the pump. With the seal vendor on site it was observed that there was a substance on the lapped seal faces that should not have been there, (CID 0056511322)was revised and now states that we should be prepared to remove coating that was put on the seal for long term storage. This is not correct. These seals should be kept dry and clean since they are lapped to within 2 light bands of flat With the cost of these seals being $10,000 and our cost saving initiative we should investigate why they are shipped this way, recognize that the potential for failure if this seal was installed as shipped, and the potential impact to the station. <I> **** Actions Taken **** Notified procurement engineering of the gap, notified my supervisor and manager, and initiated this condition report.
389385 | CR | 20190129 | CAQ | C | SOP-DG3-LU position for PP-4A BKR 1 different from SOP-ELEC- |  |  |  | N | NO | <D> **** Detailed Description **** While performing SOP-DG3-LU, PP-4A BKR 1 was found in the ON position. SOP-DG3-LU states it should be in OFF. The outside of the power panel has a laminated page from SOP -ELEC-AC-LU (Attachment 7.6 pg. 138) with BKR 1 in the ON position, and that it is a test point supply for OSP-ELEC -W102. SOP-DG3-LU needs to be updated. <I> **** Actions Taken **** MCR informed <N> **** Equipment Description **** SOP-DG3-LU
389387 | CR | 20190129 |  | 3 | Procedure changed required for DG Gov sight glass |  |  |  | N | YES | <D> **** Detailed Description **** During DG3 maint activities it has been identified that with the change to taller oil sight glass on the gov that the respective procedures need clairification/enhancement with respect to oil level setting. System engineer needs to provide prodedure mark up for the change. The level as currently set is acceptable for the DG3 PMT run. <N> Procedures should be revised to direct the standby oil level be 1/4 inch to 1/2 inch above the line in the sight glass. | 02-00-DG-ENG-1C
389389 | CR | 20190129 |  | 4 | CF-V-824 has a stem leak. | N | N |  | N | YES | <D> **** Detailed Description **** While starting CF-P-41B an old chemical stain was observed on the floor below CF-V-824. A chemical crust was observed around the stem of CF-V-824. This is a ball valve that can be replaced when CF-P-41A is tagged out for replacement per WO 02137371. Please investigate and get information needed to order replacement valve and replace when the above work order is worked. <I> **** Actions Taken **** Informed supervisor and wrote this AR/WR. <N> **** Equipment Description **** cwph | 02-00-CF-V-824
389390 | CR | 20190129 | CAQ | D | Malfunction on SEC-IDS-20 21. | N | N |  | N | YES | <D> **** Detailed Description **** CAS received a Malfunction on SEC-IDS-20 21. A walk-down was conducted on each zone, No clear cause was identified. <I> **** Actions Taken **** Compensatory Measures were posted. CR/WR Generated | 02-00-SEC-IDS-E/S/20/21
389391 | CR | 20190129 |  | 3 | eSOMS issue prevents verfication of Tracking and Control Rec |  |  |  | N | NO | <D> **** Detailed Description **** An issue has been discovered that prevents users from performing verifications in the eSOMS Tracking and Control module. Testing of the issue shows that the issue may be associated with how eSOMS authenticates the user. This issue was not present in the test regions during testing. <I> **** Actions Taken **** A critical case has been submitted to the vendor.
389393 | CR | 20190129 |  | 3 | CF-P-41A/B and CF-P-42A/B plug up when idle. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** A trend has been observed that when CF-TK-41 and 42 are swapped for service the oncoming tankâ€™s pumps wonâ€™t pump. A CR/WR ends up being written and the FIN team primes the oncoming pump per SOP-CW-CHEM-MAINT. Currently the tanks are in service until level drops to 700 gallons at which time the head pressure is diminished to the point of the pump not pumping any longer due to low suction pressure. This AR/CR is being written to consider swapping tanks on a more regular schedule such as weekly to minimize the clogging of the chemical lines and the subsequent need to prime the pumps to get them pumping again. <I> **** Actions Taken **** Informed supervisor and wrote this AR/CR.
389394 | CR | 20190129 |  | 4 | RRC-CB-ASD/2B/2 AUXILIARY SWITCH (52) | N | N |  | N | NO | <D> **** Detailed Description **** Per 10.25.218 step 7.17.4.c contact resistance above criteria limit of less than 1 ohm. Per engineering replacement of aux switch required CAT ID 20874. <I> **** Actions Taken **** Notified supervisor and engineering. Resolution obtained from engineering per step 7.17.4.c.6. <N> **** Equipment Description **** RRC-CB-ASD/2B/2
389397 | CR | 20190129 | CAQ | D | TEA-dPIS-53 (HEPA filter dP) above setpoint | N | Y |  | N | YES | <D> **** Detailed Description **** during performance of CI-11.13, TEA-dPIS-53 was observed above the setpoint. Step 7.1.11 of CI-11.13 states to submit a work request. <I> **** Actions Taken **** Wrote CR to document HEPA filter dP above setpoint. Initiated WR. Entry made into Chemistry Log <N> **** Equipment Description **** TG 441 Chemistry sample room | 02-00-TEA-FN-52
389399 | CR | 20190129 | CAQ | B | (QA) 2017 MCR Essential Lighting LCS SV Went Late | N | Y |  | Y | YES | <C> RISK: Medium. CAUSE: Uncertain. The issue in this CR will be addressed in CR 389235 <D> **** Detailed Description **** (QA) Monthly Surveillance Requirement SR 1.10.7.2 for Main Control Room (MCR) Essential Lighting was not completed by the late date in 2017 due to improper deferral requests, causing the station to meet the requirements to enter the RFO 1.10.7 Condition A; however entry was recognized due to the deferrals. SR 1.10.7.2 was subsequently met by Work Order (WO) 02103396-01 (Finished 5/30/17) and monthly through the most recent WO 02128987 (Finished 1/2/19). The station was not in compliance with the Licensee Controlled Specifications (LCS) action statements for the late surveillance for two monthly intervals. This is an extent of condition item for the issue identified in AU-MN-19 Finding AR-CR 389235. (See EDMS for full details) <I> **** Actions Taken **** Notified Quality Management, Maintenance, and Operations. This issue was identified during the Maintenance Audit AU -MN-19. <N> **** Equipment Description **** Legacy issue with MCR Essential Lighting SR 1.10.7.2 <R> The REP/REGE assignments for this CR are not required and are being cancelled. This condition is not reportable to the NRC and does not challenge past operability of plant equipment. Concurrence for cancellation has been obtained from Regulatory Affairs Management.
389400 | CR | 20190129 |  | 4 | COND-V-156C stem/ packing leakage approx 40 drop/min | N | N |  | N | YES | <D> **** Detailed Description **** COND-V-156C stem/ packing leakage approx 40 drop/min water dripping on pump skid, packing nut already extremely tight. Recommend repack/ replace <I> **** Actions Taken **** Informed MCR | 02-00-COND-V-156C
389402 | CR | 20190129 | CAQ | C | Extent of Condition Results | N | Y |  | N | NO | <D> **** Detailed Description **** During the Extent of Condition review for AR-389235, four items were found. These four PMs were deferred beyond their original asset suite late date, but have been performed and are current in Asset Suite 00380432 Defer PMRQ 00016493-01 5/22/2018 00381092 Defer PMRQ 00006829-05 6/7/2018 00380424 Defer PMRQ 00006829-03 5/22/2018 00378238 Defer PMRQ 00016487-08 3/25/2018 <I> **** Actions Taken **** Documented finding in AR. Discussed with Maintenance Management. <R> The REP/REGE assignments for this CR are not required and are being cancelled. This condition is not reportable to the NRC and does not challenge past operability of plant equipment. Concurrence for cancellation has been obtained from Regulatory Affairs Management.
389403 | CR | 20190129 | CAQ | C | Environmental Qualification Instruction Not Provided |  |  |  | N | NO | <D> **** Detailed Description **** Documentation Issue - Qualification impacting maintenance requirement was not included in drawing M944. This condition does not impact the environmental qualification but is a documentation issue requiring drawing M944 to be revised to include appropriate requirements for waterproofing the Main Steam Radiation Monitor detector connectors (MS-RE-3A thru 3D). Main Steam Radiation Monitor detectors require a water proofing seal at the cable connector to detector connection points to assure detector will not be impacted by high humidity in the Steam Tunnel due to equipment steam or water leaks. QID 277002-01 rev 2 bases environmental qualification on use of a waterproofing seal applied per GE drawing 184C4673. Procedure EQP-1-1 Rev 8 requires qualification impacting maintenance activities to be included in drawing M944. This was not done. <I> **** Actions Taken **** In reviewing History in D030 Asset Suite, two cases were noted where MS-REâ€™s were worked on. In both cases the detector cables were re-sealed using applicable heat shrink material assuring the moisture intrusion requirements were maintained. From this review it is concluded that normal Maintenance work practices following applicable drawings did get the water proofing needed on the detector to cable connectors. Suggest assign to Plant Programs to revise drawing M944.
389404 | CR | 20190129 | CAQ | C | CCER has incorrect information |  |  |  | N | NO | <D> **** Detailed Description **** Documentation Issue does not impact equipment. CCER C92 -0829 rev 00 does not correctly describe the functions of the Main Steam Radiation Monitor detectors (MS-RE-3A thru 3D). It states the REâ€™s can isolate the MSIVâ€™s and MS line drains. This function was removed by an authorized License Change. In addition the detectors provide a trip function for the mechanical vacuum pumps and valves under certain conditions. A note that the functions of the Monitors was anticipated to change was included in the CCER (Rev 0 circa 1992), but since the change did occur with some additional functions added, the note is out of date and the existing text is incorrect. <I> **** Actions Taken **** AR/CR 00252678 previously identified this issue but was closed based on the conclusion that the safety functions were correctly coded into MEL even though the functions have changed and the text is out of date. Engineering Standard 321, Rev 13 correctly identifies the safety and non-safety functions of the Main Steam Radiation Monitors. DES-4-7 requires the CCER be superseded when a deficiency exists in its text or classification.
389407 | CR | 20190129 |  | 4 | Vendor trailer has flat tire |  |  |  | N | NO | <D> **** Detailed Description **** A flat tire was found on a flatbed trailer being used for rad waste shipment to an offsite facility. Flat was discovered during the procedure required vehicle inspection (PPM 11.2.23.1). Trailer and load was moved outside PA and repair services contacted to replace tire. <I> **** Actions Taken **** Shipping supervisor and RPM notified. Tire replaced and shipment left site. Close to trend.
389410 | CR | 20190129 |  | 4 | MT-CRA-1 Scissor Lift on TG501' Stuck in the Raised Position | N | N |  | N | NO | <D> **** Detailed Description **** A large scissor man lift supporting MT-CRA-1 main hoist upgrades has become stuck in the raised position. The manlift is positioned between the "A" and "B" crane girders and crane power is off. <I> **** Actions Taken **** A second scissor lift was immediately raised to recover the personnel from the elevated work area. Several attempts were made to lower the stuck manlift. The rental equipment vendor has been contacted and is sending a technician to repair the machine. An urgent access request for the tech has been transmitted to Security and HP for processing. ------------------------------------------ Inspected the lift in its raised position. The base is substantial with outriggers that are set. It is unlikely to move. In addition, the top of the lift is between two beams that would restrain it from tipping over. The area around the lift is also marked with danger tape to warn personel to keep clear. See the pictures in the EDMS folder. According to PPI ENG CIVES-6, it is not located in a Seismic Catagory 1 area.
389411 | CR | 20190129 |  | 4 | Security door T207 door latch needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security door T207 door latch is not operating by design and needs maintenance. <I> **** Actions Taken **** CR/WR initiated. Security supervision notified. <N> **** Equipment Description **** Door T207, barrier between Turbine Building and GSB roof.
389412 | CR | 20190129 | CAQ | C | Verify impacts of CRD performance on EC16300 |  |  |  | N | NO | <D> **** Detailed Description **** Through trending and monitoring of Control Rod Drive flows and performance and working with the system engineer, Control Blade 14-55 was identified to have an insert stall flow greater than 4 gpm and a step increase in Control Rod Drive flows for the majority of the control blades was identified (CR 380528). As a result of the increased drive flow and other challenges experienced with the control rod performance, recommend Reactor Fuels review EC16300 and verify the population impacts for both Settle Time Testing or Full Stroke Testing. <I> **** Actions Taken **** Wrote the CR and discussed the issue with the Control Room. Talked with Steve Kartner to ensure that is the only Control blade with a stall flow greater than 4 gpm. Discussed the issue with my supervisor.
389413 | CR | 20190129 |  | 3 | Doc Nos not updated in SharePoint when Asest Suite Change |  |  |  | N | NO | <D> **** Detailed Description **** In reviewing records it was determined that at some point in the past the EDMS Sync Service which updates SharePoint when Asset Suite is changed did not function correctly. Identified records where document numbers changed by datamod were not updated in SharePoint. Current review indicates these events happened in 2015 to 2017. Retrieving images from Asste Suite is not impacted by this issue. <I> **** Actions Taken **** Notified Supervisor. Veriified that recent changes were updated by the EDMS Sync Service. <N> No actions are required. document numbers were corrected and sync service validated to be correctly working.
389414 | CR | 20190129 | CAQ | B | [NRC] Personnel observed wearing FitBit devices in Plant |  |  |  | N | NO | <C> CRBB - CR Bring Back from OPS to Address severity and ownership. Risk: Medium Causes: Complex / Partial Conduct of Investigation template requested by ITMGMT <D> **** Detailed Description **** Various plant personnel were observed by the NRC wearing FitBit devices in the plant, including the control room. FitBits are not listed as approved devices in 1.3.72, Control of Portable RF Transmitting Devices. Additionally this needs to be assessed for impact to Cyber Security Requirements.
389415 | CR | 20190129 |  | 3 | Vault B105 was found with 18" of water in it. | N | N |  | N | YES | <D> **** Detailed Description **** While performing 02132137-01 the vault was found with higher then normal water levels. FD-P-15 should keep the level below one foot. It appears FD-P-15 is not working properly. <I> **** Actions Taken **** Contacted my supervisor and the system engineer. Pumped out the vault with a manual pump. recommended installing a temporary pump until repairs are made. <N> **** Equipment Description **** CWPH . The condition identified under this CR will be addressed by EC 17431 and WO 02137390 which are cross referenced under this CR. No additional actions are required. No assignments are required. This CR will be closed to the WO and EC documented under the CRoss References panel. | 02-00-FD-P-15
389416 | CR | 20190129 |  | 4 | Snapshot SA Recommendation Assignment not created |  |  |  | N | NO | <D> **** Detailed Description **** This is an administrative issue. A snapshot self-assessment recommendation assignment was not created in May 2018 as referenced in Snapshot Self-Assessment report 378015. The recommended action was to communicate at the Training Monthly Department meeting how Columbia ensures oversight is provided for accreditation related action closure. The action was completed (the material was presented) at the May 2018 Training Monthly Department Meeting but completion was not documented in the closure information of the AR. <I> **** Actions Taken **** Reopened Snapshot Self-Assessment, created recommendation action 378015-08 and added closure notes (including the upload of the Monthly Department Meeting presentation where the action was completed). Contacted Quality Manager who identified the issue.
389417 | CR | 20190129 |  | 3 | Revision needed for ABN-HVAC to allow for MCR cooling |  |  |  | N | NO | <D> **** Detailed Description **** ABN-HVAC needs revision to add steps to allow for opening of doors to provide cooling, in an effort to allow for temperature reduction prior to evacuating the control room. . Insert the following steps after step 4.3.10 and prior to step 4.3.11 of ABN-HVAC . IF temperatures in the Control Room become excessive, PERFORM the following: . ENTER TS 3.7.3. . NOTE: TS 3.7.3.B allows CREF boundary to be inoperable for up to 90 days, with PPM 1.3.57 mitigating actions. . OPEN the Control Room doors as determined by the SM. <I> **** Actions Taken **** Initiated CR. Disposition to Ops procedures.
389419 | CR | 20190129 |  | 3 | Procedure Change request SOP-FLEX-GEN-DG5-START |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.2.3.g 1) (page 9) describes the operation required to raise engine speed of DG5 during startup, however, the step states: "IF voltage must be raised,...." This appears to be a copy/paste error from the previous step describing how to adjust voltage. Replace the word "voltage" with the word "speed" <I> **** Actions Taken **** Generated this AR
389420 | CR | 20190129 |  | 3 | OSP-ELEC-S703 change required |  |  |  | N | NO | <D> **** Detailed Description **** OSP-ELEC-S703 requires a change to step 7.3.62. Step 7.3.62 currently has the Operators compare the crankcase oil level, of an idling DG3, to the crankcase oil level previously recorded with DG3 in standby. Substeps b, c, and d can not be performed due to the fact that comparing an idling oil level to a standby oil level is not an accurate indication of oil usage. Please remove substeps b,c,and d from Step 7.3.62. This is a different issue than what was recently corrected with the Monthly DG surviellances. There is not a different step to compare the oil level taken in Step 7.3.62, to. The substeps should simply be removed. A step already exist (7.3.80) to verify shutdown oil level at the end of OSP-ELEC-S703. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** osp-elec-s703
389421 | CR | 20190129 |  | 3 | Lessons learned from WO 02108171-01 DO-M-P/2 Baker test |  |  |  | N | NO | <D> **** Detailed Description **** Incorporate lessons learned from task 02108171-01 DO-M-P/2 On-Line Motor Testing. During DG3 outage, while determining the best way to run DO-M-P/2 for On-Line Motor Testing, it was found that having Operations perform a partial OSP-DO-Q703 allowed Electricians and Operations to control and coordinate the running of this motor. For future occurrences of PMID 00023612 include a support task for Operations to perform this partial surveillance. This will allow for the controlled draining and refilling of the day tank and a controlled run of the Motor saving time and allowing for better planning and resource management in the future. This would also apply to DG1 PMID 23610 and OSP-DO-Q701. This would also apply to DG2 PMID 23611 and OSP-DO-Q702. <I> **** Actions Taken **** Shared lessons learned with Electrical Manager and Scheduler. Initialed this CR. <N> **** Equipment Description **** DO-M-P/1A, DO-M-P/1B, and DO-M-P/2 Baker Testing (Fuel Oil Transfer Pumps
389422 | CR | 20190129 | CAQ | D | Rev 59 of the ODCM in asset suite is not correct |  |  |  | N | NO | <D> **** Detailed Description **** Rev 59 of the ODCM in asset suite is not correct. The copy of Amendment 59 on the Licensing Tree is correct. <I> **** Actions Taken **** Provided a corrected PDF to RIM. Notified Supervisor. Wrote CR. Recommend Trend.
389423 | CR | 20190129 |  | 3 | DG3 Low Governor Oil Level | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of SOP-DG3-STBY governor oil level was observed to be approx. 1" below the top of the sight glass, the specification is within 1/4" of the top of the sightglass. Need governor oil added to within specifications. <I> **** Actions Taken **** CRS informed | 02-00-DG-ENG-1C
389424 | CR | 20190129 |  | 4 | Hi pressure steam leak discovered on RFW-DT-1A | N | N |  | N | YES | <D> **** Detailed Description **** The 1â€ steam line from MS-V-172A has a through-wall leak on 90 degree elbow; the high pressure steam leak has blown through the insulation on the feed turbines steam chest, and could possibly be impinging on the steam chest itself. Need to have a protective shield installed to avoid steam damage to the steam chest. Believed to be the 1â€ high pressure steam line from MS-V-172A to the common manifold under the turbine that drains via MD-V-8A to MD-TK-1. See pictures and video on EDMS screen. <I> **** Actions Taken **** informed Shift Management <N> **** Equipment Description **** located on east side of RFW-DT-1A skid | 02-00-RFW-DT-1A
389425 | CR | 20190129 | CAQ | D | Accumulator Trouble Rod 18-07 | Y | N |  | N | YES | <D> **** Detailed Description **** 1/29/19 at 2003 Accumulator Trouble alarm for Rod 18-07 was received for High Water. <I> **** Actions Taken **** Cleared high water level per SOP. <N> **** Equipment Description **** RB 522. | 02-00-CRD-HCU-1807
389426 | CR | 20190130 |  | 4 | Work Order Support Task taken from Finished to Working |  |  |  | N | NO | <D> **** Detailed Description **** Work Order 02132276-02 was inadvertently taken to Finished in Data Glance, and required the Shift Manager to take back to Working in Portal J. This support task had the Data Glance easy button which expedites the task through the completion process, removing it from Data Glance. It will need to be set to Finished in Portal J. This CR was written to document the status change and the necessity to take this Task to Finished in Portal J. <I> **** Actions Taken **** Contacted Shift Manager to take back to Working. Notified Electrical Craft Supervisor to Contact PSRO or eWP Support to take to Finished in Portal J when the work is complete.
389427 | CR | 20190130 | CAQ | D | TDAS communication between SCAN-2 and MONCR2 failed | Y | N |  | N | YES | <D> **** Detailed Description **** TDAS communication between SCAN-2 and MONCR2 failed. Did terminate and re-initiate twice but issue still there. Need to investigate and resolve the issue. <I> **** Actions Taken **** Stop and re-initiate twice but issue still there. CRS informed. | 02-00-TDAS-COMP-8715
389442 | CR | 20190130 |  | 3 | SOP-ELEC-480V-OPS needs to be reevaluated |  |  |  | N | NO | <C> CR (389442) downgraded from CAQ C to Severity 3 at the request of MRT (OFM) on 02.07.2019. <D> **** Detailed Description **** While preparing for the outage it was discovered that SOP -ELEC-480V-OPS section 5.8 could not be performed safely with the changes to ISPM-20 and the calorie rating of the switchgear. In the SOP it calls for electricians to install jumpers in the back of E-SL-21 to complete a make before break transfer E-SL-21 to E-SM-2 from E-SL11. What is needed is a reevaluation by engineering to either find another place to install these jumpers that would comply with ISPM-20 or evaluate a break before make transfer and what equipment would be effected and what consequences this might have on the continuing outage work. <I> **** Actions Taken **** Involved Planning and Operations in this discussion to help find a resolution. Wrote this CR to track resolution.
389449 | CR | 20190130 |  | 3 | (Non EN/CGS) Backlog Impacted by Damaged Standard |  |  |  | N | NO | <D> **** Detailed Description **** During an assessment a sound level generator was found inoperable and determined to need repair. This was an unexpected situation and as a result several commercial customers will not have their equipment returned in a timely manner. This does not affect CGS and should be assigned to AR-CALSERV recommend Cat. 3. <I> **** Actions Taken **** Notified customers impacted. Created CR and obtained quote for repair with an expedite placed on the order.
389451 | CR | 20190130 |  | 3 | DES-2-23 update for Section 3.2 NOTE is needed |  |  |  | N | NO | <D> **** Detailed Description **** The NOTE in DES-2-23 Section 3.2 between step 3.2.1 and step 3.2.2 (page 6 of 20) refers to the incorrect process for afterhours, weekends or non-standard times. Currently, this NOTE sends the user to DES-2-22 (Project Field Implementation, Configuration Control and Turnover). However, DES-2-22 does not contain the described process. The NOTE should refer the user to SWP-DOC-01 (Document Control). SWP-DOC-01 Section 4.10 (Redline of Drawings Afterhours, Weekends, or Non-Standard Times) is the described process. Suggest resolution assignment to the DES-2-23 Sponsor (Design Engineering).
389452 | CR | 20190130 |  | 4 | SA-V-99/35 has small leakby after closing | N | N |  | N | YES | <D> **** Detailed Description **** WO-02110485-01 was completed SAT for analyzing the breathing air at SA-V-99/35. However, upon closing the globe valve, there remained a very small amount of air leaking by the valve. This valve is located in the Southwest corner of the machine shop in the GSB (Yakima Bldg). <I> **** Actions Taken **** Notified PSRO and MCR. | 02-00-SA-V-99/35
389453 | CR | 20190130 |  | 3 | SWP-DOC-01 update for Section 4.10 may be needed |  |  |  | N | NO | <D> **** Detailed Description **** SWP-DOC-01 (Document Control) Section 4.10 provides procedural guidance for redline of drawings afterhours, weekends, or non-standard times. Per conversation with RIM personnel 01/30/19 AM, there is a disconnect between what RIM personnel expect with respect to redlined drawings and what SWP-DOC-01 Section 4.10 currently directs. 1) RIM personnel expect/need to see a Minor Revision number indicated on the redline drawing provided to them. SWP-DOC-01 Section 4.10 does not currently direct the personnel preparing the redline to include this. 2) RIM personnel expect/need to be provided with a phyical hard copy of the redlined drawing. SWP-DOC-01 step 4.10.11 currently states that RIM may be provided hard copes either a copy or electronic file. Suggest resolution assignment to the Sponsor for SWP-DOC-01 (RIM).
389454 | CR | 20190130 | CAQ | C | IRM-EMSQ-601F signal not correct in sect 7.5 of ISP-IRM-X306 | Y | Y |  | N | YES | <D> **** Detailed Description **** While Performing ISP-IRM-X306 (WO 02118368-04), At step 7.5.42, of ISP-IRM-X306, Signal voltage reading was not correct. Craft Informed supervisor and team was expanded to involve engineering. adjustment of AR11 module was performed IAW step 7.5.45 of the survielance. After performing the adjustment, the Signal voltage was good in range 6 and 5, but increased in range 4 and 3 and, in range 2 and 1 the signal was 13.99 vdc. Suspect an issue with the Amplifier and Attenuator Module A11 or IRM-EAMP -2F. . Supervisor and Engineering informed. <I> **** Actions Taken **** Wrote CR and WR and Contacted Engineering. | 02-00-IRM-EMSQ-601F
389455 | CR | 20190130 |  | 3 | CC-174 Certificates Issued with Incorrect Reference |  |  |  | N | NO | <D> **** Detailed Description **** Certificates Issued with Incorrect Reference due to update of QM-1 to revision 11. The revision to the Quality Manual (QM-1) was implemented on 10 January 2019 and the Certificate Statement referencing the QM-1 was not updated until January 22, 2019. The revision did not affect the quality assurance program in any way that impacts compliance with NQA-1, 10CFR 50 AppxB or ISO 17025:2005 outside of the reference. This revision is a first time evolution for the Standards Lab to utilize APPW for our Quality Manual and the timeline for submission and implementation was not apparent. Notification of the implementation was not received by individual responsible for updating the certificate language. Certificate language has been corrected and CC-174 has been initiated. Recommend assign to AR-CALSERV Category 3. <I> **** Actions Taken **** Certificate language has been corrected and CC-174 has been initiated. Entered non-conformance into CAP and began investigation. <N> All corrections have been reissued. Corrections have been reviewed for acceptance.
389456 | CR | 20190130 |  | 3 | (Non EN/CGS) CC-165 thru CC-173 Assessor Deficiencies |  |  |  | N | NO | <D> **** Detailed Description **** (Non EN/CGS) CC-165 thru CC-173 Assessor Deficiencies are being tracked through this CR in accordance with the Customer Complaint process in the Standards Lab qualtiy program. A2LA assessors conducted an onsite Accreditation Assessment Jan 22-24, 2019 and at the exit of the assessment there were 9 Deficiencies assigned and they will be addressed following the A2LA I102 - Instructions for responding to the Assessor Deficiency Report. This CR is to provide action tracking and corrective actions to the department. Recommend Assign to AR-CALSERV Category 3. <I> **** Actions Taken **** Initiated CC-165 thru CC-173 and following A2LA I102 Instructions, preparing response to accrediting body. Initiated this CR.
389458 | CR | 20190130 |  | 4 | CW-FN-17 has a cyclic Chirping | N | N |  | N | YES | <D> **** Detailed Description **** CW-FN-17 has a cyclic Chirping. Chirp sounds like it is coming from the fan side oif the motor. ther is a video attached that catches it but it is not as loud as it is by the fan. <I> **** Actions Taken **** wr/cr | 02-00-CW-FN-17
389460 | CR | 20190130 |  | 4 | E-AY-TR/N1 has a service light ( Blue) lit. | N | N |  | N | YES | <D> **** Detailed Description **** E-AY-TR/N1 has a service light ( Blue) lit. <I> **** Actions Taken **** wr/cr | 02-00-E-AY-TR/N1
389461 | CR | 20190130 |  | 3 | IEBS tables are not updating to the security computer (AIM) |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Access requested our daily corporate transfer once we issued several green badges. It was discovered by the IT Analyst, the IEBS badge tables have not been updating since 0900 on 01/29/19. We are unable to transfer any data on the corporate side currently. Contact Access Authorization for more details. <I> **** Actions Taken **** Notified Emergency Services Manager and computer engineering. <N> **** Equipment Description **** IEBS server in CAS
389463 | CR | 20190130 | CAQ | D | Hinge mechanism damaged requiring repair | N | N |  | N | YES | <D> **** Detailed Description **** There is a damaged hinge on a large gate that requires repair. Contact 2185/2141 for additional info. <I> **** Actions Taken **** Unit removed from service, faclilties contacted, security management notified <N> **** Equipment Description **** Security vehicle trap, Compensatory measures are in place as a result of damage.
389465 | CR | 20190130 | CAQ | C | Improper Radworker Behaviors Observed on RB 606' |  |  |  | N | NO | <D> **** Detailed Description **** Radiological Operations personnel observed an individual displaying less than adequate radworker practices on the RB 606 immediately adjacent to the equipment pit access hole. The individual was observed handling highly contaminated slings draped down into the equipment pit without informing or involving radiological operations. In addition, the individual was sitting on the floor inside of the contaminated area without a barrier in place as required by the radiation work permit. His legs were extended beyond the plane of the equipment pit hole. Upon identifying the improper behaviors, the RP technician stopped the individual and processed him through the personnel contamination monitor. The individual's lower legs showed signs of nuisance contamination (up to 30 ccpm by direct frisk). Contamination levels did not exceed the threshold to be considered a PERCON. <I> **** Actions Taken **** The RP technician stopped the work activity and surveyed the individual for contamination. The individual was restricted from the RCA pending discussion with radiological operations supervision. Coaching was provided for alignment on radiological standards with the individual and his supervisor. Following that session, the RCA restriction was lifted.
389466 | CR | 20190130 | CAQ | C | Contractor vehicle struck and damaged security barrier | N | N |  | N | NO | <D> **** Detailed Description **** Contractor got into vehicle and foot slipped off clutch, causing vehicle to move forward, striking security barrier. <I> **** Actions Taken **** Driver contacted supervisor, notified security, shift manager, industrial safety, and manager in accordance with ISPM-01 . Verified with security appropriate compensatory measures are in place. Took Driver to FFD for testing and fillled out form 23174. Started event investiagation in accordance with GBP-IRP-02. <N> Compensatory measures are in place as a result of damage to security barrier.
389468 | CR | 20190130 |  | 3 | Observation database org code search is not working |  |  |  | N | NO | <D> **** Detailed Description **** I am unable to search on a specific org code (52220) in the new devonway observation program. A canned report was created to retrieve all observation attribute detail for a specific time frame. The saved report can be edited to obtain department specific data. When you select â€œobserved org codeâ€ equals â€œ52220â€ no items return. The original report that contains the entire station does contain ops related information so there is data to be retrieved. A second option by selecting specific individuals in the org 52220 also does not work. <I> **** Actions Taken **** Ops and RP have been working with IS to resolve this issue. A work around was presented today and the results vary each time the report is run. This data is needed in the short term to support department trending as well as monthly department meeting data. IS continues to communicate with Devonway with no successful results.
389469 | CR | 20190130 | CAQ | C | WO 02119011 - PPM 15.2.4 Procedure Errors |  |  |  | N | YES | <C> CR (389469) upgraded from Severity 3 to CAQ C at the request of MRT (OFM) on 02.07.2019. <D> **** Detailed Description **** While performing WO 02119011 15.2.4, FP-ZONE-65 2-YEAR SENSITIVITY CHK, craft personnel arrived to step 7.2.5.x steps C and D. PPM 15.2.4 Major Rev 13 released on 5-16-18 changed steps C and D to require the craft personnel to ensure the FSP-7 CP-35 TROUBLE (Yellow Lanp) clears in addition to FCP-3 TROUBLE alarms (Drops 14.5 and 17.4). The C and D steps are incorrect in the procedure. . Before EC 13537 Fire Alarm and Detection Upgrade was implemented FP-CP-FSP7 utilized a CP-30 control module. After EC 13537 Fire Alarm and Detection Upgrade was implemented the CP-30 was upgraded to a CP-35 control panel. The CP-35 control panel fire alarm annunciation does not clear a trouble indication. On the old CP-30 control module, if a fire alarm was received trouble indications were cleared on the FSP-7 module and FCP-3. . This is a procedural error, not an equipment issue. Route CR to Fire Protection (AR-TEFP) to ensure procedure changes are made. <I> **** Actions Taken **** Initiated CR to correct procedural errors. <N> **** Equipment Description **** W487 K0/15.1 | 02-00-FP-CP-FSP7
389472 | CR | 20190130 |  | 3 | Broken Display port on corporate computer |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The IS Solution Center was called to support a potentially failing computer monitor that was flashing / not working correctly. A tech went to diagnose and found the display port connection on the computer had been broken. The display port is no longer functional, leaving the computer with only one port to display on one monitor and cannot be repaired. The display port cable locks into the connection and are similar to an HDMI port; small, flimsy, and can be broken if care isnâ€™t taken when moving. When moving computers, monitors, and components, whether from one side of the desk to another, OR to another location, care should be taken and cables should be unplugged. GBP-IS-01 Governs the moving and relocation of computer equipment. <I> **** Actions Taken **** I informed the requester of the cause for the flashing monitor and set up the computer to user only one monitor at this time. Upon return to the Solution Center, I notified my supervisor and a supervisor for the userâ€™s group.
389473 | CR | 20190130 |  | 3 | EC 16616 had insufficient level of detail on FP impacts |  |  |  | N | YES | <D> **** Detailed Description **** EC 16616 â€œDehalogenation Systemâ€ is issued and is currently being installed at the CWPH. EFIN notified Fire Protection that the project includes the FP-P-3 jockey pump as a backup water source to the dehalogenation system CL -SKID-2 when TSW pumps are off. This new piping design is shown on M508-1 (in EC 16616 EDMS R0 page 112). The fact that this project was tapping into TSW piping that comes from the FP system was not stated in the EC package text. The EC section on â€œPlant Impact and Integration - Classical Fire Protection Plan Impactâ€ section does not address this issue, which resulted in multiple rounds of FP mod review comments did not reviewing for this aspect. The 50.59 AD-17-0816 should have marked Fire Protection Yes and additional review of fire protection regulatory impact performed via a LBIE. FSAR F.2.4.1 includes a paragraph of all the fire protection water supply system interfaces with other plant systems. Although this new system interface is small, a LDCN may be warranted to list this new system interface. There is not an operability issue to the LCS 1.10.1 primary water supply system since the maximum water demand through the new sample line is 500 â€“ 1000 mL/min (about 1/8 to 1/4 gpm). This aspect has now been reviewed, is not a design concern, and construction can continue. <I> **** Actions Taken **** Discussed with Design Engineering, System Engineering, Licensing, and FP staff. <N> **** Equipment Description **** CWPH . FCR 16616R000Q has been issued and the LDCN-19-011 has been approved (reference 381705-10). All actions have been completed. This AR can now be closed. .
389474 | CR | 20190130 |  | 3 | Hydraulic Fluid Release at T-15 Nine Canyon Wind Farm |  |  |  | N | NO | <D> **** Detailed Description **** During the preparation for a Gear Box change at the Nine Canyon wind farm (T-15) some non-hazardous hydraulic fluid was release from the system and dripped out of the Nacelle. Less than 2 gallons of material was released and estimated that approximately 1 gallon of material made contact with the ground. The remaining material was either captured in the Nacelle or on the exterior of the tower. The hydraulic fluid was residue material not completely drained from system. E&RP notification was made by the supervisor. Crews went to work to clean up the spill affected areas upon identification. The area to be cleaned was found to be frozen and made cleanup efforts difficult. With E&RP concurrence the final clean will be performed once weather permits. No injuries are associated with this event. <I> **** Actions Taken **** Notifications to E&RP and Management team. Perofrmed Clean up efforts with crew. Copies of the MSDS/SDS have been uploaded to the EDMS . Not related to CGS. <N> **** Equipment Description **** Nine Canyon Wind Farm Tower 15
389475 | CR | 20190130 |  | 4 | No tape on floor near E-IR-P031 |  |  |  | N | NO | <D> **** Detailed Description **** there is a cuation sign on E-IR-P031 (RX 501) that states Radio operation prohibited with in taped area. However there is not any tape arounf the panel. Either tape needs to be placed on floor to designate the boundary or the sign needs to be updated to specify a distance that must be maintained (i.e. No radios within ft) REfer to 1.3.72 . Need to Update Sign or add tape. <I> **** Actions Taken **** Wrote CR to document <N> **** Equipment Description **** E-IR-P031
389476 | CR | 20190130 |  | 3 | Occ. Health contact required following noise exposure |  |  |  | N | NO | <D> **** Detailed Description **** On the morning of 1/30/19, an employee reported exposure to elevated noise levels during limited-scope security drills on night of 1/24/19. The elevated noise levels were created by SAAB drill weapons used by drill participants. This exposure required contact with Occupational Health on 1/30/19 and an off-site visit to an audiologist for an examination. The exposure occurred as the employee exited MT-ELEV-4 on TB 441' elevation. The SAAB drill weapon was being used in close proximity to the elevator. The employee was aware of the limited scope drill activity. Hearing protection is not required for the area and not being used by the employee as they exited the elevator. <I> **** Actions Taken **** Employee's Supervision, Occupational Health and Security were notified of the report. Started Incident Reporting process. <N> The Work Week Manager, Radiation Protection and Operations are communicated with well in advance to conducting Security Limitied Scope Drills and Force on Force Exercises. The Shift Manager grants final approval just priot to starting these activities and then a PA announcement is made to advise plant personnel of the activites and there location. After this CR was submitted additional drill signs were placed at elevator exits and "Hearing Protection is Required" was added to PA announcent.
389477 | CR | 20190130 |  | 3 | Revise ABN-ELEC-LOOP |  |  |  | N | NO | <D> **** Detailed Description **** ABN-ELEC â€“LOOP subsequent actions are not consistent with CB 7/75/1 and 8/85/1 response to a loss of offsite power. Theses busses will always load shed on a LOOP since the loss of both RPS busses will cause RC-1 and RC-2 to receive a level 2 signal. Ultimately a LOOP will always cause a loss of TSW whether or not there is an actual level 2 or 1.68 psig condition. Ref EWD-108E-001, 003, 005, 007, EWD-46E-82, 86, EWD-1E-096, 98 and 99. See attached EDMS for recommended changes. <I> **** Actions Taken **** See attached EDMS for recommended changes.
389478 | CR | 20190130 | CAQ | D | Rod Accumulator Trouble Alarm for CRD-HCU-18-03 | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-1803 was due to pressure. OPS 2 charged per SOP-CRD -HCU and alarm is clear <I> **** Actions Taken **** CRS informed | 02-00-CRD-HCU-1803
389479 | CR | 20190131 |  | 4 | HWC shutdown. | N | N |  | N | YES | <D> **** Detailed Description **** Received HS Y1184-STAT STOP alarm which is the Hydrogen system E-stop activated alarm. Also received a device down alarm which is a HSSF HCP communication error or dynamic disable. The YV-170 valve indicated closed. and the line pressure is slowly decreasing. <I> **** Actions Taken **** Notified CRS and supervision. Wrote CR Initiated recovery per ABN-HWC. | 02-00-HSSF-CAB-CHEM/LAB
389480 | CR | 20190131 | CAQ | D | Oscillograph Started due to Lower Monumental-Ashe 500KV line | Y | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3 alarm. BPA reports the cause was momentary open and reclose of the Lower Monumental- Ashe 500KV Line. Line auto reclosed. No emergent outage needed. The alarm was due to the following sensors: J7 (500KV Neutral Ground Overcurrent), J11 (SM-7 Undervoltage) , J12 (SM-8 Undervoltage), J15 (230KV Undervoltage), and J16 (Main Generator - Negative Sequence). All sensors have been reset. E-TR-S and E-TR-B voltages are 239/240/238 kV and 119/119/118 kV respectively. All plant controllers and equipment exhibited normal operation. BPA reports problem appears to be 13 miles from Ashe substation <I> **** Actions Taken **** CGS remained at 100% power throughout event.
389481 | CR | 20190131 | CAQ | D | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0064955 New World Technology Torque Gun- model E-Rad 2000 found OOT & adjusted within specs. Not used during Calibration cycle. DEF #6800A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
389482 | CR | 20190131 | CAQ | D | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0066023 Fluke Temp. Probe- model 80T-150UA DEF #6385A 9/27/17 Suspended it as Lost. Now Rejected- Found Broken Beyond Repair. DEF #6801A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
389483 | CR | 20190131 | CAQ | D | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0067225 Noshok Gauge 100 psig Passed Calibration but glycerin had leaked out. Not Repairable. Rejected. DEF #6802A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
389484 | CR | 20190131 | CAQ | D | TG BLDG 501â€™ TURBINE DECK/RFW HEATER AREA trouble alarm | N | N |  | N | YES | <D> **** Detailed Description **** TG BLDG 501â€™ TURBINE DECK/RFW HEATER AREA trouble alarm at FCP-1 is locked in and will not reset following a grid hit at 0244 on 1/31/2019. Work request is being written against FP-ID-10/1, but it is not known which detector is causing the trouble alarm to stay locked in. <I> This is non-essential fire protection. | 02-00-FP-ID-10/1
389494 | CR | 20190131 |  | 4 | Relay in EO center buzzing loudly again | N | N |  | N | YES | <D> **** Detailed Description **** Relay buzzing in Equipment Operator center SW corner on south wall in panel again, GSB 441, above and left of E -LP-5AD, picture in EDMS. No EPN on relay, AR/WR written against E-LP-5AD. Recommend investigate cause and correct. This occurred previously, see AR#377833 WR29141583 <I> **** Actions Taken **** Informed SSS, generated AR/WR. | 02-00-E-LP-5AD
389500 | CR | 20190131 |  | 3 | Some Contractors are not showing up in the Phone Directory |  |  |  | N | NO | <D> **** Detailed Description **** Some contractors are not showing up in the Employee Phone Directory due to the size of the vendor name in Asset Suite. Information Services is looking into the issue and will put a plan in place to fix the issue. Assign to ITMGMT NCAQ 3 to evaluate and resolve. <I> Assignment added to Perform DataMod to insert Records to Phone Dir.
389504 | CR | 20190131 | CAQ | C | Loss of supervised FP Detection Circuit | N | Y |  | N | YES | <D> **** Detailed Description **** While performing WO 02119011, FP-ZONE-65 2-YEAR SENSITIVITY CHK, electricians were unable to bring in a trouble condition while performing PPM 15.2.4. Upon review of EC 13537 drawing 217-00,84 it was identified the ZU-35DS module located in FP-CP-FSP7 is not wired correctly. Field wiring followed EC 13537. Field wiring in FP-CP-FSP7 matches the design for the panel. EC 13537 drawing 217 -00,84 is incorrect. The End-of-Line capacitor for the Class A detection circuit is not wired in accordance with vendor (Siemens) recommended wiring for the module. Reference EC 13537 and 217-00,84. . Detectors are locked into place upon installation (twist in place) and unlikely to fall from base. Supervisory function is primarily to identify when a detector is not in the detector base (reinstalled correctly after maintenance and/or dislodged by inadvertent contact). Previous troubleshooting has identified that detectors currently installed will perform their function of providing the control room with a fire alarm in the vent of a fire. Incorrect placement of the capacitor on the Pre-Action 65 circuit does not prevent the circuit from performing its design function. Incorrect placement of the capacitor only removes supervisory function of the circuit. The incorrectly placed capacitors are incorrectly placed, per design, in accordance with EC 13537 and 217-00,84. . . Pre-Action 65 is located in the 484â€™ EL Cable Spreading Room. . Reference CR 00386231 for similar condition. <N> **** Equipment Description **** W487 K0/15.1 | 02-00-FP-CP-FSP7
389506 | CR | 20190131 |  | 4 | unable to complete work order as written | N | N |  | N | YES | <D> **** Detailed Description **** During work on WCH-CR-51B chiller - WO 02085540 to restore configuration on 51B chiller, the valve threads are beyond repair. over the years Chicago style fitting (pipe thread) have been forced over the valve threads (garden hose thread). the threads are unable to restore back to garden style and have caps put on them. This does not effect operability of the chiller, they are for vent and drain purposes only. <I> **** Actions Taken **** Discussed with planning, we do not have new valves to replace the currently installed valves. The same issue on 51A chiller was corrected with the new chiller install. 51B is slated for a chiller replacement as well. Recommend replanning package for valve replacement, or waiting for the new chiller to be installed. <N> Appears to leave the AR CR 267259 condition for WCH-CR-51B / WCH-CU-51B TSW / WCH vent/drain configuration unaddressed. New Work Request (WR) needed? | 02-00-WCH-CR-51B
389508 | CR | 20190131 |  | 3 | (NRC Observation) Evaluate EPI-16 50.54(q) for enhancements |  |  |  | N | NO | <D> **** Detailed Description **** During a NRC Inspection, an observation was made that several 50.54(Q) screens did not have consistent information in the description block. Specifically, several examples lacked the revision number, and some failed to list the document title. This does not apply to 50.54(Q) evaluations since the details of the procedure change are documented within the evaluation. Evaluate EPI -16 for a potential enhancement to incorporate this consistency observation. <I> **** Actions Taken **** NRC Observatioin, recommend non-CAQ.
389510 | CR | 20190131 |  | 4 | Door C-107 handle does not work well | N | N |  | N | YES | <D> **** Detailed Description **** Door C-107 (OG A Dryer Skid door), in Radwaste 437', knob is broken - does not operate well. Knob spins free, 2A submaster key is required to enter room. <I> **** Actions Taken **** Initiated CR. | 02-00-W-DOOR-C107
389511 | CR | 20190131 | CAQ | D | Rod accumulator trouble alarm HCU 2639 (water level) | Y | N |  | N | YES | <D> **** Detailed Description **** Received H13-P603.A7 ROD ACCUMULATOR TROUBLE alarm for CRD-HCU-2639. Investigation revealed alarm was due to high water level. <I> **** Actions Taken **** Notifed the CRS and Shift Manager. OPS 2 drained water per SOP-CRD-HCU to clear the alarm. Submitted CR and WR to document. | 02-00-CRD-HCU-2639
389512 | CR | 20190131 |  | 3 | (NRC) Observation of RO/SRO Qualification Card LO000212 |  |  |  | N | NO | <D> **** Detailed Description **** During the NRC validation of the ILC 23 NRC examination two RO/SRO Qualification Cards (LO000212) were reviewed. During the review, it was noted that not all of the 520 hours credited towards the minimum on shift time was standing a watch under instruction. LO000212, RO/SRO Qualification Card, has a section titled Licensed Operator On-Shift Hours List. In addition to the shift logs, this is where the student hours on shift are recorded and signed off by an SRO. For each day on shift, there is a section to record what the dominant activity was for the shift (ie CRO1, CRO2, CRS, SM, etc). One of the dominate activities that could be selected is â€œSTUDYâ€. Although the students met the minimum requirements of being assigned for at least three months as an extra person on shift per ES-202 section D.1.b.1 and D.2.b.1, this terminology could lead to confusion on the part of the SRO signing for the activity as to what they are signing for. There was a communication sent out to shift management clarifying this at the beginning of ILC 23 OJT/TPE but more specificity in LO000212 would help resolve any questions that arise in the future. In particular, clarification guidance should be added to state: By signing off in the qualification guide and approving logs that document the students were on shift for OJT/TPE, you are certifying that: -The time was spent engaged in activities in training for the RO/SRO position -All phases of day to day operations were included (as appropriate) as part of this time -They were under the direct supervision of shift management (licensed personnel) during the period. In addition to the above enhancement, replace the STUDY activity option with OJT/TPE will further clarify the expectations of on shift time. <I> **** Actions Taken **** Informed Training, Operations, and Licensing Management. Recommend Non-CAQ level 3 assigned to AR-OPTRAIN.
389513 | CR | 20190131 |  | 3 | R24 Material Exception list currently used is not correct |  |  |  | N | NO | <D> **** Detailed Description **** It was determined on Wednesday 1/30/2019 that the outage Material exception list was not accurate. This list contains material/parts that was ordered for the outage but has a delivery date after P.O. 37 milestone â€œparts received and ready for issueâ€. The current report included only the items that had original delivery date after PO37 milestone, but did not include items with delivery dates that slipped. Assign Category 3 to SCS <I> **** Actions Taken **** Communicated issue with outage management. Conducted review of all purchase orders (POâ€™s) that still show as open was conducted and vendors contacted to ensure all estimated arrival times (ETA) are is still valid. Any ETA slippage will be added to the exception list for accurate reporting and follow up to ensure arrival on time for the outage.
389514 | CR | 20190131 |  | 3 | Overenrollment in training classes |  |  |  | N | NO | <D> **** Detailed Description **** Since January 21, there have been 3 known instances where training classes scheduled in Plateau have been at their listed capacity and people above that number have been subsequently enrolled, putting the class over it's limit. Class size limits are based on conference seating arrangement requirements found in ISPM-10 and approved by Fire Protection/Fire Marshall - see CR 377587 for arranging conference room seating using an unapproved plan. Previous coaching of specific groups January 23rd did not prevent similar from another group for Plateau class 50627, discovered today. In order to add someone to a class already at maximum registration, one needs to answer yes to a pop-up warning informing them the class is at maximum and that they are willing to proceed and add the person without consulting the instructor. There is a certain level of Plateau permission required to bypass the warning and add another indivdual. It would seem we need more training on what the warning means for those with such permission. <I> **** Actions Taken **** Spoke with Plateau administrator. Coached individual to find a different offering (there are 4 others) or find someone willing to be removed from class and enrolled in another to make room.
389516 | CR | 20190131 |  | 4 | Industrial safety near miss |  |  |  | N | NO | <D> **** Detailed Description **** Near Miss, An individual slipped on a carpet protector in the Dry Creek building. The individual had just entered the building and his wet shoe slipped on the carpet protector and they slowly went to a kneeling position. The carpet protector was installed to protect the new carpet during office remodel. The indivedual was not injured <I> **** Actions Taken **** The carpet protector was remove and Industrial safety and the department manager were notified
389519 | CR | 20190131 | CAQ | C | E-CP-RBHV/A, verify annunciator position | N | N |  | N | YES | <D> **** Detailed Description **** Verify position of annuciator cards on E-CP-RBHV/A compared to EWD-80E-010. Drop 3.4 is pnned as "OPEN" in field and drawing shows it as "OPEN TO ALARM". When we pinned them as the drawing states the alarm actuated. The alarm should have been clear. Need to validate correct position of pins. <I> **** Actions Taken **** Pinned as found. Inform Manager. <N> **** Equipment Description **** R572 | 02-00-E-CP-RBHV/A
389520 | CR | 20190131 |  | 3 | User was using RSA to access EN Network from foreign Country |  |  |  | N | NO | <D> **** Detailed Description **** GBP-IS-36, Information Services Guidelines for International Travel section 6.1.2.j requires that travelers UNINSTALL RSA token from all electronic devices prior to travel. The individual should have contacted Information Services prior to travel to ensure the appropriate actions as outlined in GBP-IS-36 requires to allow needed business functions. <I> **** Actions Taken **** Information Services disabled RSA access. Investigation was conducted and confirmed no abnormal behavior or anomalies were found. No further actions required. Not reportable under 10 CFR 73.54 SWP-CSW-28 <N> Individuals were coached. D-15 write-up was distributed to recommunicate the expectation.
389521 | CR | 20190131 | CAQ | D | SW-PT-40 found OOT | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of ISP-SW-X306, as found values in step 7.1.17 for SW-PT-40 were OOT. Adjusted SW-PT-40 per the procedure listed in section 7.2. All as left values are within tolerance. As left loop check within tolerance. <I> **** Actions Taken **** Contacted operations, supervision, adjusted SW-PT-40 per section 7.2, wrote CR. <N> **** Equipment Description **** SSW 1A <R> Not a reporatability concern. REP/REGE assignments have been cancelled with Compliance Supervisor concurrence.
389522 | CR | 20190131 |  | 3 | RWCU-P-3A PMT does not vent the pump case of air | N | N |  | N | YES | <D> **** Detailed Description **** SOP-RWCU-DEMIN and the PMT 0213648705 did not vent the pump. It jogs the pump to purge the air. The pump should not be operated with not water on the mechanical seal. This could be one of the reasons for the short life span of the seals. Recommend changing the PPM to vent the pump in the future. <I> **** Actions Taken **** Contacted supervisor. the pump is operating with no issues at this time. | 02-00-RWCU-P-3A
389524 | CR | 20190131 |  | 4 | Possible CW basin level discrepancy | N | N |  | N | YES | <D> **** Detailed Description **** During walkdown of the Circulating Water Pumphouse (CWPH) it was visually identified that CW C Bay was approximately 0.5-1 ft. below the level that has been maintained since ODMI 380572 prescribed continuous operation high in the band (C Bay levels GT 443â€™); however, Control Room indication of CW bay C level indicates a level of approximately 443.5â€™. This apparent discrepancy may be due to an error in the CW C Bay level instrumentation, which may also be related to the recent spontaneous closures of TMU-LCV-2A (CR 00389242). Recommend investigation and repair of CW C Bay level instrumentation and related components. This condition does not adversely impact the long-term health of the CW pumps and motors, and the CW system remains capable of performing its intended design function. ODMI 380572 prescribes high basin level in an attempt to maximize CW flow and improve generation. <N> Recent operating history has shown that CW bay levels below 443.5â€™ produce an additional 500 â€“ 1,000 gpm per 1â€ of basin level, while bay levels GT 443.5â€™ can produce a step change in flow of 20,000 â€“ 25,000 gpm. The combined flow increase from an additional 0.5-1 ft. could result in as much as a 30,000 gpm increase in CW flow, which is roughly equivalent to a 1.8 to 3.0 MWe increase in generation, depending on ambient conditions. A noticeable change in the A Bay level from before and after the CW-P-1B lift adjustment can be observed from eDNA point L086 (plot in EDMS). Screen loading on the A Bay has been relatively unchanged from before and after the CW-P-1B lift adjustment. | 02-00-TMU-LI-2A
389525 | CR | 20190131 |  | 3 | TS Bases for SR 3.8.6.6 Provides Improper Guidance |  |  |  | N | NO | <C> CR (389525) downgraded from CAQ C to Severity 3 at the request of MRT (OFM) on 02.07.2019. <D> **** Detailed Description **** TS SR 3.8.6.6 contains a note that specifies that this surveillance shall not be performed in MODE 1, 2, or 3 for the Division 1 and 2 125 VDC batteries. The TS Bases explain the reasoning for the note and provide a statement that the note is further amplified to allow portions of the surveillance to be performed for the purpose of re -establishing OPERABILITY. This amplifying verbiage does not exist in the note to TS SR 3.8.6.6. Other TS SR requirements do contain this amplifying verbiage in the note (see TS SR 3.8.1.16). <I> **** Actions Taken **** Notified Shift Manager and Licensing. Prepared Condition Report. Recommend Severity Level 3 to Licensing to review the finding and update the TS Bases as appropriate.
389532 | CR | 20190131 |  | 3 | APEL TEC Room Fire Door Found Blocked Open |  |  |  | N | NO | <D> **** Detailed Description **** Inspection of the APEL building by the Fire Protection Engineer found that the Telecommunications Control Room (TEC) second floor fire door and Halon confinement door was propped open. Note this room is an EP area of concern. Discussion with the Facilties Craft Supervisor determined that work in progress since the previous weekend had propped this door open to allow electrical cables to be routed during an HVAC upgrade. The Supervisor indicated that a Fire System /Barrier Impairment Permit had not been initiated since the exemptions allowed in procedure FPP-1.3 were to be followed. The exemption requires constant attendance to the impaired fire door, such that it can be restored immediately if necessary. Unfortunately, the Crafts left the open barrier and did not restore the Fire Door/ Halon Barrier for several days. The fire door was restored to normal service today. Recommend that this CR be routed to Facilities management and this incident discussed with all the Craft to prevent recurrence. Recommend assign this to Org 76300, AR-FACIL. <I> **** Actions Taken **** Fire Door/ Halon Barrier was restored shortly after discovery. . Not a CGS issue.
389534 | CR | 20190131 | CAQ | D | ISP-APRM-B302 as found values OOT | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing ISP-APRM-B302 following cpu card and chip replacements per WO's 02122281 01, 02. As found setpoints and gains were out of tolerance due to CPU card replacement. This was an expected condition and was corrected with work instructions and surveillance completion. <I> **** Actions Taken **** Completed work order instructions and Surveillance as wriiten to restore as found conditions to acceptable as left values. All as left values SAT.
389536 | CR | 20190131 |  | 4 | Outer insulation jacket damaged on fiber cables | N | N |  | N | YES | <D> **** Detailed Description **** During quarterly walkdowns, two fiber cables were observed to have thier outer insulation jacket pulled away from the plug. Cable is still functioning, with the inner insulation jacket intact, but one layer of protection has been comprimised. Recommend cable replacement. <I> **** Actions Taken **** This CR | 02-00-PDIS-COMP-SERVICE/DESK,02-00-PDIS-COMP-STABU
389537 | CR | 20190131 |  | 4 | Administrative password inadvertently mis-configured | N | N |  | N | YES | <D> **** Detailed Description **** During quarterly Password Change - Cyber PM a password was mis-configured on one of the NET3 Network switches. This will require a reboot and configuration correction to correct. This does not affect Operations. This is not a reportable issue. <I> **** Actions Taken **** This CR | 02-00-NET3-NETSW-5/A,02-00-NET3-NETSW-5/B
389540 | CR | 20190131 |  | 4 | Work Near protected equipment form needed |  |  |  | N | NO | <D> **** Detailed Description **** During performance of ISP-APRM-S402 (WO 02122281),the work was delayed to obtain work near protected equipment permossion per PPM 1.3.83. The craft notified the CRS that they were working next to a protected relay. The work was halted until the requirements of PPM 1.3.83 were met (permissions via telecon). The proximity to protected equipment should have been identified before execution. The positive is that our equipment was properly marked as protected and that the workers stopped and notified the CRS. The negative is that the job planning and preparation failed to plan to work near protected equipment. <I> **** Actions Taken **** Conducted walkdown with the craft. Completed requirements of 1.3.83 to allow work near protected equipment.
389541 | CR | 20190131 |  | 3 | Step 7.1.5 in ISP-APRM-S402 could not be verified |  |  |  | N | NO | <D> **** Detailed Description **** During performance of ISP-APRM-S402 (PMT for APRM-CHS-2 EC 8076) Step 7.1.5 could not be confirmed due to APRM-CHS-2 being logged as inop as a part of the EC. <I> **** Actions Taken **** Discussed with CRS, *1'd the step and moved forward with procedure. Created CR to make an enhancment to the Procedure on this step for PMT activities so we can confirm the other APRMs are operable Step 7.1.5 states "CONFIRM with Operations that all APRM and OPRM channels are operable". Since the APRM was inoperable due to the maintenance, it could not be confirmed. THis is a procedure issue only. <N> ***General Notes*** Per the IC shop there is no issue with the procedure. This CR is documenting that they had to NA a step within the procedure only. The assignment for this issue has been canceled, and the AR will be closed to no action.
389542 | CR | 20190201 |  | 3 | Poor radio communication technology delayed HWC restoration |  |  |  | N | NO | <D> **** Detailed Description **** On 1/31/19, HWC was lost when HSSF-V-YV170 isolated. During the system restoration, Field operators had difficulty hearing the radios in high noise areas (TB 441 / 471). The use of the PA and telephones had to be used. more effective communication systems (technology) may exist and should be pursued. These comments were documented on the crews 4.0 critique following the HWC transient.
389543 | CR | 20190201 |  | 4 | TG 501 P10 Gas Suspected Leakage |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The P10 Gas Bank on TG 501 Southwest, is suspected to have excessive leakage. This P10 Gas Bank supplies Gas to the Main Control Room Argos, Whole Body Contamination Monitors. Also supplies the MCR CM11 Contamination Monitor. The P10 Gas Bank is leaking approximately 500 pounds per day. This is excessive, compared to normal operation. <I> **** Actions Taken **** Notified HP Lead. Initiated CR/WR. Esoms Log Entry. <N> **** Equipment Description **** TG 501 Southwest P10 Gas Bank
389567 | CR | 20190201 | CAQ | D | Rod Accumulator Trouble alarm on CRD-HCU-1807. | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble alarm on CRD-HCU-1807 due to water. <I> **** Actions Taken **** Informed CRS/ SMK, wrote this CR and WR. | 02-00-CRD-HCU-1807
389568 | CR | 20190201 | CAQ | D | Startup Transformer Trouble alarm silently flashing. | Y | N |  | N | YES | <D> 800.C4 drop 2-7 Transformer TR-S Trouble alarm silently started flashing. Acknoledge button did not lock in annunciator. Annunciator check of the P800 panel functioned normally, when complete alarm continued to flash. Annunciator card was removed and contacts cleaned. After restoration continued to flash. Need to investigate the silent acuation and inability to acknoledge the alarm. <I> Ops sent to investigate. Low oil level alarm had come in which is written up on WR 29141100. Ops reset the alarm and the annunciator clear audible sounded in MCR and the annuciator reset button cleared the still flashing alarm. | 02-00-E-TR-S
389569 | CR | 20190201 |  | 4 | Light out above E-IR-H22/P027 leaving it in the dark | N | N |  | N | YES | <D> **** Detailed Description **** Light out above E-IR-H22/P027 leaving it in the dark. Single lamp with 2- 8 foot tubes. Instrument rack is behind Door R-Door-R415 so surrounding light dont help. Please replace the bulbs. <I> **** Actions Taken **** WR/CR <N> **** Equipment Description **** RX 522 elevation behind/above door R-DOOR-r415
389571 | CR | 20190201 |  | 4 | Abnormal noises from CW Cooling Tower 1A, due to CW-FN-1 | N | N |  | N | YES | <D> **** Detailed Description **** Abnormal, oscillating air noises from Cooling Tower 1A noted by OPS4 and various site personnel. Upon investigation it was noted that the motor had excessive vibration such that guard cover bolts had loosened and fell off. There was no scrapping or contact of fan blades to shroud. Guard cover bolts remain in area. <I> **** Actions Taken **** MCR informed. CW-FN-1 was secured and noises stopped. CR & WR written . Per watchstander, problem was the motor vibrating excessively such that bearing guard (cover) bolts had loosened and fell off. Confirmed that there was no contact of the fan blades to the shroud. | 02-00-CW-FN-1
389574 | CR | 20190201 |  | 3 | Factory refurbished breaker failed portions of bench test |  |  |  | N | NO | <D> **** Detailed Description **** This AR is being written to document another factory refurbished breaker that was pulled from stores that required repair during the bench testing task. GE Power Vac breaker UTC 543239 was bench tested under WO 02088281 -02 and repaired under WR 29146900. A new anti pump relay and a new set of aux switches were installed to replace existing components due to corrosion. Pictures attached in WO. This was a pre-outage activity that required twice the resource hours to complete. This is a duplicate of 389394 which was was not written in a way to make it clear that an excessive number of factory refurbished breakers are exhibiting problems during the bench testing tasks. <I> **** Actions Taken **** Generated AR, notified ENG, Repaired breaker <N> **** Equipment Description **** RW487 breaker shop
389575 | CR | 20190201 |  | 3 | Evaluate enhancement to FORM 27154 |  |  |  | N | NO | <D> **** Detailed Description **** FORM 27154 (OPS-2 Logs) has shiftly CCH chiller status checks. These should only be applicable to chillers aligned to supply the WMA cooling coil, typically CCH-CR-1B. Recommend making these entries conditional; only required it that CCH chiller is aligned to associated cooling coil. <I> **** Actions Taken **** Initiated AR.
389576 | CR | 20190201 |  | 4 | MS-V-172B Steam Leak has Returned Following Furmanite Repair |  |  |  | N | YES | <D> **** Detailed Description **** Refer to CR 376793. Furmanite was performed on this leak under WOT 02124692-01 on 4/16/18. A re-injection was performed under WOT 02124692-12 on 6/18/18. Per the comments, the maximum number of sticks were used per the void calculation. Engineering will not allow further injection due to restricting orifice downstream. There still is a significant steam leak. <I> **** Actions Taken **** Researched issue. Informed FIN. <N> Permanent repair WO number = R24 WO 02125690. | 02-00-MS-V-172B
389578 | CR | 20190201 | CAQ | C | Two Loose terminal screws in E-CP-H13/P611 | Y | N |  | N | YES | <D> **** Detailed Description **** DUring performance of Investigation in WO 02138310-01 found two terminal screws that were found 1/4 turn loose. they were the panel side terminals FF-34 and FF-35 associcated with the MS-LS-61D current loop. Screws were tightened per WO steps. <I> **** Actions Taken **** Notified Engineering and operations. Issue has been corrected by WO 02138310-01 <N> From: Dumlao, Elmer <edumlao@energy-northwest.com> Sent: Wednesday, February 6, 2019 12:55 PM To: Chadha, Nishant <nchadha@energy-northwest.com> Subject: CR 389578 Two Loose terminal screws in E-CP -H13/P611 Nishant, In regards to CR 389578, the 2 loose terminal screws for MS-LT-61D would not have affected the Functions of CRD-LIS -601D, MS-LIS-200D & MS-LS-300D. These units have relays that are normally energized. A loss of signal input from MS-LT-61D or a loss of power would result in an alarm in the control room. Likewise, if the signal input is greater than expected, you would also receive an alarm. | 02-00-MS-LT-61D
389579 | CR | 20190201 |  | 3 | Procedure enhancement SWP-PRO-02 |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.3.3 of SWP-PRO-02 proceeds to the wrong step <I> **** Actions Taken **** Wrote CR
389580 | CR | 20190202 |  | 4 | TSW leak out of lagging at 507 WCH chiller | N | N |  | N | YES | <D> **** Detailed Description **** There is water dripping out of the lagging above the walkway between the RW 507 WCH chillers <I> **** Actions Taken **** Wrote CR. Informed Shift Manager <N> **** Equipment Description **** See EDMS for location | 02-00-TSW-PIPE-MISC
389586 | CR | 20190202 |  | 4 | TSW-V-55 Packing Leak (significant), throttles 2/3 open | N | N |  | N | YES | <D> **** Detailed Description **** While restoring TSW to the WCH chillers operators took manual valve TSW-V-55 from closed to full open. Initially there was no leakage, at about half open it was leaking at several drops per second from the packing, possibly a light but steady stream at moments. As it stoked near 2/3 open the leakage mostly went away. As it approached full open the valve packing started leaking significantly, approximately a gallon every 1-2 minutes. The CRS was informed we operators were directed to throttle the valve closed to approximately 2/3 open where the leakage was minimal. The packing may have adjustment left, but it did not look like much. <I> **** Actions Taken **** MCR is creating a caution clearance for configuration control. | 02-00-TSW-V-55
389587 | CR | 20190202 |  | 4 | TSW-V-274 could not be vented from, plugged | N | N |  | N | YES | <D> **** Detailed Description **** During venting of TSW from TSW-V-274, operators failed to get any indication of air or water from the valve after it was cycled full open and closed multiple times. Attempts were made to clear possible blockage but failed. Per CRS, an alternate vent path was used, that being TSW-V-H751A (which is at equal height on the pipe and only several feet away). Valve and pipe from the header need to be replaced or cleared of blockage. <I> **** Actions Taken **** Informed MCR. Found alternate vent path. | 02-00-TSW-V-H751A
389588 | CR | 20190202 |  | 4 | TSW-V-274 could not be vented from, plugged |  |  |  | N | YES | <D> **** Detailed Description **** During venting of TSW from TSW-V-274, operators failed to get any indication of air or water from the valve after it was cycled full open and closed multiple times. Attempts were made to clear possible blockage but failed. Per CRS, an alternate vent path was used, that being TSW-V-H751A (which is at equal height on the pipe and only several feet away). Valve and pipe from the header need to be replaced or cleared of blockage. <I> **** Actions Taken **** Infomed CRS, found new vent path. | 02-00-TSW-V-274
389589 | CR | 20190202 |  | 4 | TSW-V-H3 has leakby (vent valve) | N | N |  | N | YES | <D> **** Detailed Description **** During venting of TSW from WCH about 1-2 drops per second of internal leakby was found on TSW-V-H3. After the pipe cap was placed on the leagage subsided. <I> **** Actions Taken **** Contained leakage with pipe cap. | 02-00-TSW-V-H3
389590 | CR | 20190202 |  | 4 | 40 Pieces of M&TE Rejected | N | N |  | N | NO | <D> **** Detailed Description **** 40 Pieces of M&TE were Suspended as Lost- Never located. Now Rejected. No Evaluation Required. Each Rejection form lists original DEF # for Suspension and New DEF # for Rejection. See EDMS for full Eval. No Action Required. <I> **** Actions Taken **** None Trending purposes only.,
389591 | CR | 20190202 |  | 4 | 30 Pieces of M&TE Rejected | N | N |  | N | NO | <D> **** Detailed Description **** 30 Pieces of M&TE were Suspended as Lost. Never Located. Now Rejected. No Evaluation Required. Each Rejection Form lists original DEF # Suspension & the New DEF # Rejection. No Action Required. See EDMS for full Eval. <I> **** Actions Taken **** None Trending purposes only.
389592 | CR | 20190202 |  | 4 | MT-CRA-1 Upgrades - Scissor Lift (2nd) Inoperative | N | N |  | N | NO | <D> **** Detailed Description **** Rental scissor lift found with control panel error code and would not start during before-use inspection. This now makes 2 of 3 rental man lifts that are currently out of service. Lift is fully retracted and in a safe configuration. <I> **** Actions Taken **** Reviewed operators manual troubleshooting guide, swapped battery from other unit, partial function was observed but not fully functional. Contacted United Rental and left message requesting call back and help.
389593 | CR | 20190202 |  | 4 | 21 Pieces of M&TE Rejected | N | N |  | N | NO | <D> **** Detailed Description **** 21 Pieces of M&TE were Suspended as Lost. Never located. Now Rejected. No Evaluation Required. Each Rejection form lists original DEF # Suspension & New DEF # Rejection. No Action Required. See EDMS for Full Eval. <I> **** Actions Taken **** None Trending purposes only.
389594 | CR | 20190202 |  | 4 | TO-TK-2 Oil leak due to clogged filter | N | N |  | N | YES | <D> **** Detailed Description **** TO-TK-2 Oil Leak from top hatch of tank, likely due to a Clogged Filter <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** 471' Turbine Bldg | 02-00-TO-TK-2
389595 | CR | 20190202 |  | 3 | SOP-FUELPOOL-DRAIN procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Steps 5.1.5n and 5.1.4n "VERIFY the water being discharged from the FPC demin meets all Chemistry requirements for discharge to CST." should not be performed while draining the SFP to the CSTs. This sample and analysis takes time and should be placed as a prerequisite and given a support task for chemistry to sample prior to the draining evolution. <I> **** Actions Taken **** Discussed change with chemisty department and OPS Shift Manager.
389596 | CR | 20190202 | CAQ | C | DG4 ramped to 1800 RPM quickly on start | N | Y |  | N | YES | <D> **** Detailed Description **** During performance of OSP-FLEX-M704, the DG4 ramped quicker than expected to 1800 RPM. After the start, there is a note in the procedure that says the DG should idle for ~5 minutes or until coolant temperature is GE 172F, but the diesel ramped to 1800 RPM within a minute, not meeting what the note said. This is written for trending/investigation purposes. <I> **** Actions Taken **** Initiated CR. Informed supervision and system engineer. | 02-00-E-DG-4
389597 | CR | 20190203 |  | 3 | Dataglance problem closing a surveillance |  |  |  | N | NO | <D> **** Detailed Description **** I tried to close a surveillance in dataglance. It was 02130669. crediting it to another work order. I authorized it in dataglance OPS screen, but then could not advance it using dataglance. I had to check it out on a tablet to start field work. Dataglance should be able to do these steps. Please address this issue so that it wont happen in the future. <I> **** Actions Taken **** Wrote CR <N> DataGlance â€œSet to Finishedâ€ supports taking support tasks directly to FINISHED status in Asset Suite from the Supervisorâ€™s Assign panel. This activity is only available when the Asset Suite Task status is APPROVED 30 or READY 45 and the JOB-TYPE (table TIDWOTSK) is equal to one of the following: . AD ADMINISTRATIVE CO CLEARANCE ORDER: HANG OR LIFT NH SHOP PM - OPS REVIEW NOT REQUIRED NP PM - OPS REVIEW NOT REQUIRED NO OTHR PM- OPS REVIEW NOT REQUIRED NS ESSENTIAL PM - OPS REVIEW NOT REQUIRED OS OPERATIONS SUPPORT SC SCAFFOLDING ERECTION/REMOVAL SH-SHOP WORK SP-SUPPORT TASK XX-ADMINISTRATIVE SUPPORT WORK ORDER TASK . In the case of WO task 02130669-01 the job-type = â€˜SVâ€™ (operations testing), so the tasks do not qualify for Set to finished.
389598 | CR | 20190203 |  | 3 | OSP-ELEC-S703 procedure change |  |  |  | N | NO | <D> **** Detailed Description **** OSP-ELEC-S703 needs to be updated for DO-F-3 position (step 7.3.35c-d). This filter does not have a 1 position but L now. <I> **** Actions Taken **** CR written
389599 | CR | 20190203 |  | 4 | PWC-V-452 leaks by excessively | N | N |  | N | YES | <D> **** Detailed Description **** PWC-V-452 leaks by excessively, causing slow rotation of the Flocculator Backwash arm and also a solid stream of water to escape the PWC-AV-1 vent tube. This only exacerbates the issue that already exists with the reduced amount of available level the flocculator has due to level switch problems. <I> **** Actions Taken **** informed MCR | 02-00-PWC-V-452
389604 | CR | 20190203 |  | 3 | (NRC) PPM 1.3.76 contains typos in section 5.3 |  |  |  | N | NO | <D> **** Detailed Description **** There are apparent typos to section 5.3 of PPM 1.3.76 â€“ â€œManaging and Approving Actions for Repetitive HIGH Risk Work. â€“ All Modesâ€, in the table of contents when compared to other sections in the procedure. â€¢ Section 2.1.2 on Pg. 4 - The responsibilities for assessing the risk significance of Work and determining actions for managing these risks are described in Section 5.1, Assessing and Classifying Risk Significance of Work, Section 5.2, Managing LOW and MEDIUM Risk Work, and Section 5.3, Managing LOW and MEDIUM Risk Work. â€¢ Section 5.3 on Pg. 24 â€“ Managing and Approving Actions for HIGH Risk Work <I> **** Actions Taken **** Wrote CR
389605 | CR | 20190203 |  | 3 | Sodium Hypochlorite spill in Pumphouse #2 (Bldg 40) | N | N |  | N | YES | <D> **** Detailed Description **** PWC-P-8 discharge tubing separated from the potable water piping it was injecting to, resulting in sodium hypochlorite being pumped onto the floor of Pumphouse #2 (Building #40). Since PWC-P-8 and its plug are located in the Flocculator Building, the pump was unplugged, thereby stopping the active spill. Ops 4 estimates there is about one gallon of sodium hypochlorite on the floor of Pumphouse #2. The buildingâ€™s drains all have raised lips, so it is unlikely that it drained into them. The sodium hypochlorite is 10-16% (chemical permit #0220). ABN-HAZMAT was entered and Hanford Hazmat responded. <N> Spill was remediated by E&RP staff on 02/03/19. NaClO was spilled to concrete, much of which was absorbed by the concrete, remaining liquid was absorbed using absorbent and paper towels . There was no threat to human health and the environment. Waste was designated under HW19-020, no further action is required. | 02-00-PWC-P-8
389606 | CR | 20190203 |  | 3 | FPC-DM-1B, abnormal hold valve and hold pump response | N | N |  | N | YES | <D> **** Detailed Description **** FPC-DM-1B hold pump (FPC-P-2B) and hold valve (FPC-V-14B) failed to operate as required when completing the precoat on FPC-DM-1B. At the end of the precoat cycle, the precoat pump turned off and the hold pump began cycling vigorously. Manual action was taken to place the hold pump in Hand and OPEN the hold valve. Flow (FPC-FIC-15B) was noted to be ~ 450 gpm and steady, with the inlet (FPC-V-6B) closed. After opening FPC-V-6B, flow dropped to ~ 200 gpm. There have been multiple instances of this issue since 10-31-17. Reference AR# 373233, 376229, 378615 and WR# 29141873. Suspect FPC-FIC-15B requires replacement, as fill and vents/re-calibrations have been unsuccessful at addressing this issue. <I> **** Actions Taken **** Informed MCR. Steps to place FPC-DM-1B in service will address restoring the HOLD Pump and HOLD Valve switches to their normal configuration. <N> **** Equipment Description **** Informed MCR. | 02-00-FPC-FIC-15B
389607 | CR | 20190203 |  | 3 | Procedure enhancement PPM 4.840.A3 |  |  |  | N | NO | <D> **** Detailed Description **** During the 1/31/19 loss of HWC, H2 Wtr chem trouble alarm came due to HSSF-V-YV170 closing. The recovery actions are in ABN-HWC, so the procedure should be revised to add a step to REFER to ABN-HWC.
389608 | CR | 20190203 |  | 3 | FPC-FIC-15B does not work in AUTO | N | N |  | N | YES | <D> **** Detailed Description **** FPC-FIC-15B is no longer functional in AUTO. FPC-FIC-15B will not allow for flow GT ~650 gpm, while in AUTO. The auto setpoint needle had to be set to max (1100 gpm) to achieve 650 gpm. This does not allow auto control with 2 FPC pumps (flows of ~ 1000 gpm). When 2 pump operation was attempted, FPC-FCV-15B began to shut when flow rose above 700 gpm, despite having an AUTO setpoint of 1100 gpm. Manual control of FPC-FIC-15B was taken, to force FPC-FCV -15B Full OPEN. This is a problem that has been degrading since at least 9-13-18 (ref. WR# 29144575), At least 7 additional AR/WR have been written against FPC-FIC-15B in 2018. Please replace. MCR to generate CT warning that AUTO control is no longer functional. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RWCR, 467 | 02-00-FPC-FIC-15B
389610 | CR | 20190203 |  | 4 | Pre-Outage RX 606 Kelly Building AC Unit Maintenance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Please perform cleaning and maintenance service on both installed RX 606 Kelly building AC units prior to R-24. It is believed the last time these units were serviced was prior to R-23, almost two years ago. Refuel floor HPâ€™s, Laborers and Reactor Maintenance personnel rely on these units to supply a comfortable environment during outages. Due to increasing outside temps, the additional heat load on the refuel floor from the massive amount of warm water filling the reactor cavity and dryer separator pit plus the frequent opening of the Kelly building doors requires these AC units to be functioning at a high level. There are no EPN numbers associated with these AC units. <I> **** Actions Taken **** Notified RP Supervision and initiated WR <N> **** Equipment Description **** RX 606 Refuel Floor Kelly Building Both Elevations.
389611 | CR | 20190203 | CAQ | D | Fire Alarm for #2 Wellhouse won't clear | N | N |  | N | YES | <D> **** Detailed Description **** Fire Alarm for #2 Wellhouse (FPC-1 drop 16-4) was received and will not clear. FP-ID-49/3 has indication that it is in alarm. Note that the Fire alarm was received concurrent with PWC-P-8 tubing failure and chlorine spill in #2 Wellhouse. <I> Non-essential fire alarm/system. | 02-00-FP-ID-49/3
389612 | CR | 20190203 | CAQ | D | TEA-SP-93 chattering. | N | Y |  | N | YES | <D> **** Detailed Description **** During tour of TEA exhaust fans on RW 531 found the sample point on the exhaust plenum chattering. Found as TEA-RSM-93 in portal J, and as TEA-SP-93 that feeds TEA-SR-26 in portal J. <I> **** Actions Taken **** Informed SSS, initated AR/WR. | 02-00-TEA-RSM-93
389613 | CR | 20190203 |  | 3 | Radio communication uses during ABN-HAZMAT |  |  |  | N | NO | <D> **** Detailed Description **** Need clarification/improve of radio used during ABN-HAZMAT between Fire brigate member, Security and Hanford Fire department. Both Security and Hanford fire department are using the Fire Brigate channel and Ops is on normal CH1 that cause some issue with communication. A clarification from OPS training FB/Med to improve the communication with all involved parties. <I> **** Actions Taken **** CRS/SM informed.
389614 | CR | 20190203 |  | 4 | CN-TK-1 pressure high | N | N |  | N | YES | <D> **** Detailed Description **** CN-TK-1 pressure high OOS; unable to vent due to valves being encased in ice <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** SE corner of DG bldg. | 02-00-CN-TK-1
389615 | CR | 20190203 |  | 3 | Poor Coordination of Refuel Bridge/Mast Work Increases Risk |  |  |  | N | NO | <D> **** Detailed Description **** When the refuel bridge is moved for maintenance, the refueling mast is required to be pulled from the spent fuel pool. From January 2018 to January 2019, the mast was pulled from the water 10 times. When pulled from the water, a thorough rinsing of the mast is performed to reduce the surface contamination levels. Despite this rinsing, contamination levels exceed 200,000 dpm/100 cm squared when the mast is dry. Laborers, RP Technicians and other workers are at increased radiological risk during decontamination efforts, surveys and work on or around the mast. Following decontamination and work, the mast is bagged to reduce this exposure during work on or around the refuel bridge. Personnel are exposed to the radiological risk again when the bag is removed to place the mast back into the spent fuel pool. There is an increased risk of airborne contamination and personnel internal and external contamination because the mast has dried and contamination levels have increased. If maintenance on the refuel bridge and refuel mast were coordinated and the number of movements reduced, the opportunities for increased radiological risk would be minimized.
389617 | CR | 20190203 |  | 3 | Card reader for door D-Door-D111 |  |  |  | N | YES | <D> **** Detailed Description **** Should evaluate reactivating the old card reader or installing a new one for door D-Door-D111 to avoid burdensome comp actions when DG-3 is devitalized. <I> **** Actions Taken **** CR written <N> AR type EVAL required for proposed configuraiton change. | 02-00-D-DOOR-D111
389618 | CR | 20190203 |  | 3 | Dataglance problem |  |  |  | N | NO | <D> **** Detailed Description **** I am unable to authorize work order task 02112796-14. Please fix this <I> **** Actions Taken **** Wrote CR. workflowed the task. ensured holds are released. <N> The users would normally be able to set WO 02112796-14 to FINISHED, but this option is not allowed if the Control Room Communication on the Asset Suit Nuclear Panel is set to '1' or '2'. The WO taks 02112796-14, although it is a support task, the Control Room Communication is set to '1'. meaning that it is "HIGH IMPACT - Only PSRO/OPS may take to 48". The software is working as designed. Operations have the ability to change the value during their Ops (CORC/WC) review. Recommend Maintenance to provide Operation awareness of populating applicable fields. An assignment is being created for maintenance to provide awareness.
389619 | CR | 20190204 |  | 4 | Security Vehicle heater fan |  |  |  | N | YES | <D> **** Detailed Description **** Security vehicle LP# 98286C needs maintenance. The heater fan is working intermittently. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** security notification made, CR/WR generated <N> **** Equipment Description **** Security Vehicle in the PA
389624 | CR | 20190204 |  | 4 | Piping clog possible cause of chemical spill. | N | N |  | N | YES | <D> **** Detailed Description **** PWC-V-746 possible piping clog may have contributed to Sodium Hypochlorite spill. It was noted by spill response personnel that very minimal water water backflowing from the PW system when the chemical feed tubing disconnected from the system. Clogging in the chemical feed line may have caused an overpressurization condition in the feed line and caused it to seperate ffrom the PW system. <I> **** Actions Taken **** responded to the spill and locally tagged PWC-V-746 closed. | 02-00-PWC-V-746
389629 | CR | 20190204 |  | 4 | DevonWay Observation system slow/unresponsive |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** When using the DevonWay Observation system, it is slow to navigate, create a new Observation, and perform searching/reporting. <I> **** Actions Taken **** This is hosted application, and the vendor, DevonWay, has been notified of the issue. <N> Vendor was contacted, investigaed the issue, has identified the issue and addressed it. The system is now running normally. No further action is required.
389630 | CR | 20190204 |  | 4 | 19 Pieces of M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** 19 Pieces of M&TE were Suspended as lost. Never Located. Now Rejected. No Evaluation Required. Each Rejection Form Lists Original DEF # Suspension & New DEF # Rejection. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
389632 | CR | 20190204 | CAQ | C | Radiation Area Posting Moved Without Rad Operations Approval |  |  |  | N | NO | <D> **** Detailed Description **** A radiation area posting on the RB 501' (Northwest Corner) was found out of its normal position. The posting is adhered to a stanchion. It was found off of its stickered location and facing the incorrect direction. It is unknown who relocated the posting, but it appears to have been moved to allow for the storage of three scaffold carts in the area. The area was clearly posted as a Radiation Area by a second posting that was approximately 2-3 feet away. <I> **** Actions Taken **** The posting was moved to its stickered location and turned to face the correct direction by a Rad Ops Technician. Feedback was provided to the owner of the scaffold carts to ensure that radiological postings are not relocated without the approval and presence of radiological operations personnel. <N> Additional actions taken have been documented under assignment 01. Parent CR is being closed with the Chemistry/Radiological Safety Manager's approval. No further action required.
389634 | CR | 20190204 |  | 3 | Trailer 124 Microwave Ovens Plugged into a Power Tap |  |  |  | N | NO | <D> **** Detailed Description **** Two microwave ovens were observed plugged into a â€œStaplesâ€ brand relocatable power tap in trailer 124 next to the CGS Transformer Yard. This is a violation of ISPM-6, section 3.7.3(e). On 1/24/2019 a similar observation occurred when refrigerators were plugged into power taps (CR 389227). <I> **** Actions Taken **** The microwave ovens were unplugged. The Transformer Yard Coordinator was notified, but he has yet to take possession of the trailer and does not know who has been in the trailer. I appears that someone may be using the trailer as a break area. <N> Trailer has been walked down by Reactor Maintenance and items unplugged. Trailer has also been locked until it is to be used.
389635 | CR | 20190204 | CAQ | C | TSP-RWM-C101 turned into records without signature |  |  |  | N | NO | <D> **** Detailed Description **** TSP-RWM-C101 Surveillance turned into records for indexing without Assigned Reviewer Signature. <I> **** Actions Taken **** Identified missing signature while processing documents, stopped and pulled the document out of the indexing process. Notified Supervisor and wrote CR then returned documents to Ops for correction.
389638 | CR | 20190204 | CAQ | D | Green Color on CMS-SR-20 Particulate Filter | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02130723-01, step 7.10.10, it was noted that the removed particulate filter had a green color to it. <I> **** Actions Taken **** Replaced filter, delivered filter to Chemistry. Continued with surveillance. Wrote CR to document. Informed Supervision. <N> **** Equipment Description **** 548Rx
389639 | CR | 20190204 |  | 4 | Remove the Obstructions In front of Breaker panel in Trailer |  |  |  | N | NO | <D> **** Detailed Description **** A desk, computer CPU and computer monitor was installed in a manner that obstructs access to the breaker panel inside Trailer 165 at the NW corner. ISPM-6, section 3.7.5(d) states that the working space in front of switchboards, motor control centers, breaker panels and disconnect switches may not be less than 3 feet, unless as designed, and must remain unobstructed. The trailer has been located south of the Rad Waste building, is currently unoccupied and will be used to house R-24 personnel. <I> **** Actions Taken **** Initiated WR 29146998 to correct the condition prior to occupancy.
389646 | CR | 20190204 |  | 4 | FPC-V- 13A dual indication issue | N | N |  | N | NO | <D> **** Detailed Description **** During work order 02128105-01 proper indictation was not recieved when stroking the valve. Dual indication was never succefully performed 2 strokes in a row. Open limit switch is believed to be the issue. Indication light stays on when valve is closed. <I> **** Actions Taken **** Stopped work placed job in safe condition notified supervision inititated CR. returned package <N> **** Equipment Description **** FPC-V-13A
389649 | CR | 20190204 | CAQ | C | Calibration Trend of SW-PT-40 | N | Y |  | N | YES | <D> **** Detailed Description **** While monitoring and trending of the Service Water system, past trends of calibration results of SW-PT-40 from ISP -SW-X306 have routinely found OOT both high and low. SW -PT-40 was recently replaced in July of 2018 and the most recent performance of ISP-SW-X306 found it OOT high (AR 389521). This CR is being generated to evaluate this trend further and determine if additional actions need to be implemented. <I> **** Actions Taken **** discussed with supervisor <N> **** Equipment Description **** Service Water A Pumphouse | 02-00-SW-PT-40
389650 | CR | 20190204 |  | 4 | Leak Identified in overhead on South Wall RHRA HX room | N | N |  | N | YES | <D> **** Detailed Description **** While performing VT-2 inspection for RHR System A, there was a leak identified coming from the overhead on the south wall of the RHR-HX-1A room. The leak did NOT appear to be coming from Service water OR RHR valve/piping. HP that were assisting with the VT-2 inspection attempted to identify the valve where the leak was coming from but the view was obstructed and were unable to better identify the EPN where the leak was originating. Leak rate is approximately 40 drops/min. Approx location was R560 K2/8.9 (south wall of HX room). <I> **** Actions Taken **** Notified HP, Shift Manager, and discussed with supervisor Source could not be located - was not RHR nor SW. DId not have contaimination. Source unknow at this time. RHR and SW remain operable. <N> **** Equipment Description **** R560 K2/8.9
389651 | CR | 20190204 |  | 4 | 1 connection for RHR-HX-1A test equip was disconnected | N | N |  | N | NO | <D> **** Detailed Description **** While doing an inspection in the RHR-HX-1A room, it was noticed that one of the thermistor connections to the serial box was disconnected. There is already a known issue with one of the probes reading (+/-) 9999.99 which is a communication error output during thermal performance tests. This unplugged connection is the most probable cause and needs to be re-connected. This is only 1 of 4 connections and there is still 3 other reliable probes obtaining temperature for test purposes. Recommend re -establish connection of probe to serial box and hook up thermal performance test equipment to test whether this fixes the communication error. <I> **** Actions Taken **** Discussed with supervisor This CR is for test equipment associated with RHR A surviellance testing. It has not system function other than to support testing.
389652 | CR | 20190204 | CAQ | B | Question concerning potential access to a posted LHRA | Y | N |  | N | NO | <C> RISK: Medium (B). CAUSE: Uncertain. Investigation Template needed. <D> **** Detailed Description **** On 2/04/19 while providing coverage for walk downs in HRA and LHRA areas on Rx 548, an HP Technician raised a question concerning a potential for unauthorized access to the Rx 548 North Pipe Space (a posted LHRA) from Rx 548 RHR â€˜Aâ€™ Heat Exchanger Room. These two rooms are connected via a pipe chase in the overhead. A scaffold exists in the Southeast portion of the RHR â€˜Aâ€™ HX Room. If accessed, personnel standing on the scaffold platform could not access the pipe chase as it is located 84 inches (7 feet) above the scaffold deck. However, a pipe runs horizontally along the wall under the pipe chase opening and if an individual free climbed upon it, the distance to the pipe chase access could be reduced to 64 inches (5 feet 4 inches). A picture is attached in EDMS showing the configuration <I> **** Actions Taken **** This physical arrangement could challenge the personnel access control requirements in Technical Specification 5.7.2.a. Following this issueâ€™s identification, as a precautionary measure, the area was locked with a LHRA Padlock to establish the access controls required to satisfy the Technical Specification. Additional investigation and evaluation into the issue is required using the guidance provided in Regulatory Guide 8.38 to determine if the access controls were adequate. This investigation will include conducting surveys of the North Pipe Space to verify its radiological conditions. This investigation will be completed on 2/05/19. The Radiological Services Manager was informed and approved the additional controls. A Licensing representative was notified as was the Shift Manager. <R> During the 2019 PI&R Inspection, this condition was proposed as a Licensee-Identified Green Non-Cited Violation of Technical Specification 5.7.2 for failure to control a Locked High Radiation Area, which could allow unauthorized access to the Reactor Building 548â€™ north pipe space. No cross-cutting aspect has been assigned to this violation.
389653 | CR | 20190204 |  | 4 | CW-A Basin Indication in MCR Downscale Low | N | N |  | N | YES | <D> **** Detailed Description **** Received â€œCW Bay Level High/Lowâ€ alarm (H13-P840.A4.7-4). CW-LI-4 indicated downscale. A few seconds later, the alarm cleared and CW-LI-4 indication returned to normal. CW-LS-4 drives the alarm and it senses CW-A basin level. CW-LI-4 also indicates CW-A basin level. CW-LT-4 drives both of these indications. CW-C basin level indication or alarms were not affected. | 02-00-CW-LT-4
389654 | CR | 20190204 |  | 4 | Cut a 3'X5' section out of the filter in RB HVAC filter | Y | N |  | N | YES | <D> **** Detailed Description **** Entered RB HVAC to cut a 3'X5' section out of the filter to support the lowering of stack flow 60 kcfm, per SOP -COLDWEATHER-OPS. RB stack flow increased following this effort to 69 kcfm. | 02-00-ROA-FL-1A
389655 | CR | 20190205 | CAQ | D | Received Oscillograph Started | N | N |  | N | NO | <D> **** Detailed Description **** The following sensors were tripped and are J7, J11, and J15: BPA reports the following: a. Cause was lower monumental - Little Goose#1 b. single pole c. No damaged equipment d. line locked out e. No emergent outage needed f. 500kv involved j. 540kv k. No RAS initiated
389656 | CR | 20190205 |  | 4 | PTZ 39 Requires Maintenance |  |  |  | N | YES | <D> **** Detailed Description **** PTZ 39 is not functioning as designed and requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervision notified. Initiated CR/WR. | 02-00-SEC-CCTV-39
389657 | CR | 20190205 |  | 4 | HT-HTP-FP/6 ckt 24F Low Temp. light flashing. | N | N |  | N | YES | <D> **** Detailed Description **** LOW TEMP light flashing on ckt 24F (in addition to POWER light not illuminated and NO CONTINUITY light flashing, written up on 1/25/19) <I> **** Actions Taken **** Notified CRS | 02-00-HT-HTP-FP/6
389658 | CR | 20190205 |  | 4 | CF-P-42B Oil Level LOW | N | N |  | N | YES | <D> **** Detailed Description **** On rounds we verify oil level is between 1/4 and full. The oil was just touching the bottom of the dipstick, which is out of spec. Needs oil added. <I> **** Actions Taken **** Informed MCR. <N> Added oil. No further action required | 02-00-CF-P-42B
389660 | CR | 20190205 |  | 3 | 02106152-02 will not set to finished |  |  |  | N | NO | <D> **** Detailed Description **** 02106152-02 will not set to finished. Gives error code. Request fix issue and set HC task to finished <N> Issue is resolved. WO 02106152-02 is now at FINISHED status. WO was processed to Work Complete in eWP. Maintenance needs to provide Operations with awareness of how to populate applicable fields. An assignment has been created for maintenance to provide awareness AR 388577.
389666 | CR | 20190205 | CAQ | D | Training Record 822862 Record Already Exists |  |  |  | N | NO | <D> **** Detailed Description **** Training Record was turned in to records for indexing and created an exception due to record already existing. <I> **** Actions Taken **** Identified the exception and notified supervisor. Wrote a CR and returned record to training for correction. <N> Operations submitted this record dated 1/31/18. It was a credit for standing watch. It had previously been entered, no further action is required.
389668 | CR | 20190205 |  | 4 | TOA-HV-1B "M" steam coil leak | N | N |  | N | YES | <D> **** Detailed Description **** TOA-HV-1B has a steam leak on the "M" steam coil. The leak was creating a plume that extended about 3ft. The steam leak was isolated and heating coil blowdown valve opened to allow the coil to drain and prevent freezing. MCR to generate LT for configuration control. Please repair coil. <I> **** Actions Taken **** Informed MCR. Isolated leak and established drain path. <N> **** Equipment Description **** TG 501E | 02-00-TOA-HV-1B
389669 | CR | 20190205 |  | 4 | PCN not completed per SWP-PRO-02. |  |  |  | N | NO | <D> **** Detailed Description **** On 02/02/2019, the night shift operating crew initiated PCN 19-0003 for SOP-HVAC/WCH-FILL. The minor revision was filed in the MCR and the Equipment Operators area, but the approval process in APW was not completed within one business day per SWP-PRO-02 step 5.5.1.f. <I> **** Actions Taken **** The operating crew that initiated the PCN will not be on shift until next week. Reviews and approvals were reassigned to the on shift operating crew. The individuals originally assigned to review / approve the PCN were notified by email of the requirements of SWP-PRO-02.
389670 | CR | 20190205 |  | 4 | 25 Pieces of M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** 25 Pieces of M&TE that were Suspended until needed are Now Rejected- Excessed. No Evaluation Required. Each Rejection form lists Original DEF # Suspension & New DEF # Rejection. No Action Required. See EDMS for lists. <I> **** Actions Taken **** None Trending purposes only.
389672 | CR | 20190205 | CAQ | C | CMS-O2H2R-2 Yokogawa not accurate | Y | Y |  | N | YES | <D> **** Detailed Description **** CMS-O2H2R-2 has been reading 1.55% Drywell O2 for over 4 days. When shifted to the Wetwell, CMS-O2H2R-2 continued to read 1.55% O2 despite Wetwell O2 actually being 1.98% O2 according to CMS-O2H2R-1 and CMS-CP-1301. The front panel indication of CMS-CP-1401 indicates Wetwell O2 at 2.05%. | 02-00-CMS-O2H2R-2
389673 | CR | 20190205 | CAQ | C | RECORDS SUBMITTED WITHOUT REQUIRED SIGNATURE |  |  |  | N | NO | <D> **** Detailed Description **** ON 01/31/2019 RECORDS WERE SUBMITTED TO RECORDS CONTROL WITHOUT SIGNATURE ON THE TRANSMITTAL FORM. THIS DOES NOT FOLLOW THE RECORDS SUBMITTAL PROCESS. <I> **** Actions Taken **** NOTIFIED MY SUPERVISOR. SENDING RECORDS BACK TO INFORMATION SERVICES (CYBER TEAM) PERSONNEL WHO SUBMITTED THE RECORD FOR CORRECTIONS AND RE-SUBMITTAL. <N> Inidividual was coached on the importance of ensuring the process is followed.
389674 | CR | 20190205 | CAQ | D | RECORDS SUBMITTED WITHOUT PROPER DOCUMENTATION |  |  |  | N | NO | <D> **** Detailed Description **** RECORDS SUBMITTED WITH INCORRECT DIC AND PROPER SUPPORTING DOCUMENTATION. <I> **** Actions Taken **** NOTIFIED MY SUPERVISOR. SENDING THESE RECORDS BACK TO CHEMISTRY DEPARTMENT FOR CORRECTIONS AND RE-SUBMITTAL.
389675 | CR | 20190205 |  | 3 | Clarification needed for PPM 10.25.6 |  |  |  | N | NO | <D> **** Detailed Description **** PPM 10.25.6 Prerequisite 3.2 states: Clearance order(s) has/have been obtained, as necessary, for performance of Sections 7.2 through 7.8. The term â€œas necessaryâ€ is ambiguous. There is no step specifying when to lift the clearance in 7.8 or later. 7.8.4 appears to require power. While performing in the field, disagreement arose on whether or not step 7.8.3 requires the clearance. This delayed completion of the work. A determination of at what point the clearance can be lifted needs to be made, then specified in the volume 10 procedure. <I> **** Actions Taken **** Conservatively rehung tags.
389676 | CR | 20190205 |  | 4 | Worker backed over cones at Security Checkpoint |  |  |  | N | NO | <D> **** Detailed Description **** On 2-5-19 a new worker realized that they are entered the wrong security checkpoint lane and attempted to back up. In doing so the individual backed over the cones. <I> **** Actions Taken **** Industrial Safety was notified as per ISPM-1 in which an event investigation was not warrented. Informaiton Services Management was notified as per ISPM-1. The individual was provided coaching for behaviors and with an emphasis of stopping if an error has been made. Please assign NCAQ 4 as all actions have been taken.
389678 | CR | 20190205 |  | 3 | eSOMs allowed craft to sign each other off clearances |  |  |  | N | NO | <D> **** Detailed Description **** Craft clicked on "what am I signed on" and got a clearance with some one elses name on it. They contact the other person and that person ask them if they could sign him off and he could. The clearance was D-SW-TCV-11A-010. Review the history and if you have additional questions contact E Knibbe.
389680 | CR | 20190205 |  | 3 | ABN-TSW |  |  |  | N | NO | <D> **** Detailed Description **** ABN-TSW step 4.3 should say "If TSW cannot be restored," so it matches the Bases
389681 | CR | 20190205 | CAQ | D | Security CCTV 19 | N | N |  | N | YES | <D> **** Detailed Description **** CCTV 19 tower not functioning as designed. Contact security at 2185 for further information <I> **** Actions Taken **** comp measure posted. Security supervision notified. CR/WR generated for electrical support <N> Compensatory measures have been established and are in place. | 02-00-SEC-CCTV-19
389682 | CR | 20190205 | CAQ | C | Trending and monitoring, DSA Dryer degradation | Y | N |  | N | YES | <D> **** Detailed Description **** DSA dryers have been identified as having low margin, have failed due point multiple time and have developed through wall leaks. Due to these issues system engineer needs to review the stategy for PM. A SMS changed the frequency of inspection based on expected wall loss. The failure on DG1 dryer occured prior to performing this inspection. It is postulated that the previous maintenance practices may have contributed to the failure. The repair WO includes direction to document material condition for engineering review and further trending as more information is needed in developing a conclusion. This information will be used to re-assess the urgency of a design change for the dryers currently scheduled for FY27. Based on a failure frequency of less than the 8 years remaining this design change does not support equipment reliability. Failure of these dryers is a operator burden as they have take action to manually bleed off moisture multiple times per shift. Cross referenced AR contain a full list of AR pertaining to dryer history. <I> **** Actions Taken **** Documented trending and monitoring results. | 02-00-DSA-DY-1A
389683 | CR | 20190205 |  | 3 | Files on server 89 g:drive missing | N | N |  | N | NO | <D> **** Detailed Description **** Files in path G:\Amanda that are maintained for the Calibration lab were noticed to be missing at approximately 2:37pm. These files are important as we are coming up on two internal audits for the Calibration Lab. <I> **** Actions Taken **** contacted 8400 IS support and spoke to support. They are going to send the request to an analyst to see if they can see the files on the back up tapes. They will contact me. (name removed)
389684 | CR | 20190205 |  | 4 | RCC-MO-4C Potentiometer | N | N |  | N | YES | <D> **** Detailed Description **** During the determ of RCC-MO-4C under WOT 02115185-08, the vendor wires on the potentiometer show sighns of severe heat damage. Also some signs of corrosion on the base of the bracket. <I> **** Actions Taken **** Took pictures, informed supervision, informed engineering, wrote CR <N> Added a photo to EDMS Docs | 02-00-RCC-MO-4C,02-00-RCC-POT-4C
389685 | CR | 20190205 |  | 3 | Hopewell Calibrator special form certificate set to expire | N | N |  | N | NO | <D> **** Detailed Description **** Hopewell Designs manufactures the BX3 Box Calibrator used at CGS for HP Portable instrument calibrations. The Cs-137 source provided in the calibrator was supplied by REVISS Services Limited in the United Kingdom. REVISS was recently acquired by a new company that has announced they will no longer maintain any existing special form certificates (SFCâ€™s) and these be allowed to expire after October 2019 on certain models, (the 6000 series), of source capsules. The Hopewell BX3 has one of the models (an R6040) of the identified sources. The loss of these SFCâ€™s could have a significant impact on the transportation of these sources because they will be re-categorized as normal form radioactive material. In the event that CGS would need to transport the source at some point in the future (such as for disposal, or reconstitution) the cost of transportation could increase significantly. . This issue is related to Class G non-plant equipment. It is a potential for cost escalation and transportation in the future and does not impact the current proper use and operation of the BX-3 Box Calibrator. This CR was initiated to document the condition and evaluate what impact the expiration of SFCâ€™s will have, and to explore possible options to resolve this issue or a long term solution. <I> **** Actions Taken **** Confirmed source model ID and information in the source tracking database. Contacted Radiological Support/Chemistry Supervision and RP Management including the Rad Material Transportation Group. A copy of the Customer Notification Letter is attached to EDMS.
389686 | CR | 20190205 | CAQ | D | CCTV 42 | N | N |  | N | YES | <D> **** Detailed Description **** Security CCTV 42 not functioning as designed. Contact security @ 2185 for more information. <I> **** Actions Taken **** CR/WR Generated. Electricians notified. Compensatory measures are in place. | 02-00-SEC-CCTV-ISFSI/42
389687 | CR | 20190205 |  | 4 | Personal Medical Condition â€“ Transport Off-Site | N | N |  | N | NO | <D> **** Detailed Description **** On Tuesday, February 5, 2019 an Energy Northwest employee experienced a personal medical condition in their work area at the Kootenai Building. The individual called x2222 for assistance at 1:43 pm. A man-down tone out was initiated and the individual was assisted by Medical Responders. Industrial Safety and an Occupational RN arrived later to assist. Hanford Fire Department (HFD) Medic 1922 and Ladder 1923 arrived at 2:04 pm. The patient was further evaluated by HFD and transported to Kadlec Medical Center at 2:21 pm - During the 2222 call, the Security Communications Center reported that Occupational Health did not pick up the call. The Main Control Room and the SCC gathered the information to dispatch responding personnel. <I> **** Actions Taken **** The employee is from organization 72300. The supervisor left site to meet the patient at Kadlec Medical Center. Emergency Preparedness was notified of the event for ERO purposes. IS call ticket SR-0000353 initiated to check the 2222 phone line for operability at Occupational Health.
389688 | CR | 20190205 | CAQ | C | Alpha activity in WEA-B effluent above procedure spec | N | Y |  | N | NO | <D> **** Detailed Description **** This does not affect plant operation. While performing surveillance 16.11.4, the gross alpha concentration for the WEA-B monthly composite particulate alpha analysis was observed to be 7.25E-12 uCi/cc which is above the procedural specification of 1.14E-13 uCi/cc. Chemistry supervision was contacted and determined that the value in ODCM table 6.2.2.1-1 (E-11 uCi/cc) has not been exceeded. The alpha activity in the rad waste building effluent air is calculated during this surveillance via dividing the alpha activity observed on the sample air filter by the total air drawn through the filter (activity/volume = uCi/cc). Due to the limited run time of WEA-B during January (approximately 20 minutes), and the smaller sample size that resulted, the detection limit for this analysis was greatly diminished and was calculated to exceed the procedural limit. The procedural limit is set to 1% of the value in ODCM table 6.2.2.1-1. Recommend catagory delta trend. <I> **** Actions Taken **** Contacted supervisor. Referred to ODCM.
389689 | CR | 20190205 | CAQ | D | Roof leak in DG2 room | Y | N |  | N | YES | <D> **** Detailed Description **** There is a roof leak in DG2 room, above the southwest side of DG-ENG-1B1. The water is not landing on the EDG, but to the left of the grating available to stand on. Likely due to snow accumulation, but should be evaluated. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** DG2 Roof
389692 | CR | 20190205 |  | 3 | Revise 4.601.A2 |  |  |  | N | NO | <D> **** Detailed Description **** The temperature for LD-MON-2B point A3-2 to annunciate and isolate is 150 F. The temperature listed in section 1-3 is 50 F. I recommend updating this procedure to the correct value. Ref IMDS for LD-MON-2B (LD-TE-18H). Step 1 in section 5-7 refers the user to Technical Specification 3.3.3 (which doesnâ€™t exist). I recommend changing it to 3.3.5.1 and deleting step 2. This would make the section consistent with the division 1 version in 4.601.A3 5-1. <I> **** Actions Taken **** None
389693 | CR | 20190205 | CAQ | D | MS-FR-613 and computer point B018 (core flow) erratic | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02138970, then taken back to complete <D> **** Detailed Description **** Between 20:40 and 20:45 on 02/05/19 total core flow indication on MS-FR-613 and computer point B018 (core flow) lowered from ~103 Mlbm/hr to ~102 Mlbm/hr and then rose back up to102.5 Mlbm/hr. Coincident to this rod line changed (upward) from 102.8% to 103.4% as observed on the TDAS overview page. Individual drive loop flows remained steady through this observation indicating no actual change in core flow. This is a similar to an occurrence documented by CR 388985 on 01/17/19. Additional similar CR's indentified in the Cross References. <I> **** Actions Taken **** Notified the CRS and Shift Manager. Sumbitted CR and WR to document the issue. | 02-00-MS-SUM-606
389694 | CR | 20190206 | CAQ | D | PP50T Requires Maintenance |  |  |  | N | YES | <D> **** Detailed Description **** PP50T is not functioning as designed and requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervision notified. Initiated CR/WR. Compensatory measures initiated. <N> **** Equipment Description **** PP50T Box located inside building 63
389695 | CR | 20190206 |  | 4 | CAS-C-1A low oil level | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1A oil level is below the minimum spec of 1/8". Please add oil. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 441 E | 02-00-CAS-C-1A
389696 | CR | 20190206 |  | 4 | RW501 elevator doors stuck | N | N |  | N | YES | <D> **** Detailed Description **** The exterior RW 501 elevator door continues to get stuck and won't let passengers off or on. The interior door attempts to open and moves just a little but then stops and the elevator pauses until the closed button is depressed. A little pressure on the exterior door from the hallway in the closed direction will sometimes open both sets of doors. This is not happening on any other floor and the track was carefully inspected for debris. It seems to be a mechanical linkage issue or that the exterior door is not contacting the close sensor completely. <I> **** Actions Taken **** Informed the MCR. | 02-00-W-DOOR-C400
389697 | CR | 20190206 | CAQ | D | 3 Pieces of M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** 3 Pieces of M&TE were Suspended as Lost. Never Located. Now Rejected. No Evaluation Required. Each Rejection form lists Original DEF # Suspension & New DEF # Rejection. No Action Required. See EDMS for list. <I> **** Actions Taken **** None Trending purposes only
389699 | CR | 20190206 | CAQ | D | Asset Suite Installation history error MS-RMS-RV/2A & 3A |  |  |  | N | NO | <D> **** Detailed Description **** This is a legacy configuration documentation issue only and does not affect the proper operation of plant equipment. Asset suite panel D034, â€œInstallation Historyâ€ lists the incorrect switch Model CR2940UN203F1 (UTC 380839) and Model CR2940UN203F1 (UTC 380843) as being installed in MS-RMS-RV/2A and MS-RMS-RV/3A respectively. It was determined via OEM email correspondence, electrical wiring diagrams, and plant walkdowns that the correct model for the subject installed switches is CR2940UB203F1 (see EDMS email correspondence). This Asset Suite issue will be corrected via scheduled replacement of the installed CR2940UB203F1 switches under R24 WO 02135237 and WO 02136021. CGS Planning has been notified and MRs have been issued for the correct model switch. Recommend trend only CR. <I> **** Actions Taken **** notified planning, moved MR's, identified correct CID to support R24 work <N> **** Equipment Description **** MS-RMS-RV/2A, MS-RMS-RV/3A | 02-00-MS-RMS-RV/2A,02-00-MS-RMS-RV/3A
389700 | CR | 20190206 |  | 4 | Laborers and HP exceeded dose budget for January |  |  |  | N | NO | <D> **** Detailed Description **** HP dose was 655 against a goal of 254. Laborer dose was 449 against a goal of 249 in the month of January. This was mostly due to RWCU ultrasonic flow work that came in a T-2 so was not in the dose budget and RW 437 recovery activities after loading SDIV piping in an open top liner. <I> **** Actions Taken **** wrote CR
389702 | CR | 20190206 |  | 4 | Door will not stay shut on SAM-12 @ HP PAP | N | N |  | N | NO | <D> **** Detailed Description **** - (HP-EQ-42814) Door on SAM-12 @ HP PAP will not stay shut to monitor items. SAM-12 will be taken OOS until fixed. <I> **** Actions Taken **** -Notified HP Supervision -Initiated Condition Report & Work Request <N> **** Equipment Description **** (HP-EQ-42814) SAM-12 @ HP PAP.
389706 | CR | 20190206 | CAQ | C | Shipping software issue |  |  |  | N | NO | <C> CR Priority and Severity moved to CAQ/C at the direction of OFM on 02.12.2019. <D> **** Detailed Description **** Shipping characterization of radioactive material shipment that do not meet DOT radioactive requirements (non-DOT shipment) can be done manually or by using a computer program. Over the last 18 months these types of shipments have been characterized manually in accordance with PPM 11.2.23.3. An issue with the Integrated Shipping & Inventory Program (ISIP) software was discovered during the implementation of PPM 11.2.23.2, Computerized Radioactive Waste and Material Characterization for a recent non-DOT shipment. The characterization report generated by the software provided conflicting characterization of the shipment. One block on the report identified the shipment as â€œLimited Quantityâ€ while another block on the report identified the shipment as â€œnon-DOT radioactive materialâ€. A review of the report and the software identified that the software does not provide all the necessary information needed to characterize a shipment as â€œnon-DOT radioactive materialâ€. The DOT definition of radioactive material (49 CFR 173.403) is any material containing radionuclides where both the activity concentration and the total activity in the consignment exceed the values specified in 49 CFR 173.436. The ISIP software reports the activity for the material compared to values in 49 CFR 173.436. The software does not report the total activity in the consignment. <I> **** Actions Taken **** RPM and shipping supervisor notified. Software vendor notified of issue. Shipment characterization reviewed for total consignment activity in accordance with PPM 11.2.23.2 and 49 CFR 173.403. Non-DOT shipments will be characterized manually using PPM 11.2.23.3.
389707 | CR | 20190206 |  | 3 | Removal of admin hold requires HGU re-enrollment |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** After removing the admin hold, the individual's green badge would not allow for PA access at the turnstyles. CAS confirmed the badge was active with no hold. Once the individual was re-enrolled in HGU, PA entry was allowed. This same issue occured with another admin hold removal (CR#388439). Contact Access Authorization for further details. <I> **** Actions Taken **** Contacted Security Services Manager and Computer Engineering Please assign to org #54211 <N> **** Equipment Description **** IEBS 1
389708 | CR | 20190206 |  | 4 | EDR-DM-9 performance has degraded | N | N |  | N | YES | <D> **** Detailed Description **** EDR-DM-9 performance has degraded. The EDR filter has to be backwashed and precoated at least once and sometimes twice a shift. I performed a backwash and precoat today and processed ~45% water from CFD decant water and the filter tripped on high D/P. I believe that the FDR iron problem and cross connecting the two systems have caused the performance issues we are now seeing. I believe it is time to consider the septa replacement for the EDR filter. This costs a lot of time and money in manpower, resin costs and disposal costs. <I> **** Actions Taken **** Contacted system engineers, shift management and wrote this CR/WR | 02-00-EDR-DM-9
389709 | CR | 20190206 |  | 4 | SA-FN-1 belt degraded | N | N |  | N | YES | <D> **** Detailed Description **** The belt is ready to break, Belt should be replaced lw. <I> **** Actions Taken **** Told my supervisor . Notified MCR <N> **** Equipment Description **** 467 above the SA compressor. | 02-00-SA-FN-1
389712 | CR | 20190206 |  | 3 | (QA) EWP Copy / Paste Vulnerability |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Sign-offs within work documents in the EWP process can be copied and pasted into other locations. Initials, dates, and signatures can be copied and pasted using features within tablets, as well as in DataGlance while in edit mode. This creates a vulnerability where sign-offs can be copied and pasted in such a manner as to make it appear activities were performed that were not. Electronically copied sign-offs would be difficult to detect and dispute. . <I> **** Actions Taken **** Notified Quality Services Supervisor and EWP Support.
389713 | CR | 20190206 |  | 4 | Chemical Transfer Pump Repair | N | N |  | N | NO | <D> **** Detailed Description **** In building 33 the sodium hypochlorite transfer pump switch is loose internally. This is the pump that is used to transfer sodium hypochlorite from the plastic drum to the storage tank. <I> **** Actions Taken **** Informed Supervision, generated CR, generated WR <N> **** Equipment Description **** Tygon tubing transfer pump below sodium hypochlorite tank
389714 | CR | 20190206 |  | 3 | DBAI SA 2019- FSAR Sect. 6.2.4.3.2.1.1.1 Incorrect Reference |  |  |  | N | NO | <D> **** Detailed Description **** FSAR Section 6.2.4.3.2.1.1.1, fourth paragraph, references calculation C106-92-03.09 for the 20 minute operation action to close reactor feedwater valves RFW-V-65A or RFW -V-65B. Section 4.10 of calculation C106-92-03.09 discusses closing of these valves at the operatorâ€™s discretion, but the 20 minute requirement is not discussed specifically. ABN-CORE does discuss the 20 minute requirement in sections 4.6.6 and Bases section 4.6.6. Therefore, in addition to C106-92-03.09, ABN-CORE should also be added as a reference. Changing references in the FSAR does not require an LDCN. See EDMS for FSAR reference markup. <I> **** Actions Taken **** Sent markups to Licensing to add additional reference of ABN-CORE to FSAR Section 6.2.4.3.2.1.1.1. This issue is documented in the DBAI SA database as well. Discussed with DBAI SA Lead, Operations, and Design Mechanical Supervisor.
389715 | CR | 20190206 | CAQ | D | Received Trouble on drop 4.3 on FCP-1 | N | N |  | N | YES | <D> **** Detailed Description **** Craft was performing PPM 15.2.25 per WO #02100772-01 and received trouble alarm on drop 4.3 on FCP-1 after initiating manual pull station FP-MPS-18/33. <I> **** Actions Taken **** Craft stop and notified supervisor. Notified FA engineer and initiated CR and WR. Engineer advised the End of line device/capacitor for zone 18 detections needs to be replaced. Trouble alarm on this zone does not inop the system for a Fire alarm is still received. Notified Control Room. <N> **** Equipment Description **** RX 572' N.8/8.3 | 02-00-FP-MPS-18/33
389716 | CR | 20190206 | CAQ | D | CIA-PS-22A found out of tolerance | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** while performing ISP-CIA-Q901 step 7.1.14 CIA-PS-22A was found out of tolerance. setpoint is at 156 psig admin limits are 154 to 158 the trip was found at 152 psig. <I> **** Actions Taken **** Calibrated CIA-PS-22A to setpoint of 156 psig. Notified CRS and supervision. initiated this CR for trending purposes. <N> **** Equipment Description **** rx 548 E-IR-67
389717 | CR | 20190206 |  | 3 | CID 8630 1250 HP Motor Set up and Maintenance. |  |  |  | N | NO | <D> **** Detailed Description **** Receiver # 68897 PO 350252, CID 8630 QL 0 was received on 08/30/2018. W/R # 29143875 and AR 382917 were created as required to ensure set up for Maintenance and Maintenance activities for long term storage. Per SCSI 3.6 section 2.7.6 if these actions are not completed within 90 days then Warehouse Supervisor is to initiate a CR. Recomend assignment to Maintenance for resolution. <N> Work being performed in parallel with W.O.# 02130225-01. Marty Robinson and Levi Dunlap walked motor down on 4/16/19. Discussed work and status with Component Manager (Reg Wainwright) permission obtained to adjust due date as issues are resolve. There is an Anti-rotation device still installed on the motor and there is a question about if the current staged location is adequate. Contacted Nelson Robles (Motors Engineer) about location and path forward. 4/17/19 Foster
389720 | CR | 20190206 | CAQ | C | (DBAI SA 2019) Improper revision of PPM 5.6.2 in MCR and SIM |  |  |  | N | NO | <D> **** Detailed Description **** During review of procedures for the DBAI self-assessment it was identified that there were two different versions of PPM 5.6.2 in the Emergency procedure cabinet in the Main Control Room. This procedure was revised on 1/14/19 and the cabinet had the old revision (Major 11/Minor 001) and new revision (Major 12/Minor N/A) enclosed. The outdated revision was enclosed with the required key and so this was an error likely situation for the operators. The simulator was also verified and the ESP cabinet had the correct version, however the CRS ABN file cabinet was out of date. All old revisions were removed immediately. Recommend review of the periodicity and/or process for inventories per PPM 5.0.6 and also ensure that document control is aware of all locations in the plant and simulator. <I> **** Actions Taken **** SM Notified <N> Operations is responsible for filing in the MCR Emergency Support Drawer. Document Control makes the copies and delivers them to the Control Room Supervisor. The Simulator is filed by Document Control but it is a Level 2 file which means that verification prior to use is required. None the less, this CR will be discussed at Document Control's weekly meeitng today. This CR should be assigned to Operations.
389721 | CR | 20190206 |  | 3 | (DBAI SA 2019) Time critical actions not listed in OI-69 |  |  |  | N | NO | <D> **** Detailed Description **** During review of procedures for the DBAI self-assessment it was identified OI-69 did not reference a time critical action called out in the FSAR. FSAR 6.2.4.3.2.1.1.1 references isolating the feed water lines within 20 minutes following the cessation of feed water flow to prevent the release of radioactivity in the event of an accident. ABN-CORE, step 4.6.6 has the required action, however OI-69 needs to be updated to reflect the time critical action. Additionally a time critical action needs to be added to reflect the 2 hour requirement to secure TO-P-EOP within 2 hours per PPM 5.6.2, Attachment 8.4, step 8.4.5. This is required per calculation 2.05.01. This is an administrative issue only. Recommend assignment to the OPS procedure group. <I> **** Actions Taken **** SM Notified
389722 | CR | 20190206 |  | 3 | (DBAI SA 2019) Administrative enhancements to OI-69 |  |  |  | N | NO | <D> **** Detailed Description **** The following are administrative enhancements to OI-69. Recommend assignment to OPS procedures group. TCOA-9 (page 14) and attachment 9.3 (page 30) needs to be updated to reflect that the action is actually completed in step 7.7.2. TCOA-33 (page 21) and attachment 9.3 (page 51) needs to be updated to reflect that step 8.4.4 is also required to meet this action in addition to 8.4.1, 8.4.2, and 8.4.3. <I> **** Actions Taken **** SM Notified
389723 | CR | 20190206 | CAQ | C | (DBAI SA 2019) Calculation 5.51.60 Review |  |  |  | N | NO | <D> **** Detailed Description **** This is a documentation issue only and no SSCs are affected. Calculation 5.51.60 (High Energy Flooding) was reviewed during DBAI SA 2019. During this review, it was discovered that this calculation is out of date in regards to current moderate energy line crack calculation ME-02 -02-02 (Reactor Building Flooding Analysis) flood heights. The flood heights in ME-02-02-02 for moderate energy lines are used as a comparison to the flood heights calculated in 5.51.60 to ensure affected equipment is reviewed for safe shutdown. If the flood height in ME-02-02-02 was higher than 5.51.60 and vice versa, affected equipment was walked down and reviewed for safe shutdown (calc. 5.51.61). Preliminary review of 5.51.60 for the ME-02-02-02 flood heights show the affected room flood heights are lower in ME-02-02-02 than those originally stated in 5.51.60. This means the possible affected equipment originally evaluated is conservative. Therefore, calculation 5.51.60 needs to be revised to correct the flood heights based on calculation ME-02-02-02 or a determination to make 5.51.60 Historical should also be pursued. Assign to AR-DMC. <I> **** Actions Taken **** Discussed with Operations, DBAI self-assessment lead and mechanical supervisor.
389725 | CR | 20190206 |  | 4 | CBD-TT-10 found OOT could not adjust. | N | Y |  | N | YES | <D> **** Detailed Description **** CBD-TT-10 found OOT. we adjusted the transmitter and when inputing, decending as left, the transmitter drifted out of tolerance. could not adjust in and have it remain in. cal. <I> **** Actions Taken **** write the CR to request transmitter be replaced. | 02-00-CBD-TT-10
389727 | CR | 20190206 |  | 4 | Zinc skid d/p gage not reading correctly | N | N |  | N | YES | <D> **** Detailed Description **** The d/p gage on the zinc skid is not reading correctly. The reading has been steady at 2.0 psi for an extended period of time. Adjustment of the zinc skid flow does not result in any change in the d/p reading. Recent adjustment of the zinc flow up to 70 gpm should have resuted in ~10 psi d/p per the design calc for ZINC-TK-1 in CVI-869-00,4. Repair or replace ZINC-DPI-5. <I> **** Actions Taken **** Informed Chemistry supervision. Attaching a WR to this AR/CR. | 02-00-ZINC-DPI-5
389729 | CR | 20190206 |  | 4 | EDR-AO-22, actuator seals blown | N | N |  | N | YES | <D> **** Detailed Description **** The pressure decay test of EDR-V-21 was found to be satisfactory with no leakage. WO#02138023 was revised to perform a pressure decay test of EDR-AO-22 which is cross tied to the same spv. The pressure decay test failed with gross leakage indicating that the piston seal of EDR-AO-22 is blown and requires rebuild. This is a borq-warner y-body globe valve with a miller double acting piston. <I> **** Actions Taken **** Notified the FIN SRO and planning. Generated work request to perform the repair. | 02-00-EDR-AO-22
389730 | CR | 20190206 | CAQ | D | Divergence between X164 and LPCS-FI-600 | Y | N |  | N | YES | <D> **** Detailed Description **** There was unusual behavior exhibited during the performance of OSP-LPCS/IST-Q702. At the start of the test when LPCS -P-1 was started these to metrics were the same. As flow was dialed in as read on LPCS-FI-600 it was observed that the X164 computer point would initally follow the FI indication and then the computer piont would then decay to a lower value than the FI. The divergance ranged from 200 gpm to around 350 gpm. Suspect that the TDAS point may be out of calibration. Both these points are fed from LPCS-FT-3 so they sould behave the same <I> **** Actions Taken **** Wrote this CR and WR against TDAS-MUX-5 | 02-00-TDAS-MUX-5
389733 | CR | 20190206 |  | 3 | SOP-RWCU-START needs revision |  |  |  | N | NO | <D> Step 5.8.1.b.2).a).(1) refers to the wrong flow switch. The step should be to "Install Fluid Components FM71 or equivalent at local CRD-FS-2A . Step 5.8.1.b.2).a).(3) refers to the wrong flow switch. Should say " CALIBRATE CRD-FS-2A per IMDS. . Step 5.8.2.b.2).a).(1) refers to the wrong flow switch. The step should be to "Install Fluid Components FM71 or equivalent at local CRD-FS-2B. . Step 5.8.2.b.2).a).(3) refers to the wrong flow switch. Should say " CALIBRATE CRD-FS-2B per IMDS. . This has been incorrect since rev 18. REvision is needed to correct procedure. <I> Wrote CR.
389737 | CR | 20190206 | CAQ | C | XO Circuits down | N | Y |  | N | NO | <D> **** Detailed Description **** All XO PRI circuits are inop <I> **** Actions Taken **** created telco ticket 3986562 Notified EP of degraded notification system. . Contacted author of CR to confirm the scope and extent of the issue. This involves outside telephone lines to EN. <N> **** Equipment Description **** XO - 80000/T1ZF/RCLDWADHN0000/SPKNWADZDS0 - 86-HCGS-526519. XO - 80001/T1ZF/RCLDWADHN0000/SPKNWADZDS0 - 86-HCGS-526520. XO - 80002/T1ZF/RCLDWADHN0000/SPKNWADZDS0 - 86-HCGS-529693. XO - 80003/T1ZF/RCLDWADHN0000/SPKNWADZDS0 - 86-HCGS-529694. Impacts inbound calls to 372-xxxx extensions only. Outbound and internal calls are not affected. ERO notification system is degraded but functional. SCC paging call panel is not affected.
389738 | CR | 20190206 | CAQ | C | (DBAI-SA 2019) Inconsistencies regarding WMA-AH-51A/B fan da |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing the design documents for the WMA system for the Self-Assessment, some inconsistencies were noted between CVI DWG 67-00,94,1 and CVI DWG 67-00,94,2 and calc 9.32.21. These inconsistencies do not call into question the ability of the system to perform its design function as total static pressure is not used in design basis calculations. Design basis calcs for room temperatures are based on design flowrates that were confirmed by field testing. CVI DWG 67-00,94,1 and DBD 351 for WMA-AH-51A shows 3.88 in wg total static pressure with 2 inch external static pressure for 22000 cfm. The 3.88 in wg is a combination of 1.88 internal pressure loss and an assumed 2 inch external pressure loss. Calc 9.32.21 provides a higher external pressure loss. The total static pressure loss should therefore be corrected to 5.5 inches to be consistent with 9.32.21, and the external pressure loss corrected to 3.62 inches. CVI DWG 67-00,94,2 and DBD 351 for WHA-AH-51B shows 5.69 in wg total static pressure with 2 inch external static pressure for 22000 cfm. The total static pressure loss should therefore be corrected to 5.5 inches to be consistent with 9.32.21, and the external pressure loss corrected to 3.62 inches. <I> **** Actions Taken **** Wrote CR.
389739 | CR | 20190206 | CAQ | C | (DBAI-SA 2019) ME-02-87-95 still mentions FARR 30/30 filters |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing ME-02-87-95 for the DBA Self Assessment, it was noticed that the calc performed analysis for the ASHFALL event using FARR filters and it also performed analysis for the ASHFALL event using MEGAPLEAT filters. EC 14202 and 14204 upgraded the filter racks and directed the use of MEGAPLEAT filters. ABN-ASH was modified to direct installing MEGAPLEAT filters at the start of an ashfall event. As such, the analysis that uses FARR filters is no longer relevant and should be removed to avoid confusion. The dust storm analysis should stay in place for dust storm until such time as FARR filters are no longer utilized for non-ashfall use. The ME-02-87-95 conclusion section is confusing as it does not discuss what is meant by minimum and average. One has to search the calc to see it means minimum filter efficiency and average filter efficiency. Recommend adding discussion in the conclusion section to eliminate confusion. <I> **** Actions Taken **** Wrote CR.
389740 | CR | 20190206 | CAQ | C | (DBAI-SA 2019 ) Keepfill pipe not in room temperature analys |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing M520 LPCS-P-2 (note 8) recirc line impact to the analysis was questioned. The analysis in ME-02-92 -43, Room Temperature Analysis, does not include the LPCS -P-2 keepfill piping heat load. Addition of keepfill pipe heat load to the MATHCAD model for the LPCS and RHR A pump rooms indicates a 0.4F increase in room temperature per room, leaving a margin of 4F margin in the RHR A pump room and 13F margin in the LPCS pump room to the maximum allowed temperature. As room temperature limits are not impacted, functionality of equipment in the rooms are not impacted. Since RHR B has a 20.7F margin, RHR C has 15.3F margin, HPCS has a 13.2F margin, and RCIC has a 7F margin, and the keepfill systems are of similar in design and scope, revision of ME-02-92-43 will show that functionality in these rooms are also not impacted by keepfill pipe heat loads. Recommend assignment to Engineering to update ME-02-92-43. <I> **** Actions Taken **** Discussed with Sid Morrison, wrote CR.
389742 | CR | 20190206 |  | 3 | (DBAI-SA 2019) DBD 316 Typos Noted |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing DBD 316 for the LPCS system for the Self -Assessment, some typographical errors/incorrect references were noted. On page 25, the differential pressure for LPCS-V-1 should be 70 psid instead of psig. On page 26, the differential pressure for LPCS-V-5 should be 485 psid instead of psig. The 6500 gpm Flow Rate in the Test Line should reference document OSP-LPCS/IST-Q702 instead of ME -02-90-16. These are document errors only.
389743 | CR | 20190206 |  | 3 | TG-TE-SMT1S, IMDS references output to a REMOVED component |  |  |  | N | NO | <D> **** Detailed Description **** The IMDS for TG-TE-SMT1S (HP Turbine 1st stage temperature) references output going to recorder TG-TR-SMT, which is at REMOVED status in passport. <I> **** Actions Taken **** loaded document in EDMS for clarity
389744 | CR | 20190206 | CAQ | D | New RRC Pump 1B Shaft overmachined at Vendor |  |  |  | N | NO | <D> **** Detailed Description **** Vendor infromed EN that the new sleeve being fabricated for the RRC-P-1B inside diameter has been over-machined. This sleeve fits over the completed shaft and is a critical fit up. <I> **** Actions Taken **** 1. Informed RXMM Supervision, Supply Chain and Engineering 2. Current approved payment schedule for FY19 and 20 was analyzed by the Project and Vendor concluding that approved and budgeted payment milestones will not be affected for FY19 and FY20. 3. Vendor will be scrapping the existing sleeve and fabricating a new sleeve resulting in a 9-10 week delivery delay. 4. Iinternal NCR's have been requested from the Vendor Note: RRC-P-1B is scheduled for R-27 (FY2025) replacement
389745 | CR | 20190206 | CAQ | D | New RRC Pump 1A Sleeve final PT Exam O/S Tolerance at Vendor |  |  |  | N | NO | <D> **** Detailed Description **** The new RRC Pump 1A Sleeve final PT exam did not pass an was outside acceptable tolerances. The indicatioon was discovered by a sub-Vendor QC and then verified by the Vendor QC. The indication appears to be a perocity in the casting and is approximately 1/4" long. <I> **** Actions Taken **** 1. Notified RXMM Management, Engineering and Supply Chain 2. The 9 week delay was analyzed for budget impacts. FY19 Payment Milestones for the pump procurement will not be affected becauase the delivery of the pump has moved from February 2019 to April 2019. 3. The Vendor will be machining the current sleeve off the shaft and replacing it with a new sleeve. 4. An internal NCR of this condition has been requested from the vendor. NOTE: RRC-P-1A is scheduled to be replaced during R-25 (FY21) All the other parts for the pump are complete.
389746 | CR | 20190206 |  | 3 | Need electrical support for OSP-DO-Q701, WO 02107361-01 |  |  |  | N | NO | <D> **** Detailed Description **** This OSP requires Electrical support to perform vibration monitoring on DO-P-1A this occurrence did not have a complimentary support task to notify Electricians that OPâ€™s would require support. This CR is to document this and to generate a WR to support step 7.2.19 <I> **** Actions Taken **** Wrote CR, supported OP's <N> **** Equipment Description **** DO=P=1A
389747 | CR | 20190206 |  | 4 | WOA-FN-4 Has loose/frayed belts. | N | N |  | N | YES | <D> **** Detailed Description **** WOA-FN-4 has loose or frayed belts, which are vibrating a lot. Please adjust/replace as necessary. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 507 behind chillers. | 02-00-WOA-FN-4
389748 | CR | 20190206 |  | 4 | HCO-T-W54 large leak | N | N |  | N | YES | <D> **** Detailed Description **** HCO-T-W54, located next to WOA-FN-4, has a large leak (pencil-sized stream). Please repair. <I> **** Actions Taken **** Laborers put up catch and signs. Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 507 behind chillers. | 02-00-HCO-T-W54
389749 | CR | 20190206 | CAQ | D | WEA-FN-6 has a broken belt | N | Y |  | N | YES | <D> **** Detailed Description **** WEA-FN-6 has a broken belt. Please replace. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 507 behind chillers. | 02-00-WEA-FN-6
389750 | CR | 20190206 | CAQ | D | Blue dot light at E-IR-H22/P015 is out. | N | N |  | N | YES | <D> **** Detailed Description **** The blue dot light over E-IR-H22/P015 is out. Please replace bulbs. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RB 501 NW | 02-00-E-IR-P015
389751 | CR | 20190207 | CAQ | D | 3 Pieces of M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** 3 Pieces of M&TE were Suspended until Needed. Now Rejected- Excessed. No Evaluation Required. Rejection forms list Original DEF # Suspensions & New DEF # Rejections. No Action Required. Calcode #44462 Heise Dig. Gauge- DEF #6941A written. Calcode #44758 Crimper- DEF #6942A written. Calcode #44759 Crimper. DEF #6943A written. See EDMS for more info. <I> **** Actions Taken **** None Trending purposes only.
389753 | CR | 20190207 | CAQ | B | TR-S Lockout | Y | N |  | N | YES | <C> RISK: Medium (B). CAUSE: Uncertain or Complex. Investigation Template Required <D> **** Detailed Description **** At 0407 on 2/7/19 TR-S Locked out. 30 prior to the lockout, the low oil level alarm and the trouble alarm came in. The "Gas Opr. Relay" and the "Transf. Min. Oil Level" flags were in and unable to be reset. The oil level was at the 0 mark. After the lockout, the "Gas Opr. Relay" flag was able to be reset. No new oil leaks were noticed. Temperatures were normal. <I> **** Actions Taken **** Entered ABN-Transformer and ABN-GRID. <N> **** Equipment Description **** XFMR Yard. | 02-00-E-TR-S
389754 | CR | 20190207 |  | 4 | (DBAI-SA 2019) Redesigned aluminum motor evaluation |  |  |  | N | NO | <D> **** Detailed Description **** **This is administrative** The 50.59 Screen No. 5059SCREEN-01-0116 was not re -evaluated to address new large frame aluminum rotor AC motors as detailed in BWROG-TP-14-009. 1. MES-10 Rev 7, Minor Rev 1, MOTOR OPERATED VALVE SIZING AND SWITCH SETTING was revised to incorporate large frame aluminum AC motors into the ComED methodology and incorporate the redesigned DC motor curves into the DC Motor Performance Methodology without performing the applicable AD. The ComED methodology and the DC motor performance methodology has been approved for use since 2002. The BWROG recently updated the ComED methodology to include the new designed Aluminum motors and incorporated the redesigned DC motor curves. MES-10 R7/R1 was revised to update the references to the BWROG reports. AD-19-0077 and 5059SCREEN-19-0018 have been issued/approved. <I> **** Actions Taken **** AD-19-0077 and 5059SCREEN-19-0018 have been issued/approved.
389755 | CR | 20190207 |  | 3 | (DBAI-SA 2019) R23 Overall evaulation on HPCS-V-4 |  |  |  | N | NO | <D> **** Detailed Description **** **This is CR is administrative** An overall documented evaulation was not performed on HPCS-V-4 valve after CR's 366178, 366179, 366640 and 366800 were initiated. All of the right work / inspections were performed, but was not rolled up into a document. The following CRâ€™s were initiated: AR 366178 Unplanned HPCS System Initiation (HPCS-V-4 does not have position indication) â€“ Severity B AR 366179 Loss of Power to HPCS-V-4 â€“ Severity C AR 366640 as-found diagnostic testing anomalies â€“ Severity C AR 366800 HPCS-V-4 Inspection and HPCS-V-12, V-1, and V-15 EOC â€“ Severity D AR 366800 provided pictures/documentation of the actuator refurbishment, brake inspection, magnesium rotor inspection, stem rotation, stem to wedge as-found condition, trace overlays, wedge pin as-found condition and the overall HPCS-V-4 observations. Note to Operations: HPCS-V-4 valve, actuator and motor was thoroughly inspected and repaired during R23. The as-left diagnostic test did not show any anomalies and was setup to meet its design functions.
389756 | CR | 20190207 | CAQ | D | 2 Pieces of M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** 2 Pieces of M&TE were found OOT & adjusted within specs. Not used during Calibration cycles. Calcode #C005416 Fluke Dig. Thermometer- model 52. DEF #6945A written. Calcode #0063921 Fluke Temp Probe- model 80PK-1. DEF #6946A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
389758 | CR | 20190207 | CAQ | D | Re-perform work to verify. MTE as found not available, | N | N |  | N | YES | <D> **** Detailed Description **** Re-perform the following work orders. MTE is suspended/lost. As found not available. Need to verify the data taken was acceptable/usable. 02084670-01 Emergency lighting annual EBUW03 02135436-01 New power supply trending data RFW-E/S-1A <I> **** Actions Taken **** Wrote CR <N> **** Equipment Description **** EBUW03 EPNs | 02-00-RFW-E/S-1A
389759 | CR | 20190207 |  | 4 | 2 Pieces of M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** 2 Quest Technolgies Thermal Environment Monitors- model Questemp 44's were found OOT. Wouldn't Power On- Sent out for Repair. Adjusted within specs. Used for personal safety only. No Plant Impact. Calcode #0065561. DEF #6947A written. Calcode #0067089. DEF #6948A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
389766 | CR | 20190207 |  | 3 | (DBAI-SA-2019) CR 312734 timely closure |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing as part of Design Basis Assurance-Self -Assessment 2019, the following issue was found with outstanding changes to the AED/SPC 206. . QA AR-CR 00312734, â€œ(QA) Design and Licensing basis for ESBO not updatedâ€ has been open since 2014. Recommend prompt review and closure. . Revising AED/SPC 206 (EC 16741) is the only remaining action. E.g., CR 00312734 has already resolved the Licensing Basis issue with LDCN-17-001, which added a reference to GO2-07-139 to Sections 8.3.1.1.7.2.1, 8.3.4, 8A.1 and 8A.2.9: The extended station blackout is not a defined event or accident and, as such, does not warrant inclusion in the FSAR (per the requirements of 10 CFR 50.71(e)). We have described the physical modifications to the plant (such as the cross-connects to DG3) in the FSAR. To improve clarity, we should add a reference to docketed letter GO2-07-139, which succinctly summarizes the role of RCIC in responding to the 10 CFR 50.63 station blackout. This letter also provides a summary of the risk management actions to be taken during an extended DG outage. . ESBO is already discussed in AED/SPC 206, so the change should be editorial. <I> **** Actions Taken **** Recommend assignment to AR-DEI
389771 | CR | 20190207 |  | 3 | (DBAI-SA-2019) PCR OSP-INST-H101 |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing FSAR 8A.2.5.4 as part of Design Basis Assessment-Self-Assessment 2019, the following issue with OSP-INST-H101 was discovered. . OSP-INST-H101, Rev 92, â€œShift and Daily Instrument Checks (Modes 1, 2, 3),â€ Step 20, Note 2 is not consistent with the entry conditions for ABN-HVAC. Note 2 says, â€œIf the temperature is GT 85Â°F, then consider reducing Control Room heat load per ABN-HVAC, HVAC Troubleâ€¦.â€ The entry condition for ABN-HVAC is 78Â°F. . Recommend changing 85 to 78 Â°F in â€œIf the temperature is GT 85Â°F, then consider reducing Control Room heat load per ABN-HVAC, HVAC Troubleâ€¦.â€
389774 | CR | 20190207 | CAQ | D | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0064568 Proto Torque Wrench- model 6064C 200in/lb found OOT & adjusted within specs. Per PPM 1.5.4 section 4.4.3 (a-c) Torque Wrench had acceptable post use verifications @ +/- .06%. DEF #6944A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
389775 | CR | 20190207 |  | 4 | Cooling tower fan 19 motor needs oil. | N | N |  | N | YES | <D> **** Detailed Description **** Cooling tower 2A fan 19 needs oil added to the motor. | 02-00-CW-FN-19
389776 | CR | 20190207 | CAQ | C | (DBAI-SA-2019) Battery LCS SR Not aligned to IEEE Standard | Y | Y |  | N | NO | <D> **** Detailed Description **** As identified during the 2019 DBAI self-assessment, the purpose of this CR is to document a misalignment between application of IEEE 450-(2002) Recommended Practice for Maintenance, Testing, and Replacement of Vented Lead Acid Batteries for Stationary Application, and LCS surveillances SR 1.8.6.1.20 and SR 1.8.6.2.15. . FSAR (8.3.2.1.7.1), states testing and maintenance of lead acid batteries is performed in accordance with IEEE 450 -2002. Section D.2 of this standard addresses intercell and terminal connection resistance, and recommends corrective action when the measured resistance exceeds a threshold value of greater than 20% of the recorded installation value (actual value). Columbia Generating Station implements this resistance check in SR 1.8.6.1.20 and SR 1.8.6.2.15, and instead of comparing resistance values against an installed baseline, the applicable surveillance compares the measured value to calculated values taken from calculation E/I-02-91-01 (derived from original OEM design data). . Since the objective of the resistance measurements is to determine if corrective maintenance is necessary (i.e., threshold to trigger maintenance) from comparison of actual measured values over time to an installed baseline, the applicable surveillances need to be revised to align with the IEEE 450-2002 method. Therefore, the intent of this CR is to drive changes to LCS SR 1.8.6.1.20 and 1.8.6.2, and applicable PPI PPM ESP-B01A-A101, ESP-B01B-A101, ESP-B02A -A101, ESP-B02B-A101, ESP-B11-A101, ESP-B12-A101, ESP -B1DG3-A101, ESP-B21-A101. Recommend CAQ C assigned to Electrical Design (AR-DEI) for resolution. <I> **** Actions Taken **** Discussed with OPS team member as part of SA; Discussed with Shift Manager.
389778 | CR | 20190207 |  | 4 | Major Maintenance Exceeded the January Dose Goal |  |  |  | N | NO | <D> **** Detailed Description **** Major Maintenance dose goal for January was 624 mrem, actual dose was 1,125 mrem. The over-run is attributed to on-going work for MT-CRA-1 upgrade project. The January estimate for MT-CRA-1 work was 675 mrem, actual dose was 1,096 mrem. The MT-CRA-1 project total dose is approximately 70% accumulated with work approximately 90% complete as of 31-Jan-19.
389779 | CR | 20190207 | CAQ | C | INCOMPLETE RECORDS SENT TO RECORDS CONTROL |  |  |  | N | NO | <D> **** Detailed Description **** QAR RECORDS SENT WERE INCOMPLETE AND MORE INFO IS NEEDED TO PROCESS THEM. <I> **** Actions Taken **** NOTIFIED MY SUPERVISION. MADE CONTACT WITH THE E &RP SENDER FOR COREECTIONS AND SENDING DOCUMENTS BACK FOR COMPLETION AND RE-SUBMITTAL.
389780 | CR | 20190207 |  | 3 | (DBAI-SA-2019) LCS B 1.7.2 reference |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing FSAR 8A.2.5.4 as part of Design Basis Assessment-Self-Assessment 2019, the following issue in the LCS Bases was discovered. . LCS Bases B 1.7.2 Control Room Emergency Chilled Water System, Reference 1 is System Description No.SD000201, Control Room, Cable Room and Critical Switchgear Rooms - HVAC (CR-HVAC). This is not a valid licensing or design basis document. Recommend replacing with an FSAR or design basis document reference. <I> **** Actions Taken **** Recommend assignment AR-LIC
389781 | CR | 20190207 |  | 3 | CI-11.13 Attachment 9.1 Needs Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** CI-11.13 Attachment 9.1 for Fume Hood Checks requests "Calibration Date" for velometer used. Not clarified in procedure or attachment if date recorded should be date calibration was performed or date calibration is due.
389782 | CR | 20190207 |  | 3 | Remote racking tool does not fit 480V breakers in GSB |  |  |  | N | NO | <D> **** Detailed Description **** As part of attempting to resotre E-SL-F10 and E-SL-F11 per WO 02120862, operators attempted to fit up the new remote racking tool to trip the 480V feeder breakers being used to supply jumper power from SL-F11 to SL-F10. The plunger for the remote racking tool is too large to fit in hole for the tripping mechanism for these breakers. Request engineering investigate and procure an appropriately sized plunger device to allow the new tool to be used on these brreakers. <I> **** Actions Taken **** Discussed with SM
389783 | CR | 20190207 | CAQ | C | (DBAI-SA-2019) AED SPC 310 Improvements |  |  |  | N | NO | <D> **** Detailed Description **** As part of the DBA Self Assessment, AED SPC 310 Revision 13 was reviewed in response to Fermi Stationâ€™s 2018-06 LER in which their station was exposed to a timing relay vulnerability which inappropriately shed load during design testing from a simulated LOCA signal after the diesel generators were already running. Fermiâ€™s latent design vulnerability was addressed by including a 52a (circuit breaker open) contact in the relay logic to block the LOCA signal. A review of CGSâ€™s protective relaying showed that although the 52a contact block is not depicted in Figure 7 or Figure 8 of AED SPC 310, there is a blocking contact depicted on the EWDs (EWD-46E-106,106A,107,107A). There are no operability concerns. Recommend assigning to AR-DEI at Severity Level C to make several identified improvements to AED SPC 310 including: (i) Re-uploading AED SPC 310 in color (as opposed to revision 13 which is in grayscale) to ensure that the color coded figures (including Figure 7 and Figure 8) can be easily understood. (ii) Removing the â€œUNVERIFIEDâ€ labels from Figures 7,8, and 9 which will be verified as part of this update. (iii) Updating the secondary undervoltage relay trip logic to depict a 2/3 permissive trip on Figure 4 with â€œ1,2,3â€ in the upper right corner of the 2762 (27 undervoltage, 62 time delay) relay. (iv) Updating Figures 7 and 8 to include the 52a circuit contact block as an AND statement similar to Figure 9 to properly depict the circuit load sequencing logic.
389784 | CR | 20190207 |  | 3 | ABN transformer needs updated |  |  |  | N | NO | <D> **** Detailed Description **** Section 7.2.1c needs updated to change the word check to arrange for bullet 1. This step is not performed by the system enigneer based on t he configuration of the buchholz relay. The word check should be changed to arranged.
389785 | CR | 20190207 |  | 3 | (DBAI-SA-2019) CER C93-0154 Contains Typographical Errors |  |  |  | N | NO | <C> CR Priority/Severity changed to Non-CAQ and Severity 3 at the endorsement of MRT on 02.14.2019 <D> **** Detailed Description **** As part of the DBA Self Assessment Review, Component Classification Evaluation Record (CCER) (CER C93-0154) for E-CB-7/71, E-CB-7/73, E-CB-8/81, and E-CB-8/83 was discovered to contain a small typographical error (â€œCS, ar not applicable to the safety functionâ€), formatting errors (large indents in the middle of body text), and unclear references to Technical Specifications stating that the â€œload center must be re-energized within 8-hours, or the plant is shutdownâ€. There are no operability concerns. Recommend assigning to AR-DEI at Severity Level C to correct the typographical errors.
389786 | CR | 20190207 |  | 3 | Door hinges in disrepair on Building 41 |  |  |  | N | NO | <C> No WR was written. <D> **** Detailed Description **** Hanford groundwater sampling crew observed that that hinges on the door at Building 41 are in disrepair and prevents the building from being locked. <I> **** Actions Taken **** Repair door hinges on entrance to Building 41 <N> **** Equipment Description **** Building 41 door hinges ------------- Work request 29147176 submitted to facilities for door repair 2/20/19 WKW - WR action and deferred to FIN Team for Action
389787 | CR | 20190207 |  | 3 | (DBAI-SA-2019) 2.05.01 Revision 14 Typographical Errors |  |  |  | N | NO | <D> **** Detailed Description **** As part of the DBA Self-Assessment Design Review, it was discovered a table in Calculation 2.05.01 Revision 14 Appendix H3 Page 6 and 7 of the calculation from Asset Suite incorrectly depicts the Division 2, 125VDC Voltage of E-B1-2 at T=4 Hours is approximately 210-220VDC. A review of the calculation Native Files displays the expected voltage range of approximately 110VDC between the values published at T=2 Hours and T=6 Hours. It appears that the Appendix H3 copy that was included in the calculation revision should be updated with the correct information from the Native Files. This typo does not impact the results or conclusions of the calculation or invalidate any of the calculation acceptance criteria. There are no operability concerns. Recommend assigning to AR-DEI at Severity Level C to correct the typographical errors with a calculation revision in accordance with DES-4-1.
389790 | CR | 20190207 | CAQ | 3 | (DBAI-SA-2019) Update IMDSs MS-LIS-100(A,B) |  |  |  | N | NO | <D> **** Detailed Description **** During the 2019 DBAI Self-Assessment for review of HPCS-V -4, IMDSs for MS-LIS-100A and MS-LIS-100B were reviewed and found to have a minor typographical error showing an incorrect calibration input value in comparison to the associate calibration procedure ISP-MS-Q913. In the IMDSs, the calibration input under instrument parameters shows an input of 60.0 INWC for a desired Output of 60 +/- 1â€, where ISP-MS-Q913 shows an input of 30.0 INWC for a desired output of 60 +/- 1â€. Update IMDSs to be consistent with ISP-MS-Q913. See EDMS for mark-ups.
389793 | CR | 20190207 |  | 3 | (DBAI-SA-2019) Update SPC 308 for Typographical Errors |  |  |  | N | NO | <D> During the 2019 DBAI Self-Assessment for review of HPCS, SPC 308 was reviewed and found to have a minor typographical errors. On Table 9 (page 32) of SPC 308 it shows Pmax in units of psig instead of psid and the footnote states â€œFootnotes for Table 8â€ instead, needs to be for Table 9. Mark-ups of the typographical errors are provided in EDMS. <N> CR moved to approved status at the request of the Initiator.
389794 | CR | 20190207 |  | 3 | (DBAI-SA-2019) Update SD000174 for Typographical Errors |  |  |  | N | NO | <D> **** Detailed Description **** During the 2019 DBAI Self-Assessment for review of HPCS, SD000174 was reviewed and found to have minor typographical errors and enhancements that could be made. Mark-ups of the typographical errors are provided in EDMS.
389795 | CR | 20190207 |  | 3 | (DBAI-SA-2019) Update E/I-02-92-17 & E/I-02-92-09 for Typos |  |  |  | N | NO | <D> During the 2019 DBAI Self-Assessment, E/I-02-92-17 and E/I-02-92-09 were reviewed. Upon review Typographical and reference errors were identified. In E/I-02-92-17 typographical and reference errors were found in the Introduction and Scope Section and Appendix F of the calculation, see EDMS for mark-ups. Recommend review of PERs referenced to insure details are adequately referenced or included in the calculation. In E/I-02-92-09 typographical and reference errors were found in Appendix C of the calculation, see EDMS for mark -ups. <N> CR found at INPROG status and moved to approved status.
389796 | CR | 20190207 | CAQ | C | (DBAI SA 2019) Calculation 5.51.61 Review |  |  |  | N | NO | <D> **** Detailed Description **** This is a documentation issue only and no SSCs are affected. While reviewing calculation 5.51.60 (High Energy Flooding) for DBAI SA 2019 is was discovered that calculation 5.51.61 (Safe Shutdown High Energy Flooding Analysis) is out of date in regards to references. Possible equipment affected by a flood was identified in 5.51.60 and reviewed for safe shutdown in 5.51.61. . Preliminary review of 5.51.61 does not indicated any equipment is affected for safe shutdown. Therefore, calculation 5.51.61 needs to be revised to correct the out of date references or a determination to make 5.51.61 Historical should also be pursued. Assign to AR-DMC. <I> **** Actions Taken **** Notified my Supervisor. Discussed with DBAI self-assessment lead Wrote this CR <N> Reopened CR per request by owed to group supervisor
389797 | CR | 20190207 |  | 3 | (DBAI-SA-2019) PCR ABN-HVAC |  |  |  | N | NO | <C> CR Priority/Severity changed to Non-CAQ and Severity 3 at the endorsement of MRT on 02.14.2019 <D> **** Detailed Description **** While reviewing FSAR 8A.2.5.4 as part of Design Basis Assessment-Self-Assessment 2019, the following issue in the Station Blackout administrative controls was discovered. . FSAR 8A.2.5.4 credits administrative controls to maintain control room temperature within the initial conditions assumed in the station blackout (SBO) analysis. Administrative controls do not limit extended operation with control room temperature above 85 Â°F. . FSAR 8A.2.5.4, Effects of Loss of Ventilation, credits initial control room temperature to ensure the control room does not exceed 120 Â°F following a SBO. The highest initial temperature evaluated in calculation ME-02-92-37 is 85 Â°F. Operation above 85 Â°F up to 104 Â°F is allowed by Technical Specification LCO 3.7.4 and supported by manual load shedding actions in ABN-HVAC. . ABN-HVAC should be revised to evaluate SBO reasonable assurance of operability (RAO) for control room equipment, when control room temperature exceeds 85 Â°F. FSAR 8A.2.5.4 credits administrative controls to restore control room temperature within the SBO analysis. <I> **** Actions Taken **** Recommend assignment to AR-OPSPROC
389798 | CR | 20190207 |  | 3 | (DBAI SA 2019) AED CAL C106-92-03.02 Review |  |  |  | N | NO | <D> **** Detailed Description **** This is a documentation issue only and no SSCs are affected. While reviewing C106-92-03.02 for the 2019 DBAI SA, it was discovered that one of the referenced procedures, PPI PPM 4.4.4.2 Inadvertent HPCS Start-Up was superseded by ABN-POWER. However ABN-POWER does not contain any steps for inadvertent HPCS start up because it was removed from ABN-POWER in Revision 10 of the procedure and moved to ABN-LEVEL. . For resolution recommend updating C106-92-03.02 to reference ABN-LEVEL. Recommend Assignment to AR-DMC. <I> **** Actions Taken **** Notified my Supervisor Discussed with the DBAI Team Lead Wrote this CR
389799 | CR | 20190207 | CAQ | C | (DBAI SA 2019) AED CAL C106-92-03.02 Review for HPCS-V-4 |  |  |  | N | NO | <D> **** Detailed Description **** This is a documentation issue only and no SSCs are affected. While reviewing C106-92-03.02 for the 2019 DBAI SA, it was discovered that the Stroke Time reference list in the calculation are out of date and need to be updated. . For resolution recommend updating the reference list in C106-92-03.02 and to look at the following calculations for extent of condition: C106-92-03.01 C106-92-03.03 C106-92-03.04 C106-92-03.05 C106-92-03.06 C106-92-03.07 C106-92-03.08 C106-92-03.09 C106-92-03.10 C106-92-03.11 C106-92-03.12 C106-92-03.13 . Recommend assign to AR-DMC <I> **** Actions Taken **** Notified my Supervisor Discussed with the DBAI Team Lead Wrote this CR <N> Reopened per request by owned to group supervisor
389800 | CR | 20190207 |  | 3 | Procedure enhancement to OSP-FLEX-Q705 (Rev 000) |  |  |  | N | NO | <D> **** Detailed Description **** Mechanical maintenance supports the FLEX-GEN-DG5 surveillances by moving the DG5 and load bank out of BLDG 600. The procedure under step 3.5 states when steps 3.3 and 3.4 have been completed then direct maintenance to perform several tasks/steps of which typically are performed by Operations. Recommend that the bulleted steps in Rev.000, Minor rev N/A be enhanced/delineated to call out MECH for sub step 3.5.4, other than that, the other steps should be referenced in 3.5 should be performed by Operations. There are also other itmes such as obtaining keys etc to the building that are called out, in this same section 3.5, which in reality should have and have already been done with respect to coordinating the evolution with Operations. Recommend a generic statement up front stating coordinate activities with Mechanical Maintenance this reduces efforts for obtaining keys etc. <I> **** Actions Taken **** Generated CR. Contact CR originator (WOODS) for more specifics to address this issue. The OSP and staging tasks can continue to be worked through, however enhancing this procedure with ensure the task preview and job scope and who is doing what is clear prior to performing for multiple organizations. <N> **** Equipment Description **** Referenced last occurrence of PMID 26234-01 for history. WOT 02136301
389801 | CR | 20190207 |  | 3 | Task instruction needed for Flocculator chem feed pump maint |  |  |  | N | NO | <D> **** Detailed Description **** Chemistry has a task on a semi-annual frequency to clean check valves on chemical feed pumps for PAX19 and PAC. No task instruction exists for this work to be completed satisfactorily. <I> **** Actions Taken **** Informed chemistry specialist for this system of the need for task instruction, and that a CR will be generated.
389803 | CR | 20190207 | CAQ | C | (QA) Ineffective Corrective Action for AR-CR 380225 ARMA |  |  |  | Y | NO | <D> **** Detailed Description **** The purpose of this ARMA action request was to identify and track PMs on all spare equipment that requires a PM. Assignment 11 contained the master list of equipment that will receive in-storage Preventive Maintenance (PM). â€¢ The list did not include at least 18 components that are currently receiving in-storage PMs. â€¢ System Engineering requested PMs on five spare components that were not on the list. â€¢ Six spare components on the list are not receiving in -storage maintenance and no AR-SMS exists to start a PM. The potential consequence is degradation of spare parts, increased repair costs and the regulatory exposure of not meeting requirements within the Operational Quality Assurance Program Description (OQAPD-01) to perform the PMs on the safety related spare equipment in accordance with the manufacturerâ€™s recommendations. Quality identified this issue during a verification assignment review (VERP) per QSI-8 Quality Action Request Type Condition Report (AR-CR) Resolution. Refer to additional details in EDMS. <I> **** Actions Taken **** Discussed with Quality Management and Supply Chain Services Management.
389804 | CR | 20190207 |  | 3 | (DBAI SA 2019) AR 381807 OE Not Reviewed by Engineering |  |  |  | N | NO | <D> **** Detailed Description **** This is a documentation issue only and does not affect any plant SSCs. During the DBAI 2019 Self-Assessment review, it was discovered that OE 432570 (AR 381807) was not reviewed by Component Engineering. Discussed this subject with the component engineer and he stated that this particular OE issue is controlled at CGS with procedures. However, a review of this OE should be performed for generic applicability. The OE is located in EDMS of AR 381807. Recommend assignment to AR-SECOMP to provide a review of the OE for generic applicability to CGS. <I> **** Actions Taken **** Discussed with OE Leads, DBAI self-assessment lead, Component Engineer, and Component Supervisor
389805 | CR | 20190207 | CAQ | C | (DBAI-SA-2019) MCC Overload Summary Missing Decimals |  |  |  | N | NO | <D> **** Detailed Description **** As part of the DBA Self Assessment Design Review, several drawing issues were identified in E528-43 and E528-44 incorrectly shows the load HP and fuse rating for several loads including: Pump DLO-P-2A2 incorrectly listed at 75HP instead of 0.75HP (see EWD-47E-014) Pump DLO-P-2A1 incorrectly listed at 75HP instead of 0.75HP (see EWD-47E-013) Valve RHR-V-40 incorrectly listed as fused at 35A instead of 3.5A (see EWD-9E-039) Pump DLO-P-2B1 incorrectly listed at 75HP instead of 0.75HP (see EWD-47E-015) Pump DLO-P-2B2 incorrectly listed at 75HP instead of 0.75HP (see EWD-47E-016) Pump DLO-P-3B1 incorrectly listed at 75HP instead of 0.75HP (see EWD-47E-019) Pump DLO-P-3B2 incorrectly listed at 75HP instead of 0.75HP (see EWD-47E-020) These are typographical errors only that appear to originate between revisions 14 and 15 of E528-44 and revisions 16 and 17 of E528-44 when the drawings were converted into a new format and some of the original drawing fidelity (including the decimal point) was lost. There are no operability concerns. Recommend assigning to AR-DESDFTE at Severity Level C.
389806 | CR | 20190207 | CAQ | C | (DBAI-SA-2019) TO-P-EOP Overcurrent Coordination |  |  |  | N | NO | <D> **** Detailed Description **** As part of the DBA Self Assessment Design Review, a known miss-overcurrent coordination issue documented in Calculation E/I-02-92-01 (DC Overcurrent Coordination) was re-evaluated for potential improvement. The subject circuit was originally reported and evaluated under PER # 292-409 as acceptable based on the recommendation of Westinghouse (the turbine manufacturer). The fuse feeding TO-P-EOP is sized at 400A per the turbine manufacturerâ€™s recommendation and is known to not coordinate with the upstream 350A fuse which protects E-MC-S2/1B. The current justification for the lack of coordination is that the loads fed from E-MC -S2/1B are non-class 1E and do not perform any safety functions. Although the load does not serve any safety functions, lack of proper coordination also impacts other non-class 1E loads on E-MC-S2/1B.. In the event of a short circuit on the branch feeder circuit serving TO-P-EOP (fused at 400A), itâ€™s likely that the upstream fuse serving E-MC-S2/1B (fused at 350A) would clear the fault first and subsequently de-energize several other non-class 1E loads served from E-MC-S2/1B. There are no operability concerns. Recommend assigning to AR-DEI at Severity Level C to evaluate additional options including: (i) sizing the overcurrent coordination feeding E-MC-S2/1B at 400A, if sufficient margin exists in the feeder cable such as allowable cable ampacity and sufficient short circuit clearing current, to reduce the risk of a fault occurring on the TO-P-EOP branch circuit clearing the upstream overcurrent protection (ii) sizing the overcurrent coordination feeding TO-P-EOP between 225A-350A for a 50HP 250VDC motor as recommended by the fuse manufacturer for an RK5 Time-Delay fuse (FRS ,TRS), which may coordinate better with the upstream 350A fuse following evaluation of the TO-P-EOP inrush and steady state current (by measurement or discussion with the vendor) to avoid nuisance tripping.
389807 | CR | 20190207 | CAQ | C | (DBAI-SA-2019) EC Cancellation of related CMR |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing NE-02-90-39 as part of Design Basis Assessment-Self-Assessment 2019, the following issue in Engineering Change configuration management was discovered. . Plant modification ECâ€™s were canceled, but the cross -referenced CMRâ€™s were not canceled, as required by DES-2 -14 and DES-4-1. A list of such canceled plant modification ECâ€™s is attached to EDMS. The list should be reviewed and actions created to cancel impacted CMRâ€™s. <I> **** Actions Taken **** Recommend assignment to AR-DEI
389808 | CR | 20190207 | CAQ | C | (DBAI-SA-2019) DC Relay Settings |  |  |  | N | NO | <D> **** Detailed Description **** As part of the DBAI Self-Assessment Design Review, the DC relay settings, as found on drawings E514-24, E514-25 and E514-26, were reviewed. Reference documents for selected relay settings need further review and clarification. A majority of the protection settings are related to component alarm functions. Associated battery charger protection settings have an overvoltage trip that is for connected equipment protection only. . The purpose of this CR is to further review (e.g., expand the team and go deeper) with the objective to validate and clarify the technical fidelity of the reference documents provided on the listed E514 drawings. This CR does not impact the operability of the associated DC system. Recommend assigning to AR-DEI at Severity Level C to further evaluate the DC protection reference documents. <I> **** Actions Taken **** Notified Supervisor and wrote CR.
389809 | CR | 20190207 |  | 3 | S-SA Primary Chemistry: Catalyst Loading |  |  |  | N | NO | <D> **** Detailed Description **** Snapshot Self Assessment on Primary Chemistry documents the need to perform Catalyst Loading analysis on a durability monitor coupon or vessel artifact to demonstrate platinum deposition of at least 0.1 ug/cm2. Interim Guidance from EPRI 2018-011, directs that plants utilizing OLNC and seeking inspection relief must now meet the Category 3a NMCA parameters and implementation steps of BWRVIP-62-A Table 3-5 and 3-8 which includes Catalyst Loading as a Primary Parameter. The implementation steps of Category 3A are in place with the exception of verification of Catalyst Loading which will require analysis of a durability monitor coupon or a vessel artifact for platinum deposition GE 0.1 ug/cm2. Assign to Chemistry <I> **** Actions Taken **** Informed Chemistry Management and BWRVIP Program Owner
389810 | CR | 20190207 | CAQ | C | F-SA 71124.08 Incorrect box checked in PPM 11.2.23.2 |  |  |  | N | NO | <D> **** Detailed Description **** During a review of shipping package number 18-40 a discrepancy was found in procedure 11.2.23.2, Computerized Radioactive Waste and Material Characterization, Attachment 7.1, Characterization Worksheet. On Page 14 of 30 under Disposal Site License Limitations, the box stating â€œStability Not Required (SOF <1.0)â€ is incorrectly checked when â€œStability Required (SOF >1.0)â€ should be checked based on the USE SOF value of 1.55. A copy of this page has been uploaded into EDMS for reference. <I> **** Actions Taken **** The correct value was contained in the characterization documents generated by the shipping computer application and on the worksheet. This error did not impact the shipment or the burial of the material. This is considered a deficiency identified during the Focused Self-Assessment on Inspection Procedure 71124.08 Radioactive Solid Waste Processing and Radioactive Material Handling, Storage and Transportation. Discussed deficiency with F-SA team, Chemistry/RP Support Supervisor and Chemistry/Radiological Safety Manager Recommend a CAQ Severity C to AR-RWSHIP.
389811 | CR | 20190207 | CAQ | C | F-SA 71124.08: Shipping package 18-75 documentation |  |  |  | N | NO | <D> **** Detailed Description **** During a review of shipping package number 18-75 the following discrepancies were found: â€¢ PPM 11.2.23.1, Shipping Radioactive Materials and Waste, Section 4.0 completed only for container ID# 1205. An additional Section 4.0 was not completed for packages with different proper shipping names. â€¢ PPM 11.2.23.2, Computerized Radioactive Waste and Material Characterization cover sheet states Attachments 7.2 thru 7.4 not used when Attachment 7.2 was used. â€¢ ISIP shipping type summary lists geometry as â€œcylinderâ€ when package summary lists container model as â€œboxâ€ â€¢ ISIP shipping type summary lists Hazard Class as â€œ0â€ â€¢ ISIP radioactive component report was not included with container ID# 1205 shipping package. â€¢ Radioactive component report for container ID# Netco-6 uses highest dose rate at 1m from bottom of container when it should come from side of container â€¢ No evidence of notification of shipment <I> **** Actions Taken **** These errors did not impact the shipment or burial of the material. This is considered a deficiency identified during the Focused Self-Assessment on Inspection Procedure 71124.08 Radioactive Solid Waste Processing and Radioactive Material Handling, Storage and Transportation. Discussed deficiency with F-SA team, Chemistry/RP Support Supervisor and Chemistry/Radiological Safety Manager Recommend a CAQ Severity C to AR-RWSHIP.
389812 | CR | 20190207 |  | 3 | S-SA Primary Chemistry: Implement portable DH analysis |  |  |  | N | NO | <D> **** Detailed Description **** Snapshot Self Assessment on Primary Chemistry documents the need for a portable analyzer to monitor feedwater and reactor water dissolved hydrgoen. EPRI Interim Guidance Letter 2016-123 B.6 Dissolved Hydrogen Measurement Checklist highlights the importance of accurate measurement of dissolved hydrogen. Currently there is no capability to measure dissolved hydrogen on feedwater and no back up monitoring is available for the in-line reactor dissolved hydrogen monitor. Excess hydrogen is an important measurement in the BWRVIP guidance to demonstrate mitigation and feedwater hydrogen is one of the secondary parameters in BWRVIP-62-A Table 3-5 that are required if the primary parameters are lost for some reason. Assign to Chemistry. <I> **** Actions Taken **** Informed Chemistry Management.
389813 | CR | 20190207 |  | 3 | F-SA 71124.08: Procedure Editorials/Enhancements |  |  |  | N | NO | <D> **** Detailed Description **** During the Focused Self-Assessment on Inspection Procedure 71124.08 Radioactive Solid Waste Processing and Radioactive Material Handling, Storage and Transportation, procedural enhancements/editorials were identified for the following procedures: â€¢ SWP-RMP-01, Radioactive Waste Management Program; â€¢ SWP-RMP-02, The Process Control Program; â€¢ PPM 11.2.23.1, Shipping Radioactive Materials and Waste; â€¢ PPM 11.2.23.41, Use of the Model 8-120B Transportation Cask See EDMS for a details regarding the editorials/enhancements. <I> **** Actions Taken **** Discussed editorials/recommendations with F-SA team, Chemistry/RP Support Supervisor and Chemistry/Radiological Safety Manager Recommend a NCAQ Severity 3 to AR-RWSHIP.
389814 | CR | 20190207 | CAQ | C | (DBAI-SA-2019) 24 VDC Charger Fusing |  |  |  | N | NO | <D> **** Detailed Description **** As part of the DBAI Self-Assessment Design Review, while reviewing E505-2 (DC One Line Diagram), it appears the 24 VDC Chargers (E-C0-1A, E-C0-1B, E-C0-2A and E-C0-2B) do not have output fuses. This is not consistent with the other station chargers which all have charger output fuse protection. The purpose of this CR is to review and evaluate the need of fuse protection on the 24 VDC charger. The CR does not impact the operability of the 24 VDC system. Recommend assigning to AR-DEI at Severity Level C to evaluate the 24 VDC chargers and the possibility of adding fuses to the output. <I> **** Actions Taken **** Notified Supervisor and wrote CR.
389815 | CR | 20190207 |  | 3 | (DBAI-SA 2019) Definition of safe load paths per NUREG-0612 |  |  |  | N | NO | <D> **** Detailed Description **** During the 2019 Design Basis Assurance Self-Assessment (DBAI) it was identified that CGS load handling procedures do not align (minor gaps) with the definition of NUREG-0612 definition. . Definition of (safe) load paths found in the implementing procedures was rather generic (i.e. load path was defined as: intended travel path of the load being moved) and does not meet NUREG-0612, section 5.1.1(1). Safe load paths are not just any paths, but are paths for transport of a heavy load that will reduce or minimize adverse effects of postulated load drops, in terms of releases of radioactive material and damage to safety systems. By definition, this path to the extent practical shall follow structural floor members, beams, etc., such that if the load is dropped, the structure is more likely to withstand the impact. . Suggest assignment to maintenance department to revise heavy load handling implementing procedures (including PPM 10.4.12) to match definition of safe load path as per NUREG-0612. <I> **** Actions Taken **** Discussed issue(s) with Supervisor and Self-assessment team lead and initiated the CR.
389816 | CR | 20190207 |  | 3 | (DBAI-SA 2019) â€“ Potential implementation of NEI 08-05 |  |  |  | N | NO | <D> **** Detailed Description **** During review of the load handling program (compliance with NUREG-0612) in support of the 2019 Design Basis Assurance Self-Assessment (DBAI) the following (minor gap) was discovered: Per section 4.17.5 of PPM 10.4.12: â€œAny deviation from a prescribed safe load path shall be marked on load path drawing and approved by a procedure revision (i.e., NOT by writing a PCN). This procedure revision requires processing per SWP-PRO-02 and completed approvals prior to useâ€¦ â€. The above statement aligns with the definition of load path per NUREG-0612, but the intent of this provision is to perform an alternate safe load path evaluation by Engineering in accordance with section 5.1.1(1) of NUREG -0612. Paragraph 4.17.5 of PPM 10.4.12 is rather vague. Recent industry guidelines and initiatives (e.g. NEI 08-05) provide acceptable actions if deviations from load path are likely to occur, or when safe load paths are nonexistent. Suggest a meeting between Maintenance, Engineering to determine if recommended industry guidelines (NEI 08-05) are presently reflected in heavy load handling procedures if not shouldnâ€™t the station adopt NEI 08-05 guidelines as discussed above (and get OPS input) and create an assignment for maintenance dept. to enhance the above procedures if determined to be necessary. See EDMS for additional details. <I> **** Actions Taken **** Discussed issue(s) with Supervisor and Self-assessment team lead and initiated the CR
389817 | CR | 20190207 |  | 3 | (DBAI-SA 2019) PPM 10.4.14 Enhancement to add 3rd party RVW |  |  |  | N | NO | <D> **** Detailed Description **** During review of the load handling program (compliance with NUREG-0612) in support of the 2019 Design Basis Assurance Self-Assessment (DBAI), it was discovered that PPM 10.4.14, â€œMiscellaneous Load Handlingâ€ does not recommend the need to review vendor supplied documents (although PPM 10.2.12 and 10.4.11 already recommend use of 3rd party review of vendor supplied engineering products). PPM 10.4.11 scope include the handling of components that are considered to meet the heavy load (and critical load) definition and used in various areas (including cranes in R471â€™, R491â€™, R542â€™, T555â€™ and Service Water Pump House to name a few). Consider potential revision of maintenance procedure PPM 10.4.14 to add (internal and) third party review of vendor supplied engineering products, (including vendor calculation, verification of load testing, finite element analyses and factor of safeties used) due to ANO-1 recent heavy load drop event (Main Transformer Rotor in their turbine building). See EDMS for additional details. <I> **** Actions Taken **** Discussed issue(s) with Supervisor and Self-assessment team lead and initiated the CR
389819 | CR | 20190207 |  | 3 | (DBAI-SA 2019) Crane operators qualification per ANSI B30.2 |  |  |  | N | NO | <D> **** Detailed Description **** During review of the load handling program (compliance with NUREG-0612) in support of the 2019 Design Basis Assurance Self-Assessment (DBAI), the following was noted: NUREG-0612 reiterates that qualifications, training, and specified conduct of crane operators shall be per ANSI B30.2-76 (namely Chapter 2-3). Upon review of implementing plant procedures (and few qualification guides) for crane operators qualifications and training requirements (see section A), there were no conclusive evidences that ANSI B30.2, Chapter 2-3 is a requirements for the qualification of CGS crane operators, though ANSI B.30.2 was referenced in many occasions. Suggest Maintenance and Training to discuss and to determine if indeed ANSI B30.2-76 is used for basis of crane operator qualifications at CGS, or show how the intent of B30.2-76 is met if other standards are used. See EDMS for additional details. <I> **** Actions Taken **** Discussed issue(s) with Supervisor and Self-assessment team lead and initiated the CR.
389820 | CR | 20190207 |  | 3 | (DBAI-SA 2019) â€“ Special lifting devices procedure revision |  |  |  | N | NO | <D> **** Detailed Description **** During review of the load handling program (compliance with NUREG-0612) in support of the 2019 Design Basis Assurance Self-Assessment (DBAI), the following enhancements (minor gaps) were recommended: -Suggest assignment for maintenance to correct PPM 10.4.12 in order to match section 5.3.1 of N14.6-78 verbiage. -Suggest maintenance to add 10 min requirement and the required inspection post-test and validate that ANSI 14.6 -78 provisions are properly followed specially testing of critical areas (load bearing members) under section 7.6. 4(h) of PPM 10.4.12. Test records must be retained and readily available. -Suggest Maintenance to determine if the load handling procedures should be revised to add this provision. See EDMS for additional details. <I> **** Actions Taken **** Discussed issue(s) with Supervisor and Self-assessment team lead and initiated the CR.
389821 | CR | 20190207 |  | 3 | DBA-SA 2019) Use of round slings in heavy load handling proc |  |  |  | N | NO | <D> **** Detailed Description **** During review of the load handling program (compliance with NUREG-0612), regulatory requirements, various industry guidelines and relevant OEs in support of the 2019 Design Basis Assurance Self-Assessment (DBAI) the following enhancement (minor gaps) was recommended: Engineering to Consult with Maintenance and determine the necessity of adding a provision regarding use of round sling (i.e. its interdiction especially for critical load) since it was not discussed in ANSI B30.9-1971 which CGS adopted implicitly via NUREG-0612. Potentially affected procedures are 10.4.3, 10.4.12 and 10.4.14. Maintenance to also consider adding statement about (wire) ropes use in load handling procedures (including PPM 10.4.12): â€œRopes shall not directly or indirectly be used as load bearing member during rigging operation but may be used as tether linesâ€. See EDMS for additional details. <I> **** Actions Taken **** Discussed issue(s) with Supervisor and Self-assessment team lead and initiated the CR.
389822 | CR | 20190207 |  | 3 | (DBAI-SA 2019) Bases for NUREG-0612 Crane Design Requirement |  |  |  | N | NO | <D> **** Detailed Description **** During review of the load handling program (compliance with NUREG-0612), regulatory requirements, industry guidelines, and OEs in support of the 2019 Design Basis Assurance Self-Assessment (DBAI) it was discovered that PPM 10.4.12 (and other relevant load handling procedures) do not clearly describe cranes design requirements. Suggest maintenance to enhance relevant heavy load handling procedures (including PPM 10.4.12) to clearly state the cranes design requirements. See EDMS for additional details. <I> **** Actions Taken **** Discussed issue(s) with Supervisor and Self-assessment team lead and initiated the CR.
389823 | CR | 20190207 |  | 3 | Work Order Finished but Instructions not signed off in eWP |  |  |  | N | YES | <D> **** Detailed Description **** During review of WO 02138234-08, "COND-V-119C Start-Up to Equalize Valve Pressure", it was noticed that the Work Instructions document in Dataglance has no steps signed off. This is contrary to SWP-PRO-01 expectations for Work Instructions. The WO Task was taken to Finish status on 1/23/19 by Operations. It is possible that the work instructions were perfomed and signed off using a Hard Copy, but that hard copy has not been located. All tasks on the WO are at Finished status, and the valve is in service. This is a documentation issue only. <I> **** Actions Taken **** Notified the AOM Ops Crew Manager. Attempted to locate the hard copy if it exists. It has not been turned in to the Ops Coordinator as would be the typical routing process for a hard copy. Recommend Severity 3 to Operations Crew AOM. <N> Hard copy of signed off work package instructions was located on 2/12/19 and scanned into eWP. . No further action required. | 02-00-COND-V-119C
389824 | CR | 20190207 | CAQ | C | Records not being processed according to ANSI |  |  |  | N | NO | <D> **** Detailed Description **** There are approximately 200 boxes of old records (Contracts and Purchase orders) dating from the 1980's to the 1990's that are being stored in file cabinets in the warehouse of Supply Chain Services. After doing a random selection I have found that the majority of these records are safety related and quality affecting records. These records are not being stored or processed in accordance with ANSI N45 .2-1971 & ANSI N45.2.9-1974 Improper storage of quality affecting records.
389826 | CR | 20190207 | CAQ | C | E 250 Records not following ANSI standards |  |  |  | N | NO | <D> **** Detailed Description **** There are approximately 20 boxes of Old Contract E-250 records (Purchase Orders and other Receiving documents) that are for quality affecting material. The records are being stored in file cabinets in the warehouse of Supply Chain Services.. These records are not being stored or processed in accordance with ANSI N45.2-1971 & ANSI N45 .2.9-1974 Improper storage of quality affecting records. <I> **** Actions Taken **** There has been an Indexing Guideline created for these records and are being done as time allows <N> E-250 FILES HAVE BEEN MOVED TO VAULT IN 183.
389827 | CR | 20190207 | CAQ | C | Records being created with no way to process |  |  |  | N | NO | <D> **** Detailed Description **** There are X-Type records (receipts, receivers, return receipts etc.) that are being created and stored with no process in place for handling these records. Some of these are for quality affecting and safety related materials. These records are not being stored or processed in accordance with ANSI N45.2-1971 & ANSI N45.2.9-1974 Improper storage of quality affecting records. <I> **** Actions Taken **** IDENTIFIED. There needs to be a Records Indexing guideline and procedure created to process these records. <N> As acting SCS services manager I agree the issues identified and actions taken satisfy and correct the issue. AHILL 04/10/2019
389828 | CR | 20190207 |  | 3 | Additional racking device adapter needed |  |  |  | N | NO | <D> **** Detailed Description **** Operations attempted to rack in the grounding device for the 4160V Y bus in E-CB-S/1 per step 5.1.7 of SOP-ELEC -230KV-OPS but was unsuccessful due to the racking device adapter being too short to rack the breaker in. Requesting engineering investigate and procure the appropriate sized adapter to allow the remote racking device tool to be used for installation and removal of grounding devices. <I> **** Actions Taken **** Notified PSRO.
389829 | CR | 20190207 |  | 3 | Method needed to update SOP-ELEC-AC-LU for CRA-42-8B10B. |  |  |  | N | NO | <D> **** Detailed Description **** Could not find an AR assignment that will update SOP-ELEC -AC-LU to include CRA-42-8B10B as the new power supply for CRA-FN-3C. <I> **** Actions Taken **** Wrote CR.
389831 | CR | 20190207 | CAQ | C | (QA) QC Rejected Inspection: MCCB Fuse Discrepancy |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Prior to installation, control fuses (CID 70010612) for MCCB E-DISC-3D1B were rejected by Quality Control during bench test activities per WOT 02121688-02 due to voltage rating discrepancies. Issue Ticket and Acceptance Tag contain different AC voltage ratings, and a different DC voltage rating is shown on EC 14852 than what is listed on both the Issue Ticket and Acceptance Tag. See EDMS for Issue Ticket, Acceptance Tag and EC 14852 rev 002 pg. 048. . Issue Ticket 14430200 lists 600VAC. The Acceptance Tag for CID 70010612 lists 500VAC. . EC 14852 rev 002 pg. 048 lists 125VDC for CID 70010612. Both the Acceptance Tag and Issue Ticket list 500VDC. . . <I> **** Actions Taken **** Notified Quality Services Supervisor, Project Planner, and MCCB Coordinator. <N> Williams Plant Services.
389832 | CR | 20190207 |  | 4 | CW-FN-17 tripped on vibrations | N | N |  | N | YES | <D> **** Detailed Description **** CW-FN-17 tripped on vibrations. CW-CT-1C stairwell is unaccessable currently and the uncovered stairwell is reported to be very icy. Vibes not reset yet. <I> **** Actions Taken **** Wrote CR. EO reset the overloads with no success. | 02-00-CW-FN-17
389833 | CR | 20190207 |  | 4 | HSSF-CAB-CHEM/LAB shows Hydrogen Tank Level Low |  |  |  | N | NO | <D> **** Detailed Description **** Received annunciator alarm for the Hydrogen Storage Supply Facility (HSSF) HT-PAL150-PRES STAT-LOW. This indicates Hydrogen Tank Level low @ HSSF. <I> **** Actions Taken **** Per CI-14.4 contacted CRS and wrote CR. This is a Hydrogen Tank Pressure Transmitter alarm. This is the alarm that comes in when the truck needs to be ordered. This is a tele-tank call, and Chemistry backs it up. It is procedurally driven to write the CR for documenting purposes. No repair work required per Chemistry Operations Supervisor.
389834 | CR | 20190207 | CAQ | D | Rod Accumulator Trouble alarm on CRD-HCU-4259. | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble alarm on CRD-HCU-4259 due to water. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-HCU-4259
389837 | CR | 20190208 |  | 4 | OPDS alarms locked in | N | N |  | N | YES | <D> **** Detailed Description **** Following restoration of TR-S, the OPDS for 230KV locked in along with the 230KV CT trouble alarm (4.800.C3 1-7, 2-7, 3-7). While PMTing the TR-S, the alarms did not clear when placing a load (SM-1,2,3) on the TR-S. <I> **** Actions Taken **** ARP actions taken and alarms acknowledged locally but didn't clear. <N> **** Equipment Description **** xfmr yard. | 02-00-E-TR-S
389839 | CR | 20190208 |  | 3 | Efficiency Reform for Pre/Post Shielding Work Packages |  |  |  | N | NO | <D> **** Detailed Description **** See Attached EDMS Doc. <I> **** Actions Taken **** Notified Supervision
389840 | CR | 20190208 | CAQ | D | Recommend evaluating E-TR-B oil addition |  |  |  | N | YES | <D> **** Detailed Description **** In light of the recent startup transformer oil level issue I recommend that we evaluate adding oil to the backup transformer during the upcoming 2/25/19 outage (WO 02131360). Per the OPS4 rounds oil level is steady at ~.25 of the 0 to 1 scale but this may be an opportunity to add and then not have to do it during R24. | 02-00-E-TR-B
389841 | CR | 20190208 | CAQ | D | E-V-TRB/OCB/TK/DRAIN frozen | Y | N |  | N | YES | <D> **** Detailed Description **** E-V-TRB/OCB/TK/DRAIN frozen. This is performed daily on OPS-4 tour. This does happen every winter but due to extreme cold weather there is a potential for the moisture we drain out freezing and expanding to cause damage to this valve. <I> **** Actions Taken **** Wrotw this CR and informed supervision <N> **** Equipment Description **** E-V-TRB/OCB/TK/DRAIN on TRB
389842 | CR | 20190208 |  | 4 | COND-V-44H difficult to operate and is stuck closed | N | N |  | N | YES | <D> **** Detailed Description **** COND-V-44H difficult to operate and is stuck closed. This is a condensate valve in the service box H on the west side of the fuel pool. The valve was not able to be opened due to more likely infrequency of operation and maintenance. <I> **** Actions Taken **** Wrote this CR/WR and contacted supervision | 02-00-COND-V-44H
389843 | CR | 20190208 |  | 3 | (NRC) Recommend aligning transformer parameter monitoring |  |  |  | N | NO | <D> **** Detailed Description **** The NRC has questioned the differences in monitoring E-TR-S and E-TR-B oil levels relative to the level gauge markings, engineering monitoring, and the operator rounds. The level meter faces for both transformers have a HI, a LO, and 25C level markings. The PPM 3.1.10 OPS4 rounds have Min: 0 and Max: 1 with the equipment operators logging oil level as a fraction between MIN and MAX. Engineering refers to level relative to the normal 25C mark. Recommend enhancing the OPS4 rounds to reflect the markings on the level instruments for both transformers.
389845 | CR | 20190208 |  | 4 | Steam leak in WOA enclosure needs repair | N | N |  | N | YES | <D> **** Detailed Description **** Operations personnel isolated WOA-HC-1/K to isolate an ongoing steam leak. Clearance L-WOA-HC-1/K is hanging to support repair. Request maintenance reepair leaking steam supply coil. <I> **** Actions Taken **** Notified SM. <N> **** Equipment Description **** WOA-HC-1/K RW 487 | 02-00-WOA-HC-1
389848 | CR | 20190208 |  | 4 | Steam leak WOA-HC-1/N and WOA-HC-1/P | N | N |  | N | YES | <D> **** Detailed Description **** Operations isolated signficant steam leaks from WOA-HC-1/N and 1/P to mitigate the amount of water on the floor on RW 487. The water is a major housekeeping issue requiring laborers to mop and vacuum up water six times per shift to prevent water overflowing in the c-zone in the hot machine shop. Water on the back side of the WOA enclosure is several inches deep. This needs to be addressed to prevent the inadvertent spread of contamination and the excessive burden required to keep up with the amount of leaking water. With these two leaks isolated, there are three heating coils currently in service. <I> **** Actions Taken **** Discussed with SM. Isolated leaks and generated local clearances. <N> **** Equipment Description **** RW 487 | 02-00-WOA-HC-1
389891 | CR | 20190209 |  | 4 | RB 606 IPM Room Fluorescent Light Bulbs burning out | N | N |  | N | NO | <D> **** Detailed Description **** The light in the RB 606 room that the IPM is located in has low light from the bulb burning out. There is a lot of scheduled work up on the RB 606 and may require attention sooner thatn later. The frisker is also located in this room which will require heavy use. The room is not dark but dimmly light. <I> **** Actions Taken **** Initiated this CR Placed information in HP Logbook and Turnover for personnel to be aware of the condition. <N> **** Equipment Description **** RB 606 IPM Room
389892 | CR | 20190209 |  | 3 | MT-CRA-1 Main Hoist does not respond to Radio Controller | N | N |  | N | YES | <D> **** Detailed Description **** During functional testing of the turbine building bridge crane, the main hoist did not respond to radio controller command inputs. The main hoist DID respond to control commands from the operator cab. The aux' hoist, trolley and bridge motions DO respond to both radio and cab commands as expected. <I> **** Actions Taken **** OEM technician contacted his engineering staff and is continuing to troubleshoot the issue now. <N> **** Equipment Description **** T -555- - -A3/13.0- Per AR author, loose wire has been located and tightened. No further actions required. | 02-00-MT-CRA-1
389893 | CR | 20190209 |  | 3 | MT-CRA-1 Radio Controller E-Stop function not as expected | N | N |  | N | YES | <D> **** Detailed Description **** During functional testing of the turbine bridge crane it was noted that actuating the emergency stop button on the radio controller did not de-power the crane as expected. The e-stop de-powered the radio transmitter only. The expected result of actuating the e -stop is the removal of power from both the transmitter and the crane. <I> **** Actions Taken **** OEM tech is working with his engineering staff to develop troubleshooting plan for this condition. <N> **** Equipment Description **** T -555- - -A3/13.0- Work request generated and cross referenced. No further actions required. | 02-00-MT-CRA-1
389894 | CR | 20190209 |  | 3 | MT-CRA-1 Bridge brake does not engage under remote control | N | N |  | N | YES | <D> **** Detailed Description **** During functional testing the bridge brake does NOT engage when the radio controller travel command is released as expected. This results in the bridge drifting forward and requires the input of a reverse command to stop the bridge motion. The bridge brake DOES actuate using the foot hydraulic control in the operator cab. <I> **** Actions Taken **** OEM tech has contacted his engineering staff for assistance in troubleshooting this condition. <N> Work request generated and crossed referenced. No further actions required. | 02-00-MT-CRA-1
389895 | CR | 20190209 |  | 4 | Yakima Lunch Room "Almost Boiling" Water Faucet Malfunction | N | N |  | N | NO | <D> **** Detailed Description **** The â€œalmost boilingâ€ water faucet in the Yakima 441â€™ lunchroom is sputtering and splashing â€œalmost boilingâ€ water when turned on. This is creating a potential scalding scenario as a small amount of â€œalmost boilingâ€ water will splash up on the individualâ€™s hand as he/she turns the â€œalmost boilingâ€ water faucet off. <I> **** Actions Taken **** Placed Caution Sign Next To Sink and Initiated WR. <N> **** Equipment Description **** Yakima Building 441' Lunchroom
389896 | CR | 20190209 |  | 3 | Apocalyptic Driving Conditions For Essential Personnel |  |  |  | N | NO | <D> **** Detailed Description **** Essential personnel driving to and from the plant this evening were subjected to very hazardous, downright dangerous driving conditions. Heavy snowfall, high winds and the severe lack of plowing on highway 4 created what could be described as an Apocalyptic scene to the point where cars were driving South in the North lanes of the highway because the North lanes were suffering less snow drifting than the South. This is obviously a very dangerous scenario as this introduced the potential for head on collisions that are normally non-existent. Although today is Saturday and Hanford is off, there are still plenty of essential personnel that are required to drive to work and relieve outgoing essential personnel. Not only does this affect essential personnel, it could potentially affect ERO activation and Hanford Fire response for medical and/or fire emergencies. At a minimum, Highway 4 should remain plowed up to the access road whether Hanford is off (weekend/nights), cancelled or delayed due to severe weather. Essential personnel should not have to risk their lives driving to work to relieve their coworkers. It is the responsibility of Energy Northwest and the DOE (Hanford) to ensure everything in their power is being done to ensure the safe arrival of their employees at work and at home. This should include making sure Hanford plows Highway 4 at least during the hours that essential personnel are traveling to and from the plant. <I> **** Actions Taken **** Contacted Supervisor and was asked to please initiate CR to document the lack of plowing of Highway 4. <N> This issue was discussed with VP-OPS & DOE and any other departments that snow plow route 4. No further actions.
389897 | CR | 20190209 |  | 4 | Yakima Building Exterior Entry Door Damaged | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The exterior entry door to the Yakima building is damaged to the point that prevents its closure. This is causing snow to blow into the corridor. No door identification number could be found. This is the single door entance to the Yakima Building coming into the Primary Access Point (PAP). <I> **** Actions Taken **** Posted interior and exterior Caution signs to warn individuals not to use said door and initiated WR. <N> **** Equipment Description **** Yakima Building Exterior Entry Door (Single Door)
389898 | CR | 20190209 | CAQ | D | Recieved 812.R2.6-2 RW BLDF EXH FLTR B D/P LOW alarm | N | Y |  | N | YES | <D> **** Detailed Description **** Recieved multiple intermittent alarms, local inspection showed nothing immediately abnormal. <I> **** Actions Taken **** Started WEA-FN-1C and stopped WEA-FN-1B per CRS and ARP | 02-00-WEA-HF-1B
389899 | CR | 20190209 | CAQ | D | Received 812.R1.10-2 "DC MCC RM COOLER FLOW LOW" alarm | Y | N |  | N | YES | <D> **** Detailed Description **** SW-FS-41 indicated 17.5 gpm <I> **** Actions Taken **** Adjusted flow to 20-25 gpm with OSP-SW-C101 | 02-00-RRA-CC-12
389901 | CR | 20190210 |  | 3 | Enhancement to SOP-FO-OPS |  |  |  | N | NO | <D> **** Detailed Description **** See EDMS for enhancement to SOP-FO-OPS. <I> **** Actions Taken **** CR initiated
389902 | CR | 20190210 |  | 4 | Security Van Door Hinge Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** During extreme weather conditions, the driver door on Security Van 72434C was blown open. This resulted in the hinge being bent. The door is able to be closed and there were no injuries. <I> **** Actions Taken **** Security Supervision notified. Intiated CR/WR. <N> **** Equipment Description **** Security van 72434C
389903 | CR | 20190210 | CAQ | C | Broken Screw During Surveillance | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of WO#02107366-01 ISP-RWCU-Q402 CFT restoration (step 7.2.14) , Test 2 Terminal 3 copper screw on the slide link broke while being tightened. <I> **** Actions Taken **** Notified supervisor and operations. Wrote this CR. <N> This CR was re-opened and assigned to AR-EFIN, severity C, by mutual agreement between Maintenance and Engineering. . Notes transferred from Note Type â€œSâ€ Wires were moved from test 2 terminal 3 to test terminal 2 by WR 29147070 with concurrence with engineering. ISP-RWCU -Q402 was then completed. . This needs to be followed up with by engineering to ensure EC or TM is in place to track this. . Additional WR 29147088 generated to replace sliding link <S> Wires were moved from test 2 terminal 3 to test terminal 2 by WR 29147070 with concurrence with engineerinrg. ISP -RWCU-Q402 was then completed. . . This needs to be followed up with by engineering to ensure EC or TM is in place to track this. . Additional WR 29147088 generated to replace sliding link | 02-00-LD-FS-15
389905 | CR | 20190210 |  | 4 | Caution Light Lit on E-AY-TR/M3 | N | N |  | N | YES | <D> **** Detailed Description **** Caution light on M3 Transformer Gas Analyzer was lit during rounds on 2/9/2019 7:53 AM. <I> **** Actions Taken **** Initiated CR/WR <N> **** Equipment Description **** Transformer Yard | 02-00-E-AY-TR/M3
389906 | CR | 20190210 |  | 3 | CIA N2 bottles below minimum availible |  |  |  | N | YES | <D> **** Detailed Description **** While performing Sunday rounds it was noted that the number of Yellow and Black N2 bottles are at or below minimum. We have 8 yellow bottle availible while the minimum is 10, and we have one black bottle which is the minimum. <I> **** Actions Taken **** inform CRS and initate CR/WR, send Chadd an email with the CR/WR#. <N> **** Equipment Description **** RX Bldg truck bay, CIA N2 bottles.
389909 | CR | 20190210 | CAQ | D | DG2 & DG3 roof seals leaking. | Y | N |  | N | YES | <C> CR reopened to cross reference additional WP 02054737, marked completion required box, then taken back to complete <D> **** Detailed Description **** Found it lightly raining from roof plug in DG2, water was falling to ground and not on equipment. Water on DG3 roof plug is only seeping through at this point and not dripping from roof. Currently there is large accumulations of snow outside. <I> **** Actions Taken **** Initiated AR, informed MCR. | 02-00-DG-GEN-DG2,02-00-HPCS-GEN-DG3
389910 | CR | 20190210 |  | 4 | HHW-V-62 leaking | N | N |  | N | YES | <D> **** Detailed Description **** HHW-V-62 is leaking about 6 drops per minute. Recommend repair/replace as necessary when SHHW system shut down in the spring. | 02-00-HHW-V-62
389913 | CR | 20190211 | CAQ | D | Need Snow Removal for Building 62 Fire Brigade Area | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing the Monthly Fire Brigade Package for Building 62, I noted that Snow Removal is needed for this area. Deep drifting snow makes it difficult to traverse the area South of Building 62 and to the Emergency Response Vehicle. This would hamper the Fire Brigade, in an actual Emergency. <I> **** Actions Taken **** Notified HP Lead Technician and PSRO. Initiate CR/WR ESOMS Log Entry. Possibly Incorporate Snow Removal for the Various Outside Fire Brigade / B5B Areas. <N> **** Equipment Description **** Building 62
389914 | CR | 20190211 |  | 3 | (QA) CR 378892 Missing Effectiveness Review |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Condition Report (CR) 378892 â€œConduct Common Cause Analysis of Maint. Human Perf. Eventsâ€ is missing an effectiveness review, contrary to requirements in SWP-CAP -01 â€œCorrective Action Programâ€ (CAP). An effectiveness review provides assurance that the corrective actions will have the desired effect. (See EDMS for full details) <I> **** Actions Taken **** This was identified as a Deficiency during the Maintenance Programs Audit, AU-MN-19. Informed Quality and Maintenance, recommend assignment to Maintenance.
389915 | CR | 20190211 | CAQ | D | Rod Accumulator Trouble Alarm for CRD-HCU-1807 | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-1807 due to high accumulator water level. <I> **** Actions Taken **** Drained water and cleared alarm. | 02-00-CRD-HCU-1807
389917 | CR | 20190211 |  | 3 | (QA) Incomplete or Missing WO PPRCLs |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) 7 of 18 Work Orders (WO) packages were either missing or had incomplete required Planner/Peer Review Checklists (PPRCL) as required by MI-1.22. Failure to receive peer reviews increases the risk of errors remaining in the work package during implementation. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Maintenance Programs Audit, AU-MN-19. Informed Quality and Maintenance, recommend assignment to Maintenance.
389918 | CR | 20190211 |  | 3 | (QA) IER 17-9 Implementation Requires Attention |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Some actions committed in response to IER L2-17-9 â€œWeaknesses in Maintenance Technical Fundamental Skills Adversely Affecting Plant Operationsâ€ are not being implemented effectively. Specifically, changes made to procedures/briefing forms to drive focus on maintenance technical fundamentals to address the concerns from IER L2-17-9, are not understood by some workers and supervisors and they are not being covered as intended. The lack of proper implementation of the lessons learned could place the station at risk for similar errors and increased risk of exposure to externally identified issues during the plant evaluation. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Maintenance Programs Audit, AU-MN-19. Informed Quality and Maintenance, recommend assignment to Maintenance.
389919 | CR | 20190211 |  | 3 | (QA) IER 17-9 Actions Not Performed As Directed |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Two IER 17-9 â€œWeaknesses in Maintenance Technical Fundamental Skills Adversely Affecting Plant Operationsâ€ actions to revise MI-1.8, Conduct of Maintenance, were not performed as directed in the Action Request (AR) Description and the changes made do not provide direction to drive the desired actions. The two actions, which resulted from the IER Response dated 3/27/18, were initiated to update the Work Implementation section of MI -1.8 to provide definitions and expectations for workers and supervisors to apply and reinforce maintenance technical fundamentals at briefs and in the field. While the wording from the IER response was properly transcribed into AR actions, the actions taken did not fully align with those directed. The lack of proper incorporation of the changes may have contributed to issues observed during the audit regarding implementation at briefings and the field. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Maintenance Programs Audit, AU-MN-19. Informed Quality and Maintenance, recommend assignment to Maintenance.
389920 | CR | 20190211 | CAQ | C | (QA) Documentation of Sealants Used Missing in 2 WOs | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) Two of six work orders (WO) reviewed were found to have incomplete documentation for the type of thread sealant used for the mechanical connections. In one case, the WO step provided an example of a sealant that could be used and in the second case, there was no direction or examples and no other documentation for what was used. Failure to document items installed or used could lead to traceability concerns and/or difficulty in understanding the work history of a component at a later date. Separate from the issues documented here, the audit team provided a recommendation to provide more clear guidance in work orders and procedures rather than simply stating to â€œuse an approved sealantâ€. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Maintenance Programs Audit, AU-MN-19. Informed Quality and Maintenance, recommend assignment to Maintenance.
389921 | CR | 20190211 | CAQ | C | (QA) Five WOs Missing Asset Suite M&TE Records |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Five instances were identified where Measure and Test Equipment (M&TE) was documented as used in the Work Order (WO) and Usage Card but not recorded in Asset Suite in the â€œRecord Calibration Informationâ€ as required by MI-3.6.4. This is a procedure compliance issue with reduce risk as no instances were identified with omissions on the M&TE usage card, which is the primary means to track and evaluate out of tolerance M&TE. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Maintenance Programs Audit, AU-MN-19. Informed Quality and Maintenance, recommend assignment to Maintenance.
389922 | CR | 20190211 | CAQ | C | (QA) PMRQ 26037-02 Not Correctly Categorized as ESSN |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Preventive Maintenance Requirement (PMRQ) 26037-02 is not correctly categorized as Essential (ESSN), contrary to PPM 1.5.13 â€œPreventive Maintenance Optimization Living Programâ€. The potential consequence is the regulatory exposure of not meeting requirements within the Operational Quality Assurance Program Description (OQAPD-01) to perform the PMs on the spare Diesel Exhaust Air (DEA) fans in accordance with the manufacturerâ€™s recommendations. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Maintenance Programs Audit, AU-MN-19. Informed Quality, Engineering and Maintenance, recommend assignment to System Engineering.
389923 | CR | 20190211 | CAQ | C | (QA) Incomplete PM on Spare DEA Fan |  |  |  | Y | YES | <D> **** Detailed Description **** (QA) A Work Order did not complete required lubrication on a Spare Diesel Exhaust Air (DEA) fan and did not take actions to ensure the incomplete Preventive Maintenance Scope was addressed as required by SWP-PRO-01. This caused an Essential PM on a critical component to not be performed within 125% of the specified interval. Failure to meet preventive maintenance requirements can degrade Quality Class 1 parts and not meet regulatory requirements. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Maintenance Programs Audit, AU-MN-19. Informed Quality and Maintenance, recommend assignment to Maintenance. <N> **** Equipment Description **** Spare DEA Fan in Warehouse
389924 | CR | 20190211 | CAQ | C | (QA) PMRQ Frequency Error for Spare DEA Fan |  |  |  | Y | YES | <D> **** Detailed Description **** (QA) A Preventive Maintenance Requirement (PMRQ) to rotate the safety related Spare DEA Fan rotor created in 2014 was incorrectly established with a 6 month frequency instead of the specified 3-month frequency. The approved SMS-AR and Manufacturerâ€™s Recommendations specified to rotate the Spare DEA Fan rotor every 3 months. The actual consequence is this spare fan was rotated at twice the specified interval for 4 years as required by the Manufacturerâ€™s Recommendations and the Operational Quality Assurance Program Description (OQAPD). (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Maintenance Programs Audit, AU-MN-19. Informed Quality and Maintenance, recommend assignment to Maintenance. <N> **** Equipment Description **** Spare DEA Fan in Warehouse
389925 | CR | 20190211 |  | 3 | (QA) DNP Actions Not IAW with PPM 1.5.13 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) 2017 Delivering The Nuclear Promise (DNP) Actions changed for 22 Preventive Maintenance (PM) frequencies without using a Scheduled Maintenance System Action Request (SMS-AR) or a PM Change Request Form (PMCR) and hundreds of component criticality changes without a PMCR contrary to PPM 1.5.13 â€œPreventive Maintenance Optimization Living Programâ€. This was a failure to enter the correct process with no known consequence. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Maintenance Programs Audit, AU-MN-19. Informed Quality and Maintenance, recommend assignment to Maintenance.
389926 | CR | 20190211 |  | 3 | Legacy issue of WO titles with (SHELL) |  |  |  | N | NO | <D> **** Detailed Description **** No Impact to Plant. Several PMs still maintain the word (SHELL) in the title to provide the insight that this is a first time PM. There has been several occasions where these jobs come through and upon review these activites or the PM scope has been performed previously. <I> **** Actions Taken **** Generated CR. Recommend assignment to planning group to add some type of review as part of work order planning (if not there currently, either in MI-1.22 or MI-1.22A) to review if the title has the word (SHELL) in it to review if it is truly a first time occurrence. If it is not, then update the model and or the associated PM work order title to remove the (SHELL) in the title. This should either be a case by case effort as each job is planned, or a once all with a query made for all work orders with SHELL in the title and perform a proper review to get a new baseline so we know which ones have not been performed. Reviewed MI-1.22 and MI-1.2 2A for words such as "Shell", "First time" and "Previously" in which the words were not found.
389927 | CR | 20190211 |  | 3 | Evaluate scaffolding improvement for transformer inspection | N | N |  | N | NO | <D> **** Detailed Description **** Monthly transformer yard inspection (model WO 02001147-01) requires oil leakage checks in step 4.2. Access to these valves for checks is difficult with existing scaffolding, and unsafe during adverse weather such as the recent snowy/icy conditions. Request we evaluate modifying existing scaffolding or installing additional scaffolding which would facilitate the safer operation/access to these drain valves. <I> **** Actions Taken **** Discussed issue with CRS and assigned system engineer. <N> Modification of existing PPM 10.2.53 scaffolding should require coordination between scaffolders and Engineering (Civil and Fire Protection).
389928 | CR | 20190211 |  | 4 | January Mech Dose overage - CR Trend |  |  |  | N | NO | <D> **** Detailed Description **** No impact to Plant. Mechanics received 703 mrem over a an original estimate of 442 mrem for January 2019. RWCU-RV -262A estimate was initially low, dose originally esimated at 68 mrem, then re-estimated for 85 mrem at day of implementation, in which the mechanics took 101 mrem. RWCU-V-213A recieved 40 mrem as emergent as was not originally part of the monthly estimate. Other "Emergent Dose" was the driver for 100 mrem overage (accounting for the ~ 60 mrem discussed above for RWCU-RV-262A and RWCU-V -213A). <I> **** Actions Taken **** Generated CR for trending purposes per departmen CIC.
389929 | CR | 20190211 |  | 3 | Bus 61/62 MCC OL TRIP alarm remains in with CB closed. | N | N |  | N | YES | <D> **** Detailed Description **** WO 02084635 E-CB-61/6M: DETAILED VISUAL INSPECTION OF SWITCHGEAR BREAKER. Following the completion of WO 02084635 E-CB-61/6M was racked in and local resets were depressed and the breaker was closed in the alarm on H13-P800 drop 6/6 (61/62 MCC OL TRIP) stayed locked in. Currently the (61/62 MCC OL TRIP) alarm has come in and cleared several times with on actions. <I> **** Actions Taken **** AR / WR 00388513 / 29146423 worked and taken to complete. condition continues. | 02-00-E-CB-61/6M
389930 | CR | 20190211 |  | 3 | RCC pH out-of-spec high | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During weekly sampling of RCC, the pH result was 8.2. The acceptable range is 5.5-8.0, per Table 6.3.9 of SWP-CHE-02. The system was re-sampled, yielding the same result. Per SWP-CHE-02, step 6.3.3, statement a., the RCC system is now in Action Level 1, requiring resolution within 90 days. An increase in conductivity was also noted and verified with the second sample, although it remains within the specified acceptable range. <I> **** Actions Taken **** Notified Chemistry Supervision and CRS, and intiated CR. <N> WR needed?
389931 | CR | 20190211 |  | 4 | RW Elevator not working properly | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-4 (RW elevator) is out of service due to the south doors making a slight grinding noise and getting stuck open. Computer resets did not fix the problem. The elevator was last located on the 437 but the door issue was seen on the 467 and 487 as well. <I> **** Actions Taken **** Took it out of service | 02-00-MT-ELEV-4
389932 | CR | 20190211 | CAQ | D | E-BU-T441/4 failed quarterly inspection | N | N |  | N | YES | <D> **** Detailed Description **** The status led on this unit is not lit. It appears to have a bad charger. <I> **** Actions Taken **** Post fire impairment and portable lantern <N> **** Equipment Description **** T441 B.4/16.0 | 02-00-E-BU-T441/4
389933 | CR | 20190211 | CAQ | D | E-BU-T441/10 failed quarterly inspection | N | N |  | N | YES | <D> **** Detailed Description **** This unit is displaying a better fault. <I> **** Actions Taken **** Post fire impairment permit and portable lantern <N> **** Equipment Description **** T441 F/12 | 02-00-E-BU-T441/10
389934 | CR | 20190211 | CAQ | D | Malfunction IDS 24 25 | N | N |  | N | YES | <D> **** Detailed Description **** IDS 24 25 is not functioning as designed. <I> **** Actions Taken **** Compensatory measure initiated. CR/WR generated. <N> Compensatory measures have been initiated on IDS malfunction zones 24/25 | 02-00-SEC-IDS-EVAL/24/25
389936 | CR | 20190212 | CAQ | D | Security IDS 7 8 Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** Security IDS 7 8 Malfunction. Top wire detached from pin in zone 8 on pole 48. Not functioning as designed. Contact security at 2185. <I> **** Actions Taken **** Compensatory measures. CR/WR generated <N> Compensatory measures have been established for malfunction zones 7/8. | 02-00-SEC-IDS-EVAL/7/8
389937 | CR | 20190212 | CAQ | D | DOOR D-104 Door latch | N | N |  | N | YES | <D> **** Detailed Description **** DOOR D-104 door latch not working as designed. <I> **** Actions Taken **** Generated CR/WR for maintenance support. | 02-00-D-DOOR-D104
389943 | CR | 20190212 |  | 4 | CW-FN-34 Will Not Start | N | N |  | N | YES | <D> **** Detailed Description **** During de-icing operation per SOP-CW-OPS CW-FN-34 was started (red light came on briefly) and it immediately tripped off. Ops 4 reset the electrical Overloads but CW -FN-34 still would not start. Ops 4 attempted to reset the vibration trip on CW-FN-34 but was unable to open the door to the covered stairwell of CW-CT-2C due to it being frozen shut. The open stairwell was deemed too hazardous to use. | 02-00-CW-FN-34
389944 | CR | 20190212 |  | 3 | OI-41 update to reflect MSLRM is now in LCS |  |  |  | N | NO | <D> **** Detailed Description **** The main steam line radiation monitor (MSLRM) were recently added to the LCS. OI-41 needs to be updated to reflect this. <I> **** Actions Taken **** Discussed with Shift Manager
389945 | CR | 20190212 |  | 4 | WOA-FN-4 broken belts | N | N |  | N | YES | <D> **** Detailed Description **** WOA-FN-4 filter was found with no DP across the filter and after looking through the sight window the motor was found spinning with two broken belts; thus disconnected from the fan. Need to replace belts. <I> **** Actions Taken **** Taking action to get the motor turned off. Informed chemistry lab personel. | 02-00-WOA-FN-4
389946 | CR | 20190212 |  | 3 | R24 Turbine Walkdown Indicator is red |  |  |  | N | NO | <D> **** Detailed Description **** The R24 Turbine work order walkdown indicator went red. The indicator monitors 63 total discipline K tasks or less than 1% (63/7272 Iis 0.86%) of the total R24 original scope. Currently, 56 tasks are status READY. The 7 remaining are planned (status 30) and in routing for reviews. . Two actions are required: 1. A recovery plan assigned to the Turbine Project 2. Assignment to Outage Management to evaluate the validity of tracking less than 1% of outage tasks on an indiviidual perfomrance indicator <I> **** Actions Taken **** Validated all tasks (63) are planned and confirmed the 7 remaining tasks are in routing for approvals (RO/SRO)
389947 | CR | 20190212 |  | 3 | OSP-HPCS/IST-Q701 section 7.3.50 & 51 change needed |  |  |  | N | NO | <D> **** Detailed Description **** OSP-HPCS/IST-Q701 section 7.3.50 & 51 sequence change needed. If performing the quarterly in modes 4 or 5 and HPCS-V-2 full flow is not needed, there is no issue. However, if the full flow test is required (quarterly every shutdown), section 7.3.50 would be N/Ad and 7.3.51 performed. Doing this causes the section to stroke time HPCS-V-4 to be N/Ad also,. This valve must also be stroked quarterly. Step 7.3.51 needs to come before 7.3.50 as 7.3.51 needs the pump running and 7.4.50 needs the pump secured and fuses pulled. Also need to change step 7.3.50 title to just say LT 650 psig as we will always be required to do this section, regardless of if HPCS-V-2 flow test is required, <I> **** Actions Taken **** No impact to HPCS operability. AR 363471 established full flow PM test in July 2017 following EC for HPCS-V-11 removal from service. This test requirement has not been performed since then so there has been no missed surveillance on HPCS-V-4. Needs fixed for future forced outage work.
389948 | CR | 20190212 |  | 4 | Step in PM WO task marked N/A |  |  |  | N | YES | <D> **** Detailed Description **** PM WO Task 02130919-01 is for Transformer Inspection by Operatios. Step 4.2 states to check for oil leakage at the "dog house" for the 3 main transformers. THis step was marked N/A with a note stating "not performed due to adverse weather conditions". This step 4.2 is a new step/scope that was recently added to the PM scope. This CR is to document the step being marked N/A per SWP-PRO-01. THe Main transformers are marked as "Critical" in Asset Suite on D031 panel. <I> **** Actions Taken **** Reviewed finished PM task. Notified Transformer system engineer. Initiated CR. <N> See email from Sys Eng in EDMS Sys Eng concurs with N/A for this performance. | 02-00-E-TR-M1,02-00-E-TR-M2,02-00-E-TR-M3
389949 | CR | 20190212 |  | 3 | Excessive Snow on Willamette (Buillding 64) Roof | N | N |  | N | YES | <D> **** Detailed Description **** Looking out the window of the Deschutes building, it appears that there is two to three feet of snow on the Willamette (Buillding 64) Roof. Consider removing the snow before more wet snow/rain is forecasted for later this week. Weight per cubic foot of saturated snow is 20 lbs per cubic foot, so for 2 feet of snow that would equal 40 pounds per square foot. The building design for snow loading recommends that structures be designed for a minimum uniform roof snow load of 25 psf. From this information, it appears that if the snow gets wet when wintry rain/snow mix is predicted later this week that the roof may be loaded beyond its design snow load. <I> **** Actions Taken **** Notified Shift Manager and Facilities. Generated CR. Discussed with Supervisor. Showed the condition to the Safety Representative. <N> **** Equipment Description **** Willamette (Buillding 64) Roof
389950 | CR | 20190212 |  | 4 | PA gate 26 for vehicle gate | N | N |  | N | YES | <D> **** Detailed Description **** The inner most motorized gate for the vehicle trap (gate 26) needs maintenace. Their is constant tone coming from the gear box. Contact security at ext 2185 for further details. <I> **** Actions Taken **** Security notification made, CR/WR generated <N> **** Equipment Description **** Inner most vehicle trap gate (gate 26)
389951 | CR | 20190212 | CAQ | D | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0067232 Fluke Gauge- model 700G27 300psig found OOT and needs repair. EFIN Eval: Usages #1 & #2 Corrected value still within limits. Usage #3 Range Used Not OOT. No Plant Impact. DEF #6791A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
389952 | CR | 20190212 | CAQ | D | M&TE Suspended/ Lost |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0064313 Fluke True RMS Mulitmeter- model 187 Can't locate. Suspended/Lost. EFIN wrote CR #389758 to Re-perform WO #02084670-01 & WO #02135436-01. All other usages- No Impact. DEF #6792A written. See EDMS for further Eval. <I> **** Actions Taken **** None Trending purposes only.
389953 | CR | 20190212 |  | 3 | NRC question on snow removal priorities | Y | Y |  | N | NO | <D> **** Detailed Description **** A question was raised concering access to FLEX equipment, snow accumulation on DG inlets, and DG flood outlet drains. These are housekeeping issues and do not impact equipment operability. However should be prioritized for snow removal to minimize the station's risk profile. <I> **** Actions Taken **** Contacted Facilities to remove snow in question
389954 | CR | 20190212 |  | 3 | Changes needed to OUTAGE WO 02116063 |  |  |  | N | NO | <D> **** Detailed Description **** Following a walk down of work to be performed changes were idenetified that need to be made to tasks 01 02 03 04. Attached a copy of needed changes to EDMS <I> **** Actions Taken **** Generated CR
389956 | CR | 20190212 |  | 4 | Records not sibmitted IAW GBP-REC-04 |  |  |  | N | NO | <D> **** Detailed Description **** On 2/12/2019 A record was submitted to Records control without following the records submittal Process for Confidential Records. They were NOT flagged appropriately and were mailed in an Iinteroffice envelope which in Section 4.7.1 of the GBP states that it should be flagged appropriately and hand delivered. <I> **** Actions Taken **** Notified my Supervision. Flagged the documents accordingly and will be notifying the sender via a follow up email with some coaching. This should be assigned to the Maintenance department.
389959 | CR | 20190212 |  | 4 | WO 02107360 Missing Inventory List |  |  |  | N | NO | <D> **** Detailed Description **** Step 4.1 of WO 020107360 could not be performed by the technician because the excel spread sheet inventory list was no longer in the file located on the S drive. <I> **** Actions Taken **** Contacted IS for help in recovering the spread sheet. IS solution center change gear system ticket will track the request. No further action required.
389962 | CR | 20190212 | CAQ | D | CRD-P-1B gearbox oil has elevated foaming present | Y | N |  | N | YES | <D> **** Detailed Description **** The sightglass on the CRD-P-1B speed increasing gearbox shows more foam than normally present. Liquid oil is visible at the lower quarter of the glass. The foam level goes to the upper quarter. The pump is currently in service, gearbox oil pressure is about 30 psig (which is normal). Recommend an oil change. Photo attached in EDMS. | 02-00-CRD-P-1B
389964 | CR | 20190212 |  | 3 | ANII Resources Not Available |  |  |  | Y | NO | <D> **** Detailed Description **** Scheduled work was not able to be performed on Tuesday, 2/12 due to the lack of an ANII inspector with State of Washington inspection certification. The normal ANII inspector is out for personal reasons. Arrangements for an interim inspector by the Energy Northwest Technical Representative were not timely and the impact to the schedule was not recognized until the day of implementation. Work orders affected include 02109743 and 02107616. Recommend SL4 to Quality. <I> **** Actions Taken **** Discussed with the WWM and the affected shops. Notified Quality Manager. Work is being rescheduled when resources can arrive on site to support.
389965 | CR | 20190212 |  | 3 | Revise ABN-TSW |  |  |  | N | NO | <D> **** Detailed Description **** Bases steps 2.1 and 4.2 state â€œThe tripped TSW pump gets another trip signal when the discharge valve reaches 5% open in the closed direction. Thus, if the tripped pump is restarted before the discharge valve reaches the 5% open position, the pump will trip again when the discharge valve reaches 5% open.â€ This is inaccurate as the TSW pump only gets a trip signal when the discharge valve is 5% open and the RMS for the pump is in any position other than auto-after-start. In both of these steps the configuration of the RMS is auto -after-start. I recommend removing this from both bases steps. <I> **** Actions Taken **** None
389966 | CR | 20190212 |  | 3 | Revise 4.800.C5 |  |  |  | N | NO | <D> **** Detailed Description **** Step 2 states â€œcheck control power fuses F5-1/F5-2.â€ These are actually fusible links like the division 1 equivalent (see 4.800.C1 1-3). I recommend modifying this step to read â€œVerify the relay control power links at SM-7 Aux Cabinet are intact. Steps 3, 4 and 5 reference the user to technical specification 3.8.1/3.8.7, 3.8.2/3.8.8 and 3.8.3 respectively. These LCOs would not be directly entered if this circuit is de-energized. These three steps should be replaced with one step stating â€œRefer to Technical Specification 3.3.8.1.â€ This LCO references the mode applicability and the supported LCOs that may need to be entered. <I> **** Actions Taken **** None <N> The write up in the Action Request Description field need to be changed to the write up in the attached EDMS word document.
389967 | CR | 20190212 |  | 3 | Revise 4.800.C1 |  |  |  | N | NO | <D> **** Detailed Description **** Section 1-3 step 2 states â€œVerify Relay Control Power Links at SM-7.â€ I recommend modifying this step to read â€œVerify the relay control power links at the SM-7 Aux Cabinet are intact. Steps 3, 4 and 5 reference the user to technical specification 3.8.1/3.8.7, 3.8.2/3.8.8 and 3.8.3 respectively. These LCOs would not be directly entered if this circuit is de-energized. These three steps should be replaced with one step stating â€œRefer to Technical Specification 3.3.8.1.â€ This LCO references the mode applicability and the supported LCOs that may need to be entered. <I> **** Actions Taken **** None
389968 | CR | 20190212 | CAQ | C | Operations received an alarm on the SW â€˜Bâ€™ system | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of ISP-SW-X305C, operations received an alarm on the SW â€˜Bâ€™ system â€“ H13-P840.A5-8.2. Technicians stopped and discussed with operations the alarm received; alarm received was on the DETERM at approx. step 7.1.8 and then received again on the RETERM at approx.. step 7.7.3. No other alarms were received and operations cleared the alarms â€“ all other testing complete SAT. <I> **** Actions Taken **** Contacted SM, contacted operations, contacted supervision, document in a CR and document in the history portion of the work order. Recommend engineering to evalute if the alarm is expected due to the use of the same power supply per the EWD. <N> **** Equipment Description **** ISP-SW-X305C Appears this alarm is one that can come in when performing the surveillance ISP-SW-X305C. SW-TS-1A and 1C share a common power supply through the supervisory system and since they are not divisionally separated a disturbance when testing can cause the opposite division to alarm. Recommend D Trend . SW - A alarm recieved and NOT B as stated. System Engineer contacted.
389970 | CR | 20190212 |  | 4 | Confidential document posted to Core Business Meeting Site |  |  |  | N | NO | <D> **** Detailed Description **** A document containing confidential business information was posted to the Core Business Meeting SharePoint Site <I> **** Actions Taken **** Deleted the file Notified invovled parties
389971 | CR | 20190212 |  | 3 | ABN-RCC procedure change |  |  |  | N | NO | <D> **** Detailed Description **** ABN-RCC section 4.2 should be reworded to be consistent with the note after the start of section 4.0. Change 4.2 to read "IF a partial loss of RCC cooling capability occurs..." vs. "loss of RCC flow". This will clarify using this section for both loss of flow and loss of cooling like degraded TSW flow. This was identified in cycle 19-1 training.
389974 | CR | 20190212 |  | 4 | MD-V-86 indicates dual on H13-P820 following Cycle MD Valves | N | N |  | N | YES | <D> **** Detailed Description **** MD-V-86 indicates dual on H13-P820 following Cycle MD Valves per WO# 02130912. Computer point for MD-V-86 T513 indicates Closed. MW returned to the initial value following the WO instructions. Please investigate. <I> **** Actions Taken **** Informed CRS/SM. CIM trand added to EDMS Docs showing valve not closed | 02-00-MD-V-86
389977 | CR | 20190213 | CAQ | C | (QA) 2 Spare SR Component PMs Missing Required Elements | N | N |  | Y | YES | <D> **** Detailed Description **** (QA) No Preventive Maintenance (PM) scope exists to rotate the horizontally-stored spare Safety-Related (SR) Low Pressure Core Spray (LPCS) Pump or to megger the spare Safety-Related Diesel Exhaust Air (DEA) Fan Motor, contrary to manufacturerâ€™s recommendations in the Vendor Manual. Two of three spare SR care and storage PMs reviewed by Quality were non-compliant with the Operational Quality Assurance Program Description (OQAPD), which states the station will follow the manufacturerâ€™s recommendations unless an exception is taken with a documented engineering evaluation. Potential consequences for the failure to properly maintain stored SR components are reduced reliability to meet design mission time requirements and increased repair costs. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Finding during the Maintenance Programs Audit, AU-MN-19. Informed Quality, Engineering and Maintenance, recommend assignment to Engineering <N> **** Equipment Description **** Spare LPCS Pump and Spare DEA Fan Motor in warehouse . Cancelled by mistake. Re-opened per request by owned to group.
389978 | CR | 20190213 | CAQ | C | (QA) 2 PM Category â€œESSNâ€ PMRQs Should Be â€œSURVâ€ | N | Y |  | Y | NO | <C> CR Bring Back (CRBB) Maintenance to Bring Back CR, discussion more with Licensing & Engineering. What Group it needs to go to and the Regulatory & MRULE impact. RISK: Medium. CAUSE: Uncertain/Complex. Investigation Template Required. Potential Regulatory & MRULE impact. MRT Change on 02.21.2019 â€“ CR 389978 Downgraded to C assigned to TEFP <D> **** Detailed Description **** (QA) Two Preventive Maintenance (PM) Requirements (PMRQs) are Essential (ESSN) PM Category instead of Surveillance (SURV), contrary to Attachment 8.4 within PPM 1.5.13 â€œPreventive Maintenance Optimization Living Programâ€. The actual consequence is a deferral request was incorrectly approved to extend a surveillance past the allowed 125%. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Maintenance Programs Audit, AU-MN-19. Informed Quality and Maintenance, recommend assignment to Maintenance. <N> Maintenance to Bring Back CR, discussion more with Licensing & Engineering. What Group it needs to go to and the Regulatory & MRULE impact. <R> Not a reportability or past operability concern. The REP/REGE assingments have been cancelled with Compliance Supervisor concerrence.
389979 | CR | 20190213 |  | 3 | (QA) High Risk Plan Timeliness and Content Issues |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Multiple High Risk Plan (HRP) approvals by the station have not been timely and 2 of 6 reviewed had content issues effecting risk management. Several HRPs over the last two months have been approved the week before implementation, one HRP identified incorrect plant impact, and one HRP was missing the risk mitigation actions in the package. Timely risk evaluation, challenging and approval ensures adequate evaluation of oversight of the risk process and overall reduction of risk to implement required station activities. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Maintenance Programs Audit, AU-MN-19. Informed Quality, PSO and Maintenance, recommend assignment to PSO.
389980 | CR | 20190213 | CAQ | C | (QA) Degraded plant equipment not properly coded |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Multiple work orders are coded as type "other" when the work will correct a problem with a deficient plant equipment contrary to the requirements of PPM 1.3.68. Work orders coded as a type "other" get a lower priority to repair and increased risk to plant operation with the degraded equipment. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Maintenance Programs Audit, AU-MN-19. Informed Quality, PSO and Maintenance, recommend assignment to PSO
389981 | CR | 20190213 | CAQ | C | (QA) Position Description Not Fully Aligned With FSAR |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The Maintenance Manager position description does not include all aspects of the experience required by the Final Safety Analysis Report (FSAR) section 13.1.3.4.1 â€œMaintenance Managersâ€. The position description is missing a requirement for â€œnondestructive testing familiarityâ€ which is specifically listed in the FSAR. This omission did not result in any issue with the current Maintenance Manager as this individual was able to provide documentation demonstrating that this, and all other, FSAR requirements were met. (See EDMS for detailed description) <I> **** Actions Taken **** Recommendation from Audit AU-MN-19 This was identified as a Deficiency during the Maintenance Programs Audit, AU-MN-19. Informed Quality, Human Resources and Maintenance, recommend assignment to Human Resources <N> PD was revised to comply with FSAR. Extent of condition completed. No further actions.
389982 | CR | 20190213 |  | 3 | (QA) SWP-CAP-01 Inconsistent For CARB Reviews |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) One step in SWP-CAP-01 â€œCorrective Action Programâ€ (CAP) is not consistent with other steps therein or with GBP-CAP-04, â€œCorrective Action Review Board (CARB),â€ incorrectly implying that CARB reviews are required for all Root Cause Evaluations. Procedure inconsistencies may cause rework and delays. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Maintenance Programs Audit, AU-MN-19. Informed Quality, Performance Improvement and Maintenance, recommend assignment to Performance Improvement
389984 | CR | 20190213 |  | 4 | Gate 26 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Gate 26 located at the vehicle trap needs maintenance. It is not closing all the way and is making a high ptiched noise. Contact security at ext. 2185 for fiurther details. <I> **** Actions Taken **** Security notification made, CR/WR generated <N> **** Equipment Description **** Gate 26 located in the PA side of the vehicle trap CR Edited to the correct gate (26 not 26A as it was previously stated).
389985 | CR | 20190213 |  | 3 | HP instrumentation needs calibration | N | N |  | N | NO | <D> **** Detailed Description **** All HP instruments in BLDG. 82 (FLEX response) cabinet will go OOC on 02/23/2019. CR generated due to requirement Note in W/O <I> **** Actions Taken **** Informed HP supervision and sent a complete list of instruments to HP instrument technician at the PSF.
389989 | CR | 20190213 |  | 4 | PWC-SEW-10 eye wash failed. | N | N |  | N | YES | <D> **** Detailed Description **** While performing safety eyewash checks on PWC-SEW-10 it was observed that the safety shower worked but neither side of the eyewash did not. An ice ball the size of a softball was formed around the right eyewash nozzle and when the ice was removed the green plastic eyewash nozzle broke off. A temporary eyewash station was placed by the acid pumps inside the CWPH. <I> **** Actions Taken **** Informed CRS and wrote CR. | 02-00-PWC-SEW-10
389991 | CR | 20190213 | CAQ | D | Packing leak on CIA-V-TK/14B | Y | N |  | N | YES | <D> **** Detailed Description **** While replacing CIA-TK-14B, a small packing leak on CIA-V -TK/14B was observed while snoop-checking the connections. Backseating the valve did not stop the leak. Packing needs adjustment/maintenance. <I> **** Actions Taken **** Informed CRS | 02-00-CIA-V-TK/14B
389995 | CR | 20190213 |  | 4 | No Ops rep at T+1 meeting. |  |  |  | N | NO | <D> **** Detailed Description **** There was no Ops rep at T+1 today. The usual Rep was in Training and the back up came in late and didn't realize the conflict. <I> **** Actions Taken **** Coached for excellence.
389996 | CR | 20190213 | CAQ | C | Received RPIS OR DMM INOP & ROD DRIVE CONTROL SYS INOP alarm | Y | Y |  | N | YES | <D> **** Detailed Description **** Received RPIS OR DMM INOP and ROD DRIVE CONTROL SYS INOP alarms - H13-P603.A7 1-7 and 2-8. Attempted to reset RDCS per ARP 4.603.A7 2-8. The RPIS OR DMM INOP and ROD DRIVE CONTROL SYS INOP alarms - H13-P603.A7 1-7 and 2-8 cleared and came back in within a few seconds. In both instances, transponder card R110 for control rod 42-03 was the only LED illuminated on the H13-P616 Fault Map <I> **** Actions Taken **** Notified the CRS and System Engineer. Submitted CR and WR. | 02-00-CRD-DMM-1
389997 | CR | 20190213 |  | 3 | REMP air samples were not obtainable | N | N |  | N | NO | <D> **** Detailed Description **** During the weekly air sampling on 2/12/19, REMP personnel were not able to retrieve air samples from station 1 and 23 due to hazardous weather conditions. Requesting facilities for support to clear the road to these two stations and they donâ€™t have any resources available due to backup with plant support. The road to station 23 is about 2 miles and station 1 is about 3/4 of a mile long. Station 1 and 23 are EFSEC 332 required air sample locations. Recommend AR to AR-ENLAB to include deviation in REMP annual report. <I> **** Actions Taken **** Contacted facilities for help. Discussed situation with supervisor and manager. Wrote CR
389998 | CR | 20190213 |  | 3 | Employee reported experiencing a sharp pain in his shoulder. |  |  |  | N | YES | <D> **** Detailed Description **** Employee was driving a plow truck in the PA when he experienced a pain in his left shoulder. <I> **** Actions Taken **** 0900-Employee reported incident to supervisor. Supervisor took Employee to OCC health Followed ISPM-1 for Accident/injury reporting. Notified Industrial safety and department manager Initiated Incident report and this CR <N> **** Equipment Description **** Protected area East of the GSB.
389999 | CR | 20190213 |  | 3 | B78 Warehouse With Truck Parked Inside Not Allowed |  |  |  | N | NO | <D> **** Detailed Description **** Fire Protection inspectionn of Snake River Warehouse Building 78 found a delivery truck parked inside. The truck was found on the East side, inside the overhead door, in the main aisle between the rack storage. The warehouses and inventory are considererd high dollar value property by NEIL. Parking a fueled vehicle inside the warehouse overnight is not allowed by the Fire Code or by the NEIL Insurance. While it is acceptable to load and unload motor vehicles, they must be moved to the outside when not attended. Protected and covered parking is available under the East side canopy at Building 76. If inside parking of vehicles is desired, a formal review needs to be conducted to find an acceptable location. However, there will need to be adequate separation from combistible storage as well as oil containment berm. Also, NEIL representative will have to review and approve. . Recommend that this be assigned to Org Code 71200 to discuss at a D15 and reinforce the requirement. <I> **** Actions Taken **** Discussed this with the Warehouse Acting Supervisor (D.L.). The truck was pulled out soon after my inspection. This needs to be discussed at the Warehouse D15 to ensure all warehouse personnel are informed.
390001 | CR | 20190213 |  | 3 | STATE FM-Record Water Temperature of Kootenai Water Tanks | N | N |  | N | NO | <D> **** Detailed Description **** State Fire Marshal inspection in December 2018 found that the water temperature for the two fire water storage tanks at the Kootenai Complex is not being recorded. Monitoring the temperature is required by NFPA 25, the Standard for Inspection, Testing and Maintenance of Water Based Fire Protection Systems. This is important during the heating season, when the tank heaters are in use and the water temperature is below 40 degrees F. This temperature recording is required weekly since there is no low temperature alarm for the Kootenai tanks. Assign this CR to AR-TEFP to revise the weekly fire pump test procedure FPP-2.2.3 to include a notation for the tank water temperature.
390004 | CR | 20190213 |  | 4 | CAS-PS-AUTO/1A | N | N |  | N | YES | <D> **** Detailed Description **** FOUND PS OUT OF TOLERANCE. ADJUSTED BACK WITHIN TOLERANCE PER IMDS. WO 0212810401 <I> **** Actions Taken **** ADJUSTED PS PER IMDS AND INITIATED CR FOR TRENDING PURPOSES | 02-00-CAS-PS-AUTO/1A
390005 | CR | 20190213 |  | 4 | Exceeded CCW action level time | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Service building heater chemistry is out of spec low and is in closed cooling water action level 2 per SWP-CHE-02. This action level requires the system chemistry be restored to in-spec conditions within 30 days. Due to a severe leak on the system chemistry has not added chemicals since the chemicals would go right down the drain. The leak is estimated to be roughly 36 gal a day. Chemistry has been waiting to do the chemical add until after the leak is fixed. The leak is still currently on going See AR#388920 and WR#29146666. <I> **** Actions Taken **** Notified Shift Manager, Chemistry supervision and EFIN, and Chemistry specialist. <N> **** Equipment Description **** The leak is on GSB basement surrounded by scaffolding and a leak catch under it.
390008 | CR | 20190213 | CAQ | C | ABN-EARTHQUAKE inaccuracy |  |  |  | N | NO | <D> **** Detailed Description **** Attachment 7.4 of ABN-EARTHQUAKE does not have the Modified Mercalli Intensity Scale (MMI) numbered, leading to a mistake in the shading scheme indicating when a shutdown is required. Step 4.5 bullet 1 says "...Shutdown..." if the following is true: "The MMI scale is 6 or greater with (sic) 3.1 miles of plant." MMI 6 corresponds to the sixth column, which is not shaded. Also, the step numbers in the bases section is are not correct. <I> **** Actions Taken **** This CR was written. <N> **** Equipment Description **** This is a procedure.
390009 | CR | 20190213 | CAQ | C | (QA) 4 EP Non-Compliances with SWP-PRO-03 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Four Emergency Preparedness (EP) implementing procedures (PPM 13.XX.XX) do not annotate some Emergency Plan (EP-01) regulatory requirements in French brackets with an â€œRâ€ followed by a reference number, contrary to SWP-PRO-03 â€œWriterâ€™s Manualâ€. This is a procedure use and adherence issue. The potential consequence is that regulatory requirements not annotated in a procedure could be inadvertently revised or eliminated. The following are examples where EP-01 requirements are not annotated with an â€˜Râ€™ followed by the reference number in a plant procedure: â€¢ EP-01 rev 066 section 2.3.3b states, â€œRadiological Emergency Manager (REM) reports to the EOF Manager. The REM is responsible for managing radiological dose assessment and field monitoring activities.â€ o PPM 13.11.7 â€œRadiological Emergency Manager Dutiesâ€ rev 037-003 states, â€œ3.2.6 Oversee the performance and evaluate the results of dose projection activities; 3.2.7 Oversee the performance and evaluate the results of Field Monitoring Team activitiesâ€ â€¢ EP-01 section 2.3.3c states, â€œField Team Coordinator provides overall management of field teams, . . .â€ o PPM 13.9.1 â€œEnvironmental Field Monitoring Operationsâ€ rev 045-002 section 3.2 â€œField Team Coordinatorâ€ step 3.2.1 states, â€œDirect Environmental Field Monitoring Team activitiesâ€, but there is no â€œRâ€ in French brackets followed by a reference number. â€¢ EP-01 section 2.4.1b states, â€œMaintenance Manager is responsible for . . . acting as the focal point between the TSC and OSC for the work control process.â€ o PPM 13.10.14 â€œMaintenance Manager Dutiesâ€ rev 009-001 step 2.2.3 states, â€œCommunicate maintenance / task information between the TSC and OSCâ€, but there is no â€œRâ€ in French brackets followed by a reference number. â€¢ EP-01 section 2.4.1d states, â€œChemistry/Effluent Manager is responsible for monitoring the Plant effluent and area radiation monitors.â€ o PPM 13.10.16 â€œChemistry / Effluent Manager Dutiesâ€ rev 003-002 step 3.2.1 states, â€œProvide chemical / effluent expertise for accident detection and assessment using effluent and area radiation monitorsâ€, but there is no â€œRâ€ in French brackets followed by a reference number. â€¢ The above four PPMs are a sampling of EP procedures, but performing an Extent of Condition may reveal other similar issues. Recommend assignment to EP as CAQ (OQAPD - Procedures) <I> **** Actions Taken **** Notified EP Manager.
390010 | CR | 20190213 | CAQ | D | ES 16 | N | N |  | N | YES | <D> **** Detailed Description **** ES 16 needs maintenance. contact security at ext. 2185 for further details <N> Compensatory measures have been established for ES16. | 02-00-SEC-TAS-ES16T
390012 | CR | 20190213 | CAQ | C | (QA) EP-01 Responsibility Not Delineated in Procedure |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) An example was identified where one aspect of one position-specific responsibilities from the Emergency Plan (EP-01) are not clearly delineated in a station procedure. While the part of the EP-01 responsibilities in question are contained within Emergency Response Organization (ERO) Positional Checklists, these checklists cannot be credited as procedures because they are not controlled in accordance with SWP-PRO-02 â€œPreparation, Review, Approval, and Distribution of Proceduresâ€. This is a noncompliance with SWP-PRO-04, Nuclear Procedure Program, to have procedures for all activities that could violate regulatory requirements. No examples were identified where this issue had an actual consequence during implementation as the checklists have the detail necessary to ensure the job is performed properly. The following example was identified where parts of responsibilities from the Emergency Plan (EP-01) are not clearly delineated in a station procedure: â€¢ TSC Operations Manager responsibilities for Severe Accident Guidelines (SAGs) missing. o EP-01 rev 066 section 2.3.2h states, â€œ. . . The TSC Operations Manager is responsible for implementing Severe Accident Guidelines (SAGs) . . .â€ o PPM 13.10.5 â€œOperations Manager Dutiesâ€ section 3.2 lists eight responsibilities, which do not include the responsibility for implementing Severe Accident Guidelines (SAGs). However, this requirement in EP-01 section 2.3.2h is being implemented outside of an Administrative or Technical Procedure: + The sixth bullet under â€œPosition Functions/Responsibilitiesâ€ on page 1 of Form 26512 â€œTSC Operations Manager Checklistâ€ states, â€œImplements Severe Accident Guidelines (SAGs)â€. Insights: â€¢ The decision was made in June of 2016 to elevate SAG implementation oversight to the level of a positional responsibility and it was added to Form 26512 â€œTSC Operations Manager Checklistâ€ at that level. However, it was not concurrently added to PPM 13.10.5 â€œOperations Manager Dutiesâ€ section 3.2 when the positional checklist was revised. Recommend assignment to EP as CAQ (Regulation LBD and Procedures). <I> **** Actions Taken **** Notified EP Manager.
390013 | CR | 20190213 |  | 3 | Revise 4.800.C1 section 9-2 |  |  |  | N | NO | <D> **** Detailed Description **** Step 10 should be deleted. E-RMS-7FDA was removed per EC 12954 and ABN-LIGHTING-CR has been updated to reflect this. <I> **** Actions Taken **** None
390014 | CR | 20190213 | CAQ | C | (QA) ERO Checklists Not Reviewed As Directed By PPM 13.14.9 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Emergency Response Organization (ERO) Positional Checklists are not being reviewed and approved using the SWP-PRO-02, Preparation, Review, Approval, and Distribution of Procedures, process as directed by PPM 13.14.9, Emergency Program Maintenance. Instead, these checklists are being revised using the GBP-PRO-03, Preparation, Review and Approval of Corporate Procedures, Department Instructions and Manuals, process which does not require the same level of reviews. No examples were identified where this issue had an actual consequence during implementation and it was noted that all changes to the positional checklists do receive a 10 CFR 50.54(q) screening. â€¢ PPM 13.14.9 â€œEmergency Program Maintenanceâ€ step 1.3.2 states, â€œEmergency Preparedness ERO Positional Checklist forms are revised in a manner similar to Plant Procedure Manual Volume 13 procedures; either as major revisions or editorial changes. (Editorial changes are shown in PassPort as a minor revision).â€ â€¢ PPM 13.14.9 step 4.3.3.a states, â€œUse of this process ensures that major revisions to ERO Positional Checklists receive the same review and evaluation as Emergency Plan Implementing Procedures.â€ Factual Basis: â€¢ Review of various ERO Positional Checklists and discussions with Emergency Preparedness personnel revealed that they are intentionally reviewed using the GBP-PRO-03 process. â€¢ SWP-PRO-02 currently does not acknowledge ERO Checklists, nor require ERO Checklist revisions to be similar to the Plant Procedure Manual Volume 13 procedures as stated within PPM 13.14.9. â€¢ Although the above checklists were revised under GBP -PRO-03, they did receive a 50.54(q) screening, but no specific review by a Qualified Procedure Reviewer (QPR), contrary to SWP-PRO-02. Insights: â€¢ Changing the manner in which ERO Positional Checklists are reviewed from SWP-PRO-02 to GBP-PRO-03 was an intentional decision; however, PPM 13.14.9 was not updated to reflect this. Recommend assignment to EP as CAQ (OQAPD - Procedures). <I> **** Actions Taken **** Notified EP Manager.
390015 | CR | 20190213 |  | 4 | (QA) Form Missing in Alt. EOF Binder |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) During an audit of the Alternate Emergency Operations Facility (EOF), it was identified that a form was missing from a binder. Specifically, Form 25665 â€œEP-Reactor Plan Event Notification Worksheetâ€ was missing from Section 8 of Binder 1067 â€œAssistant EOF Managerâ€. While all other binders were found to be in order and the form was available at the recharge cart, this does not meet PPM 13.11.2 Section 3.1.4 which directs all ERO Members to â€œRestore area and materials upon event termination. Subsequent to the identification, Emergency Preparedness personnel corrected the issue. Subsequent to identification, the issue was immediately corrected. No further action required. Recommend SL4 to EP as missing form was readily available and not impact on EP function. <I> **** Actions Taken **** Notified EP manager and EP corrected the issue.
390016 | CR | 20190213 | CAQ | C | (QA) Severity Level A CA Not Completed as Documented |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Severity Level A Condition Report (CR) Corrective Action (CA) was not completed as directed and documented. AR-CA 377412-06 identified 37 PMIDs that required updating with an â€œEPâ€ flag and AR-CA 377412-07 documented that the 37 PMIDs from the -06 action were updated to flag them as being â€œEPâ€. However, the audit team identified that five PMID PM Requirements included in this population were not updated. Subsequent to the identification of this issue, Emergency Preparedness (EP) personnel reviewed the closure and stated that the five items in question did not require an â€œEPâ€ flag. However, this contradicted the closure notes which stated that all 37 were updated, and there was no mention/approval for deviating from the directed action as required by SWP-CAP-01, Corrective Action Program, step 4.6.2(d). Based on discussion with EP, there is no impact since the PMIDs were not required to be flagged; therefore, this is strictly a non-compliance with SWP-CAP-01 requirements. Factual Basis: â€¢ AR-CR 377412, AMA-CF-52 Carbon Filter Replacement Outside Standards Timeframe, was categorized as Level A due to a Hi Risk/Recurrence/Severity & Cause Known rating. CA 377412-06 closure documentation provided a list of 37 PMIDs that required to have an â€œEPâ€ code added to the PortalJ â€œapplicable modeâ€ field. â€¢ 377412-07 Closure documentation states that all 37 PMIDs identified by EP Management were manually updated. â€¢ A review of the 37 PMIDs determined that five PMID PM requirements within the scope specified by 377412-06 did not have the â€œEPâ€ code in the PortalJ â€œapplicable modeâ€ field: o 19452-02 (Type Other) missing EP code o 15965-01 (Type ESSN) and 15965-02 (Type Other) o 15963-01 (Type ESSN) and 15963-02 (Type Other) Insights: â€¢ Interview with the PM Coordinator indicated that he worked with an Emergency Preparedness Contractor to identify and make the changes and if intentionally not coded there is not a record of the reason for deviation from the list provided in 377412-06. Recommend CAQ to Maintenance (OQAPD - CAP) to determine the flagging and consider evaluation of how SL A CAs were not accurate upon closure. <I> **** Actions Taken **** Notified Maintenance Support Manager and EP.
390017 | CR | 20190213 | CAQ | C | (QA) Severity Level A CR Corrective Actions Not Sustainable |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Severity Level A AR-CR 377412 corrective actions specified in the Apparent Cause Evaluation (ACE) are not sustainable as they are not embedded in a process to ensure future performance. Corrective actions provided coding to existing EP Preventive Maintenance (PMIDs), but did not ensure the process would consistently code EP PMIDs in the future or take consistent actions for EP coded PMIDs. â€¢ AR-CR 377412, AMA-CF-52 Carbon Filter Replacement Outside Standards Timeframe, was categorized as Level A due to a Hi Risk/Recurrence/Severity & Cause Known rating. The approved ACE (Rev 0) causes are: o Apparent Cause - AC1: Official EP delineator has not been established within the PM program to alert users of EP related equipment. o Barrier Analysis noted the Administrative Barrier of PPM 1.5.13 was ineffective as â€œProcedure contains instructions to send PM change request to Emergency Preparedness for approval but PM panel does not have a flag to inform the PM Coordinator to send request to EP for approval.â€ â€¢ A review of CAs taken determined that there is no reasonable assurance of sustainability due to: o No procedure or process guidance exists to continue coding new EP PMIDs with â€œEPâ€ in the â€œApplicable Mode.â€ The Administrative Barrier of PPM 1.5.13 did not incorporate continued coding and could negate the risk mitigation of actions AC1.1 through AC 1.3 for new EP PMs o No procedure or process guidance exists to take action if an EP PMID has â€œEPâ€ in the â€œApplicable Mode.â€ The Administrative Barrier of PPM 1.5.13 did not incorporate the use of coding and could negate the risk mitigation of actions AC1.1 through AC 1.3 for all EP PMs should there be a change in personnel processing SMS-ARs. FULL TEXT OF THE CR WITH REQUIREMENTS IS IN EDMS. Recommend CAQ assignment to Maintenance to develop sustainable guidance and consider evaluation of how SL A CA were not effective in addressing sustainability. <I> **** Actions Taken **** Notified Maintenance Support Manager and EP.
390018 | CR | 20190213 |  | 4 | MT-ELEV-4 Faults | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-4 fault 'Brake Did Not Lift' occured twice in one shift on different elevations and locked out the elevator. Pressed 'System Fault Reset' pushbutton at CRS direction and alarm was cleared. The elevator was returned to service. <I> **** Actions Taken **** Informed MCR. Wrote CR | 02-00-MT-ELEV-4
390020 | CR | 20190213 |  | 4 | Running Vehicle left unattended in Parking Lot |  |  |  | N | NO | <D> **** ANONYMOUS CR - Detailed Description **** upon leaving the site at 6PM a vehicle was noticed running with no one in attendance. The employee approached and was coached on leaving a car running unattended. The employee was unaware their car was running. Apparently they had their keys in their pocket and the car which had a push button start had been running since they arrived that morning at 8:30 AM. The employee said that it had been noisier than usual when they arrived with facilities vehicles running and others arriving all around them. They had not noticed that their car was running and were not aware that they could get that far away from their car with the keys in their pocket. The door to their vehicle was locked, <I> **** Actions Taken **** Wrote this CR for awareness. <N> ANON CR written, moved to OPS for Review.
390021 | CR | 20190213 | CAQ | D | MW 70 | N | N |  | N | YES | <D> **** Detailed Description **** MW 70 is not working as designed. <I> **** Actions Taken **** Compensatory measure in place, contacted plant electricians for support and generated CR/WR. <N> Compensatory measures have been established for MW70. | 02-00-SEC-MW-ISFSI/70R
390022 | CR | 20190213 |  | 4 | RX 522' Broken Light Switch Toggle (Door R-414) | N | N |  | N | NO | <D> **** Detailed Description **** -Light switch toggle just inside Door R-414 on RX 522' is broken and needs replaced. <I> **** Actions Taken **** -Initiated CR & WR. -Notified Supervision via e-mail. <N> **** Equipment Description **** RX 522' Door R-414
390023 | CR | 20190213 |  | 4 | Poor Lighting on RX 501' | N | N |  | N | NO | <D> **** Detailed Description **** -The lighting on RX 501' is poor around E-IR-H22/PO15 (Outside Steam Tunnel Entrance). There are light fixtures that have no lamps installed. Some are in a HRA and some are not. This will be a heavy traffic area during the outage and should be addressed. <I> **** Actions Taken **** -Initiated CR & WR. -Notified Supervision <N> **** Equipment Description **** RX 501'
390024 | CR | 20190214 |  | 4 | XD-6 | N | N |  | N | YES | <D> **** Detailed Description **** XD-06 failed its daily test. <I> **** Actions Taken **** Took XD-6 out of service and generated CR/WR | 02-00-SEC-XD-6
390025 | CR | 20190214 |  | 4 | PWC leak at bldg 35 sidewalk. | N | Y |  | N | YES | <C> MRT Change on 02.21.2019 â€“ CR 390025 Downgraded to NON-CAQ <D> MCR recieved report of PW leak from bldg 35 sidewalk. Operator closed PWC-V-526 to isolate leak from PW header. Facilities contacted MCR to report that they will attempt to isolate the leak in bldg 58. <I> Please fix this. <N> BLDG 35, BLDG 58 | 02-00-CGS-BLDG-MISC
390031 | CR | 20190214 |  | 4 | Employee Lanyard broke and badge was lost in IA |  |  |  | N | NO | <D> When reporting to work the morning of 02/14/19 a green badged employee discovered that their access badge and another item were missing from their lanyard. It is believed to have been lost while performing snow removal activities near the end of the prior day. <I> the lost badge was reported to Access Authorization and the badge was placed on hold, a new badge was issued to the employee. Department manager was notified and this CR was generated for tracking and trending purposes. Recommend assigning this CR to AR FACIL, CAT-D <N> CR found at INPROG, moved to Approved status.
390032 | CR | 20190214 | CAQ | D | ARM-RIS-3 Radiation Level Spike | N | Y |  | N | YES | <D> **** Detailed Description **** During the performance of CSP-INST-H201 ARM-RIS-3 local meter was observed at 650 mr/hr then dropped back to 400 mr/hr. Review of ARM-RR-600 (MCR Recorder) showed spiking corresponding to similar levels. <I> **** Actions Taken **** Informed CRS/RO. HP checked the reading. | 02-00-ARM-RIS-3
390034 | CR | 20190214 |  | 4 | CAS-C-1B Low Oil | N | N |  | N | YES | <D> **** Detailed Description **** Oil level is less than 1/8 full with compressor shutdown. Oil is visible sight glass. Ops-3 rounds state level should be between 1/8 and 1/2 full when compressor is shutdown. Please add oil. <I> **** Actions Taken **** Notified CRS | 02-00-CAS-C-1B
390038 | CR | 20190214 | CAQ | D | Evaluate use of Red Plastic Seals on CIA-PCV-2A & 2B |  |  |  | N | NO | <C> Trend to CR 388926 and AR Eval. <D> **** Detailed Description **** CR388926 identified that Red plastic seals were used versus wire and lead seals to lock CIA-PCV-2A and CIA-PCV-2B. Need to evaluate the use of red seals because wire and lead seals are no longer used. Will also need to update the drawings as appropriate based on evaluation. <I> **** Actions Taken **** Initiated CR. Recommend action to engineering to evaluate the use of red plastic seals for this application and update drawings as necessary.
390039 | CR | 20190214 |  | 4 | TDAS X035 OUT OF TOLERANCE | N | N |  | N | YES | <D> **** Detailed Description **** TDAS X035 FOUJND OUT OF TOLERANCE DURING ISP-SLC-X302 WO 02107625-01. <I> **** Actions Taken **** NOTIFIED OPS AND INITIATED CR/WR PER SURVEILLANCE INSTRUCTIONS | 02-00-SLC-FT-1
390040 | CR | 20190214 |  | 3 | Unexpected reboot of PDIS-CPU-DATA2 | N | N |  | N | YES | <D> **** Detailed Description **** At approx 0100 2/14/19, PDIS-CPU-DATA2 unexpectedly rebooted. System is up, but not fully functioning. This system provides eDNA to GDS for data from PPC train. Currently TDAS is primary so Operations has not been affected. However, if TDAS were to go down, GDS would be unavailable even when switched to PPC as primary. . This is not a reportable condition. . System should be rebooted to restore functionality. Please assign to Computer Engineering as a 3 for investigation with vendor. <I> **** Actions Taken **** Notified SM and Cyber Security. Generated WR to reboot server to restore functionality. | 02-00-PDIS-CPU-DATA2
390043 | CR | 20190214 |  | 4 | Plant public enouncements audible in the simulator | N | N |  | N | YES | <D> **** Detailed Description **** The plant public announcements are cross talking onto the simulator public announcement speakers. The PA system is otherwise operating as designed in both simulator transfer mode and normal mode. <I> **** Actions Taken **** Notified: EP, and the simulator staff. Recommend closing to WR. <N> **** Equipment Description **** Simulator
390044 | CR | 20190214 |  | 4 | Simulator training start delayed ~ 15 minutes |  |  |  | N | NO | <D> **** Detailed Description **** Date 2/12/19, Upon starting LR001484, the simulator program faulted with the message to close the program or debug. Unloaded and restarted the computer, creating an ~ 15 minute delay. No additional issues expereinced, all required training was conducted . CR written for trending purposes.
390045 | CR | 20190214 | CAQ | D | FP-P-110 small coolant leak | N | Y |  | N | YES | <D> **** Detailed Description **** FP-P-110 small coolant leak during PPM 15.1.4 monthly run. The leak was approximately 1 drop/sec. See attached images and video for leak location. <I> **** Actions Taken **** Informed MCR. Wrote CR. Opened FPSI 19-0055. | 02-00-FP-P-110
390047 | CR | 20190214 |  | 3 | PPM 10.2.10 - Enhance for composition gasket Material |  |  |  | N | NO | <D> **** Detailed Description **** Currently per PPM 10.2.10 a .5 (50%) reduction of the calculated torque value is used if a composition gasket is used if the torque is determined from PPM 10.2.10 based on the bolting material, size and Design Temperature. As documented under CR 388041 and WOT 02033672-10, duriing the previous RHR Maintenance window in Dec of 2018, Engineering allowed going to the calculated torque value that the bolting would allow for the temperature as the gasket installed (CATID 5359) could handle the gasket stress which was considered a positive. Recommend Engineering review tool/calculator called "Gasket Calculator 2.0, 3.0, 4.0" etc" that is available by a reputable Industry know manufacturer/supplier (GXXXXXX) etc and have Engineering Review for having this auto calculator on a specific server or approved for use for info with Engineering review and updated accordingly. <I> **** Actions Taken **** Generated CR. PM 10.2.10 is fairly generic and references the 50% reduction. However newer material and specifics are available which can be input for the actual material (Part # being used) and the bolt pattern, configuration, bolt size, material and Design Temp can be used to aid in determining a more appropriate torque value based on the actual system configuration to support the actual flanged connection. This was originally documented under AR CR 353326 back in 2016 specifically for 3" 150 lb flat face flanges with B7 connections. However that CR was cross referenced to an AR EVAL 357804 which resulted in stating no action was needed based on follow up. Having a means in the procedure or planing guide which states for known specific gasket materials to contact Engineering for potentiial higher allowable torque values based on the 80% of bolt yield for the Design Temp. Contact Levi Woods or initiator of AR CR 353326 back in 2016 for more follow up/additional information.
390048 | CR | 20190214 | CAQ | C | MRule Evaluation needs to be re-evaluated for CR 00368369. |  |  |  | N | NO | <D> **** Detailed Description **** Maintenance Rule Evaluation (System Inbox screening) for CR 00368369, DG4 tripped on High Coolant temperature, needs to be re-evaluated. Currently this is not identified as a Functional Failure. Per discussions with system engineer it appears that this should be identified as a Functional Failure and Maintenance Preventable Functional Failure. . This CR should be assigned to System Engineering to re -evaluate CR 00368369 for Maintenance Rule impacts.
390049 | CR | 20190214 |  | 4 | PO.28 Late Identification Contract Requisitions |  |  |  | N | NO | <D> **** Detailed Description **** P.O. 28 Milestone requests that all outage support contract requisitions (CR) are to be in Asset Suite by July 25, 2018. A tracking log of additional CRâ€™s received post 7/25/2019 identified 27. Of the 27 items on the report, 18 of them were identified prior to the milestone or were emergent ads approved by PHC with reasonable explanations of why they generated additional requests after milestone closure. An additional 3 items on the report are not associated with R24 and will be removed from the report. The remaining 6 items were misses by the organization to identify needs prior to milestone closure. When we looked at these 6 we recognized that a common theme of turnover/unclear roles and responsibilities played a part. While this number seems low and is an improvement from the past 3 outages it still doesnâ€™t represent organizational excellence. <I> **** Actions Taken **** Reviewed with outage management the list of late ads. Created this CR for trending purposes. Notified SCS ORT member of the expectation to provide an update for those not currently awarded to ensure continuous visibility to the outage team. Will address the missed items with the responsible organization as part of the R-24 SCS lessons learned post R-24. Recommend this be a trend CR
390050 | CR | 20190214 |  | 4 | MD-V-86 downstream temperature increase, loss of 3.5 MWe | N | N |  | N | YES | <C> MRT Change on 02.21.2019 â€“ CR 390050 Downgraded to NON-CAQ <D> **** Detailed Description **** MD-V-86 (RH X-Under Drain to Condenser) downstream temperature (ENW.CONDENSE.MDTT86) spiked on 2/4/19 at 08:40 from 210 degF to 260 degF. A generation loss of 3.5 MWe was observed. Corresponding decreases were observed in Turbine 1st Stage Pressure (-1 psia), Final Feedwater Temp (-0.19 degF), and GV4 position (-0.4%). It was noted that MD-V-86 was cycled on 2/12/18 at 20:00 and downstream temperature increased from 260 degF to 284 degF (CR 389974). The additional MWe from this temperature increase is under investigation. Indications point to a fully open valve. Recommend measures be taken to close valve. This valve is currently scoped to be replaced in R24. See EDMS for temperature plots and analysis. <I> **** Actions Taken **** Initiated CR. Discussed with Engineering. | 02-00-MD-V-86
390052 | CR | 20190214 |  | 3 | Procedure enhancement 4.800.C4 Drop 1-7 TR-S lockout |  |  |  | N | NO | <D> **** Detailed Description **** TR-S lock out lesons learned: Update lockout trip from Buchholz sudden pressure relay to include sudden pressure or conservator low level. Reference SD000182 and recent TR-S lockout event
390055 | CR | 20190214 |  | 4 | Drill participant names weren't provided in a timely manner |  |  |  | N | NO | <D> **** Detailed Description **** ERO Drill participant names weren't provided in a timely manner to the EP Planner for the OSC. Two days before the drill, 10 names remained unidentified and one business day before the drill, eight names were still outstanding, This delays the ability to develop drill related documents, (such as an accurate accountability report). <I> **** Actions Taken **** Names were eventually received and included into required documents.
390056 | CR | 20190214 |  | 4 | Multiple OSC & TSC PCs did not have the latest updates |  |  |  | N | NO | <D> **** Detailed Description **** Multiple OSC & TSC PCs did not have the latest updates. IS determined that personnel are using these computers and shutting them OFF, rather than leaving them ON; the PCs can't receive updates when turned off. The affected PCs are clearly marked with a large red placard stating "DO NOT TOUCH ! Emergency Preparedness Equipment". <I> **** Actions Taken **** I adjusted the monthly EP center walkdown to perfom a Restart on each computer to push a search for updates in case it had been turned off during the period of a past update, but that will no stop a future update from being missed if personnel continue to shutdown the machines.
390057 | CR | 20190214 |  | 4 | Over January Dose Goal |  |  |  | N | NO | <D> **** Detailed Description **** Williams Plant Services was over the January Dose goal of 315 MR, with an actual of 505 MR. This was mainly due to RWCU piping Flowmeter insulation removal, which was 305 MR received for the Insulators. This work was not in the original monthly dose goal schedule. The other work we supported that caused us to go over our goal was the MT -CRA-1 support. We received over 200 MR on this Project in the month of January alone. <I> **** Actions Taken **** Contacted Management
390058 | CR | 20190214 |  | 3 | CID 0059100174 Directional Control Valve coils for old style |  |  |  | N | NO | <D> **** Detailed Description **** Existing stock (12 each) of CID 0059100174 Directional Control Valve coils are for deleted style HCU Directional Control Valve which are no longer installed in any CGS CRD-HCU(s) and are wrong size/design for use on existing Directional Control Valves. These items should be removed from stock and excessed. This was discovered by Craft during WO 02138999 Emergent Priority 1A RDCS repairs and extended RDCS LCO time for re-planning and rework. <I> **** Actions Taken **** Wrote CR to document Issue.
390060 | CR | 20190214 |  | 4 | PWC-SEW-10 leak |  |  |  | N | YES | <D> **** Detailed Description **** PWC-SEW-10 eye wash leak due to freezing piping. One of the eye wash nozzles broke off, and the seal on the actuation valve for the eye wash ruptured and was spraying water. The heat trace for this eye wash was previously written up for not operating properly (HTP-FP-6, circuit 24F). <I> **** Actions Taken **** Isolated PWC-SEW-10 using PWC-V-355. Informed MCR. Wrote CR. | 02-00-PWC-SEW-10
390061 | CR | 20190214 |  | 3 | Ice Melt is Causing ARGOS Foot Alarms |  |  |  | N | NO | <D> **** Detailed Description **** -Ice melt is causing multiple nuisance foot alarms when workers are being monitored by the ARGOS. All workers having this issue have come directly from the outside where their shoes were in contact with the ice melt. -Recommend possibly looking into an alternative method to melt ice. <I> **** Actions Taken **** -Verified floors to make sure these were nuisance alarms. -Found bag with Shift Manager outside and performed direct frisk. (approx 60 ccpm on a frisker) -Notified Supervision
390062 | CR | 20190215 |  | 4 | S-CR-24 points 12 & 9 reading erratically. | N | N |  | N | YES | <D> **** Detailed Description **** S-CR-24 points 12 & 9 reading erratically. Following performance of COND-DM-1F backwash and precoat, S-CR-24 pts 12 & 9 are reading very erratically. The high conductivity alarms for both sample points are constantly coming in and clearing. Chemistry performed a grab sample to verify the reading, and concluded that the grab samples were normal. Tracing the history back over the last 24 hours, sample point 12 has been very erratic prior to the CFD backwash and precoat. <I> **** Actions Taken **** Informed MCR and Chemistry Supervision. Recommend I&C troubleshoot the instrument and possibly vent the instrument. | 02-00-S-CR-24
390067 | CR | 20190215 |  | 4 | Heating coil steam leaks on TB HVAC 1A supply | N | N |  | N | YES | <D> **** Detailed Description **** An audible steam leak was heard inside the supply to TOA -FN-1A heating coils. Investigation found two heating coil unit steam leaks. The inlet valves HS-V-T1L and HS-V-T1O were isolated per the CRS, the two leaks went away (on two separate heating coils). EDMS images/video. <I> **** Actions Taken **** Inlets closed per CRS to eliminate the leaks. CRS further directed to remove leaking coils from service per applicable procedure. | 02-00-TOA-HC-1A
390068 | CR | 20190215 | CAQ | D | CRD-FI-4A flow less than 0.12gph | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-FI-4A flow is less than 0.12 gph. OPS 2 rounds require it to be greater than 0.12 gph. <I> **** Actions Taken **** Wrote CR. Informed MCR. <N> OPS 2 rounds say "If flows are out of tolerance, notify I&C to perform PPM 10.27.75. | 02-00-CRD-FI-4A
390069 | CR | 20190215 |  | 3 | Minor drawing corrections suggested - AED S852, A511, A526 |  |  |  | N | NO | <D> **** Detailed Description **** AED S852 correction needed: 1) AED S852 zone E/15 references AED A526 section 110 â€“ 110. Section 110 â€“ 110 does not exist on AED A526. The likely intended reference was AED A526 zone J/7 section 111 â€“ 111. AED A511 corrections suggested: 1) AED A511 zone F-H/6 references (3) to section 104 â€“ 104 on AED A526 zone E/14 should reference AED 526 zone F/14. 2) AED A511 zone F/7 reference to section 111 â€“ 111 on AED A526 zone G/8 should reference AED A526 zone J/7-8. 3) AED A511 zone F/7 reference to section 105 â€“ 105 on AED A526 zone J/10 should reference AED A526 zone J/11. 4) AED A511 zone F/7 and F9 reference to section 26 â€“ 26 on AED A522 zone H/15 should reference AED A522 zone E/14. AED A526 correction suggested: 1) AED A526 section 104-104 reference to AED A511 zone H/6 should reference AED A511 zone F-H/6. . These corrections should be considered but this condition is not worthy of CAQ characterization. Recommend NonCAQ resolution to Mechanical Design & Drafting. . This is purely an administrative issue - there is no associated adverse impact or effect upon the physical plant or the continued operation, function, or qualification of any SSC. <N> This was noted while reviewing AR EVAL 273858.
390070 | CR | 20190215 | CAQ | D | cctv 23 FAILURE | N | N |  | N | YES | <D> **** Detailed Description **** Video loss of CCTV 23 and 23 Thermal <I> **** Actions Taken **** Comp put in place, notified supervision, CR/WR generated <N> **** Equipment Description **** South Side isolation zone (building 88) | 02-00-SEC-CCTV-23,02-00-SEC-CCTV-23T
390071 | CR | 20190215 | CAQ | C | Drawing discrepancies on M515-2 |  |  |  | N | NO | <D> **** Detailed Description **** Drawing discrepancies noted on drawing M515-2. Preaction system P65 installed aux drain valve has an EPN of FP-V -P65/102 on its label, but the valve list for detail F on the drawing lists 04 as the valve number for this valve, would be FP-V-P65/4. Portal J shows this EPN is a preaction 65 air bleed, not the aux drain valve. FP-V -P65/102 is not listed in the valve table. For preaction system P66, there are three installed valves listed as auxiliary drains, FP-V-P66/57, FP-V-P66/81, and FP-V -P66/82. The valve list for this preaction only lists one auxiliary drain with valve number 34. Portal J lists FP -V-P66/34 as the preaction 66 air bleed. None of these three EPNs are listed on the table, nor does the detail reflect three aux drain valves for preaction system 66. <I> **** Actions Taken **** Recommend updating drawings to reflect field configuration of valves with correct EPNs listed in the valve table. | 02-00-FP-V-P65/04,02-00-FP-V-P65/102,02-00-FP-V-P66/34,02-00-FP-V-P66/57,02-00-FP-V-P66/81,02-00-FP-V-P66/82
390073 | CR | 20190215 | CAQ | D | IDS 18 and 19 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** IDS 18 and 19 needs maintenance. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** comp in place, security notification made, CR/WR generated <N> **** Equipment Description **** Poles 150, 154, 155, 165, 168, 171, 173
390074 | CR | 20190215 | CAQ | D | ES-16 | N | N |  | N | YES | <D> **** Detailed Description **** 02/15/2019 Electrical Maintenance went to inspect ES-16, it was noticed that ES-16 was moved about 6 inches to east, which in turn damage the tamper alarm device. This damage happened when Facilities personnel was performing snow removal. ES-16 sits above ground and was covered with snow and was not noticeable. Electrical Craft was able to re -align ES-16 cover and fix the tamper alarm device. ES-16 will need to be resealed and grouted when the weather is more favorable for this activity. R. Izaguirre <I> **** Actions Taken **** Notified Facilities Supervisor, Security and initiated CR for repair on ES-16 <N> **** Equipment Description **** ES-16 is located north of SWPH-1A
390075 | CR | 20190215 |  | 3 | SAFETY/LOWER THE BAR OR RAISE IT |  |  |  | N | NO | <C> MRT Change on 02.21.2019 â€“ CR 390075 upgraded to 3 assigned to AR-PERFIMP <D> **** ANONYMOUS CR - Detailed Description **** ON 2/14/2019 AT 11:36 A.M. AN E-MAIL WENT OUT THAT DUE TO ADVERSE WEATHER CONDITIONS (FREEZING RAIN) ALL NON -ESSENTIAL EMPLOYEES WOULD BE RELEASED FROM WORK AT 12:15 P.M. AT 11:45A.M. MYSELF AND OUR WHOLE SHOP WAS TOLD TO NOT LEAVE UNTIL R24 WALKDOWN OVER TIME HAD BEEN ASKED TO MEET THE SHOP R24 MILESTONE. LESS THAN 5 HOURS EARLIER, UPPER MANAGEMENT WERE HANDING OUT CHOCOLATE BARS WITH THE COMPANY'S 2019 FOCAUS AREAS. WITH NUMBER ONE BEING SAFETY FIRST. UNTIL MANAGEMENT IS HELD TO THE SAME ACCOUNTABILITY AS WORKERS I DON'T SEE ENERGY NORTHWEST COMING OFF THE BOTTOM QAURTILE IN SAFETY AS THE VIDEO WITH OUR V P OF OPERATIONS STATED. <I> **** Actions Taken **** TALKED WITH MY SUPERVISOR AND MANAGER <N> ANON CR created; screened for ECP, moved to OPS for review. . There was a similiar question in our "ask senior leadership" forum. the question and response is below: Q: Yet again, Hanford closed work for the day, and ENW did not. If ENW expects us to use our PT for snow days, why don't they incorporate some "bad weather" time into our PT banks? When a family member passes away, we use PT because that bereavement was built into what we receive for PT. Perhaps do the same for bad weather? Just a thought. Thank you. . A: Thank you for your inquiry. Energy Northwest will from time to time vary from other employers on decisions for delays, early releases and closures. We carefully assess road conditions during times of inclement weather to make the best determination possible for our overall workforce. However, you are in the best position to determine when you can get to work safely or when you need to come in late or take the day off. . You mentioned an understanding that bereavement leave was built into our personal time accrual rate. Similarly, the amount of our PT accruals was built to factor in some consideration for inclement weather when employees make a personal determination not to drive to work. This can be seen in our collective bargaining agreements; for example, the Nuclear Bargaining Unit agreement states, â€œPersonal Time is deemed to be in recognition of maintaining an eight (8) hour day and a forty (40) hour week and provides for vacation, conduct of personal business, inclement weather, personal illness, family illness, family death or special holidays.â€ . We recognize Safety First as a 2019 station focus area, so please know that supervisors and managers will do their best to support your decision to use PT or make up time in accordance with company policy and our labor agreements in these situations. . Steve Lorence Corporate Support Services General Manager
390076 | CR | 20190215 |  | 4 | TOA-HC-1A additional steam leak | N | N |  | N | YES | <D> **** Detailed Description **** An additional steam leak on TOA-HC-1A has been found while hanging a clearance on the system. Inlet valve HS-V-T1N was closed per CRS to remove steam from the unit. Trap drain was opened to drain water to prevent from freezing and causing further damage. <I> **** Actions Taken **** Shut off steam and opened trap drain. Clearance will be hung for configuration control. | 02-00-TOA-HC-1A
390077 | CR | 20190215 |  | 3 | (NRC) threaded connection on preaction drain line w/ no cap | N | Y |  | N | YES | <D> **** Detailed Description **** NRC identified that the common drain line on preaction system P65 is open piping with a threaded connection that looks as if a cap should be installed. A review of M515-2 does not reflect this as a capped connection. This same configuration exists on all preaction systems (P65, P66, P79, P80, P81, P82, P83, and P84). This condition does not impact the functionality of the preaction systems, as all drain are currently closed with no supervisory alarms actuated in the main control room. Evaluate whether a pipe cap is needed for these connections. <I> **** Actions Taken **** Walked down preaction systems, reviewed drawing M515-2. Wrote this CR. The AED M515-2 P65, P66, P79, P80, P81, P82, P83, and P84 'P' valves (FP-V-P65/04, FP-V-P66/34, FP-V-P79/663, FP-V-P80/693, FP-V-P81/723, FP-V-P82/753, FP-V-P83/783, and FP-V-P84/813) are all depicted as closed and NOT capped on the flow diagram. This configuration aligns with SOP-FP-LU which describes these Aux Drain valve EPNs as closed (C) and NOT as closed and capped (C+). As such, the field configuration appears to align with the line up procedure and the flow diagram depiction. <N> **** Equipment Description **** Drain lines associated with preaction systems P65, P66, P79 P80, P81, P82, P83, P84
390078 | CR | 20190215 |  | 4 | SAFETY / LOWER THE BAR OR RAISE IT |  |  |  | N | NO | <D> **** ANONYMOUS CR - Detailed Description **** ON 2/14/2019 AT 11:36 A.M. AN E-MAIL WENT OUT THAT DUE TO ADVERSE WEATHER CONDITIONS (FREEZING RAIN) ALL NON -ESSENTIAL EMPLOYEES WOULD BE RELEASED FROM WORK AT 12:15 P.M. AT 11:45 MYSELF AND OUR WHOLE SHOP WAS TOLD TO NOT LEAVE UNTIL R24 WALKDOWN OVER TIME HAD BEEN ASKED TO MEET THE SHOPS R24 MILESTONE. LESS THAN 5 HOURS EARLIER, UPPER MANAGEMENT WERE HANDING OUT CHOCOLATE BARS WITH THE COMPANY'S 2019 FOCUS AREAS. WITH NUMBER ONE BEING SAFETY FIRST. UNTIL MANAGEMENT IS HELD TO THE SAME ACCOUTABLITY AS WORKERS I DON'T SEE ENERGY NORTHWEST COMING OFF THE BOTTOM QAURTILE IN SAFETY AS THE VIDEO WITH OUR V P OF OPERATIONS STATED <I> **** Actions Taken **** TALKED WITH SUPERVISOR AND MANAGER AND WROTE THIS CR <N> ANON CR created; screened for ECP, moved to OPS for review. Duplicate of CR 390075
390079 | CR | 20190215 |  | 4 | Abnormally loud inside the ASD building | N | N |  | N | YES | <D> **** Detailed Description **** While on OPS-4 rounds, it was observed that the inside of the ASD building was abnormally loud. I was not able to pinpoint the sound, though it did seem louder near the filter capacitors. Noise may be from the recirc. pumps running at higher frequency due to core life. ASD 1A/2 and ASD 1B/2 coolant resistivity was near the 5 Mohm low limit. ASD 1B/1 and ASD 1A/1 coolant resistivity was approximately 8 Mohm. ASD transformers had normal temp/level/pressure. <I> **** Actions Taken **** Notified MCR <N> **** Equipment Description **** ASD building
390080 | CR | 20190215 |  | 3 | (NRC) RPT trip coil available lights are very dim | Y | N |  | N | YES | <D> **** Detailed Description **** RPT circuit breaker trip coil available lights in the main control room on panels H13-P609 and H13-P611 are all very dim, but light DS6B is brighter than the other three. The NRC resident questioned if the brightness of the lights in the simulator matched the lights in the plant and why DS6B was brighter than the other three. Evaluate if simulator matches the plant in this regard and why one light shines brighter than the other three. <I> **** Actions Taken **** Wrote this CR. <N> **** Equipment Description **** RPT trip coil available lights on H13-P609 and H13-P611
390081 | CR | 20190215 |  | 4 | CAS mod PMT inadequate for CAS-C-1A and 1C | N | N |  | N | YES | <D> W/O 02128861 and 02128862 complete already but did not this is a process issue for these PMTs - WRs generated to retest appropriately (anytime the unit is in STBY). **** Detailed Description **** include a step to (with compressor off) cycle the supply disconnect off, wait a few seconds (30 sec) then reclose the disconnect and verify the high temperature alarm at the compressor does not come in on repowering. Also verify the control room annunciator (trip) is clear. W/O 02128860 for CAS-C-1B is corrected and scheduled 2/20/19 <N> ***General Notes*** Per the planning supervisorr this issue has been addressed.
390082 | CR | 20190215 | CAQ | D | FP-PR-1 not recording FP header pressure | N | N |  | N | YES | <D> **** Detailed Description **** FP-PR-1 is not recording FP header pressure. Ink cartridge needs to be replaced and/or needs to be adjusted. <I> **** Actions Taken **** Notified CRS <N> **** Equipment Description **** FP-PR-1
390083 | CR | 20190215 | CAQ | C | RDCS lockup | Y | Y |  | N | YES | <C> CR request from Engineering to upgrade this CR to C and assign to SEEIC. <D> **** Detailed Description **** At 1808 on 2/15/19 Received 4.603.A7 drop 2-8 â€œRod Drive Control System Inoperableâ€ and 4.603.A7 drop 1-7 â€œRPIS or DMM INOPâ€. RDCS was reset approximately 30 minutes late. Attached map in back of 4.603.A7 drop 2-8 and picture of P616 map in EDMS. PPC also displayed point A516 INTLK ROD BLOCK concurrently with the RDCS lockup. <I> **** Actions Taken **** Followed ARP informed CRS | 02-00-CRD-RDCC-1
390084 | CR | 20190216 |  | 4 | Received 4.602.A5 drop 4-7 RWCU PUMP A Trouble | N | N |  | N | YES | <D> **** Detailed Description **** Received 4.602.A5 drop 4-7 RWCU PUMP A Trouble alarm due to low flow. Local flow was indicating greater than alarm set point of 1.5 GPM. Local readings were fluctuating and around 2 GPM as indicated on locally installed ultrasonic flow meter. Flow was momentarily raised per ARP to clear the low flow alarm, the CRD-FCV-512A was returned to the previous position and continued to indicate around 2 GPM as indicated on locally installed ultrasonic flow meter. <I> **** Actions Taken **** Followed ARP | 02-00-CRD-FS-2A
390085 | CR | 20190216 |  | 4 | ASD 1A2 resistivity is low out of spec. | N | N |  | N | YES | <D> **** Detailed Description **** ASD 1A2 resistivity as read on GY-CI-10A2 is LOOS. Its currently reading 4.896 and its minimum spec is 5. This appears to be due to normal usage of the glycol. The other 3 channels are also low but still above 5. Recommend replacing all 4 ASD glycol filters. | 02-00-GY-F-10A2
390086 | CR | 20190216 | CAQ | D | IDS 16 17 Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** IDS 16 17 is not functioning as designed. Contact security for more details. <I> **** Actions Taken **** Security Supervision notified. Initiate CR/WR. Compensatory measures initiated. | 02-00-SEC-IDS-E/S/16/17
390087 | CR | 20190216 |  | 4 | TN05 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** TN05 is not functioning as designed and requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervision notified. Initiated CR/WR. TN05 placed out of service. | 02-00-SEC-TN-5
390091 | CR | 20190216 |  | 3 | Danger Barrier Violation TG 501' West |  |  |  | N | NO | <D> **** Detailed Description **** An individual crossed a danger barrier without properly complying with all entry requirements. The barrier was on TG 501 west to support overhead crane work. The project supervisor notified the shift manager of the event. ISPM -18 requires that "Personnel shall NOT cross Danger flagging, tape, rope, or barricatde without authorization." This person did not have authorization. <I> **** Actions Taken **** Benched individual pending investigation. Initiated actions for all supervisors / manager to communicate the ISPM-18 requirements regarding Danger / Caution barriers. Initiated OI-34 notifications.
390092 | CR | 20190216 | CAQ | C | No Condition provided for potential ODCM RFO 6.2.2.5 case |  |  |  | N | NO | <D> **** Detailed Description **** ODCM 6.2.2.5 "Ventilation Exhaust Treatment System" requires that appropriate portions of the Ventilation Exhaust Treatment System be functional. The only condition (6.2.2.5.A) provided is for gaseous release without treatment when projected organ dose exceeds 0.3 mrem. If RFO 6.2.2.5 is not met solely due to a nonfunctional exhaust filter (i.e., the equipment is not in use or is in use but dose remains below 0.3 mrem) then no compensatory measure is provided which requires use of LCS 1.0.3. <I> **** Actions Taken **** None.
390093 | CR | 20190216 |  | 4 | Monaco Alarms building 26 | N | N |  | N | YES | <D> **** Detailed Description **** SCC received several Supervision and Trouble alarms on the Monaco System. The area was walked down and there was no apparent cause. Contact Security for more details. <I> **** Actions Taken **** The area was walked down and no issues were identified. Shift Manger notified. Initiated CR. <N> **** Equipment Description **** Trouble/Supervision alarms for building 26.
390094 | CR | 20190216 | CAQ | D | IDS 14 15 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** IDS 14 15 requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Compensatory measures initiated. Security supervision notifed. Initiate CR/WR. | 02-00-SEC-IDS-E/S/14/15
390095 | CR | 20190216 |  | 3 | procedure enahancment 4.800.C3 |  |  |  | N | NO | <D> **** Detailed Description **** procedure enahancment 4.800.C3 for drops 1-6, 1-7, 2-6, 2 -7, SOP-ELEC-230KV-OPS, and SOP-ELEC-115KV-OPS. Need direction to reset relay targets and annunciator after condition clears. Alarms and relays will not relatch untill reset. This was seen on the recent 230KV outage.
390096 | CR | 20190217 |  | 4 | Health Physics Break Area Overhead Space Heater Not Working | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** GSB Health Physics Break Area Dayton Space Heater is not working. Equipment Operator did initial Inspection. Did not find any breakers open for heating unit. <I> **** Actions Taken **** CR/WR Initiated. HP Lead Technician Notified. Equipment Operator Initial Waldown Completed. Esoms Entry Completed. <N> **** Equipment Description **** GSB HP Break Area
390099 | CR | 20190217 | CAQ | D | IDS 20 21 Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** IDS 20 21 is not functioning as designed. <I> **** Actions Taken **** Compensatory measure in place, contacted plant electricians for support and generated CR/WR Not reportable. | 02-00-SEC-IDS-E/S/20/21
390100 | CR | 20190217 | CAQ | D | MW 70 High Alarm Rate | N | N |  | N | YES | <D> **** Detailed Description **** MW 70 is not functioning as designed. <I> not reportable. | 02-00-SEC-MW-ISFSI/70R
390101 | CR | 20190217 |  | 4 | CW Chemical Dispersant CF-P-41B Pumping Issues | N | N |  | N | YES | <D> **** Detailed Description **** Trending check of the inventory use for TK-41 and the pump in service, CF-P-41B, indicates that the pump is not pumping enough to maintain residuals. Pump setting are at 95/95. Chemical pump CF-P-42A was placed into service on Thursday 2/14/19 to supplement chemical addition. Inventory trend indicates CF-P-42A is not pumping. <I> **** Actions Taken **** Manually feed 50 gallons per day or as per the direction of chemistry until the pumping issue is resolved. <N> **** Equipment Description **** CF-P-41B and CF-P-42A
390102 | CR | 20190217 |  | 4 | Piping downstream of PWC-V-418 leaking | N | N |  | N | YES | <D> **** Detailed Description **** Through wall leak on piping downstream of PWC-V-418 <I> **** Actions Taken **** Informed SSS, initiated CR <N> **** Equipment Description **** Wellhouse #2 (Bldg. 40); piping downstream of PWC-V-418
390103 | CR | 20190217 | CAQ | D | SE ISFSI Camera Tower High Alarm Rate | N | N |  | N | YES | <D> **** Detailed Description **** TVSFSSET Junction Box Tamper High Alarm rate. <I> **** Actions Taken **** Compensatory measure in place, contacted plant electricians for support and generated CR/WR. <N> **** Equipment Description **** SE ISFSI Camera Tower
390104 | CR | 20190217 |  | 3 | Recommended enhancement to ABN-FIRE |  |  |  | N | NO | <D> **** Detailed Description **** ABN-FIRE has a step to contact Security CAS to monitor the card reader log for accountability. The CAS phone number is not programmed into the control room CRS-EP phone. Add the CAS number (2036/2891) to the procedure. <I> **** Actions Taken **** None.
390105 | CR | 20190217 |  | 4 | RRA-EUH-6 fan does not run | N | N |  | N | YES | <D> **** Detailed Description **** When the disconnect for RRA-EUH-6 in the Rx Building truck bay is energized and/or the air curtain fan is started, RRA-EUH-6 fan does not run. May be blown fuses and not a relay or temperature setting issue, due to RRA-EUH-5, 7, 8 fans will run and provide heat to truck bay. Please investigate. Although not labeled, Starting on the west end of the south row of heaters, RRA-EUH-6 is the second fan on the south wall. <N> **** Equipment Description **** Rx 441 truck bay, 15 feet off floor | 02-00-RRA-EUH-6
390106 | CR | 20190217 | CAQ | C | TEA-RIT-13 IMDS Update |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of ISP-TEA/PRM-X301 WO#02105303-01, the high voltage power supply for channel 2 was adjusted from 1776 to 1796 per work instructions in order to achieve the desired transfer ratio. <I> **** Actions Taken **** Performed HVPS adjustments per work instructions and initiated a CR to update TEA-RIT-13 Ch. 2 High Range Gross Detectorâ€™s IMDS â€œModify HVPSâ€ value. All as left values were satisfactory. <N> **** Equipment Description **** WEA-RIT-13 RW 525
390107 | CR | 20190217 | CAQ | D | Rattle Snake Rattlesnake Mountain facility - on Backup Power | N | Y |  | N | YES | <D> **** Detailed Description **** Rattle Snake Rattlesnake Mountain facility is currently running on backup generator power. At ~1400 on 2/17/2019 alarms were received regarding the Rattlesnake facility on Rattlesnake Mountain. Security contacted the IS Duty Officer and Facilities to report the alarms. IS Duty officer contacted the telecom supervisor who reached out to Benton PUD. Benton PUD dispatched workers to the Rattlesnake facility to investigate the issue. Work is ongoing at the rattlesnake facility and will likely continue tomorrow morning 2/18/19. Rattle Snake Rattlesnake Mountain facility is currently running on backup generator power. Security has been updated, MCR has been contacted, in addition EP has been informed of the situation. Updates will be provided as more information is obtained. Please contact the IS Duty officer if you need further information or have any questions. <I> **** Actions Taken **** Contacted Benton PUD they are working the issue Contacted Security, EP, and MCR. Contacted IS Telecom Analyst to confirm all tenants are on backup power. Update - - Power was restored at 1440 to the Rattlesnake Facilities on Rattlesnake Mountain. Benton County Road Dept will start snow removal tomorrow afternoon 2/19/2019 to ensure access can be regained to the Rattlesnake Facilities. There is a potential for a repeat failure due to not being able to adequately access and address the cause of the issue, they were able to reset/restart the power from a remote station on the mountain. Facilities, IS Leadership, Security, and OPS have been updated on the current state of power as of 1500 on 2/18/2019. <N> **** Equipment Description **** Rattlesnake Facility Power Benton PUD cleared line fault aand reset breaker.
390108 | CR | 20190217 |  | 4 | FD-SUMP-T2 pillows need replaced. | N | N |  | N | YES | <D> **** Detailed Description **** while performing rounds it was noted that the FD-SUMP-T2 pillows looked to be half way submerged so they need replacing. <I> **** Actions Taken **** Initiate CR and WR, inform CRS. | 02-00-FD-SUMP-T2
390109 | CR | 20190218 | CAQ | D | High Alarm Rate SEC-MW-61 | N | N |  | N | YES | <D> **** Detailed Description **** CAS is receiving a high alarm rate on SEC-MW-61 for unknown reasons. Request electrical support to investigate. <I> **** Actions Taken **** Compensatory measures initiated; CR/WR Generated | 02-00-SEC-MW-ISFSI/61CR
390110 | CR | 20190218 |  | 3 | PPM 10.2.235 step needs correction. |  |  |  | N | NO | <D> **** Detailed Description **** Step 7.8.2.f of PPM 10.2.235 incorrectly identifies Yoke to Adaptor Plate mounting bolts as 3/4"-10 hex head cap screws with a torque of 170 ft-lbs. The step should identify the Yoke to Adaptor Plate mounting bolts as 1-1/4"-8 with a torque value of 650 ft-lbs. Ref CVI OMM 818-00,6 pages 30 and 32. <I> **** Actions Taken **** Identified discrepancy, verified OMM and CVI drawings, consulted with Crane Nuclear SME, and wrote this CR. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
390111 | CR | 20190218 |  | 4 | CAS-C-1A modification PMT failure | N | N |  | N | YES | <D> **** Detailed Description **** Post Maintenance testing of the modification to prevent a loss of power from causing an over temperature trip of CAS-C-1A failed. The steps are documented in work order task 02128861-05. The loss of power was simulated by opening the disconnect for CAS-C-1A for 30 seconds to verify that the over temperature light was not lit when power was restored. The over temperature light was found ON and the over temperature trip had to be reset to clear the compressor trip alarm. CAS-C-1A was in STOP when power was cycled to ensure it did not auto-start just before the disconnect was opened. <I> **** Actions Taken **** Returned CAS-C-1A to standby. CAS-C-1A remains available since it has demonstrated all the capability it had before the modification. | 02-00-CAS-C-1A
390112 | CR | 20190218 | CAQ | D | IDS 24 25 Constant Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** IDS 24 25 is not functioning as designed. <I> **** Actions Taken **** Compensatory measure in place, contacted plant electricians for support and generated CR/WR. | 02-00-SEC-IDS-EVAL/24/25
390113 | CR | 20190218 | CAQ | D | (NRC Identified) Snow melt leaking into DG building | Y | N |  | N | YES | <C> Duplicate of CR 390116 <D> **** Detailed Description **** Snow melt is leaking into the roof openings of the diesel generator building. There is a large puddle of water on the upper platform under the exhaust pipe for DG-2. The collecting water is pooling on this upper elevation and running down the wall seal to the lower elevations. Some puddling of water is occurring in the 441 DG corridor. There was no indication that the water was impacting the Operability of functionality of the DGs. Pictures included in EDMS <I> **** Actions Taken **** Mopped up the puddles on the 441, posted wet floor signs, and informed HP and the laborers of the issue. Operations will continue to monitor the issue for further complications | 02-00-D-BLDG-MISC
390114 | CR | 20190218 | CAQ | D | Unable to complete Step 7.1.18 for OSP-SW-M102 |  |  |  | N | NO | <D> **** Detailed Description **** While performing OSP-SW-M102, procedure Step 7.1.18 was unable to be completed due to the red â€˜KEEP OFFâ€™ tag on the scaffold access ladder. The ladder is necessary to gain access to the room cooler for the MC-8BB Room at RB 572â€™. In the past, it was possible to visually see SW-V-112 in the overhead of the room from the floor inside the room. However, that is no longer possible because of scaffold planking blocking the view of SW-V-112. Now the only safe access to visually check the valve position is from outside the room and through the double fire door access. Operations Supervision was unable to contact the proper scaffold personnel in an attempt to find out why the red tag is in place. <I> **** Actions Taken **** informed Shift Supervision of issue Surviellance late date is 2/27/19. Step was completed on 2/18/19. The surveillance has been successfully completed. <N> **** Equipment Description **** scaffold access ladder outside MC-8BB Room, Rx 572.
390115 | CR | 20190218 | CAQ | D | (NRC Identified) Capture nut for rod on SW-EJ-1A loose | Y | N |  | N | YES | <D> **** Detailed Description **** SW-EJ-1A has 4 threaded rods that hold the assembly together. Each threaded rod has two capture nuts on each side of the expansion joint to lock the threaded rod in place. One of the capture nuts on one of the threaded rods was finger tight and could be spun by hand. <I> **** Actions Taken **** Verified that the similar assemblies for SW-P-1B (SW-EJ-1B) and HPCS-P-2 (SW-EJ-2) as well as the remaining capture nuts on SW-EJ-1A were more than finger tight and could not be spun by hand. There was no indication of leakage from the joint with the loose capture nut or from any of the expansion joins examined. None of the Standby Service Water systems were in service at the time of the inspection but there was no indication of any past leakage from any of the joints examined. | 02-00-SW-EJ-1A
390116 | CR | 20190218 | CAQ | D | (NRC identified) Roof leak into Diesel Space | Y | N |  | N | YES | <C> Trended to CR 390113 <D> **** Detailed Description **** NRC identified Water leaking into the Diesel Exhaust Piping room and running down the wall and onto the Diesel Corridor floor. <I> **** Actions Taken **** Supervision Notified AR/WR generated Wet floor sign placed in the general area of Diesel Corridor. <N> **** Equipment Description **** Roof Leak into Diesel space and Diesel Corridor
390118 | CR | 20190218 | CAQ | D | Residual Pressure Found While Working FP-AO-SGT/56 | N | N |  | N | YES | <D> **** Detailed Description **** While performing take 2 prior to commencing work on the air operator for FP-V-SGT/56 it was noted that PI-SGT/6B2 was reading approx. 100#, this is on the upstream side of FP -V-SGT/56. Reccomend removing the pressure gauge and bleeding off pressure from this point. This will determine if this indication is due to locked in pressure and if there is any leakby in the system. <I> **** Actions Taken **** Stopped work, consulted CRS/SM. | 02-00-FP-PI-SGT/6B2
390119 | CR | 20190218 |  | 4 | CAS-C-1A continuously leaking air while shutdown. | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1A was not running and was found to be leaking air and its sump pressure was about the same as the CAS header pressure (108 psig). The check valve CAS-V-284A may have been stuck open. CAS-C-1A was started and the leak stopped. Recommend investigating the cause of the leak and fixing. <I> **** Actions Taken **** Started CAS-C-1A | 02-00-CAS-C-1A,02-00-CAS-V-284A
390124 | CR | 20190219 |  | 4 | Lights need replaced on TB 471 West side | N | N |  | N | YES | <D> **** Detailed Description **** WR 29140960 was created in January 2018 to replace lights on TB 471 West Side. Several lights were replaced on 1/24/19 and the WR was closed. However, there are still over 10 lights that are not functioning. This CR and work request are to document these lights for replacement or repair . 3 florescent lights are still out or flickering 7 of 14 lights in the mezzanine area are out 1 of 3 lights above the IBD enclosure is still out <I> **** Actions Taken **** Informed Electrical Maintenance Non-essential lighting <N> **** Equipment Description **** TB-471 West
390126 | CR | 20190219 |  | 4 | Plateau unavailable |  |  |  | N | NO | <D> **** Detailed Description **** Plateau CBT was not responding to requests for access and was not available for Training. <I> **** Actions Taken **** The condition of Plateau was verified and the service which runs Plateau was confirmed online with the the application not responding. The service was restarted and the Plateau returned to service. No additional actions required. Request NON-CAQ 4.
390128 | CR | 20190219 |  | 3 | Incorrect weld detail on ladder support drawing S679-2 |  |  |  | N | NO | <D> **** Detailed Description **** Weld Detail on drawing S679-2 detail D-2040 needs to be corrected to show a plug weld not a square groove. The ladder supports are being constructed under WOT 02125361 This has no impact on any installed lader supports This is a updating of the weld detail to AWS standard <I> **** Actions Taken **** The was identified by QC during the weld Inspection
390129 | CR | 20190219 |  | 3 | R24 procedure change to SOP-ELEC-SH6-MAINT |  |  |  | N | NO | <D> **** Detailed Description **** EC 17480 (Alternate Power for Radwaste Building Elevator 4). This EC provides a permanent alternate power to the Radwaste Building Elevator (MTELEV- 4) during the E-SL -63/SH-6 bus outage. The normal power supply for MT-ELEV-4 at MTDISC- 6B2D will be transferred to the new alternate power supply at MT-DISC-3D2D via a manual transfer switch MT-MTS-6B/3D located near E-MC-6B and E-MC-3D during the E-SL63/SH-6 bus outage. SOP-ELEC-BOP-TEMPPOWER section 5.5 and 5.6 needs to be deleted and steps added to SOP-ELEC -SH6-MAINT. Per the EC this transfer is only allowed in Mode 4/5. <I> **** Actions Taken **** wrote CR
390135 | CR | 20190219 |  | 3 | ZINC-TK-1 contents may be expended | N | N |  | N | NO | <D> **** Detailed Description **** The FW Zinc concentration has been trending down steadily since 2/4/19. In response to the lowering zinc values, the flow rate through ZINC-TK-1 has been raised from 40 gpm up to the current value of 60 gpm. This steady trend down in FW Zinc indicates that the depleted Zinc pellets in ZINC -TK-1 may be completely expended. A total of 30 kg of Zinc was added to the zinc skid in R23 and projected to last until R24. The calculated usage based on the average FW zinc concentration and FW flow is 26.7 kg as of 1/31/19. The cause of additional zinc use is unknown at this time. WO 02113446 for adding Depleted Zinc is already planned and ready to work, however it is coded R24. This work order should be recoded to DAILY and scheduled appropriately. This will require planning to add clearance order tasks and increase the scope to include removal of the column vessel head and basket for inspection to determine the remaining inventory of depleted zinc per OMM 869-00,4 section 5.2. A sufficient amount of zinc should be added upon reassembly to last until R25. This will preclude the need to perform this work in R24. Note, the scaffold has already been built for this work order in preparation for the outage. <I> **** Actions Taken **** Informed Chemistry supervision and management.
390138 | CR | 20190219 |  | 4 | RW elevator not working. | N | N |  | N | YES | <D> **** Detailed Description **** The RW elevator is indicating it is on the 525 elevation and not responding to commands. Resetting logic fixed the issue. Trending CR. <I> **** Actions Taken **** Dispatched EO to reset logic. It worked. <N> **** Equipment Description **** RW 437-525 | 02-00-MT-ELEV-4
390139 | CR | 20190219 | CAQ | D | SGT-TS-2B1/2 AF for the high switch oot | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing calibration of SGT-TS-2B1/2 (02105443-01) the AF trip for the HIGH switch was OOT high by 1 DEG. <I> **** Actions Taken **** Informed Supervisor and calibrated switch back into tolerance. Created CR for Trending
390143 | CR | 20190219 |  | 4 | THOR ABORT DURING EP DRILL ON 02/19 |  |  |  | N | NO | <D> **** Detailed Description **** SIMULATOR WENT TO FREEZE AUTOMATICALLY DUE TO THOR ABORT. EP DRILL WAS INTERRUPTED FOR 15 MIN.
390144 | CR | 20190219 |  | 3 | Misfiled Drawings in TSC |  |  |  | N | NO | <D> **** Detailed Description **** During the Team C drill, two drawings were found misfiled in the hard copy files. This make finding the desired drawings more difficlult. Suggest the hard copy files be reviewed to ensure all drawing have been properly filed. <I> **** Actions Taken **** Refiled the two drawing that were out of place. <N> The drawers of EWD drawings located in the TSC were gone through to ensure that the drawings were in numerical order. As a result, there were approximately 23 drawings that were either duplicate revisions or old revisions. The duplicate/old revisions have been removed from the files. No further actions required.
390145 | CR | 20190219 |  | 3 | Mechanical Craft OSC Craft Lead computuer - Asset Suite | N | Y |  | N | NO | <D> **** Detailed Description **** During ERO Drill, the OSC Craft lead Mechanical craft computer, would not allow for loading Asset Suite. When the Network Icon was clicked, then the Asset Suite it would give an error. Contacted the Computer Eng in the drill in which the installation of the Asset suite was not sucessful. <I> **** Actions Taken **** Generated CR. This occurred on several machines based on the drill critique.
390146 | CR | 20190219 |  | 3 | TSC Fax Issue during drill |  |  |  | N | NO | <D> **** Detailed Description **** During the drill the TSC fax machine would not transmit to the drill scenario number (377-3699) provided. 3 attempts were made and an alternate number was obtained to complete the fax. <I> **** Actions Taken **** Obtained an alternate fax number. This is a drill number only and is not required per PPM 13.14.11.
390148 | CR | 20190219 | CAQ | D | Intermittent fail alarm on rad air monitoring unit in TSC | N | Y |  | N | YES | <D> **** Detailed Description **** Emergency Plan rad air monitering unit in the TSC has an intermittent fail light. TSC-CP-RAD/1 effluent rad monitor, in the TSC, used for emergencies, had intermittent fail lights on iodine channel(TSC-RIS-1B) during the EP drill. <I> **** Actions Taken **** talked to HP supervisors and created a Work request <N> **** Equipment Description **** TSC-RIS-1B
390149 | CR | 20190219 | CAQ | 3 | EWD'S for MSIV's have errors |  |  |  | N | NO | <D> **** Detailed Description **** EWD-1E-048, 049, 50, 51 and EWD-1E-052, 053, 054, 055 line diagram for MSIV test solinoid at G7 on drawing states "energize to test open MS-V-***" this is incorrect, pressing the test pushbutton energizes the solenoid to close the MSIV. the drawings should be updated. this is a drawing issue only. <I> **** Actions Taken **** wrote CR
390151 | CR | 20190219 | CAQ | C | EWD's for Outboard MSIVs do not match E555 drawing |  |  |  | N | NO | <D> **** Detailed Description **** EWD-1E-052, 053, 054, 055 list Fuse AA-F01 as B22H-F10A and fuse BB-F02 as B22H-F12A. this does not match E555-E-CP -H13/P623. The E555 drawing lists the fuses as B22H-F10B and B22H-F12B. . The EWD's listed need to be updated to match the E555 drawing. <I> **** Actions Taken **** Wrote CR
390152 | CR | 20190219 |  | 3 | Pump and fittings for 6.5.22 location unknown |  |  |  | N | NO | <D> **** Detailed Description **** During the ERO Drill on 2/19/19. we were asked to use the ERO Tech support document "CRD Insertion Using an External High Pressure Pump" the document says to use the pump and fittings purchased for PMM 6.5.22. the location for the pump and fittings is not known. The system engineer was contacted and did not know were the pump and fittings were located. this pump and fittings needs to be located or repurchased and the location needs to be listed in the ERO tech support document and/or 6.5.22 <I> **** Actions Taken **** Wrote CR <N> Originator discussed w/ Eng. & discovered that the equipment was mode 4/5 equipment, not missing or expected to be staged on location. It was verified to not be EP equipment (refer to PPM 13.14.11). No deficiency in completing EP functions related to this issue. Equipment is not credited in EP-01 (Emergency Plan), vol.13 procedures (emerg. response), EP Instruction, or EPC (EP Checklist). PPM 6.5.22 (mode 4/5 - Rx fuels) is the only Controlled document assoc. w/ this CR that refers to this equip. Rec. non-caq
390153 | CR | 20190219 |  | 4 | Drill Comms made w/out the preface "This is a drill" |  |  |  | N | NO | <D> **** Detailed Description **** Drill Comms made w/out the preface "This is a drill". There were a couple of PA announcements and 2 Alert Tones that were made without making the prior statement "This is a Drill". There was also a phone call made to the actual Main Control Room instead of the Simulator. <I> **** Actions Taken **** Immediately informed the EP controlller phone network. Made an update coaching announcment in the TSC & OSC. Recommend non-CAQ, level IV.
390154 | CR | 20190219 |  | 3 | Federal EIA reports in jeopardy due to Java version update |  |  |  | N | NO | <D> **** Detailed Description **** The Energy Information Agency (EIA) requires under federal law that electrical generators report generation data on a monthly and annual basis. Currently, ENW is unable to submit EIA reports on the EIA site due to issues related to Java versions. Current workarounds for the EIA-923M (monthly generation report) consist of simple emails to EIA staff who manually enter information from ENW. However, no workaround currently exists for EIA-860, EIA-923A, and EIA-923S reports, which are annual reports with much more extensive user interfaces and input fields. Without access to EIA data entry tools, ENW would have to pursue manual workarounds for these as well. This creates significant risk of mis-entry of federal database reports and jeopardizes ENW's timely submittal. These reports are currently due on 3/4, 3/20, and 3/25. Information Systems help ticket is #0037791. <I> **** Actions Taken **** Initiated CR. Provided EIA troubleshooting guide to IS. Discussed with IS. Submitted help tickets.
390156 | CR | 20190219 |  | 4 | PWC-V-355 leak by while caution tagged shut | N | N |  | N | YES | <D> **** Detailed Description **** PWC-V-355 is leaking by as indicated by constant water flow out of broken PWC-SEW-10. PWC-V-355 was caution tagged shut to isolate the safety shower on 2/14/19 and there was no indication of leakage by PWC-V-355 at the time. See attached video for current conditions. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-PWC-V-355
390164 | CR | 20190220 |  | 3 | ERO team Organizational Effectiveness during drills |  |  |  | N | NO | <C> CR reopened by decision of the MRT on 2/25/19 and assigned as a severity level 3 to AR-EMERP. <D> **** Detailed Description **** During the 02/19/19 Team C ERO drill, there were examples where the OSC Team could have had improved performance. Monitoring radio traffic of Ops crew members prior to them being assigned to the OSC, informing those same Ops crews and repair Teams of changing radiological conditions. Best practices to be shared with all Teams include HP and Chemistry doing screenshots of eDNA dose rate data at the start of the drill to facilitate trending as conditions change. Whether new Team members are in their first drill, or some from different Teams are filling in, those and other best practices from the four individual ERO Teams should be captured and shared with all Teams to help members be plug and play, and establish ERO excellence. This could be accomplished via an annual meeting of the 4 Team members of each OSC position to establish best practices, and sustained by positional learnings being shared among similar members after each ERO drill and then discussed at pre-drill briefings. <I> **** Actions Taken **** Provided HP Evaluator comments post-drill.
390174 | CR | 20190220 |  | 3 | Plan contingency task for WO 02117675 |  |  |  | N | NO | <D> **** Detailed Description **** Planning to perform a contingency task on WO 02117675, WMA-42-8f1b starter coil replacement. Contingency is to replace E-RMS-FRTS5 (Part ID 24910B). In addition, a CatID will need to be generated by planning to allow procurement of the switch. <I> **** Actions Taken **** Planning and Electrical Maintenance notified, work removed from the 2/25/19 work week.
390177 | CR | 20190220 |  | 3 | Windows Forced Restart During ERO Drill |  |  |  | N | NO | <D> **** Detailed Description **** During the team charlie ERO drill on 2/19/2019, one of the engineering work stations was forced to restart to apply a requied windows update. The update disrupted completion of the task being worked on, and caused a delay of several mintures to install the update and reboot the computer. Recommend changing the windows update policy to allow deferment of these upgrades to prevent recurrence. <I> **** Actions Taken **** Discussed task interuption caused by forced restart during drill critique. Initiated CR as directed by team charlie leadership.
390178 | CR | 20190220 |  | 4 | Degraded lanyard orange plastic strap |  |  |  | N | NO | <D> **** Detailed Description **** While installing new â€œRaise The Barâ€ card to lanyard I noticed the orange plastic strap had severely degraded. Pictures in EDMS show that the orange plastic strap had nearly cracked through which could potentially have caused an FME issue or loss of employee badge. Recommend others to verify the integrity of their lanyard orange plastic straps. <I> **** Actions Taken **** Notified supervisor and others in our group. At least one other individual had signs of cracking on their orange plastic lanyard strap.
390180 | CR | 20190220 | CAQ | D | FP-V-SGT/61 has packing leak. | N | N |  | N | YES | <D> **** Detailed Description **** FP-V-SGT/61 has a packing leak when closed. This valve is normally open, but was closed for a clearance hang. Please adjust/replace packing. Leak is approx. 1 drop/5 secs. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RB 572 on wall behind RCC surge tank. | 02-00-FP-V-SGT/61
390181 | CR | 20190220 |  | 4 | E-MC-5M ground indication lights showing possible ground | N | N |  | N | YES | <D> **** Detailed Description **** On OPS4 tour found all ground indication lights for E-MC-5M out indicating a ground. There is no current trouble alarms in MCR, Changed light bulbs. <I> **** Actions Taken **** Changed groudn fault bulbs, informed MCR. Initiated AR & WR. | 02-00-E-MC-5M
390184 | CR | 20190220 |  | 3 | PPM 12.9.10 contains potential PCSC error |  |  |  | N | NO | <D> **** Detailed Description **** PPM 12.9.10 step 8.3.1 contains information to open SW-V -154G to provide flow to the SSW corrosion rate monitoring station after a complete shutdown of the system. This step should be modified to state to open SW-V-154G three (3) turns (to provide alignment with SOP-SW-LU). PPM 12.9.10 Step 8.8.7 is correct and has this information currently. PPM 12.9.10 Step 8.9.4 states to document the number of turns required to close SW-V-154G. While this step is not incorrect, it should not be needed IF SW-V-154G is always 3 turns open. In comparison, SOP-SW-LU states SW-V-154G is throttled 3 turns open and is correct. This is a potential Plant Component Status Control (PCSC) issue that must be resolved. Fully opening SW-V-154G will change the service water flow to PRA-CC-1B which is throttled to maintain PRA-CC-1B Operability. This condition was identified during Stakeholder reviews of EC 17441 Service Water Biofouling Monitor installation. <I> **** Actions Taken **** Notified Supervisor.
390185 | CR | 20190220 |  | 4 | Valve installed in 2003 did not meet Limitations on Use | N | N |  | N | YES | <D> **** Detailed Description **** During planning for the replacement of MS-V-110B on WO 02134730, it was identified that the valve installed in 2003 under WO 01054000 did not have the proper documentation required by the Limitations on Use for CAT ID 54206362. AR EVAL 390182 has been written for evaluation of valve currently installed. Further review identified that MS-V-110A was replaced using the same valve under WO 00BPR8. <I> **** Actions Taken **** Discussed issue with Procurement Engineering, notified Supervision, Contacted Shift Manager, Initiated AR EVAL 390182 and wrote this CR. | 02-00-MS-V-110B
390187 | CR | 20190220 |  | 3 | ERO Qual Group Clarification |  |  |  | N | NO | <D> **** Detailed Description **** On 2/16/2019, shift RP technicians encountered a question regarding the shift qualifications for the oncoming crew. Specifically, an individual showed qualifed in PQD for qual groups HCAA and EPAI but did not have the SCBA practical required for the PA04 qual group. HPI-0.17 section 6.9.5 only requires HCAA and EPAI to cover minimum staffing for shift coverage. HPI-0.17 does not make reference to the PA04 qual group. Since PQD showed the individual qualified for both HPAA and EPAI, it was determined that he was fully qualified to assume shift responsibilities. . The question remaining is whether the EPAI qual group should have shown as "not qualified" if the requirements for the PA04 qual group were not met. This question may also exist for all ERO positions that require the ability to don SCBAs. <I> **** Actions Taken **** Reviewed ISPM-17 and HPI-0.17 for qualification requirements. The shift technicians contacted HP supervision, and it was determined that the individual was qualified in accordance with the listed requirements for minimum staffing. The shift crew verified this decision with the SSS to ensure minimum staffing was met.
390188 | CR | 20190220 | CAQ | D | E-B0-2B Average Specific Gravity too low | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** E-B0-2B Average Specific Gravity too low Average Specific Gravity came to 1.2053. The Criteria was to be Greater than1.207. Per work instruction 4.7 of WO 02134475-01 if the average is less than 1.207 but Greater than 1.2050 then the battery needs to be placed on equalize per PPM 10.25.234 (see WO) <I> **** Actions Taken **** report findings to supervision. initiate CR initiat WR <N> **** Equipment Description **** E-B0-2B
390189 | CR | 20190220 |  | 3 | Revise ABN-RHR-SDC-LOSS |  |  |  | N | NO | <D> **** Detailed Description **** The procedure referenced in the 3rd bullet in step 4.1.8 needs to be changed to SOP-FPC-OPS. <I> **** Actions Taken **** None
390191 | CR | 20190220 | CAQ | D | High water level CRD-HCU-1019 | Y | N |  | N | YES | <D> **** Detailed Description **** Receieved Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-1019. Investigation showed high water level. <I> **** Actions Taken **** Ops 2 drained the water per SOP-CRD-HCU | 02-00-CRD-HCU-1019
390192 | CR | 20190220 |  | 3 | Quarterly CORC Caution Tag Audit (WO 02130378) |  |  |  | N | NO | <D> **** Detailed Description **** Quarterly CORC Caution Clearance Audit 10CFR50.59 The Quarterly CORC Caution Tag Audit (WO 02130378) has documented the caution clearances that have been hanging for GE 30 days. There are 10 new Caution clearances added to this total since the last audit: C-CBD-SR-1(2) -001, C-DW-DWS-4 -002, C-EDR-P-5A/5B -003, C-E-TR-M2/DH/E -001A, C-FP-V-127 -001, C-MS-V-115B -002, C-PWC-LT-100 -002, C -RHR-V-73A -003A, , C-SMA-FN-1 -001, C-TOA-V-T3C -001. Request Technical Services/Systems Engineering Manager (or designee) to determine whether a 50.59 review is required. <I> **** Actions Taken **** Wrote CR.
390193 | CR | 20190220 |  | 3 | Quarterly CORC Danger & Local Tag Audit (WO 02130377) |  |  |  | N | NO | <D> **** Detailed Description **** Quarterly CORC Danger & Local Clearance Audit 10CFR50.59 The Quarterly CORC Danger & Local Tag Audit (WO 02130377) has documented the danger & local clearances that have been hanging for GE 30 days. 10 new clearances have been added to this total since the last audit; D-MT-ELEV-4/AC -001, D-OG-RF-20B -002, L-E-DISC-3D7B -001, L-HS-V-T2K -001, L -HS-V-T2L -001, L-ROA-HC-1/N -001, L-SEA-FN-51 -002, L -TMU-V-7B -001, L-TOA-HC-1B/O -001 & L-WOA-HC-1/K -001. Request Technical Services/Systems Engineering Manager (or designee) to determine whether a 50.59 review is required. <I> **** Actions Taken **** Wrote CR.
390194 | CR | 20190220 | CAQ | D | DSA-PCV Air Leak Trending | Y | N |  | N | YES | <D> **** Detailed Description **** During system walkdown for turnover it is noted that the previously identified air leak is slightly louder than previous. The air is exiting the regulator as the new valve type is self regulating. As previously documented it is postulated that the soft seat in the reagulator may have rust particulate in it causing it not to seat. Maintenance should investigate and replace internals as required during the next opportunity. The air leak is small and should be classfied as insignificant. The leak also does not impact ability of the air compressors to maintain the Air Reciever pressure. <I> **** Actions Taken **** Wrote CR | 02-00-DSA-PCV-37/1A
390195 | CR | 20190220 |  | 4 | Configure RRC-CB-ASD/1B/2 | N | N |  | N | NO | <D> **** Detailed Description **** During inspection step 7.17.4.c. Auxilliary switch contacts as found resistance readings were above acceptance criteria of 1 ohm. <I> **** Actions Taken **** Notified supervisor and replaced auxilliary switch.
390196 | CR | 20190220 | CAQ | D | Anchor missing for deckplate to G203 pump pit | N | N |  | N | NO | <D> **** Detailed Description **** While supporting 'SW POND "B" INSPECTION OF INTAKE SCREENS' it was noted that 1 of the 4 security bolts (Northwest) was not holding as well as the other 3. Upon removal of the plate it was noticed that the concrete anchor is missing. <I> **** Actions Taken **** Notified Control Room <N> **** Equipment Description **** G203 pump pit in SWPH 'B'
390197 | CR | 20190220 |  | 3 | RCC Motor High Temperature | N | N |  | N | YES | <D> **** Detailed Description **** During trending and monitoring for system walkdowns it has been discovered that RCC Motor Bravo has high exhaust temperature. Review started in August when discussions were had to remove the motor replacement from the October RCC work week due to engineering Change not ready. Since August the RCC room temperature decreased slightly from 95F to approx 88F. The air cooled motor is original plant equipment and likely degraded due to dust accumulation internally. The temperature trend on the exauhst air since august has been 188,198,200,202,212 and 214F as measured today with a FLIR which is above the continuous rating of 95C. Consideration should be taken to clean/blow out the internals for the B/C motor or using a spot cooler to temporarily reduce the internal winding temperature. The B motor also shows a slight increase in audible noise as compared to last month. For reference the A motor which has been replaced runs at 136F. The C motor has a higher temperatur of approx 175-185F it is not running currently. The B RCC Pump outboard bearing which has been monitored for high heat 145F the previous 3 months has returned to a lower temperature of 113F as measure through the bearing case. <I> **** Actions Taken **** Contacted SM. | 02-00-RCC-M-P/1B
390198 | CR | 20190220 |  | 4 | Preoutage bench test of MCCBs not completed as scheduled |  |  |  | N | NO | <D> **** Detailed Description **** Documentation only AR. Preoutage bench test of MCCBs not completed as scheduled under WO 02128098-04 due to required M&TE not functional. Schedule C adherence hit and preoutage work can not be completed as scheduled due to nonfunctional primary injection test (PITS) equipment. <I> **** Actions Taken **** Cal lab has been informed and are working a parallel path to obtain a rental unit in conjunction with making repairs to the existing PITS equipment. Working other preoutage tasks that don't require this test equipment. <N> **** Equipment Description **** M&TE equipment located on T471 and the other in the cal lab
390199 | CR | 20190220 | CAQ | C | EWD-50E-030 Drawing Error |  |  |  | N | NO | <D> **** Detailed Description **** This CR is not associated with an equipment issue, the purpose of this CR is to identify an error on drawing EWD -50E-030. Specifically, the drawing incorrectly shows E -MTS-6B/C1/7 connecting to a 120V circuit on E-MC-6B. Per E503-6, this connection is to E-MTS-8A-C1/2B to E-MC-8A at 480VAC. <I> **** Actions Taken **** Initiated CR
390200 | CR | 20190220 |  | 3 | Trend: Behaviors Challenging Meets Commitments |  |  |  | N | NO | <D> **** Detailed Description **** Review of ACEMAN Thumbs Down submissions for 4th quarter 2018 and first half of the 1st Qtr 2019 revealed that â€œmeets commitmentsâ€ was the most significant recurring Individual Excellence attribute. The â€œMeets Commitmentsâ€ items were reviewed and Nuclear Safety Culture codes were applied. Top six codes applied: PA.1B, WP.1B, CO.1C, P .1C, PA.2C and WP.3B are affecting <I> **** Actions Taken **** Uploaded supporting trend validation sheet and data to EDMS, discussed trend with Performance Improvement Manager, initiated CR.
390201 | CR | 20190220 |  | 4 | Late eSOMS entries for Maintenance |  |  |  | N | NO | <D> **** Detailed Description **** Maintenance had 5 late entries: 1 Painter called in for Jury Duty but came to work for 1/2 day; 2 I&C techs worked more than scheduled hours; and 1 Electrician held over on 2 separate occasions without having time entered in eSOMS first. No violations occurred when eSOMS was updated. <I> **** Actions Taken **** Updated eSOMS with correct hours. Notified managers of details of late entries.
390202 | CR | 20190220 |  | 4 | In-Line Conductivity disagree by GT 10% | N | N |  | N | YES | <D> **** Detailed Description **** SP-3, SP-3B, and SP-71 In-Line Recorder conductivity disagrees by GT 10% to the sink grab sample conductivity. SP-3B and SP-71 to In-Line Meter conductivity disagrees by GT 10% to the sink grab sample conductivity. All conductivity cells are still within acceptable limits of 20%. <I> **** Actions Taken **** Informed Supervision. | 02-00-PSR-CE-3A,02-00-PSR-CE-3B,02-00-S-CE-71
390203 | CR | 20190220 |  | 3 | Corporate transfer issue with IEBS computer |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** It was discovered by the IT Analyst, badge data was not transmitting from the IEBS computer. Contact Access Authorization for further details. <I> **** Actions Taken **** Notified Computer Eng and Emerg Serv Mgr. Please assign to org #54211
390204 | CR | 20190220 |  | 4 | Lighting in the Reactor Building | N | N |  | N | YES | <D> **** Detailed Description **** Two lighting fixtures have bulbs that are out on the West side of the reactor building on the 501'. Additionally two lighting fixtures are out on the SE side of the Reactor building on the 471' near E-IR-H22/P010. <N> **** Equipment Description **** West side 501 and SE 471 of the RB
390205 | CR | 20190220 |  | 3 | ePRF app issues |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Invalid qual codes were processed, and an invalid ssn was generated <I> **** Actions Taken **** Invalid Qual codes will be removed by Training Dept, bad ssn has been fixed. Will research specific cause.
390206 | CR | 20190220 |  | 4 | Loss of facilities power at Building 356 Site 4. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** It was reported to facilities that B-356 lost power. Facilities electricians found no tripped breakers in the electrical panels. <I> **** Actions Taken **** Supervisor Initiated W/R 29147191 to investigate electrical problem. <N> **** Equipment Description **** Located at Site 4 Building 356.
390207 | CR | 20190220 |  | 3 | Unacceptable hazard per ISPM-20 for SOP-ELEC-480V-OPS jumper |  |  |  | N | NO | <D> **** Detailed Description **** Jumpers installed per SOP-ELEC-480-OPS for transferring E -SL-11, 21 and 31 back to their normal feeder cannot be performed as written without exposing electrical craft to undue hazard. The procedure sections 5.6, 5.8, 5.11 and 5.12 expose electrical craft to a potential arc flash greater than ARC suit protection can provide per ISPM-20 Columbia Arc Flash Study requirements when the back panel at the breaker must be opened to install the jumper.. Electrical maintenance, Operations, and Engineering met to determine an alternate method to perform the procedure with temporary jumpers. Based on the need to install the jumpers directly on to the â€œBâ€ contacts at the breakers and no viable alternative to meet the logic, there is no temporary jumper solution. A design mod needs to developed to install a keylock or other jumper connection points external to the switchgear. <I> **** Actions Taken **** For R24 and future outages, using the break before make sections of the procedure will result in a power loss during bus transfers which results in cycling equipment power and lighting. However, this portion of the procedure can be performed as written to support R24. For online work, some PMs cannot be performed on line without performing a break-before-make cycle with potential to drop loads that could result in an unplanned power reduction or loss. Two PMs already scheduled on line are affected by this issue. 02135152 E-CB-21/2 INSPECTION scheduled 8/26/19 (T-20) cannot be performed at all and 02109170 E-CB-31/21 scheduled 11/18/19 (work can be performed but PMT cannot). Other PMs associated with SL -11,21, and 31 breakers and transformers are also potentially affected. <N> AR type EVAL needed for requested design modification.
390208 | CR | 20190220 |  | 3 | procedural changes to 12.9.8, Chlorine Analyzer |  |  |  | N | NO | <D> **** Detailed Description **** The following changes for procedural clarity are proposed for 12.9.8, Chlorine Analyzer: Page 5, Step 4.2.2: MOVE substep (h.) up to between substeps (e.) and (f.) CLARIFY substep (i.) to specify amount of 18N sulfuric acid to be added. Page 6, Step 4.2.2: ADD a new NOTE between substeps (i.) and (k.) cautioning user to "Take care to NOT BUMP keypad while wiping the cell interior with a cotton-tipped swab." [performed in substep (k.)] <I> **** Actions Taken **** initiated CR
390209 | CR | 20190220 | CAQ | B | (QA) Elevation - Spare Equipment Preventive Maintenance |  |  |  | Y | NO | <A> Action 15- "OPIT" action was conducted by the owed to group manager and OPIT was reviewed prior to completion by CAP Manager with comments incorporated. Action was later reopened as the original type of action was listed incorrectly as an ASGN. Documentation of this is in the notes tab and all was conducted within the appropriate timeframe. <C> RISK: Medium. CAUSE: Complex/Unclear. Investigation Template Needed. Medium Risk (SWP-CAP-06): Repetitive/recurring conditions associated with a Low Consequence Issue. <D> **** Detailed Description **** (QA) Elevation - Spare Equipment Preventive Maintenance. Quality determined that the corrective actions taken to resolve an Area Requiring Management Attention (ARMA) were ineffective in ensuring the readiness of important spare equipment (AR-CR 389803). As a result, Quality is elevating this issue as required by QSI-2, Quality Oversight Activities for Continuous Monitoring in accordance with QSI-19, Escalation Process. Refer to EDMS for additional details <I> **** Actions Taken **** Discussed this Elevation with the Supply Chain Services Manager, Maintenance Manager and Plant Components Engineering Supervisor
390210 | CR | 20190220 | CAQ | C | FP-AO-SGT/56 new piston seal not like for like | N | N |  | N | NO | <D> **** Detailed Description **** During performance of PM to replace elastomers on FP-AO -SGT/56 it was discovered that the piston seal removed from the actuator is not the same as the new piston seal in the rebuild kit (CID 37300). The original seal removed from the actuator is a double cup seal or lip seal and the new piston seal is a standard O-ring (see attached photos). <I> **** Actions Taken **** Contacted Work Week Manager, Supervisor and Component Engineering
390211 | CR | 20190220 |  | 4 | SWPH-B Ladder incorrectly staged against plant equipment | N | N |  | N | NO | <D> **** Detailed Description **** A ladder in SWPH-B was incorrectly staged against plant equipment (see attached photos in EDMS, IMG 2005, IMG 2010). This ladder was in an approved ladder holding bracket, but it was touching the SW Corrosion Monitoring loop PVC piping. During previous walkdowns of this area the ladder holding bracket has been empty. Currently an 8 foot step ladder is in the holding bracket. The ladder was moved up within the bracket by one step to provide clearance with the PVC piping below. However, it is recommended that the 8 foot ladder be replaced with a 6 foot ladder (or just removed entirely) to avoid any contact in the future with the PVC piping. If an 8 foot ladder is desired for longer term storage in the SWPH-B then consideration should be given to re -locating the ladder holding brackets to a different location (possibly near the entry into SWPH-B, see attached photo in EDMS, IMG 2028). The placement of the ladder was initially documented on a Stakeholder Form 7 during reviews of EC 17441, SW Biofouling Monitor installation. A subsequent walkdown confirmed and corrected the ladder storage (see attached photos in EDMS, IMG 2019, IMG 2022). This ladder storage location in the SWPH-B is on the South Wall and is a Quality Class 1 Seismic Category I area. The SW B Corrosion Monitoring Loop is a Quality Class 2, Seismic Category II. Because the ladder was in the ladder holder, there was no issue/concern with any safety-related equipment. Though found touching the QC 2 SC 2 SW Corrosion Monitoring Loop, there was no apparent impact to its continued function and the condition was corrected immediately. <I> **** Actions Taken **** Notified Supervisor who was performing an observation at the time. Corrected the ladder storage from impacting any plant equipment. Initiated WR associated with this CR to replace the 8 foot step ladder with a 6 foot step ladder or to move the ladder storage brackets (a typical detail allows this without a design change). <N> **** Equipment Description **** SWPH-B South wall
390212 | CR | 20190220 |  |  | (QA) RHR-M-P/2A Determs Incorrectly Documented |  |  |  | Y | NO | <D> (QA) During closeout review, Quality Control identified that determs performed under WOT 02117218-01 for RHR-M-P/2A and motor heaters were documented on incorrect Cable Termination Instructions (CTIs) from implementing EC 14635. CTIs used to document Determs were EC pages D.3-3 and D.3-5, which contain action codes â€œTâ€ for terminations and â€œNCâ€ for no change. Determs were documented on the â€œNCâ€ side of the incorrect CTIs, with cable and termination point details added by craft. CTIs from EC pages D.3-2 and D.3-4 should have been used to document Determs, as referenced in WOT 02117218-01 instruction steps 4.6 and 4.7. . . Craft Supervisor confirmed the â€œNCâ€ section of EC pages D.3-3 and D.3-5 were used to document Determs. Details from EC 14635 pages D.3-2 and D.3-4 for Determs were compared against the termination point details added by craft under the â€œNCâ€ section of EC pages D.3-3 and D.3-5, and determined to be electrically correct. This is an administrative issue and does not affect installed plant equipment. . <I> Notified Quality Services Supervisor, Quality Control Level III and Maintenance Craft Supervisor.
390215 | CR | 20190220 |  | 3 | (SA) ORAT R24 - Objective 1 - Standards Deficiencies / Gaps |  |  |  | N | NO | <D> **** Detailed Description **** D-1: Perform a reevaluation of SDSP Enclosure 3.2.3 and WO 02115595 contingency plans for inclusion of LCO 3.9.8 and LCO 3.9.9 actions Problem Statement: SDSP Enclosure 3.2.3, Secondary Containment Recovery Plan and WO 02115595 need a revision to add an additional â€˜entry conditionâ€™ required by technical specifications. While In Mode 5, if there is a loss of the operable SDC system and an alternate method of decay heat removal is not available, LCO 3.9.8 and 3.9.9 require restoration of secondary containment and isolation of open secondary containment penetrations. However, neither SDSP Enclosure 3.2.3, Secondary Containment Recovery Plan, nor WO 02115595 contain LCO 3.9.8 or LCO 3.9.9 as an entry condition (i.e. the only discussions in the contingency is for a fuel handling accident and uncontrolled loss of reactor cavity inventory). <I> **** Actions Taken **** Notified Outage WC.
390216 | CR | 20190220 |  | 3 | (SA) ORAT R24 - Obj. 1 and 5 - Standards Deficiencies / Gaps |  |  |  | N | NO | <D> **** Detailed Description **** D-2: Reevaluate accuracy and completion of the secondary containment WO and BI instructions for prompt restoration during R24 Problem Statement: Many barrier impairments and/or WO instructions lack the correct verbiage regarding a prompt restoration per the contingency plan. <I> **** Actions Taken **** Notified outage WC.
390217 | CR | 20190220 |  | 3 | (SA) ORAT R24 - Objective 2 - Standards Deficiencies / Gaps |  |  |  | N | NO | <D> **** Detailed Description **** D-1: Incorporation of Tech Spec Changes Related to TSTF -542 Problem Statement: Additional changes are required to PPM 1.20.3 to implement Tech Spec Amendments 249 and 251. The following changes are required (a procedure markup is included in EDMS): â€¢ Attachment 8.1 â€“ Update the shutdown safety matrix to reflect that one ECCS subsystem is required to be operable at all times in Mode 4 and 5 by TS 3.5.2. Also update item 1.5 as required. â€¢ Attachment 8.1 â€“ Revise the shutdown safety matrix note (+) for crediting one operating RHR shutdown cooling subsystem for low pressure coolant injection to eliminate this note in Mode 3. This allowance was removed by TS Amendment 249. â€¢ Attachment 8.1 items 1.3, 1.5, and 1.7 â€“ Clarify the exception for allowing snubber inspection and testing on the operable shutdown cooling and ECCS subsystems (i.e., use of LCO 3.0.8). Also, snubber maintenance and testing needs to be considered for vessel inventory control (item 1.7). â€¢ Attachment 8.1 â€“ Update item 1.7 to reflect the requirements of 3.5.2 for RHR-V-8 or RHR-V-9. Specifically, the definition of drain time requires that at least one valve must be capable of automatic isolation without offsite power available or the penetration must be isolated, or a dedicated operator must be used to isolate the penetration). Additionally, this section should be updated to address the RWCU suction line. <I> **** Actions Taken **** Notified outage WC
390218 | CR | 20190220 |  | 3 | (SA) ORAT R24 - Objective 2 - Standards Deficiencies / Gaps |  |  |  | N | NO | <D> **** Detailed Description **** D-2: Outage Schedule Logical Link Missing Problem Statement: Rev C of the outage schedule for R24 is missing a logical link between two outage schedule activities. SO-0R606-1720 â€œRestore from Alternate Shutdown Cooling to RHR-B Shutdown Coolingâ€ is scheduled for three hours from 0100 to 0400 on May 18th. SO-0R606-OPR â€œRHR Operable Milestoneâ€ is scheduled for 0100 on May 18th. This is an error in the logical linkage of the schedule because during the realignment, RHR B remains INOPERABLE. This appears to be a missing â€œFinish to Startâ€ link for WO 02111877-08 â€œRestore RHR-B from FPC Assist Modeâ€ (finish) to (start) of RHR Operable Milestone. <I> **** Actions Taken **** Notified outage WC
390219 | CR | 20190220 |  | 3 | (SA) ORAT R24 - Objective 5 - Standards Deficiencies / Gaps |  |  |  | N | NO | <D> **** Detailed Description **** D-2: Update and upload instructions for WO 02115619 to eliminate OPDRV guidance and include WIC guidance. Problem Statement: WO 02115619 â€“ WIC (WATER INVENTORY CONTROL) READINESS WORK ORDER R24 â€“ The WO is coded for R24 though none of the instructions under the -01 task are current (all are for R23) and the process that is planned is for OPDRVs rather than WIC. <I> **** Actions Taken **** Notified outage WC.
390220 | CR | 20190220 | CAQ | D | MCR lighting is degraded. 381 lights are out or flickering. | N | Y |  | N | YES | <D> **** Detailed Description **** 41% of the MCR lights are either burnt out or flickering (mostly out). That amounts to 381 bulbs. The back half of the MCR (back 7 rows) has 56% of the lights either burnt out or flickering. The degraded lighting condition has created a substandard environment in the MCR. 13% of the Normal-Emergency AC Lighting Units listed in LCS 1.10.7 are either burnt out or flickering. <I> **** Actions Taken **** All Normal-Emergency AC Lighting Units in the MCR listed on Table 1.10.7-3 of LCS 1.10.7 were verified to have met the requirements of SR 1.10.7.2 as specifically found in step 7.1.10 of PPM 15.2.39. Those requirements are that at least one bulb per emergency fixture is lit. One fixture, E-LF -7FDA/1E, is at the minimum with only one bulb working. <N> **** Equipment Description **** MCR lighting | 02-00-W-BLDG-MISC
390221 | CR | 20190221 |  | 4 | Extension 0113 rings to busy when called and cannot call out | N | N |  | N | YES | <D> **** Detailed Description **** This is the intercom in the MCR bathroom. From NUREG 0700 section 10.2.6-2 Point-to-Point Intercom Systems Intercom systems should be provided to interconnect the control room with important plant areas and other areas where control room or operating personnel might be. Additional Information: Areas served by intercoms might include the Shift Supervisor's Office, Plant Security Office, operators' lounge, locker rooms, and restrooms. A person in distress in the restroom may not be able to recieve help in a timely manner without the intercom system <I> **** Actions Taken **** After attempting to contact indvidual using the intercom and was unable. Wrote this CR. | 02-00-W-BLDG-MISC
390222 | CR | 20190221 |  | 4 | MT-ELEV-4 fault | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-4 was locked out and the controller indicated 'Brake did not lift" alarm. System Fault Reset was pressed and the elevator functioned as expected. This fault has been written up previously in AR #390018. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-MT-ELEV-4
390223 | CR | 20190221 |  | 4 | 29147078 needs to be coded as a front panel MCR alarm |  |  |  | N | YES | <D> **** Detailed Description **** This alarm goes off 20 to 30 times a shift some days. It is a front panel alarm and is not coded as such in the nuclear screen. As such it is not getting the attention needed for silencing. Please mark this as a MCR front panel alarm, or OPS distraction, or burden and fix it. This should be worked while the temperature is low and cooling tower fans can be removed from service with minial impact to generation <I> **** Actions Taken **** Wrote this AR to help focus attention on an item that should be included in the OPS aggregate. <N> **** Equipment Description **** E-CB-61/6M CA code has been added to the WR 29147078 Nuclear panel problem type.
390224 | CR | 20190221 |  | 4 | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0064720 Fluke Module- model 700P00 1in found OOT. Not used during Calibration cycle. No Plant Impact. Rejected- Unable to adjust. DEF #6949A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
390225 | CR | 20190221 |  | 4 | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065172 Fluke Thermocouple Probe- model 80T-150UA Had Broken Tip but Passed as Received Data. Un-economical to Repair. Rejected. No Plant Impact. DEF #6950A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
390226 | CR | 20190221 |  | 4 | CAS/ SAS PTZ Camera Control | N | N |  | N | YES | <D> **** Detailed Description **** The PTZ camera function in CAS/SAS needs maintenance. Contact security at ext. 2185 for further details. <N> **** Equipment Description **** Central and Secondary alarm stations
390232 | CR | 20190221 | CAQ | D | FDR-P-18B discharge piping leak | N | N |  | N | YES | <C> CR reopened to cross reference additional WO 02118121, then taken back to complete <D> **** Detailed Description **** FDR-P-18B discharge piping has a substantial leak (discharge pressure was indicating 20 psi, see attached video). RWCR was notified and switched to the other FDR -SUMP-T5 pump <I> **** Actions Taken **** Notified RWCR and MCR. | 02-00-FDR-P-18B
390233 | CR | 20190221 |  | 4 | X Ray- 3 | N | N |  | N | YES | <D> **** Detailed Description **** X-Ray-3 stopped working and has a red indicator light lit up on the control panel. | 02-00-SEC-XR-3
390234 | CR | 20190221 |  | 4 | Fast pressure or power status alarm received for E-TR-M2 | N | N |  | N | YES | <D> **** Detailed Description **** Received email notification from operations staff that they had received the fast pressure annunciator for E-TR-M2 on night shift. This is the same alarm identified in AR-CR 3888842. The purpose of this CR is to document the alarm being received by the control room. Based on the email the local alarm was reset and no lights were illuminated on the sudden pressure relay. <I> **** Actions Taken **** Uploaded email to EDMS. | 02-00-E-MON-M2/63S
390239 | CR | 20190221 |  | 3 | (QA) ARMA - Operator Performance in Training | N | N |  | Y | NO | <D> Operator performance in training has not met Operations or Training Management expectations over the previous three years. Actions taken by Operations and Training had limited success and do not demonstrate sustainable excellent performance. In order to ensure success, Operations collaborated with Quality Assurance to provide independent corporate oversight to assess future corrective actions and verify the actions are effective and sustainable. See EDMS for full Memo. <I> Informed Operations Manager, Training Manager and Quality Manager. <N> Recommend assignment to Operations Manager.
390240 | CR | 20190221 |  | 3 | Recommendation - PEC Parking Lot Designated Walkways |  |  |  | N | NO | <D> **** Detailed Description **** A number of individuals have been observed to take pathways from the PEC Main Parking Lot to the PAAP entrance that are not marked or designated as a walkway (particularly from the 1st and 2nd aisles). These unmarked pathways are not regularly maintained walkways and may have ice or other trip hazards present. Moreover, walking through unmarked pathways may result in a vehicle accident. <I> **** Actions Taken **** Generated CR. . Recommend a broadcast EN News article and communication in the monthly safety meetings address this behavior. . Additionally, recommend designated pathways be marked from the 1st, 2nd, and 3rd parking aisles to the PAAP entrance. Snow/Ice removal plans and maps will need to be updated with these new pathways. See EDMS for proposed map. <N> **** Equipment Description **** Parking Lot (not plant equipment) . A message to remind personnel to use the designated walkways has been added to the D15 safety message for 2/27/2019.
390242 | CR | 20190221 |  | 3 | OJT/TPE Guide CH001160 Requires Revision |  |  |  | N | NO | <D> **** Detailed Description **** Task Title: Obtain and prepare a gas sample for tritium; PQD Code: CH001160; Qualification Program: Chemsitry Technician; Identified Issue/Suggested corrective actions: OJT/TPE guide CH001160 requires a revision to ensure that the performance steps align with the correct steps within the current procedure. <I> **** Actions Taken **** CR generated to track revision.
390244 | CR | 20190221 | CAQ | C | *Trending and Monitoring* Administrative issue | Y | N |  | N | NO | <D> **** Detailed Description **** Calculation ME-02-02-25 and ME-02-02-27 used the incorrect total stroke length to calculate design stroke times and the number of handwheel turns. The calculations used stroke length input from vendors. One vendor stated the stroke lengths were â€œbased on historical data for that particular type of valve. In reality, this valve could be slightly different. However, for the most part, the values for lift should be close enough for use in the calculation.â€ ** This issue was identified by comparison between design stroke time and actual field stroke time. The applicable stroke lengths were confirmed via previous WOâ€™s (i.e. actuator refurbishments and diagnostic testing). The applicable valves are SLC-MO-1B, RRC-MO-16A/16B, RHR-MO -48A/48B, RHR-MO-24A/24B, MS-MO-16 and AS-MO-V/68A and V/68B. ** ME-02-02-25 and ME-02-02-27 along with the applicable MOV Master data sheets need revised with the correct stroke length. ** <I> **** Actions Taken **** This is administrative. The field stroke times were compared to FSAR/TECH Specs and were found to be acceptable. The stroke times are also monitored via IST and are within the acceptance criteria. ** Attached in EDMS shows the applicable documentation for the actual stroke lengths.
390245 | CR | 20190221 |  | 4 | CW-CT-2A requires cleaning due to high level. | N | N |  | N | YES | <D> **** Detailed Description **** CW-CT-2A distribution plenum level is at 12". This requires that an AR/WR be generated to clean the upper deck. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** CW-CT-2A | 02-00-CW-CT-2A
390247 | CR | 20190221 | CAQ | B | FLEX-CAB-4 Unsat | N | Y |  | N | YES | <C> Risk: Medium - Repetitive/recurring conditions associated with a low consequence issue. Cause: Unclear Severity "B" with investigation template required. . As per the MRT on 2/26/19 the owed to group changed to AR-PPROG. <D> **** Detailed Description **** Per OSP-FLEX-A106 FLEX-CAB-4 is missing the following items: *Two (2) 8-foot round slings (10 ton capacity each) *Two (2) 8-foot nylon slings (1/2 ton capacity each) *Two (2) 4-foot nylon slings (1/2 ton capacity each) *Two (2) shackles (2 ton capacity each) *Eight (8) Web sling protectors In addition, FLEX-HOI-6 is incorrectly labled as FLEX-HOI-4 Finally, the cabinet has two 3 foot slings that are not mentioned in the inventory. <I> **** Actions Taken **** Informed MCR Informed Site Rigging Coordinator Event investigation requested by the Shift Manager due to entry into LCS and previous corrective actions for FLEX equipment not being in the correct location ineffective. Performance improvement is taking the lead to determine process and behavior improvements. <N> **** Equipment Description **** FLEX-CAB-4, RB 471 South
390251 | CR | 20190221 |  | 3 | Editorial Change ESP-B02A-B101 Bat Chgr Load Tst 02107899-01 |  |  |  | N | NO | <D> **** Detailed Description **** Editorial Change ESP-B02A-B101 Battery Charge Load Test (24 month) 02107899-01 Attachment 9.3 (pg. 14 of 16) â€“ BCT battery Test Configuration Lists, under TEST SETUP, Test Type: Service Test. The type of service test we are performing is a Modified Performance test which allows us to set the following parameters: Temperature: F Cell Voltage: 2 Correction: None In 2017, when this was last performed, this same correction had to be made. See EDMS document of old Pg. 14. Contacted Engineer (Robert Roman) and confirmed that nothing had changed and that this is what the service test type still should read Modified Performance. <I> **** Actions Taken **** Electrical Maintenance Supervisor informed. <N> **** Equipment Description **** ESP-B02A-B101 Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
390252 | CR | 20190221 | CAQ | D | OIL WEEP ON FILTER LINE CONNECTION TO ENGINE | Y | N |  | N | YES | <D> **** Detailed Description **** THE OIL LINE GASKET WHERE IT MEETS THE ENGINE BLOCK NEEDS TO REPLACED. DURING DG3 RUNS IT HAS BEEN OBSERVED THAT OIL WEEPAGE ORIGINATED FROM THIS LOCATION. ALTHOUGH IT IS CONSISTENT AND NOT CURRENTLY INCREASING IT SHOULD BE REPAIRED DURRING THE DG3 MAGOR MAINTENANCE IN JAN 2020. OIL RUNS DOWN THE ENGINE AND IS APPARENT ON THE ENGINE DRIVEN PUMP DIRECTLY BELOW THE LEAK SOURCE. <N> WR for investigation/repair? | 02-00-DLO-F-1
390253 | CR | 20190221 | CAQ | D | (QA) RHR-M-P/2A Determs Incorrectly Documented |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) During closeout review, Quality Control identified that determs performed under WOT 02117218-01 for RHR-M-P/2A and motor heaters were documented on incorrect Cable Termination Instructions (CTIs) from implementing EC 14635. CTIs used to document Determs were EC pages D.3-3 and D.3-5, which contain action codes â€œTâ€ for terminations and â€œNCâ€ for no change. Determs were documented on the â€œNCâ€ side of the incorrect CTIs, with cable and termination point details added by craft. CTIs from EC pages D.3-2 and D.3-4 should have been used to document Determs, as referenced in WOT 02117218-01 instruction steps 4.6 and 4.7. . Craft Supervisor confirmed the â€œNCâ€ section of EC pages D .3-3 and D.3-5 were used to document Determs. Details from EC 14635 pages D.3-2 and D.3-4 for Determs were compared against the termination point details added by craft under the â€œNCâ€ section of EC pages D.3-3 and D.3-5, and determined to be electrically correct. This is an administrative issue and does not affect installed plant equipment. . . <I> **** Actions Taken **** Notified Quality Services Supervisor, Quality Control Level III and Maintenance Craft Supervisor. . Correct CTIs (EC pages D.3-2 and D.3-4) have been printed, signed by craft and QC and uploaded to DataGlance under WOT 02117218-01. No further action required.
390254 | CR | 20190221 | CAQ | C | IMDSs associated with EC-13094 are not issued |  |  |  | N | NO | <D> **** Detailed Description **** The Instrument Master Data sheets for the new HCV system installed under EC-13094 have not been issued. Example is HCV-RIS-RAD/1. The IMDS are needed for new procedure and work order development. <I> **** Actions Taken **** Initiated CR, this is an administrative issue. Maintenance on HCV-RIS-RAD/1, PMID 26676-01 scheduled due date is 5 -4-19 with current start date of 8-6-19.
390255 | CR | 20190221 |  | 4 | Remove RP000001 from SCBA Qual Group - PA04 |  |  |  | N | NO | <D> **** Detailed Description **** Respiratory Protection Training (RP000001) and Safety-4.5 SCBA (RP000002) are both currently required for the SCBA qual group. Respiratory Protection Training (RP000001) covers all respirators including cartridge type filtered respirators, bubble suits and to some extent SCBAs. Safety-4.5 SCBA (RP000002) is specific respirator training for SCBA users. The requirements need to be specific to the applicable type of respirator. <N> RP000001 is required for all respirators regardless of type of respirator. Respirator specific training is in addition to RP000001. No further action is required.
390256 | CR | 20190221 |  | 3 | No PM initiated for new HCV-TT-1 and HCV-TI-1 | N | Y |  | N | NO | <D> **** Detailed Description **** HCV-TT-1 and HCV-TI-1 were installed under EC-13094 but no AR-SMS has been generated to determine planned maintenance that needs to be performed for the new instrumentation. Consequently new procedure and work orders have not been generated. <I> **** Actions Taken **** Reserved 10.27.120 for calibration of the new instruments and initiated CR. This is an administrative issue. <N> AR-SMS 391755 has been generated for Maintenance Procedures to generate the PMs. The AR is now re-assigned to the group (Maintenance Procedures). .
390257 | CR | 20190221 | CAQ | C | No PM initiated for new HCV-RD-54 and 60 | Y | Y |  | N | NO | <D> **** Detailed Description **** HCV-RD-54 and HCV-RD-60 were installed under EC-13094 but no AR-SMS has been generated to determine planned maintenance that needs to be performed for the new rupture discs. Also it is unclear if they had been added to the IST program. The rupture discs need to be replaced at least every five years. <I> **** Actions Taken **** Initiated CR, this is an administrative issue. <N> AR SMS 392086 has been generated to begin the process of developing the PMs associated with Rupture Discs HCV-RD-54 and HCV-RD-60. This AR is now assigned to the Maintenance Procedure group to generate the PMs. .
390258 | CR | 20190221 |  | 3 | could not verify correct Rev of MSAU card |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WOT 02118365-02, could not verify the correct Rev of replacement MSAU card for IRM-H (REV 17). <I> **** Actions Taken **** Contacted supervisor, Scott O'Conner and Engineering, to find resolution. Engineering has contacted GE to verify this card is the correct REV. Returned the part to stores until the issue is resolved and will reschedule the replacement. <N> Email from GE confirmed that the markings on the replacement MSAU card were for the required revision 17 version. Emails are attached to the EDMS. No further action is required to obtain a different card.
390260 | CR | 20190221 | CAQ | C | Extent of Condition Identifies Non Compliance with IST | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of an Extent of Conditon under AR 386998, it was discovered that manual valves SW-V-75AA and SW-V-75BB are not meeting the full requirements of the IST Program to verify obturator movement during valve exercising. This verification ensures that a stem to disc seperation has not occurred in these manual valves. Exercising of these valves on a 2 year frequency per the IST Program has occurred, however, the surveillance does not include the necessary acceptance criteria to ensure the valve disc has moved to its required position. This CR is being written to document the non-compliance and to drive resolution of this issue. Recommend C to AR-PPROG. <I> **** Actions Taken **** Wrote CR, discussed with Supervisor and System Engineers and contacted control room. <N> .
390263 | CR | 20190221 |  | 3 | Outage procedure milestone not met |  |  |  | N | NO | <D> **** Detailed Description **** An engineering change is being implemented that will add overcurrent protection to three Westinghouse model DS-632 circuit breakers. The maintenance procedure, PPM 10.25.2, that inspects those breakers does not currently include instructions on how to test and adjust the components. Although the EC identified that PPM 10.25.2 would require a revision, no assignment was created to notify the maintenance procedure group. The pre-installation inspection of the first modified circuit breaker is scheduled for the week of March 25th in support of replacing the breaker in R24. Recommend assignment to maintenance procedure group to revise PPM 10.25.2. Marked up copy of procedure has been uploaded to EDMS Docs. <I> ENG-DES-50 does not include reference to Standard Design Process (SDP) guidance on theCurrent for creation of PROC assignments for affected procedures (Design Guidelines > PROCEDURE CHANGES). This appears to be why the PROC assignments for EC CC 17061 were not created. See AR CR 390280 (ENG-DES-50 lacking applicable Guideline references). Also see existing AR CR 387436 (Assignments not created for procedure changes tied to ECs). PROC AS 373133-14, PROC AS 373133-15, and PROC AS 373133-16 for EC CC 17061 have been initiated. . <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
390264 | CR | 20190221 |  | 3 | Intent of PM not met for FP-AO-SGT/56 | Y | N |  | N | NO | <D> **** Detailed Description **** Due to parts issues documented in ARCR 390210, the piston seal could not be replaced and the old piston seal had to be reused with Engineering concurrence. Although the old seal was in excellent condition, this does not meet to intent of the PM work order to replace elastomers on FP -AO-SGT/56. This PM will be need to be regenerated to satisfy the scope. <I> **** Actions Taken **** Wrote CR
390267 | CR | 20190221 |  | 4 | Operations Vehicle (F350) steering issues |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The Operations Department Vehicle (F350) is showing signs of power steering degredation. The steering wheel is abnormally difficult to rotate in both the right and left directions. The power steering pump is crying out louder than normal when turning the steering wheel. No power steering fluid leak could be found and Vehicle Maintenance verified the power steering fluid reservoir to be at a normal level. No obstructions/debris were seen at the front axles. Vehicle Maintenance has been informed of the issue and will schedule further investigation. The truck is still driveable. This AR/WR generated for documentaion and to track resolution. This vehicle is utilized for B .5.B. <I> **** Actions Taken **** Informed Vehicle Maintenance. Verified no power steering leaks and normal resevoir level. <N> **** Equipment Description **** Operations Vehicle - F350
390268 | CR | 20190221 | CAQ | D | low specific gravity following load test on E-B0-2A | Y | Y |  | N | NO | <C> CR reopened to add completion required check. <D> **** Detailed Description **** Per work order 02107899-01, and ESP-BO2A-B101 step 7.1.33, A CR and Work Request must be generated due to required intry into LCS 1.8.6.1M following discharge test if the specific gravity of any cell is below 1.195 or the average of all cells is below 1.205. each cell is above 1.195, However the calculated average is only 1.1975. Battery will be placed into equalize charge once E-C0-2A comes out of current limit. The Work Request for tracking equalize charge is 29147224 <I> **** Actions Taken **** Notified CRS, Supervisor and Write CR <N> **** Equipment Description **** E-B0-2A Vital Island Battery Room #2
390269 | CR | 20190221 | CAQ | D | FP Wet System 13 Water Motor Gong | N | N |  | N | YES | <D> **** Detailed Description **** Personnel performing work around the CWPH found the FP Wet System 13 sprinkler system water motor gong laying on the ground outside of the CWPH. It is assumed ice from the roof made conact with the gong and broke the gong. . Due to the position of the water motor gong in the system, FP suggests isolating the system at FP-V-223 to avoid any flooding of CWPH. <I> **** Actions Taken **** Intiated FPSI 19-0057, intiated CR, contacted SM. <N> **** Equipment Description **** CWPH | 02-00-FP-V-223,02-00-FP-V-W13/240
390270 | CR | 20190221 |  | 3 | small leak on GY water filtration system | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Found a very small leak on the GY-F-10A1 system. Changed filters and are unaware as to whether the leak is resolved as of yet <I> **** Actions Taken **** Contacted control room to make them aware of the possible situation. <N> WR for investigation/repair?
390271 | CR | 20190221 |  | 3 | Relocate Refuel Floor Kelly Building AED |  |  |  | N | NO | <D> **** Detailed Description **** In the near future, prior to R-24, the lower level of the Refuel Floor Kelly Building will be receiving a much needed makeover. This includes new furniture and cabinets for the Refuel RP Techs. Currently the Kelly Building AED resides inside an RP Supply cabinet along with a First Responders duffle bag. This cabinet is being removed from the Kelly Building as part of said makeover. Request the AED be relocated and installed on the west wall of the Kelly building between the SW elevator and the storage closet. Just above the elevator call button would be a perfect location. Instead of being tucked away inside of another cabinet, this would also make the AED much more visible and accessible in the unfortunate event that its duty is called upon. <I> **** Actions Taken **** Initiated WR and uploaded picture of location into EDMS file for reference. <N> **** Equipment Description **** Refuel Floor Lower Level Kelly Building AR-EVAL 390447 intiated and cross referenced to evaluate the move of AED located in the Rx 606 Kelly Building.
390274 | CR | 20190221 |  | 3 | Incorrect torque and disassembly requirements for WO |  |  |  | N | NO | <D> **** Detailed Description **** WO 02120348-10 has steps to disassemble the Level transmitter and upon reassembly torque the cage to cage head bolts to 120ft-lbs and the arm flange to torque tube flange to 130ft-lbs. This torque is different than the manufacturer recommendation. Ref CRâ€™s 348999 and 349423 previously written to capture the needed changes. Also disassembly is not required. This was discussed with planner to make the necessary changes to reflect in the current WO. WO 02087143-10 was performed with the correct work steps and torque values.. <I> **** Actions Taken **** CR generated for documentation , update associated WOâ€™s to reflect necessary requirements.
390275 | CR | 20190221 | CAQ | D | CCH-CR-1B oil level high during run | Y | Y |  | N | YES | <D> **** Detailed Description **** CCH-CH-1B oil level is specified to be above the lower sight glass but not above 1/2 up the upper sight glass. Level was found, while the chiller was running (note that it was in purge at this time), at about 80% up the upper glass. CRS informed the maintenance supervisor, it was checked and postulated it may be due to low load and it would get checked again on days. If possible it may be of interest to included a 'unloaded band' for oil level in the surveillence. | 02-00-CCH-CR-1B
390276 | CR | 20190222 |  | 4 | Alarm on CWPH-B HVAC panel | N | N |  | N | YES | <D> **** Detailed Description **** PMA-FN-51 LOW DIFFERENTIAL PRESSURE Red light still lit on panel indicating fan was running. Also observed air flow coming from duct. Fan unit on roof is completely eclosed, not allowing visual inspection of the fan/ motor. <I> **** Actions Taken **** Informed MCR | 02-00-PMA-FN-51
390277 | CR | 20190222 |  | 4 | Puddle found underneath DW-V-100/55 | N | N |  | N | YES | <D> **** Detailed Description **** During a walkdown of the RHR-A pump room, DW-V-100/55 was found to be leaking and a two square foot puddle of water was found on the floor underneath the valve. The valve is in a high rad area so a leakage rate was not performed. Demin water makeup to the suppression pool (which uses DW -V-100/55) was secured a day and a half earlier. This valve is the isolation valve for the RHR-A room Demin Water hose connection. The valve was taken in the closed direction, but very little movement was observed. I was unable to determine if the valve was leaking by the seat or the manual valve was slightly open. <I> **** Actions Taken **** Wrote CR and informed CRS | 02-00-DW-V-100/55
390280 | CR | 20190222 |  | 3 | ENG-DES-50 lacking applicable Guideline references |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing AR CR 390263 to determine what likely occurred, it was determined that ENG-DES-50 is lacking at least some references to applicable Standard Design Process (SDP) Guidelines existing on theCurrent. For example, references to EC Module Guidelines > AFFECTED DOCUMENT LIST (ADL), Design Guidelines > CALCULATIONS, and Design Guidelines > PROCEDURE CHANGES do not currently exist in ENG-DES-50. These lack of guidance references in ENG-DES-50 means there is no link for the procedure user for the guidance or procedural requirement per ENG-DES-50 to perform the guidance provided. Please update ENG-DES-50 to reference the applicable Guideline references it is currently lacking. Please also update EC Module Guidelines > AFFECTED DOCUMENT LIST (ADL) to indicate the type of assignment for procedures and new calculations (type PROC and type CALC respectively). It is also recommended that Design Guidelines > CALCULATIONS be updated to remove its current direction for initiation of an AR CR for CMR deferrals. These should be tracked via a CALC assignment associated with the project AR EVAL. . This is an administratie process issue - recommend resolution assignment to the Procedure Sponsor for ENG-DES-50 (Design Engineering).
390281 | CR | 20190222 |  | 4 | CF-P-42A discharge is clogged | N | N |  | N | YES | <D> **** Detailed Description **** With CF-P-42A running, discharge pressure is approximately zero, with no chemicals injecting to the CW basin. Suspect chemicals hardened in piping or debris is clogging the discharge path. <I> **** Actions Taken **** Informed CR. Batch adding 50 gallons on nightshift. | 02-00-CF-P-2A
390282 | CR | 20190222 |  | 4 | Bldg 26 - Broken outlet cover for exterior 120VAC recepticle | N | N |  | N | YES | <D> **** Detailed Description **** The outlet cover for the exterior 120VAC recepticle existing outside the south central entrance to Building 26 (a.k.a. Plant Engineering Center (PEC) or Deschutes Building) is broken. Please replace. Photos are attached to the EDMS of this AR CR 390282. <N> **** Equipment Description **** Building 26 - PEC / Deschutes Building
390283 | CR | 20190222 |  | 4 | Installed temporary hoses do not comply with SWP-MAI-02 | N | N |  | N | YES | <D> **** Detailed Description **** Two iInstalled temporary hoses in the CWPH observed that do not comply with SWP-MAI-02 or SWP-CM-02. Neither is labelled with any field identification (e.g., with a Hose Tag per SWP-MAI-02 or as a PCTC per SWP-CM-02). 1) Blue hose from CF-V-833 to CW C bay. CF-V-833 is currently CLOSED. 2) Coiled braided hose from CL-V-100. CL-V-100 is currently OPEN. See the photos attached to the EDMS of this AR CR 390283. <N> The Hose connected to CF-V-833 is controlled per SOP-CW-CHEM and is connected on step 5.10.2.a and removed on step 5.10.2.f. Therefore it does not need a hose tag per SWP -MAI-02 5.2.16.b.3 . The hose attached to CL-V-100 is work in progress for the new dehalogenation skid and isnâ€™t turned over to OPS yet | 02-00-CF-V-833
390284 | CR | 20190222 |  | 4 | CWPH east exterior 120VAC outlet cover is broken off | N | N |  | N | YES | <D> **** Detailed Description **** The cover for the CWPH east exterior 120VAC outlet (south of P-DOOR-B109) is broken off. Moisture has intruded into the 120VAC outlet intended to be protected by the cover. See the photos attached to the EDMS of this AR CR 390284. | 02-00-P-BLDG-MISC
390286 | CR | 20190222 | CAQ | C | PM extension frequency | Y | N |  | N | NO | <D> **** Detailed Description **** The following PM's should not have been extended: PM 12225-02 SW-MO-12A LUBE/INSPECT, FULL PM PM 12226-02 SW-MO-12B LUBE/INSPECT, FULL PM The SMS was not routed to the component engineeer for approval which would have rejected the PM from moving from 2 years to 4 years. These valves are cycled excessively and require the 2 year PM. Diagnostic test data shows that these valves need the 2 year PM performed (especially the stem lubrication). This PM also supports the high unseating loads on SW-V-12A. Additionally, these PM's support assumptions in the MOV calcualation such as stem coefficient of friction and Rate of Loading. There is no justification for moving the PM's to 4 years. These were originally scoped into the outage. The decision was to perform the work prior to the outage. This work needs to be performed in the 2 year time frame.
390287 | CR | 20190222 |  | 4 | unable to close COND-V-1077E. Wedge may be cocked | N | N |  | N | YES | <D> **** Detailed Description **** Tried to shut valve to do a Backwash/Precoat. Got to ~90% open and couldn't move valve further without mechanical advantage. Moving the handwheel like a "knocker" valve makes a metallic popping sound inside the valve body. That is why I think the wedge is cocked. I have successfully "straightened out" wedge gate valves at home using a sledge on the valve body while moving the handwheel. <I> **** Actions Taken **** Wrote this WR/CR and notified control room This valve is required to be closed during the BW/PC of the CFD. If the valve cannot be operatord, then the plant will be operating with only 5 CFDs (and occasional 4 cfds). This has been added to the PCL / WCI-09 Text. | 02-00-COND-V-1077E
390288 | CR | 20190222 | CAQ | D | ISFSI SE TV TOWER TAMPER | N | N |  | N | YES | <D> **** Detailed Description **** CAS received an ISFSI SE TV TOWER TAMPER ALARM and it remained in constant. <I> **** Actions Taken **** Security Compensatory measure in place, contacted plant electricians for support and generated CR/WR <N> **** Equipment Description **** SE ISFSI TV Tower
390289 | CR | 20190223 | CAQ | C | Bldg. 82 Inventory | N | Y |  | N | YES | <D> FLEX-TRLR-1 is missing items in compartments 1H2, 1H3, 1A11, and 1B8. Fuel level in FLEX-GEN-B-82 and FLEX-VEH-4 is less than recommended level. <I> Informed CRS, initiated CR | 02-CM-FLEX-GEN-B-82,02-CM-FLEX-TRLR-1,02-CM-FLEX-VEH-4
390290 | CR | 20190223 |  |  | Bldg. 82 Inventory |  |  |  | N | YES | <D> Items missing from FLEX-TRLR-1 compartments 1H2, 1H3, 1A11, and 1B8. Fuel level in FLEX-GEN-B-82 and FLEX-VEH-4 less than recommended level. <I> Notified CRS and initiated CR | 02-CM-FLEX-GEN-B-82,02-CM-FLEX-TRLR-1,02-CM-FLEX-VEH-4
390293 | CR | 20190223 |  | 4 | CW Bay netting has holes in it. | N | N |  | N | YES | <D> **** Detailed Description **** CW Bay has netting over it to protect from getting debris in it. the holes are mostly in the area the temp acid hose is by. there are also several wear holes around where the goose necks are. Please replace or repair. <I> **** Actions Taken **** WR/CR <N> **** Equipment Description **** CW Bay netting.
390294 | CR | 20190223 |  | 4 | CW-CT-2C covered stairs roof is damaged allowingbirds & poop | N | N |  | N | YES | <D> **** Detailed Description **** CW-CT-2C covered stairwell roof is damaged allowing pigeons access to the stairwell and they have been pooping all over the stairwells and handrails. they have several areas of the hand rails unusable. | 02-00-CW-CT-2C
390295 | CR | 20190223 |  | 4 | BUS SL-21 Ground alarm. | N | N |  | N | YES | <D> **** Detailed Description **** SL-21 ground alarm due to E-MC-2B. OPS3 reset the ground relay and the alarm is clear. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-E-MC-2B
390296 | CR | 20190223 | CAQ | D | Received RPIS or DMM INOP and RDCS INOP alarms. | Y | N |  | N | YES | <D> **** Detailed Description **** Received RPIS or DMM INOP, H13-P603.A7.1-7, alarm accompanied by ROD DRIVE CONTROL SYS INOP, H13-P603.A7.2-8, alarm. Reset RDCS per P603.A7 drop 2-8. "RPIS OR DMM INOP" (H13-P603.A7.1-7) & "ROD DRIVE CONTROL SYS INOP" (H13 -P603.A7.2-8) alarms are clear. RWM reinitialized. See EDMS for pictures of H13-P616. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-DMM-1
390298 | CR | 20190223 |  | 3 | OSP-FLEX-A106 step needs clarification, Bldg 600 | N | N |  | Y | YES | <D> **** Detailed Description **** Step 9.3.1.e references verifying all loose sound powered phone cases and SCBA's are strapped down. There are no SCBA's so this has the individuals searching for them when they dont exist. Or do they and they are missing. <I> **** Actions Taken **** please evaluate and clarify. <N> **** Equipment Description **** OSP-FLEX-A106
390299 | CR | 20190223 | CAQ | C | OSP-FLEX-A106 Discrepancies with step 9.3.2 ,bldg 600 | N | Y |  | N | YES | <D> **** Detailed Description **** OSP-FLEX-A106 Discrepancies with step 9.3.2: John Deere Wheel Loader was not present initially but it is required to have a tow hitch. It does not have one currently on it. Flex-VEH-5 ispare Propane canister couldnt be found. <N> **** Equipment Description **** Flex Equipment bldg 600
390300 | CR | 20190223 | CAQ | C | OSP-FLEX-A106 bldg 600, checking the expiration date of oil? | N | Y |  | N | YES | <D> **** Detailed Description **** OSP-FLEX-A106 inventory has you checking the expiration date of oil on page 12? no expiration date for the oild was found. Nor was the following bullet on the same page "Tote with gasoline stabilzer" nope no stabilizer there. <I> **** Actions Taken **** cr <N> **** Equipment Description **** BLDG 600 Flex
390301 | CR | 20190223 | CAQ | C | OSP-FLEX-A106 Storage rack C Shelf C3 doesnt have a keybox | N | Y |  | N | YES | <D> **** Detailed Description **** OSP-FLEX-A106 Storage rack C Shelf C3 doesnt have a keybox, but the inventory sheetm says there should be one there. there is a key box in Bldg 600 not there but it only has one key and thats for the dump truck. <I> **** Actions Taken **** cr <N> **** Equipment Description **** BLDG 600
390302 | CR | 20190223 | CAQ | C | OSP-FLEX-A106, FLEX-TRLR-2 missing stuff (Bldg 600) | N | Y |  | N | YES | <D> **** Detailed Description **** OSP-FLEX-A106, FLEX-TRLR-2 missing stuff (Bldg 600) -4 x 4 2 1/2 tee for RHR supply mislabeled as FLEX-CONN -Water4 vice ....WATER6. - missing one of three fire hydrant wrenches (page 15) -Missing 2 of 8 4-5" spanner wrenches (page 15) -missing B.5.b 5" to 6" NH Storz suction adapter (page 16) -missing 2 1/2" x 4" Storz adapter (page 16) - Missing 1 of 3 head lamps (page 16) -3 3/4" -7/8" combination wrenches are not combination wrenches but 3 of each wrench. -missing one of two 5" x6" adapter to wye suction <N> **** Equipment Description **** Flex equipment
390303 | CR | 20190223 | CAQ | C | OSP-FLEX-A106 BLDG 600 missing equipment | N | Y |  | N | YES | <D> **** Detailed Description **** OSP-FLEX-A109 BLDG 600 missing equipment on page 12 the two 12 AWG 50 foot extension cords were unable to be found (SOP-FLEX-120V220V-GEN-OPS) <I> **** Actions Taken **** cr <N> **** Equipment Description **** flex bldg 600
390305 | CR | 20190223 | CAQ | D | HCU 18-59 accumulator trouble alarm | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7for CRD-HCU -18-59 low pressure. Ops 2 re-pressurized per SOP-CRD-HCU. <I> **** Actions Taken **** Re-pressurized. <N> **** Equipment Description **** RB 522 | 02-00-CRD-HCU-1859
390306 | CR | 20190224 |  | 4 | RW 487' Floor Degradation is Causing a Tripping Hazard | N | N |  | N | NO | <D> **** Detailed Description **** -Some of the flooring degradation on RW 487' is causing a tripping hazard. This is a safety concern and needs to be addressed. <I> **** Actions Taken **** -Notified Shift Manager -Notified Supervision via e-mail -Setup Floor Signs with Caution Signs attached to alert workers in the area. <N> **** Equipment Description **** RW 487' outside Hot Machine Shop
390310 | CR | 20190224 | CAQ | C | OSP-FLEX-A106, B-82 no exp date on oil, no Stable | N | Y |  | N | YES | <D> **** Detailed Description **** OSP-FLEX-A106, B-62 requires you to check the expiration date on the oil in Bldg 62 (page 20), but there is no expiration date listed on the oil. There also is no gasoline stabilizer in the storage area listed. please fix procedure and missing equipment. <I> **** Actions Taken **** cr <N> **** Equipment Description **** OSP-FLEX-A106, B-62
390311 | CR | 20190224 | CAQ | C | OSP-FLEX-A106, B-82 missing bolts,nut,boots | N | Y |  | N | YES | <D> **** Detailed Description **** OSP-FLEX-A106, B-62 is missing ABN FSG-NSRC-001 equipment (bolts, nuts, boots). as listed on the inventory of storage rack b shelf B2. page 21. <N> **** Equipment Description **** OSP-FLEX-A106, B-82
390312 | CR | 20190224 |  | 3 | OSP-FLEX-A106, B-82 and 600 FLEX-BERM-1 thru 6 removed | N | N |  | N | YES | <D> **** Detailed Description **** OSP-FLEX-A106, B-82 and B600 flex berms were removed and replaced with a berm around the area that contains the spill. tehy are no longer a large plastic catch pan. there fore they can no longer meet the requirement of that listed in the inspection on page 31 step 9.7.1 verify the berm is located underneath the equipment. additionally i dont believe they are labeled like the ones they replaced. <I> **** Actions Taken **** wr/cr <N> **** Equipment Description **** OSP-FLEX-A106, B-82 and BLD 600
390313 | CR | 20190224 |  | 3 | OSP-FLEX-A106, B-82 FLEX-VEH-6 has no need for propane | N | N |  | N | YES | <D> **** Detailed Description **** OSP-FLEX-A106, B-82. FLEX-VEH-6 on page 33 says it needs a spare propane tank at 100% full. This is a manula pallet jack as listed in portal J and also verified it is a manual pallet jack and has no need for propane. please correct inventory. <I> **** Actions Taken **** cr <N> **** Equipment Description **** OSP-FLEX-A106, B-82 FLEX-VEH-6
390314 | CR | 20190224 | CAQ | C | OSP-FLEX-A106 Plant Equip, Location of bkrs questioned | N | Y |  | N | YES | <D> **** Detailed Description **** OSP-FLEX-A106 Plant Equip, Location of bkrs questioned. E-EQ-BDB416/1200/1 and E-EQ-BDB416/1200/2 were both inspected sat. But the requirements for the inspection on page 37 step 9.11.1 state to verify that the "item is greater than 3 feet from surrounding seismic interfaces with other components". E-EQ-BDB416/1200/1 is stored less than one foot from 480 volt breaker lifting trolly and next to the Breaker arc chute storage box. E-EQ-BDB416/1200/2 is approximately less than 1 foot below E-CP-HCV/1. Please evaluate if this is the best place to store them, designate a spot and change the step so we arent quessing if its OK where we find them. <I> **** Actions Taken **** cr <N> **** Equipment Description **** OSP-FLEX-A106
390315 | CR | 20190224 | CAQ | D | RPS TEST BOX FAILED TO EXTINGUISH | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of ISP-RPS-Q906 CFT, step 7.1.35, the RPS test box failed to extinguish. It was connected to terminals 2 and 4 of RPS-RLY-K4B. <I> **** Actions Taken **** Stopped and informed CRS and Shift manager. Worked with operations to confirm that RPS-RLY-K4B was pulled in, annunciators and computer points were in expected states. Permission was granted to continue with procedure and no Half SCRAM occurred when leads were removed | 02-00-RPS-RLY-K4B
390316 | CR | 20190224 | CAQ | D | OSP-FLEX-A106 Bldg-600 vehicle/generator fuel not full | N | Y |  | N | YES | <D> **** Detailed Description **** OSP-FLEX-A106 page 32 requires that that equiment vehices fuel be verified full. Flex-GEN-B-600 and FLEX-VEH-3 (dump truck) were not full. please fill them. <N> **** Equipment Description **** Blg 600
390317 | CR | 20190224 | CAQ | D | Malfuntion IDS 24 25 | N | N |  | N | YES | <D> **** Detailed Description **** CAS Received a Malfuntion Alarm on IDS 24 25 due to water in the area. <I> **** Actions Taken **** Compensatory measure in place, contacted SM and plant electricians for support and generated CR/WR. | 02-00-SEC-IDS-EVAL/24/25
390318 | CR | 20190224 |  | 4 | PW leak. | N | N |  | N | YES | <D> **** Detailed Description **** At 1900 on 2/24/19, a PW leak was noticed by security north of CW-CT-2B. The leak was isolated with PWC-V-323 and PWC-V-531. PWC-V-322 would have most lkely been an isolation closer to the leak, but it was unable to be located due to water and snow on the ground. This leak isolates water to BLDG 13, the CWPH, and the Kootenai/Klickitat bldgs among others minor bldgs. <I> **** Actions Taken **** Isolated leak. Called out facilities to assist. Informed chemistry halogenation is affected until PW is restored to the CWPH. <N> **** Equipment Description **** Outside the CWPH | 02-00-PWC-V-322
390319 | CR | 20190224 | CAQ | D | HCU 50-47 high water. | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-50-47 was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear. <I> **** Actions Taken **** cleared high water <N> **** Equipment Description **** rb 522 | 02-00-CRD-HCU-5047
390320 | CR | 20190224 | CAQ | D | SP-1 Cond Element >10% from Grab Sample | N | Y |  | N | YES | <D> **** Detailed Description **** SP-1 Cond grab sample is >10% from meter and recorder readings. Adjustment is required. <I> **** Actions Taken **** CR and WR written. Chemistry supervision and MCR/SM/CRS informed. | 02-00-S-CE-1
390321 | CR | 20190225 | CAQ | C | RWCU precoat tank overflowed. | N | N |  | N | YES | <D> **** Detailed Description **** During a Backwash/Precoat of RWCU-DM-1B, the RWCU precoat tank overflowed. ABN-RAD-SPILL was entered due to the radioactive spill. The spill was stopped by securing RWCU-P-4 (precoat pump). About a quarter inch of water is on the floor. <I> **** Actions Taken **** HP informed. Evacuated the area. CSCO generated for configuration control. Initial investigation identified this as a Human Performanc error and not equipment issue. <N> **** Equipment Description **** RW 467 | 02-00-RWCU-P-4
390326 | CR | 20190225 |  | 4 | Records not submitted IAW SWP-SEC-11 |  |  |  | N | NO | <D> **** Detailed Description **** On 2/21/2019 A Record was submitted to Records Control without following the records submittal process for Withhold from Public Records. They were not flagged appropriately. <I> **** Actions Taken **** Notified my supervision. Flagged the Documents Accordingly and with be notifying the sender from Regulatory Affairs via follow up email with some coaching. <N> The record that was submitted was identified as Withhold From Public Disclosure IF there were attachments. There were no attachments to the letter. Therefore, it is not classified as WIthhold and this CR should not have been initiated. Please close this CR with no actions required.
390327 | CR | 20190225 |  | 4 | Undeclared Prohibited Item |  |  |  | N | NO | <D> **** Detailed Description **** Undeclared Prohibited item (marijuana paraphernalia) was brought to Security checkpoint by Visitor for Org 52631. Visitor was informed of Benton Co Ordinance prior to arriving onsite by point of contact. <I> **** Actions Taken **** Denied Access to SDOCA, Benton Co Notified, Shift Manager Notified. SEL Entry by Sec LT, CR written.
390330 | CR | 20190225 |  | 3 | MI-3.4 Taken to History prematurely |  |  |  | N | NO | <D> **** Detailed Description **** During the procedure review process of PPM 10.2.14 â€œMaintenance Coatings Programâ€ it was discovered MI-3.4 â€œCoating Daily Work Practicesâ€ was taken to History (7-12 -17) prior to the commitments being incorporated into the latest PPM 10.2.14 Maintenance Coatings Program revision. Additionally the paint and thinner specifications chart needs to be updated by Engineering to include Carbogaurd 893N and Carbogaurd 890N for VOC lb/gal, cure time, and allowable application (gal) for SGT, CREF, and TSC. Recommend assignment to AR-MNTPROG for disposition and assignment of corrective actions. <I> **** Actions Taken **** Initiated CR, discussed with Maintenance procedure writer and provided new mark-up. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
390332 | CR | 20190225 |  | 3 | (R24LL) Vertical Slice Mtg Discussion Quals |  |  |  | N | NO | <D> **** Detailed Description **** (R24LL) During the R24 vertical slice critique, the team identified that qualifications was not discussed as part of the vertical slice meetings per PPM 1.20.1. The team agreed the vertical slice is probably not the right time to review qualifications because 1) many WOTs are being moved during this time, and 2) the correct department representative in the room to understand the resource impact. The recommendation is that Outage Management evaluate proceduralizing a forcing function for qualification review by each shop after the vertical slice meetings are complete. Assign as a Cat 3 to AR-OTMG <I> **** Actions Taken **** Captured in 4.0 Critique
390333 | CR | 20190225 |  | 3 | (R24LL) (R24LL) Backbone SO Tasks in Outage Schedule |  |  |  | N | NO | <D> **** Detailed Description **** (R24LL) During the R24 vertical slice critique, the team identified there are too many backbone system outage (SO) WOTs in the outage schedule. Suggestion is that once the actual work is in the schedule and logic tied to the SO task, the SO doesnâ€™t need to be visible in the schedule anymore. The SO tasks caused confusion during the schedule reviews and are driving too many tasks. Recommendation is for Outage Management to evaluate the amount of SO tasks in the backbone schedule and determine how they can be streamlined for future outages. Assign as a Cat 3 to AR -OTMG <I> **** Actions Taken **** Captured in 4.0 Critique
390341 | CR | 20190225 | CAQ | D | Received ROD ACCUMULATOR TROUBLE alarm for CRD-HCU-2619. | Y | N |  | N | YES | <D> **** Detailed Description **** Received ROD ACCUMULATOR TROUBLE, H13-P603.A7 drop 6-7, alarm for CRD-HCU-2619. ROD ACCUMULATOR TROUBLE, H13-P603 .A7.6-7, alarm for CRD-HCU-2619 was due to high water level. OPS2 has drained water per SOP-CRD-HCU and the alarm is clear. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-HCU-2619
390342 | CR | 20190225 |  | 3 | TSP-DG2-B502(B501) procedure changes needed |  |  |  | N | NO | <D> **** Detailed Description **** TSP-DG2-B502 (B501) step 7.2.1 procedure change(s) needed to ensure diesel is barred over prior to performing the surveillance. The System Engineer is the technical point of contact for these changes. <I> **** Actions Taken **** Contacted System Engineer and Ops procedure lead concerning these changes.
390344 | CR | 20190225 |  | 3 | Procedure enhancement required PPM 15.2.39 |  |  |  | N | NO | <D> **** Detailed Description **** There has been repeated battery failures for essential EBU 8HR lights. PPM 15.2.39 needs to be revised to make sure electricians replace essential EBU light batteries with newer (non-expire shelf life of the batteries) when battery replacement is required. Mark ups have been provided in the EDMS folder. <I> **** Actions Taken **** Initiated CR <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
390347 | CR | 20190225 |  | 3 | PCR NFM-3-2 irradiated fuel inspection update NE-02-00-08 |  |  |  | N | NO | <D> **** Detailed Description **** Procedure enhancement recommended by AR 377100-03. Irradiated fuel inspection may identify unrecovered foreign material in a fuel assembly. NFM-3-2 should be revised to create an assignment to update the fuel history database (NE-02-00-08) with any restrictions on future use of the affected fuel assembly. E.g., YLG135, documented in AR 366360 was discharged due to unrecoverable foreign material, a conservative risk decision. The accept-as-is disposition concluded YLG135 was suitable for continued use. <I> **** Actions Taken **** Recommend assignment to AR-RXFUEL. Procedure sponsor KAVILA.
390348 | CR | 20190225 |  | 3 | Hard Hat waiver not posted |  |  |  | N | NO | <D> **** Detailed Description **** Williams Plant Services employees were working in our electrical bucket shop in building 32. Normally for that space there is a hard hat waiver on the door because of the room having a ceiling. On this day we were having an observer. The observer noticed that the waiver was not posted on the door. We had already been doing a little work in the room by this time. When asked about the waiver, it could not be found. So we went to our upper management about the issue on whether or not this should even be a non-hard hat area. It was decided by Management and ENW safety, that this particular area needed a Notice sign instead of a waiver stating that no hard hats are to be worn. Since we did not have a waiver posted at the time of the work we were doing, we are initiating a CR. <I> **** Actions Taken **** Condition Report written, and contacted management.
390349 | CR | 20190225 |  | 4 | Received several TG Bldg Sample Rm Monitor Trouble alarms. | N | N |  | N | YES | <D> **** Detailed Description **** The MCR has received several TG Bldg Sample Room Monitor Trouble, H13-P851.S2,5-1, alarms. The alarm instantly clears. Notified the Shift Chemist and the CRS. <I> **** Actions Taken **** Possible sources of alarms are from S-CR-1 High Conductivity, S-AR-2 feedwater dissolved oxygen and SR-2 or SR-4 failure. Chemistry suspects the alarm is from the feedwater dissolved oxygen instrumentation. Please repair, replace or inhibit the alarm. | 02-00-S-AR-2
390351 | CR | 20190225 |  | 3 | 15.2.12 1.3.57 note needs revision |  |  |  | N | NO | <D> **** Detailed Description **** The note in section 7.1 and 7.2 of 15.2.12 indicates no barrier impairment is required when performing the sections. This is no long IAW the requirements of 1.3.57. Performing sections 7.1 and 7.2 requires a moderate breach in the negative portion of the boundary requiring an impairment be used. Reference table 4.12.3.a. The procedure needs to be revised. <I> **** Actions Taken **** initiated CR
390353 | CR | 20190225 |  | 3 | Procedure change needed for MSP-WMA-B104 |  |  |  | N | NO | <D> **** Detailed Description **** Per WO# 02102869-01 which changed the elapsed time meter for WMA-FN-54B to one that has a reset button. Steps 7.3 of MSP-WMA-B104 needs to remove wording that requires a clearance and removal of the meter to reset. The steps need to include recording the run time and pressing the reset button and verify meter reads zero. <I> **** Actions Taken **** notified supervision and procedure writer <N> **** Equipment Description **** . Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
390354 | CR | 20190225 |  | 3 | RFT-LOC-1B found lower bearing found bad | N | N |  | N | YES | <D> **** Detailed Description **** During 02136184 we found the lower bearing went bad. This also destroyed other parts internally. The 1 and 2 year PM's need to be performed at this time. Additionally, it's been noted before during feedback, the PM frequency interval is too long for the cleaning, inspection, and gear oil change. It needs to go back to 3 months. Recommend an assignment to maintenance to verify PM frequency is back to 3 months. <I> **** Actions Taken **** Notified supervisor | 02-00-RFT-LOC-1B
390355 | CR | 20190225 |  | 3 | RxMaint In-Processing Database fails to open |  |  |  | N | NO | <D> **** Detailed Description **** REACTOR AND MAJOR MAINTENANCE IN PROCESSING DATABASE fails to open using the In-Processing application. <I> **** Actions Taken **** IS evaluted the issue and found that a microsoft security update is causing some MS Access 97 file formats to fail to open based on column name character limits. IS has opened a case with Microsoft to resolve the issue.
390356 | CR | 20190225 |  | 3 | 6 IMDS were sent to Document Control. Signed but not dated. |  |  |  | N | NO | <D> **** Detailed Description **** Document control received six Instrument Master Data Sheets (IMDS) that were signed but not dated to process. <I> **** Actions Taken **** Informed my supervision and returned IMDS to engineer to fix and resubmit.
390361 | CR | 20190225 |  | 4 | SSS Motorola radio deskset |  |  |  | N | YES | <D> **** Detailed Description **** The radio deskset COMM-DESKET-15B in the SSS does not work very well. It is difficult to understand most of the radio communications. Please fix or replace <I> **** Actions Taken **** CR written <N> **** Equipment Description **** COMM-DESKET-15B in the SSS office
390362 | CR | 20190225 |  | 4 | Engineering Support Task cancelled for WMA-CC-52B1 work |  |  |  | N | NO | <D> **** Detailed Description **** This CR is being generated since the support task WOT 02114584-08 for engineering was canceled. Engineering uses these WOTs to plan resources appropriately and to ensure engineering can support the work as planned and as scheduled. These support tasks have been canceled on similar previous WOs for cleaning and inspecting the cooling coils for these air-to-water HXs. To ensure support is available, recommend on future WOTs requiring engineering support that these support tasks either be created or not canceled. This is a degrading trend. <I> **** Actions Taken **** notified supervisor
390363 | CR | 20190225 |  | 3 | Procedure change to SOP-COLDWEATHER-OPS |  |  |  | N | NO | <D> **** Detailed Description **** SOP-COLDWEATHER-OPS section 6.2.7 states â€œESTABLISH temporary logs for the following: â€¢?MONITOR Spray Ponds for icing. â€¢?MONITOR unoccupied buildings for broken piping and other abnormal conditions.â€. Which unoccupied buildings are supposed to be monitored? How thorough of an inspection is expected to be done? This is a burdensome requirement to have OPS-4 inspect every unoccupied building on site. OPS-4 already goes to most of the non-occupied plant buildings on rounds. <I> **** Actions Taken **** CR written
390364 | CR | 20190225 |  | 4 | 115kV/13.8kV SH-F0 Transformer faulted. | N | N |  | N | YES | <C> CR reopened for additional notes to be added. <D> **** Detailed Description **** 115kV/13.8kV SH-F0 Transformer faulted due to a damaged ground bushing which cleared two fuses on the primary side of the transformer. <I> **** Actions Taken **** Facilities personnel are working with BPA to cross connect to Site 1 power. <N> **** Equipment Description **** No known EPN - SH-F0 115kV/13.8kV Transformer
390365 | CR | 20190225 |  | 4 | Hach In-Line Turbidimeter Range Error After Power Restored | N | Y |  | N | YES | <D> **** Detailed Description **** Hach Model 1720C In-Line Turbidimeter reset multiplier setting upon power being restored. This INOPs the chart recorder that the state of Washington requires to prove water quality. Per On-Call Eff Manager direction, I&C is requested to reset Hach scale to the correct setting and therefore correcting the output issue to the chart recorder and restoring it to function. Manager also directed 4 hour readings be taken while chart recorder is INOP. Also verified that the high turbidity shut down is still functional while in the present state. <I> **** Actions Taken **** On-Call Eff Manager and MCR informed of issues. CR and WR written. 4 hour temp log started to record INF and EFF turbidity readings. <N> **** Equipment Description **** Flocculator BLDG
390366 | CR | 20190225 |  | 4 | RWCU-RMS-P/4 control switch is loose in panel | N | N |  | N | YES | <D> **** Detailed Description **** The control switch for RWCU-P-4, located on E-CP-G33/P026 in the Radwaste Control Room, is loosely mounted in the panel door and will rotate freely when the switch is operated. This will cause damage to wiring connections on the backside of the control switch. Please have the FIN Team address this. <I> **** Actions Taken **** wrote AR / WR <N> **** Equipment Description **** located on E-CP-G33/P026 in the Radwaste Control Room | 02-00-RWCU-RMS-P/4
390367 | CR | 20190225 |  | 3 | The potable water system valves need to be properly labeled | N | N |  | N | YES | <D> **** Detailed Description **** All of the Plantâ€™s Potable Water System valves that are located in the ground inside and outside the Protected Area need to be identified with a colored pole. This would make locating the isolation valves especially helpful when there is a line break and water leak. Especially in the winter when there is snow covering the valveâ€™s location. If the valves can not be located in time to stop the leak, this would cause the Plants potable water supply tank to be emptied, which would also render the demineralized water trailer inoperable, and so on. The valves need to be properly labeled above ground so they are easy to locate. Proper above ground location labeling would keep snow removal personnel from covering the locations. <I> **** Actions Taken **** wrote AR / WR <N> **** Equipment Description **** all PWC system valves located in valves boxes | 02-00-PWC-V-351
390368 | CR | 20190225 |  | 4 | Not able to take rounds on the Ops 3 tablet |  |  |  | N | YES | <D> **** Detailed Description **** The ops 3 tablet is not allowing the user to take rounds. The program is not pre loading the prior shift readings. The synchronize option was tried, the application was completely closed and restarted, and the tablet itself was powered down and restarted and nothing seems to work. <I> **** Actions Taken **** Supervision notified CR/WR generated <N> **** Equipment Description **** Ops 3 Tablet issues
390369 | CR | 20190225 |  | 4 | Unable to advance work order task in DataGlance |  |  |  | N | NO | <D> **** Detailed Description **** Work order task 02131657 could not be advanced past Ready in DataGlance. <I> **** Actions Taken **** Verified no holds and package had been validated. Notified Shift Management. Advanced task in PASSPORT to Working.
390373 | CR | 20190226 |  | 3 | SOP-RWCU-DEMIN Poor Human Factoring |  |  |  | N | NO | <D> **** Detailed Description **** Procedure for RWCU-DM-1B (5.5.7) layout has too many substeps resulting in an error likely situation. Specifically substeps t through dd which resulted in the overflow of RWCU-TK-2. <I> **** Actions Taken **** Informed SM, initiated CR.
390374 | CR | 20190226 |  | 4 | RWCU Pump A Trouble | N | N |  | N | YES | <D> **** Detailed Description **** P602-A5 4.7 RWCU Pump A Trouble alarm is locked in. Ops 2 is investigating. <I> **** Actions Taken **** Ops 2 is investigating <N> **** Equipment Description **** RB 522. | 02-00-RWCU-P-1A
390377 | CR | 20190226 |  | 4 | Preoutage task not necessary |  |  |  | N | NO | <D> **** Detailed Description **** Pre outage WOT 02114217-03 TRANSPORT RPIS PROBE TO RX BUILDING 501' FOR INSTALLATION was cancelled. It was determined in R23 that the best way to transport the probes was to wait until they are needed during the outage. That way they are not sitting on the R501 for an extended period of time, running the risk of damage. Rx Maintenance performs the work and coordinates with Operations and Security. <I> **** Actions Taken **** CR written to document as a lesson learned.
390379 | CR | 20190226 | CAQ | B | (QA) LORQ Exam Security not Verified Prior to Admin. |  |  |  | Y | NO | <C> Risk: Medium (Possible NRC finding) Cause: Unclear. Severity: B with investigation template required. <D> **** Detailed Description **** Individuals that validated Exam 2 of the 2018 LORQ biennial written exam were then administered Exam 3 that included one duplicate SRO question. Exam security verification steps of NRC IP 71111.11, Licensed Operator Requalification and Licensed Operator Performance, require exams to have no duplication of test items validated by the same individuals. In addition, TDI-24, Exam Security, Step 4.2.6 provides guidance that allows duplication of test items if the test items were part of an open exam bank at the start of the year. Not following the guidance of IP 71111.11 presents a vulnerability to additional regulatory oversight. This issue is classified as a finding for not following the guidance of IP 71111.11. <I> **** Actions Taken **** Informed Training Manager, Operations Training Manager and Quality Management. Attached detailed issue sheet to EDMS. <N> Cause: TDI-24 Exam Security, section 4.2.6 is not in alignment with NRC IP 71111.11 guidance, which allowed the duplication of an exam question to occur if in open exam bank. Action needs to be taken to revise TDI -24 to align with NRC IP 71111.11 which will correct the condition. the note was included in the first issuance of TDI-24 on June 23, 2016. After interviews with the procedure developer, the reason for adding the note is indeterminate. An Extent of Condition action has been created to ensure alignment of TDI-24 and NRC IP 71111.11 requirements. No additional actions/analysis necessary.
390380 | CR | 20190226 |  | 3 | (QA) Biennial written exams not validated per TDI-23 |  |  |  | Y | NO | <C> This CR changed to Non-CAQ 3 as per the MRT. <D> **** Detailed Description **** The 2018 Licensed Operator Biennial Written Exams were not validated per the requirements of TDI-23, LORQ Annual Exam Development and Administration. Interviews with validators and exam writer identified four steps not performed during the validation process. Not following these steps could affect exam results. Such as high miss questions during validation not being rigorously reviewed and then being high miss during approved exam. Additionally, time constraints during validation should have been an indication of examinees possibly running out of time during actual exam. This issue is classified as a deficiency for not following procedural guidance. <I> **** Actions Taken **** Informmed Training Manager, Operations Training Manager and Quality Manager. Attached detailed issue sheet to EDMS. <N> No additional action needed.
390381 | CR | 20190226 |  | 3 | (QA) Biennial exam expectations not defined |  |  |  | Y | NO | <C> This CR changed to Non-CAQ 3 as per the MRT. <D> **** Detailed Description **** During the first day of the 2018 Operator Requalification Biennial Written Exam (Exam 1), several individuals entered answers into the Vision database after the three-hour exam time limit had expired. TDI-23 does not provide guidance for a time requirement for exam completion. Additionally, TDI-23 needs additional guidance to ensure validations are completed in â€œnear-test conditionsâ€ to ensure the highest accuracy of validation results. This issue is classified as a deficiency for not providing clear expectations for exam administration. <I> **** Actions Taken **** Informed Training Manager, Operations Training Manager and Quality Manager. Attached detailed issue sheet to EDMS.
390382 | CR | 20190226 | CAQ | D | WEA-FN-6 has one of 2 belts broken | N | Y |  | N | YES | <D> **** Detailed Description **** WEA-FN-6 has one of 2 belts broken, please replace <I> **** Actions Taken **** wr/cr | 02-00-WEA-FN-6
390384 | CR | 20190226 | CAQ | D | FP-TK-110 Low Level | N | Y |  | N | YES | <C> Level restored in the tank. <D> **** Detailed Description **** See cross referenced CR 390364. When SHF0 lost power on 2/25/19, FP-P-110 auto started as expected. This resulted in FP-RV-2 lifting and discharging outside the building and flowing to the evaporation pond. Several thousand gallons were pumped from FP-TK-110, resulting in level less than 284,640 gallons as required by LCS SR 1.10.1.1.b. FP-P-110 and FP-RV-2 worked as designed; there is no FP equipment malfunction. <I> **** Actions Taken **** Secured FP-P-110, entered LCS 1.10.1.A. Opened FPSI 19 -0058. | 02-00-FP-P-110,02-00-FP-TK-110
390390 | CR | 20190226 |  | 3 | Site Wide Procedure Missing CNO Signature |  |  |  | N | NO | <D> **** Detailed Description **** SWP-SEC-12 was submitted to Document Control for processing but it did not have the CNO signature in accordance with SWP-PRO-02. <I> **** Actions Taken **** SWP-SEC-12 WAS RETURNED VIA NEEDS MORE INFO IN THE APW PROCESS. <N> Procedure was resubmitted with the proper routing and received CNO signature.no further action required.
390391 | CR | 20190226 |  | 3 | PPM 1.11.15 needs correction |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** HP procedure states incorrect limitation for storing radioactive material in satellite RCA's. In PPM 1.11.15 "Control of Radioactive Material", step 5.5.3.b.3.a, it says >20 dpm/100cm2 smearable alpha contamination. It should be Greater Than or Equal To. This would coincide with another procedure (HPI-12.103, "Radioactive Material Storage Within Building 167 and guilding 600", section 4.1.2 <I> **** Actions Taken **** notified HP Craft Supervisor and wrote this CR.
390392 | CR | 20190226 |  | 4 | Building 238 and B186 exterior landing need correction |  |  |  | N | NO | <C> After review, the CRG changed the facility code to 01 for the IDC instead of 02 for Columbia. <D> **** Detailed Description **** Building 238 and Building 186 are both located at old Site 4. B238 used for Rigging training. B186 used for Outage training. Both buildings have a problem with exits where the elevation between the floor and the exterior landing are not the same. This change in elevation at the exterior exits does not meet the International Building Code (2015 edition) Section 1010.1.5. This problem needs to be resolved by the Facilities and Commercial Engineering Group, Org Code 76300.
390393 | CR | 20190226 |  | 4 | Light out in Rx SW airlock/vestible | N | N |  | N | YES | <D> **** Detailed Description **** It was noted during tour that all lights are out in the airlock going to the truck bay in the reator buildng. it is very dark in this airlock and if someone doesn't have a flashlight it is a bad situation. Recommend replacing the lamps in here. If it cannot be fixed the a portable lanterns should be put in here. <I> **** Actions Taken **** informed supervision, asked for help drvinig resoloution | 02-00-R-BLDG-MISC
390394 | CR | 20190226 | CAQ | D | IDS 17 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** IDS 17 is not functioning as designed and requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security supervision notified. Initiate CR/WR. Compensatory measures initiated. <N> **** Equipment Description **** IDS 17
390398 | CR | 20190226 | CAQ | C | SW-V-611 Missing documentation | N | N |  | N | NO | <D> **** Detailed Description **** During the walkdown of WO 02080115-01, it was identified that weld record (2-13233) and ASME Small Items Parts Verification sheet documentation is missing. The paper (01) task cannot be found. The records were transferred from the pre-fab task (08) per the work instructions. All work within this task is Safety related, Quality Class 1, seismic category 1. This valve is ASME Section III, Code Class 1 and per PPM 1.3.30 Section titled â€œSmall Itemsâ€. The initial task to pre-fabricate SW V 611 was performed in March of 2018, in support of an Emergency Diesel outage window. The installation task (01) was pushed out from the schedule for the following window on the applicable component, to be performed in March of 2019. Upon completion of the 08 task, the original (QC reviewed inspected and signed) Weld Record 2-13233 and the ASME Small Items Parts Verification sheet was transferred to the paper copy of the 01 task, per step 4.5 of task 08. The work order was retained for implementation at a future date. Through the process of EWP implementation, many packages were relocated to WOP and/or documentation was uploaded to Dataglance for electronic use; work order planning was moved to building 64 and many packages were transferred to that location. During this process, the paper copy of W.O. 02080115-01 was misplaced and is now missing. A thorough investigation across multiple departments has been completed and currently the paper copy of the package and the necessary documentation appears to be unrecoverable. The 01 task has the ASME weld record in Portal J (EDMS docs) but it has no evidence of QCI review, additionally the welding which was performed in task 08 was completed but the electronic copy of the work order does not have QC acceptance documentation of the welds performed. These welds were accepted by QC using the currently missing paper copy. This work will be required to be re-performed prior to implementation of the install of SW V 611. QC will need to determine if and where there should be a Fit-Up hold point The valve is located in a secure, locked material storage area with the pipe and the cap, all together as a pre -fabricated spool. The acceptance tags and the issue tickets were retained with the new component to maintain traceability. The ASME Small Items Parts Verification sheet will need to be re-generated and parts acceptance with an ASME PIC and QC will be required to be re-performed. These documents will need to be re-performed electronically and added to the EWP to work through Dataglance for implementation of the work. <I> **** Actions Taken **** Cotacted QC, code programs and planning, made them aware of the outstanding issues and communicated with Mechanical Maintenance management to work through the process of rectifying this condition report.
390403 | CR | 20190226 |  | 4 | PWC-P-102 breaker on PWC-CP-102 will not close. | N | N |  | N | YES | <D> **** Detailed Description **** PWC-P-102 breaker on PWC-CP-102 will not close. This breaker needs to be closed to allow starting PWC-P-102 to restore potable water to part of the site potable water loop. PWC-P-103 is caution tagged off due to PWC-V-414 is broken. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-PWC-CP-102
390404 | CR | 20190226 | CAQ | C | EWD-84E-003 has several errors that need to be corrected |  |  |  | N | NO | <D> **** Detailed Description **** While performing work in WO#02038028-01 for WMA-EHO-AD52/2 several errors were found in EWD-84E-003. These errors in the drawing didnt match what was in the field and need to be corrected. Also the identification on the control switches in the main control room and on the simulator need to be changed to reflect the EPN that is on EWD-84E-003. <I> **** Actions Taken **** contacted supervison and engineering for resolution. Wrote this CR
390407 | CR | 20190226 |  | 4 | Potable Water Leak Discovered Near B600 Security Access Bar | N | N |  | N | YES | <D> **** Detailed Description **** At approximately 1130 a leak was discovered near the B-600 Security Access Barrier. The leak appears to be originating from an abandoned leg to the east of the PW loop. <I> **** Actions Taken **** The leak was isolated by closing PWC-V-342 and PWC-V-560. Control Room Supervisor was notified as well as management WO #02139410-01 was written for repair <N> **** Equipment Description **** PWC-V-390 provides PW to an abandoned line NE of PA fence | 02-00-PWC-V-390
390408 | CR | 20190226 |  | 4 | HPCS Motor Computer Point W132 (winding temp) erratic | N | N |  | N | YES | <D> **** Detailed Description **** During trending and monitoring it was observed that the W132 (HPCS winding temperature 2) has been erratic over the past few days with multiple indicated temperature spikes. Based on the motor being at steady state conditions (not running) and the very short duration of the temperature spikes this is believed to be just an issue with the computer point (W132). <I> **** Actions Taken **** CR written and supervisor notified. <N> **** Equipment Description **** EDNA computer pt W132 HPCS motor is in RxBldg 422' | 02-00-HPCS-M-P/1
390409 | CR | 20190226 | CAQ | D | FP-V-SGT/51 leaked by on clearance | N | N |  | N | YES | <D> **** Detailed Description **** FP-V-SGT/51 leaked by on clearance D-FP-V-SGT/56-002. This cause pussure (about 100 PSIG) to builld up between FP-V -SGT/51 and the valve we were doing diagnostics on (fp-v -sgt/56). <I> **** Actions Taken **** With supervisor and operations concurrence, we were able to use our test equipment to slowly open FP-V-SGT/56 and vent pressure through drain valve FP-V-SGT/53. Gauge FP-PI -SGT/6B2 pressure went to zero. We closed FP-V-SGT/56 again and the pressure immediately increased back to about 100 PSIG. We stopped and expanded the teamâ€¦ultimately stopping the diagnostics testing. | 02-00-FP-V-SGT/51
390410 | CR | 20190226 | CAQ | D | HPCS Flow Computer Point X122 Inaccurate at No Flow | Y | Y |  | N | YES | <D> **** Detailed Description **** During trending and monitoring it was observed that the X122 (HPCS Flow) has been erratic since yesterday with an indicated flow of 200 gpm. HPCS is currently in standby and there is no flow in the system. HPCS-FIS-4 was walked down and confirmed no flow was present. This is believed to be an issue with the computer point. <I> **** Actions Taken **** CR written and supervisor notified. <N> **** Equipment Description **** EDNA computer point X122 HPCS pump is in RxBldg 422' | 02-00-HPCS-P-1
390411 | CR | 20190226 |  | 3 | EWD-46E-312B drawing error | N | N |  | N | YES | <D> **** Detailed Description **** SCI-MUX-OPWA/1 is labeled SCI-MUX-OPWA/6 and SCI-MUX-OPWA/2 is labeled SCI-MUX-OPWA/7 EWD-45E-012 can be used for verification <I> **** Actions Taken **** Notified drawing error to Supervision | 02-00-SCI-MUX-OPWA/1,02-00-SCI-MUX-OPWA/2
390412 | CR | 20190226 | CAQ | C | Provide support of FP pipe nipples on SGT deluge | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing diagnostics testing on FP-V-SGT/56, we noticed the air supply valve FP-V-SGT/181 had a very long unsupported Â¼â€ pipe nipple. The air isolation valve was on the end of it. With the valve tubing removed this created a long leverage arm when we would manipulate the air isolation valve. We were concerned there was a potential for the Â¼â€ pipe to break at the pipe 90 it was connected to. We looked for the nearest isolation and it looks like it is at the top of the ceiling in the 572â€™ RX overhead. Also, we noticed if that pipe nipple failed it would effect all air operated valves on the SGT FP deluge system for both trains. We feel all the air isolation valves with long Â¼â€ pipe nipples should have additional support near their isolation valves. <I> **** Actions Taken **** stopped and informed our supervisor and showed the Shift Manager. <N> **** Equipment Description **** fp-v-sgt/181 . Needs an AR EVAL to authorize any permanent configuration change (if that is what is being requested). Sounds as if this is a condition that may only exist when some tubing has been disconnected for a Maintenance activity. If that is the case (only a temporary deadweight support is needed), then that should be installed and removed with work instructions.
390413 | CR | 20190226 | CAQ | C | Legacy issue regarding Coupon Station in SW B PH | Y | Y |  | N | NO | <D> **** Detailed Description **** When design change 86-0068-0A installed the coupon station in the Service Water â€œBâ€ pumphouse, the pipe break evaluation discussed the flooding aspect, but did not address the impact of a pipe break to the room cooler performance. Because the coupon station piping teeâ€™s off from the inlet to the PRA room cooler, a break in the coupon piping would increase the coupon piping flowrate and thereby reduce the flowrate to the cooling coil. Using an existing FATHOM model of the coupon pipe, it was determined that a break in the PVC portion of the line would result in a 2.1 gpm increase in coupon flowrate. This is a conservative value based on Service Water deadhead pressure instead of normal operating pressure and assumes the drain valve, SW-V-156G, is full open instead of throttled as indicated on M524-3. Because of how piping dynamics works, the expected decrease in PRA flow rate would be less than 2.1 gpm. Per ME-02-92-43 revision 13, page 17, the minimum required flowrate is 30 gpm, while OSP-SW-M102 gives a recommended range of 80 to 92 gpm. Therefore, the PRA room coolers have more than sufficient margin to absorb a loss of 2.1 gpm due to a break in the coupon station line. . As such, the PRA system is fully capable of performing its design function of heat removal from the Service Water building. This is a legacy issue. ME-02-92-43 will require revision to incorporate the effects of a pipe break in the seismic II PVC piping and to document the FATHOM model. <I> **** Actions Taken **** Revised FATHOM model to incorporate break in PVC pipe, compared exist margin to loss of margin, determined sufficient margin still exists.
390415 | CR | 20190226 | CAQ | D | Unable to proceed with FP-V-SGT/56 diagnostics |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** While working on WO# 02087557-01 FP-AO-SGT/56 diagnostics testing, we found the upstream clearance isolation valve SGT/51 was leaking by (see CR 390409). This was trapping 100 PSIG pressure between the isolation valve and the valve we were testing. Pressurized water would be forced out the clearance drain valve SGT/53 every time we stroked our control valve SGT/56. With ops permission, were able to use a bucket and slowly open SGT/56. It looks like we are leaking by at a rate of about Â½ gallon per minute. Ops tried to tighten the isolation valve without success. <I> **** Actions Taken **** We stopped the job and discussed options with our supervision. It was determined we needed to stop the diagnostics job until a resolution is found. The valve engineer said FP-V-SGT/56 operability will be confirmed from the PMT-5 in WO#02073779
390416 | CR | 20190226 | CAQ | C | Limitorque Actuators Exceed 2000 Cycle Limitation | Y | Y |  | N | YES | <D> Limitorque has a 2000 stroke limitations on their actuators. Review identified SW-MO-12A, SW-MO-12B and SW -MO-29 exceed the 2000 stroke limitation. <I> Attached evaluation provides resonable assurance that SW -MO-12A, 12B and SW-MO-29 can still perform their design functions. This is based on the full lube and inspect PM's, Actuator Refurbishments, diagnostic test data, margin, component history, and EPRI 1016701 Limitorque Actuator Fatigue Life Extension. CATID's were created to obtain new actuators/motors and WO's are in place. <N> AR EVAL needed for new motor operator motors (SW-M-V/12A, SW-M-V/12B, and SW-M-V/29)? | 02-00-SW-MO-12A,02-00-SW-MO-12B,02-00-SW-MO-29
390417 | CR | 20190226 | CAQ | C | CMS-RMS-1318 and 1418 not addressed in M937 | Y | Y |  | N | YES | <D> **** Detailed Description **** QID 025002-01 rev 7 added a qualified life on the H2/O2 analyzer remote switches based on data in QID 285012-01. From thermal aging analysis using Arrhenius methodology, the qualified life is 22 yrs using a conservative assumption of 10 deg F heat rise and a maximum abnormal ambient of 104 deg F (114 deg F). An error occurred when only eight of the switches were listed on the QRMS section of QIF 025002-01 rather than ten. This error was transferred to rev 21 of drawing M937. As a result, switches CMS-RMS-1318 and CMS-RMS-1418 have exceeded the EQ thermal qualified life. Mitigating considerations: Actual temperatures at the equipment location have been well below the maximum abnormal value of 104 deg F during plant operations. Using area average Arrhenius data would allow a much longer qualified life. Using 10 deg F heat rise was a conservative estimate for the panels. The switches are not close to heat producing equipment. EQ Evaluation (EC 17611) has been initiated to calculate a new qualified life based on actual temperatures in the area vs. the maximum design temperatures. This method is acceptable based on AED SPC 210, page 210-30. Evaluation concluded the thermal qualified life for these switches in their installed locations is GT 50 years. These components should be replaced at the next earliest convenience to address future ambient temperature variance in the installed locations. <I> **** Actions Taken **** Evaluated qualified life based on actual temperatures in the area. Initiated CR. | 02-00-CMS-RMS-1318,02-00-CMS-RMS-1418
390418 | CR | 20190226 |  |  | Loss of Power without Timely Bldg Evacuation Announcement |  |  |  | N | NO | <D> **** Detailed Description **** The loss of power to many Facility buildings on 2/25/2019 should have prompted area wide PA announcements to evacuate the buildings within 15 minutes of the incident in accordance with procedure GBP-EPP-01. I observed much confusion in Deschutes Building 26 from personnel, Supervisors and Managers on the proper actions. The first announcement that provided any direction was well beyond the 15 minutes. This announcement was luke warm at best, and did not direct personnel to leave the buildings that had lost power. The second announcement that came a little later was much better, however it still did not direct personnel to leave the buildings that did not have power. .
390419 | CR | 20190226 | CAQ | C | Tubes plugged in WMA-CC-52B1 | Y | Y |  | N | YES | <D> **** Detailed Description **** Both the supply and return headers were visually inspected with a boroscope during performance of cooling coil inspection for WMA-CC-52B1 (WO 02114584). The as found condition of the supply header had one blocked tube and one partially blocked tube. A backflush was recommended in order to attempt to remove the debris. Post backflush inspection revealed that the backflush was successful in removing the fully blocked tube in the supply header. The material identified that was partially blocking the tube could not be removed. WMA-CC-52B1 has 14 tube inlet/outlet in each header. Material appeared to be lodged into the tube and is not expected to migrate further through the system. With 1 tube partially blocked by foreign material therefore lowering flow through the one tube, the remaining 13 tubes will increase in flow due to total flow to the coil not being degraded. With only a partial blockage, flow is still available to provide a cooling medium and maintain the cooler performance above the design equipment operability requirements. Design equipment operability temperature limits are maintained per Calc ME-02-92-43. Conservatively assuming that no flow increases occur when a tube is completely blocked and that the as-left foreign material is fully blocking the tube, room temperatures would be expected to rise ~1Â°F which is still under design limits specified for supporting loads under these conservative conditions. Photos have been uploaded to the EDMS. <I> **** Actions Taken **** Discussed with supervisor and notified shift manager. | 02-00-WMA-CC-52B1
390420 | CR | 20190226 |  | 3 | Enhancement needed for cooling coil backflush instructions |  |  |  | N | NO | <D> **** Detailed Description **** During performance of WO 02114584, per the Work Instructions, maintenance was directed to perform a backflush of the Service Water side of WMA-CC-52B1. To do this, Fire Protection water is used for performing the backflush. Prior to performing back flushing of the Service waterside of these coils, maintenance wanted to ensure that the water being used was clean and flushed the water into a drum to eliminate any possible foreign material that may have accumulated within any dead legs. The initial water flushed into a drum did in fact have debris and silt in it. Maintenance performing this flush prior to the back flushing prevented additional debris and silt from entering into the safety related Service Water system. This showed good maintenance fundamentals and helps ensure good equipment reliability. Photos of the water quality before and after flushing of the Fire Protection water have been uploaded to EDMS. Recommend that future WOs pertaining Room cooler cooling coil inspections have instructions updated to include flushing fire protection lines to remove any potential for debris in the system prior to performing any back flushes. <I> **** Actions Taken **** Discussed with supervisor
390422 | CR | 20190226 |  | 3 | Loss of two failed controllers from warehouse |  |  |  | N | NO | <D> **** Detailed Description **** The two failed controllers were delivered to the warehouse pending shipment to vendors for failure analysis. Previously installed controllers, HD-LIC-2C and BS-PIC-18A, were delivered to the warehouse on 11/1/18 with repair/return sheets. However, they were held for shipment and not logged into repair/return list since the items did not need repair and only failure analysis was desired. On 12/19/2018, when items were ready to be shipped, an extensive search was conducted by warehouse personnel and system engineer without the items being found. Subsequent searching and communication to other personnel has also proved to be unsuccessful in locating the controllers. <I> **** Actions Taken **** Notified supervisors. Communicated to other warehouse personnel. Provided description and photos of controllers for identification. Conducted searches. Initiated CR.
390423 | CR | 20190226 | CAQ | C | Volume adjustment required during MSP-WMA-B104 | Y | N |  | N | YES | <D> **** Detailed Description **** On 2/26/19 during performance of MSP-WMA-B104 (WO 02105820 MSP-WMA-B104 - WMA-FU-54B - CARBON ADSORBER TEST), the flowrate recorded at test point â€˜Aâ€™ in step 7.4.12 was 1,064 cfm. The required flowrate at this point is GE 900 and LE 1000 ACFM. The as-found flowrate recorded at test point â€˜Bâ€™ was 41.34 cfm. The total as-found flowrate (A+B) was 1105.34 cfm. Tech Spec 5.5.7 requires a total CREF flowrate between 900 â€“ 1100 cfm. Following discovery, the system engineer discussed these results with the CRS. With concurrence from the CRS, the associated volume damper was adjusted to decrease the flowrate at point â€˜Aâ€™ to within the required range, with an as-left value of 998.6 cfm. The as-left flowrate at point â€˜Bâ€™ was 43.29. The total as-left CREF flowrate (A+B) is within the required range at 1041.89 cfm.
390424 | CR | 20190226 | CAQ | D | (NRC) Wedge found in automatic closing door | N | N |  | N | NO | <D> **** Detailed Description **** Wedge found in double doors on TG 411 East RCA entrance. doors are designed to close automatically in the case of emergency. This impeded the function of the door <I> **** Actions Taken **** Informed HP Supervison and removed Wedge <N> CR re-opened per Licensing request to add (NRC) to the title.
390425 | CR | 20190226 |  | 4 | Another PW leak identified | N | N |  | N | YES | <D> **** Detailed Description **** Security identified another PW leak near the vehicle access to the protected area. <I> **** Actions Taken **** OPs1 and OPs4 investigated and determined the leak could be isolated by PWC-V-345 and PWC-V-402. PWC-V-345 was previously closed by another leak. PWC-V-402 was closed and the leak appears to have stopped. | 02-00-PWC-V-402
390426 | CR | 20190227 | CAQ | D | E-CB-S/3 Open Light Socket Broken | Y | N |  | N | YES | <D> **** Detailed Description **** The Open indication light socket on E-CB-S/3 is broken. Then light bulb was found recessed in the socket and the screw on the back of the socket was found pushed partially out. Light Socket requires replacement. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TB 471' West on SM-3 | 02-00-E-CB-S/3
390430 | CR | 20190227 |  | 4 | CF-V-620 indicates itermediate (remotely) | N | N |  | N | YES | <D> **** Detailed Description **** CF-V-620 is indicating intermediate (in the RWCR), when it should be full Closed. The valve appears to be fully closed, by Local indication. CF-V-620 is located by the RWCU precoat tank and is currently in a HCA. Detailed inspection of limit switches/mechanical agitation has not yet been performed. Proper position indication will be required to continue with the RWCU-DM-1B Backwash and Precoat (improper position indication may cause logic issues). <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** RWCR for erroneous indication. RW 467, precoat tank area | 02-00-CF-V-620
390431 | CR | 20190227 |  | 4 | MT-ELEV-4 Brake did not disengage Faults | N | N |  | N | YES | <D> **** Detailed Description **** Twice in one shift the â€œBrake did not disengageâ€ fault came in. The elevator was stuck on the RW 525â€™ when the down button was pushed on the RW 501â€™ the light came on and went off after about 5 seconds but the elevator didnâ€™t move. The elevator was returned to service by pressing the system fault reset pushbutton on the control panel in the elevator machine shop. At the end of shift the same fault came in and the elevator was stuck on the RW 441â€™ until the reset pushbutton was pressed. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RW | 02-00-MT-ELEV-4
390433 | CR | 20190227 | CAQ | D | MTE not available for AS-FOUND, re-perform work orders |  |  |  | N | YES | <D> **** Detailed Description **** Fluke 187, ID NO 0064546 not available for AS-FOUND calibration. Re-perform section 4.4.2 of work orders for CRD HCUs. W/O 02136900 CRD-HCU-4203 W/O 02136918 CRD-HCU-3403 This data is required for monitoring/trending of the power supplies. <I> **** Actions Taken **** Wrote CR. | 02-00-CRD-HCU-3403,02-00-CRD-HCU-4203
390434 | CR | 20190227 |  | 4 | PWC-TBIT-2 set on wrong range | N | N |  | N | YES | <D> **** Detailed Description **** PWC-TBIT-2 recorder does not match the local meter reading. In the past, this has been due to the recorder default range following a power outage. The recorder range needs to be reset to match the local readout. <I> **** Actions Taken **** Contacted FIN for repair. Instructed chemistry tech to record local reading every 4 hrs. We are currently on the cross-tie to site one so this is not a regulatory concern. | 02-00-PWC-TBIT-2
390444 | CR | 20190227 | CAQ | D | FDR-V-92 shows dual indication when closed | N | N |  | N | YES | <D> **** Detailed Description **** The FDR-TK-6 inlet valve, FDR-V-92, show dual indication when taken closed. It was closed to send FDR water to EDR -TK-2 using the crosstie valve. In this configuration there is no water level increse in FDR-TK-6 per our indication; though it cannot be known for certainty if the valve is full closed based off this alone because the piping arrangement may tend to send water to EDR under normal conditions. CR 388123 is on this same issue, it does not appear to have been worked. FDR-V-92 was cycled multiple times, never displayed closed indication. | 02-00-FDR-V-92
390448 | CR | 20190227 |  | 3 | The PI for Total Scope WD Compl is Yellow for Maint. |  |  |  | N | NO | <D> **** Detailed Description **** The PI Indicator for Walkdowns Complete for Total Scope for R 24 is currently Yellow. Maintenance needs a recovery to return to Green. <I> **** Actions Taken **** Notified Outage Management and Maintenance Manager.
390451 | CR | 20190227 | CAQ | D | CMS-SR-13 reading differs from recorder | Y | Y |  | N | YES | <D> **** Detailed Description **** CMS-O2H2-1 O2 reading (1.71%) differs from CMS-SR-13 indication (1.77%). Delta is in all points monitored. This is an OPS-INST-H101 reading on day shift and CMS -O2H2R-2 is already not being used due to being locked up. This recorder is PAM. <I> **** Actions Taken **** included both readings on H101s. Recorder appeard to have taken a step down on 2/26/19 night shift. | 02-00-CMS-O2H2R-1
390452 | CR | 20190227 |  | 4 | CW-CT-1C Distribution Deck Water Level High | N | N |  | N | YES | <D> **** Detailed Description **** CW-CT-1C Distribution Deck Water Level is at 12 inches. The Operator rounds directed me to write this CR. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-CW-CT-1C
390453 | CR | 20190227 |  | 3 | Two badge photos were incorrect in the Lenel Computer |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Security Officers identified two incorrect badge photos in the Lenel computer. Investigation is on-going and the correct photo's have been restored by the IT Analyst. <I> **** Actions Taken **** Notified Sec Serv Mgr, Security Supervision and completed this CR.
390456 | CR | 20190227 |  | 4 | RADTRAD Error Notice 17, Revision 1, Natural Deposition |  |  |  | N | YES | <D> **** Detailed Description **** Energy Northwest calculations do not use the model described in the error notice (Powers model) and are not impacted by this error notice revision. Alion Science and Technology notified RADTRAD Users Group Member of an error affecting RADTRAD versions 3.03 and 3 .10. This error notice is a revision (Revision 1) of an error notice sent to users back in 2012 and captured under AR/CR 00272570. The error affects containment decontamination of radionuclides due to sprays, filtration systems and natural deposition when the Powers model is used. This revision of the error notice corrects a removal coefficient used for BWRs from 0.01hr-1(Revision 0) to 0.1hr-1 (Revision 1). <I> **** Actions Taken **** Form 26146R2 was completed and uploaded to EDMS. An e-mail notification was sent to RADTRAD users to inform them of the error. A copy of the e-mail was uploaded to EDMS. . Recommend COMP-NA | FW-00-SOFT-TECH-RADTRADV310
390457 | CR | 20190227 |  | 4 | Near miss â€“ Individual slipped and fell, no injury. |  |  |  | N | NO | <D> **** Detailed Description **** Individual slipped and fell on snow/ice while crossing from north overflow parking lot to Deschutes parking lot near building 11. Individual was walking with their hands out of their pockets which minimized the fall. No injury, near miss. <I> **** Actions Taken **** Notified supervisor and got shoe grippers for vehicle.
390459 | CR | 20190227 | CAQ | C | DG-ENG-1A2 Governor Speed Setting Low | Y | N |  | N | YES | <D> **** Detailed Description **** It was identified that the speed seeting dial for DG-ENG -1A2 is currently set at just below 38, the acceptable range is between 38 and 40. The dial should be adjusted to within the acceptable band when DG1 is no longer protected. This setting impacts the mechanical governor which is not a credited feature of the governor control system and is NOT relied upon for safety system performance. <I> **** Actions Taken **** SM notified, other DG governor settings were verified, all other governor speed settings were found within proper band. <N> Adjusted Speed Setting on DG-1A2 to middle of the band to 39 Per SOP-DG1-START. JAW 2/28/2019 | 02-00-DG-EHO-1A2,02-00-DG-ENG-1A2
390460 | CR | 20190227 | CAQ | D | (NRC) DG1 governor settings appear to be below the LOW value | Y | N |  | N | YES | <D> **** Detailed Description **** DG-ENG-1A1 speed setting but the dial appears to be slightly below 13.47. SOP-DG1-START states, 13.47 for LOW, 13.48 for NORM and 13.49 for HI DG-ENG-1A2 speed setting but the dial appears to be slightly below 13.38. SOP-DG1-START states, 13.38 for LOW, 13.39 for NORM and 13.40 for HI. . Per SOP-DG1-START, if Speed Setting is out of specification, adjust to normal value and initiate a CR for trending. Speed Setting adjustment can be made with the engine running or shutdown. <I> **** Actions Taken **** SM was informed and engaged system engineering. . DG-ENG-1A1 mechanical speed setting was verified to be set AT the LOW value of 13.47, which is acceptable per SOP-DG1 -START. DG-ENG-1A2 mechanical speed setting was verified to be set BELOW the LOW setting of 13.38; see also CR 390459. | 02-00-DG-ENG-1A1,02-00-DG-ENG-1A2
390461 | CR | 20190227 | CAQ | C | Untimely entry of equipment issue into CAP |  |  |  | N | NO | <D> **** Detailed Description **** On afternoon of 2/26 the NRC resident raised a question regarding the governor settings on DG-ENG-1A1 and DG-ENG -1A2. This condition was not verified and/or a AR initiated to document the concern before the end of shift, as per SWP-CAP-01. <I> **** Actions Taken **** Notified SM, Ops Mgmt, and Licensing.
390462 | CR | 20190227 | CAQ | D | DG-2 Generator South Bearing Oil level LOW OOS | Y | N |  | N | YES | <D> **** Detailed Description **** On rounds, DG-2 generator south bearing oil level was approximately 2/16â€ below top of high level mark. Logs state operability is questioned when oil level indicates 3/16â€ below top of high level mark. Oil needs to be added soon as it is very close to affecting operability. <I> **** Actions Taken **** Notified MCR | 02-00-DG-LG-6
390463 | CR | 20190227 | CAQ | D | DG-1 Generator South Bearing Oil level LOW OOS | Y | N |  | N | YES | <D> **** Detailed Description **** On rounds, DG-1 generator south bearing oil level was approximately 1/16â€ below top of high level mark. Logs state operability is questioned when oil level indicates 3/16â€ below top of high level mark. Oil needs to be added soon as it is close to affecting operability. <I> **** Actions Taken **** Notified MCR | 02-00-DG-LG-5
390464 | CR | 20190227 |  | 4 | Students Removed from Training With Less 24 Hrs Notice |  |  |  | N | NO | <D> **** Detailed Description **** Contrary to GBP-TQS-01, Training Attendance, students were removed from Accredited Training shortly prior to the start of training. Plant General Manager was not obtained. The missed training is not related to a qualification. Assign to RP Ops for trend. <N> Students removed from training were RMC Laborers. RMC Laborers not in an accredited training program and are not required to attend HP accredited training. No further action is required.
390466 | CR | 20190227 |  | 4 | High Alarm rate on W-Door-C240. | N | N |  | N | YES | <D> **** Detailed Description **** W-Door-C240 not working as designed. Request Elect Maintenance to investigate <I> **** Actions Taken **** CR/WR Generated | 02-00-W-DOOR-C240
390467 | CR | 20190227 |  | 4 | RW Elevator "Brake Did Not Lift" Fault | N | N |  | N | YES | <D> **** Detailed Description **** RW elevator had another "Brake Did Not Lift" fault causing the elevator to be inoperable until the fault was reset by pushing the "System Fault Reset" button in the elevator machine room, RW 467' . This is a frequent issue with the RW elevator. It should be fixed as soon as possible to prevent any complications that may extend the refueling outage. <I> **** Actions Taken **** Notified MCR | 02-00-MT-ELEV-4
390470 | CR | 20190227 |  | 3 | PDIS computer PM needs updating |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of computer PM titled "PDIS clean various computers" under WO 02107626 01 it was discovered that much of the equipment listed in the PM no longer exists and has been replaced with newer equipment. <I> **** Actions Taken **** Informed supervision, computer engineering and writing this CR to document. <N> **** Equipment Description **** 501 RW MCR
390471 | CR | 20190227 |  | 4 | Basic Rigging Challenge Practical Failures |  |  |  | N | NO | <D> **** Detailed Description **** 5 individuals failed to meet evaulation criteria for the Basic Rigging Challenge Practical (ME000668). <I> **** Actions Taken **** No remediation planned or provided due to design of the evaluation. Notified appropriate supervisors. Recommend CR to trend for AR-TRNMT
390473 | CR | 20190227 |  | 3 | E-TR-N1 and N2 accessory checks for R24 |  |  |  | N | NO | <D> **** Detailed Description **** The accessory checks for the normal transformer MWOs were updated as part of AR-SMS 375306. WOs 02110185 and 02110186 were generated before and do not have the steps that would be required for adding oil to each transformer. The addition of the oil to the transformer should be part of the scope for R24 for these transformers during the performance of the accessory tests for each transformer. Recommend assignment to planning to update these WOs.
390475 | CR | 20190227 |  | 3 | Main XFMR accessory tests do not have steps for oil add |  |  |  | N | NO | <D> **** Detailed Description **** AR-SMS 375306 was initiated to incorporate the addition of oil to each of the new main transformers while performing the accessory checks during the outage. A review was performed on the current MWOs and the WOs for each new main transformer accessory test being performed in R24 and there is no step to add oil to the transformer in these WOs. This step was recommended by AR-SMS 375306 and assignment 2 was completed without making these changes. Transformer MWO WO E-TR-M1 01149882 02110267 E-TR-M2 01149883 02110182 E-TR-M3 01078724 02110183 E-TR-M4 WO 0119884 currently has this information in its accessory test PM and it is not impacted by this AR-CR. This is an administrative issues and it has no impact on any of the main transformers. This review and discovery is being performed as part of the cause determination of AR -CR 389753. Recommend assignment to planning to update these WOs.
390477 | CR | 20190227 |  | 3 | SO-V-310 sample point on PM WO | N | N |  | N | NO | <D> **** Detailed Description **** PM Work order 02127128 for collection of Seal Oil samples was recently revised in which 4 addtional sample points are used to collect samples. The historical WO typically obtained samples from SO-V-209, SO-V-320, SO-V-324. The Model WO and PM work orders were updated to include SO-V -208, SO-V-283, SO-V-310 and SO-V-315. Although a recent change from the last occurrence, these same four additional valves had been used for the PM (In addition to the original three) back in 2/2018 under WO 02095770. Discussion with Engineering and Operations was made prior to perforanace due to SO-V-208 being tied to a high level alarm, as well as SO-V-283 as if opened long enough, level in the tanks could lower and expose hydrogen. During opening of SO-V-310 (task 07) ( vent on TSW-HX -9), (SO-V-320 drain also used historically) craft observed air flow (potential hydrogen due to the tie to the Hydrogent side Seal Oil tie) and closed SO-V-310 per their work instructions. <I> **** Actions Taken **** Craft contacted supervision as the amount of air/potenttial hydrogen was more than expected. Followed up with Engineering. Engineering stated that the room is vented and even if worst case the valve was opened for up ~ 1 minute to prime for a sample that would not be expected to be an issue. Informed them that I would generate a CR to document that perhaps this valve should be used by ops or on a different frequency to prime/vent as good practice for the system and that if sampling from a vent is desired to be continued in the future, (as opposed to just unsing the drain SO-V-320) then additinal instructions, notes should be added to the step for how much venting is expected from SO-V-310 and why it is allowable/acceptable. Engineering agreed to take the CR for review and what may be needed for SO-V-310 if used in the future or it this valve should be cycled/vented on a more frequent basis.
390478 | CR | 20190227 |  | 4 | PWC pipe through-wall leak near PWC-V-418 | N | N |  | N | YES | <D> **** Detailed Description **** There is a through-wall leak in the PWC system downstream of PWC-V-418 (1.25" pipe). It is approximately 400ml/min leak rate that is spraying and puddling on the floor. There is no electrical equipment being wetted. <I> **** Actions Taken **** Informed MCR. Wrote CR. . PWC leaks are too numerous. This poises a safety hazard for workers in very cold, slick, wet conditions to locate, excavate and isolate these leaks. <N> **** Equipment Description **** PWC pipe downstream of PWC-P-102 in bldg 40
390480 | CR | 20190227 |  | 4 | PWC-P-102 excessive seal water leakage | N | N |  | N | YES | <D> **** Detailed Description **** PWC-P-102 has excessive seal water leakage that is splashing around the spray guard and puddling in Bldg 40. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-PWC-P-102
390481 | CR | 20190227 |  | 3 | Procedural Guidance Needed in 11.2.4.5 Renaissance Fastscan |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During several recent Whole Body Counts, in the GSB, using the Fastscan, we are seeing Whole Body Count Reports, with No Nuclides listed in the Peak Analysis and Summary Report. Procedural Guidance is needed for the Fastscan Operator, when this situation occurs. <I> **** Actions Taken **** Notified HP Lead Technician Notified HP Supervision Initiated CR Esoms Log Entry <N> **** Equipment Description **** GSB Whole Body Count Room
390483 | CR | 20190227 |  | 4 | Delays in restoring WMA-54B due to bad test equipment |  |  |  | N | NO | <C> Reopened CR to edit grading. <D> **** Detailed Description **** while attempting to test WMA-54B, the test equipment did not function properly. both LMP-3000 testing machines were unable to work. the shop had to use a thrid machine before bieng able to test the system. <I> **** Actions Taken **** Retrieved 2 additional test machines in order to get 1 to work. Coordinated with supervision and operations to keep informed of the delays to restoration during testing. working with engineering and supervision about having old machines repaired or replaced with new models. <N> **** Equipment Description **** tools and test equipment
390484 | CR | 20190227 |  | 4 | Wires Not Labeled |  |  |  | N | NO | <D> **** Detailed Description **** It was discovered that wires were not labeled after opening pull station FP-MPS-23/5 while working work order 02116227-07. The Cable Termination Instructions (CTI) and work package listed labeled wires. The Supervisor and the Craft stopped and closed the pull station. <I> **** Actions Taken **** Steps have been added to the work package to trace the wires back to the smoke detectors so that the wires can be properly labeled. Contacted Management and Planner.
390486 | CR | 20190227 |  | 3 | (QA) EP-01 â€œEmergency Planâ€ Figure 3-1 Not Up To Date |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Revision 066 to the EP-01 â€œEmergency Planâ€ did not update Figure 3-1 â€œOutside Response Agency Resourcesâ€ to reflect the name change from â€œArevaâ€ to â€œFramatomeâ€. The Emergency Plan is Chapter 13.3 of the Final Safety Analysis Report (FSAR). Regulation 10 CFR 50.71(e) requires periodic updates of the FSAR â€œto assure that the information included in the report contains the latest information developedâ€. The failure to ensure a license basis document is current could lead to a loss of regulatory margin. Factual Basis: â€¢ Revision 066 to EP-01 updated â€œArevaâ€ to â€œFramatomeâ€ within the Table of Contents, sections 3.3.1 and 3.2.4, Table 4-1, Appendix 1, and Appendix 4. â€¢ Within revision 066 to EP-01, Figure 3-1 still shows â€œArevaâ€ instead of â€œFramatomeâ€. Recommend SL-3 to EP (name change not significant to E-Plan function) <I> **** Actions Taken **** Discussed with EP Management.
390487 | CR | 20190227 |  | 3 | (QA) LDCN-18-016 Did Not Drive SWP-IRP-02 Revision |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) LDCN-18-016 for EP-01 Rev 066 did not ensure all affected station procedures were revised to align with the change, contrary to SWP-LIC-03 â€œLicensing Document Change Processâ€. This resulted in SWP-IRP-02 â€œCorporate Nuclear Safety Review Boardâ€ (CNSRB) being inconsistent with EP-01 â€œEmergency Planâ€ and PPM 13.13.2 â€œEmergency Event Termination and Recovery Operationsâ€ with respect to the required CNSRB actions following a Site Area Emergency or General Emergency. Additionally, SWP-IRP-02 is inconsistent with EP-01 regarding CNSRB reviews of Emergency Plan changes. These inconsistencies among the requirements in two station procedures and a Licensing Basis Document could result in a procedure compliance issue where requirements in SWP-IRP-02 are not performed. --------------------------- Complete details are contained in document in EDMS. Recommend SL-3 to EP if SWP-IRP-02 is not updated at time of screening. <I> **** Actions Taken **** Discussed with EP and Quality Management
390488 | CR | 20190227 | CAQ | D | (QA) LS-18-0373 Conflicts With 50.54(q) Screen # 18-032 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The License Basis Impact Evaluation (LBIE) Screening LS-18-0373 conflicts with the 50.54(q) Screening # 18-032 regarding the need for a 50.54(q) Effectiveness Evaluation for the proposed changes to EP-02 â€œERO On-Shift Staffing Analysis Reportâ€ Rev 003. The consequence is two different pages within the Quality Assurance Record for this revision are in conflict with each other, and this could invite regulatory scrutiny for a possible missing 50.54(q) Effectiveness Evaluation. Factual Basis: â€¢ LBIE Screening LS-18-0373 Question 3b asks, â€œHas a 50.5 4(q) screening (Form 26878) identified that a 50.54(q) evaluation is required?â€ (This question is answered with a check in a â€œYesâ€ box) â€¢ The 50.54(q) Screening # 18-032 Block 7 asks, â€œIs a Â§50 .54(q) Effectiveness Evaluation required?â€ (This question is answered with a check in a â€œNOâ€ box) Insight: â€¢ Preparer of both screening documents listed above said the 50.54(q) Screening # 18-032 is correct, and no 50.54(q) Effectiveness Evaluation is required, and he plans to revise LBIE Screening LS-18-0373 accordingly. Issue has been corrected. Recommend SL-D to EP for error on regulatory process 50.54. <I> **** Actions Taken **** Discussed issue with EP Management.
390489 | CR | 20190227 | CAQ | D | (QA) CAQ AR-CR Has Incorrect Assignment Type |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) AR-CR 383303 identified a Condition Adverse To Quality (CAQ) regarding an incorrect value for classification of an Unusual Event in PPM 13.1.1. The only documented action, to correct the Emergency Action Level (EAL) value is an assignment type ASGN. The use of ASGN assignment results in the corrective action not being visible as part of the Corrective Action Program backlog and not being subjected to the requirements of SWP-CAP-01 for approvals and extensions to ensure Conditions Adverse to Quality are properly addressed. The issue in AR-CR 383303 has been addressed at the time this CR is being initiated and the assignment type has been changed to CA. Recommend SL-D to EP for CAP Compliance Issue. <I> **** Actions Taken **** Discussed with EP Management.
390490 | CR | 20190227 |  | 3 | (QA) Procedures/Instructions Specify Outdated Records Proces |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Several current procedures and instructions still specify outdated â€œmicrofilmingâ€ for the processing of records. Specifying an incorrect process could lead to confusion later when individuals cannot locate the more recent records on microfilm, contrary to the procedures/instructions that specified microfilming. Recommend SL-C to RIM to coordinate actions (QA Records and Procedure issues). Complete details for the CR are contained in EDMS. <I> **** Actions Taken **** Disucssed with RIM and EP Management.
390491 | CR | 20190227 |  | 4 | WOA-42-7E2C (WOA-FN-3) lights are not functioning | N | N |  | N | YES | <D> **** Detailed Description **** WOA-42-7E2C (WOA-FN-3) lights are not working. Bulbs were verified to be good. CRS permission was obtained to attempt resetting the thermal overloads but no change was seen. WOA-FN-3 services the bathrooms on the RW 487. Suspect blown fuse(s). <I> **** Actions Taken **** Informed MCR. Verified bulbs in working order. Attempted Thermal Overload reset- unsuccesful. <N> **** Equipment Description **** RW 487 | 02-00-WOA-42-7E2C
390492 | CR | 20190227 |  | 4 | WOA-HV-1 Heating coil leak | N | N |  | N | YES | <D> **** Detailed Description **** WOA-HV-1 has a Heating steam leak from the uppermost coil on the East side of the unit. Multiple heating coil tubes had completely broken off and a 3 foot plume of steam was issuing from the coil. The steam leak has been isolated and Local Tags are in place to facilitate maintenance. <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** RW 487 | 02-00-WOA-HV-1
390493 | CR | 20190227 |  | 4 | TO-LOC-1 room oil sump at 1/2 full | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** TO-LOC-1 room oil sump is at 1/2 full. Per the OPS 3 logs, the oil sump should be pumped once half full. There has not been any unusual rise in sump level. The sump has reached half full due to normal accumulation. Please pump down, but there is no urgent need. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TO-LOC-1 Oil sump
390494 | CR | 20190228 |  | 4 | PRA-EUH-92B Fan uncoupled from motor | N | N |  | N | YES | <D> **** Detailed Description **** PRA-EUH-92B fan has uncoupled from the motor. The heater was found on (heating coils warm) with the fan not turning. Upon further inspection the motor was also not turning. The heater was on as indicated by a red light at PRA-EUH -92B. To protect the heating element PRA-RMS-EUH/92B was taken to OFF and Caution tag created. See EDMS for photos. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TMU Pumphouse | 02-00-PRA-EUH-92B
390495 | CR | 20190228 |  | 4 | PRA-EUH-92A Fan Motor not Running | N | N |  | N | YES | <D> **** Detailed Description **** PRA-EUH-92A was energized and the heating coils warm. The fan motor did not start following the 20 second time delay after the heater was energized as shown on EWD-95E-007. Please investigate and repair or replace. <I> **** Actions Taken **** informed MCR <N> **** Equipment Description **** TMU Pumphouse | 02-00-PRA-EUH-92A
390504 | CR | 20190228 |  | 4 | RRC-P-1B Upper Seal Chamber Pressure eDNA Indication Erratic | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The RRC-P-1B upper seal chamber pressure (ENW.MODBUSHS .RF3009) is behaving erratically (see the graph in the EDMS folder). Both the local pressure gauge (RRC PI 1B) and the control room pressure indicator (RRC-PI-602B), donâ€™t exhibit this behavior. So, the problem appears to be in the signal to the computer. This is an indication only issue and doesnâ€™t affect the ability of the RRC pump to perform its required function. <N> **** Equipment Description **** eDNA Point ENW.MODBUSHS.RF3009
390505 | CR | 20190228 |  | 3 | Large transformer oil addition is not consistent |  |  |  | N | NO | <D> **** Detailed Description **** A review of large transformer accessory testing revealed the following: Oil is not added for E-TR-M1, E-TR-M2, E-TR-M3, and E-TR -M4. Oil is directed to be added in the model work orders for E-TR-N1, E-TR-N2, E-TR-B, and E-TR-S but does not ensure the transformers are full or record the amount of oil added. Some MWOs are written as conditional steps which permit no oil to be added. CR 389753 documents the lockout of E-TR-S on low oil level. 207 gallons of oil was added to E-TR-S prior to restoring the transformer to service. We need to ensure that our transformers are full of oil every two years to give us the maximum margin and to record the amount of oil necessary to keep them full for trending <I> **** Actions Taken **** The model work orders for transformer accessory testing and the work orders that are at plan or greater that require revision are listed on a document in the EDMS folder attached to this condition report. The attached work orders must be revised prior to R24.
390506 | CR | 20190228 |  | 4 | Monthly Radwaste Roof Survey Not Performed for February |  |  |  | N | NO | <D> **** Detailed Description **** The monthly radiological survey of the radwaste building roof (WO 02131211) was not performed for the month of February. This activity was intentionally deferred based on safety concerns during the inclement weather that occurred during February. Refer to AR-SMS 390158 for information on the cancel request for this work. Dose rates inside of the radwaste building do not present a significant change from January's routine survey data; therefore, there is no indication that conditions on the radwaste roof have changed. The next instance of this survey will be performed as scheduled during March 2019. <I> **** Actions Taken **** AR-SMS 390158 was generated to cancel request WO 02131211. Radwaste building dose rates for February were reviewed to evaluate the likelihood that conditions on the radwaste building roof changed during the month. There are no indications that conditions on the radwaste building roof have changed.
390508 | CR | 20190228 |  | 4 | Rad Waste control room lighting | N | N |  | N | YES | <D> **** Detailed Description **** There are 76 overhead lights out in the rad waste control room. <I> **** Actions Taken **** Completed Space inspection and initiated CR <N> **** Equipment Description **** Rad waste control room - RW 467
390509 | CR | 20190228 |  | 4 | Sink leak in Chemistry Lab | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The sink in the WEA-FN-4 fumehood in the back of the chemistry lab on 487' Radwaste has a leak. Water has been observed on the threads between the sink drain and its pipe. Water is collecting in the bottom of the cabinet under the sink. The sink is in a contaminated fumehood, so the leakage must be treated as contaminated. Action is needed to prevent the spread of contamination. <I> **** Actions Taken **** Placed bucket under sink drain that needs to be checked constantly to prevent overfill of potentially contaminated liquid. Notified MCR, Chemistry Supervision <N> **** Equipment Description **** WEA-FN-4, back chemistry lab 487' Radwaste
390510 | CR | 20190228 |  | 3 | PPM 5.5.11 procedure change - implement after cycle 19-3 |  |  |  | N | NO | <D> **** Detailed Description **** PPM 5.5.11 (Rod insertion in ATWS conditions) will be changed to allow crews to insert control rods in a more timely manner in ATWS conditions by allowing for parallel actions by reactor operators. This new procedure change will be practiced in cycle 19-3 prior to implementation. Implementation date will be 9/9/19. An email has been sent to all crew shift managers and the operations procedures group with additional information. <I> **** Actions Taken **** Initiated CR. Initiated TREQ 19-0031. AR to Ops procedure group. Implementation date is 9/9/19.
390511 | CR | 20190228 |  | 4 | TOA-FL-1A not connected to motor | N | N |  | N | YES | <D> **** Detailed Description **** Discovered one end of TOA-FL-1A roll on ground at the coupling to motor. In this state, filter cannot be jogged to have clean filter media. This was the only TOA filter that was functional or not end of roll of all four. <I> **** Actions Taken **** Notified CRS | 02-00-TOA-FL-1A
390512 | CR | 20190228 |  | 3 | Procedure Enhancement SOP-RPS-SHUTDOWN |  |  |  | N | NO | <D> **** Detailed Description **** CR 382443 documented that P&L 4.2 of SOP-RPS-START and SOP-RPS-SHUTDOWN was no longer correct due to the new PRNM has a different chassis power supply design this is no longer an issue. SOP-RPS-START was changed but SOP-RPS SHUTDOWN was not. <I> **** Actions Taken **** Found during procedure review CR 342491.
390513 | CR | 20190228 |  | 4 | High Risk RWP Inadvertently Taken to ACTIVE |  |  |  | N | NO | <D> **** Detailed Description **** High Risk R24 radiation work permit (RWP) 30004292 was inadvertently taken to an ACTIVE status by a supervisor without receiving RPM approval. The RWP was rolled back to a PLAN status upon identification of the error. The supervisor was aware that the work was high radiological risk, but was reviewing multiple RWPs at the same time and inadvertently took the wrong RWP to ACTIVE. <I> **** Actions Taken **** The RWP was rolled back to a PLAN status. It is currently pending RPM review and approval.
390515 | CR | 20190228 | CAQ | C | (NRC) Exam Security Near Miss on ILC-23 NRC Exam |  |  |  | N | NO | <D> **** Detailed Description **** During simulator evaluations on 2/27/19 a marking was found in a procedure by the CRS that was left by the CRS of the previous scenario (station identified). Although this is categorized as a Near Miss because it was determined the markings did not compromise the exam, the behaviors demonstrated by the procedure reviewer could lead to an exam compromise if further action is not taken. <I> **** Actions Taken **** Actions taken, informed the NRC, Operations, and Training management. The individual who checked the procedure has been removed from the exam process until further coaching can be documented. An additional peer checker was put in place to peer check all procedure reviews for the remainder of the NRC exam. Recommend additional action to benchmark other sites to determine if improvements could be made to the existing process.
390520 | CR | 20190228 |  | 4 | RW 487' and RW SE Stairwell Lighting Requires Attention | N | N |  | N | YES | <D> **** Detailed Description **** Lighting fixtures at L.9 13.2, L.9 11.1 and Q.1 13.2 on RW 487' elevation require new light bulbs. There are several lighting fixtures in the RW southeast stairwell that require new light bulbs. The lighting in the stairwell is poor and if additional lights go out, this may create a safety hazard. <I> **** Actions Taken **** Included this CR number on monthly floor inspection form. <N> **** Equipment Description **** L.9 / 13.2 L.9 / 11.1 Q.1 / 13.2
390521 | CR | 20190228 |  | 4 | Reactor building lighting deficiencies | N | N |  | N | YES | <D> **** Detailed Description **** Lighting deficiencies in the reactor building. Note that this does not include every failing/dead/removed bulb, nor was every location visited. The issues are predominantly with fluorescent bulbs, but some LED and (what appear to be) sodium vapor are dead. N, S, E, W used as direction. See EDMS for word document. <I> **** Actions Taken **** Informed SM. <N> **** Equipment Description **** Lighting in RB.
390522 | CR | 20190228 |  | 3 | EL000331 ELFA Installation of Ground Devices |  |  |  | N | NO | <D> **** Detailed Description **** EL000331 ELFA Installation of Ground Devices OJT/TPE GuidE needs to have step 12, page 6 removed. It is a perform 10.25.141a 8.0 Documintation added to WO & have filed into plant files records. This is aadministration function after the work is completed serves no purpose in the trainning process. <I> **** Actions Taken **** Notified trainning of the need to revise OJT/TPE guide AR generated per 5.3.7a of GEN-TQS-03
390523 | CR | 20190228 | CAQ | D | M&TE OOT | Y | Y |  | N | NO | <D> **** Detailed Description **** Calcode #0063972 Fluke Temp. Probe- model 80PK-1 found OOT & adjusted within specs. Not used in the OOT range of 300F Degree. No Plant Impact. DEF #6953A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
390524 | CR | 20190228 |  | 3 | Loss of FP-TK-110 Inventory | N | Y |  | N | YES | <D> **** Detailed Description **** This CR is being written to address loss of water inventory from FP-TK-110 during the loss of power transient that occurred on 2-25-19, reference CR 390364. . During the loss of facilities power, FP-P-110 auto-started as designed on loss of power to FP-CP-110. When this occurred FP-P-110 ran for approximately 154 minutes before being secured. FP-RV-2, relief valve for FP-P-110 maintained FP system integrity by flowing water into the drain piping to the evaporator ponds. . Evaluation of this condition identified that FP-RV-2 is set to relieve at approximately 160 PSI and will flow approximately 800-1000 GPM at this setting. Approximately 154,000 gallons of water was put into the evaporator ponds. Reference drawing M573-2. . Procedure 4.FCP.3 contains information for securing FP-P -110 when notification is received the pump is running. 4.FCP.3 should be updated to contain a note advising operations FP-P-110 should be secured â€œas soon as reasonably achievableâ€ during a FP-P-110 auto-start to eliminate loss of FP-TK-110 inventory. . If additional â€˜loss of facilities powerâ€™ procedures are created due to this event, the new or revised procedure should also reference loss of FP-TK-110 water inventory and provide the appropriate actions in the new procedure as well. . The FP System functioned as designed on 2-25-19. . Reference CR 390364 and CR 390384. <N> **** Equipment Description **** Yard - By Flocculator Bldg. | 02-00-FP-TK-110
390525 | CR | 20190228 |  | 3 | ARM POWER SUPPLY MONITOR BOX 0068449 |  |  |  | N | NO | <D> **** Detailed Description **** DURING THE PREP WORK FOR W/O # 02103846-06 THE PROCEDURE ISP-REA/PRM-X301 CALLS FOR A ARM POWER SUPPLY MONITOR BOX C003954 THIS HAS BEEN REJECTED AND REPLACED WITH 0068449 THE TEST EQUIPMENT MODEL C003954 NEEEDS REPLACED WITH 00684449 <I> **** Actions Taken **** TALKED WITH SUPERVISOR AND TOOL CRIB PERSONEL <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
390526 | CR | 20190228 |  | 3 | TSP-RHR-B803 needs revision |  |  |  | N | NO | <D> **** Detailed Description **** TSP-RHR-B803 is the RHR System C leakage surveillance. It mistakenly references RHR B in the purpose and in 7.1. The procedure should be revised. <I> **** Actions Taken **** Initiated CR
390527 | CR | 20190228 |  | 3 | TO-PS-ZA1 need IMDS updated | N | N |  | N | NO | <D> **** Detailed Description **** The IMDS for TO-PS-ZA1 shows model type for the pressure switch to be Model 555 Type J302, when installed and new pressure switch are Model 555 Type J402. Recommend redline the IMDS to correct the error. Additionally evaluate if this is the correct switch for the range of operation. This is a 0 -100 psi pressure switch operating at 13 psi. <I> **** Actions Taken **** Spoke with system engineer wrote CR
390528 | CR | 20190228 |  |  | NA |  |  |  | N | NO | <D> **** Detailed Description **** NA
390529 | CR | 20190228 |  | 3 | Concerning â€œCR390075 â€“ SAFETY/LOWER the BAR or Raise itâ€ |  |  |  |  | NO | <D> **** ANONYMOUS CR - Detailed Description **** Concerning â€œCR390075 â€“ SAFETY/LOWER the BAR or Raise itâ€. The CR was Answered and Closed without addressing the actual content of the CR. The General Notes referred to a â€œASK Senior Managementâ€ question concerning PT, but CR390075 was written due to concerns about the safety of EN non-essential Employees that were told they needed to stay and continue working. Please address CR390075 original content. <I> **** Actions Taken **** Wrote this CR to address content of CR390075 <N> ANON CR created; moved to OPS for review.
390530 | CR | 20190228 |  | 4 | RW MT-ELEV-4 brake did not lift | N | N |  | N | YES | <D> **** Detailed Description **** The radwaste elevator, MT-ELEV-4, had a fault again. Due to 'brake did not lift.' The computer reset was depressed and the machine was functional afterward. This has happened numerous times over the past fer weeks. <I> **** Actions Taken **** Informed MCR. | 02-00-MT-ELEV-4
390532 | CR | 20190228 |  | 3 | MRule Performance Criteria for TR-B is required for Unavaila |  |  |  | N | NO | <D> **** Detailed Description **** Currently the Backup Transformer has regularly scheduled maintenance that is performed on line. The Maintenance Rule (MRule) Program has this function designated as risk significant. The exemption for not tracking unavailability for risk significant functions in the MRule program given is â€œNot generally taken out of service during applicable operating conditions (no scheduled OOS time) unless there is a functional failure.â€ . The need to develop Availability performance criteria for TR-B (E115 system) needs to be reviewed per NUMARC 93-01. Potential exists based on the PSA risk that the TR-B (E115 system) could be made Non-Risk Significant. . Recommend that the CR be assigned to System Engineering group. <I> **** Actions Taken **** Discussed this CR with System Engineering Supervisors.
390533 | CR | 20190228 | CAQ | D | (QA) Missing/Lost Weld Records for RRA-CC-8/9, TSW Piping | N | N |  | N | NO | <D> **** Detailed Description **** (QA) Hard copy weld records with QC review/approval signatures per WOT 02106152-08 have been determined lost or missing. Missing/lost weld record nos.are: 2-13575, 2-13587, 2-13588 2-13589, 2-13590, and 2-13591 per WOT 02106152-08. A search for the weld records has been performed throughout by Williams Contractor Admin personnel. . This CR was initiated to address the loss of the original quality weld records with QC Review SIgnatures. <I> **** Actions Taken **** Notified Williams Management and Quality Services Supervisor. Action Taken: Quality re-performed WO review of the re-created weld records and resigned as QC review approval. Weld records were submitted to Williams Contractor. <N> **** Equipment Description **** Records administrative, no Plant work. Weld records are for fabrication activities and R24 Field install work. No further action is required.
390535 | CR | 20190228 |  | 3 | E820-2 drawing discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** E820-2 grid location F-11 for the 230KV tower lists lights and their power supplies. EWD-46E-464 lists lights supplied by the circuits on E-LP-3CB. Circuit 9 is listed on the EWD as supplying power to 3 lights on the 500KV tower. The 230KV tower drawn on E820-2 shows two lights powered by circuit 9 that should be drawn as being powered by circuits 1 and 3 (as shown on E820-1). Recommend a field walkdown to verify the power supply for these lights on the 230KV tower, then update applicable drawings as necessary.
390540 | CR | 20190228 |  | 4 | Electrical wall outlet plate bottom half broke and missing | N | N |  | N | NO | <D> **** Detailed Description **** Electrical wall outlet plate bottom half broke and missing. Need to add a new wall plate to the outlet. It is on the west side of the hallway in the Wenatchee buildngjust north of the scaffold office. <I> **** Actions Taken **** Attempted to call facilaties supervixser. Ended up wrting a CR.
390541 | CR | 20190228 | CAQ | D | DG3 roof plug leak | Y | N |  | N | YES | <D> **** Detailed Description **** The northwest corner of the DG3 roof plug is leaking approximately 20 drops per minute. The leak is not falling on HPCS-GEN-DG3. <I> **** Actions Taken **** Informed the Shift Manager, SSS, Ops 2, and Health Physics. . Note the NRC has also commented on this (CR 390113). | 02-00-HPCS-GEN-DG3
390543 | CR | 20190228 |  | 3 | Incorrect Dates for Amendment 65 in the FSAR |  |  |  | N | NO | <D> **** Detailed Description **** Amendment 65 to the Final Safety Analysis Report (FSAR) does not contain consistent amendment dates throughout the chapters and appendices. In most cases, the amendment is dated in the future. In two cases, it is dated December 2017. In two other cases, it is dated December 2018. In one case, it is dated November 2019. Lastly, it is dated December 2019 a total of 153 times. <R> Per 10 CFR 50.71(e) we are required to provide an updated FSAR to the NRC every 2 years. For Columbia that mean within 6 months after the end of each outage -- not to exceed 24 months from the last submittal. The correct amendment and date for the FSAR being built at this time is December 2019. RPI-14.0 explains the admendment and date convention for Columbia's FSAR. The instances noted in the CR of pages dated December 2019 are correct. There are 9 instances that have dates that are incorrect. Those dates will be corrected in AR 384463 -- the 2nd administrative LDCN for Amendment 65. Please note also that Columbia's FSAR is maintained on a by page basis -- meaning the dates and amendment numbers are changed only if text is changed on that pages. There are therefore many different dates and amendment numbers in the FSAR. Also early in Columbia's history the FSAR was updated more frequently than every 2 years. Again accounting for many different amendments and dates within the FSAR. DRJ 3/4/19
390544 | CR | 20190228 |  | 3 | NRC inspectors were delayed |  |  |  | N | NO | <D> **** Detailed Description **** On the morning of February 28, 2019, two NRC inspectors were delayed in getting their DLRs, which impacted their inspection time. Please assign as SL 3 to AR-LIC <I> **** Actions Taken **** Upon being notified by the inspectors that they were waiting on their DLRs, an HP representative was immediately dispatched to issue the DLRs. <N> Discussed with the staff the importance of verifying inspection activities and locations. Additionally, the lead inspector identified that it wasn't well communicated where they were going to be for the day, resulting in no one being available to process their DLRs. No further action needed.
390545 | CR | 20190228 |  | 2 | [NRC] Observation on Causal Evaluations |  |  |  | N | NO | <D> **** Detailed Description **** The NRC is concerned with the level of involvement that is required on their part in order for the station to produce correct causal evaluations.
390546 | CR | 20190228 | CAQ | D | (QA) E-BU-R522/3 indicates charger fault | N | N |  | Y | YES | <D> **** Detailed Description **** (QA) E-BU-R522/3 service alert light is flashing and indicating a charger fault. During a quality field walkdown an auditor identified that E-BU-R522/3 service alert light was flashing three times with a pause and then flashing 3 times again, which is a charger fault. The green light is on steady indicating it is in the ready mode. <I> **** Actions Taken **** Initiated this CR & WR and discussed with Operations. | 02-00-E-BU-R522/3
390547 | CR | 20190228 |  |  | Jet pump operability ind vs est RRC flow GT 10%. |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Jet pump operability A block indicates no. Initially part of TDAS-MUX-15/15A issues. The mux issues are resolved but the indicated and established flows remain GT 10% for both loops. Surveillance is still satisfactory because this section continues to have 2 out of 3 portions "yes"
390548 | CR | 20190228 | CAQ | D | FCP-1 Drop 6-2 Trouble alarm locked in. | N | N |  | N | YES | <D> **** Detailed Description **** 4.FCP.1 drop 6-2 RW BLDG 507' Mech Equip Room trouble alarm is locked in. Following reset of another alarm drop 6-2 trouble locked in and will not clear. ARP directs write CR. <I> **** Actions Taken **** Wrote CR Attempted to reset throughout day. | 02-00-FP-CP-FCP1
390549 | CR | 20190228 | CAQ | D | Three TSC Satellite phones inoperable | N | Y |  | N | YES | <D> **** Detailed Description **** During the Satellite Base phone testing WO 02108292 it was found that 3 satellite phones in the TSC where not working. The base station for these phones was reset and the phones started working. Note: There are 11 other satellite phone lines in the TSC that were not affected and remained fully functional. Affected phones: TSC/Plant/NRC Liaison Line1 Maintenance Manager Line 2 TSC information Coordinator Line 2 <I> **** Actions Taken **** Notified supervision, EP, and fixed the problem. Phones have been restored. Recommend closing. <N> **** Equipment Description **** TSC and B82
390550 | CR | 20190228 |  | 4 | CFD Precoat Tank Coating (CF-TK-4) | N | N |  | N | YES | <D> **** Detailed Description **** This CR does not identify a new equipment condition. The interior coating of CF-TK-4 was identified as degraded via AR CR 182571 in 2008. Recoating the tank requires an outage and has been deferred several times. Based on walkdown with Ops the tank condition does not appear to be much different than when originally identified in 2008. The purpose of this CR is to request NDE to perform a wall thickness measurement to assist in prioritizing recoating the tank. This does not affect the functionality of the tank. <I> **** Actions Taken **** Walked down with Ops (Operations) and informed supervisor. - CAP Edit - Name removed. <N> **** Equipment Description **** W467' | 02-00-CF-TK-4
390551 | CR | 20190228 | CAQ | C | Smoke detectors in field do not match the drawing |  |  |  | N | YES | <D> **** Detailed Description **** Drawing CVI 217-00,84,50 is incorrect for zone 13. Smoke detectors 13-19, 13-20, 13-21 and 13-22 are shown on the drawing in a configuration matching an ionization detector. It was verified in the field they are DS-2 photo-electric detectors and confirmed by using the maintenance and surveilance procedures 15.2.2 and 15.2.14. The drawing is being modified as part of EC 16607. The drawing will be corrected by the modification. This does not affect operability of the zone or system as the detectors have been properly maintained. This is only a drawing issue. <I> **** Actions Taken **** Initiated CR. | 02-00-FP-ZONE-13
390552 | CR | 20190228 | CAQ | D | MS-PS-23B and MS-PS-23D as found trip out was tolerance | Y | N |  | N | NO | <D> **** Detailed Description **** MS-PS-23B as found trip was found at 1087 while performing WO 02104712-01 ISP-MS-Q904. MS-PS-23B as left Trip is now 1079 after adjustment was performed using the ISP-MS-Q904.. .. MS-PS-23D as found trip was found at 1084 while performing WO 02104712-01 ISP-MS-Q904. MS-PS-23D as left Trip is now 1080 after adjustment was performed using the ISP-MS-Q904 <I> **** Actions Taken **** Both SORâ€™s where adjusted with-in tolerances had new O -ring(s) installed and this CR was written to document per ISP-MS-Q904. Surveillance complete SAT <N> **** Equipment Description **** MS-PS-23B and MS-PS-23D
390553 | CR | 20190301 |  | 4 | CBD-POIC-1 mangled & damaged. | N | N |  | N | YES | <D> **** Detailed Description **** CBD-POIC-1 found damaged and mangled. Nearby cart that is normally stored under phone booth looks like possible cause given height of cart in relevance to controller and no longer in its normally stored spot due to work for Halogenation Blowdown project. This controlled is instrumental in setting Circ Water Blowdown to the river rate. <I> **** Actions Taken **** Informed CRS, initiated AR. . See AR 380269, WR 29142637. Note that this has existed since 5/29/18 - "a temporary knob has been installed is currently functional, but needs a permanent solution." | 02-00-CBD-POIC-1
390554 | CR | 20190301 |  | 4 | Pump House #2 (BLDG 40) door lock broken. | N | N |  | N | YES | <D> **** Detailed Description **** BLDG 40 lock tumbler does not want to rotate fully to unlock door. Great effort has to be made and this may break the key entirely. <I> **** Actions Taken **** Informed MCR. Initiated AR <N> **** Equipment Description **** Building 40 | 02-00-CGS-BLDG-MISC
390555 | CR | 20190301 |  | 4 | DWST chemistry out of spec | N | N |  | N | NO | <D> **** Detailed Description **** While performing weekly sample of DWST the following analysis were discovered to be out of spec.: Silica (12ppb / 11ppb) limit = 5ppb, Chloride (4.8ppb / 4.6ppb) limit = 1ppb , Sulfate (6. 4ppb / 6.0ppb) limit = 2ppb, UV Chloride (5. 0ppb) limit = 3ppb, UV Sulfate (5 8ppb) limit = 3ppb. <I> **** Actions Taken **** Informed On-call Chemistry Manager, CRS & SM. On-Call Chemistry Manager requested Ops secure CST makeup and commence feed and bleed on DWST. Sample of CST's was in spec and normal. Sampled Demin Water Trailer, results were in spec and normal. <N> **** Equipment Description **** DWST located in GSB basement DWST chemistry has returned to specification. No further action required.
390582 | CR | 20190301 |  | 3 | ESOMs issue inpacted TRB outage / R24 |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** during tagout approval for hanging, a WARNING conflict arose between a danger tag and a no tag hung by another danger C/O. The option to accept this warning was not available and it prevented the hang option of the second clearance during the TRB outage. The ISO C/O was hung with NO tags on the B/7 fuses. This prevented the GND C//O from being hung since the ground C/O added RED tags to the same fuses. This type of conflict has generated a box with the option to accept the conflict and hang the next C/O in the past. <I> **** Actions Taken **** reviewed R24 clearances for similar conflicts - they do exist. <N> SUPV has reviewed and approved the closue of this CR. See EDMS for evidence.
390583 | CR | 20190301 |  | 4 | Coffee spilled in the security X-Ray 3 in the PAAP | N | N |  | N | YES | <D> **** Detailed Description **** On 3/1/2019 a sizeable amount of coffee was spilled inside a x-ray machine at the PAAP. The owner of the coffee is unknown and the individual did not own up to their actions therefore not allowing an opportunity to coach for excellence . This obviously is not achieving excellence. <I> **** Actions Taken **** Shift manager notified. Security supervision notified. Equipment taken out of service. CR/WR generated. <N> **** Equipment Description **** SEC-XR-4 located in the PAAP. Equipment has been worked and returned to service.
390584 | CR | 20190301 |  | 3 | TRB OCB blowdown valve freezing | Y | N |  | N | NO | <D> **** Detailed Description **** see EDMS for possible method to prevent freezing of the air operated TRB oil filled circuit breaker. B/D valve has frozen several times requiring heating to thaw the valve and operate it per the OPS 4 logs. CR initiated for evaluation per SM request <N> The EDMS document is from the OMM
390585 | CR | 20190301 |  | 4 | ALARA plan requirement not enacted |  |  |  | N | NO | <D> **** Detailed Description **** The ALARA for RWP 30004232 plan has an entry which states â€œMove SOP/Undress Area outside of RHR â€œAâ€ Pump Room to allow workers to move to and undress in a low dose area.â€ It was determined during implementation that this was not practical because of space considerations, so the step off pad was not moved outside of the room. The ALARA plan should have been amended along with any needed modifications to the dose estimate modifications to the dose estimate This is a self-assessment standards deficiency <I> **** Actions Taken **** Notified acting RPM.
390586 | CR | 20190301 |  | 3 | ED set point adjustments not properly documented |  |  |  | N | NO | <C> CR Severity moved to 3 and to AR-RPOPS group at the request of MRT 03.05.2019 <D> **** Detailed Description **** During RHR-MO-40 and RHR-MO-49 work ED dose set points were adjusted to numbers >100 mrem several times during the course of the work. The set point changes were made to allow workers to complete longer entries without having to exit the area and were appropriate. In most of these cases the permission was documented as coming from the Radiological Operations Supervisor as required by PPM 11.2.9.31. However in two cases specific craft supervisors were listed as have given approval and in another case the non-specific term Supervisory Authorization was used. PPM 11.2.9.31 requires that manual ED dose set point adjustments to 100 mrem or greater - 300 mrem require approval of the Radiological Operations Supervisor. After discussions with the HP craft supervisors involved with the work it appears likely that the Rad Ops Supervisor did approve the setpoint changes but the documentation of the approval was performed incorrectly. This is a self-assessment deficiency. <I> **** Actions Taken **** Discussed with acting RPM and RP supervision. The topic of requirements for ED setpoint adjustments and doucmentation for the approval is being covered in the current RP training continuous training cycle under the class HP19088 HP Trigger Points.
390587 | CR | 20190301 |  | 3 | Notifications not made to Rad planning as per GEN-RPP-02 |  |  |  | N | NO | <D> **** Detailed Description **** In several cases manual adjustments to ED dose set points were made of >25% and no documentation that rad planning was notified as required by GEN-RPP-02. These adjustments were made while implementing RWP 30004448. It appears that the cause of this deficiency is that the guidance for manual adjustment of ED set points is contained in PPM 11.2.9.31, while the requirement to notify rad planning is contained in GEN-RPP-02 but not mentioned in 11.2.9.31. Recommend adding the requirement to 11.2.9.31. This is a self-assessment identified deficiency. The topic of manual ED set point adjustment is being covered in the current RP continuous training cycle class HP001988 HP Trigger Points. <I> **** Actions Taken **** Notified the acting RPM .
390588 | CR | 20190301 |  | 4 | Motor removed in 2012 not sent offsite for refurbishment | N | N |  | N | NO | <D> **** Detailed Description **** The 200 hp motor removed from RCC-M-P/1A in 2012 has not yet been delivered to the warehouse to be shipped offsite for refurbishment and return to stores. This motor (UTC 384612) is currently in the RCA on W437' elevation near the trash compactor - see the photos attached to the EDMS of this AR CR 390588. This is an issue at this time primarily because System Engineering is currently advocating FY19 replacement of RCC-M-P/1B in response to AR CR 390197. If the motor removed in 2012 had been removed from the RCA and sent off for refurbisment as had been intended and did not require a rewind as part of its refurbishment, it is likely that a design change would not be required for its subsequent use to replace RCC-M-P/1B or RCC-M-P/1C. Because this was not done, an emergent modification may be required for installation of CID 20018 at RCC-M-P/1B. . In 2012, the original motor at RCC-M-P/1A was removed and replaced with CID 20018 per EC MALT 9605 via PM WO 01155945. WOT 01155945-15 and its PPM 1.3.74 Repair Data Sheet provided direction for Electricians to coordinate with the Warehouse and HP to get the removed motor package and have it shipped offsite to Schulz Electric for refurbishment. However, the step in the WOT to coordinate with Warehouse and HP was N/A'd and although the step in the WOT to complete the PPM 1.3.74 Repair Data Sheet was initialed, the craft action on page 2 of the Sheet to deliver the item to the Warehouse was not actually completed and none of the craft checkboxes on page 2 of the Sheet were checked. Subsequently on 01/03/13, AR CR 276593 (RCC-M-P/1A: Location is unknown / no CID attached) was initiated and errantly dispositioned - errantly concluded that the motor had been disposed of as contaminated waste by HP. Subsequently on 08/30/18, AR CR 384080 ('Lost' 200HP motor removed from RCC-M-P/1A found on W507') was initiated and went COMP-NA to WR 29144399 which was actioned to WO 02134438 on 09/04/18 and has been at PLAN status in Portal J since then. . <I> **** Actions Taken **** 1) Notified appropriate personnel and initiated this AR CR 390588 as requested. 2) Technical Services indicated they had taken action to drive getting the removed motor removed from the RCA and delivered to the warehouse for shipment offsite to be refurbished and returned to stores per PPM 1.3.74. 3) Design Engineering Minor Mods has preliminarily pulled FY21 design DECP AS 283724-03 for RCC-M-P/1B replacement with CID 20018 forward as emergent FY19 work in anticipation that this will be needed by the station in response to AR CR 390197.
390591 | CR | 20190301 |  | 4 | MT-ELEV-2 door sticking | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-2 (SW RB elevator) was identified as being stuck on 606. The elevator was called to 572, it showed up based off the light indication, but the door only shuddered. The door was able to be pushed open after a few attempts on both the 572 and 606 but it is sticking fairely badly, it needs more than a nudge on at least 2 floors. <I> **** Actions Taken **** Informed CRS, pulled ropes on every elevation to render the elevator unavailable. | 02-00-MT-ELEV-2
390592 | CR | 20190301 |  | 3 | (Non EN/CGS) CC-175 Wrong Procedure Used |  |  |  | N | NO | <D> **** Detailed Description **** During the recalibration of a commercial customer asset, the technician noted that the wrong procedure was listed on the previous calibration. Procedure used did not test temperature function but all others were tested. Recommend assign to AR-CALSERV <I> **** Actions Taken **** CC-175 was initiated and CR generated. Investigation initiated and recalibration completed with correct procedure.
390593 | CR | 20190301 |  | 4 | Coffee mug inadvertently opened and sent through x-ray |  |  |  | N | NO | <D> **** Detailed Description **** The Individual had a sealed coffee mug with a screw on lid and an air relief tab. The air relief tab was somehow jarred and popped open after the individual put the mug in their backpack. The backpack was placed on the belt and ran through the x-ray machine where coffee spilled out of the top of the relief and onto the belt of the x-ray machine. <I> **** Actions Taken **** The entire crew was provided Coaching for Excellence on the requirements of putting liquids through the x-ray machines. Additionally, it was recommended that we go a step further and place a screw top mug inside a sealable container if it contains liquid. <N> equipment has been worked and has been returned to service.
390594 | CR | 20190301 | CAQ | D | E-RLY-87/TB/C | Y | N |  | N | YES | <D> **** Detailed Description **** WO# 02106512, E-RLY-87/TB/C AS-FOUND TESTING WAS SATISFACTORY BUT DURING THE CALIBRATION OF E-RLY-87/TB/C THE AS-LEFT MINIMUM PICKUP AUX RELAY WOULD NOT FUNCTION PROPERLY. THE AUX RELAY CHATTERS & DOES NOT PICKUP WITH CRISP INTENTIONS. <I> **** Actions Taken **** NOTIFIED SUPERVISOR, OPS SPARE RELAY LEFT INSTALLED | 02-00-E-RLY-87/TB/C
390595 | CR | 20190301 | CAQ | D | E-RLY-87/TB/A AS FOUND THROUGH CURRENT OUT OF TOLERANCE | Y | N |  | N | YES | <D> **** Detailed Description **** E-RLY-87/TB/A ASFOUND THROUGH CURRENT OUT OF TOLERANCE COM3 THROUGH CURRENT AS FOUND WAS 31.95 AMPS COM4 THROUGH CURRENT AS FOUND WAS 31.96 AMPS TOLERANCE RANGE IS 31.0 TO 31.9 AMPS PER 10.25.25 ADJUSTED RESISTOR R3 AS LEFT THROUGH CURRENT COM3 & COM4 IS 31.12 AMPS AS LEFT IS SAT. THE ADJUSTMENT TO R3 CAUSES RETEST OF RELAY SO R1 & R2 HAD TO BE ADJUSTED ALSO ALL AS LEFT SETTING ARE WITHIN TOLERANCE <I> **** Actions Taken **** CR/AR FOR TRENDING, NOTIFIED SUPERVISOR, & OPS | 02-00-E-RLY-87/TB/A
390596 | CR | 20190302 |  | 4 | BLD 88 HVAC Needs Maintenance |  |  |  | N | YES | <D> **** Detailed Description **** BLD 88 HVAC Needs Maintenance, not working as designed. Temperature is 65 degrees, HVAC has not ran for past 8 hours. <I> **** Actions Taken **** Shift Manager Notified, Ops Walked down. CR/WR Initiated. <N> **** Equipment Description **** Building 88
390597 | CR | 20190302 |  | 3 | Lack of Procedural Guidance for Loss of SHF0 |  |  |  | N | NO | <D> **** Detailed Description **** On 2/25/19 the 115kV/13.8kV SH-F0 transformer faulted and dropped the buses supplied. This resulted in a loss of the flocculator, demineralized water trailer and autostart of FP-P-110. The only procedure dealing with this bus is FCEI-3.4.1, which is written for planned outages of the facilities buses. Consider creating a guidance in a new or existing procedure (i.e., ARP) to provide for prompt action to secure FP-P-110 and orderly shutdown and restart of affected plant equipment. <I> **** Actions Taken **** Discussed with FP Engineer and Facilities.
390615 | CR | 20190302 | CAQ | D | CRD-HCU-0235 required entry into ABN-ROD | Y | N |  | N | YES | <D> **** Detailed Description **** While performing OSP-CRD-C703 Control rod settle time testing CRD-HCU-0235 required entry into ABN-ROD. A high d/p of 295psid was used per ABN-ROD to withdraw from position 00 to 02. Drive header d/p was returned to 262psid and CRD-HCU-0235 was withdrawn to 48 with no other issues. | 02-00-CRD-HCU-0235
390616 | CR | 20190302 | CAQ | D | CRD-HCU-3403 double notched from position 00 to 04 | Y | N |  | N | YES | <D> **** Detailed Description **** While performing OSP-CRD-C703 Control rod settle time testing CRD-HCU-3403 double notched from position 00 to 04 while perform settle time testing. Testing was completed SAT at position 04 with a settle time of 1.10 seconds. However it was noted that the direction control valves may need adjusting. The control rod was observed to withdraw faster than normal and insert slower than normal. CRD D/P on CRD-DPI-602 was 262psid , CRD cool water flow on CRD-FI-605 was 63gpm with CRD insert stall flow indicating high on CRD-FI-604 at 4.2gpm steady. ABN-ROD was entered and attachment 7.1 filled out. | 02-00-CRD-HCU-3403
390617 | CR | 20190302 |  | 4 | FLM steam leak walkdown at 70% power | N | N |  | N | YES | <D> **** Detailed Description **** During the TG walkdown per WO 02134901, the following leaks were found: --COND-LCV-32B W3 packing leak --BS-MANWAY-6/2 S5 leak, first identified in AR 374685 (there are 2 leaking manways, 6/2 AND 4/3). --HD-LS-6AHT potential S4 leak below level switch. Hard to tell due to massive water leak (RFW-V-111A, WO 02129073) below the switch. --Unknown epn, S5 leak at ceiling south of 6A heater. This valve has leaked before, just need to figure out the epn.+ <I> **** Actions Taken **** Updated FLM maps. <N> **** Equipment Description **** TG 471 heater bay | 02-00-BS-MANWAY-6/2,02-00-COND-LCV-32B
390618 | CR | 20190302 | CAQ | D | E-CB-B7 open indicating light socket | Y | N |  | N | YES | <D> **** Detailed Description **** The green open indicating light socket appears to have some broken pieces of an old light bulb stuck inside preventing light bulb replacement. <I> **** Actions Taken **** initiated CR <N> **** Equipment Description **** SM 7 Switch Gear | 02-00-E-CB-B/7
390619 | CR | 20190302 |  | 4 | Steam Leak on trap upstream of HCO-V-T3ED | N | N |  | N | YES | <D> **** Detailed Description **** Stream Leak on trap upstream of HCO-V-T3ED, leak appears to be on the union out of the trap to the blowdown valve. <I> **** Actions Taken **** wr/cr | 02-00-HCO-V-T3ED
390620 | CR | 20190302 | CAQ | C | RHR Sys B Discharge Pressure High and rising. | Y | Y |  | N | YES | <D> **** Detailed Description **** RHR System B Discharge Pressure is High and rising. RHR -PI-612B denotes 400 psig. TDAS pt. X076 denotes 381 psig. Annunciator H13-P601.A2,5-6 states RHR-PIS-22B alarms at GE 455 psig. Pressure has been rising since RHR-P-2B was secured on 28 FEB 19 0302. Current rate of pressure rise is about 1 psig/Hr. <I> **** Actions Taken **** Notified the CRS and Shift Manager. Reference T.S. 3.4.6, 3.4.9, 3.5.1, 3.6.1.5, 3.6.2.3 and 3.6.1.3. Reference LCS 1.6.1.5. This event is similar to the pressurization of RHR Sys A on 12 JAN 19. Reference CR 388782 and WR 29146584. Preparing to vent RHR-SYS-B per OSP-RHR-M102. | 02-00-RHR-P-2B
390621 | CR | 20190303 |  | 4 | Received Main Transformer TR-M2 Trouble Alarm. | N | N |  | N | YES | <D> **** Detailed Description **** Received Main Transformer TR-M2 Trouble, H13-P800.C4,2-1, Alarm. OPS 4 reports the alarm was due to Fast Pressure or Powerstatus lamp 63S illuminated. The Reset Button was depressed per the ARP and ABN-TRANSFORMER and the alarm has cleared. <I> **** Actions Taken **** Notified the CRS and SM. Entered and subsequently exited ABN-Transformer. DGA analyzer verified normal operation. Alarming module could not be determined. | 02-00-E-TR-M2
390622 | CR | 20190303 |  | 3 | ABN-Transformer step 7.4.14a |  |  |  | N | YES | <D> **** Detailed Description **** While performing ABN-Transformer step 7.4.14a was not fully completed as the module in alarm could not be identified. The following step resets the alarm which cleared the unidentified module. The procedure and equipment needs enhancement to better define the modules and label them by EPN. <I> **** Actions Taken **** Informed MCR, & System Engineer | 02-00-E-TR-M2
390623 | CR | 20190303 |  | 4 | SA-V-23 appears to be mostly blocked | N | N |  | N | YES | <D> **** Detailed Description **** SA-V-23, the filter blowdown valve used to depressurize the RWCU demin air header, appears to be mostly clogged. Very little air comes out of it when open, and the header consequently takes very long to depressurize as indicated on SA-PI-71. This results in longer backwash times for the RWCU demins. Please unclog this valve. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 467 off platform near RWCU precoat tank. | 02-00-SA-V-23
390630 | CR | 20190303 |  | 4 | SMA-HC-1 has a lower coil leak in almost same spot. | N | N |  | N | YES | <D> **** Detailed Description **** SMA-HC-1 has a lower coil leak in almost same spot that was repaired in WO 2126345, adn reported in WR 29139942. Please evaluateand repair. <I> **** Actions Taken **** wrote WR/CR | 02-00-SMA-HC-1
390631 | CR | 20190303 |  | 4 | Opputunity to minimize universal waste generation at CGS. |  |  |  | N | YES | <D> **** Detailed Description **** ARs 390220 and 390508 document lighting issues in the RWCR and MCR. This would be a perfect oppurtunity to NOT replace the fluorescent bulbs! Instead this is a beautiful orrputunity to allow/drive completion of the EC (Believed to be 17267 for MCR) and begin replacing the mercury containing fluorescent lamps with LED lamps. Though it would take time and effort to accomplish it seems that relamping the MCR whilst on the cusp of having the ability of installing LED lamps would be wastful. Please evaluate if this can be made a priority and allocate resources to acomplish it. This AR doesn't talk to lighting in the remained of the power block which also has numerous AR's. <I> **** Actions Taken **** Discussed with supervision. Talked with others about EC status. Elected to generated AR to help raise awreness and hopefully get LED lighting. | 02-00-CGS-BLDG-MISC
390633 | CR | 20190303 |  | 4 | HTP-FP-5, 3F low temp light blinking | N | N |  | N | YES | <D> **** Detailed Description **** HTP-FP-5 in the CST pit, 3F low temp light is blinking | 02-00-HT-HTP-FP/5
390634 | CR | 20190303 |  | 4 | Heating steam union leak | N | N |  | N | YES | <D> **** Detailed Description **** The heating steam piping union joint between HCO-V-T3EA and HCO-V-T3ED is leaking and condensing resulting in a large puddle of water on the T501' west side floor. The union has cold lagging below it around the strainer blowdown valve and laced hot lagging above the steam inlet valve. The laced lagging will need to be removed to affect repairs to the joint. <I> **** Actions Taken **** Notified CRS and SM. Requested laborers clean up and contain the water. | 02-00-HCO-V-T3EA
390635 | CR | 20190303 |  | 3 | DataGlance eSOMS issues |  |  |  | N | NO | <D> **** Detailed Description **** Issue with interface between DataGlance & eSOMS. WO 02137757 PPM 15.3.16 is at complete status with a quality record already generated, however in eSOMS the surveillance still shows up as an open surveillance. The attributes screen had the closure date and time already filled in however the open item was still checked, this should have been taken care of automatically. <I> **** Actions Taken **** Informed supervision and unselected the open item box manually.
390636 | CR | 20190303 |  | 4 | Relief for SA-RV-265 has started flowing again. | N | N |  | N | YES | <D> **** Detailed Description **** Camera installed for AR 388627 shows water flowing at about a 1/3 pencil stream of water. This camera is showing that what ever adjustments/repairs that were made may be degrading and will need to be addressed. <I> **** Actions Taken **** Informed supervision. attached Video to EDMS. Wrote CR/WR. | 02-00-SA-RV-265
390638 | CR | 20190303 |  | 4 | Loss of NVRP1 | N | N |  | N | YES | <D> **** Detailed Description **** CAS had a momentary loss the NVRP1 Video feed. <I> **** Actions Taken **** The video feed was restored. A walk up of IDS was performed to confirm video function. Condition Report intiatied. <N> **** Equipment Description **** CAS
390639 | CR | 20190303 |  | 4 | Cooling tower 1B DOOR is ajar. | N | N |  | N | YES | <D> **** Detailed Description **** Door to cooling tower 1b basin is ajar. A build up of ice is preventing closing the door (this is the large door to drive into the basin) . <I> **** Actions Taken **** Informed supervision <N> **** Equipment Description **** CW tower 1b door
390640 | CR | 20190303 |  | 3 | FLLLP MELLA Boundary critical parameter |  |  |  | N | NO | <D> **** Detailed Description **** Recommend incorporate FLLLP critical Parameter into the Thermal Limits section of Plant Overview on TDAS and PPCV so SRO/IA and RO can closely monitor the parameter. <I> **** Actions Taken **** Wrote the CR. . Per AR ASGN 350488-01, this was supposed to be done as part of the MUR project. <N> **** Equipment Description **** TDAS/PPCV
390641 | CR | 20190303 |  | 4 | BRE 37 | N | N |  | N | YES | <D> **** Detailed Description **** The UPS in BRE 37 needs maintenance. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Security notification made, CR/WR generated <N> **** Equipment Description **** BRE 37 SE corner of the PA near PH 1A
390642 | CR | 20190303 | CAQ | C | SW System Locked Valve Questions |  |  |  | N | NO | <D> **** Detailed Description **** SW-V-48 is the SW-SYS-A supply to LPCS-M-P/1. This valve is specified to be OPEN per OSP-SW-M101 (not LOCKED OPEN). SW-V-48 is NOT in PPM 1.3.29, Locked Valve Checklist. SW-V-22A, -22B and -22C ARE listed in PPM 1.3.29 as LOCKED OPEN but are not denoted LO on M524-1 or M524-2 as L.O. These valves are required to LOCKED OPEN in OSP-SW-M101 and -M102. Two suggestions: 1. Update M524-1 and M524-2 to show SW-V-22A, -22B and -22C as L.O. 2. Evaluate changing SW-V-48's position from OPEN to LOCKED OPEN and update OSP-SW-M101, PPM 1.3.29 and M524-1 to reflect this. Making this change would eliminate any dose required to go up to this valve from the mezzanine, but more importantly would prevent any risk (industrial or plant risk) associated with manually checking the valve's position. This has NO impact to LPCS or SW system Operability. <I> **** Actions Taken **** This was discovered while investigating the reason for WO 02131769, OSP-SW-M101 (10:00 DAYS) SW A VLV POS. VERIF being coded as MEDIUM risk.
390643 | CR | 20190303 |  | 4 | OG-TIS-601B actual temp LT low setpoint, but no alarm. | N | N |  | N | YES | <D> **** Detailed Description **** OG-TIS-601B actual temperature indication is 280Â°F, and its low temperature alarm setpoint is 300Â°F. This should cause RECOMBINER B INLET TEMP LOW, H13-P672.A9.2-2, alarm, but the alarm is clear. . RECOMBINER A INLET TEMP LOW, H13-P672.A9.1-2, alarm is currently locked in, and its input is OG-TIS-601A. OG-TIS -601A actual temperature is 410Â°F, well above the low temperature alarm setpoint of 300Â°F, so RECOMBINER A INLET TEMP LOW, H13-P672.A9.1-2, alarm should not be in alarm. . Perhaps the wiring from the TIS's to the alarms have been swapped. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-OG-TIS-601B
390645 | CR | 20190303 |  | 4 | Camera cleaning list |  |  |  | N | YES | <D> **** Detailed Description **** Following cameras need to be cleaned: CCTV01, CCTV13, CCTV14,CCTV15, CCTV17, CCTV32, CCTV42, CCTV45 <I> **** Actions Taken **** CAS issued camera list, notified supervision, WR/CR generated <N> **** Equipment Description **** Cameras located inside the PA
390646 | CR | 20190303 |  | 3 | NLO Watch Standing Qualification Near Miss |  |  |  | N | NO | <D> **** Detailed Description **** During shift turnover a new EO was scheduled to stand TGSS. New EOâ€™s were told by training that they were qualified to stand the EO position of TGSS (Turbine Safe Shutdown). Prior to taking the watch the new EOâ€™s quals were checked in PQD and they were not qualified to stand the watch. There was an extra EO on shift who was able to take the watch. The new EOâ€™s did complete the qual group EOAK (Safe Shutdown Operator) and are green in PQD. However, to stand the position of TGSS EOâ€™s must be qualified the duty area EOSS (Safe Shutdown EO Qualification). The new EOâ€™s have not been assigned to any duty areas and are not SCBA qualified (Qual Group PA04) which is a required qual group for EOSS. It appears the qualification manual MAN QUAL 4.7 (Operations Duty Area) or PQD duty area were not adequately checked prior to informing the new EOâ€™s that they were qualified to stand TGSS. <I> **** Actions Taken **** Informed Supervision
390647 | CR | 20190303 | CAQ | D | E-BU-WFB441/1 fault light is lit, (5 blinks). | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-WFB441/1 fault light is lit, (5 blinks). <I> **** Actions Taken **** wr/cr | 02-00-E-BU-WFB441/1
390648 | CR | 20190304 |  | 3 | Procedure change for SOP-TMU-Start. |  |  |  | N | NO | <D> **** Detailed Description **** SOP-TMU-START step5.61.e, 5.7.1.e, 5.6.4.c and 5.7.4.c both reference "test the ground indicating lights to ensure they illuminate". these lamps have been removed and replaced with a ground fault relay. <I> **** Actions Taken **** Wrote CR to effect change
390649 | CR | 20190304 |  | 4 | ASD transformers are at a negative pressure | N | N |  | N | YES | <D> **** Detailed Description **** RRC-TR-ASD/A/2 was at -1.5# RRC-TR-ASD/A/1 was at -0.5# RRC-TR-ASD/B/2 was at -0.25# RRC-TR-ASD/B/1 was at -1.0# Please evaluate adding N2 to the transformers <I> **** Actions Taken **** wrote CR/Wr | 02-00-RRC-TR-ASD/A/1,02-00-RRC-TR-ASD/A/2,02-00-RRC-TR-ASD/B/1,02-00-RRC-TR-ASD/B/2
390650 | CR | 20190304 |  | 4 | COND-P-1C Oil Level low | N | N |  | N | YES | <D> **** Detailed Description **** The oil in the lower sight glass on COND-P-1C is at the low mark of 1/8" below midline. <I> **** Actions Taken **** Informed CRS | 02-00-COND-P-1C
390651 | CR | 20190304 | CAQ | D | MT-ELEV-4 Outer Door C-400 on 501â€™ Jammed Open | N | N |  | N | YES | <D> **** Detailed Description **** The red plastic lower door guide on the RW 501â€™ outer elevator door is broken and the fastener that attached it is now lodged in the door track preventing the outer door from closing. Pieces of broken red plastic were found outside of the elevator door. This door (C-400) is a fire door. The previous door guides were metal and more robust, consideration should be given to replace the plastic door guides with the old metal style. Please investigate and repair. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** RW 501' | 02-00-MT-ELEV-4
390652 | CR | 20190304 |  | 4 | CAS SCS Requires Maintenance |  |  |  | N | YES | <D> **** Detailed Description **** System not operating as designed. Issue identified during Observation 2019-1232. <I> **** Actions Taken **** CR Initiated, Security Management Notified. <N> **** Equipment Description **** CAS
390662 | CR | 20190304 | CAQ | D | M&TE Rejected |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0063208 AVO Biddle Megger- model BM11D found OOT. EFIN Eval: The unit provided output voltage that was higher than the value selected. For Meggering, this is conservative. Rejected- MFG can no longer support the BM11 unit for repairs and calibration. DEF #6952A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
390663 | CR | 20190304 |  | 4 | PM not performed by scheduled late date |  |  |  | N | NO | <D> **** Detailed Description **** WOT 02131736-01 (RWP Reviews and Terminations) was not performed by the PM late date of 03/03/2019. This task is typically performed every Sunday on dayshift; however, the shift crew on dayshift did not have any individuals qualified to perform this task. <I> **** Actions Taken **** Assigned a qualified HP Technician to complete the WOT on 03/04/2019.
390668 | CR | 20190304 | CAQ | D | High water accumulator 22-03. | Y | N |  | N | YES | <D> **** Detailed Description **** High water accumulator 22-03. OPS 2 corrected IAW ARP. | 02-00-CRD-TK-125/2203
390670 | CR | 20190304 |  | 3 | OSP-SW-M101 needs editorial change |  |  |  | N | NO | <D> **** Detailed Description **** OSP-SW-M101 needs editorial change. On page 7 of 23 step 7.1.19 SW-V-827A is located south of CCH-CR-1A and is actually NORTH of CCH-CR-1A. <I> **** Actions Taken **** Wrote this CR and notified supervision
390671 | CR | 20190304 |  | 4 | WOA-HC-1 "O" & "P" have steam leaks. | N | N |  | N | YES | <D> **** Detailed Description **** WOA-HC-1 "O" & "P" coils have developed new steam leaks. see the attributes screen in the work requests for pictures. Due to the current outside temperatures the coils were left in service. Informed the shift support supervisor. <I> **** Actions Taken **** Informed supervision and wrote this AR/WR. <N> **** Equipment Description **** W 487 R6/15.9 | 02-00-HS-V-W9O,02-00-HS-V-W9P
390678 | CR | 20190304 |  | 4 | Bldg 9 kitchen sink drain needs repair | N | N |  | N | YES | <D> **** Detailed Description **** Kitchen sink drain â€œTâ€ needs to be reworked. These two connections pull apart easily (the vertical one is also weighted down by the water filter tie wrapped to the drain piping) and are causing water damage to the sink cabinet. Picture showing connections needing repair can be found in EDMS docs of the CR. <N> **** Equipment Description **** Building 9 kitchen sink drain
390679 | CR | 20190304 | CAQ | C | FP-PI-W13B replacement | N | N |  | N | YES | <C> CR edited at the request of Initiator to change to the correct EPN (FP-PI-W13B). <D> **** Detailed Description **** while performing 15.1.16 FP-PI-W13B was found to be defective. Needs to be replaced <N> **** Equipment Description **** CWPH | 02-00-FP-V-W13/244
390681 | CR | 20190304 |  | 3 | PPM 1.9.13 procedure revision needed (Transformer yd access) |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.9.13 was recently revised to exempt Operations department personnel from qual group SFBD. This procedure needs to be revised to state Operations personnel rather than Operations watchstanders. This could create confusion in outages when ops personnel (electrical production) are needed to enter the transformer yard. This procedure revision needs to be active prior to the start of R24. <I> **** Actions Taken **** Contacted Ops procedure group. Initiated CR.
390682 | CR | 20190304 | CAQ | D | (QA) CMS-SR-13 bottle rack clamps incorrectly installed | Y | Y |  | Y | YES | <D> **** Detailed Description **** (QA) CMS-SR-13 bottle rack clamps on two of the five cylinders incorrectly installed. During a quality field walkdown an auditor identified that two of the five bottle clamps on the west side of CMS-SR-13 bottle storage rack have the "ears" pointing up instead of down. These are on the bottles for CMS-TK-1302 and CMS-TK-1303. All five clamps on the east side are in the correct orientation per CVI 210A-04,240. Refer to pictures and snip of CVI in EDMS. <I> **** Actions Taken **** Discussed this issue with an EFIN engineer who stated that the pictures show the bottles are adequately restrained and it appears to be a configuration problem. Initiated this CR & WR and discussed with Operations. | 02-00-CMS-TK-1302
390683 | CR | 20190304 | CAQ | D | CRD-LIS-601A was found slightly out of tolerance | Y | N |  | N | NO | <D> **** Detailed Description **** While performing ISP-CRD-X301 (WO# 02122595-01), we found CRD-LIS-601A to be very slightly out of tolerance for table 7.5a (desired was 16.67 mA +/- 0.03 mA and our value was 16.72 mA). <I> **** Actions Taken **** informed operations and Adjusted SAT, per the procedure, to a value of 16.68 mA
390685 | CR | 20190304 | CAQ | C | need editorials for step 7.13.12 of ISP-CRD-X301 |  |  |  | N | NO | <C> MRT change Priority/Severity to CAQ C/MNTPROG on 03.07.2019 (not an editorial change). Create Corrective Action(s). <D> **** Detailed Description **** The last to EPNs of step 7.13.12 in ISP-CRD-X301 are CRD -LIS-602C and CRD-LIS-602D. They should be CRD-LIS-601C and CRD-LIS-601D <I> **** Actions Taken **** worked with supervisor, CRS and SM and made editorials. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
390686 | CR | 20190304 |  | 3 | Work Order removed from schedule |  |  |  | N | NO | <D> **** Detailed Description **** WO 02113390, E-DISC-7AA3B locking pin broke was removed from the TR-B window on 3/2/19. This work would have delayed BPA from performing assessory testing during the TR-B window. The E-DISC-7AA3B was correctly scheduled however initial work delays due to eSOMs and grounding breaker installation issues prevented BPA from starting assessory testing which was a higher priority than the disconnect issue. Disconnect work does not effect operation of TR-B as the disconnect fully functions in its currenct configuration. This work only repaired the disconnect handle locking spring. <I> **** Actions Taken **** Removed from schedule Tracking only Action: Work Management reschedule. <N> For trend, lessons learned information, no additional actions required.
390687 | CR | 20190304 |  | 4 | Personal Medical Condition - Transport Off-Site | N | N |  | N | NO | <D> **** Detailed Description **** On Monday, March 4, 2019 at 10:14 a.m a 2222 call went out concerning an EN employee needing medical care at the security checkpoint. Occupational Health RN and EN advanced first aiders provided care to the individual until HFD paramedics arrived. Hanford Fire Department (HFD) Medic 1923 and Ladder 1923 arrived at 10:26 a.m. The patient was further evaluated at the scene by HFD and transported to the hospital for further evaluation. Medic 1923 transported the patient to Kadlec Medical Center at 10:48 a.m. <I> **** Actions Taken **** Emergency Preparedness was notified for ERO purposes. Wrote this CR to docment response times, etc.
390688 | CR | 20190304 |  | 3 | Missed meeting |  |  |  | N | NO | <D> **** Detailed Description **** Three Maintenance personnel did not attend PCSC Committee meeting. Shop members include I&C, Electrical and Mechanical. Notifications were made to shop leads. <I> **** Actions Taken **** CR initiated
390689 | CR | 20190304 |  | 3 | CY2018 CGS Tier Two Report Error |  |  |  | N | NO | <D> **** Detailed Description **** In accordance with 40 Code of Federal Regulations 370, an annual Emergency and Hazardous Chemical Inventory (Tier Two) Report for Columbia Generating Station must be submitted to the Washington State Emergency Response Commission (SERC), Benton County Emergency Management, and local fire department. Per AR 387868-02, the Tier Two report must undergo peer/technical review and reviewed and approved by the CGS Plant General Manager and Environmental and Regulatory Programs. The calendar year (CY) 2018 CGS Tier Two Report was submitted by the Chemistry preparer to the SERC prior to Environmental and Regulatory Programs (E&RP) Manager review and approval. In addition, the incorrect version of the report was signed by the Plant General Manager. This error was discovered by E&RP after all of the reviews were completed. The error was corrected prior to submittal due date. Recommend assign to Chemistry. <I> **** Actions Taken **** Discussed with Environmental and Regulatory Programs Manager, Chemistry Operations Supervisor, and CGS Chemical Management Lead. No additional action is required per the Chemistry Operations Supervisor.
390690 | CR | 20190304 |  | 4 | Personal vehicle struck in parking lot. |  |  |  | N | NO | <D> **** Detailed Description **** Personal vehicle was struck in the parking lot between 0600 and 1530. Accident was not reported, owner of the vehicle discovered it when preparing to exit site. <I> **** Actions Taken **** Individual notified security and Benton County Sheriff.
390691 | CR | 20190304 | CAQ | C | need editorials for step 7.13.12 of ISP-CRD-X305 |  |  |  | N | NO | <C> MRT change Priority/Severity to CAQ C/MNTPROG on 03.07.2019 (not an editorial change). Create Corrective Action(s). <D> **** Detailed Description **** The last two EPNs of step 7.13.12 in ISP-CRD-X305 are CRD -LIS-602B and CRD-LIS-602D. They should be CRD-LIS-601B and CRD-LIS-601D. <I> **** Actions Taken **** Documented Editorial in ISP-CRD-X305 and Wrote CR <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
390692 | CR | 20190304 | CAQ | C | VESDA Zone 20 Fault | N | Y |  | N | YES | <D> **** Detailed Description **** FP-CP-ISP/1 indicates a fault in zone 20. When attempting to reset the fault, the local alarm and remote alarms in the control room momentarily clear but then immediately come back in. This fault existed prior to turnover of the system from the vendor to Operations. Making identification of exactly what is affected by VESDA zone 20 is the fact that zone 20 listed in LCS 1.10.6 is for the RW 437 Room 106, not anything to do with the vital island which is where the VESDA system samples to identify issues. VESDA zones listed in the LCS are 22, 23, and 25. Request assistance in determining and correcting the cause of the fault and what areas are affected for the purpose of issuing any required impairments. <I> **** Actions Taken **** Notified CRS. | 02-00-FP-CP-ISD/1
390693 | CR | 20190304 |  | 4 | MCR phone should be moved to avoid damage to plotter |  |  |  | N | NO | <D> **** Detailed Description **** During a housekeeping tour it was noticed that the phone in the back of the MCR is very poorly positioned in regards to the new plotter. The phone cord can dangle down and get snagged on and potentially break a very expensive piece of printing equipment. Recommend moving the handset to East side of the pillar to allow better access to the phone and prevent any equipment damage. <I> **** Actions Taken **** Wrote CR/WR. <N> **** Equipment Description **** Phone in the back of the MCR by the plotter
390694 | CR | 20190304 |  | 4 | Closed stairwell Lower door hinge is broken |  |  |  | N | YES | <D> **** Detailed Description **** Facilities labors drove by Cooling tower 1A and noticed the door looked like it was sitting funny. They stopped and found that there was pieces of the top of the door laying on the ice and the bottom hinge was broken. The ice was built up pushing the door off the middle and top hinges. Pictures were added to the EDMS file. <I> **** Actions Taken **** Labors put the door in a safe condition by removing it and placing it in the closed stairwell. Supervisor was notified of the issue. <N> **** Equipment Description **** Closed stairwell | 02-00-CW-CT-1A
390696 | CR | 20190304 |  | 4 | MC-6L Ground Fault Light Socket Broken | N | N |  | N | YES | <D> **** Detailed Description **** MC-6L Ground Fault Light Socket Broken. Bulb was burnt out so the bulb swapped out but the socket was observed to not be working. <I> **** Actions Taken **** CR/WR initiated. Supervision Notified. <N> **** Equipment Description **** MC-6L Ground Fault Light Socket not working.
390697 | CR | 20190304 |  | 4 | Cooling jacket sample analysis outside of hold-time |  |  |  | N | NO | <D> **** Detailed Description **** The hold time for ammonia and ATP analysis for the DG-1C cooling jacket sample was not met for the sample collected 2/27/2019. <I> **** Actions Taken **** Notified chemistry specialist. Sample results will be annotated with hold-time discrepancy. Recommend CR for trending. . Per PPM 12.14.11 Section 2.0, Discussion "ATP and ammonia help to trend biological activity and inhibitor degradation. ATP samples need to be delivered to the offsite lab as soon as possible because they need to be analyzed within 24 hours of sampling."
390698 | CR | 20190304 |  | 4 | Insufficient lighting 548' Rx building CMS-SR-21 room |  |  |  | N | YES | <D> **** Detailed Description **** Insufficient lighting 548' Rx building CMS-SR-21 room. 4 out of 6 halogen bulbs out. If any additional lighting goes out the room would not be safe to work in without supplemental lighting. %2fqT0H&id=8BE87F7677E3A77948712B58751C21B90811CCEC&thid=OI <I> **** Actions Taken **** CRS informed <N> **** Equipment Description **** Lighting 548' Rx building CMS-SR-21 room
390699 | CR | 20190304 | CAQ | D | TEA-SR-26 display status code "no flow control" | N | Y |  | N | YES | <D> **** Detailed Description **** TEA-SR-26 display status code "no flow control" This indicates that the SR has automatic control of the flow control valves and that they have been taken to full open to compensate for system condidtions. No action required currently but system will need to be cleaned to allow flow to move more freely. <I> **** Actions Taken **** Specialist informed. | 02-00-TEA-SR-26
390700 | CR | 20190304 |  | 3 | 12.9.13 procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** suggested enhancement to include a section for adjusting MUD product flow in auto/manual operation. <I> **** Actions Taken **** Detailed procedural revision supplied to specialist.
390701 | CR | 20190305 |  | 4 | BRE 37 PA Speaker Requires Maintenance |  |  |  | N | YES | <D> **** Detailed Description **** The PA Speaker for BRE 37 is not functioning as designed and requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervision notified. Initiated CR/WR. <N> **** Equipment Description **** BRE 37 PA Speaker
390713 | CR | 20190305 |  | 3 | SOP-CW-CHEM requires enhancement |  |  |  | N | NO | <D> **** Detailed Description **** SOP-CW-CHEM requires enhancement. Step 4.10, NPDES Blowdown Limitations, contains a NOTE in the step referring to specific NPDES limits. The maximum pH (9.5) and amount of accumulated time (7 hours 26 minutes) that we are allowed outside of our NPDES limit listed in this NOTE do not match the requirements as listed in the NPDES permit. The upper pH limit listed in the permit is 10.0 standard units and the maximum time allowed per month is 7 hours and 30 minutes. <I> **** Actions Taken **** Initiated this condition report and notified the procedure sponsor if discrepancy. <N> Procedure update only, procedure wording did not result in NPDES permit non-compliance.
390714 | CR | 20190305 |  | 4 | Fail to finish pre-outage work for quadvoter SOV replacement |  |  |  | N | NO | <D> **** Detailed Description **** CID 21911 has an AR hold on it (AR 387755) to be returned to the OEM to have the correct nameplate installed. As a result the solenoid valves are not available to perform the pre-outage task to inspect and flush for foreign material. This task will need to be performed once the valves have returned from the OEM. <I> **** Actions Taken **** Notified Manager and Work Week Manager of the fail to finish.
390715 | CR | 20190305 |  | 4 | Wet 14 flange leak | N | N |  | N | YES | <D> **** Detailed Description **** While performing 15.1.16 a small leak of about 3 drops per minute was found on a bolted flange at Wet 14 inside Building 62 electical camera shop. Flange bolts may need to be tightened. <N> **** Equipment Description **** Wet 14
390726 | CR | 20190305 |  | 3 | Chemistry CT Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** Student failed a continuing training examination for CH001806. This PQD code does not affect qualifications. eTAR class ID 396923. The Chemistry supervisor has been informed. Remediation to be determined.
390727 | CR | 20190305 |  | 4 | Flocculator requires what may be too much backwashing | N | N |  | N | YES | <D> **** Detailed Description **** Currently the flocculator requires backwashing 1 to 2 times per shift. This is considerably more than normal for this time of year even with the current demineralized water needs. Suspect that it may be time to consider either adding filter media if there has been media loss (last done 01044200 2002), replacing the media (last replaced WO 01162454 8/6/10), cleaning the settling tubes and chamber 1&2, or adjusting the chemical addition pumps more. Please investigate and Correct the percieved issue. A look back through eSOMS rounds at the few parameters the OPS takes on PWC-FU-1 does NOT show any abnormalities in headloss, inlet turbuidity, or effluent turbuidity. This doesn't seems to prevent PWC-FU-1 from generating good water but the throughput is substandard at best. This is requiring an excessive amount of time on the part of OPS4 to address. <I> **** Actions Taken **** Discussed with peers, informed supervision, wrote this ar. | 02-00-PWC-FU-1
390729 | CR | 20190305 |  | 4 | Lighting in RW 487' RW Chemistry Lab | N | N |  | N | NO | <D> **** Detailed Description **** There are 10 lighting housings that are out or nearly out in the chemistry lab. That amounts to almost half of the lab lighting. The lights need to be changed out. <I> **** Actions Taken **** Notified MCR, Chemistry Supervision. <N> **** Equipment Description **** Chemistry lab RW 487' main lab area
390731 | CR | 20190305 |  | 3 | PPM 1.3.76 could be enhanced to align online and outage. |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.3.76 is silent on responsibilities for outage manager and Assistant outage manager.Section 5.3.4 "Conduct a Challenge Meeting" describes the online process but is silent on outage challenge meeting even though the same process is followed just at diffent times. <I> **** Actions Taken **** Discovered during a HRWP challenge meeting and documented in CR.
390732 | CR | 20190305 |  | 4 | (NRC) The NRC residient is questioning VESDA system status |  |  |  | N | NO | <D> **** Detailed Description **** The NRC resident has raised questions concerning a main control room VESDA system trouble alarm and a local Zone 20 fault alarm and the impact on the ability of the system to perform it's required functions per LCS 1.10.6. The Zone 20 alarm is on FP-CP-ISP/1. This control panel has four VESDA inputs from detection zones 22 and 23 on RW 467' vital island. These four channels were declared non -functional on 3/4/19 under CR 390692. <N> **Clarification Notes** The VESDA panel FP-CP-ISD/1 has four input channels; FP -ISD-1/1A, FP-ISD-1/1B, FP-ISD-1/1C, and FP-ISD-1/1D. The VESDA panel is completely seperated from detection zones 22 and 23 and does not come from zones 22 and 23. FP-ZONE-22 and FP-ZONE-23 now only have duct detectors remaining, as the ionization smoke detectors were removed by EC 16066. . Siemens vendor documentation describes the difference between a MINOR and MAJOR fault. A fault 20 whish is locked in on FP-CP-ISD/1 is only a minor fault. Only URGENT fault would adversely affect detector functionality.
390733 | CR | 20190305 |  | 4 | Vendor dose was budgeted for Rx maint (NDE) instead of ENG |  |  |  | N | NO | <D> **** Detailed Description **** On or about 02/25/18 there were two NDE Vendor technicians brought in to assist with the installation of RWCU Ultrasonic Flow measuring equipment. Because the nature of their work is Non Destructive Examinations, the ALARA Planning and dose budget reflected that the estimated dose for this work would be taken by NDE (Rx Maint). When the dose report came out the day after the work completed, the Vendor dose had been recorded as â€˜Engineer Deptâ€™ dose. This resulted in ENG Dept significantly exceeding their weekly and monthly dose goal, and Rx Maintenance coming in well below their dose goal. A similar situation occurred in R23 outage with the FAC supplemental help. When supplemental personnel are brought in to assist us with outage or other work, the organization code number that they are brought in under is not visible during the normal Radiological planning of their Work Orders/ ALARA Tasks. For instance, the FAC (Flow Accelerated Corrosion) workers will be brought in by Engineering, but may have a resource type of VEND and a resource code of NDE or SPEC. Rad Planning needs to be informed, either by group bringing in vendor (Dose Champion) or the Work Order Planner, what organization code number the Vendors are being brought in under so that the dose can be correctly distributed in the dose budget. <I> **** Actions Taken **** Documented this CR. Ensured that the FAC R24 dose expenditure will be in the Engineers' dose budget, and will show up on the dose report for outage for Engineers.
390734 | CR | 20190305 |  | 4 | Dewatering pump DW-P-2 on SERDS Skid Inoperable |  |  |  | N | YES | <D> **** Detailed Description **** While dewatering condensate resin liner, SERDS skid pump DW-P-2 became inoperable. <I> **** Actions Taken **** Shut down SERDS skid and notified Superision and Chem/RP Support Supervisor. Initiated CR. <N> **** Equipment Description **** Inoperable pump DW-P-2 at 437'RW resin processing area
390735 | CR | 20190305 |  | 4 | HCP-2 CP-31 trouble and FCP-3 drop 16.4 locked in trouble | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of ppm 15.2.31 step 7.8.4, the trouble light came on as expected on HCP-2 CP-31 module. This light did not clear during the restoration step 7.8.6 as it should. Craft stopped and contacted supervision. This issue has happened before and CR# 364001 was written and WR# 29134588 initialized to address the problem. <I> **** Actions Taken **** Informed supervision and completed restoration. More troubleshooting is needed to addess the issue. <N> **** Equipment Description **** Primary guard house halon system
390736 | CR | 20190305 |  | 3 | CAS-C-1A, minor air A2 leak at fitting | N | N |  | N | YES | <D> **** Detailed Description **** During the PMT of CAS-V-284A a small A2 leak was observed at the 2" aftercooler tubing connection from CAS-V-284A to CAS-HX-6A. This connection was observed to be in poor condition when removed and cleaned. It was inspected and due to lack of parts it was reused. PMT was completed and check valve functioned properly. PMT was completed and check valve functioned properly. Recommend parts replacement during next scheduled maintenance. <I> **** Actions Taken **** Notified operations Generated WR, Identified parts required and created CID's | 02-00-CAS-C-1A
390737 | CR | 20190305 |  | 4 | Degraded Turbine Building (441') door along the main hall | N | N |  | N | NO | <D> **** Detailed Description **** Door T-114 between the main RCA 441' Cooridor and the Turbine Building is degraded along the upper hinge. It appears the hinge side of the door is separating from the main part of the door along the top corner down through the upper hinge. This is causing the upper corner to sag into the other door so that the door isn't closing correctly (or fully) on its own. Signage doesn't indicate this is a fire door, but it does identify it as a security door with instructions to contact security before blocking open. This is a high traffic door during outage, and should be evaluated for safety reasons. <I> **** Actions Taken **** CR generated for evaluation and tracking. Took/attach picture to CR. Notified Supervision <N> **** Equipment Description **** Door T-114 : RCA 441' Cooridor into Turbine Building
390738 | CR | 20190305 | CAQ | D | REA-E/S-613B Power Supply | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During ISP-REA/PRM-X302 the as found value for REA-E/S-613B Power Supply was out of tolerance reading -24.28VDC. The Desired value is -24.00VDC +/- 0.25VDC. <I> **** Actions Taken **** Adjusted to desired value of -24.00VDC per ISP-REA/PRM -X302. Initiated CR and notified CRS. All as left values are satisfactory.
390742 | CR | 20190305 | CAQ | D | RRC-PS-18B AF trip OOT | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of ISP-RRC-Q901 (WOT 02114426-01) the AF trip of RRC-PS-18B was OOT high, but not outside Tech Spec limits. This is a Barton PS and while calibrating the switch noticed a vibration resonating from the tubing into the switch. This vibration could be the reason this switch keeps drifting out of tolerance. Recommend Engineering evaluate the vibration and replace this Barton switch with a different type of PS. <I> **** Actions Taken **** Notified Supervisor/CRS/ and calibrated switch back into tolerance. <N> An examination of RRC-PS-18Bâ€™s quarterly calibrations (PMID 17375-01 â€“ ISP-RRC-Q901) shows that the last time this instrument required adjustment was September 2016. The instrument, therefore, is not drifting routinely and an evaluation for replacement is not required. (RRC System Engineer)
390743 | CR | 20190305 |  | 4 | XD-04 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** XD-04 presents an actuator warning and requires maintenance. <I> **** Actions Taken **** XD-04 taken out of service. Initiate CR/WR | 02-00-SEC-XD-4
390744 | CR | 20190306 |  | 3 | WO 02137540 ISP-SEIS-M202 didnt have OPS Authorization Flag |  |  |  | N | NO | <D> **** Detailed Description **** WO 02137540 for ISP-SEIS-M202 did not have OPS Authorization for the WO. Please correct this for future WOs for this surveillance. <I> **** Actions Taken **** wrote CR
390750 | CR | 20190306 | CAQ | D | Received ROD ACCUMULATOR TROUBLE alarm for CRD-HCU-0223 | Y | N |  | N | YES | <D> **** Detailed Description **** Received ROD ACCUMULATOR TROUBLE, H13-P603.A7.6-7, alarm for CRD-HCU-0223. OPS 2 cleared the "ROD ACCUMULATOR TROUBLE" alarm for CRD-HCU-0223 per SOP-CRD-HCU. The alarm was due to high water level. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-HCU-0223
390755 | CR | 20190306 |  | 3 | Evaporator Ponds are Reaching Maximum Capacity | N | N |  | N | YES | <C> CR re-assigned to AR-ENLAB at the request of ENLAB supervisor. <D> **** Detailed Description **** All five Evaporator Ponds are close to maximum capacity. Due to issues with extra backwashing from the flocculator (CR 390727), additional MUD trailer reject water, and snow/rain water, the Evaporator Ponds are close to maximum capacity. Cold temperature are not helping with evaporation and all ponds are frozen over. <I> **** Actions Taken **** Recommend that any non-routine water that might be scheduled to be discharge to the Evap Ponds be reviewed by Environmental Service prior to discharge. This would include such things as heat exchanger flushes/drains. Flocculator backwashing should be kept to minimum. Flocculator has been placed on PCL due to excessive BW cycles. <N> **** Equipment Description **** Evaporator Ponds Actions need to be taken to prevent overflowing of the ponds, which will trigger reporting to regulatory agencies. If evaporation ponds 3 or 4 overflow this event may have radiological impacts.
390759 | CR | 20190306 |  | 3 | IMDS for SCI-MUX-IPWA/4 CH5 is incorrect |  |  |  | N | YES | <D> **** Detailed Description **** SCI-MUX-IPWA/4 IMDS for channel 5 is FP-PT-1 but the correct EPN is FP-PT-10 Can use EWD-62I-001 for reference | 02-00-FP-PT-10
390763 | CR | 20190306 |  | 3 | Chemical permit/tag program missing needed information |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The labels that are attached to various chemicals are missing data in the hazard box. Instead of giving a 0-4 rating in the fire hazard, health hazard, specific hazard and reactivity it gives question marks â€œ?â€. As a sample look up Loctite 515, permit number 0135. When this was brought up, the answer given was to use the numbers off of the MSDS from the computer. That we have two programs and they donâ€™t always match. This does not help with chemicals in cabinets in the field. Some chemicals have numbers and some have "?". It was also brought up that this could be covered in a pre-job brief. It begs the question, if that is the answer, then why have numbers in the box at all? This is a gap in excellence. One should be able to do a chemical inspection and be able to get the information from the label and not have to cross reference using a computer. <I> **** Actions Taken **** Brought up at D15, spoke with supervisor, wrote this CR.
390767 | CR | 20190306 |  | 4 | HP exceeded dose goal for the month of Feb. |  |  |  | N | NO | <D> **** Detailed Description **** HP dose for the month of Feb. was 377 against a goal of 274. The dose overage was due to pre-job surveys and RWCU ultrasonic flow meter instalation job coverage. <I> **** Actions Taken **** Wrote CR
390770 | CR | 20190306 |  | 4 | Near Miss Exiting Parking Lot |  |  |  | N | NO | <D> **** Detailed Description **** Near miss occurred when individual did not stop (dark colored pick-up truck) exiting the Deschutes main parking lot during inclimate weather around 1800 hours on February 28. Individual pulled out in front of Hanford patrol and another vehicle (driving in opposite directions) to turn left. Both vehicles had to brake to avoid collusion. Individual should have stopped and let traffic pass before pulling out of parking lot. Individual also exceeded the speed limit towards the security pop-up barriers. <I> **** Actions Taken **** Wote this CR for awareness.
390772 | CR | 20190306 | CAQ | C | floaters discovered in E-B1-1 during inspection | Y | Y |  | N | NO | <D> **** Detailed Description **** during the annual inspection of E-B1-1, electricians discovered "floaters" in the following cells 27, 29, 31, 32, 33 and35. Per engineer, the floaters may be a sign that the battery cells are nearing the end of service life, but the material floating does not affect the operability of the battery overall. <I> **** Actions Taken **** notified PSRO, Supervisor and Engineer, write CR. <N> **** Equipment Description **** E-B1-1
390775 | CR | 20190306 | CAQ | D | Floater material in E-B1-1 Foreign material | Y | Y |  | N | NO | <C> Trend to CR 390772 <D> **** Detailed Description **** reference CR# 390772. The CR# is to track/trend Foreign material as the previously mentioned CR did not contain the words "Foreign Material" in the subject line Per 10.1.13 section 7.6.6. The Floaters have been determined to not affect operability at this time. CRS and supervisor agree that the risk vs. reward to attempt to retrieve floaters at this time is not worth it. <I> **** Actions Taken **** Write WR <N> **** Equipment Description **** E-B1-1 cells 27, 29, 31, 32, 33 and 35 battery room 1
390781 | CR | 20190306 |  | 3 | procedure enhancement for 24month battery test |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The ESP-Bxx-B101 and ESP-Bxx-F101 surveillances need to be evaluated for the statement about operability following a battery discharge. ESP-B02A-B101 drives electricians to measure specific gravity and place battery on equalize charge per 10.25.234 following discharge test per step 7.1.33. Then, per step 7.1.36, says to Notify CRS/Shift Manager that battery operability is determined by successful completion of a Monthly, Quarterly and Weekly surveillance. This step is not adequate as it leaves the operability of the battery un-tracked without a WO#, WR# or any other formal tracking device for the maintenance department. The operability of the battery is dependent on three surveillances that do not make to work schedule. I recommend either a separate task during the planning process to track operability after battery testing, or add verbiage in step 7.1.36 to initiate a CR and WR to track. <I> **** Actions Taken **** Write CR <N> **** Equipment Description **** E-B0-2A Battery Room 2 An assignment has been created within the Maint. Procedure revision data base. a link to this data base has been added to the EDMS of this AR.
390784 | CR | 20190306 |  | 3 | Basic Rigging Initial Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** Two students did not successfully pass written exam with an 80% or highter. Remediate students on (3-7-19) with one-on -one instructor discussion, reviewing learning objectives. A second exam (ME000070 EX2) will then be administered per TDI-02. <I> **** Actions Taken **** Notified Supervisors
390785 | CR | 20190306 |  | 4 | Rx Building lighting on 572' elevation (South East) | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Several flourecent light bulbs need to be replaced behind ROA-HV-1. This area is currently very dark. This is a safety concern due to the potential for steam leaks to exist in the area (from Rx building heating steam). Please relamp. Note: this area was not addressed in AR 390521. ROA-HV-1 is located on RX 572' , South East corner <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** Rx 572 South East
390786 | CR | 20190307 |  | 4 | Heating Steam leak on TOA-HC-2A | N | N |  | N | YES | <D> **** Detailed Description **** Heating Steam leak in heating coil TOA-HC-2A. Steam is causing excess water accumulation on 501 West elevation. <I> **** Actions Taken **** Notified CRS | 02-00-TOA-HC-2A
390790 | CR | 20190307 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065983 New World Dig. Torque Wrench- model B-RAD 500 found OOT & adjusted within specs. Not used during Calibration cycle. DEF #6955A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only
390791 | CR | 20190307 |  | 4 | scheduled work failed to complete on time |  |  |  | N | NO | <D> **** Detailed Description **** Work on WEA-FN-1C, WO 02128389 was scheduled to complete on 3/5/19 this was a "B" grade work package (Daily Adherence), work was not completed until 3/6/19. while working the package, steps in the work plan had mechanics hooking up air to the supply air, after involving IC group in troubleshooting, it was determined that the test air was supposed to be hooked up to the control side instead. work was stoped to get the package changed. <I> **** Actions Taken **** Notified proper groups of failure to complete worked with planning to correct the package to allow for completion. work was completed the following day with the proper steps in the package.
390798 | CR | 20190307 |  | 4 | Lighting RX 501' | N | N |  | N | NO | <D> **** Detailed Description **** While changing lamps out on the RX 501' it was discovered that 4 fixtures on the west side that are on circuit 6BA-B -3 will not come on after lamps have been changed. The fixture in front of the air lock door on the NW corner has a broken pen socket holder that needs to be replaced this is on 3DA-A-2. One fixture on circuit 6BA-B-2 located over the CRD repair room vestibule on the SW corner may need new ballast as well as the fixture next to it on circuit ELP -8B-B-6. Also the fixture above the Main Steam Flow Panel on the east wall has a deficiency tag on it. It is on circuit ELP-7B-B-6. <I> **** Actions Taken **** CR was written contacted OPS about possible tripped breaker on circuit 6BA-B-3. Non-essential lighting. <N> **** Equipment Description **** RX 501 lighting
390801 | CR | 20190307 |  | 4 | E-LP-6BAB ckt 3 breaker won't reset | N | N |  | N | YES | <D> **** Detailed Description **** E-LP-6BAB ckt 3 is trip free and will not reset <I> **** Actions Taken **** Informed MCR, SSS <N> **** Equipment Description **** E-LP-6BAB ckt 3 RB 501 SW | 02-00-E-LP-6BAB
390807 | CR | 20190307 | CAQ | D | E-BU-W467/7 Fault Condition | N | N |  | N | YES | <D> **** Detailed Description **** While performing FP-CP-ISD/1 VESDA troubleshoot on 3-6-19 under WR 29147448, E-BU-W467/7 appeared to be in a fast charge or fault condition. . E-BU-W467/7 is not an Appendix R light listed in LCS 1.10.7 . Reference drawing E729-1 <I> **** Actions Taken **** Wrote CR, initiated FPSI 19-0068. This is non-essential lighting. <N> **** Equipment Description **** RW 467 RPS Room (Room number C213) | 02-00-E-BU-W467/7
390811 | CR | 20190307 |  | 3 | Used lamps not stored properly per station standards. | N | N |  |  | NO | <C> ANON CR Generated: Approved and moved to OPS for review. <D> **** ANONYMOUS CR - Detailed Description **** Used lamps found leaning against lamp storage area not inside the gaged area dedicated for used lamps. Lamps where not handled/stored per station expectation, SWP-ENV-03 and GIH-8.1.4 <I> **** Actions Taken **** Initiated CR notified supervisor. <N> **** Equipment Description **** GSB machine shop lamp storage area north east corner
390812 | CR | 20190307 | CAQ | B | New Fuel shipping container slide off of forklift forks |  |  |  | N | NO | <C> RISK: Medium. CAUSE: Uncertain/Complex. Investigation Template Required. Reopened assignments at maintenances request so a major rev can be done on the HUIT and OPIT due to comments from PARB 8/6/19 <D> **** Detailed Description **** The first new fuel container offloaded from truck #8 slide off of the forks while the operator was applying the brakes and fell a short distance to the ground where it then tipped over on its side and came to rest. The crew stopped all activity and notified their supervision <I> **** Actions Taken **** EN Supervisors were notified of the event at 0756 and went to the new fuel receipt area to verify incident. We found the shipping container on its side with no obvious damage. The incident area was photographed and a dose survey was performed on the container to verify that it had not been opened. The container was then carefully lifted off of the asphalt, placed on dunnage, and moved into a safe and stable location. All work was stopped and an event investigation was started per GBP-IRP-02. Notified the CRS/SM, HP, Security, WC, RXE, Industrial Safety, RX Mgr, and Maintenance Mgr. All work was placed was placed in a safe configuration. HP surveys completed to verify no release to the environment. <N> ***General Notes*** An event investigation has been conducted on this event. Documentation and further information can be found within the EDMS of this AR. . Cause is considered clear due to the event investigation identifying that individuals involved in the event were content with substandard conditions associated with ice on the fork lift forks, and breaks not functioning well on the fork lift. The brakes associated with the green clark fork lift is a long standing issue that was never corrected. Complaceny was also identified as a contributing cause. corrective actions being taken are the following. 1) all a new fork lift is in the process of being rented for the rest of the New Fuel Reciept campaign. the fork lift involved will be inspected, and fixed as needed. Fuel will be inspected by GNF as soon as a plan is completed. individuals involved in the event were sent to Fitness for duty. A station stand down has been submitted. Further corrective actions will be conducted pending the event inviestigation completion and potential causal evaluation recomendations.
390813 | CR | 20190307 |  | 3 | HD-LT-6B/6B2 potential impact by spray from RFW-HX-6A drain | N | N |  | N | YES | <D> **** Detailed Description **** The leak recently identified in CR 390617 from the RFW-HX -6A tube-side 1" drain line (leakby past RFW-V-111A)(1140 psig) is spraying in the direction of HD-LT-6B and HD-LT -6B2. Also HD-LS-6AHT is above the leak though not being directly sprayed. These types of level transmitters and level switches are vulnerable to heat and water intrusion failures. Recommend that a temporary modification be pursued to reduce or redirect this leak. Previous video of leak from CR 390617 added to EDMS for reference. Leak can be partially viewed on camera TG#21 and TG#17. Camera TG#21 is being spraying and has been slow to respond at times. Direct viewing of the leak is not possible on camera so monitoring of condition is limited. It does appear that the leak may be slightly worse than when viewed on camera earlier this week. WR initiated for temporary modification. <I> **** Actions Taken **** Discussed leak with FIN. Leak repair being pursued. Discussed with supervisor. Reviewed T5 sump run times and plant water usage. <N> **** Equipment Description **** T471 west side of heater 6A. | 02-00-RFW-V-111A
390814 | CR | 20190307 | CAQ | C | Removal of admin hold required HGU re-enrollment |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** CAS removed an admin hold in their AIM computer. The individual's green badge would not allow for PA access, when presented at the turnstyles. Once the individual was re-enrolled in hand geometry, PA access was granted. Contact Access Authorization for further details. <I> **** Actions Taken **** Contacted Security Services Mgr and notified Computer Engineering. Please assign to org #54211 (See Cross Referenced CR's 389707 and 388439)
390815 | CR | 20190307 |  | 4 | Near Miss During Outside New Fuel Movement |  |  |  | N | NO | <D> **** Detailed Description **** At approximately 0745 on 03/07/2019, New Fuel Box RA -2045, the first box of thirteen was off loaded. After picking up the fuel box, the fork lift approached the loading zone, as it did the box slipped off of the forks and dropped onto the ground. Two HP Technicians were in the vicinity of the area where the box fell. There were no injuries as a result of the event. <I> **** Actions Taken **** The HP Technicians reported the incident to their Supervision, the RP Manager was then notified as well as Industrial Safety. Stopped work pending completion of major event investigation. HP surveys completed to verify no release to the environment. <N> ***General Notes*** Maintenance recomends this CR be closed to CR# 390812 because both CR's identify the same event. All information from the event investigation and other documentation will be addressed within CR# 390812.
390816 | CR | 20190307 |  | 4 | TG-ID-1 manual start PB not lit | N | N |  | N | YES | <D> **** Detailed Description **** Step 4.15 of WO 02131788-01 is to verify the Manual Start pushbutton is illuminated. The light is illuminated under normal operating conditions and is off. The light was off upon arrival. It appears that TG-ID-1 is operating correctly at this time. <I> **** Actions Taken **** Notified Ops and supervision. The strip chart was replaced and the old chart delivered to the control room. | 02-00-TG-ID-1
390817 | CR | 20190307 |  | 3 | R24 Procedure Revisions after Milestone | N | N |  | N | NO | <D> **** Detailed Description **** R24 procedure revision assignments have come through after the R24 Procedure Milestone has passed. These late revision assignments have not followed the process and outage milestones. Determination needed if fast track of revisions is needed for R24. Additional assignments may be needed to ensure that changes to procedures that affect parts, planning and scheduling have also been made. <I> **** Actions Taken **** See attached list in EDMS of procedure revision assignments to date.
390818 | CR | 20190307 |  | 3 | New Motors and there storage affecting scheduled work |  |  |  | N | YES | <D> **** Detailed Description **** While attempting to perform W.O. 02077541-10 New Motor Testing of COND-M-P/2A spare motor there are two motors with the identifed CID. Both motors are still crated up and unavailable for testing. There is not enough information in the work order and on the outside of the crates to identify which motor engineering wants prepared. Questions came up about what process drives receipt of new large motors and gets them uncrated, filled with oil, space heaters energized, and add to Spare motor PM. <I> **** Actions Taken **** Electrical Supervision, Management, and Engineering informed about issues creating a road block in completing the scheduled work. Work Order 02077541-10 returned until these issues can be resolve. <N> **** Equipment Description **** Spare moror CID# 8632
390819 | CR | 20190307 | CAQ | C | (QA) Incorrect Revision of Work Instructions Used |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) During closeout review, Quality Control identified that the latest version of the work instructions were not used for the performance of WOT 02117218-13 (RHR-M-P/2A). Not using the latest work instructions resulted in QC acceptance of new parts being documented in the work instructions instead of the parts list attachment IP09 as required. The QC Supervisor and Level III reviewed the documentation that was made and determined that all QC hold points were performed as intended and this was a documentation issue only. Quality is unaware of any other impact from using the incorrect revision of instructions, but Maintenance should take action to confirm this and document in this CR disposition. Action should also be taken by Maintenance to understand how the wrong revision was selected for use in Data Glance for the work and communicate lessons learned. Recommend SL-C (OQAPD â€“ Procedures) to Electrical Maintenance. <I> **** Actions Taken **** Notified Quality Services Supervisor, Quality Control Level III, and Electrical Maintenance Component Manager
390820 | CR | 20190307 |  | 3 | SOP-ELEC-DIV2-TEMPPOWER proposed revision |  |  |  | N | NO | <D> **** Detailed Description **** See EDMS documents for proposed changes. Changes can be found on pages 113-116 of the attached procedure.
390821 | CR | 20190307 | CAQ | C | (QA) Attachments for WO Not Completed |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) During QC closeout review for WOT 02117218-66 (RHR-M -P/2A), Quality Control identified that required attachments were not filled out. The torque table was not filled out for reconnection of leads after the swapping of phases and the CTI form was also not filled out. The QC Supervisor and Level III reviewed the documentation that was made on the splice checklist and work order steps and determined that all QC hold points and the work were performed as intended and this was a documentation issue only. This was based on the fact that the Splice Checklist (SIC) was signed twice and torque verifications were written in with a note and signature. There is no effect on plant equipment because of these issues. Recommend SL-C (OQAPD â€“ Procedures) to Electrical Maintenance to determine if action is needed to re-create documentation and/or document justification for no further action. <I> **** Actions Taken **** Notified Quality Services Supervisor, Quality Control Level III, and Electrical Maintenance Component Manager
390823 | CR | 20190307 |  | 4 | PWC-P-8 pumping back to storage tank. | N | N |  | N | YES | <D> **** Detailed Description **** PWC-P-8 is lifting the relief valve and pumping chlorine back to the storage tank. This Pump blew the line a couple of weeks ago. I suspect that there is a plug somewhere or the line is pinched off. | 02-00-PWC-P-8
390824 | CR | 20190307 |  | 4 | Late eSOMS entries for Maintenance (2/9/19 - 2/22/19) |  |  |  | N | NO | <D> **** Detailed Description **** Three electricians and one mechanic heldover their regular shift hours without having time entered in eSOMS. One Electrician left for PT 1/2 hour later than scheduled, and 1 I&C Tech returned from PT 1 hour earlier than scheduled. One mechanic had his time inadvertently removed on a day when he worked. And one Mechanical Supervisor and one Painter had travel times greater than their scheduled travel times. No violations occurred when eSOMS was updated <I> **** Actions Taken **** Updated eSOMS & notified department and shop managers, FFD Lead, and Maintenance CIC.
390827 | CR | 20190307 |  | 3 | (Non EN/CGS) CC-176 Wrong PO Entered |  |  |  | N | NO | <D> **** Detailed Description **** CC-176 is to document a NON EN/CGS customer complaint involving an extra zero being entered on the PO. PO should have been 390000-0191 and was entered as 390000-00191. This email is in regards to the calibration report documentation for item 5 on Intermech PO # 390000-0191. Item 5 - Energy NW asset number is ITM-WTP-076 Energy NW Calibration Report - Page 1 and 2. The PO Number listed on page 1 and 2 on the calibration report is 390000-00191. The PO Number should be 390000-0191. Please have the PO Number corrected on page 1 and 2 and email the corrected calibration report for ITM-WTP-076. Recommend Assign AR-CALSERV <I> **** Actions Taken **** Initiated CC-176 and CR to track and trend. Issued Corrected certificate. <N> All records affected were corrected in the electronic database and reprinted to reflect the correct information. The customer receievd the corrected copy within hours of the phone call and due to contract requirements that information is only available on the ENSL Sharepoint site.
390828 | CR | 20190307 | CAQ | C | (NRC 2019 PI&R) Inadequate documentation when closing CAs |  |  |  | N | NO | <D> **** Detailed Description **** Some corrective actions are being closed without adequate justifications when corrective actions are not implemented as written. SWP-CAP-01, section 4.7.5, requires a justification has to why there was a deviation from the original assignment. Additionally if the action originated from a causal evaluation, procedural guidance requires a review of the evaluation should be conducted (and documented) to determine if a revision is necessary. Examples include: 369215-04, 352217-04, 371264-13 <I> **** Actions Taken **** Recommend assignment to AR-PERFIMP
390829 | CR | 20190307 | CAQ | C | (NRC 2019 PI&R) CA not implemented as written |  |  |  | N | NO | <D> **** Detailed Description **** NRC observation: AR 352217-04 was not implemented as written and does not meet the intent of the original action. <I> **** Actions Taken **** Recommend assignment to AR-CHEMRAD
390831 | CR | 20190307 |  | 4 | High Memory Usage on NET3-FW-ASACENTER | N | N |  | N | YES | <D> **** Detailed Description **** NET3-FW-ASACENTER was found to have high memory usage requiring a system reboot. . This is not a reportable condidtion. This does not impact operations. <I> **** Actions Taken **** Generated CR/WR and notified SM. | 02-00-NET3-FW-ASACENTER
390832 | CR | 20190307 |  | 3 | APEL Roof Purlin Cracked | N | N |  | N | NO | <D> **** Detailed Description **** At approximately 0830 March 7th, 2019, APEL tenant notified Facilities of abnormal ceiling level. Facilities, Industrial Safety, and Engineering assessed the area and identified a cracked purlin. <I> **** Actions Taken **** Facilities and APEL building management made proper notifications and Facilities formulated a plan of action. Tenants were also evacuated from the east office areas of APEL for their safety. Facilities Engineering and Industrial Safety performed an assessment of the entire APEL building and determined no other areas are at risk.
390833 | CR | 20190307 |  | 3 | B64 Fire Sprinklers Out of Required Position in Ceiling Tile | N | N |  | N | YES | <D> **** Detailed Description **** Inspection of Building 64, Willamette Building by the Facility Fire Protection Engineer finds that multiple fire sprinkler heads are extending beyond their required position in the ceiling tiles in excess of 1 inch in some places. The sprinkler escutcheon is hanging below the ceiling tile in violation of NFPA 13 requirements. This causes a gap at the ceiling tile that is not allowed. With so many fire sprinklers observed with problems, this could mean that the roof is deflecting due to snow and ice load. <I> **** Actions Taken **** Discussed this with the Facility Supervisor in charge of fire sprinklers. WR written to repair the fire sprinklers. It is unknown what the extent of condition is for the rest of the building services above the ceiling. <N> **** Equipment Description **** B64 Wet Pipe Fire Sprinkler System
390835 | CR | 20190307 |  | 3 | Improper FME posting at TMU |  |  |  | N | NO | <D> **** Detailed Description **** A sign was discovered posted at the TMU pumphouse improperly listing the area as an FME area and stating that a pre-job brief was required prior to entry. This posting does not meer the requirements of PPM 10.1.13. <I> **** Actions Taken **** SM/CRS informed. FME coordinator was contacted. Improper signage was removed and caution signage similar to what is posted at the CWPH was posted. The FME cordinator recomends that this CR be screened as a Non-CAQ severity level 3 to AR-MNTPROG so the FME cordinator can take ownership of this issue and correct it.
390836 | CR | 20190307 | CAQ | D | RHR-DPIS-12A found OOT | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of ICP-RHR-Q901, RHR-DPIS-12A as found trip was OOT at 182â€ H2O (Admin limits are 165â€ H2O to 176â€ H2O). Adjusted per attachment 9.1 and to as left trip value of 166â€ H2O. <I> **** Actions Taken **** Informed operations, supervision, wrote CR
390837 | CR | 20190307 |  | 4 | RB SW Elevator doors are sticking | N | N |  | N | YES | <D> **** Detailed Description **** They still work but occasionally need extra time to open and/or assistance. Recommend fixing. <I> **** Actions Taken **** Assisted the elevator doors in opening | 02-00-MT-ELEV-2
390838 | CR | 20190308 | CAQ | D | Recieved Accumulator trouble alarm 30-27 | Y | N |  | N | YES | <D> **** Detailed Description **** Recieved accumlator trouble alalrm for HCU 30-27 due to high water level. <I> **** Actions Taken **** Cleared alarm per ARP. | 02-00-CRD-HCU-3027
390841 | CR | 20190308 |  | 3 | Vendor overhauled breaker has blocked arc chute puffer tubes | N | N |  | N | NO | <D> **** Detailed Description **** Vendor overhauled breaker UTC 368837 drawn from stores has blocked arc chute puffer tubes. The puffer tubes perform a critical function in that the arc that is developed when a breaker is opened under load is forced into the arc chutes with a blast of air, quickly extinguishing the arc. Boroscope inspection has revealed that the puffer tubes are blocked with excess silicon RTV. Bench testing of this breaker is being performed under WO 02111272-05 as a pre -outage task. CID 12555. UTC 368837. Pre-outage task at risk of not completing as scheduled. <I> **** Actions Taken **** Notified system Engineer and vendor. Generated this AR and WR to attempt to clear blocked puffer tubes. <N> **** Equipment Description **** W487 breaker shop
390843 | CR | 20190308 |  | 4 | Chemical residual on outside piping of Building 40 | N | N |  | N | YES | <D> **** Detailed Description **** Small amount of chemical residual was found on a piece of outside piping along the east wall of Building 40. This piping contains the chemical feed line from PWC-P-8 to the injection point into the potable water system. Further invesigation needed. <I> **** Actions Taken **** Informed oncall chemistry supervision. Wrote CR to document | 02-00-PWC-P-8
390844 | CR | 20190308 | CAQ | D | D-DOOR-D104 knob sticking open, mechanism doesn't engage | N | N |  | N | YES | <D> **** Detailed Description **** Door sticking, maglock holding door closed as latch does not always engage everytime. <I> **** Actions Taken **** Generated CR. EXISTING PROBLEM SEE BI 19-0079 FROM12FEB19. WR 29147084. <N> D-DOOR-D104 is a non-essential fire door. This door also serves as a security barrier but the security mag latch is functioning normally. The standard door latch which is degraded serves no security function. | 02-00-D-DOOR-D104
390846 | CR | 20190308 | CAQ | C | Possible RWCU-V-44 impacts core thermal power calculation | Y | N |  | N | YES | <D> **** Detailed Description **** During RWCU differential flow indication investigation per work order 02137234, the following evidence of RWCU-V-44 leakby was observed: Initial configuration per work order 02137234: RWCU-V-104 was throttled open: at least some flow was passing through the system bypass because total flow was raised from 151 gpm (with RWCU-V-44 alone throttled open) to greater than 300 gpm. RWCU-V-44 was throttled closed per 02137234 step 4.42.2. System flow dropped to 164 gpm (using computer point B009GPM). RWCU-V-42 was closed per step 4.44. Flow dropped to below the RWCU pump trip setpoint and RWCU-P-1A tripped on low flow. RWCU was restarted per a contingency step in the work order and flow was raised to 240 gpm by throttling RWCU-V-104 further open. <I> **** Actions Taken **** Conclusion: there is substantial leakage past RWCU-V-44 when closed, at least during the high head/low flow condition present during this investigation. This impacts the core thermal power calculation because only RWCU flow through the RWCU demineralizers is included in the heat balance and RWCU-V-44 flow also passed through the RWCU NRHX. The heat balance is currently conservative due to insertion of substitute values for demineralizer flow that are greater than total RWCU system flow. <N> new substitute values of 0.1 mlbm/hour being used for RWCU -DM-1A and 1B flows as recommended by Reactor Engineering | 02-00-RWCU-V-44
390849 | CR | 20190308 |  | 4 | Received 602.A6.2-8 RECIRC B SYSTEM VIBRATION HIGH | N | N |  | N | YES | <D> **** Detailed Description **** Found RRC-VBI-P1B/XE red alarm light flashing and highest indication of ~25 MILS. Identified no abnormal thrust bearing temperature trends. NOTE: This occured during RWCU troubleshooting which briefly isolated RWCU demins and raised and lowered RWCU flows. <I> **** Actions Taken **** alarm has been reset | 02-00-RRC-VBI-P1B/XE
390850 | CR | 20190308 | CAQ | D | CMS-SR-20 Particulate Filter Green Color | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO#02131785-01, it was noted that the removed Particulate Filter had a green color to it instead of the normal white color. <I> **** Actions Taken **** Notified Supervisor, continued with surveillance, and wrote CR to document. <N> **** Equipment Description **** 548RX
390851 | CR | 20190308 |  | 3 | Procedure enhancement for SOP-RWCU-OPS |  |  |  | N | NO | <D> **** Detailed Description **** Procedure enhancement for SOP-RWCU-OPS section 5.4 ( Reset of RWCU-TIS-8 ) While performing troubleshooting on RWCU system WO 02137234, bypassed the high temperature isolation to keep RWCU-V-4 open, while the demins were offline. This helped out the efforts for the troubleshooting plan, and would be a benefit to clearing a high temperature condition. Call Steve Kartchner or K. Farley for Questions on the procedure change
390852 | CR | 20190308 |  | 3 | PPM 16.1.7 Editorial |  |  |  | N | NO | <D> **** Detailed Description **** PPM 16.7.1 Requires a procedure enhancement for figure 2 to reflect the location of TP3 per the vendors drawing <I> **** Actions Taken **** Notified CRS and Supervisor that step 7.3.19 did not indicate the correct location to connect the DMM to per figure 2. Verified the correct location by referencing the Vendors OMM and pulled a spare part, PRM-SQRT-2 from the warehouse to ensure the correct circuit board and vendor drawings were being referenced. Generated a CR to ensure PPM 16.7.1 will be enhanced. PPM 16.1.7 was completed satisfactory. <N> **** Equipment Description **** PRM-SQRT-2 . 16.1.7 rev. 014.003 uploaded to asset suite.
390853 | CR | 20190308 | CAQ | C | Inner Accelerometers confirmed tripped for AR-CR 390812 |  |  |  | N | NO | <D> **** Detailed Description **** The inspection of the New Fuel Shipment Inner container associated with AR-CR 390812 was completed. The results indicate that two of three inner container accelerometers were tripped. These results together with the event documented in AR-CR 390812 were discussed with the Fuel Vendor and industry peers. The Fuel vendor recommends shipping the Fuel Bundles back to the factory for inspection and potential refurbishment/replacement. Recommend a Cat C to Rx fuels. <I> **** Actions Taken **** Discussed findings with Fuel Vendor and Industry Peers Currently Coordinating Shipping Plan Notification of Supervision
390854 | CR | 20190308 |  | 3 | CC-177 Out of Tolerance Standard 0067951 | N | N |  | N | NO | <D> **** Detailed Description **** Standard Out of Tolerance -0067951 Not used for any CGS instruments and not necessary to recall any commercial customers as used as a display device and did not have an impact. Recommend assign to AR-CALSERV Cat 3 <I> **** Actions Taken **** Investigation conducted, CR generated and CC-177 initiated.
390855 | CR | 20190308 |  | 3 | CC-178 Out of Tolerance Standard 001-123-49-003 |  |  |  | N | NO | <D> **** Detailed Description **** Calibration Standard 001-123-49-003 found "Out of Tolerance" when it was found to be inoperable. However it was discovered that a pico fuse (F1) blew during warm up before use. This unit was repaired and calibrated by the Manufacturer and found to be within tolerance. It does not appear that the unit was ever actually out of tolerance but due to the lack of power could not be verified. Recommend assign to AR-CALSERV <I> **** Actions Taken **** Initiated CC-178, OOT investigation and generated a CR to track and trend.
390856 | CR | 20190308 |  | 3 | Individual left badge at workstation |  |  |  | N | NO | <D> **** Detailed Description **** A contract employee left their blue badge at their workstation overnight. Recommend CAT3 to ITMGMT. <I> **** Actions Taken **** Contractor notified supervisor of missing badge. Security was notified, disabled access, and recovered the badge. Shift manager has been notified.
390857 | CR | 20190308 |  | 3 | Lights out in RW/RX and DG buildings | N | N |  | N | YES | <D> **** Detailed Description **** Lights out in RW/RX and DG buildings 467-'RW above E-C1-2A/2B - 2 lights - Above Door-C-215 and 2 in hallway vital island -outside Battery room #1 -In RW stairwell between 441 and 452 1 light -RCIC pump room several lights - RHR-C pump room several lights - LPCS pump room 1 light -CRD pump room 5 lights out RX stairwell SW 7 lights out 471'RX -9 lights out 501'RX 6 lights out 522 RX 6 lights out 548"RX 8 lights out, DG-TG corridor 5 lights out 572'RX 2 lights out north side, DG-3 room 8 lights out DG-2 room 9 lights out,DG-1 room 14 lights out <I> **** Actions Taken **** contacted SM/CRS/STA/SSS and issued this CR Work request initiated and cross referenced. M Pezzetti okay to close
390858 | CR | 20190309 |  | 4 | Several leaks outside of TOA-HC-1A | N | N |  | N | YES | <D> **** Detailed Description **** There are several steam leaks on unions of piping behind TO-HC-1A. a steam leak was observed from the supply side coming from under the lagging of HSV-1K and HS-V-1M. There was also more significant leaks from the union after the strainer blowdlown valve HCO-V-T1AD and the respective strainer. A Smaller steam leak appeared to be in the same place on the M coil but was covered in lagging. Would recommend a craft inspection to document need repair and a WO to be drawn up to disassemble the piping when not in use and returning it. Please note the middle coil L was out of service at the time. There is a significant amount of water and steam on the back side of the area its dark and will require a flashlight. there is also exposed steam pipes that are hot if in use. <I> **** Actions Taken **** Wrote CR and WR. | 02-00-HCO-V-T1AD,02-00-HCO-V-T1CD
390859 | CR | 20190309 |  | 4 | FANS left running on the T 501 from outside | N | N |  | N | YES | <D> **** Detailed Description **** there are two fans that appear to be piped to take a sucction from outside and discharge it to long flexible duct hoses. This was being used during the crane work to provide cooling to a vary hot area. these fans are still running with the ducting all thrown hodge podge up in the area. the fans appear to be plugged into the bang box in the middle of the equipment. Why are they still running?, is this a temp mod?. Is this being controlled by a work order? Is the WO still open and this part is yet to be done? <I> **** Actions Taken **** wrote CR. please evaluate and correct the fans or educate me on why they are still there. <N> **** Equipment Description **** temp fans on the 501
390861 | CR | 20190309 | CAQ | D | Received ROD ACCUMULATOR TROUBLE, for CRD-HCU-4259. | Y | N |  | N | YES | <D> **** Detailed Description **** Received ROD ACCUMULATOR TROUBLE, H13-P603.A7.6-7, alarm for CRD-HCU-4259. Notified OPS2.OPS2 cleared the ROD ACCUMULATOR TROUBLE alarm for CRD-HCU-4259 per SOP-CRD-HCU. The alarm was due to high water level. <I> **** Actions Taken **** Infromed CRS/SM | 02-00-CRD-HCU-4259
390862 | CR | 20190309 |  | 3 | Consider Revision to ABN-SITE-ACCESS for Storm Crews |  |  |  | N | NO | <D> **** Detailed Description **** Recommend adding a provision to ABN-SITE-ACCESS that if access to the site is or is anticipated to be impaired that the operating crews should stay onsite. Utilize the cots and MREs in the TSC for bedding and food. This is a recommendation from the heavy snow and difficult access in early March 2019. <I> **** Actions Taken **** discussed with SM and wrote CR
390863 | CR | 20190309 |  | 4 | Clark Forklift Brakes |  |  |  | N | NO | <D> **** Detailed Description **** Workers brought up a concern that the brakes on the Clark forklift are not working properly. While operating the forklift the brakes are sensitive to operate. This poses challenges to operators when attempting to make fine movements with the forklift. <I> **** Actions Taken **** Removed the Clark forklift from service. Contacted a Clark dealer to visit the site and inspect the brakes for degradation or damage. Results from the inspection show that the brakes are in very good condition with no signs of degradation or damage. Pictures have been uploaded to EDMS. The Vendor suggested that this style of brakes should be warmed up by driving the forklift around and applying the brakes. This will allow them to be operated at a more precise level. The Vendor indicated that this forklift is safe to operate and does not need to be tagged out for brake concerns.
390864 | CR | 20190309 |  | 4 | More material needed in fabrication task |  |  |  | N | NO | <D> **** Detailed Description **** The task to build the LLRT header 02135267-01 did not include any valves, a discussion was had with I&C and material will be purchased locally due to the quantity needed. This task will be completed on the work request generated from the CR. <I> **** Actions Taken **** This is not a planning issue it was discussed with SMEâ€™s that it would be better to have it fabricated in this fashion. As instructions stated to get with I&C for fabrication details. <N> **** Equipment Description **** LLRT test header
390865 | CR | 20190309 |  | 4 | BRE 37 Door | N | N |  | N | YES | <D> **** Detailed Description **** BRE 37 Door requires maintenance. Contact Security for more details. <I> **** Actions Taken **** Security Supervision notified. Initiate CR/WR. <N> **** Equipment Description **** BRE 37 Door
390866 | CR | 20190309 |  | 4 | BRE 37 Camera Monitor | N | N |  | N | YES | <D> **** Detailed Description **** The camera monitor located in BRE 37 requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security supervision notified. Initiated CR/WR <N> **** Equipment Description **** BRE 37 Monitor
390867 | CR | 20190309 |  | 4 | RW 467' Decon Area is in need of Relamping | N | N |  | N | NO | <D> **** Detailed Description **** -Decon Area is dark and there are several light lights that are not working. This area will be utilized often during the outage for decon work and should be higher up on the relamping priority list. <I> **** Actions Taken **** -Notified Supervision -Initiated CR/WR <N> **** Equipment Description **** RW 467' Decon Area area was relamped on 3-9-19
390868 | CR | 20190309 | CAQ | D | Received Rod Accumulator Trouble for CRD-HCU-06-27. | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-06-27. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-06-27 was due to high water level. <I> **** Actions Taken **** Dispatched OPS-2 to investigate OPS 2 drained water per SOP-CRD-HCU and alarm is clear | 02-00-CRD-HCU-0627
390869 | CR | 20190310 |  | 4 | ASD lights need replacement | N | N |  | N | YES | <D> **** Detailed Description **** ASD building has two lights that need attention. One in front of and one behind panel RRC-SN-ASD/1B. Both lights take what appears to be 8ft bulbs. One light has both bulbs out while the other is dull and blinking. <I> **** Actions Taken **** Wrote CR. <N> **** Equipment Description **** ASD building lighting
390870 | CR | 20190310 |  | 4 | Received MAIN XFMR TR-M1 TROUBLE, H13-P800.C4,1-1, alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received MAIN XFMR TR-M1 TROUBLE, H13-P800.C4,1-1, alarm due to Cooler Group 1 failure, cooler group 1 oil pump is not running with overload tripped. In conjunction received BUS 21 GROUND, H13-P800.C2,8-2, alarm due to E-MC-2B. Attempted to reset cooler group 1 oil pump overload however it would only momentarily reset and then come back in. OPS3 reset the ground relay for MC-2B and the BUS 21 GROUND alarm is clear. TIMELINE 0337 Received BUS 21 GROUND, H13-P800.C2,8-2, alarm. Dispatched OPS3. 0340 Received MAIN XFMR TR-M1 TROUBLE, H13-P800.C4,1-1, alarm. Dispatched OPS4. Entered ABN-TRANSFORMER. 0342 OPS3 reports that the SL-21 ground alarm is due to E -MC-2B. OPS3 reset the ground relay and the alarm is clear. 0345 OPS 4 reports MAIN XFMR TR-M1 TROUBLE due to Cooler Group 1 failure, cooler group 1 oil pump is not running with overload tripped. 0358 OPS4 attempted to reset overloads per ABN-TRANFORMER however alarm cleared momentarily and then came back in. Outside air temperature is 19F. 0400 Received BUS 21 GROUND, H13-P800.C2,8-2, alarm. 0400 OPS4 reset overloads per ABN-TRANFORMER alarm is clear. 0405 OPS3 reports that the SL-21 ground alarm is due to E -MC-2B. OPS3 reset the ground relay and the alarm is clear. 0405 Received MAIN XFMR TR-M1 TROUBLE, H13-P800.C4,1-1, alarm. Alarm due to Cooler Group 1 failure, cooler group 1 oil pump is not running with overload tripped. Left cooler group 1 oil pump overload in tripped in condition | 02-00-E-TR-M1
390871 | CR | 20190310 | CAQ | D | EDR-P-12 tripped after precoat. | N | N |  | N | YES | <D> **** Detailed Description **** EDR-P-12 hold pump started then tripped after precoat. The hold pump indicates off and the hold valve indicates closed both in the RWCR and at the field panel. The pump off light is also lit at MC-8A-2C. <I> **** Actions Taken **** Notified supervisor and initiated this AR/WR. <N> **** Equipment Description **** RW-467 | 02-00-EDR-P-12
390872 | CR | 20190310 | CAQ | D | MS-RIS-610B display failed | N | Y |  | N | YES | <D> **** Detailed Description **** MS-RIS-610B display failed. Turned unit on and took reading. Display then illuminated with all indications showing. Display does not respond to any input keys <I> **** Actions Taken **** CRS declared unit inop. LCS 1.3.6.3 | 02-00-MS-RIS-610B
390873 | CR | 20190310 | CAQ | D | D-DOOR-D104 latch still broken | N | N |  | N | YES | <C> Trend to CR 390844 (duplicate) <D> **** Detailed Description **** This doors latch is still not working. The only reason why it stays closed is securities vital access latch. Impairment 19-0079 is still hung. It was posted on 2/12/19 with a expected duration of 7 days. <I> Existing problem. See BI 19-0079 from 2/12/19. WR 29147084. | 02-00-D-DOOR-D104
390874 | CR | 20190310 |  | 3 | PeopleSoft unavailable |  |  |  | N | NO | <C> SUPV has reviewed and approved of closing this CR. See EDMS for evidence. No further aciton is required. <D> **** Detailed Description **** PeopleSoft application was unavaiilable on Sunday 3/10/19 due to Oracle database lost connection. <I> **** Actions Taken **** Infrastructure analyst rebooted server. PeopleSoft became available again. Need to research Oracle database connection. Recommend NCAQ3 to ITMGMT.
390881 | CR | 20190311 |  | 4 | SEC-XR-03 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** SEC-XR-03 is not functioning as designed and requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervision notified. Initiated CR/WR. X-Ray was taken out of service. | 02-00-SEC-XR-3
390885 | CR | 20190311 | CAQ | D | FDR-V-104 spurious closing on system start | N | N |  | N | YES | <D> **** Detailed Description **** FDR-V-104 spurious closing on system start. Suspect an issue with FDR-PS-16, which senses pressure from the running FDR-P-16 and closes to allow FDR-V-104 to open. Suggest calibrating/ backfiling FDR-PS-16 <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** FDR-PS-16, IR 58, RW 467 | 02-00-FDR-PS-16
390887 | CR | 20190311 |  | 3 | Isophase bus inspection WO deficiencies | N | N |  | N | NO | <D> **** Detailed Description **** Lessons learned from R20 isophase bus inspection have not been incorporated into the upcoming R24 work order. The following issues were documented in WO 01195793 which performed the Isophase bus inspection in R20: . There are a set of rigid links below the baffle bushing that are removed for cleaning and inspection of the silver contact surface. Removal of all links at one time will result in a section of the isophase conductor falling. Link removal needs to be staggered or dummy links installed to ensure the bus is supported properly throughout the inspection. Several links needed to be re-silvered in R20 to ensure proper low resistance connections in the bus, the work order has steps for inspecting the silver surfaces and determine if re-silvering is required but there does not appear to be a vendor lined up to perform this activity if it is needed. Task 8 is a vendor task and referenced Electrical Builders Inc. (EBI) but there is no requirement to ensure they are onsite or available to perform the task. . At grid 6 in the transformer yard there are three links that were inaccessible for inspection and maintenance. WO 02010742 was initiated to cut holes in the bus to allow the necessary inspections. This was not incorporated into the 8 year bus inspection PM. Without a revision to the WO to incorporate these actions these links will not be inspected. Fasteners also need to be ordered for this section of bus to ensure the proper configuration is installed. . Precautions and Limitation 2.7 as well as work order steps 4.6.4.2, 4.7.4 and 4.8.3 direct the use steel wool to clean the silver plated contact surfaces. Steel wool is NOT to be used for cleaning the silver plating as it will remove the silver surface resulting in a high resistance connection and potential overheating in the bus. Delta Unibus does have allowances for using stainless steel wool for some cleaning but the method if use is very restrictive to prevent damaging the silver surfaces. If stainless steel wool use is allowed there should be adequate guidance to ensure the silver surface is not damaged. . Several steps direct replacement of the fastener hardware. Review of the material requests shows washers are ordered but there are no replacement bolts ordered for the rigid links below the clamp shells. Materials should be second checked to ensure the proper fasteners are ordered for the replacements. . The 2011 work order was revised to inspect the isophase bus baffle plate fasteners located below the generator CTs and replace fasteners as necessary, there is no guidance in the R24 work order to inspect the baffle plate fasteners. This inspection should be added to the R24 work and materials ordered to replace fasteners as necessary. <I> **** Actions Taken **** Discussed with supervisor, initiated CR to document and drive enhancement of work instructions
390890 | CR | 20190311 |  | 4 | OG-RF-20A high oil level | N | N |  | N | YES | <D> **** Detailed Description **** OG-RF-20A standby oil level is greater than 1/2, currently approximately 5/8 . Operator rounds require a CR to document and correct. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-OG-RF-20A
390891 | CR | 20190311 |  | 4 | OG-RF-20B oil level high | N | N |  | N | YES | <D> **** Detailed Description **** OG-RF-20B standby oil level is greater than 1/2, currently approximately 5/8. Operator rounds require a CR to document and correct. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-OG-RF-20B
390892 | CR | 20190311 |  | 4 | Trailer 122 Not Acceptable for Occupancy | N | N |  | N | NO | <D> **** Detailed Description **** Trailer 122 has been fully remodeled. Per ISPM-10, prior to occupancy all building remodels require life safety and fire protection inspection. Fire Marshal inspection of T122 finds multiple problems that need to be resolved prior to occupancy. Unfortunately, the building was found occupied and in use. The deficiencies have been documented and EMailed to the Facility & Commercial Engineering Group. These items should be completed prior to occupancy. . This is a repeat finding. Previous findings have been made where building remodels and trailers have been occupied prior to the required inspection. . EMail has been added to EDMS section. <I> **** Actions Taken **** EMail to F&CE Manager and Project Manager. Copy to the occupants and the supervisor of the occupants.
390897 | CR | 20190311 |  | 4 | 7 Pieces of M&TE Suspended Until Needed | N | N |  | N | NO | <D> **** Detailed Description **** 7 PSA Validators were NOT used and are now Suspended until needed per: C. Smith. No Plant Impact. No Action Required. See attached EDMS for models and DEF #'s. <I> **** Actions Taken **** None Trending purposes only.
390901 | CR | 20190311 |  | 3 | Hard Copy Records Scan/Destroy outside of the record process | N | N |  | N | NO | <D> **** Detailed Description **** Asset Management Department has been scanning records and destroying hard copies not in accordance with GBP-REC-02. <I> **** Actions Taken **** Notified Supervisor, working with department to obtain approved documentation to allow for scan and toss per procedure.
390903 | CR | 20190311 | CAQ | D | RPIS maintenance display cover loose | Y | N |  | N | YES | <D> **** Detailed Description **** The RPIS maintenance display cover appears to be loose. The fasteners should be tightened. See photo in EDMS. <I> Attempted to tighten the screw on the cover that is loose. Screw would not engage a threaded connection indicating that the threaded connection is failed in some manner. <N> **** Equipment Description **** E-CP-H13/P615 | 02-00-CRD-RPIS-1
390905 | CR | 20190311 |  | 4 | TMU-RLY-5051/TMU1A/A AS FOUND TIME CHECK OUT OF TOLERANCE | N | N |  | N | YES | <D> **** Detailed Description **** During calibration of TMU-RLY-5051/TMU1A/A per PPM 10.25.20 (WO#02093957-01) TIME/CURRENT check was out of tolerance at 4.45 seconds. The data sheet tolerance is 4.46 - 4.94 seconds. The relay tested Sat with all other checks in tolerance. <I> **** Actions Taken **** Notified supervisor and PSRO. Adjusted per PPM 10.25.20. All As left Data in tolerance. | 02-00-TMU-RLY-5051/TMU1A/A
390906 | CR | 20190311 |  | 4 | Tool crib badge in/sccess gate on Radwaste 467' | N | N |  | N | NO | <D> **** Detailed Description **** Conduit associated with card reader at key card/badge access gate for Tool crib on 467' Radwaste needs maintenance. See attached pics on EDMS. <I> **** Actions Taken **** Generated CR and auto WR. <N> **** Equipment Description **** Tool Crib Radwaste 467'.
390907 | CR | 20190311 |  | 4 | TMU-RLY-5051/1C/7/A AS FOUND TIME CHECK OUT OF TOLERANCE |  |  |  | N | YES | <D> **** Detailed Description **** During calibration of TMU-RLY-5051/1C/7/A per PPM 10.25.20 (WO#02093957-01) TIME/CURRENT check 2 was out of tolerance at 4.43 seconds. Data sheet tolerance is 4.46 - 4.94 seconds.The relay tested Sat with all other data in tolerance. <I> **** Actions Taken **** Notified supervisor and PSRO. Adjusted per PPM 10.25.20. All As left data in tolerance. | 02-00-TMU-RLY-5051/1C/7/A
390908 | CR | 20190311 |  | 3 | DEFERRED CMRs - EC 17582 |  |  |  | N | NO | <D> **** Detailed Description **** The following CMRs are deffered as they are conservative in nature. The new motor has a lower full load amperage rating. EC 17586 EC 17587 EC 17591 EC 17592 EC 17593 <I> **** Actions Taken **** CR written to track completion of CMRs. <N> Due Date: 05-26-19
390909 | CR | 20190311 | CAQ | C | RWCU-M-V/1 new motor | N | N |  | N | NO | <D> **** Detailed Description **** During review of vendor information for the new RWCU-M-V/1 motor identified the motor frame size was smaller than the design required (Frame 56 instead of Frame 180). The motor start torque was the correct size (60 ft-lb). R24 is scheduled to replace RWCU-M-V/1 motor. **Any actions should be assigned to Component Engineering** <I> **** Actions Taken **** Framatome was contacted and they currently have 3 motors available. A CID was created, loaded to the WO and routed to Procurement.
390910 | CR | 20190311 |  | 4 | Squib Load at the Security Training Facility |  |  |  | N | NO | <D> **** Detailed Description **** During Security Quarterly training, an officer experienced a squib load round while firing the handgun. A squib load does not contain enough gunpowder, which causes the bullet to become stuck in the barrel of the weapon. Upon recognition of the squib load, the instructors immediately called a cease-fire, expanded the team, and discontinued range activity until an evaluation of cause, and extent of condition were completed. <I> **** Actions Taken **** As per industry standards when there is a quality issue with ammunition you discontinue use of that lot of ammunition and contact the manufacturer for evaluation. An armorer will remove the stuck bullet and inspect the handgun for damage. A safety walk down of the range was completed. A new lot of ammunition was selected for use and range operations were resumed. CR submitted.
390912 | CR | 20190311 | CAQ | D | TDAS X142 out of tolerance | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** during performance of ISP-RCIC-X301 CC (WO# 02108687-01), computer point X142 was found slightly out of tolerance. Desired GPM values are 0.0 +/- 50, 350 +/-10, 495 +/- 10, 600 +/-10 and 700 +/- 10. As found values were: 0.0, 330, 484, 589, and 692. <I> **** Actions Taken **** per step 7.10.1 of the procedure, I wrote this CR/WR and informed operations and noted on cover sheet <N> **** Equipment Description **** TDAS PIONT X142
390913 | CR | 20190311 | CAQ | D | Received RPIS or DMM INOP and RDCS INOP alarms | Y | Y |  | N | YES | <D> **** Detailed Description **** Received RPIS or DMM INOP, H13-P603.A7.1-7, alarm accompanied by ROD DRIVE CONTROL SYS INOP, H13-P603.A7.2-8, alarm. Reset RDCS per P603.A7 drop 2-8 ARP. RPIS OR DMM INOP, H13-P603.A7.1-7, & ROD DRIVE CONTROL SYS INOP, H13 -P603.A7.2-8, alarms are clear. RWM reinitialized per SOP-RWM-START. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-RDCC-1
390915 | CR | 20190311 |  | 3 | MRule Evaluations & System Inbox overdue items |  |  |  | N | NO | <D> **** Detailed Description **** This CR is being written to document the negative trend on timeliness of the screening of CRs for Maintenance Rule program impacts. Several System Inbox items and Maintenance Rule (MRule) evaluations are not being completed within the time requirements of Engineering Instruction SYS-4-22, Maintenance Rule Program. This creates a risk that determination of MRule exceedance of performance criteria and/or the required ICES reporting may not be timely. . Recommend Severity 3 be assigned to AR-ER. <I> **** Actions Taken **** Notification was made to the System Engineers and System Engineering Supervisors of the issue.
390916 | CR | 20190311 | CAQ | D | Could not find 2 survey maps in permanent records |  |  |  | N | NO | <D> **** Detailed Description **** While looking for radiation survey data for 2009 for the Rad waste (RW) 437 and RW 467 Monthly Routine Survey on a request from Regulatory Affairs, we were unable to locate 2 record surveys in microfilm, or imaged in Asset Suite Records module. It appears surveys where initiated in the old Visio survey folder (as the unsigned original RW 437 and RW 467 Monthly Routine surveys were found) in SharePoint, but the actual records were either not printed, reviewed, and approved; were lost; or were sent to records under a different Document Identification Code (DIC) numbers. Other Monthly Routine Surveys for RW, Reactor, and Turbine Buildings as part of the same search request were found. This appears to be limited to this time frame (2009-2010) as record storage and DIC numbers used by RP were in transition. Since this time surveys are now sent and stored electronically with Records Control with VSDS. <I> **** Actions Taken **** Contacted RP Supervision and discussed. Searched extensively in microfilm and in Assest Suite Record images for these 2009 Surveys and could not locate these 2 surveys. Initiated this CR to document condition.
390918 | CR | 20190311 |  | 4 | TSW-TC-11 temperature indication pegged at high stop. | N | N |  | N | YES | <D> **** Detailed Description **** TSW-TC-11 temperature indication is GT 200 F at the high peg. Output pressure is 13 psig and TSW-TCV-11 is about 30% open. All Exciter TSW field temperatures are indicating normal temps. ( 70-80 F). Suspect a bad temp. sensor? <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 501 W Review of temperatures in eDNA show the cooler inlet temperatures are approximately 140F and the outlet temperatures are approximately 90F, suspect a bad temperature indicator on the controller as stated in the CR. | 02-00-TSW-TC-11
390919 | CR | 20190311 |  | 4 | COND-P-2B and COND-P-2C oil sump levels high. | N | N |  | N | YES | <D> **** Detailed Description **** COND-P-2B oil level is 3/4 and COND-P-2C oil level is 23/32. The high spec per the logs is 11/16. All temps are normal. Recommend allowing levels to return to normal via normal leakage. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 441 E | 02-00-COND-P-2B,02-00-COND-P-2C
390920 | CR | 20190312 |  | 4 | Building 40 door | N | N |  | N | NO | <D> **** Detailed Description **** The door for building 40 is extremely difficult to open. <I> **** Actions Taken **** Initiated this CR and contacted supervision <N> **** Equipment Description **** Building 40 entry door
390924 | CR | 20190312 |  | 4 | Damaged light socket on TSW-CP-F/1B | N | N |  | N | YES | <D> **** Detailed Description **** The light socket for the Power ON light appears to be damaged on TSW-CP-F/1B preventing a new light bulb from being inserted correctly. <I> **** Actions Taken **** Iniated this CR. <N> **** Equipment Description **** East wall in CWPH. | 02-00-TSW-CP-F/1B
390926 | CR | 20190312 | CAQ | D | Door R109 needs maintenance | Y | Y |  | N | YES | <D> **** Detailed Description **** The door latch on R109 needs maintenance. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Security notification made, CR/WR generated This door is a secondary containment barrier, non-essential fire barrier, security barrier, and a HELB barrier. | 02-00-R-DOOR-R109
390929 | CR | 20190312 |  | 3 | 5.5.2 Procedure Enhancement | N | N |  | N | NO | <D> **** Detailed Description **** I have noted, at times, that the operating crews have closed RHR-V-68B with only wet well spray in service. RHR-V-68B is the minimum flow path for SW system B, and should only be closed when a large volume flow path has been lined up to take its place; only the injection (only when RPV pressure is less SW pump shutoff head) and drywell spray paths pass enough flow to fulfill this requirement. Please add a note prior to step 4.3.4 reminding operators that minimum flow is important to the SW system.
390931 | CR | 20190312 |  | 3 | Procedure change for OSP-RCIC/IST-Q701 | N | N |  | N | YES | <D> **** Detailed Description **** While performing a pre job brief in preperation for OSP -RCIC/IST-Q701 it was noted that in steps 7.2.96 and 7.2.97 RCIC-PI-604 was mislabeled as RCIC-P-604. Also, the note preceeding step 7.4.7.d directs the operator to use Attachment 9.6 durring the following steps. There is no Attachment 9.6 in the procedure, but there are two Attachment 9.5's in the procedure. <I> **** Actions Taken **** Wrote CR and informed CRS | 02-00-RCIC-P-1
390932 | CR | 20190312 | CAQ | D | Water tight door R422 handwheels | Y | Y |  | N | YES | <D> **** Detailed Description **** Working WO# 02139023-01 Door R007 , and Door R012 both doors have handwheel mounting bolts loose. this issue was found last annual inspection, CR 00377284, and 00377282. in the last year of door operation with the mounting bolts loose, not sure of possible extra dammage, due to not repairing in a timely manner. <I> **** Actions Taken **** another CR and WR | 02-00-R-DOOR-R007,02-00-R-DOOR-R012
390933 | CR | 20190312 | CAQ | C | Received RPIS or DMM INOP and RDCS INOP alarms. | Y | Y |  | N | YES | <D> **** Detailed Description **** Received RPIS or DMM INOP, H13-P603.A7.1-7, alarm accompanied by ROD DRIVE CONTROL SYS INOP, H13-P603.A7.2-8, alarm. Reset RDCS per P603.A7 drop 2-8 ARP. RPIS OR DMM INOP, H13-P603.A7.1-7, & ROD DRIVE CONTROL SYS INOP, H13 -P603.A7.2-8, alarms are clear. RWM reinitialized per SOP-RWM-START. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-RDCC-1
390934 | CR | 20190312 | CAQ | D | R5 Door top hinge is degraded | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** while entering the RCIC room at the RX 422, electricians noticed that the submarine style door is degraded at the top hinge. This is a potential safety issue as the top door hinge on R5 does not seem to be functioning as designed. This door could become unhinged altogether and seriously injure someone or even affect sensive plant equipment that is adjacent to the door. The door appears to seal adequately when it is closed. <I> **** Actions Taken **** Write CR, Notify CRS and Supervisor attach video and generate a WR <N> **** Equipment Description **** R5 door
390935 | CR | 20190312 |  | 4 | RWCU-P-3A seal leak | N | N |  | N | YES | <D> **** Detailed Description **** While performing a walk through of the RW 467' area a Health Physics technician observed that the RWCU-P-3A seal was leaking around 0.5 to 0.75 gallons/minute. The Health Physics technician also noted that RWCU-P-3A had been worked on recently. RWCU-P-3A was off at the time and both RWCU demins were in service at around 135gpm each. The leakage was mostly going down the nearby floor drain in the locked high rad contaminated area, but some was splashing out onto the step off pad and also onto the narrow hallway in the clean area. The area was roped off. <I> **** Actions Taken **** Wrote CR and informed CRS and radwaste control room <R> REP/REGE assingments have been cancelled with Compliance Supervisor concurrence. | 02-00-RWCU-P-3A
390936 | CR | 20190312 |  | 4 | Damaged Security fence by door R106. | N | N |  | N | NO | <D> **** Detailed Description **** There is damage on the fencing outside door R106. Request facilities access and repair as needed. Damage was not reported to security and cause is unknown. <I> **** Actions Taken **** CR/WR generated <N> **** Equipment Description **** Outside door R-106.
390937 | CR | 20190312 | CAQ | D | Received RPIS or DMM INOP and RDCS NOP alarms again. | Y | Y |  | N | YES | <D> **** Detailed Description **** Received RPIS or DMM INOP, H13-P603.A7.1-7, alarm accompanied by ROD DRIVE CONTROL SYS INOP, H13-P603.A7.2-8, alarm. Reset RDCS per P603.A7 drop 2-8 ARP. RPIS OR DMM INOP, H13-P603.A7.1-7, & ROD DRIVE CONTROL SYS INOP, H13 -P603.A7.2-8, alarms are clear. RWM reinitialized per SOP-RWM-START. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR | 02-00-CRD-RDCC-1
390939 | CR | 20190312 |  | 4 | PWC-P-102 Circuit Breaker will not stay closed | N | N |  | N | YES | <D> **** Detailed Description **** The circuit breaker for PWC-P-102 on PWC-CP-102 appears to have the Trip button stuck in just enough to cause immediate breaker open after close. Reference AR 00390403 for previous occurrence. This was discovered during performance of section 5.3 of SOP-PW-OPS. <I> **** Actions Taken **** CRS and Electrical notified. | 02-00-PWC-CP-102
390942 | CR | 20190312 | CAQ | D | Received RPIS or DMM INOP and RDCS INOP alarms again. | Y | Y |  | N | YES | <D> **** Detailed Description **** Received RPIS or DMM INOP, H13-P603.A7.1-7, alarm accompanied by ROD DRIVE CONTROL SYS INOP, H13-P603.A7.2-8, alarm. Reset RDCS per P603.A7 drop 2-8 ARP. RPIS OR DMM INOP, H13-P603.A7.1-7, & ROD DRIVE CONTROL SYS INOP, H13 -P603.A7.2-8, alarms are clear. RWM reinitialized per SOP-RWM-START. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR | 02-00-CRD-RDCC-1
390943 | CR | 20190312 |  | 4 | TMU-RLY-5051/TMU1A/C As found time out of tolerance | N | N |  | N | YES | <D> During calibration of TMU-RLY-5051/TMU1A/C per PPM 10.25.20 (WO#02093957-01) As found TIME/CURRENT check 2 was out of tolerance at 4.43 seconds . The data sheet tolerance is 4.46-4.94 seconds. The relay tested Sat with all other data in tolerance. <I> Notified supervisor and PSRO. Adjusted per PPM 10.25.20. All As left data in tolerance. <N> CR at INPROG, moved to Approved Status for OPS review. | 02-00-TMU-RLY-5051/TMU1A/C
390944 | CR | 20190312 | CAQ | D | (IST) LPCS-P-1 PERFORMANCE STEP CHANGE | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of OSP-LPCS/IST-Q702 under WO 02118311, LPCS-P-1 showed a step change decrease in pump performance to 95% of normal. The IST Action Level Low is 90% and has not yet been reached. LPCS-P-1 had been performing consistently around 99% of normal since 2007. When reviewing eDNA data during this test, flow and discharge pressure appear more sporadic than normal. LPCS-FT-3 last calibrated 11/7/18 and LPCS-PT-57 last calibrated 5/7/18, both with no issues. This CR is to document trending and it is recommended that another data point be gathered during the next test to better evaluate the pumps status. The next performance of OSP-LPCS/IST-Q702 is due 5/6/19. <I> **** Actions Taken **** Talked with supervisor and system engineering. Contacted Control Room. | 02-00-LPCS-P-1
390945 | CR | 20190312 | CAQ | C | INCOMPLETE SUREVEILLANCE PROCEDURE SUBMITTED TO RECORDS |  |  |  | N | NO | <D> **** Detailed Description **** CONTROL FOR PROCESSING. SURCEILLANCE PROCEDURE CSP-INST -D201 WAS SUBMITTED TO RECORDS CONTROL FOR PROCESSING WITHOUT THE ASSIGNED REVIEWER'S SIGNATURE AND DATE <I> **** Actions Taken **** NOTIFIED SUPERVISION AND RETURNED THE INCOMPLETE RECORD TO CHEMISTRY FOR COMPLETION AND RESUBMITTAL <N> Surveillance procedure CSP-INST-D201 has been completed and resubmitted to records. No further action required.
390946 | CR | 20190312 |  | 3 | TDAS Pt X142 has too many Poly1 variables | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** When attempting to calibrate X142 it was noted that it has two separate Poly1 variables in it's attributes. In one set M=0.99878 and B= -4.99711. In the other set M= 0.0006105 and B= -0.25. <I> **** Actions Taken **** Discussed with system engineer who requested this CR be written. Note that the second set of variables is the "correct" set. Engineering needs to evaluate whether the first Poly1 should be removed from the attributes page.
390947 | CR | 20190312 |  | 3 | INCOMPLETE ETAR TRAINING RECORDS SUBMITTED TO RECORDS |  |  |  | N | NO | <D> **** Detailed Description **** CONTROL FOR PROCESSING. THREE ETARS WERE SUBMITTED TO RECORDS CONTROL FROM OPERATIONS FOR PROCESSING WITHOUT ANY SUPPORTING/ATTACHED DOCUMENTS. <I> **** Actions Taken **** NOTIFIED SUPERVISION AND RETURNED THE INCOMPLETE RECORDS TO OPERATIONS FOR CORRECTION AND RESUBMITTAL
390948 | CR | 20190312 | CAQ | C | while performing WR# 29147524 sluggish response RCIC-FT-3 | Y | Y |  | N | YES | <D> **** Detailed Description **** when making changes to transmitter it had a sluggish responce. RCIC-FT-3 it took several seconds for the MA to stabelize when pressure was removed. <I> **** Actions Taken **** notified supervisor . POD approved 3/13/19 and uploaded to EDMS. Completed the RCIC quarterly and associated testing on 3/14/19 (WO 02137502). No issues experienced with RCIC flow indication or control. Ops, Engineering and I&C evaluated data during the run and compared it to data from previous performances of OSP-RCIC/IST-Q701. We have determined there is no DNC on RCIC-FT-3. There are no remaining open compensatory measures or corrective actions. | 02-00-RCIC-FT-3
390950 | CR | 20190312 |  | 3 | Generic Weaknesses Identified by the NRC during ILC 23 Exam |  |  |  | N | NO | <D> **** Detailed Description **** The following generic weakness was identified by the NRC during the administration of the ILC 23 NRC Operating Exam (this is not exam material): The majority of candidates failed to identify the proper RRC Loop Temperature when using SOP-RHR-SDC section 5.8.23. <I> **** Actions Taken **** Notified Operations and Training management. Incorporated the identified weak area into Attachment 2 of LO01608/LO01609 RO/SRO Post NRC Exam Checklist which will be completed during transition training. Recommend Non-CAQ severity D assigned to AR-OPSTRN.
390951 | CR | 20190312 | CAQ | D | EDR-DM-9 hold pump failed to start after precoat. | N | N |  | N | YES | <D> **** Detailed Description **** EDR-DM-9 hold pump failed to start following automatic precoat. The demin was shutdown per procedure. Stop was held for >10 seconds while controller was dialed to 0. Pressing 'stop' after the end of the precoat cycle started the hold pump. Demin D/P rose rapidly to a high value while processing ~20% of water to sample tanks. Demin tripped on high D/P and was B/W and precoated again. <I> **** Actions Taken **** Informed FIN RO (email), informed CRS. B/W and precoated EDR-DM-9 again. | 02-00-EDR-DM-9
390952 | CR | 20190312 |  | 4 | Received ADSORBER TRAIN A FLOW HIGH/LOW | N | N |  | N | YES | <D> **** Detailed Description **** Received ADSORBER TRAIN A FLOW HIGH/LOW 4.672.A9 1-3, verified proper alignment of OFFGAS SYSTEM. OG-FIS-616A is reading 27.3 SCFM and the alarm point is set at 30 SCFM. OG-RMC-618A is reading 81%. There is no indication of a leak into offgass system. | 02-00-OG-FIS-616A
390953 | CR | 20190313 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | YES | <D> **** Detailed Description **** Plant controllers and equipment response was normal. McNary - John Day single phase open and reclose was the cause. See log entry. Trending CR. <I> **** Actions Taken **** Dispatched Ops 2 The fault was J7- 500KV neutral ground overcurrent. There is no impact to the TRB or TRS lines. <N> **** Equipment Description **** RW 525. | 02-00-E-OSC-1
390956 | CR | 20190313 | CAQ | D | M&TE Rejected |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0060910 Fluke Dig. Mulitimeter- model 8842A found OOT. Rejected- Unable to adjust- No Longer supported. EFIN Eval: Range in question was not used. DEF #6954A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
390957 | CR | 20190313 | CAQ | D | M&TE Suspended/ Lost |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0065518 Fluke IR Thermometer- model 561 Missing from Tool Crib. Suspended/Lost. EFIN Eval: Usage #1 since re-performed. Usages #2 & #3 No data taken. DEF #6956A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
390958 | CR | 20190313 | CAQ | D | M&TE Rejected |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0059400 Omega IR Thermometer- model OS520 Rejected- No adjustments. EFIN Eval: Usage #1 Surveillance since re-performed. Usage #2 Go-N-Go. No plant Impact. DEF #6957A written. Action Required. <I> **** Actions Taken **** None Trending purposes only.
390960 | CR | 20190313 |  | 4 | MT-CRA-9A leaking oil | N | N |  | N | YES | <D> **** Detailed Description **** During operation of MT-CRA 9A there has been intermittent drops of oil identified on the ground. <I> **** Actions Taken **** Contacted Mechanical department to investigate. Mechanics determined that the crane is ok to stay in operation but recommend checking the oil level which will require a clearance. . Confirmed with author the oil is dripping and collecting on the base; it is not able to enter the sepnt fuel pool. | 02-00-MT-CRA-9A
390966 | CR | 20190313 |  | 4 | Vehicle Trap Gate | N | N |  | N | YES | <D> **** Detailed Description **** Vehicle Trap Gate 26 jumped track, requires maintenance <I> **** Actions Taken **** Security Equipment Cord Notified, FIN Notified, CR/WR generated . | 02-00-SEC-GATE-26
390968 | CR | 20190313 |  | 3 | (QA) 6 SLIs Not Aligned with QM-1 for ISO 17025:2017 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Six current Standards Laboratory Instructions (SLIs) are not aligned with the QM-1 â€œQuality Manualâ€ on the Laboratoryâ€™s commitment to meet the new ISO/IEC 17025:2017 standard. Failure to identify the ISO 17025:2017 requirements in the compliance matrix in SLI 2-43 â€œAudits and Assessmentsâ€ could result in noncompliance with the 2017 standard, which contains at least 50 new requirements beyond the 2005 standard. Failure to incorporate the new ISO 17025:2017 requirements into the other five SLIs could also result in noncompliance with the 2017 standard. This is a nonconformance with QM-1 â€œQuality Manualâ€, which requires documents affecting quality to be â€œcontrolledâ€ and â€œcorrectâ€. Requirements: (see EDMS) Factual Basis: (see EDMS) Insights: â€¢ Updates to the five SLIs above to change ISO/IEC 17025 :2005 to 17025:2017 were not coordinated with the changes to QM-1 rev 11, which committed the Standards Laboratory to ISO/IEC 17025:2017. â€¢ Two of these five SLIs have not been revised since 2015 and 2017; however, the other three SLIs were revised close to the time QM-1 changed (one SLI was actually revised on the same day as QM-1). â€¢ Quality could not find change management guidance within any SLI to ensure changes to the QM-1 â€œQuality Manualâ€ will drive changes to keep SLIs aligned with QM-1, and to ensure the QM-1 â€œpublishâ€ date is are coordinated with the â€œpublishâ€ dates for the changes to the affected SLIs. â€¢ Laboratory management stated that some of their customers may stay with the ISO/IEC 17025:2005 standard; therefore, QM-1 and many SLIs may need to include both the 2005 and 2017 standards. <I> **** Actions Taken **** Contacted Business Services Manager responsible for ENSL. . This is a Deficiency identified in Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV. <N> On 11/5/19 we found out that that the POC meeting scheduled for 11/7/19 is being cancelled due the inability for the POC committee to meet quorum requirements. This rescheduling of the POC meeting impacts approval of three Site Wide Procedure that are required in order to satisfy the AR closure action derive from the FY19 Calibration Lab internal audit. I have listed the ARâ€™s that will require extension beyond the 11/15/19 date. This extension request is in accordance with the requirements of SPW-CAP-01. . There were four assignments associated with this AR. The intent of this AR was to assure that with the â€œrenewedâ€ accreditation to the ISO 17025 2017 standard and with the carry over accreditation to ISO 17025 2005 standard were identified in the affected Standard Laboratory Instructions (SLI). The Calibration lab was granted dual accreditation by A2LA for a period of two years. . QM-1 is no longer an implementing document/manual for the Quality Program for Columbia Generating Station. Controlled procedures SWP-ESD-01 CGS Quality requirements, SWP-ESD-02 CGS Calibration Lab Technical Requirements and SWP-ESD-03 Calibration Lab Administrative requirements will now be the Quality and Corrective Action Program implementing procedures. . . Through the APW automated procedure process, modifications to SLI's 2-6, 2-25, 2-26, 2-31, 2-32, 2-34, 2-38, 2-37, 2-39 2-40, 2-43 were incorporated. The procedures are identified in in the compliance matrix in SLI 2-43. Per the spreadsheet loaded into the EDMS panel on the parent AR. These SLIâ€™s have been edited and approved to include the language that reflects that the lab is accredited to both the ISO 17025 2017 and the 2005 standards. ....................... See document loaded in EDMS for AR extension notes.
390969 | CR | 20190313 | CAQ | C | (QA) Incomplete Documentation of 8 CC/CR Resolutions |  |  |  | Y | NO | <A> I have reviewed and approved of the actions taken in the subassignement and the closure notes to document the actions taken. <C> Failed to fully document how the non-conformances with 10 CFR 50 Appendix B, NQA-1-2008, Q-M01. <D> **** Detailed Description **** (QA) Resolutions for eight out of thirteen Customer Complaints (CCs)/Condition Reports (CR) identified during ENSL A2LA and Quality Assurance audits were not fully documented. Resolutions of CC-142, -143, -144, -145, -150, and the AR-CRs 358700 and 376624 failed to fully document how the nonconformances with 10 CFR 50 Appendix B, NQA-1 -2008, and QM-1 â€œStandards Laboratory Quality Manualâ€ requirements were resolved to restore conformance. In all cases, the associated CC/AR-CR closures did not reflect all corrective actions taken to resolve the nonconformances. These are eight nonconformances with ANSI/NCSL Z540-1-1994 and ISO/IEC 17025:2017, which requires recording actions taken to resolve Customer Complaints. Requirements: (see EDMS) Factual Basis: (see EDMS) Insights: (more Insights in EDMS) â€¢ Self-assessments are not routinely performed to assess the sufficiency of documentation for deficient condition resolutions for audit-related or inspection-related CCs/CRs. â€¢ Many of the ARs reviewed lacked the objective evidence necessary to prove that an issue was resolved, even in cases where the issues were fully fixed. <I> **** Actions Taken **** Contacted the Business Services Manager responsible for ENSL. . This is a Deficiency identified in Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV.
390970 | CR | 20190313 |  | 4 | 606 lighting |  |  |  | N | NO | <D> **** Detailed Description **** Lighting on 606 in the Northwest corner is not working. This is an overhead light that provides lighting over the fuel inspection area. <I> **** Actions Taken **** Set up light stringers to provide additional lighting to the area. <N> **** Equipment Description **** overhead lighting northwest corner of Rx 606
390972 | CR | 20190313 | CAQ | C | (QA) 7 ENSL-Defined CAQs not identified as such in CCs & CAP |  |  |  | Y | NO | <A> I have reviewed and approved of the sub assignment actions and the clsure notes to document the actions. <C> Not in compliance with 10 CFR Appendix B, NQA-1, and SLI-2-25. <D> **** Detailed Description **** (QA) Energy Northwest Standards Laboratory (ENSL) had seven instances of a Condition Adverse to Quality (CAQ) occurring that was not identified as â€œCAQâ€ in the Customer Complaint (CC) and Corrective Action Program (CAP), contrary to requirements in 10 CFR 50 Appendix B, NQA-1, and SLI-2-25. This is similar to an issue within the previous 2016 audit AU-CL-16 where Quality identified seven CAQs were not identified by ENSL (see Weakness AR-CR 358700). In 2016, the Customer Complaint (CC) form did not have a way to identify a CAQ, but the CC form later included a Check Box for CAQ. However, in the seven new instances, each CC form had a mark in the Check Box for â€œnon-CAQâ€ instead of the Check Box for â€œCAQâ€. These seven new examples are nonconformances with 10 CFR 50 Appendix B Criterion XVI â€œCorrective Actionâ€ and NQA-1 Basic Requirement 16 â€œCorrective Actionâ€. Requirements: (see EDMS) Factual Basis: (see EDMS) <I> **** Actions Taken **** Contacted the Business Services Manager responsible for ENSL. . This is a Deficiency identified in Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV.
390973 | CR | 20190313 | CAQ | C | (QA) 3 Customer Complaints Not Documented/Tracked in AR-CRs |  |  |  | Y | NO | <C> CR Priority and Severity changed to CAQ, C/CALSERV at the request of OFM on 3.18.2019. <D> **** Detailed Description **** (QA) Three Customer Complaints (CC) were documented within the Severity Level (SL) 1 CR 368501 â€œ(Non EN/CGS) CC-151 [through] -153 (FRM) Shipping & Handling Damagesâ€ without a sufficient level of detail to understand the issues. Additionally, none of the three CCs were tracked in the Action Tracking database, contrary to QM-1 â€œStandards Laboratory Quality Manualâ€. While these three CCs were eventually documented in three individual corrective actions under one Condition Report (CR), this CR was not completed until approximately 10 months after initiation when the one CR was being prepared for closure. In addition to not meeting requirements of the Quality Manual, failure to document any details of the issues in the CR challenges managementâ€™s ability to understand and properly screen the issues for resolution. Also, the lack of any Corrective Actions for each issue resulted in the outstanding resolution not being visible to the management team on any backlog reports. Each of these three conditions are a nonconformance with QM-1. Requirements: (see EDMS) Factual Basis: (see EDMS) Insights: â€¢ ENSL is performing duplication of efforts by using two programs for corrective action (Customer Complaints and SWP-CAP-01/GBP-CAP-01). This creates an error-likely situation where some requirements may get overlooked. <I> **** Actions Taken **** Contacted the Business Services Manager responsible for ENSL. . This is a Deficiency identified in Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV. <N> CR re-opened at the request of Standards Lab
390974 | CR | 20190313 |  | 3 | Non-EN vehicle contacted other non-EN vehicle while parking |  |  |  | N | NO | <D> **** Detailed Description **** An employee struck another employee's personal vehicle while parking. No damage to EN property occurred. No injuries resulted from the accident. <I> **** Actions Taken **** Reported the accident to applicable parties as required per ISPM-1. Initiated Condition Report.
390975 | CR | 20190313 | CAQ | C | (QA) Actions for 3 Customer Complaints Not Tracked in AR-CRs |  |  |  | Y | NO | <A> I have reviewed and approve of the actions taken and the closure notes to document the actions. <C> CR Priority and Severity changed to CAQ, C/CALSERV at the request of OFM on 3.18.2019. <D> **** Detailed Description **** (QA) Actions to address Customer Complaints (CCs) for ENSL were not tracked in the Action Tracking database as required by QM-1 â€œStandards Laboratory Quality Manualâ€. Three examples demonstrate that AR-CRs are being initiated well after the creation of the CCs, which does not meet the QM-1 for the tracking AR-CR. For one CC, the actual resolution of the issue was documented as complete on the CC form approximately 77 days after the initiation of the CC and CR. The failure to establish corrective actions in the Action Tracking database does not meet QM-1, and it introduces a situation where the outstanding action is not visible in the Energy Northwest Corrective Action Program (CAP)/Non-CAP backlog reports. Requirements: (see EDMS) Factual Basis: (see EDMS) <I> **** Actions Taken **** Contacted the Business Services Manager responsible for ENSL. . This is a Deficiency identified in Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV.
390976 | CR | 20190313 |  |  | SLI-2-30 & TPD Not Align with Qual directory | [5 empty] | <D> Revisions to the Qualification Directory should be reconciled with associated procedures.
390977 | CR | 20190313 |  |  | Standard Lab Personal not assigned to Qual Groups | [5 empty] | <D> Three laboratory employee IDs were indentified that did not have the respective Qualification Groups listed for training completed.
390978 | CR | 20190313 | CAQ | C | (QA) No CCs/CRs for ENSL-CAQ on 5 Broke/Missing Tamper Seals |  |  |  | Y | NO | <A> I have reviewed and approved of the actions taken and the closure notes. <C> Not sure if these were used in the plant. <D> **** Detailed Description **** (QA) Five Customer Complaints (CCs) and associated Action Request Condition Reports (AR-CRs) were not initiated by the Standards Laboratory staff when five customer equipment items were found with a Condition Adverse to Quality (CAQ) for broken or missing tamper seals, contrary to QM-1 â€œQuality Manualâ€. A review of 18 calibration records revealed five calibration records indicate that tamper seals were either broken or missing, but no CCs or AR-CRs were found. One of the five records indicate the equipment had been tampered with. This a nonconformance with 10 CFR 50 Appendix B Criterion XVI â€œCorrective Actionâ€ and NQA-1 Basic Requirement 16 â€œCorrective Actionâ€ for not identifying five CAQs. Requirements: (see EDMS) Factual Basis: (see EDMS) Insights: â€¢ Interview with one Technician revealed it is not the practice to write CRs on tamper seal discrepancies; and stated they only document the discrepancy on the calibration record notes and install a new seal, and then management would see the notes when reviewing calibration records. <I> **** Actions Taken **** Contacted the Business Services Manager responsible for ENSL. . This is a Deficiency identified in Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV. . <N> I have reviewed and approved the closure actions and comments. Rich Hatten 5/21/19 .. 11/6/19 On 11/5/19 we found out that that the POC meeting scheduled for 11/7/19 is being cancelled due the inability for the POC committee to meet quorum requirements. This rescheduling of the POC meeting impacts approval of three Site Wide Procedure that are required. in order to satisfy the AR closure action derive from the FY19 Calibration Lab internal audit. I have listed the ARâ€™s that will require extension beyond the 11/15/19 date. This extension request is in accordance with the requirements of SWP-CAP-01. . 11/6/19 uploaded recovery plan into EDMS and requested AR extension. . 12/12/19 Closure Notes Customer complaints are no longer used for CGS notification of corrective actions. Guidance obtained from SWP-CAP-01 and utilization of the Corrective Action Process replaces Customer Complaints. The customer complaints have been replaced by a CR and Out of Tolerance form specified in the new procedure SWP-ESD-02 section 2.3 which uses Form 20024 and an Asset Suite Condition Report to document the out of tolerance M&TE or standard. Missing or damaged Tamper seals for CGS assets are also identified to the Corrective Action process and identified through a CR upon initial discovery of the compromised seal. Guidance for Tamper seal compromise and subsequent corrective action for CGS are provided by procedure SWP -ESD-03 section 3.16. The procedure, SWP-ESD-03, provides guidance to reference SWP-CAP-01 to initiate a CR and provide notification to the plant. . For this five missing tamper seals identified during the audit all M&TE with the missing or damaged seals were located and the tamper seals were affixed to the M&TE prior to any use at CGS. ............................................................ AR being extended. See extension notes in EDMS. (not enough characters remain in this note type)
390980 | CR | 20190313 | CAQ | C | RAM labels and stickers contain incorrect trefoil color |  |  |  | N | NO | <D> **** Detailed Description **** (IP 71124.01 SA Deficiency) Most Radioactive Material (RAM) labels and stickers used throughout the plant use a standard radiation symbol (trefoil) that is not in alignment with 10CFR20.1901. Specifically, the trefoil used is red. 10CFR20.1901 requires the trefoil to be magenta, purple, or black. The labels and stickers do contain the words "Caution Radioactive Material" and are on a yellow background, both of which are compliant with the 10CFR20.1901 and 1904. All labels and stickers identified in use are effectively communicating the radiological hazard present. <I> **** Actions Taken **** Verified that all other required information was aligned with the regulations. Notified Radiological Operations Supervisor and the Chemistry/Radiological Services Manager. Initiated actions to order replacement labels and stickers.
390981 | CR | 20190313 | CAQ | C | (QA) Finding - No Tamper Seals on 3 Calibrated M&TE for CGS |  |  |  | Y | NO | <C> This was calibrated and ready to send back to Columbia for Plant use; and nothing is in place to prevent or peer check this. This was stopped by QA. <D> **** Detailed Description **** (QA) Tamper seals were not installed on 3 pieces of M&TE that were calibrated and ready to send back to the Columbia nuclear plant for use. The three pieces of M&TE a Clemco CMS-2 (0068232), and 2 Tektronix TDS3032B O-scopes (0053527 and 0063868). The Clemco CMS-2 has a calibration adjustment screw accessible on the front panel. Tektronix TDS3032B has a CAL button on the back of the instrument. The potential consequence is that adjustments could be made to these pieces of M&TE without evidence of tampering. This is a noncompliance with both QM-1 â€œStandards Laboratory Quality Manual" and ANSI/NCSL Z540-1-1994 â€œCalibration Laboratories and Measuring and Test Equipment General Requirementsâ€. Requirements: (see EDMS) Factual Basis: (see EDMS) Insights: â€¢ Although QM-1 section 11.6 above does not specifically mention â€œmissingâ€ tamper seals, â€œmissingâ€ is very much like â€œbrokenâ€ tamper seals for allowing â€œcompromiseâ€ and for not protecting the â€œintegrity of the calibrated itemâ€ and â€œinterests of the laboratory and the customerâ€. (Also, a broken tamper seal could subsequently fall off and become a missing tamper seal.) â€¢ The technicians interviewed knew where in the laboratory to find the tamper seals to be installed. â€¢ During the AU-CL-14 audit, Quality identified a similar issue with respect to missing tamper seals within AR-CR 319403 â€œ(QA) ENSL Lab Standard without Tamper Indicating Sealsâ€. <I> **** Actions Taken **** Contacted the Business Services Manager responsible for ENSL. . This is a Finding identified in Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV. . <N> Based on the discussion at the Quality audit Exit meeting on 3/14/19, there is a need for an Extent of Condition to be performed for any other M&TE that has already been sent from ENSL to CGS without the required tamper indicating seals to protect the integrity of the calibration by ENSL.
390982 | CR | 20190313 | CAQ | C | Form 27139 does not fully align with USNRC RG 8.15 |  |  |  | N | NO | <D> **** Detailed Description **** (IP 71124.01 SA Deficiency) The TEDE ALARA evaluation form (27139) used at CGS does not reflect all of the requirements of USNRC Regulatory Guide 8.15 section 2.1. Specifically, the form does not clearly evaluate the impacts of engineering controls or the potential for access limitations, exposure stay times, or other controls before assigning the use of respiratory protection. These considerations are not covered by the RWP planning checklist, and they were not discussed in the ALARA plans for the reviewed RWPs. <I> **** Actions Taken **** Notified the Radiological Operations Supervisor and the Chemistry/Radiological Services Supervisor.
390983 | CR | 20190313 | CAQ | C | (QA) ENSL Did Not Properly Address CAQ/SCAQ for OOT Cal. Std |  |  |  | Y | NO | <C> Non-conformance with 10 CFR 50 Appendix B, Criterion XVI. <D> **** Detailed Description **** (QA) When a power system simulator calibration standard was found Out of Tolerance (OOT), a Condition Report (CR) was not promptly initiated for a Condition Adverse to Quality (CAQ) for the non-conformance that could adversely affect the Columbia nuclear plant, contrary to SWP-CAP-01 â€œCorrective Action Programâ€. After the OOT standard was found to be a Significant CAQ (SCAQ) based on the Energy Northwest Standards Laboratory (ENSL) definition, the cause and corrective action to prevent repetition were not documented as required by the QM-1 â€œQuality Manualâ€ and resolution was not timely as required by industry standards committed to within QM-1. The unacceptable handling of this CAQ is a nonconformance with 10 CFR 50 Appendix B, Criterion XVI. Corrective Action and NQA-1 â€œQuality Assurance Requirements for Nuclear Facility Applicationsâ€ Requirement 16 Corrective Action. Requirements: (see EDMS) Factual Basis: (see EDMS) Insights: â€¢ The Customer Complaint documents an incorrect assumption that none of the associated M&TE would be affected, which caused delays in the assessment. â€¢ This resolution of this AR-CR should clearly document the data that shows either no re-calibration required, or customer notification for the re-calibration for Columbia cal. codes 64539, 66287, 65521, and external serial number HWH-B62204. <I> **** Actions Taken **** Contacted the Business Services Manager responsible for ENSL. . This is a Deficiency identified in Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV. <N> 11/6/19 On 11/5/19 we found out that that the POC meeting scheduled for 11/7/19 is being cancelled due the inability for the POC committee to meet quorum requirements. This rescheduling of the POC meeting impacts approval of three Site Wide Procedure that are required in order to satisfy the AR closure action derive from the FY19 Calibration Lab internal audit. I have listed the ARâ€™s that will require extension beyond the 11/15/19 date. This extension request is in accordance with the requirements of SWP-CAP-01. 11/6/19 uploaded recovery plant into EDMS and requested AR extension. ...................... See document in EDMS for AR extension notes.
390985 | CR | 20190313 | CAQ | D | WEA-FU-9E, unavailable for use, found partially removed | N | Y |  | N | YES | <D> **** Detailed Description **** While attemptint to perform PM on WEA-FU-9E, it was found that the system duct work has been removed and never reinstalled. WO 02118823 from AR 302783 removed the ductwork to the fan, system is currently just blanked off. the system needes to be abandoned in place/removed and PM's retired or it needs to be hooked back up with properly documented ducting. <I> **** Actions Taken **** Contacted engineering and operations on status of the system. Recommend: OPS hang a caution tag on the fan "DO NOT USE, SYSTEM PARTIALLY REMOVED". Recommend: Engineering evaluate if system should be abanded or restored. Recommend: Engineering write SMS for PMID 13192-01 to retire or put on hold until system restoration. <N> Cross referenced WO 02128875 and uploaded e-mail from Engineering. Initiated and cross referenced AR-EVAL 391034 to evaluate permanent installation. | 02-00-WEA-FU-9E
390988 | CR | 20190313 | CAQ | D | OG-AY-12B rising trend for OG Hydrogen Concentration | N | Y |  | N | YES | <D> **** Detailed Description **** OG-AY-12B hydrogen concentration indicates a slowly rising trend. On 3/4/19, hydrogen concentration was 0.14% and has since shown a slow but overall rising trend. As of 3/13/19 at 12:00 it indicates 0.30%. This is twice the reading of OG-AY-12A which currently indicates 0.14%. <I> **** Actions Taken **** Notified the CRS and Shift Manager. Submitted CR and Work Request. | 02-00-OG-AY-12B
390989 | CR | 20190313 |  | 2 | Aggregate review of risk recognition events |  |  |  | N | NO | <D> **** Detailed Description **** Between December 1, 2018 and March 7, 2019 six events have occurred where the common or contributing cause theme has emerged where failure to recognize the risk or consequence of decisions made. Actions conducted prior to (job planning and preparation) or during implementation of a work task resulted in the events cross-referenced to this condition report (see EDMS for additional event details). Further investigation should occur to review the events in aggregate and identify any gaps in current station Focus Area â€œKey Actions and Behaviorsâ€ or areas for improvement response actions. Recommend SL-2 to AR-ENTRISK or AR -PERFIMP. <I> **** Actions Taken **** Discussed issue with Performance Improvement Manager, Strategic Plan and Risk Manager and initiated CR <N> No suggested additional actions at this time and no gaps identified in the station focus area "Key Actions and Behaviors", allow the focus area actions run time to then measure effectiveness and performance of the organization. The station focus areas reinforce the use of the HU tools, Excellence Model expectations and Risk Management Principles in our everyday work. See assessment matrix and additional details in EDMS.
390990 | CR | 20190313 |  | 4 | D102 door cage | N | N |  | N | YES | <D> **** Detailed Description **** The exterior cage hinges for Door D102 need maintenance. contact security at ext. 2185 for further details <I> The barrier function of the door remains functional. contact security for additional details. | 02-00-D-DOOR-D102
390993 | CR | 20190313 |  | 3 | FLEX-CAB-4 Interferes with LLRT Test Station |  |  |  | N | NO | <D> **** Detailed Description **** The current location of Flex Box (FLEX-CAB-4) on RB 471' just west of crane floor hatch (A1 hatch, Storage Location Permit 325) interferes with the LLRT test area use during refuel outages (see CR 363632). Per LCS SR 1.11.1.1 bases, the designated storage areas have been evaluated and selected to protect the FLEX equipment from hazards. Storage in nondesignated locations requires an engineering evaluation to maintain the N+1 requirement. I recommend an evaluation to support relocating FLEX-CAB-4 to the RB 471â€™ east of the A1 hatch opening through the end of R24, or permanently. This would eliminate moving this heavy cabinet around and the attendant safety/bump hazard risks. <I> **** Actions Taken **** Reviewed LCS 1.11.1 and bases, FLEX-01, OSP-FLEX-A106, TM -2183 and TM-2187. Discussed with I&C and Engineering.
390994 | CR | 20190313 |  | 3 | SLI-2-30 & TPD Not Align with Qual directory |  |  |  | Y | NO | <D> **** Detailed Description **** Revisions to the Qualification Directory should be reconciled with associated procedures.
390995 | CR | 20190313 |  | 3 | Standard Lab Personal not assigned to Qual Groups |  |  |  | Y | NO | <D> **** Detailed Description **** Three laboratory employee IDs were indentified that did not have the respective Qualification Groups listed for training completed. <N> this is a duplicate CR - 391076 and 391077
390996 | CR | 20190313 |  | 4 | ED run through Security X-Ray machine |  |  |  | N | NO | <D> **** Detailed Description **** Employee had ED on outside the protected area to access the Evap ponds that are posted as an RMA. Upon returning to the protected employee placed ED in tray and it started into the X-ray machine. The mistake was realized and the belt was reversed but it had already been exposed. Employee reported to HP access. Employee spoke with HP Supervisor and was coached. RCA restriction was lifted. <I> **** Actions Taken **** Initiated CR, coached employee, employee spoke with HP Supervisor, lifted emplyees restriction
390998 | CR | 20190313 | CAQ | C | C-509 door on RW 525 leakage at upper top/side seal. | Y | N |  | N | YES | <D> **** Detailed Description **** WO 02107913 performs Fire Door Operability - Semiannual, Annual, Biennial PM on the various Fire Doors in the plant. RW 525 - Div A HVAC room, Eastside door C-509 has leakage at the top and upper sides. Per discussion with craft who typically performs these checks, it used to be to check for contact between the door and the seal. The craft now use paper to check the seal. Current leakage seems to be close to what it has been in the past per discussion with the craft, however this CR was for documenting. <I> **** Actions Taken **** Discussed with Engineering as information and generated CR. WIll call CRS after initiating the CR as the line was busy prior to generating this AR CR. Expect no issues from any previous values as again the leakage appears to be consistent with that observed in the past. Reference AR CR 298467 generated previously in 2013 regarding this small W-DOOR-C509 door. <N> From TM-2082: AR-CR 298467 identified leakage around W-DOOR-C509 between the RW 525 Division 1 HVAC room and the Cable Chase. Extent of condition inspections found leakage around multiple other doors leading into and between BOS areas. Subsequent testing was performed under WO 02052961 to quantify the impact of observed leakage. The testing found that the CRE could be adequately pressurized with respect to the adjacent spaces, in spite of the identified leakage. The testing went on to measure boundary space pressures with each identified door propped Â½ inch open. It was found that positive pressure was maintained with respect to the Control Room under all tested conditions. Thus, it was concluded that leakage around any of the doors (W-DOOR-C223, W-DOOR-C313, W -DOOR-C314, and W-DOOR-C509) that is less than would be created by propping the door 1/2 inch open does not prevent positive pressurization of the Control Room with respect to the adjacent spaces. | 02-00-W-DOOR-C509
390999 | CR | 20190313 | CAQ | D | MS-DPIS-9A found OOT | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of ISP-MS-Q931, MS-DPIS-9A as found trip was OOT at 132 psid (Calibration limit: 128 psid to 130 psid). Adjusted per step 7.2.34 and attachment 9.1 to as left trip value of 129 psid. <I> **** Actions Taken **** Informed operations, supervision, adjusted per attachment 9.1, wrote CR. <N> **** Equipment Description **** RX 501
391000 | CR | 20190313 |  | 4 | CREH Program doc is not in alignment with PPI PPM 1.5.16 |  |  |  | N | NO | <D> **** Detailed Description **** The current revision of the Control Room Envelope Habitability Program CREH-01 (Rev. 0, Minor Rev. 001) does not contain a signed approval page as required per PPI PPM 1.5.16, attachment 7.1. This issue will be resolved with a planned revision of CREH-01 per assignment 376075-41. It was also noted that CREH-01 resides on Sharepoint as an APW (Automated Process Workflow) document. CREH-01 will be extracted from APW and the master copy will be controlled by CREH manager as required by 1.5.16. This is an administrative issue only and does not affect plant equipment. <N> Assignment 00391025-01 created to verify that CREH-01 has been extracted from APW.
391001 | CR | 20190313 | CAQ | C | (QA) CC/CR Not Created for ENSL-CAQ on Unverified Proced Use |  |  |  | Y | NO | <C> Condition Adverse to Quality (CAQ) for use of an unverified and unapproved procedure to calibrate a load cell, contrary to 10 CFR 50 Appendix B and NQA-1. <D> **** Detailed Description **** (QA) Condition Report (CR) was not initiated upon realizing a Condition Adverse to Quality (CAQ) for use of an unverified and unapproved procedure to calibrate a load cell, contrary to 10 CFR 50 Appendix B and NQA-1. There is also no evidence of the generation of a Customer Complaint form, contrary to SLI 2-25 â€œCustomer Relationsâ€, which drives initiation of the CR. The actual consequence was that load cell was erroneously found to be Out of Tolerance based on the use of an unverified and unapproved calibration procedure; however, after the Standards Laboratory identified this error and used the latest verified and approved calibration procedure, the load cell was found to be in tolerance. This a nonconformance with 10 CFR 50 Appendix B Criterion XVI â€œCorrective Actionâ€ and NQA-1 Basic Requirement 16 â€œCorrective Actionâ€. Requirements: (see EDMS) Factual Basis: (see EDMS) Insights: â€¢ The author of the unapproved revision was not accessible during the time of the first calibration, and could not be contacted for additional information. â€¢ Condition Reports need to be generated for procedural noncompliance issues to ensure ENSL-defined CAQ are promptly identified and corrected, and to alert the laboratory personnel of the possible need to perform an Extent of Condition. The initiation of a Condition Report also provides the opportunity for trending of CAQs by the laboratory. â€¢ After notification by Quality of the load cell issue above, the ENSL Quality Manager initiated CC-175 and AR-CR 390592 for a similar issue for use of the wrong procedure to calibrate a multimeter. <I> **** Actions Taken **** Contacted the Business Services Manager responsible for ENSL. . This is a Deficiency identified in Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV. <N> 11/6/19 On 11/5/19 we found out that that the POC meeting scheduled for 11/7/19 is being cancelled due the inability for the POC committee to meet quorum requirements. This rescheduling of the POC meeting impacts approval of three Site Wide Procedure that are required in order to satisfy the AR closure action derive from the FY19 Calibration Lab internal audit. I have listed the ARâ€™s that will require extension beyond the 11/15/19 date. This extension request is in accordance with the requirements of SWP-CAP-01. 11/6/19 uploaded Recovery Plan into EDMS and Requested AR extension. 12/12/19 Closure Notes Currently the Calibration is working with Records and Information Management to develop a method of controlling automated calibration procedure within Asset Suite. . The described method is not available to the Calibration Lab. Currently procedures are controlled administratively. New procedure SWP-ESD-03 section 3.0 and Attachment 7.1 contain the guidelines for SLI development. Form 20031 is used to show that that there has been review and approval for use of the automated procedures. ............................................................ See EDMS for AR extension notes.
391003 | CR | 20190313 | CAQ | B | Finding - ENSL Program Deficiency in CC/CAP Implementation |  |  |  | Y | NO | <C> RISK: Medium. CAUSE: Unknown/complex. Investigation Template Required. ... Non-conformances with CAP requirements in 10 CFR 50 Appendix B Criterion XVI â€œCorrective Actionâ€. <D> **** Detailed Description **** (QA) Energy Northwest Standards Laboratory (ENSL) has a Program Deficiency in implementation of their Customer Complaint (CC) / Corrective Action Program (CAP), as evidenced by the seven audit issues listed below. These seven new issues include nonconformances with CAP requirements in 10 CFR 50 Appendix B Criterion XVI â€œCorrective Actionâ€ and NQA-1 Basic Requirement 16 â€œCorrective Actionâ€, as well as, nonconformances with CC requirements in the ISO/IEC 17025:2017 and ANSI/NCSL Z540 .1:1994.1 standards. The previous audit identified five old issues similar to the seven new issues listed below regarding CC/CAP implementation, which suggests there may be a broader issue. Repeat issues include failure to initiate Condition Report (CRs) for Conditions Adverse to Quality (CAQs) and not identifying CAQs within CCs/CRs. New issues include not initiating CCs and CRs, not properly addressing and resolving an ENSL-defined CAQ/SCAQ, not creating action assignments and not tracking corrective actions within CRs, and not documenting all corrective actions taken in CC/CR resolutions. Failure to initiate CCs/CRs could result in ENSL not recognizing, tracking, and trending problems, which could hinder the resolution of problems. However, the only unresolved issues identified were from the previous audit, one for not initiating CRs and one for not identifying CAQs as such in CCs or CRs. Factual Basis: (see EDMS) Insights: â€¢ Interviews with ENSL personnel revealed a reluctance to initiate a CC and/or a CR for issues that can be easily corrected outside of the CC/CR processes. â€¢ ENSL is performing duplication of efforts by using two programs for corrective action (Customer Complaints and SWP-CAP-01/GBP-CAP-01). This creates an error-likely situation where some requirements may get overlooked. <I> **** Actions Taken **** Contacted the Business Services Manager responsible for ENSL. . This is a Fiinding identified in Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV. <N> 11/6/19 On 11/5/19 we found out that that the POC meeting scheduled for 11/7/19 is being cancelled due the inability for the POC committee to meet quorum requirements. This rescheduling of the POC meeting impacts approval of three Site Wide Procedure that are required in order to satisfy the AR closure action derive from the FY19 Calibration Lab internal audit. I have listed the ARâ€™s that will require extension beyond the 11/15/19 date. This extension request is in accordance with the requirements of SWP-CAP-01. 11/6/19 Recovery Plan loaded into EDMS and AR extension requested. . 12/12/19 Closure Notes The calibration lab has taken the action to split the CGS calibration program from the commercial customer program. . Controlled procedures SWP-ESD-01, SWP-ESD-02 and SWP-ESD-03 have been developed and reviewed to address this audit finding. On 11/14/19 these procedures were presented to POC on 12/5/19 with approval with comments obtained. The comments made are incorporated into SWP-ESD-01/02/03 and resubmitted and approved in the APW system. plitting the Quality program for the calibration lab will serve to address this audit finding. . No longer will one Quality manual or one set of procedures define the quality aspect of the calibration program. Customer complaints have been eliminated from the CGS program and embrace of SWP-CAP-01 will define the calibration labâ€™s corrective action program as the program applies to CGS. ........................... AR extended per SWP-CAP-01. Email with VP approval attached to EDMS approving recovery plan. Recovery plan attached to EDMS. D. Van Alyne 12/12/19.
391004 | CR | 20190313 |  | 4 | Poor Lighting RW467' Valve Galleries and Associated Rooms | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Poor Lighting in RW467' "A" Valve Gallery / "A" Valve Gallery Pipe Space / "A' RWCU Hold Up Pump Room. Poor Lighting in RW467' "B" Valve Gallery. The lighting situation in these areas, does not meet OSHA Standards. <I> **** Actions Taken **** Notified HP Lead Technician Notified HP Supervision Initiated CR/WR ESOMS Log Entry Made <N> **** Equipment Description **** RW 476' Valve Galleries
391005 | CR | 20190313 | CAQ | C | (QA) ARMA - No Impl. Instructions for 3 Requirements in QM-1 |  |  |  | Y | NO | <C> Non-compliance with 10 CFR 50 Appendix B Criterion V. <D> **** Detailed Description **** (QA) No Standards Laboratory Instructions (SLIs) exist to implement three specific requirements within QM-1 â€œStandards Laboratory Quality Manualâ€, which requires administrative SLIs to implement specific requirements of this manual. This is a noncompliance with 10 CFR 50 Appendix B Criterion V â€œInstructions, Procedures, and Drawingsâ€, which requires quality affecting activities to be prescribed by instructions, procedures, or drawings. Implementing instructions are required because work is not normally performed with the companyâ€™s quality manual in hand. An actual consequence of no SLI for the use of tamper seals was inconsistent use when Quality found only one of seven similar decade boxes had tamper seals. Actual consequences of no SLI for a QM-1 change process including change management instructions were approximately 189 calibration certificates were issued since 1/10/19 incorrectly showing the previous revision of QM-1. Requirements: (see EDMS) Factual Basis: (see EDMS) Insight: â€¢ QM-1 does not commit to or make reference to any of the Columbia Generating Station procedures for preparation, review, approval, or revision of documents affecting quality. <I> **** Actions Taken **** Contacted the Business Services Manager responsible for ENSL. . This is an Area Requiring Management Attention (ARMA) identified in Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV. <N> 11/6/19 These are the notes that support a fourth extension of this AR. On 11/5/19 we found out that that the POC meeting scheduled for 11/7/19 is being cancelled due the inability for the POC committee to meet quorum requirements. This rescheduling of the POC meeting impacts approval of three Site Wide Procedure that are required in order to satisfy the AR closure action derived from the FY19 Calibration Lab internal audit. I have listed the ARâ€™s that will require extension beyond the 11/15/19 date. This extension request is in accordance with the requirements of SWP-CAP-01. 11/6/19 Recovery Plan uploaded into EDMS and AR Extension has been requested. . 12/12/19 Closure Notes . Tamper seal are now addressed in SWP-ESD-03. Section 3.15 of that procedure contains the procedural guidance that addressed receiving an asset without a Tamper seal and addressing tamper seal on calibration standards. QM-1 nor SLI are used to address missing tamper seal on CGS M&TE or standards assets. Qm-1 and SLI are only used with the calibration labâ€™s commercial customers. . . QM-1 change management will follow the requirements outlined in GBP-COM-07. QM-1 will only apply to commercial calibrations performed by the lab and support the A2LA ISO 17025 accreditation ........................................ See EDMS for AR extension notes.
391007 | CR | 20190313 |  | 3 | SOP-DEH-OPS sect 5.19 enhancement |  |  |  | N | NO | <D> **** Detailed Description **** SOP-DEH-OPS sect 5.19 enhancement. Step 5.19.5 states "Monitor DEH Quadvoter area temperature". there is noequipment or devices to monitor the temperature at this time. Please eliminate this step. <I> **** Actions Taken **** SM authorized NA
391009 | CR | 20190313 |  | 3 | SA-PRV-1 missing pressure plate | N | N |  | N | NO | <C> EOC Is needed to be done. <D> **** Detailed Description **** During the performance of WO 02132476-01 it was identified that the pressure plate was missing on SA-PRV-1(cat id 0060114600) a new pressure plate was procured and installed per the vendor manual. It appears that SA-PRV-1 was replaced under WR 29144952 10/2018. ommend an action to inspect and verify pressure plate installation on all cat ID 0060114600 that are currently in stores. ommend an action to inspect and verify pressure plate installation on all cat ID 0060114600 that are currently in stores <I> **** Actions Taken **** Procured and installed pressure plate on SA- PRV-1, generated CR
391010 | CR | 20190313 |  | 3 | E-CB-N2/6 trouble racking in |  |  |  | N | YES | <D> **** Detailed Description **** While attempting to rack in E-CB-N2/6 the electronic racking tool stopped several times and then racked out the breaker. Upon using an EO the breaker racked very smooth until just at the point of stab engagement then became very stiff. On the first attempt the EO stopped and racked out the breaker to a safe position to expand the team. OPS, Elec and SSS inspected the breaker and cubicle. A minor slack adjustment was made on one of the stabs and they were relubed. It was decided to try one more time, when the EO racked the breaker to the stab engagement position it was still stiff but it was able to completely seat and disengage the screw device. <I> **** Actions Taken **** MCR & Elec supervision Informed, | 02-00-E-CB-N2/6
391011 | CR | 20190313 |  | 4 | Generation impacted by work delay |  |  |  | N | NO | <D> **** Detailed Description **** 5 CW fans are out of service to support visual inspection of MC-5M. That was to be complete and bus returned to service at 1900 3/13/2019. Work was not completed as schedule. This results in approximately 5MW electric being lost every hour. Since the work will not be completed until the next day a substantial amount of generation is being lost. 20 extra hours without these 5 fans is 100 MW electric of lost generation. For perspective it takes 44 MW electric to run the entire station for one hour. Currently the cost of power is low at $32 a MW. Roughly $3200 in lost generation <I> **** Actions Taken **** There were no electricians on swing shift qualified to complete the inspection. Questioned the WWM why this work was not completed as scheduled. Emphasized the impact to generation and requested this be completed by COB thursday.
391013 | CR | 20190313 | CAQ | D | Accumulator Trouble Alarm | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-22-39 was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear. <I> **** Actions Taken **** Cleared alarm per SOP <N> **** Equipment Description **** RB 522 | 02-00-CRD-HCU-2239
391014 | CR | 20190314 |  | 4 | 2 Pieces of M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** 2 Pieces of M&TE were found OOT. Both were Not used during Calibration cycles. Calcode #0066227 Fluke Module- model 700PD3 +/-5PSID/G. Adjusted within specs. DEF #6965A written. Calcode #0067371 Hytorc Gauge 10,000psig. Rejected- Unable to adjust. DEF #6966A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391019 | CR | 20190314 |  | 3 | Exam Failure |  |  |  | N | NO | <D> A student (ORG 84000) scored a failing grade on the written exam for ME000070 Basic Rigging initial training. <I> Consulted TDI-02 for exam failure procedure. Notified student's supervisor. Notified training supervisor. <N> Williams Plant Services.
391026 | CR | 20190314 |  | 4 | No 80% In Progress Review documented on RWP 30004179. |  |  |  | N | NO | <D> **** Detailed Description **** During the docuemntation of the Post Job Review for RWP 30004179 the 80% In Progress Review that is required as per PPM 11.2.2.14 Step 4.2.2 was not found. <I> **** Actions Taken **** Notified Radiological Support Supervisor and documented this CR.
391028 | CR | 20190314 |  | 3 | New fuel receipt/new fuel channeling observation |  |  |  | N | NO | <D> **** Detailed Description **** Recommend evaluating the winch/rigging device used for installing channeling on new fuel. The set up includes a winch, climbing rope, and pulleys. The climbing ropes outer protective sheath had minor fraying. There was tape being used on the rope designating a stop point for the winch operator. The tape could come free due to going through pulleys and become FME on the refuel floor. Recommend evaluating improved tooling (rigging set up) for the personnel channeling new fuel. <I> **** Actions Taken **** Discussed with maintenance, reactor engineering, and initiated CR . <N> The RFF Supervisor inspected the rope referenced. The area noted as "Frayed" is a section that breaks over a sheave and is as expected. The rope installed on the winch is Samson Amesteel II Plus core dependent double braid synthetic rope with a minimum strength of 10,400 lbs. This rope was installed on 2/7/19, prior to the NFR campaign. The most weight the winch picks up is 75 lbs. The black electrical tape was placed in a specific location to ensure the hook is only pulled up to the lower rafter. Please reference CE-02-02-15 for Calculation details. The Channel Handling Rig is considered plant equipment and any changes will have to be evaluated. The rigging rope will be replaced prior to NFR in 2021.
391029 | CR | 20190314 |  | 3 | Incorrect COND Valve Name/Descriptions in Portal J |  |  |  | N | NO | <D> **** Detailed Description **** COND-V-403 the Name in Portal J reads â€œ2 IN. Gate valve cond return from hydrogen injector.â€ Should read â€œ2 IN. Gate valve COND supply to the hydrogen injectorâ€ COND-V-405 the Name in Portal J reads â€œ2 IN. Gate valve COND supply to the hydrogen injector.â€ Should read â€œ2 IN. Gate valve COND return from the hydrogen injector." These incorrect valve names/descriptions were found in the following procedures and need to be corrected, PPM 5.5.3, SOP-COND-SHUTDOWN, SOP-HWC-START, SOP-COND-FILL. <I> **** Actions Taken **** Informed Supervision . Portal J COND-V-403 and COND-V-405 Name description has been changed as stated in this AR on 03/18/19 by the Engineering Data Steward (EDS).
391030 | CR | 20190314 | CAQ | D | FP-HS-RWB14 nozzle has degraded insulation on handle | N | Y |  | N | YES | <D> **** Detailed Description **** The E-Rated nozzle inside FP-HS-RWB14 needs to be replaced. The rubber insulation on the pistol grip handle is cracked and degraded, due to age and a sturdy amount of simulated use (drills). The nozzle is still functional, but should be replaced at our next earliest convienence. This AR generated to track replacement of the nozzle. This hose box is located in the RW building Stairwell, immediately outside the RW 487 cable spreading room enterance. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RW building stairwell (adjacent to elevator), 487 elevation | 02-00-FP-HS-RWB14
391031 | CR | 20190314 |  | 4 | VENDOR/CONTRACTOR ONSITE USING E-CIGARETTE/VAPE PEN |  |  |  | N | NO | <D> **** Detailed Description **** VENDOR /CONTRACTOR WAS SEEN WALKING UP TO THE FRONT DOOR OF THE DESCHUTES BUILIDNG AND WAS USING A E-CIGARETTE/VAPE PEN PRIOR TO ENTERING THE BUILDING. <I> **** Actions Taken **** VENDOR/CONTRACTOR WAS COACHED ON ENERGY NORTHWEST GBP REGARDING THE USE OF E-CIGARETTE/VAPE PEN. THESE ARE ONLY TO BE USED IN DESIGNATED TOBACCO USE AREAS. MY SUPERVISION WAS THEN INFORMED . WITH THE UPCOMING OUTAGE AN ADDITION TO IN PROCESSING AND THE VISITOR SECURITY FORM MAY BE NEEDED TO EDUCATE/INFORM TECHNICAL REPRESENTATIVES, CONTRACTORS AND VENDORS THAT ARE NEW TO THE SITE OF OUR POLICY REGARDING THE USE OF E-CIGARETTES/VAPE PENS.
391033 | CR | 20190314 | CAQ | D | Door T-107 missing floor plate | N | N |  | N | YES | <D> **** Detailed Description **** Working 15.3.17 Door T-107 is missing metal floor plate , allowing the bottom bolt to drop into a 1/2 hole in the concrete. not securing the at the bottom. needs to have another installed <N> **** Equipment Description **** T441 seal oil room | 02-00-T-DOOR-T107
391035 | CR | 20190314 | CAQ | D | Fire Doors Not meet criteria 15.3.17 | N | N |  | N | YES | <C> CR reopened to cross reference additional WR 29148994, then taken back to complete <D> **** Detailed Description **** working 15.3.17 found C-203 Door closure arm needs to be replaced D-103 Door has a rip in metal near strike. | 02-00-D-DOOR-D103,02-00-W-DOOR-C203
391036 | CR | 20190314 |  | 3 | Administrative/Enhancement update for CGSâ€™s MSRV related Cat |  |  |  | N | NO | <D> **** Detailed Description **** Detail description: In response to Purchasing requests AR 382525 and AR 382510 while reviewing the MSRV drawings provided by the OEM Emerson (formerly Crosby) it was discovered that the Cat. IDs for the requested parts referenced the valve assembly number N63790 instead of the more specific number N63790-3. CGSâ€™s MSRV specific assembly number N63790-3 is reflected on the drawing DS-A-63790-3, Rev. 5 (CVI DWG 932-00,1,1). Action: Procurement Engineering to search for MSRV CIDs based on the current BOMs in Asset Suite. Identify those CIDs that reference the less specific valve assembly number and/or drawing number. Uncheck the "approved for reorder" flag and enter a "C" note indicating that re-review is required prior to next procurement to update the assembly number and/or drawing number. This condition is an administrative issue and not an equipment issue which does not affect the CGSâ€™ SSC. There is no concern regarding parts previously ordered, received, or installed. This is considered an enhancement to support the current OEM, Emerson. Recommend Severity level â€œ3â€ to Procurement Engineering for resolution. <I> **** Actions Taken **** Discussed the condition with System, Procurement and Design Engineering and initiated this CR.
391037 | CR | 20190314 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #31972 King Temp. Calibrator- model 3605 found OOT & Needs Adjustment. Not used during Calibration cycle. DEF #6970A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391038 | CR | 20190314 | CAQ | D | CIA-PRV-14B leaking at pressure indicator gauge | Y | N |  | N | YES | <C> CR reopened to cross reference additional WR 29149303 and marked completion required box, then taken back to complete <D> **** Detailed Description **** CIA-PRV-14B leaking at pressure indicator gauge, observable with Snoop. Recommend replace with new style pressure regulator, or fix pressure gauge connection to stop leakage. <I> **** Actions Taken **** Informed MCR, generated AR/WR. | 02-00-CIA-PRV-14B
391041 | CR | 20190314 |  | 4 | B68 - Truck Parked Inside Building Not Allowed |  |  |  | N | NO | <D> **** Detailed Description **** Fire Protection inspection of APEL building high bay area found a truck parked in the building. This is not allowed in the Business Occupancy per the Fire Code. While it is acceptable to load and unload vehicles under continuous watch, the vehicle must be parked outside when not attended. Discussion with the Facility Dept. Supervisor indicates this vehicle has been parked in the high bay for several days and nights. This is a fire risk and a Building Code/ Fire Code violation. . The Facility Supervisory made a commitment to remove the truck prior to the end of the business day, today. <I> Not a CGS condition. <N> Truck was removed before COB 3/14/19.
391044 | CR | 20190314 |  | 4 | Spare circuit breaker open times out of tolerance |  |  |  | N | YES | <D> **** Detailed Description **** While performing the pre-installation inspection of a spare breaker (UTC 543239), the open times were found to be out of tolerance. The open time range is 35 to 50 milli -seconds. The recorded open times range between 34.0 to 34.4 milli-seconds. The breaker contacts need to be adjusted to bring the open times into tolerance. This is a spare breaker that is to be installed during R24. <N> **** Equipment Description **** Circuit Breaker CID 19531, UTC 543239, staged in Bldg 11
391046 | CR | 20190314 |  | 4 | AMS-3 recorders replaced | N | N |  | N | YES | <D> **** Detailed Description **** while performing w/o # 02126949-01 with ppm 10.24.167 for hp-eq-34119 and hp-eq-c020698 both recorders required being replaced. Both then were calibrated to within tolerances. <I> **** Actions Taken **** notified supervisor wrote this cr <N> **** Equipment Description **** 487 radwaste hp cage area | 02-00-HP-EQ-34119
391049 | CR | 20190314 |  | 4 | E-RLY-51/3/2/A As found times out of tolerance | N | N |  | N | YES | <D> **** Detailed Description **** During calibration of E-RLY-51/3/2/A per PPM 10.25.20 (WO#02104169-01) the As found Time/Current checks were out of tolerance. Check 1 was 2.85 seconds with a data sheet tolerance of 2.55 to 2.82 seconds. Check 2 was 12.75 seconds with a data sheet tolerance of 10.92 to 12.08 seconds. All other data Sat. <I> **** Actions Taken **** Notified supervisor and PSRO. Cleaned and adjusted relay per PPM 10.25.20. All As left data in tolerance and relay tested Sat. | 02-00-E-RLY-51/3/2/A
391050 | CR | 20190314 |  | 4 | Reactor 422' RCIC Room Poor Lighting |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Reactor 422' RCIC Room Poor Lighting. <I> **** Actions Taken **** Notified HP Lead Notified HP Supervisor CR / WR ESOMS Log Entry <N> **** Equipment Description **** RX422' RCIC Room
391053 | CR | 20190314 |  | 4 | REA ductwork is a dose source in upper Kelly building |  |  |  | N | NO | <D> **** Detailed Description **** The REA ductwork which runs through the upper level of the Kelly buidling on 6060 Rx is creating dose rates as high as 1 mrem/hr in the space. Cleaning of this ductwork would be expected to cut the dose for personnel in the area by a factor of 1/3 to 1/2. There are three access panels in the ductwork that could be used for the duct cleaning. <I> **** Actions Taken **** Wrote CR and work request. <N> **** Equipment Description **** WEA ductwork in upper Kelly building.
391055 | CR | 20190314 |  | 4 | Leak from RFW-V-111A degrading trend. | N | N |  | N | YES | <D> **** Detailed Description **** The leak from RFW-V-111A is degrading as evidenced from viewing cameras TG #17 and #21. Leak has been monitored throughout the week and has appeared "steady", however today the leak is bigger as seen on both cameras. If the TMR installed cap were to fail, the leak should then also be visible on camera TG #12. Reference AR/CR 390617 and 390813. <I> **** Actions Taken **** Informed Engineering, SM, FLM, FIN, and outage management. | 02-00-RFW-V-111A
391056 | CR | 20190314 | CAQ | D | CRD HCU Accumulator alarm trends for Cycle 25 repairs | Y | N |  | N | YES | <D> **** Detailed Description **** The following CRD HCU accumulators have multiple water alarms and should have WOs generated for online scheduling of their accumulators in Cycle 25. The accumulators have not yet reached the threshold for requiring repair but will be planned in advance to allow for scheduling with future downpowers. The accumulators alarm once every several months and are expected to continue to degrade. It is desirable to plan now for replacement rather than after leakage drives a required replacement. Generate WOs for online replacement. CRD-HCU-2603, CRD-HCU-5819, CRD-HCU -2203, CRD-HCU-4207 | 02-00-CRD-HCU-2203,02-00-CRD-HCU-2603,02-00-CRD-HCU-4207,02-00-CRD-HCU-5819
391057 | CR | 20190314 |  | 4 | E-CB-51/5M CONTACT RESISTANCE TEST |  |  |  | N | NO | <D> **** Detailed Description **** WHILE PERFORMING 10.25.2 STEP 7.1.24 CONTACT RESISTANCE TEST THE ACCEPTANCE CRITERIA WAS EXCEEDED. <I> **** Actions Taken **** CONTACTED SUPERVISOR AND ENGINEERING. REMOVED 3 MAIN CONTACTS FROM STORED BREAKER SN24Y9349B-1 AND INSTALLED IN E-CB-51/5M AND TORQUED TO 18 INCH LBS. RE-PERFORMED STEP 7.1.24 AND ALL CRITERIA SATISFACTORY AT LESS THAN 100 MICRO OHMS. BREAKER INSPECTION IS COMPLETE AND ALL SATISFACTORY. <N> Line side pole assemblies were replaced under the existing WO with resulting resistance readings satisfactory. 51/5M breaker placed back into service. No further actions required. Recommend track and trend only.
391058 | CR | 20190314 | CAQ | C | TASM exceeded 90 days |  |  |  | N | NO | <D> **** Detailed Description **** A TASM was implemented to provide additional cooling for work supporting MT-CRA-1 modification. WOT 02114492-21 Implemented the TASM on 12/6/18. This TASM exceeded the 90 day limit for requiring a 10 CFR 50.59 screen per SWP-CM -02. WOT 02114492-22 performs restoration. Restoration is in progress and penetrations are capped. <I> **** Actions Taken **** Notified Engineering | 02-00-T-BLDG-MISC
391059 | CR | 20190314 |  | 4 | RWCU Hx Replacement Steering Committee Quorum Not Met |  |  |  | N | NO | <D> **** Detailed Description **** Steering Committee Quorum not met. The required number of committee members to meet the RWCU Hx Replacement Steering Committee Project Charter as established by GBP-ERM-05, Special Project Steering Committees was not able to be met due to quorum member having multiple competing priorities. <I> **** Actions Taken **** Discussed with Supervision and wrote this CR to document not meeting the requirements of the project charter for a steering committee meeting.
391060 | CR | 20190314 |  | 3 | OSP-RCIC/IST-Q701 procedure enhancment |  |  |  | N | NO | <D> **** Detailed Description **** OSP-RCIC/IST-Q701 requires documentation of Cold Quick Restart on the M301 page of portal J. This is still possible but would be easier if it was documented as a closure comment in the review section of DataGlance, this would better align with out transition to DataGlance as the controling program. <I> **** Actions Taken **** wrote CR
391061 | CR | 20190314 |  | 3 | SOP-FPC-SPC needs some better reference. |  |  |  | N | NO | <D> **** Detailed Description **** When Placing the FPC demin on the Suppresion pool per SOP -FPC-SPC section 5.1.13 you line up and start FPC-P-3 which will be your driving force of water thru the demins from the suppresion pool. Then SOP-FPC-SPC tells you to put the demin back on line using SOP-FPC-Demin which is assuming your driving force is the FPC pumps. It references ensuring only one FPC running, only going to 575 gallons if one FPC pump is running. The suppresion pool filtering loop doesnt care how many pumps are running it cares about FPC-P-3. please include in this new section we need what the final flow should be thru the demin. <I> **** Actions Taken **** very thourough brief was held, this topic was adressed
391062 | CR | 20190314 | CAQ | C | CC-179 Tamper Seals Missing from M&TE |  |  |  | N | I DONT KNOW | <A> I have reveiwed and approved of the actions taken and the closure notes that document the actions. <D> **** Detailed Description **** During ENSL's AU-CL-19 audit it was noted that M&TE was missing tamper resistant seals and while some were remedied immediately an initial extent of condition shows that a recall of suspect M&TE is prudent. Determination of specific equipment models identified by QA will be included but it would be wise to instruct Tool Crib attendant to look for any additional M&TE that is a potential candidate for tamper seals. Recommend Assign to AR-CALSERV <I> **** Actions Taken **** Initiated customer complaint CC-179 and this CR, contacted maintenance supervisor.
391063 | CR | 20190314 |  | 4 | Loose decking under grading on the South side of the CWPH. | N | N |  | N | NO | <D> **** Detailed Description **** Near FP-V-80B on the south walkway which is over the circwater basins there is a section of decking that is loose underneath the grading and needs repair. The walkway is secure and safe for use but needs to be addressed so the issue doesnâ€™t get worse. See pictures in EDMS. <I> **** Actions Taken **** Initiated CR and reported to safety. <N> **** Equipment Description **** Walkway on the South side of the CWPH.
391064 | CR | 20190314 |  | 4 | Unknown isolation leaking into common drain hdr on FPC-IR-1 | N | N |  | N | YES | <D> **** Detailed Description **** Unknown isolation leaking into common drain hdr on FPC-IR -1. drain is leaking from 1 drop a second to 1 drop every 2 seconds. there is a addition flow out of the common drain header to the inside of the instrument rack previously identified with WR 29129827. This CR/WR is only to identify the leaking isolation and repair replace as necessary that is currentlyleaking into the common drain header. <I> **** Actions Taken **** wr/cr Equipment on FPC-IR-1 is associated with FPC-DM-1A and FPC -DM-1B. | 02-00-FPC-IR-1
391065 | CR | 20190314 |  | 4 | CW Chemical Feed Pumps not pumping | N | N |  | N | YES | <D> **** Detailed Description **** Currently running CF-P-41 B (new pump) at 95/95, CF-P-42A (new pump) at 95/95, plus manually feeding 50 gals per day. Both 41B and 42A are not pumping according to tank draw down trending. Relying now on the last means, manual addition, of adding chemical dispersant to the CW/TSW system for scale protection of the main condenser. Manual chemical additions have kept the residuals within target range. <I> **** Actions Taken **** Need to clear the check valves on the two pumps so that they will start pumping again. When clearing the check valve, obtain samples of the material interfering with the pump and provide it to Chemistry for evaluation. Manual addition rate has been increase to compensate for the pumps not pumping. <N> **** Equipment Description **** CF-P-41B and CF-P-42A
391066 | CR | 20190314 |  | 4 | ZINC-TK-1, basket o-ring found inside basket | N | N |  | N | YES | <D> **** Detailed Description **** During the internal inspection of the basket when the elbow was removed. It was noticed, that possible oring material was inside. NDE was contacted and a boroscope was used and verified that the basket to head oring was broken and protruding from its groove. Pieces of this o-ring are inside of the basket and will require removal as planned. <I> **** Actions Taken **** Notified work week and FIN managers. Head removal is in progress to remove the basket. | 02-00-ZINC-TK-1
391067 | CR | 20190314 |  | 4 | MT-ELEV-2 (SW RB) door is not opening. | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-2 door to the reactor building sticking and will not open. Was tried on multiple floors. <I> **** Actions Taken **** Removed elevator from service until problem is addressed. | 02-00-MT-ELEV-2
391068 | CR | 20190315 |  | 3 | Pro Locator Portable Fire Detection System Battery Dead |  |  |  | N | NO | <D> **** Detailed Description **** The Pro Locator Portable Fire Detection System in the RWCR was found with a dead battery. I recharged the battery. I don't know of a program in place to check/recharge the battery on this piece of equipment. There needs to be one created by the Fire Protection Department. <I> **** Actions Taken **** Wrote this CR and contacted the Main Control Room
391076 | CR | 20190315 |  | 3 | (QA) SLI-2-30 & TPD-23 Do Not Align With Qual. Directory |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) SLI-2-30 and TPD-23 do not align with Qualification Directory 2.18, Standards Laboratory, for the courses assigned to qualification groups. This caused no unqualified workers because the Qualification Directory (QD) 2.18 has more training courses specified so is conservative to the scope specified in QM-1 implementing procedures mitigating the risk of unqualified workers. Factual Basis: â€¢ QM-1, Quality Manual, Revision 11, section 6.1 states â€œEnergy Northwest Standards Laboratory personnel who perform, verify, or manage activities affecting quality are qualified for those activities by education, previous experience, and/or training. See SLI 2-30, Training and Qualification.â€ â€¢ SLI 2-30, Training and Qualification, Revision 8.1 Attachment 2 is different than QD, as follows: o States SL000002 is listed for all SLA series qualification groups, QD 2.18 does not list it in SLAA o States SL000004 is listed for only SLAC qualification group, QD 2.18 has it also in SLAR o States SL000029 is listed only SLAG qualification group, QD 2.18 has it also in SLAF â€¢ TPD-23, Standards Laboratory Training Program, Revision 0, Minor 1, Attachment 6.1 is different than Qualification Directory o States SL000001 is listed for only SLAA qualification group, QD 2.18 has it in all SLA series qualification groups o States SL000004 is listed for only SLAC qualification group, QD 2.18 has it also in SLAR o States SL000029 is listed only SLAG qualification group, QD 2.18 has it also in SLAF Insight: â€¢ Revisions to the Qualification Directory were not reconciled with associated procedures. <I> **** Actions Taken **** Contacted the Manager responsible for ENSL. . This is a Deficiency identified during the Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV.
391077 | CR | 20190315 |  | 3 | (QA) Standards Lab Personnel Not Assigned To Qual. Groups |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Three Individuals not assigned to Qualifications required by QM-1. The affected Qualification Groups SLAA, Basic Metrology, and SLAB, Metrology, are not task specific qualifications. Though the individuals had all the listed courses in the required qualification groups this does not meet the expectations to manage work assignments by applicable qualification groups. Factual Basis: â€¢ QM-1 rev 11 section 6.1 states â€œEnergy Northwest Standards Laboratory personnel who perform, verify, or manage activities affecting quality are qualified for those activities by education, previous experience, and/or training.â€ â€¢ TPD-23 â€œStandards Laboratory Training Programâ€ rev 000 -001, section 3.1.1 states that Standards Laboratory Administrative support personnel and Technicians â€œshall complete the initial Standards Laboratory required reading listed in Qual Group SLAA.â€ â€¢ SWP-TQS-01 â€œTraining, Qualification and Simulatorsâ€ rev 019-002, section 3.2.4.c.2 states that Line managers and supervisors should â€œassign qualification groups to their employees.â€ â€¢ Qualification Directory 2.18, Standards Laboratory, Qualification Group SLAA, Basic Metrology, states the target population is â€œIndividuals who, due to their work assignment, work within a Standards Laboratory.â€ â€¢ Qualification Directory 2.18, Standards Laboratory, Qualification Group SLAB, Metrology, states the target population is â€œTechnicians who work within a Standards Laboratory.â€ â€¢ Two ENSL employees were not assigned to Qualification Group SLAA, Basic Metrology. Verified both individuals have credit for qualification specified course SL000001 in Passport. â€¢ A third employee is a Technician and was not assigned to Qualification Group SLAB, Metrology. Verified individual has credit for qualification specified courses SL000001 and SL000002 in Passport. Insights: â€¢ Training and qualification responsibilities were reassigned to a new individual approximately a year ago, which may have reduced program implementation proficiency, due to insufficient oversight. â€¢ After notification by Quality, all three laboratory employee IDs were added to the respective Qualification Groups listed above and completed the required training. <I> **** Actions Taken **** Contacted the Manager responsible for ENSL. . This is a Deficiency identified during the Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV.
391078 | CR | 20190315 |  | 3 | (QA) Tool Kits for Field Calib's Not Maintained per SLI-2-39 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Only one of the three technicians that performs field calibrations was able to produce a tool kit for performing field calibrations. The tool kit that was produced was contained in two parts with the procedural documentation contained in a metal clipboard and the environmental monitoring equipment stored separately in its own storage case. The potential consequence is that required components of the tool kit may not be taken into the field, if the tool kit is not already assembled and ready for field work. Factual Basis: â€¢ SLI 2-39 step 3.3 states: â€œA Tool Kit for Field Calibrations will be maintained, to include (but not limited to): o A current copy of QM-1 and this SLI (2-39). o Calibration SLI(s) relative to the work being performed will be reviewed prior to commencement of work and as necessary shall be made part of the tool kit for the respective field calibrations. o If required a Job Hazard Analysis (JHA) will be performed prior to commencement of the field calibration. o If manufacturer's operating manuals or other references are needed in the performance of field calibrations, they will be reviewed prior to commencement of work and, as necessary, shall be made part of the tool kit for the respective field calibrations. o Environmental monitoring equipment shall be used to monitor environmental conditions at the time the field calibrations are performed. As a minimum, this will include temperature and relative humidity.â€ â€¢ Tool kits are currently not being maintained with all required items listed above, contrary to SLI 2-39. Insights: â€¢ Interviews with three technicians that perform field calibrations revealed: o One technician provided a checklist of items to bring to a field calibration. They use the checklist when gathering tools and equipment to go on a field calibration. This checklist contains some of the items required by SLI-2-39, but not all of the items. o One technician was able to verbally discuss the requirements for the tool kit. o One technician was able to provide their tool kit as described above. â€¢ The tool kit that was provided had not been purged of job specific documents from a completed field calibration. This could lead to mixing documents from multiple tasks. â€¢ One technician was provided access to company email on their cell phone to allow them to retrieve some of the documents, like vendor manuals, electronically while in the field. <I> **** Actions Taken **** Contacted the Manager responsible for ENSL. . This is a Deficiency identified during the Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV.
391079 | CR | 20190315 |  | 3 | (QA) SLI 2-31 Has Expired A2LA Accreditation â€œValid Toâ€ Date |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Current SLI 2-31 â€œCalibration Capabilitiesâ€ contains an old A2LA â€œScope of Accreditation to ISO/IEC 17025:2005 and ANSI/NCSL Z540-1-1994â€, which shows accreditation expired on 1/31/19. However, this expiration date had been extended on 1/15/19 to expire on 2/28/19; and this later expiration date had been extended again on 2/25/19 to expire on 3/31/19. This is a nonconformance with QM-1 â€œQuality Manualâ€, which requires documents affecting quality to be â€œcontrolledâ€ and â€œcorrectâ€. Requirements: â€¢ QM-1 rev 11 (effective 1/9/19) section 10.2 â€œProcedures/Document Controlâ€ states, â€œENSL utilizes Standards Laboratory Instructions (SLIs) in the performance of calibrations and other work associated with the calibration process.â€ â€¢ QM-1 rev 11 section 10.2a states, â€œThe preparation, review, approval, issuance and change of documents affecting quality are controlled to assure that correct documents are being employed. Such documents, including changes thereto, are reviewed for adequacy and approved for release by ENSL Management prior to use. Approval authority for the laboratory implementing instructions and calibration instructions is vested with ENSL Management . . .â€ â€¢ QM-1 rev 11 section 10.2b states, â€œProcedures / Standards Laboratory Instructions, at a minimum, specify the standards to be used . . . ENSL Management indicates approval and acceptance of these documents for use by a signed cover sheet.â€ Factual Basis: â€¢ SLI 2-31 â€œCalibration Capabilitiesâ€ rev 12.0 (effective 6/12/17) Attachment A contains the outdated â€œA2LA Scope of Accreditation to ISO/IEC 17025:2005 and ANSI/NCSL Z540-1 -1994â€, which was revised on 6/6/17 and is â€œValid Toâ€ 1/31/19. â€¢ SLI 2-31 was not updated to reflect at least two extensions of the A2LA Accreditation â€œValid Toâ€ Date, contrary QM-1, which requires documents affecting quality to be â€œcontrolledâ€ and â€œcorrectâ€. <I> **** Actions Taken **** Contacted the Manager responsible for ENSL. . This is a Deficiency identified during the Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV. <N> Verified changes were made and uploaded into EDMS. Manager approved closure.
391080 | CR | 20190315 |  | 3 | (QA) SLI 2-25 does not fully comply with ISO 17025:2017 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) SLI 2-25 â€œCustomer Relationsâ€ rev 11.2 does not state when to notify customers of an identified nonconformance or when to recall nonconforming work, contrary to ISO 17025: 2017 section 7.10.1e. Actual consequences are customers were not notified that calibration certificates issued to customers between 1/10/19 and 1/22/19 show the incorrect QM-1 â€œQuality Manualâ€ revision. Requirement: â€¢ ISO 17025:2017 section 7.10.1 states that â€œthe laboratory shall have a procedure that shall be implemented when any aspects of its laboratory activities or results of this work do not conform to its own procedures or the agreed requirements of the customer â€¦ the procedure shall ensure that (e) where necessary, the customer is notified and work is recalled.â€ Factual Basis: â€¢ ENSL became committed to ISO 17025:2017 when QM-1 revision 11 was issued on January 10, 2019. â€¢ On January 22, 2019, ENSL took action to update the calibration certificate code to refer to QM-1 revision 11. â€¢ On January 30, 2019, a customer identified that a calibration certificate for a calibration performed on January 15 incorrected referred to QM-1 revision 10 instead of revision 11. â€¢ ENSL took action to issue an amended calibration certificate to the customer initiating the complaint. â€¢ All calibration certificates issued between January 10 and January 22 refer to the incorrect revision of QM-1. These certificates were not recalled by ENSL. â€¢ ENSL personnel indicated that calibration certificates are re-issued at the request of the customer; however, the customers of the affected documents were not contacted to notify them of the oversight. â€¢ SLI 2-25 revision 11.2 does not contain guidance on notifying customers of nonconformances or when to recall previously issued certificates. Insights: â€¢ This is a legacy issue because ISO 17025:2005 section 4.9.1 contains equivalent requirements to those requirements cited above from ISO 17025:2017 section 7.10.1. â€¢ Nonconformances identified by A2LA, NQA-1, Quality Assurances, or other auditors should be evaluated to determine the population of customers that they potentially impact. These customers should be notified of these issues to determine if the gaps challenge their own procedures or quality programs. Additionally, generic issues identified by customers through the customer complaint process should be treated the same way. <I> **** Actions Taken **** Contacted the Manager responsible for ENSL. . This is a Deficiency identified during the Quality Audit AU-CL-19. . Recommend routing to AR-CALSERV.
391082 | CR | 20190315 |  | 3 | (QA) GBP-EBS-02 Step Points to Historical GBP-AM-01 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) GBP-EBS-02 â€œInter-Organizational Supportâ€ step 3.1.3 points to GBP-AM-01 â€œCost /Benefit Analysisâ€, which was taken to â€œHistoryâ€ status in 2017. Citing a procedure that no longer exists could create confusion when generating new Inter-Organizational Agreements. Factual Basis: â€¢ GBP-EBS-02, Revision 2, Minor 1, section 3.1.3 states, â€œEnsure a CBA is prepared if required in accordance with GBP-AM-01, Cost/Benefit Analysis.â€ â€¢ GBP-AM-01, Revision 1 in Asset Suite documents this procedure being taken to history on 4/3/17. <I> **** Actions Taken **** Contacted the Contracting Officer and acting Manager responsible for ESD. . This is a Deficiency identified during the Quality Audit AU-CL-19. . Recommend routing to AR-VPESD. <N> Modified procedure GBP-EBS-02 and removed reference to procedure GBP-AM-01 in step 3.1.3. Consulted with Nancy Weston and she indicated that editorila change could be used. Used the Automated Procedure process to modify and approve the procedure. Set the implementation date to 4/12/19.
391083 | CR | 20190315 |  | 3 | PAAP-Voicertr-01 hardware failure |  |  |  | N | YES | <D> **** Detailed Description **** The PAAP-Voicertr-01 that supports 1 circuit has failed. This device is part of a redundant system and has little to no impact on normal operations. <I> **** Actions Taken **** Troubleshooting for this device has been conducted and it was determined that the equipment suffered a failure. A backup gateway is currently in place for cold standby and will be configured and put into service. <N> **** Equipment Description **** PAAP rm 10 rack 3
391084 | CR | 20190315 |  | 4 | N1/3 Factory refurbished breaker missing fastener |  |  |  | N | NO | <D> **** Detailed Description **** During circuit breaker inspection, a seismic latch assembly came apart due to a missing e-ring. The breaker being inspected is a spare that is to be put in service during the week of March 25th. The inspection was scheduled to complete the week of March 11th with a C adherence and now will slide into next week due to the e-ring not being available in stores. <I> **** Actions Taken **** CID 38704 created, and MR submitted to obtain new e-ring. Notifed WWM. . This is a spare breaker being refurbished for in-plant use. <N> **** Equipment Description **** W487 breaker shop
391085 | CR | 20190315 |  | 3 | (Non EN/CGS) CC-180 Calibration not Performed per PO Request |  |  |  | N | NO | <D> **** Detailed Description **** Customer (Non EN/CGS) notified ENSL Supervisor that ENSL provided calibration of two pressure gauges that did not use the accuracy of the referenced ASME B4 .100 Grade A or the pressure range as was requested on PO. <I> **** Actions Taken **** Initiated this CR. Notified customer that ENSL could either re-calibrate their pressure gauges as was originally requested or utilize the data obtained from the original calibrations to provide calibration reports using the accuracies and pressure range requested. Initiated Customer Complaint 180 and this CR. Notified customer ENSL would either re-calibrate their pressure gauges or utilize the data from the original calibrations to provide calibration reports as was requested on the PO. <N> Customer complaint CC-180 has been completed and close.
391086 | CR | 20190315 |  | 3 | WO 02130424 Task 05 and 06 problem in portal J |  |  |  | N | NO | <D> **** Detailed Description **** When you press the F9 key for WO 02130424 Task 05 and 06 you get the following error message "Your transaction was unable to complete processing due to an application program failure. If problem persists, report this to your application support group" <N> Pressed F9 in task status field and received an error. Closeout Notes: User released the hold from DataGlance and when went back to view in Asset Suite the error was corrected. . Was not able to recreate the problem or figure out if it was a duplicate gen-arg issue. . Recommend closing CR and Trend.
391087 | CR | 20190315 |  | 3 | WO 02138304 Task 02 and 03 problem |  |  |  | N | NO | <D> **** Detailed Description **** When you F9 on the status of WO 02138304 Task 02 and 03 you get the following error message "Your transaction was unable to complete processing due to an application program failure. If problem persists, report this to your application support group. <N> User released the hold from DataGlance and when went back to view in Asset Suite the error was corrected. . Was not able to recreate the problem or figure out if it was a duplicate gen-arg issue. . Recommend closing CR and Trend.
391088 | CR | 20190315 | CAQ | C | PM could not be performed as written |  |  |  | N | NO | <D> **** Detailed Description **** WO 02132295-01 LPCS-P-1 Spare Pump Maintenance could not be performed as written. Step 4.6 to check desiccant and humidity indicator could not be performed due to the position of the pump. It is currently positioned with the discharge flange down, on plywood supporting the pump. Both the top of the pump and suction ends were accessible and were able to be inspected, and have desiccant and humidity indicators installed. The top and end were re-wrapped per work instructions. The pump will have to be rolled and put on cribbing if the discharge is to be accessible. <I> **** Actions Taken **** Following SWP-PRO-01 CR/WR generated, will get System Engineering Manager concurrence prior to taking task to Finished. Attached snip of SWP-PRO-01 to EDMS <N> **** Equipment Description **** Spare LPCS Pump PM
391089 | CR | 20190315 |  | 3 | Portal J/Data Glance WOâ€™s missing FMR holds |  |  |  | N | NO | <D> **** Detailed Description **** While performing close out reviews on WO tasks found FMR holds missing on the following WOâ€™s 02130420-01, 02130927 -01, 02131252-01, 02131474-01, 02131486-01, and 02131487 -01. The model WOâ€™s for these tasks have FMR holds. The history and look ahead task are also missing FMR holds. The tasks already sent to records of the PMIDâ€™s of the WOâ€™s listed are missing FMR signatures. Not knowing the scope of the issue I spot checked some FP PMâ€™s and found, WOâ€™s 02137404-01 and 02137623-01 have the same issue. A data mod was run March/April of 2018 and put FMR holds on the model WOâ€™s, but the FMR hold is not transferring to the WOâ€™s being tasked from the PMIDâ€™s.Need to correct this issue so WOâ€™s do not get closed and go to records missing FMR signatures. Also need to get a list of WOâ€™s since the FMR data mod and validate and get the FMR signatures required. WOâ€™s of the PMIDâ€™s (WOâ€™s) listed have missing FMR signatures. For additional details please contact Engel Knibbe. <I> **** Actions Taken **** Put FMR routing hold for WOâ€™s 02130420-01, 02130927-01, 02131252-01, 02131474-01, 02131486-01, and 02131487-01. Also put FMR holds on the look ahead WOâ€™s for PMID 213836 -02. Still need to correct the FMR hold transfer from model to task issue for PMID 21383-02 <N> When the Asset Suite backgrounds a WO it will only background hold codes SRO, RO & WD. Will add assignments to Evaluate and make code changes to the WO backgrounding programs to include additional Hold Codes. . Moving due date out 1 month to accomidate additional changes to the code in the WOBAK program.
391090 | CR | 20190315 |  | 4 | Aux Boiler failed to fire during monthly operability run | N | N |  | N | YES | <D> **** Detailed Description **** Aux Boiler failed to fire during monthly operability run. Cause of the trip was "LOW ATOMIZING AIR PRESSURE". Alarm response procedures for the condition were followed A subsequent reset and re-fire was also unsuccessfull. Mechanical support was provided and will be looking into the proper operation of AS-PS-8 and other associated solenoid valves. Video of the failed fireing sequence was recorded and is attached. <I> **** Actions Taken **** Contacted CRS. Initiated CR. . Same thing happened 6/17/17, CR 367913. WO 02127857 is at APPROVED. | 02-00-AS-BLR-1
391091 | CR | 20190315 |  | 4 | RWCU High level alarm | N | N |  | N | YES | <D> **** Detailed Description **** RWCU precoat tank level high alarm came in at approximately 1635 on 3/15/19. Upon investigation the tank did not appear full (about 12" down from the lid) nor was there any water movement in the tank indicating in-leakage. Per the ARP tank level was lowered using CF-V-646 and the alarm cleared. No evolution or changes had been made to RWCU sys all shift. Possible level instrument issue. <I> **** Actions Taken **** MCR informed, | 02-00-RWCU-LS-75
391095 | CR | 20190316 | CAQ | D | Lights on Manual pull station and Hose reel burned out. | N | Y |  | N | YES | <D> **** Detailed Description **** Found lights (normally on) at Hose reel FP-HS-CO2/1 & FP -PS-CO2/1 burned out. <I> **** Actions Taken **** Informed SSS & MCR. | 02-00-FP-HS-CO2/1,02-00-FP-PS-CO2/1
391096 | CR | 20190316 |  | 4 | TSW-F-1B Motor Not Rotating |  |  |  | N | YES | <D> **** Detailed Description **** The motor on TSW-F-1B is not rotating. This maybe related to CR 390924 (Damaged Light Socket on TSW-CP-F/1B) if the damaged socket resulted in a blown fuse. The d/P across that filter is trending up. Recommend investigation and repair and working this issue with WR 29147534 <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** CWPH | 02-00-TSW-F-1B
391097 | CR | 20190316 |  | 4 | Fuse 8-5 in E-TR-N1 Taped to Panel |  |  |  | N | YES | <D> **** Detailed Description **** Inside the control cabinet for E-TR-N1 Fuse 8-5 has been removed and taped to the back of the panel. This is a poor electrical safety practice as it could fall and short out other components in the cabinet. Operations removed this fuse and placed it in a plastic bag and left inside the cabinet. This fuse has been disconnected from the system as seen in CVI DWG 45-00,86. See EDMS for as found condition. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** E-TR-N1 Control Panel | 02-00-E-TR-N1
391098 | CR | 20190316 |  | 4 | E-RLY-83/TRN1 DID NOT ALARM WHEN ON EMERGENCY POWER |  |  |  | N | YES | <D> **** Detailed Description **** When performing model work order #01172150 task #01, the 83E alarm was not received and the local amber alarm light did not illuminated during Step 4.5.2. The Control Room did not receive the alarm for XFMR TR-N1 Trouble as required for Step 4.6.1. The power transfer switch sounds and appears to be working as it should, it is just the alarms are not coming in as they should. It is suspected that the Aux contacts on E-RLY-83/TRN1 are failing this CR is for trending only as this issue is being tracked per WO 02126139. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** E-TR-N1 Control Panel | 02-00-E-RLY-83/TRN1
391099 | CR | 20190316 |  | 3 | OPDS-ANN-B2/5F E-TR-B Open Phase Alarms |  |  |  | N | YES | <D> **** Detailed Description **** Three new alarms on OPDS-ANN-B2/5F in the TR-B Open phase building have been in since the TR-B Outage on 3-1-2019. â€œSET 1 LOSS OF POT 1â€; â€œSET 2 LOSS OF POT 2â€; and â€œLOSS OF INST POTâ€ are still in. Alarm Response Procedure is required to understand and reset these alarms by operations. Also Both OPDS-METER-B3/5L and OPDS-METER-B4/5L are now reading â€œrcdâ€ for Watt hours on phase A and â€œPOSâ€ for VAR hours on phase A. See Attached Photos. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** Building 44 TR-B Open Phase Building | 02-00-OPDS-ANN-B2/5F
391100 | CR | 20190316 |  | 3 | 4.602.A5.6-8 enhancements |  |  |  | N | NO | <D> **** Detailed Description **** In order to prevent lifting RWCU-RV-3 with seal purge while the RWCU system is isolated, Step 8 needs a step to throttle open RWCU-V-104.
391101 | CR | 20190316 |  | 4 | CW-CT-2C Water Level High |  |  |  | N | YES | <D> **** Detailed Description **** CW-CT-2C level is at 13" which is High and the tower likely requires cleaning <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** CW-CT-2C | 02-00-CW-CT-2C
391102 | CR | 20190316 |  | 4 | Hydraulic Line Break |  |  |  | N | NO | <D> **** Detailed Description **** During snow removal activities near Building 183, a hydraulic line on a front loader broke, spraying oil to the ground. The spill was contained to concrete and immediately cleaned up. Less than 1 gallon of oil spilled to the ground. <I> **** Actions Taken **** Notified E&RP Manager, F&CE Manager, and wrote CR. Reviewed GBP-ENV-18 and determined spill is not reportable.
391103 | CR | 20190316 |  | 3 | Dataglance interface failure after upgrade to 8.4 | N | N |  | N | NO | <D> **** Detailed Description **** At the conclusion of the upgrade to Dataglance v8.4, the interfaces to eSOMS failed to work, although they were functioning correctly prior to releasing control to the users. <I> **** Actions Taken **** Upon investigation, it was determined that a component in a config file residing on the database server was altered during the creation of the standby database, which disabled the database link. The item was corrected and connection was restored.
391104 | CR | 20190316 | CAQ | D | E-BU-SWA5/9 lighting unit charger fault | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-SWA5/9 has a red light blinking in sets of 3. According the the label on the unit, 3 blinks means a charger fault is present. <I> **** Actions Taken **** Informed CRS. | 02-00-E-BU-SWA5/9
391105 | CR | 20190316 |  | 4 | ROA-TIS-6 controller sticking | N | N |  | N | YES | <D> **** Detailed Description **** ROA-TIS-6 controls ROA-V-21. When inlet air temp gets below the setpoint, V-21 opens to admit steam to ROA's heating coils. ROA-TIS-6 was found indicating temp to be ~45 F while the setpoint was at 55 F and the heating steam valve (V-21) was still closed, when it should have been open. The controller setpoint was adjusted up/down and back to the original value. Upon doing this it triggered V-21 to go open as it should have been (via indicating lights). This CR is for trending a degraded controller. | 02-00-ROA-TIS-6
391106 | CR | 20190316 |  | 4 | TSW-TI-10ag high OOS | N | N |  | N | YES | <D> **** Detailed Description **** TSW-TI-10AG, Generator H2 cooler return temp, is at 122F. The OPS 3 rounds indicate the high spec is 120F. TSW-TCV-9 indicates about 1/3 open. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-TSW-TI-10AG
391107 | CR | 20190316 |  | 4 | COND-TI-27A high OOS | N | N |  | N | YES | <D> **** Detailed Description **** COND-TI-27A, RFT A outboard seal water temp, indicates 340F. The OPS 3 rounds have the high spec at 325F. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-COND-TI-27A
391110 | CR | 20190317 |  | 3 | eWP and Portal J not communicating status of WO's |  |  |  | N | YES | <D> **** Detailed Description **** Following upgrade of the Electronic work package system (eWP), WO's that were completed in eWP did not change status in portal J as required. <I> **** Actions Taken **** IS duty officer will be contacted for resolution. <N> **** Equipment Description **** Electronic Work Package system . Upon investigation and consultation with the DataGlance vendor, it was determined that an application configuration file had not been updated to reference the correct TCP/IP port number as part of the application upgrade on 3/16/2019. Successfully tested an updated configuration file in the Development and QA environments. Updated the file in the Production environment. Restarted the application. Work order task status changes were then getting passed between the DataGlance and Asset Suite applications. This issue is not related to the issue documented in CR 00391103.
391111 | CR | 20190317 | CAQ | D | E-BU-SWA4/2 Emergency Light System Failure | N | N |  | N | YES | <D> **** Detailed Description **** The charging status light is flashing which indicates an emergency system failure and the Lightning bolt light is constantly on indicating low battery capacity. This emergency light is located in the TB 471â€™ NW stairwell. Investigate and repair. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** TB 471' NW Stairwell | 02-00-E-BU-SWA4/2
391112 | CR | 20190317 |  | 4 | E-TR-85/82 Oil Drain Valve Packing Leak | N | N |  | N | YES | <D> **** Detailed Description **** There is a small oil leak from the packing of the oil drain on E-TR-85/82. There is a small puddle of oil underneath the valve and inside the oil berm surrounding the transformer. See EDMS for Photos. Recommend packing adjustment. The oil was wiped up and oil pads placed underneath. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** TB 441 inside Aux Boiler room | 02-00-E-TR-85/82
391113 | CR | 20190317 | CAQ | D | Rx chloride above SWP-CHE-02 good practice | Y | Y |  | N | NO | <D> **** Detailed Description **** On 3/16/19 at 0138 an SP-1 anion sample was analyzed at 1.11 ppb, SWP-CHE-02 good practice value per table 6.1.13 for reactor water chlorides is LE1 ppb. Primary chemistry action level 1 value is GE3 ppb. The next sample taken at 0757 was within the good practice guidance and was analyzed at 0.581 ppb Cl. COND-DM-1D was backwashed, precoated, and placed in service at 2220 on 3/15/19. Small increases of chloride are common following a new CFD precoat. This CR is for trending. <I> **** Actions Taken **** Notified OPS, supervision and wrote CR
391114 | CR | 20190317 | CAQ | D | E-CB-1/2 Open Light Socket Broken | N | N |  | N | YES | <D> **** Detailed Description **** The Open Light Socket on E-CB-1/2 is broken and needs to be replaced. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** TB 471' West | 02-00-E-CB-1/2
391115 | CR | 20190317 |  | 4 | ROA-FL-1 is at end of roll. | N | N |  | N | YES | <D> **** Detailed Description **** ROA-FL-1 is end of roll. Unknown which filter unit roll, MCR did not want to make entry to verify which roll. <I> **** Actions Taken **** Informed MCR of alarm, initiated AR. | 02-00-ROA-FL-1A,02-00-ROA-FL-1B
391116 | CR | 20190317 |  | 4 | TMU-P-1C Prelube Flow Low Alarm | N | N |  | N | YES | <D> **** Detailed Description **** TMU-P-1C Prelube Flow Low alarm (H13-P824.M.6-3) is locked in with TMU-P-1C not running. Both divisions of the Supervisory System MUXâ€™s read identically and are giving the alarm. SCI-RLY-OCR1A/2/3 and SCI-RLY-OCR1B/2/2 read â€œCLSD Iâ€. | 02-00-SCI-RLY-OCR1A/2/3,02-00-SCI-RLY-OCR1B/2/2
391117 | CR | 20190317 | CAQ | D | SLC-RLY-M600A light burned out, SLC-DIV-1 OOS alarm in | Y | N |  | N | YES | <D> **** Detailed Description **** At 1852 P-603-A7 drop 6-2 alarm came in for "SLC-DIV 1 OOS". Investigation found the light burned out for SLC -RLY-M600A. The light failure is driving the alarm. The requirements of OSP-SLC-M101 are still satisfied for SLC Operability. <I> Initiated temporary log to monitor indications on both SLC -RLY-M600A and SLC-RLY-M600B three times per shift with the alarm locked in | 02-00-SLC-RLY-M600A
391119 | CR | 20190318 |  | 4 | FAX machine in SM Office not working | N | N |  | N | YES | <D> **** Detailed Description **** FAX required for OSP-ELEC-W101 (Attachment 9.1) to Munro was not able to be performed for the DG-2 outage, which started today. Two attempts were made, a FAX machine picked up on the other end, but no FAX was ever sent or received by Munro. To compensate a copy of the enclosure was emailed to the Munro Dispatcher's personal @bpa.gov address. He was made aware he needed to print it out and turn it over to his relief. Request Telecomm replace the Shift Manager's FAX machine and test it as required. <N> **** Equipment Description **** Shift Manager's FAX machine
391122 | CR | 20190318 |  | 3 | New EWP Revision |  |  |  | N | NO | <D> **** Detailed Description **** The new EWP revision doesnâ€™t allow custom stamps to be saved <N> We reached out to the DataGlance vendor on how to generate and save stamps. . A powerpoint has been distributed to the Maintenance Supervisors and to the eWP support Team.
391124 | CR | 20190318 |  | 4 | EVALUATION OF CARBOLINE SEVICE LEVEL 1 COATING NEEDED |  |  |  | N | NO | <D> **** Detailed Description **** The current Service Level 1 coating for use at CGS (Amercoat) is not available in inventory or by supplier. Carboline Service Level 1 coatings are available but have not been evaluated for use at CGS. An evaluation is requested to determine suitability for use at CGS, and for a required revision to PPM 10.2.14 MAINTENANCE COATING PROGRAM. This coating will be needed for R24 pre-outage and outage project activities. . This AR-CR is to document the need for an evaluation of the Carboline product in a timely manner to support R24 pre -outage and outage project activities. . This is not a plant equipment issue. . <I> **** Actions Taken **** 1) Discussed issue with Coatings Program Engineer and Design Engineer Supervisor to determine aa acceptable path forward. . 2) Generated AR-EVAL 391123 to request the necessary evaluation. . 3) Informed WWM of impact on scheduled pre-outage work. <N> Clarification: Replacement Coatings have been evaluated and are available under CatID 38475, 38476 & 16500372. What remains to be done is an update of the "VOC vs Allowable Application" table to include the new products and then added to PPM 10.2.14.
391125 | CR | 20190318 |  | 3 | Notification to Risk Committee not performed consistently |  |  |  | N | NO | <D> **** Detailed Description **** Notification to Risk Committee as defined in ERM-03 have not been consistently performed. ERM-03 section 4.5 defines notification to management risk committee for certain elevated station risks, specifically, the notification of any High Risk Work Plans (HRWP), ODMIâ€™s, and OCC-03â€™s. The purpose of this procedure step is to ensure risk communication, it is not an authorization control. Notifications are to be performed via email to #riskcommittee. It was identified that this is not consistently occurring as several HRWP, OCC-03â€™s and ODMIâ€™s were not emailed to #riskcommittee in the last 6 months. Recommend assignment to AR-ENTRISK to evaluate effective procedure institutionalization between ERM-03 and station procedures and forms that trigger notification (i.e. 1.3.76, 1.3.67, OCC-03). Low severity <I> **** Actions Taken **** ERM staff coached project managers who did not perform HRWP notification as defined in 1.3.76. Evaluated procedures and forms for triggers and identified areas for procedure updates to clarify notification requirements. <N> AR moved out 2 weeks due to finalization and alignment needs of the team regarding resolution of the issue. Management approval for extension was granted - D.Dunigan Notification has been evaluated, additional actions created to determine complete resolution pathforward. BSR is considering changes to notification requirements and procedures.
391126 | CR | 20190318 |  | 4 | Man down call - Personal Medical Condition |  |  |  | N | NO | <D> **** Detailed Description **** Personal Medical Condition â€“ Transport Off-Site On Monday, March 18, 2019 at 08:15 a.m a 2222 call went out concerning an employee needing medical care at bldg. 106 (Dry Creek - Reactor Maintenance). Occupational Health RN and EN advanced first aiders provided care to the individual until HFD paramedics arrived. Hanford Fire Department (HFD) Medic 1923, Medic 1924 and Ladder 1923 arrived at 08:30 a.m. The patient was further evaluated at the scene by HFD and transported to the hospital for further evaluation. Medic 1923 transported the patient to Kadlec Medical Center at 08:50 a.m. Emergency Preparedness was notified for ERO purposes. <I> **** Actions Taken **** Wrote this CR, expanded team
391129 | CR | 20190318 | CAQ | D | (2019 PI&R) CR 390247 sev.â€œBâ€ with no investigation template |  |  |  | N | NO | <D> **** Detailed Description **** It was discovered that CR 390247 â€œFLEX-CAB-4 Unsatâ€ was graded as a severity B with no assignment to perform an investigation template. Per the CR notes, an investigation template is required. Additionally an Event Investigation was requested but no evidence was found that one was performed. <I> **** Actions Taken **** Talked to Engineering CIC and 2019 PI&R inspection team. A Human Performance Investigation template (HUIT) assignment created under CR 390247.
391130 | CR | 20190318 |  | 4 | RX 501' West RHR Pipe Space No Lighting |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** RX 501' West RHR Pipe Space No Lighting. Both rooms and scaffold are dark. <N> **** Equipment Description **** RX 501' West RHR Pipe Chase
391131 | CR | 20190318 | CAQ | D | Washer missing on E-CB-8/DG2 | Y | N |  | N | YES | <D> **** Detailed Description **** during performance of 02134285-01 step 4.7 breaker was missing the flat washer on MOC pin upper link. <I> **** Actions Taken **** informed supervisor, initiated CR. <N> **** Equipment Description **** SM-8 Washer replaced under 02134285 . The breaker function was not impacted by the missing flat washer as the linkages were still being held together by a lock washer and nut. The work being performed was upgrading the component fasteners as recommended by Westinghouse in response to CR 362861. <R> REP/REGE assignments have been cancelled with Compliance Supervisor concurrence. | 02-00-E-CB-8/DG2
391133 | CR | 20190318 |  | 4 | Several out-of-specs during channel calibration | N | N |  | N | YES | <D> **** Detailed Description **** While performing PPM 10.27.56, SPVD Channel Calibration per WOT 0211032701 on 3/15/19-3/16/19, the following EPNs were found out of tolerance at the corresponding steps of the surveillance: MS-SPVD-SCU/1B step 7.4.17, MS-SPVD-SCU/1C step 7.5.6, MS-SPVD-SCU/1D step 7.7.6, MS-SPVD-SCU/2C step 7.9.6, MS-SPVD-SCU/2A step 7.10.6, MS-SPVD-SCU/2D step 7.11.6, MS-SPVD-SCU/3B step 7.12.6, MS-SPVD-SCU/3C step 7.13.6, MS-SPVD-SCU/3A step 7.14.6, MS-SPVD-SCU/3D step 7.15.6, MS-SPVD-SCU/4B step 7.16.6, MS-SPVD-SCU/4C step 7.17.6, MS-SPVD-SCU/4A step 7.18.6, MS-SPVD-SCU/4D step 7.19.6, MS-SPVD-SCU/5C step 7.21.6, <I> **** Actions Taken **** All instruments adjusted in tolerance, all as-left values SAT. | 02-00-MS-SPVD-SCU/1B,02-00-MS-SPVD-SCU/1C,02-00-MS-SPVD-SCU/1D,02-00-MS-SPVD-SCU/2A,02-00-MS-SPVD-SCU/2C,02-00-MS-SPVD-SCU/2D,02-00-MS-SPVD-SCU/3A,02-00-MS-SPVD-SCU/3B,02-00-MS-SPVD-SCU/3C,02-00-MS-SPVD-SCU/3D,02-00-MS-SPVD-SCU/4A,02-00-MS-SPVD-SCU/4B,02-00-MS-SPVD-SCU/4C,02-00-MS-SPVD-SCU/4D,02-00-MS-SPVD-SCU/5C
391134 | CR | 20190318 | CAQ | D | DSA-F-2B bent o-ring groove on bottom of filter housing | Y | N |  | N | YES | <D> **** Detailed Description **** Upon disassembly of DSA-F-2B under WOT 02135646-01 o-ring groove on bottom of filter housing was found bent. <I> **** Actions Taken **** Contacted Engineering to document as found condition. Inspected filter bowl housing for full o-ring contact area which identified that the the bent groove did not/does not appear to impact the o-ring seal. Looked for inventory and a replacement filter head/housing is not onsite. Engineering concurred for pursuing re -assembly in existing condition. If desired, future planning could puruse entire housing replacement in a future window. * Uploaded picture of on EDMS. <N> From the license renewal form that was filled out for WO 02135646, despite the o-ring groove on the bootom of the filter housing, all the seating surfaces looked SAT and unaffected by the bent groove. While there does not appear to be any concern in performing its intended function, recommend plan for replacement at next available window to restore this degraded condition. <R> REP/REGE assignments have beencancelled with Compliance Supervisor concurrence. | 02-00-DSA-F-2B
391135 | CR | 20190318 | CAQ | C | (2019 PI&R) CR 378892 assignments with inadequate closure |  |  |  | N | NO | <D> **** Detailed Description **** During extent of condition review for CR 390828 additional assignments under 00378892 were identified as not meeting the deliverable within the assignment. 00378892-06: Spot check not documented within closure notes. 00378892-07: Expectation was set for Component Managers via email but expectation being set for craft is not documented within the closure notes. <I> **** Actions Taken **** CR initiated and discussed with department Manager.
391137 | CR | 20190318 | CAQ | D | bent tubing associted with DLO-V-709B1. | Y | N |  | N | YES | <D> **** Detailed Description **** Craft identified a previous condition with bent tubing associated with DLO-V-709B1 in the DG2 room. <I> **** Actions Taken **** Generated CR to document condition to support review and planning in a future window if necessary. <N> Engineering evaluated the slightly bent tube. There was a slight downward bend to the pipe but nothing impacting the pipe from performing its intended function. There was no noted cracking or other degredation of the pipe. | 02-00-DLO-V-709B1
391140 | CR | 20190318 | CAQ | C | torque on DCW flexs as found, below torque values | Y | N |  | N | YES | <D> **** Detailed Description **** During maintenance on DCW Flex lines, as found torque was identified as significantly lower then expected value. on DCW-FLX-1B2 and 2B2 during disassembly the torque value on the flanges was not near the desired 188 ft/lbs. <I> **** Actions Taken **** Notified supervision and engineering. Iniated CR to document as found condition. No corrective actions required as new flex lines are being installed and torqued per instructions. | 02-00-DCW-FLX-1B2,02-00-DCW-FLX-2B2
391142 | CR | 20190318 |  | 4 | Paap 12 door sticking and hard to open |  |  |  | N | YES | <D> **** Detailed Description **** Security door Paap 12 is sticking and hard to open. Request assistance to rectify, nothing is visually being wedged in the door frame. Keep this WR open to track the replacement of the door locking mechanism as it needs replaced/overhauled as well. For additional information contact originator or extension 8317. <I> **** Actions Taken **** CR/WR generated <N> **** Equipment Description **** Paap 12, building 25
391143 | CR | 20190318 |  | 3 | Misalignment between TPD-15 and Qual Manual 4.6 |  |  |  | N | NO | <D> **** Detailed Description **** TPD-15, Refuel Floor Training Program Descrption, has not been revised since 2008. In November 2018, Qual Manual 4.6 was revised to remove qual groups RFAB and RFAC and the TPD was not updated accordingly. <I> **** Actions Taken **** Notified Operations Training Manager and AOM - Training
391144 | CR | 20190318 |  | 3 | ACUMEN not providing updated data to PPC for parallel run |  |  |  | N | YES | <D> **** Detailed Description **** After restarting PPC-COMP-ACUMEN from the power outage it was observed that PPC Messaging was not updating the data in the file provided to the PPC. This results in the PPC not getting updated data from ACUMEN and has been in this state since installation activities on 3/5/19 . This has no impact on any other PPC or 3DM processes. Since the ACUMEN system is currently in parallel run status, there is no impact to Operations. This is not a reportable condition. . Recommend to Computer Engineering as a 3 to investigate and restore the correct configuration. <I> **** Actions Taken **** Generated CR and contacted vendor | 02-00-PPC-COMP-ACUMEN
391146 | CR | 20190318 | CAQ | C | (QA) Supplier documents approvals not per approved process |  |  |  | Y | NO | <D> **** Detailed Description **** During a supplier audit of a safety related pump manufacturer, it was identified a replacement pump ASME Design Report owners review signature block was signed by an EN employee not qualified to approve that document. A second document, the pump Seismic Analysis Report, was approved by the same engineer per telecon by the EQ Engineer. The EQ Engineer was contacted to verify the telecon approval. The EQ Engineer stated the document review task was still open. The engineer had not been authorized to sign the document. This pump is still being fabricated and does not affect any installed plant equipment. Reference PO 00348152 Recommend assignment to Technical Services Engineering <I> **** Actions Taken **** Contacted my supervisor, the ASME Design Authority, Technical Services Engineering, wrote this CR. <N> Training Department does not consider this to be a qualification event. The individual who signed was knowledgeable in the industry, but did not hold the correct title to sign the review for an ASME design report. The second part of this CR was a compliance issue.
391147 | CR | 20190318 | CAQ | C | (NRC 2019 PI&R) CA improperly labeled & closed to AR-Self |  |  |  | N | NO | <D> **** Detailed Description **** AR-CR 376172 identified the causes and the corrective action plan prior to CRG grading, therefore, the CR was graded as severity level B, document and correct. One of the corrective actions identified was to install bump covers. An assignment was created to evaluate feasibility of this corrective action, however, assignment type â€œASGNâ€ was used rather than â€œCAâ€. When the assignment determined that bump covers could not be installed and alternate barriers needed to be evaluated, it was then closed to a pre-existing AR-Self. <I> **** Actions Taken **** Recommend assignment to AR-OPSST to document justification for the alternate completion and create corrective actions as appropriate.
391148 | CR | 20190318 | CAQ | D | Foreign materials found in DCW-HX-1B1 | Y | N |  | N | YES | <D> **** Detailed Description **** Referencing WO 02103773 for Cleaning and Inspecting DCW -HX-1B1, some foreign materials were found on the inlet and outlet tubesheets of the heat exchanger (see EDMS). These foreign materials were retrieved and the heat exchangerâ€™s tubes are being cleaned for any possible materials inside. Therefore, thereâ€™s no risk to operation, this is for trend only. <I> **** Actions Taken **** Discussed this with System Engineer and OCC eng. Manager then initiated this CR <N> Plugging margin for DCW-HX-1B1/1B2, per ME-02-17-10 is 32 tubes (either on the inlet or outlet side). Thermal performance trends on both HXs are currently trending steady at 48 (1B2) and 44% (1B1) margin to technical specifications. Based off of the above criteria and that there was only material found partially obstructing only 3 tubes there is no concern for the HX performing its intended function. <R> REP/REGE assignments have beencancelled with Compliance Supervisor concurrence. | 02-00-DCW-HX-1B1
391149 | CR | 20190318 | CAQ | C | (2019 PI&R) Justification not documented for no CA taken |  |  |  | N | NO | <D> **** Detailed Description **** AR-CR 372667 does not have any corrective actions assignments and does not document why corrective actions are not needed. This is not in compliance with SWP-CAP-01. <I> **** Actions Taken **** Recommend assignment to AR-OPSST to document justification for no corrective actions or create corrective actions as appropriate.
391150 | CR | 20190318 |  | 4 | Program stall fault on SCI-MUX-OR1B/2 | N | N |  | N | YES | <D> **** Detailed Description **** WHILE REMOVING ASTROMED FROM SCI-MUX-OR1B/1 by WR 29145876, IT WAS OBSERVED THAT SCI-MUX-OR1B/2 HAD A PROGRAM STALL FAULT. Fault messages were checked and were cleared per ARP 4.824.M. 4 Program stall faults had been recieved. SCI-MUX -OR1B/2 faults are clear. SCI-MUX-OR1B/2 should be replaced. This mux is associated with TMU-RMS-V/19B only. . CID 60807964 for MUX <I> **** Actions Taken **** Wrote CR and generated WR to replace MUX. | 02-00-SCI-MUX-OR1B/2
391151 | CR | 20190318 | CAQ | D | SW-V-736B piping is plugged | Y | N |  | N | YES | <D> **** Detailed Description **** SW-V-736B (DG2 SW supply drain) piping is completely plugged. This was intended to be the drain path for work on both E-GEN-DG2 DCW Heat Exchangers. Due to the piping blockage, several hours of time and resources were wasted while we were forced to drain the large volume of SW supply and return piping, via the much smaller (also clogged) HX drain lines. Additionally, this drain path is very valuable, as a point to direct SW system leakby away from components being worked on (SW isolations valves have a legacy of being poor maintenance isolations). Attempts to unplug the line with bailing wire were performed by Maintenance personnel, but unsuccessful. <I> **** Actions Taken **** Informed MCR. Attempted to "rod out" the drain line, with no success. <N> **** Equipment Description **** DG2 | 02-00-SW-V-736B
391152 | CR | 20190318 |  | 3 | Add P&L to clarify remote breaker racking tool fit-up |  |  |  | N | NO | <D> **** Detailed Description **** The use of the remote breaker racking tool requires several steps to set up the tool to ensure proper fit in the breaker cubicle and alignment with the breaker. Consider adding guidance to SOP-ELEC-BKR-OPS (in the form of a P&L) to specify that the fit-up of the tool can be verified any time prior to racking the breaker as long as the motive force to the tool is not present (not connected). <I> **** Actions Taken **** Discussed with shift management.
391154 | CR | 20190318 |  | 3 | SW-V-196 and SW-V-197 current design/Maintenance drain | Y | N |  | N | NO | <D> **** Detailed Description **** Currently as part of maintenance on DCW-HX-1B1 and DCW-HX -1B2, SW-V-196 and SW-V-197 are used for draining the end bells. These valves are a needle style valve (1/2' ported style) that limited the flow during the drain of the HX work. <I> **** Actions Taken **** Generated CR. If work is time critical, then these valves should be reviewed for change out to ball type valve to allow for more flow and a reduced time to drain the associated HXs to support the work.
391157 | CR | 20190319 | CAQ | D | PWC-P-5 through wall leak on pump casing | N | Y |  | N | YES | <D> **** Detailed Description **** While performing operator rounds PWC-P-5 was found to be spraying water upwards about 10 feet onto overhead electrical cableing. The leak is a through wall leak on the pump casing. PWC-RMS-P/5 was taken to off. See attached photos. <I> **** Actions Taken **** Notified CRS and wrote CR | 02-00-PWC-P-5
391158 | CR | 20190319 | CAQ | C | Configuration management issue on DG-ENG-1B2 | Y | N |  | N | YES | <D> **** Detailed Description **** WO#02128135-01 instructions do not match field sizes and do not match the drawing M512-3 for which flex hoses go to which air start motor. Work instructions state DSA-M-6B2/2 should be connected to DSA-FLX12B2/1, in the field the hose has the EPN tag DSA-FLX-11B2/1. DSA-M-6B2/4 says it should be connected to DSA-FLX -12B2/2, in the field the hose has the EPN tag DSA-FLX -11B2/2. Upon further investigation it was identified that all of the DSA air start motors on DG-ENG-1B1 and DG-ENG -1B2 have the same issues. The hoses ordered for the task are the 32.75â€ CID58621682 and the hoses that go to the specified air start motors to be replaced are 24.75â€ CID58621675. This physical configuration control issue needs to be evaluated and recommend extent of condition be checked on the other trains to eliminate the risk of error in further maintenance activities. <I> **** Actions Taken **** Initiated the condition report, notified my supervisor and the main control room as well as the OCC. See EDMS for pictures <N> The component in the field are mislabeled per the drawing. The two 32.75" hoses that need to be replaced and the changes are as follows: DSA-FLX-12B2/1: 1.25 "ODX32 .75 "LG FLEX CONN SUPPLY TO DSA-M-6B2/2 should specify being connected to DSA-M-6B2/1 instead. DSA-FLX-12B2/2: 1.2 "ODX32.75"LG FLEX CONN SUPPLY TO DSA-M-6B2/4 should specify being connected to DSA-M-6B2/3 instead. Design engineering should also review for extent of condition for any additional drawing impacts as well. | 02-00-DSA-FLX-12B2/2
391159 | CR | 20190319 |  | 3 | eSOMS Plant Water Balance Erroneous Values |  |  |  | N | NO | <D> **** Detailed Description **** The STA/IA attempted to perform the daily water balance calculation on eSOMS. Total volume of water in the plant was calculated to be over 400,000 gallons lower than the previous dayâ€™s value. All operator shift logs reflect normal values in CSTs, Suppression Pool, RPV, RW System, and the Spent Fuel Pool. The calculated water balance is incorrect with no obvious reason to explain why. <I> **** Actions Taken **** STA/IA Re-reviewed the shift logs for the Radwaste Control Room Operator and the Reactor Operator logs. Nothing unusual was noted on any of the logs. Informed the CRS and shift manager. Attempted to have operators re-upload their logs to eSOMS. Re-performed the Water Balance calculation multiple times and still received bad values. Initiated this CR to expand the team due to the calculation remaining erroneous. <N> SUPV has reviewed and approved closure of this CR. See EDMS for evidence. No further action is required.
391160 | CR | 20190319 | CAQ | D | DCW-HX-1B1 / 1B2 End Bell inspection | Y | N |  | N | YES | <D> **** Detailed Description **** Based on an inspection performed of the DCW-HX-1B1/1B2 end bells following cleaning the replacement of the end bells is recommended. This was due to some visible pitting/erosion that was present along the end bell surface at the area that meets with the divider plate. Previous thermal performance data for these two Heat Exchangers was all acceptable. <I> **** Actions Taken **** OCC was notified and engineering recommended to replace the four end bells with the new end bells from the warehouse. This replacement activity was in-progress. WO 02103773 and 02103774. <N> **** Equipment Description **** DG2 room | 02-00-DCW-HX-1B1,02-00-DCW-HX-1B2
391161 | CR | 20190319 |  | 3 | DWR G4 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** The G4 Datastrip wireless reader failed its daily operability test. Contact security at ext 2185 for further details <I> **** Actions Taken **** Security notification made, IS ticket # IR-0039845 initiated. <N> **** Equipment Description **** Security Checkpoint
391164 | CR | 20190319 | CAQ | D | Received accumulator trouble alarm 4247 | Y | N |  | N | YES | <D> **** Detailed Description **** Alarm due to water <I> **** Actions Taken **** OPS 2 drained / cleared alarm | 02-00-CRD-TK-125/4247
391166 | CR | 20190319 |  | 4 | M&TE Suspended/ Lost |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0068239 Control Co. Stopwatch- model 1051 Missing from the Tool Crib. No Activity in Met/Track or Portal J. Suspended/ Lost. No Plant Impact. DEF #6971A written. No Action Required. <I> **** Actions Taken **** None Trendng purposes only.
391167 | CR | 20190319 |  | 4 | M&TE Susp |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0064281 Proto Torque Wrench- model J6062C 200in/lb. Missing from Clean Tool Crib. Per PPM 1.5.4 section 4.4.3 (a-c) Torque Wrench had acceptable post use verifications @ +/- .06% by Stds Lab Techs. Suspended/ Lost. DEF #6972A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391175 | CR | 20190319 | CAQ | C | General corrosion on DCW-HX-1B1/1B2 | Y | N |  | N | YES | <D> **** Detailed Description **** During the PM inspections of DCW-HX-1B1/1B2 (WO 02103773 and 0210774 respectively), corrosion/erosion and some pitting were found on the inlet/outlet channel heads (including divider plates), reversing chambers, and the channel end covers. The end covers were replaced with new like-for-like covers and the channel heads & reversing chambers were cleaned. The visual inspection didnâ€™t identify any degradation that can affect the thermal performance or the functionality of the heat exchangers. The as-left condition is satisfactory and no additional repairs are needed. Therefore, thereâ€™s no operability concern with putting the heat exchangers, in their current condition, in service again. Recommend this CR to heat exchanger engineer in code programs for resolution. <I> **** Actions Taken **** Discussed CR with system engineer and OCC eng. manager then initaited this CR <N> **** Equipment Description **** DG2 room | 02-00-DCW-HX-1B1,02-00-DCW-HX-1B2
391177 | CR | 20190319 | CAQ | D | ISFSI Outside Ambient temp indicates yellow. | Y | N |  | N | YES | <D> **** Detailed Description **** ISFSI Outside Ambient temp indicates yellow on SFS-TR -MASTER1, SFS-TR-MASTER2, and SFS-TR-MASTER3. Outside Amibent indicates 24.7 F on current temperature printout. Current Outside Ambient on TDAS indicates 29.6 F. Have I&C maintenance investigate. <I> **** Actions Taken **** Infromd CRS/SM | 02-00-SFS-CP-ISFSI/TMS
391179 | CR | 20190319 |  | 4 | WEI-2296 Rejected |  |  |  | N | NO | <D> **** Detailed Description **** As found out of tolerance. Attempts were made to adjust and could not be calibrated within specifications. <I> **** Actions Taken **** Rejected sticker placed on tool. Inventory "status" changed to "rejected" and the "state" was changed to "D" for deactivated. CR number documented in the equipment history for future reference.
391182 | CR | 20190319 |  | 3 | PPM 12.4.21 needs enhancment |  |  |  | N | NO | <D> **** Detailed Description **** Step 7.4.8 needs to be updated with the words "using protocol 4" deleted. Other protocols are availalbe to use for counting. <I> **** Actions Taken **** Informed Chemistry Count Room specialist. Wrote CR.
391189 | CR | 20190319 |  | 4 | Ammunition in Vehicle |  |  |  | N | NO | <D> **** Detailed Description **** Ammunition was discovered at the vehicle gate during a vehicle search. The individual was In-processing for the upcoming Outage. <I> **** Actions Taken **** The individual was sent home and the Benton County Sherriff was notified.
391190 | CR | 20190319 |  | 3 | CMR 12157 for Calc. 5.51.52 cannot be Located |  |  |  | N | NO | <D> **** Detailed Description **** This is a documentation issue only. CMR 12157 to calculation 5.51.52 (Shutdown Analysis for Pipe Breaks Outside Containment) cannot be located in Portal J or in the calculation hard copy files. Engineering Change 11373 removed the sample racks WOA-SR-18A/B and WOA-SR-19A/B and CMR 12157 removed the reference to the sample racks in calculation 5.51.52. The information for the CMR is located in the Topic Notes for the CMR, however, the markup pages for the calculation are not available. CMR 12157 will need to be recreated by using the Topic Notes of the CMR and EC 11373 and store the recreated CMR in the correct location as stated in DES-4-19. . Bechtel prepared CMR 12157, however, did not follow the procedure for storing the electronic version of the CMR. CMR 12157 was approved in Portal J in 2013. Currently, CMR 12157 is designated as an outstanding document against calculation 5.51.52 and will be incorporated into calculation 5.51.52 when the calculation is to be revised, . Recommend assignment to AR-DMC to recreate CMR 12157 against calculation 5.51.52. . <I> **** Actions Taken **** Searched several locations for the CMR 12157 with no results. The Bechtel files available do not contain this CMR either. Searched the hard copy files under 5.51.52 with no results. <N> See EDMS for markup of some of the calc. 5.51.52 pages. The whole calculation will need to be reviewed to capture all of the WOA-SR-18A/B and WOA-SR-19A/B entries.
391192 | CR | 20190319 | CAQ | C | DLO-ST-1B2 tank cover found a jar | Y | N |  | N | YES | <D> **** Detailed Description **** The FME cordinaator walked down the DG 2 room to support FME observations and identified the DLO-ST-1B2 top cover was left raised approx 3 inches. The concern is that foreign debris could enter the tank without an FME cover being installed. The tank needs to be inspected to ensure that no debris entered the tank while it was left partially open. <I> **** Actions Taken **** The FME cord. discussed the issue with Maint. Mechanics, and OPS personnel. OPS promptly ivestigated the issue. OPS management identified the Operator that opened the tank to isolate a valve on the internal side of the DLO Strainer tank to support clearance work. The operator in question states that they left the tank lid in a closed state with no need for an FME cover. the Investigation is still on going. The FME cordinator recomends that this CR be screened as a CAQ severity level C to ensure that the inspection of the tank takes place, and coaching takes place for the individual that left the tank open. <N> Following review of the DG2 scope, the WO instructions tied to DLO, and the clearnaces for DG2, there DLO ST-1B2 was not openned during the DG2 Safety System Window. . D-DG2-DLO-002 was reviewed for tags and affected work orders. 0213078801 was previously included in the Clearance for a leak on DLO-F-2B2, however this WO was cancelled prior to the window. . WO 0212838201 (DLO-PI-2B1) did not impact the subject filter. WO 0209232301 & 0209232501 for DLO-M-P/3B1 & DLO -M-P/3B2 respectively, are electrical scope only and did not impact piping or tank systems. <S> Closeout inspection on 3-19-19 was completed during D-DG2 -DLO -002 clearance removal. This DNC no longer exists. Coaching has been provided to Maintainence and Operations. No further CA's required. | 02-00-DLO-ST-1B2
391194 | CR | 20190319 |  | 3 | Request for editorial change to SOP-LO-OPS |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.8.5 of PPI PPM SOP-LO-OPS states that the hose for oil addition is to be run to the float valve compartment of the Lube Oil Conditioner (TO-LOC-1). The float valve compartment is the correct location; however, the descriptive aid in parentheses says that it is the â€œNorthwest Compartmentâ€. The float valve compartment is in the Southeast corner. [The northwest compartment is the precipitation compartment and has multiple screens that would inhibit placing the hose.] Please edit Step 5.8.5 to read â€œSoutheast Compartmentâ€. See EDMS
391196 | CR | 20190319 |  | 3 | Incorrect Revision Number Found on Issued Form |  |  |  | N | NO | <D> **** Detailed Description **** Form 26381 is utilized for grading self-assessments at the Performance Assessment Review Board meetings. The current revision is eight, however, the footer says â€œ26381 R7â€. It would appear that during the last form revision the 7 was not changed to an 8 prior to issuance. <I> **** Actions Taken **** Discussed with the CAP supervisor. Initiated revision for form 26381.
391199 | CR | 20190319 |  | 4 | NRC identified lighting issue RW elevator stairwell |  |  |  | N | YES | <D> **** Detailed Description **** NRC identified lighting issue in RW building elevator stairwell, one flat above the 507 elevation. One of the flourencent lights is out and the other is very dim. <I> **** Actions Taken **** CR/ WR was written and CRS is informed <N> **** Equipment Description **** RW building elevator stairwell one flat above 507 elevation
391200 | CR | 20190319 |  | 3 | Service building heater pH in CCW action level 1 |  |  |  | N | NO | <D> **** Detailed Description **** SBH in the GSB had a serious leak that just recently was fixed. As the corrosion inhibitor chemicals were all gone chemistry did a chemical add. The corrosion inhibior concentration is normal now but the pH was still low which will require a sodium hydroxide add to bring the pH back into specified band per SWP-CHE-02. Currently chemistry for the SBH is in action level 1 which allows 90 days for resolution. <I> **** Actions Taken **** Notified MCR, Chemistry Supervision, and Chemistry technical specialist. Calculated, and mixed the necessary chemicals for the planned add on the week of 3/25/19
391202 | CR | 20190319 | CAQ | C | (NRC) Questions on road closures used for rad shipments |  |  |  | N | NO | <D> **** Detailed Description **** Region IV NRC staff had questions on two rad shipments made in 2013 and 2014. Shipments 13-07 on 3/26/13 and shipment 14-07 on 4/22/14 contained RWCU resin and were shipped to the burial site. The shipping log and paperwork for both shipments note that DOT regulations do not apply due to roads being closed (not entering public roadway) for the shipment. The NRC staff questioned the applicability of 10 CFR 71.5 (b) to the shipments. <I> **** Actions Taken **** RPM and Licensing notified. <R> This issue is resulting in a Severity Level IV Violation of 10 CFR 71.5.b for shipping type B materials in a type A container in accordance with DOT shipping standards without prior NRC approval. No CCA due to the age of the issue.
391206 | CR | 20190319 |  | 4 | Small crack found on CW-FN-1 blade | N | N |  | N | YES | <D> **** Detailed Description **** During walkdown of CW-FN-1, a roughly 4 inch circumferential crack was observed near the base (neck) of blade 2 on CW-FN-1 (currently out of service for WO 02138748). The cracked blade should be replaced prior to returning the fan to service. The bases of the remaining blades were inspected and no additional cracks were found. The older Tuf-Lite II model fan blades have a history of blade failure caused by fatigue cracking near the base of the blade (CR 48965) ; however, the fan blades on CW-FN-1 were replaced with the more resilient Tuf-Lite III blades in 2007 (WO 01106105-01) and were projected to have a 20 year life span. The cracked blade should be retained for further evaluation to determine the severity of the crack and potential failure mechanism. | 02-00-CW-FN-1
391207 | CR | 20190319 |  | 4 | CW-FN-19 oil level is at the ADD mark |  |  |  | N | YES | <D> **** Detailed Description **** CW-FN-19 is at the ADD mark while the fan is running. No abmormal leakage was noted. Please restore oil level to normal band. CW-FN-19 is on top of CW-CT-2A. | 02-00-CW-FN-19
391208 | CR | 20190319 |  | 4 | degraded overhead light in CW-CT-1A truck bay | N | N |  | N | YES | <D> **** Detailed Description **** Approximately half of the fasteners for one of the overhead lights in the truck bay of CW-CT-1A are not properly engaged and the end of the light fixture is hanging several inches from the ceiling. The light fixture did not appear to in imminent danger of failure; however, it is recommended that repairs be made prior to R24 for industrial safety and to prevent an inadvertant introduction of foreign material into the CW system. <N> **** Equipment Description **** CW-CT-1A truck bay, over head lights
391209 | CR | 20190319 |  | 4 | Minor First aid (bandaid needed) |  |  |  | N | NO | <D> **** Detailed Description **** While attending training at the MPF, employee grabbed the DisplayPort cable plug with their right hand to remove for use with a laptop to view instructional video on the conference room TV. The cable plug bound in the port while attempting to unplug, requiring additional force to remove. When the plug broke free of the port, the employeeâ€™s right pinky finger came into contact with the computer chassis, causing a minor scrape and a small cut on the end of the finger. This cut required a band-aid in order to stop the bleeding. <I> **** Actions Taken **** Notified training instructor, then occupational health, industrial safety, and my supervisor (department manager) as required by ISPM-1. Also completed incident reporting requirements in PTL as required, reference Incident Report #19-0002.
391210 | CR | 20190319 |  | 4 | New camera at RFW-VMP-1 needs adjustment |  |  |  | N | YES | <D> **** Detailed Description **** It appears that there is a different camera installed to monitor RFW-VMP-1. The new camera vibrates excessively, does not zoom in far enough, and the angle at which it monitors RFW-VBI-XE/P1B creates too much glare. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR. . This needs to get corrected promptly, as we are monitoring the vibrations per ODMI 386522. <N> **** Equipment Description **** RFW-VMP-1 camera
391211 | CR | 20190319 | CAQ | D | MS-TR-6 | Y | N |  | N | YES | <C> CR was reopened at shift managers request to update the operability determination notes. <D> **** Detailed Description **** While performing rounds it was observed that the CRD temperature recorder for HCU 14-27 was reading burnout. <I> **** Actions Taken **** Wrote CR and informed CRS | 02-00-MS-TR-6
391212 | CR | 20190319 | CAQ | D | Rod accumulator trouble on CRD-HCU-2207 (hi water level) | Y | N |  | N | YES | <D> **** Detailed Description **** Rod accumulator trouble on CRD-HCU-2207 due to high water level. <I> **** Actions Taken **** Cleared alarm per SOP-CRD-HCU, informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-HCU-2207
391213 | CR | 20190319 |  | 3 | step change in RFW-P-1B thrust bearing metal temperature | N | N |  | N | YES | <D> **** Detailed Description **** ODMI 386522 calls for increased monitoring of the RFW-P-1B thrust bearing metal temperature using the eDNA points W008 and W009. The action level for this monitoring is a step change in temperature of GT 10 degrees or an increase in temperature to 160 degrees. On the morning of 03/16/2019, point W008 experience a step drop in temperature from 124 to 117 degrees. This does not meet the trigger criteria for the ODMI but there is no apparent cause for the drop. The eDNA point has remained at the new reduced temperature value. A screen capture of the affected point is attached <I> **** Actions Taken **** informed the Shift Mananger and CRS | 02-00-RFW-P-1B
391214 | CR | 20190320 | CAQ | D | SW-V-197 leaking by | Y | N |  | N | YES | <D> **** Detailed Description **** SW-V-97 is leaking by, draining approximately 1 pint per minute to the floor scupper. Recommend repair or replace as necessary. <I> **** Actions Taken **** Informed SSS, generated AR/WR. . Leaking valve is SW-V-197, not SW-V-97 | 02-00-SW-V-197
391215 | CR | 20190320 |  | 4 | HSSF-EUH-1 found on with building beyond hot. | N | N |  | N | YES | <D> **** Detailed Description **** HSSF-EUH-1 found on with building beyond hot. They Portable eye wash was almost too hot to grab. Portable eye wash was completely empty and depressurized. It is suspected this was due to the temperature of the room. the setting appears to be on three. the back of the heater can be viewed from the outside from the window. breaker was opened and door left open to cool down. eyewash needs refill /repair/replace, heater needs a better thermostat. <I> **** Actions Taken **** Informed the MCR, opened disconnect HSSF-DISC-EUH/1 | 02-00-HSSF-EUH-1
391216 | CR | 20190320 | CAQ | D | Received RHR Pump 2B Room HVAC Out of Service alarm. | Y | Y |  | N | YES | <D> **** Detailed Description **** Received RHR 2B Out of Service, H13-P601.A2,6-6 alarm due to RHR Pump 2B Room HVAC Out of Service BISI alarm. Informed the CRS and Shift Manager. Reference T.S. 3.4.9, 3.5.1, 3.6.1.5 and 3.6.2.3. Reference LCS 1.7.1. <I> **** Actions Taken **** An Equipment Operator reports that RRA-42-8F4E is in ON and itsâ€™ green light is illuminated. Possible RRA-RLY-80/FN3 failure. | 02-00-RRA-FN-3
391218 | CR | 20190320 | CAQ | D | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. The alarm was due to the J7 sensor 500KV neutral ground overcurrent, J8 sensor 230kv Neutral Ground Overcurrent, J11 sensor SM-7 Undervoltage, J12 sensor SM-8 Undervoltage, J15 230KV Undervoltage, and J16 sensor Main Generator Negative Sequence. All sensors have been reset. E-TR-S and E-TR-B voltages are 237/238/237 kV and 117/118/117 kV respectively. BPA Dittmer reports ASHE LO-MO line tripped open and automatically reclosed (single phase). There was not a need for an emergent outage and no RAS was initiated. All plant controllers and equipment exhibited normal operation
391219 | CR | 20190320 |  | 3 | QA Missed Opportunity |  |  |  | Y | NO | <D> **** Detailed Description **** QA review of AR-CRs written during the week of June 11 thru 14 2018 in response to observations made by the NRC during the FLEX program inspection determined that Quality missed an opportunity to identify issues that did not demonstrate excellence. See EDMS for entire evaluation. Quality should evaluate for potential process improvements. <I> **** Actions Taken **** Discussed with Quality Manager.
391220 | CR | 20190320 | CAQ | C | Procedure enhancement 1.5.18 FLEX equipment |  |  |  | N | NO | <D> **** Detailed Description **** Rev 6 (current) of 1.5.18 has actions in step 6.1.3 of actions to take if equipment is restored to functional, but does not have the actions to take when the equipment is removed. . Look at step 6.1.5 of rev 4 of 1.5.18. . the steps were lost in the revision process. Please restore them <I> **** Actions Taken **** Wrote CR
391221 | CR | 20190320 |  | 4 | E-TR-M1 Gas Analyzer yellow light | N | N |  | N | YES | <D> **** Detailed Description **** Transformer M1 gas analyzer yellow light lit <I> **** Actions Taken **** Initiated CR <N> **** Equipment Description **** Transformer Yard; M1 gas analyzer | 02-00-E-TR-M1
391222 | CR | 20190320 |  | 4 | Test Bends not qualified |  |  |  | N | NO | <D> **** Detailed Description **** While working work order 02108851-18, to qualify tube bends. It was discovered that two sizes of pipe could not be qualified using the Teledyne Pines bender in Building 32, per Welding Engineering. When bending tube and pipe greater than 1â€ with this bender the bends could not be qualified due to exceeding ovality requirements called out in PPM 10.2.28. The bender is compressing the throat of bend causing distortion. After working with ENW Engineer, we will recommend getting guidance and or Service from Teledyne. <I> **** Actions Taken **** Confirmed with Engineering and Management to document in condition report.
391223 | CR | 20190320 |  | 3 | WO 02138508 problem in Portal J |  |  |  | N | NO | <D> **** Detailed Description **** When you click in the status field and press the F9 key for WO 02138508 Task 02 and 03 you get the following error message "Your transaction was unable to complete processing due to an application program failure. If problem persists, report this to your application support group." This is preventing CORC personnel from removing the RO2 hold on these tasks. <N> User released the hold from DataGlance and when went back to view in Asset Suite the error was corrected. . Was not able to recreate the problem or figure out if it was a duplicate gen-arg issue. . Recommend closing CR and Trend.
391224 | CR | 20190320 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3 and XFMR TR-B | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3 and XFMR TR-B TROUBLE H13-P800.C4.2-5 alarms in and clear. Oscillograph Started alarm was due to the J9 sensor 115kv Neutral Ground Overcurrent and J15 230KV Undervoltage. The sensors have been reset. E-TR-S and E-TR-B voltages as indicated on H13-P800 are 237/238/237 kV and 117/118/117 kV respectively. BPA Munro reports Midway Benton 115kv line relayed off and back on (single phase). There was not a need for an emergent outage and no RAS was initiated. All plant controllers and equipment exhibited normal operation. OPS4 reported no alarms on XFMR TR-B.
391229 | CR | 20190320 | CAQ | D | MET-WMON-1A,1B,2A,2B OOT | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of ICP-MET-S301 (0210472101) ALL AF TESTING FOR THE BEARINGS OF THE ANOMOMETERS WERE DETERMINED FAILED. MET-WMON-1B AF SPEED VALUES WERE OOT HIGH <I> **** Actions Taken **** INFORMED SUPERVISOR CREATEDD CR AND REPLACED ALL 4 INSTRUMENTS. AL VALUES/TESTS IN TOLERANCE SAT
391231 | CR | 20190320 |  | 4 | Cooling Tower & Parking Lot Lighting Burned Out |  |  |  | N | YES | <D> **** Detailed Description **** (Industrial Safety) Cooling tower yard lighting (SW Corner) near trailer 174 and the South gravel parking lot lighting is burned out. This condition puts employees walking or working in these areas at risk of personal injury and increases the potential for a vehicle accident. <I> **** Actions Taken **** Initiated this CR and Work Request <N> **** Equipment Description **** Yard Lighting
391242 | CR | 20190320 |  | 4 | Missed Sodium Hypochlorite Delivery 3/19/2018 |  |  |  | N | NO | <D> Bulk chemical delivery of sodium hypochlorite was missed on 3/19/2019. Delivery was scheduled to arrive between 800 -1400, truck arrived at 1500. Operations did not have enough staff to offload the chemical until after shift change. Driver did not have enough hours to accommodate the additional time. <I> Delivery rescheduled to 3/20/2019, notified Shift Manager of new delivery date, and notified Chemistry of missed delivery, wrote condition report for trending.
391243 | CR | 20190320 |  | 3 | Procedure correction for 12.14.12 |  |  |  | N | NO | <D> **** Detailed Description **** Step 6.3.6.g and 6.3.7 need to be removed from 12.14.12. These steps lift the clearance before the drains and vent is shut for RCC-F-1. Step 6.3.8.d and 6.3.8.e will lift the clearance once the drains and vents are closed.
391245 | CR | 20190320 |  | 4 | Non-EN vehicle contacted other non-EN vehicle at check point |  |  |  | N | NO | <D> **** Detailed Description **** On Monday (03/18) an employee in a personal vehicle was processing through the vehicle check point when their foot slip off the brake resulting in the vehicle rolling and making contact with a personal vehicle in front of them. Both individuals pulled off after proceeding through the access point and identified that there was no damage to either vehicle. ISPM-1 was reviewed and the incident was reported to their supervisors. <I> **** Actions Taken **** Reported the accident to applicable parties as required per ISPM-1. Initiated Condition Report.
391246 | CR | 20190320 |  | 4 | 10.27.59 and 10.27.60 require revision - Safe-T-Cable |  |  |  | N | NO | <D> **** Detailed Description **** EC 17374 was approved to allow the use of Safe-T-Cable as a substitute for lockwire on the MSRV load cells. 10.27.59 and 10.27.60 require revision to reflect this. Markups of both procedures are being provided to the maintenance procedure writer. <I> **** Actions Taken **** Initiated CR for revision and provided markups to procedure writer. <N> All actions required under this CR have been taken. An assignment has been created under the Maint. proceudre revision data base. A link to the data base has been created within the EDMS of this AR.
391247 | CR | 20190320 |  | 4 | RWCU-P-28 trips when opening RWCU-V-438A | N | N |  | N | YES | <D> **** Detailed Description **** While performing A RWCU-TK-104B resin transfer in accordance with SOP-RW/RWCU-OPS section 5.4 , RWCU-P-28 tripped when opening RWCU-V-438A. RWCU-TK-104B had been recirculated for greater than 90 minutes per step 5.4.9. Upon request from the Resin Drying System Operator, proceeded on with the procedure. On step 5.4.15, open RWCU-V438A, I opened the valve and then immediately, RWCU -P-28 tripped off. I attempted repeating the procedure again, with the same result. <I> **** Actions Taken **** Informed MCR and wrote CR. | 02-00-RWCU-P-28
391248 | CR | 20190320 | CAQ | D | SW-PCV-15B is Leaking By in the Indicated Closed Position | Y | Y |  | N | YES | <D> **** Detailed Description **** SW-PCV-15B is slightly leaking by in the indicated closed position. While performing a walk down of CCH-CR-1B, it was observed that the piping downstream of the CCH-CR-1B condenser (CCH-CU-1B) was cool to the touch. Using an infrared thermometer, the surface of the CCH-CU-1B outlet piping was found to be 54.8Â°F. The temperature of the pipe should have been at room temperature (~64Â°F). SW-P-1B was running and CCH-CR-1B was in standby mode. When CCH-CR-1B is in standby mode, SW-PCV-15B should be in the closed position. SW-PCV-15B controls the SW outlet flow through CCH-CR-1B. With SW running and CCH-CR-1B in standby mode, the expected condenser pressure is approximately 0 â€“ 3 inHg vacuum. With SW-PCV-15B partially opened it allows cooler water to flow through the condenser. The cool water is causing the condenser pressure to decrease to 10 inHg vacuum as indicated on SW-PI-7B. This condition does not affect the ability of CCH-CR-1B to perform its current licensing basis design function. With SW-PCV-15B leaking by, it results in a slightly more depressed condition in the chillerâ€™s condenser prior to startup. Upon chiller start-up, the chiller is fully capable of operating the chiller in the desired condenser pressure band. Lower pre-start conditions have been viewed in past surveillances and it has not affected the ability of the chiller to perform its design function. During these instances, the condenser refrigerant pressure increased to the normal running reference band (9 inHg â€“ 4.5 psig) with the chiller surveillance SAT. The annual PM (PMID 26645) to calibrate SW-MO-PCV/15B is currently planned for 12/16/2019 in WO 02128071. It is recommended that SW-MO-PCV/15B be calibrated in the next available CCH-CR-1B work window. Future work should include positive means to verify that the valve is completely closed in standby by measuring the condenser outlet temperature with SW-P-1B running. | 02-00-SW-PCV-15B
391249 | CR | 20190320 | CAQ | D | RWCU-MO-44 leak by & trace anomaly | Y | N |  | Y | YES | <D> **** Detailed Description **** During diagnostic testing on RWCU-MO-44 per WR 29147493 identified the following: 1) Trace showed the valve closed but was still leaking by at approx 100 gpm. This represents of internal valve degradation. 2) To achieve approx. 500 gpm, the valve is cycled less than 3 seconds open. Calculation shows the valve is 0.192" from the seat, signifying the valve is oversized for this application. 3) Anomaly was observed near the seat. It's difficult to detemine what the anomaly is because the valve is only stroked 0.192" from the seat. <I> **** Actions Taken **** The WR repeated the steps and the results were the same. RWCU-V-44 is scheduled to be replaced as part of the Heat Exchanger replacement in R25. An action should be added to design to ensure the right size/application valve is selected. The trace showed the valve has sufficient seating force to prevent leakby. See attached supporting documentation and screen prints of the trace. | 02-00-RWCU-V-44
391251 | CR | 20190320 |  | 4 | Damaged fencing outside door R-106 |  |  |  | N | YES | <D> **** Detailed Description **** The chain link fence outside door R-106 was found to be damaged. needs repair. Appears to be damaged from snow removal activies. <I> **** Actions Taken **** Initated CR Took pictures <N> **** Equipment Description **** Fencing outside Door R-106 for truck entrance
391252 | CR | 20190320 |  | 4 | Failed to finish WO during week due to parts not here |  |  |  | N | NO | <D> **** Detailed Description **** Unable to execute WO 02120341-17 (pre-outage) to fabricate a new stem nut, due to the stem not being here for the work. The stem and actuator not being here has the ability to impact outage work. this Stem has been on order since January 2018, the manufacture had an issue with fabricating the part, it now has a scheduled delivery of 4/19/2019 this work is on RWCU-V-4 <I> **** Actions Taken **** Contacted procurement about parts not being here. notified supervision and work week manager
391254 | CR | 20190320 |  | 3 | DSA-PCV-1B and DSA-PCV-2B out of limits | N | N |  | N | YES | <D> **** Detailed Description **** While performing 10.27.30B step 7.2.7 DSA-PCV-1B As Left values are149psi and 145psi for DSA-PCV-2B. Per step 7.2.8 directs to notify Supervisor and write CR <I> **** Actions Taken **** notified Supervisor CR written | 02-00-DSA-PCV-1B,02-00-DSA-PCV-2B
391255 | CR | 20190320 |  | 3 | Access control (dose)/respirator qualification file locked w |  |  |  | N | NO | <D> **** Detailed Description **** Currently RP-Ops performs a nightly routine that collects exposure records and current resp. qualifications and saves it to the local drive. This information provides necessary information in the event of network outage and emergencies to facilitate access to the buildings RCAs. While performing problem resolution associated with the current bat file it was observed that access to the folder was unavailable. This prevented the BAT file from performing its intended action. The last updated available pdf at the RP access is date 3/15/19. The bat file provides no indication if the current file has been updated correctly. There are 2 issues with the current process. The first is lack of an indicator the file has been updated (although by opening and verifying date stamp can be an indicator). The second is of course lack of access to be able to retrieve the current file location to update the local drive. <I> **** Actions Taken **** Notified IS, RP-Supervision, OSC/EOF EP planner were notified. Recommended modifications to the process.
391259 | CR | 20190320 |  | 3 | PPM 11.2.9.32 need engineering review of sensitive equipment |  |  |  | N | NO | <D> **** Detailed Description **** PPM 11.2.9.32 contains a list of sensitive plant equipment in an attachment. The telemetry devices used by Radiation Protection are not to be used within 3 ft of this equipment. This list appears to be unchanged since 2009, and there is at least one system (PRM) that has been deactivated and could be removed from this list. Recommend an assignment to determine if new exclusion zones have been established since 2009. <I> **** Actions Taken **** Notified Design Engineering and RP Supervision
391261 | CR | 20190320 | CAQ | B | GNF Fuel Bundle Inspection Report | N | N |  | N | YES | <C> RISK: Medium. CAUSE: Uncertain/Complex. Close to CR 390812; Action needed in 390812 to address this issue. <D> **** Detailed Description **** Report indicated that there was significant damage to all spacers on bundles YLX137 and YLX130. In addition, it was noted that one lock tab washer on the upper tie-plate for bundle YLX130 exceeded as built tolerance. During final inspection, all bundles are subject to a comb gage inspection to verify rod-to-rod clearances. Both bundles were inspected utilizing the comb gage and the gage could not be inserted in several of the bundle sections. In Bundle YLX130 a cluster separator was found broken (packaging material inserted in the bundle). The damage to the fuel bundle spacers indicates that the fuel pellets were subjected to unknown and abnormal forces. Chipped fuel pellets can lead to pellet-cladding interaction fuel failures during the next cycle. Inspection of the pellets would require a bundle tear down and cutting open each fuel rod. Due to the lack of time, a bundle tear down and dismantling of the fuel rods was not performed. Based on the spacer damage GNF, Energy Northwest, and an outside Fuel Expert conservatively recommended completely rebuilding two new bundles instead of using the existing fuel rods in the dropped bundles. See attached Fuel Inspection Report from GNF attached in EDMS See Pictures attached <I> **** Actions Taken **** Bundles sent back to manufacturer for replacement <N> **** Equipment Description **** New Fuel Bundle ***General Notes*** This issue is being evaluated under CR# 390812. This CR should be screened as a CAQ B due to the following critieria Cause is considered clear due to the event investigation identifying that individuals involved in the event were content with substandard conditions associated with ice on the fork lift forks, and breaks not functioning well on the fork lift. The brakes associated with the green clark fork lift is a long standing issue that was never corrected. Complaceny was also identified as a contributing cause. corrective actions being taken are the following. 1) all a new fork lift is in the process of being rented for the rest of the New Fuel Reciept campaign. the fork lift involved will be inspected, and fixed as needed. Fuel will be inspected by GNF as soon as a plan is completed. individuals involved in the event were sent to Fitness for duty. A station stand down has been submitted. Further corrective actions will be conducted pending the event inviestigation completion and potential causal evaluation recomendations. CR# 391261 should be closed to all actions being performed under CR# 390812. an assignment has been created under CR# 390812 to address this issue per SWP-CAP-01. This has been approved by the Maintenance manager
391263 | CR | 20190320 | CAQ | D | Siren C2 intermittent com failure | N | Y |  | N | YES | <D> **** Detailed Description **** During the weekly siren pol test C2 intermittently failed to respond. Further testing throughout the day showed no problems. All surrounding sirens showed no sign of any problems. <I> **** Actions Taken **** Retested thoughtout the day with no probems. Notified EP. Recommmend closing to the WR. <N> **** Equipment Description **** Franklin county at site #C2
391264 | CR | 20190320 | CAQ | D | SEC-IDS-20 Not functioning as intended | N | N |  | N | YES | <D> **** Detailed Description **** CAS recieved multiple alarms on IDS 20. CAS operators could not verify what caused the alarms via CCTV or after a physical walkdown of the zone was completed. The cause of the alarm activity is unknown. <I> **** Actions Taken **** Compensatory measures were posted. A walkdown of the zone was conducted. Security Management and Electrical Maintenance were notified. CR/WR was generated. <N> **** Equipment Description **** IDS 20 | 02-00-SEC-IDS-E/S/20/21
391265 | CR | 20190320 | CAQ | C | CVI drawing 02C34-04,3,1 editorial |  |  |  | N | NO | <D> **** Detailed Description **** CVI drawing 02C34-04,3,1 incorrectly shows RFW-RMS-S2 being used to select between the signals from RFW-DPT-4A and RFW-DPT-4B (Ch. A or Ch. B level control signals). It is in fact RFW-RMS-S1 that performs this function (ref. EWD -72E-073). The drawing should be corrected. | 02-00-RFW-RMS-S1,02-00-RFW-RMS-S2
391267 | CR | 20190320 | CAQ | C | DURING DG-2 START FOR PMT, RECEIVED "DC FUEL PUMP FAILURE" | Y | N |  | N | YES | <D> **** Detailed Description **** DURING DG-2 START FOR PMT, RECEIVED "DC FUEL PUMP FAILURE" ALARM. . CAT ID 0068700072 . Reference Work Order numbers: 02136006 & 02136007 <I> **** Actions Taken **** Initiate CR, contacted operations, contacted OCC. After the engine was taken to 110% rated speed the "DC FUEL PUMP FAILURE" alarm cleared. PMT's were performed at 110% rated speed and tested SAT with alarms clearing after initiation. <N> **** Equipment Description **** DG-2 . DC fuel pump failure alarm cleared at rated speed not 110% of rated speed, the DG was not operated above 900 rpm, 60Hz. | 02-00-DO-PS-5B1,02-00-DO-PS-5B2
391268 | CR | 20190320 | CAQ | C | REA-RE-609D FAILED | Y | N |  | N | YES | <D> **** Detailed Description **** While performing ISP-REA/PRM-X304 step 7.10.3 RESTORATION part it was noticed that the RIS didnâ€™t indicate field counts (detector not reading). This indicates a failed detector. Due to the detector not reading in OPERATE the RC-2 remains locked in. <I> **** Actions Taken **** Expanded the team and notified CRS, SM, and supervision to implement a plan to bring channel back to service. | 02-00-REA-RE-9D
391269 | CR | 20190320 |  | 3 | NET4-COMP-EPO Write-Cache battery failure | N | N |  | N | YES | <D> **** Detailed Description **** While performing reboots in support of maintenance to resolve iLO issues (CR 389349), NET4-COMP-EPO was found to have multiple errors at the bios screen. Most were iLO related, but there was one critical error for the write -cache battery (HP Smart Storage Battery 1 Failure). This is preventing the server from booting up and needs to be replaced. . This does not impact Operations, the server only performs Cyber Security functions. This is not a reportable condition. . Recommend as a 3 to Computer Engineering. <I> **** Actions Taken **** Generated CR, notified SM and Cyber Security. | 02-00-NET4-COMP-EPO
391270 | CR | 20190320 | CAQ | D | REA-RE-9D HI-HI alarm out of tolerance | Y | N |  | N | YES | <D> **** Detailed Description **** While performing ISP-REA/PRM-X304 step 7.2.15 taking the as found reading for the HI-HI alarm. The range (7.60 to 7.78) with the set point of 7.78 the alarm came in at 7.80. <I> **** Actions Taken **** Procedure directs us to inform CRS (operations) about the alarm being out of tolerance.
391271 | CR | 20190320 | CAQ | C | LCS required surveillance completed without SRO review |  |  |  | N | NO | <C> CR (391271) Priority and Severity changed to CAQ C at the request of MRT on 3.25.2019 Quality affecting program noncompliance. Ensure SWP-CAP-01 is followed regarding C level CRs. <D> **** Detailed Description **** ISP-SEIS-M202 performed under WO 02137540 was taked to finished status with out an SRO review. It appears that the surveillance never went to Hold for OPS. <I> **** Actions Taken **** Review surveillance . Verified ISP-SEIS-M202 was reviewed by an SRO.
391272 | CR | 20190320 |  | 4 | Trainees failed Cycle 19-2 NLO exam |  |  |  | N | NO | <D> **** Detailed Description **** Two Non-Licensed Operators failed the 19-2 NLO training cycle exam. At the discretion of line managment.Per TDI -02, qualifications were not revoked after reviewing the exams and the individual PQD records. One individual did not hold any watch station qualifications. A review of the exam from the other operator determined the failure was due to lack of attention to detail an not a knowledge gap. <I> **** Actions Taken **** Crew managment was informed of the failure and remediation plans were developed, which are pending approval
391273 | CR | 20190321 | CAQ | D | TDAS MUX 3 failed | N | Y |  | N | YES | <D> **** Detailed Description **** TDAS MUX 3 failed. This affects 2 ERDS points (X118 and X122) and several GDS inputs <I> **** Actions Taken **** informed CRS/SM. Comp measure established per PPM 13.14.11 to manually transmit ERDS data. | 02-00-TDAS-MUX-3
391274 | CR | 20190321 |  | 4 | Inadequate Communication Between Work Groups |  |  |  | N | NO | <D> **** Detailed Description **** DG2 was INOPERABLE for planned maintenance with the DG2 room de-vitalized to allow access and egress through the south door (D-DOOR-D102). Prior to declaring DG2 OPERABLE the SM needed to communicate with the Security Lieutenant to arrange for appropriate compensatory measures. Security was not given the expected heads-up by the SM per the 10-30 -60 minute rule. <I> **** Actions Taken **** Discussed with OCC and Security. Comp measures were put in place.
391275 | CR | 20190321 |  | 3 | Significant increase in GA dose rates at ARM-RIS-29 | N | N |  | N | YES | <D> **** Detailed Description **** Dose rates at ARM-RIS-29, have increased from 20mR/hr to 60mR/hr in the last 24hr period. ARM is located on RW 437 behind shield adjacent to RWCU-P-29. Possible cause of increase is RWCU resin being present in piping from tranfer after failure of RWCU-P-28. <I> **** Actions Taken **** informed Shift Manager <N> **** Equipment Description **** rw 437 behind shield wall Dose rates are elevated due to plant operations and delayed resin processing. Troubleshooting is in progress and dose rates will be evaluated again when system is restored to normal operation. CR is being closed with the approval of the RP Operations Supervisor. | 02-00-ARM-RIS-29
391278 | CR | 20190321 | CAQ | D | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0066200 Ashcroft Gauge 300psi found OOT & adjusted within specs. EFIN Eval: WO #02100980-01 Actual pressure greater than indicated pressure. This is conservative for this application. No Impact. DEF #6967A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391279 | CR | 20190321 | CAQ | C | E-CB-DG2/8 charging springs didn't discharge when racked out | Y | N |  | N | YES | <D> **** Detailed Description **** The charging springs didn't discharge while racking out E-CB-DG2/8 per SOP-ELEC-BKR-OPS step 5.20.12. The breaker is currently removed from the cubicle and strapped to white iron in the DG-2 Room. We didn't manually discharge the springs. <I> **** Actions Taken **** Wrote this CR and WR. Notified Field Supervisor | 02-00-E-CB-DG2/8
391280 | CR | 20190321 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065243 Fluke Thermocouple Probe- model 80T-150UA found OOT & adjusted within specs. Not used during Calibration cycle. DEF #6973A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391281 | CR | 20190321 | CAQ | D | threaded pipe union downstream from SW-V-196 leaks | Y | N |  | N | YES | <D> **** Detailed Description **** threaded pipe union downstream from SW-V-196 leaks. Attempted to tighten but it only seemed to make it worse. | 02-00-SW-V-196
391282 | CR | 20190321 |  | 3 | Addition of Seismic Monitoring reading to CRO3 logs |  |  |  | N | NO | <D> **** Detailed Description **** A new reading to perform shiftly checks of the Seismic Monitoring System LEDs is required. Recommended wording for reading has been added to EDMS folder. <I> **** Actions Taken **** Initiated CR.
391284 | CR | 20190321 |  | 4 | 2 Pieces of M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** 2 Pieces of M&TE were NOT used and are now Rejected- Unable to adjust. Calcode #31972 King Temp. Calibrator- model 3605. DEF #6970A addressed an OOT on 3/8/19. DEF #6974A written for the Rejection. Calcode #39536 Starrett Vernier Caliper- model 123Z-12. DEF #6975A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391285 | CR | 20190321 | CAQ | C | M783 has incorrect information. |  |  |  | N | NO | <D> **** Detailed Description **** Drawing M783 is a TOP TIER drawing and it has some incorrect information. The makeup and instrument stream is shown to be a 100 psig header when in fact it is a 110 psig header. Please investigate and correct. See marked up drawing in EDMS. <I> **** Actions Taken **** Informed instructors and generated this AR/CR.
391287 | CR | 20190321 |  | 3 | Minor enhancement to SOP-MT-START |  |  |  | N | NO | <D> **** Detailed Description **** SOP-MT-START could use a minor enhancement in the form of a note enhancement to indicate a potential expected alarm. Step 5.5.20 and 5.5.21 could have a note added that give the operator the information as follows; Note: After the Sync switch is placed into Auto P800-C4 drop 10-1 500Kv Sync incomplete may alarm if the breaker is not closed within 3 minutes. <I> **** Actions Taken **** Discussed this with other operators.
391290 | CR | 20190321 |  | 3 | OI-75 Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Remove the requirement to record all ODQRB scores in Portal J (step 3.3.3); only the exceptional scores (1, 2,& 5) will be recorded in Portal J.
391292 | CR | 20190321 |  | 4 | GSB Main Lunch Room Filtered Hot Water Very Low Flow | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** GSB Main Lunch Room . Filtered Hot Water has very low flow. Possibly needs filters changed. <I> **** Actions Taken **** HP Lead Tech Notified CR/WR Initiated <N> **** Equipment Description **** GSB Main Lunch Room
391294 | CR | 20190321 | CAQ | D | E-CB-DG2/8 breaker closed indicating bulb broken | Y | N |  | N | YES | <D> **** Detailed Description **** On 3/21/19 during recovery of DG2 following maintenance the red (closed) indication light bulb on the door of the breaker cubical broke off in the socket. WR needed to replace bulb or socket as needed. <I> **** Actions Taken **** Wrote CR/WR to repair. Contacted OCC ops rep and FIN. | 02-00-E-CB-DG2/8
391296 | CR | 20190321 |  | 3 | PPM 1.5.13 Section 4.1, step 4.1.2 is Counter Productive |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.5.13 Preventive Maintenance Optimization Living Program has a step that hurts station Preventive Maintenance Program and can have schedule adherence impacts, planning impacts, and the right information at the right time impacts. The step dictates that AR-SMS requesting PMs or PM changes cannot be initiated until it can be processed in Asset Suite. For upcoming scheduled modifications, that will be implemented, this forces Engineering to create an action, which may or may not be completed in a timely manner or have the right information due to turnovers, or people changing jobs. In addition, the rest of the plant may not be aware a PM is needed for a certain component, until the AR-SMS is created at a later date and it's actual due date passess or scheduled in such a manner it requires resource allocation in order to perform. Commited mods which will be installed, and have a vendor recommended preventive maintenance must be initiated prior to mod implementation in order for the station to review/approve maintenance, schedule, plan and allocate resources to support preventinve maintenance. This also allows maintenance or engineering to assess if training is needed. This step in the procedure, does not help the station. It masks needed reviews by multiple departments and has an indirect impact on future PM implementations. Recommend to re-assess step, to allow AR-SMS on mods which are currently locked-in to be installed on the schedule after T-7 process (WO must have a schedule implementation date) . <I> **** Actions Taken **** Discussed with Supervisor and notified PM Program Coordinator the step in the procedure does not help the station.
391297 | CR | 20190321 |  | 3 | PPM 10.25.95 enhancements |  |  |  | N | NO | <D> **** Detailed Description **** Revise PPM 10.25.95 to provide better guidance for measuring the main generator shaft potential and ground brush currents. A marked up copy of the recommended changes was placed in the EDMS tab. <I> **** Actions Taken **** Initiated CR for procedure change <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
391298 | CR | 20190321 |  | 4 | FO-TK-1 below minimum spec of 90 inches | N | N |  | N | NO | <C> CR 391298 reassigned to Severity 4 at the request of MRT on 3.26.2019. <D> **** Detailed Description **** FO-TK-1 is below minimum specification. Tank level is approximately 85 inches. The low specification is 90 inches. <N> DG Fuel order has been placed for delivery 3/27/19 Ref MR 00243697
391300 | CR | 20190321 |  | 4 | Received Circ blowdown rad high (H13-P602.A5 3-6) due to wel | N | Y |  | N | YES | <D> **** Detailed Description **** Received Circ blowdown rad high alarm, this was due to CBD-RIS-608 spiking above 10,000 CPS. CIRC water blow down was secured and the control switch was taken to close. Sent OPS 4 to circ water pumphouse and reported that there was welding occurring at the halogenation skid. Normal values are 20-25 CPS. Alarm setpoint is 180 CPS. Work control should identify any welding activities at CWPH and inform the control room of the activity, so blowdown can be secured. | 02-00-CBD-RIS-608
391301 | CR | 20190321 | CAQ | D | Timing relay adverse trend | Y | Y |  | N | YES | <D> **** Detailed Description **** E-RLY-RHRB/62/2 was put into service on 6/8/13 and has been found out of calibration during every test since. The relay is calibrated every 2 years by PMID 17636-01 and was found out of tolerance in 2015, 2017, and 2019. For each test, the relay as found time was outside of the LCS range (18.74 to 20.03 seconds) but within the TS range (17.24 to 21.53 seconds). Additionally, the relay is timed during performance of TSP-DG2/LOCA-B501 and was found to be outside of the Tech Spec range during the 2017 test. At each performance, the relay was adjusted into tolerance. Based on this trend, it is recommended the relay be replaced during the next calibration surveillance, due in January 2021. As the relay has not been found outside of the Tech Spec range during a calibration, it is deemed acceptable to leave it in service until that time. | 02-00-E-RLY-RHRB/62/2
391304 | CR | 20190321 |  | 3 | (Non EN/CGS) Commercial Customer Calibration |  |  |  | N | NO | <D> **** Detailed Description **** (Non EN/CGS) Customer indicated that their item was returned back calibrated, but the item lost location and strayed repeatedly when being used. Asset# KAI-M-015 <I> **** Actions Taken **** Sent Calibration information and customer email to Standards Laboratory Management to review and provide a response to customer based on investigation. I let customer know that his complaing was being reviewed and supervisor or myself would get back with him once we have an answer back about results on what is found. Initiated customer complaint #182.
391305 | CR | 20190321 |  | 3 | [NRC] Observation on manual seismic data |  |  |  | N | NO | <D> **** Detailed Description **** The NRC shared the following observation. If there was a failure of the seismic motion recorder during a seismic event, the station would be tasked to perform an OBE determination evaluation manually. The new seismic system saves all data on memory chips even if the recorder has failed. The NRC inspector suggested an enhancement to develop guidance to manually retrieve and read the data.
391306 | CR | 20190321 |  | 3 | Clarify LLRT procedure PPM 8.3.453 requirements |  |  |  | N | NO | <D> **** Detailed Description **** PPM 8.3.453 allows for evaluating opening a WIC permit when performing procedure. However, step 7.1.5 in body infers a permit is required. This is not accurate. A permit can be opened but is not always required. Step 7.1.5 should say "evaluated per PPM 3.4.1 vice "open" permit . This aligns with previous step 3.8 to evaluate the isolation logic operability. <I> **** Actions Taken **** CR written
391307 | CR | 20190321 | CAQ | D | Rod Accumulator Trouble CRD-HCU-1011 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble, H13-P603, A7.6-7, alarm for CRD-HCU-1011. OPS-2 reports the cause of the alarm is high moisture level. OPS-2 has drained the accumulator per SOP-CRD-HCU and the alarm has cleared. <I> **** Actions Taken **** Informed CRS/SM | 02-00-CRD-HCU-1011
391308 | CR | 20190321 |  | 3 | [NRC] Does the SMS meet the intent of RG 1.12 rev. 2 |  |  |  | N | NO | <D> **** Detailed Description **** The NRC is questioning if the station is meeting the intent of RG 1.12 â€“ Nuclear Power Plant Instrumentation for Earthquakes (rev. 2), position 7. In the current configuration of the Seismic Monitoring Instrumentation, triggering the free-field sensor would not annunciate in the Control Room. The station needs to evaluate if having only foundation level sensor annunciation in the control room meets the requirements of RG 1.12 rev. 2 or if both are required. <N> This CR was reopened at the authors request as it was inadevertently cancelled.
391309 | CR | 20190321 |  | 3 | (Non EN/CGS) CC-181 Memorandum CCN297466 Received 20 Mar 19 |  |  |  | N | NO | <D> **** Detailed Description **** Customer (Non EN/CGS) BNI (CONTRACTOR) has performed a review, subject above, and found the requirements of NQA-1 2000 have not been sufficiently established directly in the QAM. Energy Northwest (EN) is requested to review BNI concerns addressed in the enclosed memorandum and revise the QAM to meet NQA-1 2000 requirements. (See attached Memo in EDMS) <I> **** Actions Taken **** Initiated CR and Customer Complaint CC-181 <N> Manager's approval received.
391310 | CR | 20190321 | CAQ | C | (NRC 2019 PI&R) CA not implemented as written |  |  |  | N | NO | <D> **** Detailed Description **** NRC observation: Corrective action 369479-01 was not implemented as written. Justification and approval for not completing the corrective action as written wasnâ€™t documented in the CR. <I> **** Actions Taken **** Recommend assignment to AR-RADPR.
391313 | CR | 20190321 | CAQ | D | Recieved low flow alarm for RRA-CC-17/SW-FS-44 | Y | Y |  | N | YES | <D> **** Detailed Description **** Performed OSP-SW-C102. OPS 2 reports that as found flow was 8.2 GPM which is above the requred value of 8 gpm. As left value was 13 gpm. OPS-SW-C102 has a QAR doc from 1-4-19. This alarm subsequently came in again with no changes is the system. SW-FS-44 may need to have the instrument line flushed to aleviate this problem as that the flushing of RRA-CC-17 seems inefective at correcting the issue. 02112149-22 looks like it may be the last time this switch was flushed. <I> **** Actions Taken **** Dispatched operator 2 times to flush the coil. Wrote this AR. | 02-00-SW-FS-44
391314 | CR | 20190321 |  | 3 | FM likely entered CBD pipe in CWPH | N | N |  | N | YES | <D> **** Detailed Description **** During the attempted removal and completion of the Hot Tap on the Angle tap on CBD(1)-1, it is likely the pilot bit entered the pipe. After opening the CL-V-102 valve to determine if the broken pilot bit could be seen, it was not evident that it was in the angle tap. The cutter portion of the broken tool was removed and again the angle tap was searched for the end of the pilot bit. The pilot bit was not seen nor felt when inserting tools to "feel" for the bit. <I> **** Actions Taken **** Work was stopped and supervisor was notified. Supervisor notified Operations and Engineering. The decision was made to continue with completion of the angle tap, the tap was completed and material (fines and cutter) collected from the angle tap. This possibility had been previously been reviewed in an OCC-3 and engineering evaluation. Recommend Delta Trend. <N> **** Equipment Description **** CBD(1)-1
391316 | CR | 20190321 | CAQ | D | MT-CRA-2 power indication light and illumination lights. | N | N |  | N | YES | <D> **** Detailed Description **** During performance of weekly MT-CRA-2 surveillance under WOT 02133978-01 craft identified the local power indication light (red) on the cab was not illuminated, and two of the 6 illumination lights (white) on the bottom of the crane bridge were also out. <I> **** Actions Taken **** Craft informed supervision of bulbs not illuminated. There was no issue with performance of MT-CRA-2 Interlock surveillance (MMP-HOI-C101) and all required interlock functions were met. | 02-00-MT-CRA-2
391318 | CR | 20190321 |  | 3 | Late eSOMS entries for Maintenance |  |  |  | N | NO | <D> **** Detailed Description **** On 3/1 an Electrician worked 14 hours when he was scheduled in eSOMS to work 12. On 3/19 an I&C tech started work at 0600 when he was scheduled to start at 0600. No violations occured when eSOMS was updated. <I> **** Actions Taken **** Updated eSOMS and notified shop managers of late entries
391319 | CR | 20190321 |  | 3 | Individual stepped onto plant equipment |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** A site visitor was observed stepping onto a pipe snubber and an angle support for a cable tray in the Reactor Building 548â€™ RHR A Heat Exchanger room. The individual was coached at the job site and Operations was informed. <I> **** Actions Taken **** Notified Operations <N> The individual was counselled in the field and there were no issues with equipment damage or operability of equipment in the area. No further actions needed.
391320 | CR | 20190321 |  | 3 | RPSA - Exposure records submittal delays to records center |  |  |  | N | NO | <D> **** Detailed Description **** RP Self-assessment - Exposure records have been kept in interim storage for over the past year awaiting the development of a dosimetry records center. The record center would allow a scan and toss program for exposure records. To minimize the level of re-work of record scanning and storage, early on it was decided that the records would be scanned and maintained in interim storage. Due to schedule delays and work priorities from the supporting work groups, the process has not been fully implemented. This has left exposure records in interim storage for over a year contrary to procedure HPI-6.4 <I> **** Actions Taken **** Notified RP Supervision See SA-00388465
391321 | CR | 20190321 | CAQ | C | RPSA - RP program records weakness |  |  |  | N | NO | <D> **** Detailed Description **** Self-assessment, SA-00388465, identified an overall weakness in RP records program that indicates a lack of focus that ranges from generation to transmittal to the records center. Review of RP program records from 2016 to 20x18 have been submitted with inaccurate information (both shipping and survey information) and records have been lost or become missing. Record duplications for submittal have been identified; some with varying revisions. Record submittal has been identified for incorrect processing request and resulted in misidentified DICs and storage. Confidential record submittal have occurred without proper identification. <I> **** Actions Taken **** Notified RP Supervision
391322 | CR | 20190321 |  | 3 | Universal Waste Management Not Meeting Requirements |  |  |  | N | NO | <D> **** Detailed Description **** During walkdown of the Universal Waste Storage area located in the machine shop next to the GSB, several deficiencies were discovered. A partial box of broken fluorescent lamps were discovered stored in the area. A container of universal lamps was found without a label. This condition is not meeting requirements in GBP-ENV-17 for managing universal waste. The area could use improvements with housekeeping. Full containers of universal waste should be transferred to the warehouse for disposal and containers should be stored standing in the upright position. <I> **** Actions Taken **** If E&RP was aware of the broken bulbs, they could have been included in a shipment of hazardous waste which happened early in the day, reducing waste disposal cost. Discussed issue with E&RP Manager and notified electric shop. Broken bulbs were taken to Bldg. 117 for proper accumulation.
391323 | CR | 20190321 | CAQ | C | E-CB-DG2/8 bent frame during rack-out | Y | N |  | N | I DONT KNOW | <C> CR reopened and assigned CAQ C/OPSST at operations manager request <D> **** Detailed Description **** E-CB-DG2/8 became bent on the upper/right corner as it was being racked out. As a follow up to CR 391279, where the charging spring didn't discharge as it was supposed to when racked out, Electricians made adjustment to the tripper levers per WO# 02140631. After adjustments were made, OPS racked the breaker in and charged the spring electrically. The fuses were then removed and OPS crew attempted to rack the breaker back out to verify the springs would trip as designed. The breaker appeared to "hang up" and made a loud percussion sound. With verbal direction, the Equipment Operator continued racking the breaker out to the "test " position, where the charging spring did discharge as designed. Upon further inspection of the breaker and cubicle, we noticed some minor damage that appears to have been caused by friction between the breaker cover, and the upper right cubicle <I> **** Actions Taken **** Write CR and WR and upload pictures to EDMS library <N> **** Equipment Description **** DG 2 E-CB-DG2/8
391324 | CR | 20190321 |  | 4 | RX 522' South Pipe Space has NO LIGHTING |  |  |  | N | NO | <D> **** Detailed Description **** -RX 522' South Pipe Space needs Relamped. It is a High Radiation Area. <I> **** Actions Taken **** -Notified Supervision -Initiated CR & WR. <N> **** Equipment Description **** RX 522' South Pipe Space
391325 | CR | 20190321 | CAQ | D | REA-RE-9D field cable connector needs to be replaced | Y | N |  | N | YES | <D> **** Detailed Description **** AR 391268 was written to document the failure of REA-RE-9D. This is a repeat occurence, as the same failure occurred the last time the sureveillance was performed 18 months ago. The suspected cause of the repeat failuters is the cable connector at the detector. <I> **** Actions Taken **** A work order needs to be planned and scheduled to repair the connector. | 02-00-REA-RE-9D
391328 | CR | 20190321 |  | 4 | TOA-TIS-24A reading low, TOA-V-21A won't shut | N | N |  | N | YES | <D> **** Detailed Description **** TOA-TIS-24A was reading GT 20F lower than outside temp, and TOA-V-21A was open. CRS permission was obtained to place TOA-V-21A in close, however the valve remained open with TOA-RMS-21A in close. Recommend investigate, repair, replace as necessary. <I> **** Actions Taken **** Informed CRS, attempted to close TOA-V-21A, generated AR/WR. | 02-00-TOA-RMS-21A,02-00-TOA-TIS-24A,02-00-TOA-V-21A
391329 | CR | 20190321 | CAQ | D | TG BLDG 441' Center Area Fire Alarm FCP-1 (1-2) | N | N |  | N | YES | <D> **** Detailed Description **** FCP-1 drop 1-2 TG BLDG 441â€™ CENTER AREA CONDSR/EQUIP RMS fire alarm is locked-in. Investigation revealed no evidence of a fire. Thermal Detector FP-THD-2/10 appears to be in alarm. This detector is located in the â€˜Bâ€™ SJAE room on TG 441â€™ at coordinates F.5/12.5. This SJAE is not currently in service. No evidence of a steam leak identified. <I> **** Actions Taken **** Notifed the CRS and SM. Fire Brigade and OPS 3 inspected covered area for evidence of fire - with no evidence found. | 02-00-FP-THD-2/10
391330 | CR | 20190321 |  | 3 | Windows Server Patching Caused Unexpected Restarts |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Issue: The Microsoft patch deployment for 3/21/19 scheduled for 9 PM restarted many of the Windows servers automatically. The maintenance window was scheduled for 10:30 PM. Reviewed SCCM deployment, forced suppress reboot, and forced servers to re-check in. Recommend NON-CAQ 3 <I> **** Actions Taken **** Notified IS Duty Officer. Notified Application Analyst to help verify impacted systems. . SM contacted IS to cancel the scheduled LAN outage at ~21:15 due to the ongoing DG2 outage.
391331 | CR | 20190322 | CAQ | D | E-BU-W525/4 is flashing red failure lights | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-525/4 is flashing red failure lights. the sequence is 3 red lights which according to the legend is charger failure. | 02-00-E-BU-W525/4
391332 | CR | 20190322 |  | 3 | Data Glance tablet icons went away and not saving. |  |  |  | N | NO | <D> **** Detailed Description **** when changing from airplane mode to wifi the icons to refresh, syc, MTE, field work complete etc all went away and was no longer updating data glance. <I> **** Actions Taken **** filled out a paper copy before data was lost scanned it in forced checked in the package and opened it up on a anouther tablet. The data was lost but we were able to take the package to finished
391334 | CR | 20190322 | CAQ | D | C-408 Emergency Egress | N | Y |  | N | YES | <D> **** Detailed Description **** CAS recieved multiple alarms displaying that the C-408 emergency egress had been activated. It was verified that emergency egress had not been activated and C-408 functions as intended. Call 2185 for futher details. <I> **** Actions Taken **** A successful operability test and multiple walk throughs were perfomed on C-408 to verify functionality. Shift Manager, Security Mangagement, and Electical Maintenance were notified. CR/WR generated. <N> **** Equipment Description **** C-408 Main Control Room Door
391335 | CR | 20190322 | CAQ | D | DG-ENG-1B2 standby oil level is 1/16' high OOS. | Y | N |  | N | YES | <D> **** Detailed Description **** DG-2 south engine oil level is 1/16" above the high mark .The max. spec is miniscus at the high mark. The operabillity is not in question since the max spec. is 3/16 above the high mark. Per the OPS-2 logs, please restore oil level to normal. <I> **** Actions Taken **** Notified supervisor/CRS. <N> **** Equipment Description **** DG-2 | 02-00-DG-ENG-1B2
391336 | CR | 20190322 |  | 4 | E-MH-E1B Check french Drain | N | N |  | N | YES | <D> **** Detailed Description **** Working 02108117-01 found water to be above 12". second inspection still had water present. <I> **** Actions Taken **** Contacted Engineer , Due to Snow melting / Drainage slow, recheck for water mid april if no water present , no further action required. | 02-00-E-MH-E1B
391337 | CR | 20190322 | CAQ | B | SW-V-2B failed to open during start of SW-P-1B | Y | N |  | N | YES | <C> RISK: Medium. CAUSE: Uncertain/Complex. Investigation Template Required. <D> **** Detailed Description **** SW-V-2B failed to open during start of SW-P-1B for performance of OSP-SW/IST-Q702. SW-V-2B will open only when switch was held in open with SW-P-1B running. When SW-V-2B switch was released, SW-V-2B went closed. SW-P-1B was turned OFF and SW-V-12B had to be manually closed. Entered ABN Breaker Fault and ABN SW. Recieved SW-P-1B Motor trip with the pump running as well. <I> **** Actions Taken **** Informed CRS/SM. OI-34 notifications. <N> Per SWP-CAP-06 this event is determined to be MEDIUM risk. Cause of the change in MOC pin drive force is uncertain at this time. Recommend Severity "B" with an EQIT. | 02-00-SW-V-2B
391338 | CR | 20190322 |  | 3 | 11.2.13.1, revision to relax survey of Common Carriers shipm |  |  |  | N | NO | <D> 11.2.13.1, Radiation and Contamination Surveys, Procedure should be revised to align with 11.2.14.2, Receipt of Radioactive material. 11.2.13.1, Radiation and Contamination Surveys, Step 5.10.1 States that all Radioactive Shipments require surveys of transport vehicles. While, 11.2.14.2, Receipt of Radioactive material, Steps 3.7, 4.2.3, 4.2.4, 4.2.5, and 4.3.1 designate exclusive use shipments as requiring vehicle surveys. This procedure rightly has no regulatory limit for common carrier vehicle therefor a survey of this type of shipment is unnecessary. The package survey is all that is required. <I> Presented argument about this unnecessary work to Qualified Rad Shipper and HP Supervision. Wrote CR. . Found at INPROG, moved on to APPROVED.
391339 | CR | 20190322 |  | 3 | Cal Code 0068382 Out of Calibration |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** ASTRO-MED UNIV-6, TMX-18 INPUT MODULE Cal Code 0068382 cal due date: 3/9/2019 not returned for calibration. Found Astro-Med UNIV-6 input card (asset # 0068382) that was transferred to us on 2-26-19 was not received with the TMX-18 base unit. A different card (asset # 0066963 Cal due 6/27/2019), an Astro-Med IHVM-6B was in the chassis of the base unit in its place. 0066963, was previously used with the Astro-med TMX-18 base unit listed below: (0065958). Appears the cards were swapped in the field and not returned to the base unit. Cards are calibrated individually and not specifically required to be paired to a specific TMX-18 base unit. It could be used in the field inadvertently. Recommend assign to Mech Shop (org. 52233) <I> **** Actions Taken **** Generated CR, notified supervisor.
391340 | CR | 20190322 |  | 3 | SCC Hanford Fire radio channel not functioning as intended | N | N |  | N | YES | <D> **** Detailed Description **** The SCC's Hanford Fire radio channel is reciving a good signal but it is not transmitting as intended. Call 8065 for further information. <I> **** Actions Taken **** Notified Hanford Fire, Information Services, Security Management and Shift Manager. Generated CR <N> **** Equipment Description **** SCC
391341 | CR | 20190322 | CAQ | C | Calibration of WMA-TS-8A2 | Y | Y |  | N | YES | <D> **** Detailed Description **** During calibration of WMA-TS-8A2 per 02132472, TS could not be calibrated, ordered new TS CATID 60111121 SN A782084-003 and new switch would not calibrate on side 1 or side 2, ordered a second new switch SN A782084-004, and side one would not calibrate but did calibrate on side 2, the second new switch SN A782084-004 did calibrate on side 2, will install new switch using side 2 SN A782084-004 per engineering direction <I> **** Actions Taken **** Ordered new switch for replacement, calibrated side 2 of new switch, received permission from engineering to use side 2 of new switch, new switch will be installed per 02132472 . Based upon PPI ENG DES-2-8 Attachment 10.3 screening, Engineering concluded that the change from side 1 to side 2 for replacement of WMA-TS-8A2 using CID 60111121 SN A782084-004 (UTC 523488) was acceptable and that document updates may follow the maintenance activity using the ADOC process. The CID 60111121 SN A782084-003 new temperature switch from the warehouse that could not be calibrated should be quarantined and returned to ASCO for forensic investigation. The previously installed temperature switch removed from WMA-TS-8A2 (SN A782084-002) should also be quarantined and sent to a thrd party for forensic investigation. Recommend resolution by System Engineering. . SWP-DOC-01 redline mnr rev 001 for AED EWD-84E-050 rev 5 was prepared and taken to the Main Control Room. <N> **** Equipment Description **** W 467 vital island BATT rm #2 C-217 | 02-00-WMA-TS-8A2
391343 | CR | 20190322 | CAQ | D | B5b-P-1 tire pressures low out of spec | N | Y |  | N | YES | <D> **** Detailed Description **** B5B-P-1 has multiple tires that are slightly low on air pressure (~ 95#, with a low limit of 100#). The staged air compressor in Bldg. 600 has a broken ON/OFF switch and could not be used to fill the tires. Please repair/replace the Bldg. 600 air compressor. The compressor in question belongs to the Facilities Auto Shop. Note: Key M208 is required for entry into bldg. 600. This key can be checked out from the SSS office. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** Bldg. 600. Key M208 required for entry. | 02-00-B5B-P-1
391344 | CR | 20190322 |  | 3 | WO 01148474 (B5B-P-1) change required |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Model WO 01148474 requires a change to step 4.24. Step 4.24 requires the Air compressor to be plugged in; however, the onboard air compressor is not used for B5B-P-1. Please remove the step to plug in the Air compressor. See PPM 15.1.29 for verification that air compressor is not required to be plugged in for B5b-P-1. <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** WO 01148474 . Model WO 01148474 was revised to include the wording "If needed" at step 4.24. THis is consistent with 15.1.29 step 7.4.41. Also updated the future generated PM work order tasks. No further actions are needed.
391345 | CR | 20190322 | CAQ | D | Blue dot lighting needs replaced | N | N |  | N | NO | <D> **** Detailed Description **** Blue dot lighting in the RB NW stairwell between the 471 and 441 elevations needs to be replaced - flickering badly. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** Blue dot lighting RB NW stairwell between 471 and 441
391346 | CR | 20190322 |  | 3 | Procedure Update Request SOP-DG-DCW |  |  |  | N | NO | <D> **** Detailed Description **** A note should be added before step 5.1.1 in section 5.1 of SOP-DG-DCW that this procedure requires two individuals to complete, as the valve/LS for each diesel is on the opposite side of the tank as the level gauge. <I> **** Actions Taken **** Initiated CR.
391347 | CR | 20190323 | CAQ | D | Adjust Sure Close Mechanism on Removed SW-CB-P1B | Y | N |  | N | YES | <D> **** Detailed Description **** While performing PPM 10.25.105 in WO #02140678, MOC Pin Pull Force was in the low band of the acceptable criteria. <I> **** Actions Taken **** Craft notified supervision, OCC and EOC, new task was created to adjust the Sure Close Mechanism per PPM 10.25.105 step 7.8.8 <R> REP/REGE assignments are being performed under CR 391337. These REP/REGE assignments have been cancelled. | 02-00-SW-CB-P1B
391351 | CR | 20190323 |  | 4 | PWC-P-102 abnormal noise and shaft movement | N | N |  | N | YES | <D> **** Detailed Description **** PWC-P-102 is making an abnormal noise and there is slight movement of the shaft in the inward and outward direction. PWC-P-102 has previously been written up for abnormal packing leakage. WR# 29147340 identified that no further packing adjustment is left. The repair of this pump should be prioritized, as PWC-P-103 (the sister pump) is also in a degraded condition (ref. WR# 29144483), due to a broken suction valve. PWC-P-102 and PWC-P-103 provide pressure to the PW ring header. A 2A SM key is required for entry into the PWC-P-102 and 103 bldg. See EDMS for short video <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** Bldg. 40 . 2A SM key required for entry. | 02-00-PWC-P-102
391352 | CR | 20190323 |  | 3 | TS 3.8.1.B.3.1 Position Paper | Y | N |  | N | NO | <D> **** Detailed Description **** Request licensing document a position paper relative to the scope of support systems needed to be addressed under TS 3.8.1.B.3.1 and 3.8.1.B.3.2 for common mode failure analysis with a DG Inoperable or running other DGs within 24 hrs. Having a position paper would support SROs with application of TS when assessing operability issues with DG and DG support systems ensuring a consistent application. Examples of support system failures and whether inside the scope or not would be appropriate. For example, if PRA -FN-1A failed then SW-P-1A is required to be declared Inoperable as well as DG-1. Would a common mode failure analysis be appropriate in this example to satisfy TS?
391353 | CR | 20190323 |  | 4 | Cathodic System Loss of DC alarm in. | N | N |  | N | YES | <D> **** Detailed Description **** P821 board W drop 6-4 Cathodic System Loss of DC at Well No. 2 Pumphouse. <I> **** Actions Taken **** Ops 4 investigated and found CP-RECT-DW2 reads 30 volts and 7 amps. Wrote CR. 00391353 | 02-00-CP-RECT-DW2
391354 | CR | 20190323 | CAQ | D | CRD-HCU-1803 Rod Accumulator Trouble High Water Level | Y | N |  | N | YES | <D> **** Detailed Description **** Received "Rod Accumulator Trouble" alarm on CRD-HCU-1803. Ops2 reports the alarm is due to high water level; that he has drained the water, and the alarm is clear. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RB 522' | 02-00-CRD-HCU-1803
391355 | CR | 20190323 |  | 3 | Procedure enhancement OSP-SW/IST-Q702 |  |  |  | N | NO | <D> **** Detailed Description **** Step 7.3.50 of OSP-SW/IST-Q702 only applies during performance of CPT. Request following statement be added to 7.3.50 "N/A if CPT not performed"
391356 | CR | 20190324 |  | 4 | TSW-TC-11 (MG Exciter) indicated temp pegged high | N | N |  | N | YES | <D> **** Detailed Description **** TSW-TC-11 (MG Exciter) indicated temp is pegged high (GT 200F). The Auto Setpoint dial is set to 135F and the air output signal is 13 PSIG. TSW outlet temps for the Exciter were all indicating normally, at ~ 75 to 85F. This appears to be a controller indication issue only. TSW-TCV-11 appears to be in a normal, throttled, position. Please investigate/repair. <I> **** Actions Taken **** Informed MCR. Verified no abnormal Exciter temp alarms in MCR. Verified normal TSW outlet temps and normal position/ operation of TSW-TCV-11. <N> **** Equipment Description **** TG 501W | 02-00-TSW-TC-11
391357 | CR | 20190324 |  | 4 | e-TR-m2 cooler group 2 fan failed to start | N | N |  | N | YES | <D> **** Detailed Description **** e-TR-m2 cooler group 2 fan #4 failed to start. No overload trip present, motor contactor was found deenergized. Fan E-M-M2/F4 was restored per ABN -TRANSFORMER. AR# 00386517 was written for this same issue and was closed out with no action taken. As weather conditions become warmer this could become prevelant. <I> **** Actions Taken **** inform CRS , initiate AR and WR. | 02-00-E-M-M2/F4
391362 | CR | 20190324 |  | 4 | CL-TK-4 Level Indication Erratic Readings | N | N |  | N | YES | <D> **** Detailed Description **** Per OPS4 Logs there has been a slow downward trend consistent with normal usage. During the past four days level appears to be recording erratically between approx. 950 Gal down to approx. 500 Gal back up to 900 Gal and back down to approx. 400 Gal. Conferred with Chemistry and it is believed that Level Indication is malfunctioning. Special concern to be taken when receiving delivery of Sodium Bromide without an accurate tank level. <I> **** Actions Taken **** Spoke with Chemistry. Notified MCR. Initiated CR. | 02-00-CL-LI-4
391363 | CR | 20190324 |  | 3 | Error likely step in OSP-CCH/IST-M702 |  |  |  | N | NO | <D> **** Detailed Description **** page 21 has one single substep one line long and the rest of the page is blank. page 22 has the rest of the substeps for the same step that started on page 20. A single step and a mostly blank page could suggest that step / substep is that last one. This is a layout issue not a technical issue.
391364 | CR | 20190325 |  | 4 | DEH-MON-2 shows low disk space | N | N |  | N | YES | <D> **** Detailed Description **** A winodw pop-up indicates LOW DISK SPACE on DEH-MON-2 with additional information stating "you are running very low on disk space on LOCAL DRIVE (C:) To free space on this drive ..." <I> **** Actions Taken **** Notified CRS, initiated this CR/WR to free up disk space on the associated drive | 02-00-DEH-MON-2
391371 | CR | 20190325 | CAQ | C | W.O. package missing QC documents | N | N |  | N | NO | <D> **** Detailed Description **** Pre outage W.O. 02120897 -04 was printed and checked out, but is missing the necessary Q.C documents. <I> **** Actions Taken **** notified supervision and wrote CR
391380 | CR | 20190325 |  | 3 | Condensate Booster Motor UTC Serial No. do not match EC's | N | N |  | N | NO | <D> **** Detailed Description **** COND-M-P/2A-UTC 538493 does not match EC 16345 Serial No. COND-M-P/2B-UTC 538492 does not match EC 11527 Serial No.l EC 11527 for COND-M-P/2B and EC 4744 for COND-M-P/2C change to the new GE motors need to include the the first three letters of the serial numbers. Spare Condensate Booster Motor UTC 541368 does not have the correct serial number recorded. The new GE motors have two different serial numbers. EC 11527 for COND-M-P/2B and EC 4744 for COND-M-P/2C have been verified that the current recorded serial numbers match the motors that are installed in the plant. This is a documentation issue <I> **** Actions Taken **** Notified Supervision, Engineering and Warehouse of issue. Attached EDMS document with recommended actions to correct the issues.
391382 | CR | 20190325 |  | 3 | SOP-H2/CO2-OPS enhancement | N | N |  | N | NO | <D> **** Detailed Description **** SOP-H2/CO2-OPS has several cautions about not exceeding 3 psi when purging with CO2 to prevent CO2 from getting into the SCW system. This precaution is not necessary as the CO2 will not permeate the teflon hoses. Please remove the cautions about not exceeding 3 psig when purging as they conflict with section 5.19 which allows pressurizing with CO2 for leak inspections. <I> **** Actions Taken **** Discussed with OPS, initiated CR for procedure change
391383 | CR | 20190325 |  | 3 | CI-13.7 Gross Alpha Determination reqiures an enhancement | N | N |  | N | NO | <D> **** Detailed Description **** CI-13.7 Gross Alpha Determination procedures requires an enhancement. Step 6.13 references the use of a lab instrument that is no longer in use. <I> **** Actions Taken **** Contacted the appropriate chemistry personnel regarding the issue and wrote condition report.
391388 | CR | 20190325 |  | 3 | Dose saving suggestion: RCC-V-133A(B) operabilty | N | N |  | N | NO | <D> **** Detailed Description **** During the performance of OSP-FPC/IST-Q701, RCC-V-133A(B) operability is checked. These valve checks require 2 operators and 1-2 hours in the FPC HX room and they typically pick up 10-20 mrem every time we do these checks. Recommend evaluating if the frequency of these checks can be extended to 2 to 4 years. This would save time and a significant portion of the OPS dose received each year outside of the outage. Right now we get 50-100 mrem per year by performing these checks
391389 | CR | 20190325 |  | 3 | 11.2.9.12 Issued Rev does not load | N | N |  | N | NO | <D> **** Detailed Description **** When attempting to open the ISSUED Rev of 11.2.9.12 Rev 8 opens instead of Rev 8 Minor Rev2 which is the current Revision. Unable to retrieve the current revision at this time. <I> **** Actions Taken **** Initiate CR Notified HP Supervision <N> Found out the current Rev is on an old Procedure format. Procedure should be converted to the new format due to the Effective date on old procedure format does not match the Issue date in Portal J The old format did not contain minor revision numbers nor were dates updated on the files when doing an editorial. Procedure formats are updated as as a change is identified within the document. No further action is required. The background information was communicated with the originator.
391391 | CR | 20190325 |  | 3 | Motor for R-24 COND-M-P/2A Install not being PM'd | N | N |  | N | YES | <C> CR re-assigned to AR-RXMAINT at the request of Maintenance. <D> **** Detailed Description **** Two new condesate motors were delivered in 2015. PM 23590 performed on WO 02127099 on 10-25-18 was the first document that PM'd these motors. Both motors had their WOT instrucitons N/A'd because one of the motors was installed in the plant and the WOT instructions referenced bldg 74 but the motors were in bldg 188. Motor shafts have not been rotated quarterly as they should have and can lead to shaft sag and cupping of the bearings. Need the motor destined for COND-M-P/2A installation checked and tested prior to installation to assure equipment reliability for 14 years. <I> **** Actions Taken **** Contracted Supervision Contacted & Notified Component Engineer & Supervisor Contacted and notifed Electrician Supv & Mechanical Supervisor. CR 390818 reviewed | 02-00-COND-M-P/2A
391393 | CR | 20190325 | CAQ | C | Work order 02107551-03 RHR-V-4C lost weld record | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During the process of disbanding the WOPP and moving files to Records Management, a weld record for work order task 02107551 RHR-V-4C was lost. This document was created by Code Programs,and signed by QC and ANI, as evidenced by their respective hold codes (WR, QCI, ANI) being lifted, and and their respective review hold codes (CPR, QCR) being placed. These were placed in or around August of 2018. A search of the ex-WOPP area, the file cabinets transported to Records Management from the former WOPP area, all work order packages currently in the Valve Team's possesion and a query to QC did not result in finding the document. <I> **** Actions Taken **** Informed supervision, consulted with QC, conducted an extensive search for the missing document, and wrote this CR. <N> Weld record has been recreated, re-reviewed / re-signed by QC & AHII and given to affected work group for use.
391394 | CR | 20190325 |  | 3 | Water found in Electrical Vault B105 | N | N |  | N | YES | <D> **** Detailed Description **** During the inspection of Electrical vault B105 WO 02132638-01water was found to be over the 1â€™ depth tolerance and had touched/submersed the cables in the vault. The pump itself doesnâ€™t seem to be working. Another submersible pump will have to be utilized to remove the water for investigation and testing of the cables. <I> **** Actions Taken **** CR/WR generated and Engineering notified per work instructions <N> **** Equipment Description **** Electrical vault B105 inside the CWPH MCC room The submersible pump isnt pumping the water out
391397 | CR | 20190325 |  | 3 | Safety concern MT-CRA-4, not an operability issue |  |  |  | N | NO | <D> **** Detailed Description **** Need to purchase and attach truck/wheel bearing Zerk fitting extensions to MT-CRA-4. This crane isnâ€™t typical compared to our other cranes on site due to the grease point for bearings are located on the bottom side of the bearing block. This location required mechanics to hang outside of the handrail and pump grease to these bearings (half the time you canâ€™t even see if you are pumping grease into these fittings). Craft has suggested to run tubing from the fitting to a safe location on the catwalk handrail(s) â€œZerk grease fitting extenderâ€ this should not be a design change due to the existing Zerk fitting will still be in place (6 locations need extensions and 2 bearings already have extensions on them). <I> **** Actions Taken **** Wrote this CR <N> **** Equipment Description **** MT-CRA-4, GSB Crane
391398 | CR | 20190325 |  | 4 | OG Analyzer N2 Calibration Right Gas Bottle LOW | N | N |  | N | YES | <D> **** Detailed Description **** The Right OG Analyzer N2 Bottle is 200 psig which is below the min spec and needs to be replaced. This was last replaced on 1-17-19 per WR 29146540 <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** TB 441 | 02-00-OG-TK-RIGHT
391401 | CR | 20190326 | CAQ | C | Incorrect Closure of CR 390812 | N | N |  | N | NO | <D> **** Detailed Description **** CR 390812-02 action to perform HUIT was not submitted to Corrective Action Program for approval (e.g. in the closure notes or via an assignment route list) per SWP-CAP-01, section 4.6.1(g). <I> **** Actions Taken **** Contacted CAP supervision, notified owed to group and initiated CR. Recommend CAQ â€“ C to AR-MNTPROG to obtain HUIT approval and document reason for non-compliance.
391409 | CR | 20190326 |  | 4 | RX SW Elevator out of service | N | N |  | N | YES | <D> **** Detailed Description **** The southwest reactor building elevator is stuck in between the 606 and 572 elevations. <I> **** Actions Taken **** Hung caution/out of service bands and infomed the main control room. <N> Credited elevator fire doors are closed and performing the fire barrier function. | 02-00-MT-ELEV-2
391412 | CR | 20190326 |  | 3 | CAT ID 37006, 2 of 3 picked from stores failed | N | N |  | N | NO | <D> **** Detailed Description **** WO 02021357-02 (pre R24 WO could not be completed as scheduled. Of the 3 relays picked from stores, 2 would not bench test SAT. All thre relays were purchased from another plant for spare parts. This is an inventory issue, not a plant installed equipment issue. <I> **** Actions Taken **** One of the failed relays was returned to WH 75, the next on was also returned to 755 with a repair data sheet. Relay was sent off to be rebuilt, but vendor is not sure it can be rebuilt. The first one returned to stores has not been able to be located. Engineering ihas submitted an OSCR to remove work from R24, due tp confidence that we will have a working relay prior to the outage. <N> Vendor is Rolls Royce
391414 | CR | 20190326 |  | 4 | B34 Kootenai Halon System 104C Tank R4 Low Pressure | N | N |  | N | YES | <D> **** Detailed Description **** Inspection of the Halon systems in the Kootenai building today found that System 104C Reserve Tank R4 had lower pressure and lower liquid level than previous inspections. Typical tank pressure is 360 psi. allowed to be plus/minus 5 percent. The recorded pressure today was 290 psi which is below the allowed 5 percent or 342 psi. Since this is reserve tank, it is not a critical item that needs immediate attention. This Halon tank should be sent off for detailed inspection and servicing by a listed Halon testing company. <I> **** Actions Taken **** WR 29147744 written. <N> **** Equipment Description **** B34 Halon System 104C TANK R4 (Reserve) This is a facilities related fire protection system.
391415 | CR | 20190326 |  | 3 | Typo in SOP-CW-OPS | N | N |  | N | NO | <D> **** Detailed Description **** SOP-CW-OPS refers to EPN: CW-PH-1 in steps 5.8.5.b, c, and d. The EPN should be EPN: CW-PHR-1. <I> **** Actions Taken **** Recommend condition report be directed to AR-OPSPROC to correct procedure.
391417 | CR | 20190326 | CAQ | D | EDR-V-19 did not indicate closed on GDS | Y | N |  | N | YES | <D> **** Detailed Description **** During valve stroke timing and 2-year VPI per OSP-EDR/IST -Q701 (work order 02108168), EDR-V-19 did not indicated closed on GDS when it was closed per the surveillance. The red and green position lamps operated properly and the valve had a normal stroke time and satifactory local inspection. <I> **** Actions Taken **** Verified problem was not due to an out of service TDAS-MUX. TDAS-MUX-3 is out or service but this signal is associated with TDAS-MUX-15 (X495-06). | 02-00-EDR-V-19
391419 | CR | 20190326 |  | 3 | (NRC) Control of Ipads identified as potential gap | N | Y |  | N | NO | <D> **** Detailed Description **** An observation was made that iPads are being left outside the main control room unattended. It is suggested that the station review this behavior to determine if there are any potential cyber issues that need to be addressed. <I> **** Actions Taken **** Disccussed with operations manager, left message with IS manager, and notified SM. This is a potential issue with cyber security and does not represent a violation.
391420 | CR | 20190326 | CAQ | D | CIA-TK-5B Holding Strap Not Fully Tight. | Y | N |  | N | YES | <D> **** Detailed Description **** During inspection of the CIA nitrogen cylinders in the truck bay, the holding strap around the bottom of CIA-TK-5B was found to be a little loose. The strap was still in place around the cylinder. <I> **** Actions Taken **** Notified the Shift Manager. OPS 2 tightened the strap further and inspected the other N2 bottles. | 02-00-CIA-TK-5B
391421 | CR | 20190326 |  | 3 | SOP-ELEC-SH5-MAINT STEP 5.22.7 SHOULD BE "AUTO" | N | N |  | N | NO | <D> **** Detailed Description **** SOP-ELEC-SH5-MAINT step 5.22.7 should be "AUTO" not "STANDBY" that the switch is placed in. <I> SOP-ELEC-SH5-MAINT step 5.22.7 revised via minor editorial PCN to read "Place FP-P-1 to AUTO" Major Rev 12, MR 001.
391425 | CR | 20190326 |  | 3 | Manual CTP Calculation enhancement | N | N |  | N | NO | <D> **** Detailed Description **** Based on the review and recommendation from the Plant Process Computer (PPC) bridging strategy project, the current process of using the analog instruments for manual Core Thermal Power (CTP) calculation under procedure PPM 9.3.1 may need enhancement. There are no regulatory requirement impact and the recommendation is for procedure enhancement only. <I> **** Actions Taken **** Procedure Enhancement proposal discussed during PPC bridging strategy team meeting.
391427 | CR | 20190326 |  | 3 | Alignment issue between SWP-PRO-01 and MI-3.6.4 | N | N |  | N | NO | <D> **** Detailed Description **** SWP-PRO-01 specifies documentation of conditional steps that are not applicable under current conditions. These steps are required to be marked "N/A" prior to moving onto the next step. It does not require the "N/A" to be initialed by the user. MI-3.6.4 requires conditional steps that are marked "N/A" to also be initialed by the user prior to work package closure. There does not seem to be alignment between what is required by the field implementer and what is required to be verified during work package closure. <I> **** Actions Taken **** Discussed with peers for clarification prior to generating this CR.
391428 | CR | 20190326 |  | 3 | E-AY-TR/M3 caution alarm light is illuminated | N | N |  | N | YES | <D> **** Detailed Description **** While performing a system walkdown of the CGS transformer yard it was identified that the Caution light for E-AY -TR/M3 was in alarm. The purpose of this CR is to document the alarm and this alarm has no impact on operation of E -TR-M3. | 02-00-E-AY-TR/M3
391429 | CR | 20190326 | CAQ | D | PS 21 seemed to be failed on SRM-EMSQ-600B | Y | Y |  | N | YES | <D> **** Detailed Description **** During performance of ISP-SRM-X302, on steo 7.10.9 we get the AF HV voltage reading. When this was measured there was a very low voltage present (approx 1-2 VDC). This measurement should be around 600 VDC. <I> **** Actions Taken **** Informed CRS/Supervisor and created CR to document issue, so we can replace the HV PS. <N> L19-SRM-DET-B-001 | 02-00-SRM-EMSQ-600B
391430 | CR | 20190326 |  | 4 | Declared prohibited item at the security checkpoint | N | N |  | N | NO | <D> **** Detailed Description **** Declared prohibited item (alcohol) was brought to the Security Checkpoint by a contract visitor. Visitor was informed of Benton County ordinance by the point of contact prior to arriving onsite. Access was denied. <I> **** Actions Taken **** Security supervision, Benton County and shift manager notified. CR generated. Access denied.
391431 | CR | 20190326 |  | 3 | TSP-CR/HVAC-B102 contains typo | N | N |  | N | NO | <D> **** Detailed Description **** Step 8.3.14 of TSP-CR/HVAC-B102 needs to be changed from "WMA-CC-51A1" to "WMA-CC-51B1".
391432 | CR | 20190326 |  | 3 | ASD Replaced GTOs capacitor rating issue | N | N |  | N | YES | <D> **** Detailed Description **** Currently, GTOs for ASD drives are being refurbished by EPC under project AR316044. It was during that process, SME had questions on peach bottom drives snubber capacitor rating being different than what is shown in dwgs for plant installed snubber capacitors. Drawing 246B4314 sheet 11CB defines the capacitor values as qty 2 4U in parallel or 8 UF total which is attached with this CR. Peach bottom are part number 68A7868P6 (5uF). CGS ones are 68A7868P4 (4uF). Previously, AR 00186054 /00178017 and WO 01158615 documented that the capacitors on the replacement GTOs from Peach Bottom must be replaced with capacitors from CGS GTOs before installation in 2008 time frame. However, there has been no known record of capacitors replacement when installing peach bottom GTOs in CGS drives. This leads to a conclusion that there is potential of capac capacitor mismatch if peach bottom drives GTO were installed without capacitor replacement. Upon reaching out to SME on the impact, they do not foresee electrical problem with running the GTO modules with 10 uF caps as long as all 4 modules in a bridge leg are the same. There is reasonable assurance of operation of the drives and this presents no problem with some legs having all 10 uF snubber caps and some legs having all 8 uF snubber caps installed. The worst case would be if 1 GTO failed, and there are 2 GTOs with 10 uF caps, and 1 GTO with a 8 uF cap.There will be unequal sharing of voltage which would result in higher than normal snubber discharge current (snubber dump) at turn-on on the GTO with the highest voltage. The snubber watts loss will be higher with the 10 uF caps by a factor of 1.25. This wouldnâ€™t be a problem unless there were enough 10 uF units in service to tax the cooling system, which the vendor considers unlikely. Recommendation is to replace the 10 uF caps wit 8 uF caps on all spares, and on any operating units at their earliest convenience.WR has been created to inspect capacitor in all drives and replace if any discrepancies found. Recommend assignment to System Engineering. <I> **** Actions Taken **** NOTIFIED SUPREVISOR, DISCUSSED WITH SHIFT MANAGER AND WROTE CR TO DOCUMENT THIS ISSUE. | 02-00-RRC-IMD-ASD1A/1,02-00-RRC-IMD-ASD1A/2,02-00-RRC-IMD-ASD1B/1,02-00-RRC-IMD-ASD1B/2
391433 | CR | 20190326 |  | 4 | CW-T-1B high water level | N | N |  | N | YES | <D> **** Detailed Description **** CW-T-1B level at 14 inches requiring a CR. <I> **** Actions Taken **** CRS notified <N> **** Equipment Description **** Top of CW cooling tower 1b | 02-00-CW-CT-1B
391434 | CR | 20190326 | CAQ | C | TSW-RIS-5 Failed source check | N | Y |  | N | YES | <C> Engineering request this CR be reopened and assigned to AR -SEEIC (Severity C). <D> **** Detailed Description **** While performing CSP-INST-M201, performed source check on TSW-RIS-5. The results were 6,830 cpm. Source check passed the requirements of the surveillance which has an expected response range between 6,000 - 9,000 cpm. RM 2300 display for TSW-RIS-5 has an internal set point set at a minimum of 8,000 cpm to pass surveillance. So the source check automatically failed the internal set point, which in turn failed the operability of TSW-RIS-5 and was put in an RFO situation. <I> **** Actions Taken **** Contacted CRS, Chemistry specialist and chemistry supervisor. Initiated actions in 019-TSW-RIS-5-002 which requires 12 hour grab samples of TSW-SR-34 for operability. It was deemed the set point range should be the same for CSP-INST-M201 and the internal setpoint of RM 2300. <N> **** Equipment Description **** TSW-RIS-5 on BD-RAD-24 in MCR. O19-TSW-RIS-5-002 ***** Jim Hysjulien is acting Supervisor for Cyrus Vadoli. | 02-00-TSW-RIS-5
391436 | CR | 20190326 |  | 3 | Unable to open multiple documents at once in SharePoint |  |  |  | N | NO | <D> **** Detailed Description **** An issue in SharePoint prevents a user from opening a document when another document of the same document type is open from the same location, i.e., one Word document is open and the user is unable to open a second Word document from the same location. The user can open multiple documents if the page is refreshed after opening each document, or the user backs out of the page and returns to it. <I> **** Actions Taken **** Working on troubleshooting and determining course of action to resolve situation.
391438 | CR | 20190326 |  | 3 | RW 467' Centrifruge Room "A" Housekeeping Needed |  |  |  | N | NO | <D> **** Detailed Description **** While performing a pre job HP Survey for work on RWCU-V -438A, it was noted that the RW 467 Centrifruge Room 'A' is in need of house keeping. <I> **** Actions Taken **** The HP technician reported the condition to his supervisor. See pictures uploaded into EDMS. Recommend any house keeping be performed after the RWCU line in the room is flushed and area is down posted from a LHRA.
391440 | CR | 20190326 |  | 3 | CC-183 Out of Tolerance Standard 002-56-01-035 |  |  |  | N | NO | <D> CC-183 Out of Tolerance Standard 002-56-01-035. Recommend assign to AR-CALSERV Cat 3 <I> Issued customer complaint and entered a CR. . Found at INPROG, moved to APPROVED.
391441 | CR | 20190326 |  | 3 | Corporate PMDD (iPads) without red labels | N | N |  | N | NO | <D> **** Detailed Description **** It was identified that iPads that are approved to enter the power block are not presently labeled with a red ENERGY NORTHWEST FOR CORPORATE USE ONLY label. Upon deployment of the iPads, the PMDD were hardened correctly and approved to enter the power block by Cyber Security as per procedure at the time with the correct white label. However, when the procedure was updated, no additional action was taken to go back and apply a red labels to the iPads. This is identified as a corporate administrative correction to be performed and does not constitute non-compliance with 10CFR 73.54. <I> **** Actions Taken **** Notified Cyber supervisor, Cyber program manager, CIO. Coordinating application of red labels to iPads.
391443 | CR | 20190326 |  | 3 | Mixed Waste from 507â€™RW Solvent Stations |  |  |  | N | NO | <D> **** Detailed Description **** 507â€™RW solvent stations, utilized for MOV degreasing during R-23, underwent recent maintenance in preparation of R-24. The recent maintenance of the solvent stations generated several gallons of mixed waste which will result in expensive disposal costs that have not been budgeted â€”potentially $60k. The maintenance/cleaning of the station was not preformed post R-23. This delay in cleaning/maintenance and craft potentially not utilizing the recycling function of the station is likely to have contributed to the solvent becoming a mixed waste. The WO to clean and perform maintenance of the units needs to be scheduled so the task is performed post outage (shortly after heavy use) and not deferred to a pre-outage task. <I> **** Actions Taken **** Notified E&RP manager initiated CR. <N> **** Equipment Description **** 507'RW thru double doors
391444 | CR | 20190326 | CAQ | D | Received H13-P840 A4 drop 9-5 CW PH HI/LO alarm. | N | N |  | N | YES | <D> **** Detailed Description **** Received H13-P840 A4 drop 9-5 CW PH HI/LO alarm and alarm is locked in. PH is 8.34 and steady using point F141. Locally at CW-PNL-1 CW-PHITS-1 is at 8.34 and CW-PHR-1 is 8.35 both steady. No other automatic actions occured. CW blowdown remains in service. <I> **** Actions Taken **** Started temporary log in the Main Control Room. Alarm has cleared at approximately the same time as power was turned off to the de-halogenation skid. | 02-00-CW-PHITS-1
391447 | CR | 20190326 |  | 4 | Oil leak on 70 ton mobile crane |  |  |  | N | NO | <D> **** Detailed Description **** When doing the monthly inspection on the 70T, we found an oil leak. The leaks appears to be coming from the rotating structure, on the back of the cab. <I> **** Actions Taken **** notified master rigger, supervisor, and wrote this CR. <N> **** Equipment Description **** 70 ton mobile crane.
391448 | CR | 20190326 |  | 4 | SO-42-2D4C Motor Starter PMT found greater than 10% voltage | N | N |  | N | YES | <D> **** Detailed Description **** Voltage readings on SO-42-2D4C found to be greater than 10% (Ground AÃ¸ 286.5v, BÃ¸ 239.4v, CÃ¸ 316.2v) <I> **** Actions Taken **** Contacted MCR and wrote this CR <N> **** Equipment Description **** Motor starter for SO-P-H2S. WO 02073810 04 | 02-00-SO-42-2D4C
391449 | CR | 20190326 |  | 3 | eSoms process issue |  |  |  | N | NO | <D> **** Detailed Description **** Sheet O19-WEA-RIS-14-001. LCS 1.3.3.1.C is entered immediately, the time for entry was made same time as 1.3.3.1.A as required. LCS 1.3.3.C is to restore channel to operable status in 7 days, however eSOMS show the time is expired at the same time as entered. <I> **** Actions Taken **** Informed supervision
391450 | CR | 20190326 | CAQ | D | FPC HX Room (RRA-CC-20) SW low flow | Y | Y |  | N | YES | <D> **** Detailed Description **** Following start of SW-P-1A the â€œFPC Rm Cooler Flow Low/Temp Hiâ€ alarm (H13-P812.R1.4-2) was received. CRS issued OSP-SW-C101to clear the alarm. During the performance of OSP-SW-C101 the equipment operators noted that the as-found initial flow indicated on SW-FI-71A was 35 gpm, which less than the minimum required value of 38.5 gpm. Per note 11 of Attachment 9.1 of the OSP-SW-M101, the FPC room contains no Tech Spec associated equipment and therefore no equipment was rendered Inoperable by the low flow. The flow was then successfully raised 44 gpm. <I> **** Actions Taken **** Dispatched 2 operators to add unexpected occupational exposure to operations dose report with no clear path forward to address these SW low flow alarms on a more permanent basis | 02-00-RRA-CC-20
391460 | CR | 20190327 |  | 4 | Received Oscillograph Start Alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3 alarms in and clear. Oscillograph Started alarm was due to the J12 sensor SM-8 Undervoltage. The sensors have been reset. E -TR-S and E-TR-B voltages as indicated on H13-P800 are 238/238/238 kV and 118/118/117 kV respectively. BPA/DITTMER reports Eddie Celilo 500kv line #2 relayed off .The fault is under investigation There was not a need for an emergent outage and no RAS was initiated. All plant controllers and equipment exhibited normal operation <I> **** Actions Taken **** Informed CRS
391461 | CR | 20190327 |  | 4 | PWC-FU-1 | N | N |  | N | YES | <D> **** Detailed Description **** at 0330 3/27 19, we attempted to start a backwash on the flocculato. PWC-LI-100 was reading 18.2 ft. the yellow backwash light would not illuminate when the button was depressed and the cycle would not start even when held >1 min. we checked the lightbulb and verified it worked. after that would not work, we tried resetting the high turbidity trip to see if the flocculator would start. it did not at this time. at 4am, we were directed to attempt the backwash procedure with the section assuming that the level indicator was malfunctioning and level was lower than we expected. the SS3 was taken to off, and the flocculator immediately started with PWC-LI-100 still indicating 18 ft. the flocculator was run in dump until turbidities were within spec, then the flocculator SS3 high turbidity shutdown was taken back to on and the flocculator set to fill. request PWC-LI-100 be replaced/troubleshot <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-PWC-FU-1
391463 | CR | 20190327 |  | 4 | M&TE Suspended/ Lost |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0066199 Ashcroft Gauge 300psi Can't be Located and is Suspended/ Lost. No Activity in Met/ Track or Portal J. DEF #6976A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391464 | CR | 20190327 |  | 4 | PWC-V-423. Leaks by the seat. | N | N |  | N | YES | <D> **** Detailed Description **** During work on PWC-V-414 it was observed that PWC-V-423 was leaking by its seat and required the clearance order boundary to be expanding to allow work to continue. This valve needs to be replaced during the next opportunity when potable water is crosstied. The inbody seat is washed out. The replacement valve was verified to be CID#54315352 and is a 3/4" Globe valve with threaded FPT connections. <I> **** Actions Taken **** Generated WR <N> **** Equipment Description **** BLDG 40 | 02-00-PWC-V-423
391467 | CR | 20190327 |  | 3 | CRAFT ABLE TO SIGN OFF RANDOM PEOPLE FROM CLEARANCES |  |  |  | N | NO | <D> **** Detailed Description **** when in ESOMS by clicking on the "sign off any clearance" icon random clearance holders will pop up and craft is able to sign them off as if the craft has supervisor rights in ESOMS. <I> **** Actions Taken **** NOTIFIED CRAFT, SHOP'S SUPERVISION AND MANAGER
391468 | CR | 20190327 |  | 4 | RadWaste Control Room Bookcase Shelving Unevenly Spaced |  |  |  | N | NO | <D> **** Detailed Description **** The shelving in the bookcases in the RadWaste Control Room are not evenly spaced. As a result, it is difficult to remove the Procedure binders for filing or use without the individualâ€™s potentially scrapping their knuckles. The shelves need to be adjusted to remove this potential safety issue and increase ease of use. <I> **** Actions Taken **** Notified supervision and initiated condition report.
391469 | CR | 20190327 | CAQ | D | E-TR-B termination box should be wiped down and oil pads nee | Y | N |  | N | YES | <D> **** Detailed Description **** During a system walkdown of the transformer yard it was discovered that the oil absorbant rags under the E-TR-B low side termination cabinet need replaced because they are soaked with water/oil. As part of replacement of the rags the low voltage cabinet outside cover should be wiped down so it can be determined if the oil leak has gotten worse. Currently the level for E-TR-B is acceptable and this CR is being initiated to clean up around E-TR-B to make sure the leak can be quantified now that the winter weather is gone. | 02-00-E-TR-B
391470 | CR | 20190327 |  | 3 | Trend - Maintenance DataGlance Work Order closure |  |  |  | N | NO | <D> **** Detailed Description **** Maintenance monitoring of supervisor reviews of work packages within DataGlance revealed a negative trend in the number of items over 14 days old awaiting review. As of 3/27/19, 262 items are awaiting review. This is a slight improvement, but not substantial enough to consider the trend reversed. Prior monitoring identified the following trend. 2/27/19 â€“ 279 1/28/19 â€“ 183 12/13/18 â€“ 97 11/26/18 â€“ 75 10/25/18 - 3 <I> **** Actions Taken **** Initiated CR, notified Maintenance Manager
391474 | CR | 20190327 | CAQ | D | Spare fuses need to be removed | Y | Y |  | N | YES | <D> **** Detailed Description **** EC 15891 spared fuses in E-CP-H13/P823 per design and documentation correctly reflects that. The fuses were not removed as part of the work order. <I> **** Actions Taken **** This is closure on AR/CR 388746-01 to evaluate discrepancies between E555-E-CP-H13/P823 and the Plant. The documentation is correct and the plant is not. <N> **** Equipment Description **** Main Control Room Panel E-CP-H13/P823 | 02-00-E-CP-H13/P823
391479 | CR | 20190327 | CAQ | D | EDR-V-393A did not go full shut | N | N |  | N | YES | <D> **** Detailed Description **** EDR-V-393A did not go full shut following system flush IAW SOP-RW/EDR-OPS step 5.14.13.c Valve was initially full open, but indicates mid position instead of full shut <I> **** Actions Taken **** Informed MCR | 02-00-EDR-V-393A
391484 | CR | 20190327 |  | 3 | FM Discovered during resin add to EDR-DM-29 | N | N |  | N | YES | <D> **** Detailed Description **** FME Discovered during resin add to EDR-DM-29. While drainin resin to EDR-DM-29 it was noticed at the very end of the add there was a piece of plastic that appeared out of the resin. the mixer was off at this time and as the plastic became visible it quickly disappeared down the drain to the EDR-DM-29. There was insufficient time to run down the stairs and stop the transfer. The transfer was completed. the Field supervisor was contacted immediately and the MCR notified. The resin is transferred in paper barrels with a plastic bag lining. the plastic bags were immediately inspected to ensure their integrity and also counted to ensure all 13 were were present. This count and integrity check was second checked. With a supervisor present the count was repeated. It was also noticed that there were two slivers of white plastic about 1/16wide and and approx 1.5 inches long in the mix when the bag found. <I> **** Actions Taken **** Supervisers was informed, believe the material was in the resin added. The tank was inspected prior to filling. Concern to evaluate is eventually it will be in EDR tank 1 and there is no strainer on the transfer pump. will it make it thru the pump? | 02-00-EDR-DM-29
391487 | CR | 20190327 |  | 4 | Disabled ANN-ANN-P840.A4,9-5 per PPM 1.3.1 Section 4.13.8. | N | Y |  | N | YES | <D> **** Detailed Description **** Disabled ANN-ANN-P840.A4,9-5 per PPM 1.3.1 Section 4.13.8 as the tile will be renamed 'CW Chemistry Trouble' by EC 16616. Reference Caution C/O C-ANN-ANN-P840-001. Shift Managers permission was granted. Reference WO 02119558 - Install new dehalogenation skid. The CRS has established a new Temporary Log for CRO 1 to monitor CW ph every four hours. <I> **** Actions Taken **** Disabled ANN-ANN-P840.A4,9-5 per PPM 1.3.1 Section 4.13.8. Proceedurally required CR. Proceedurally required WR. Please cancel the WR as the annunciator is tracked by the EC and Caution C/O. <N> **** Equipment Description **** ANN-ANN-P840.A4,9-5
391488 | CR | 20190327 |  | 3 | Revise WCI-4 for EP equipment priority. |  |  |  | N | NO | <D> **** Detailed Description **** Currently WCI-4 attachment 4.4 directs issues related to PPM 13.14.11 EP category A1 or A2 equipment get coded as priority 1 activities in the work control process. Priority 1 normal schedule guidance is to treat the work as emergency work to start now and work around the clock. WCI-4 should be revised to indicate a priority of 2A for these components. <I> **** Actions Taken **** Contacted the Work Control Manager.
391489 | CR | 20190327 | CAQ | D | sw-te-2b NEEDS REPLACEMENT | Y | N |  | N | YES | <D> **** Detailed Description **** During replacement of SW-TE-2A ans SW-TE-2D (WR 29146265 and 29146720) the craft noticed that SW-TE-2B element was damaged and needs to be replaced. SW-TE-2B is working and indicating at SW-TI-2A, but needs to be replaced soon <I> **** Actions Taken **** Wrot CR and WR to replace SW-TE-2B | 02-00-SW-TE-2B
391490 | CR | 20190327 |  | 3 | PWC-AV-4, Incorrectly labled | N | N |  | N | NO | <D> **** Detailed Description **** PWC-AV-4 is incorrectly labled as FP-AV-102. <I> **** Actions Taken **** Generated Lable request.
391493 | CR | 20190327 |  | 3 | Incomplete information on MOT Document |  |  |  | N | NO | <D> **** Detailed Description **** On 02/21/19 Engineering/Organization 54420 submitted document MOT-CRHOI-1-1 electronically to Doc Control for processing. Doc Control is unable to process document due to information within the document being cut off. <I> **** Actions Taken **** CR initiated, MOT was returned for corrections.
391494 | CR | 20190327 |  | 4 | Level 1 Procedure Filing Error in Work Control |  |  |  | N | NO | <D> **** Detailed Description **** While filing SOP-LHGP-PM in Work Control, Document Control staff identified that SOP-HHGP-PM had been misfiled in its place back on 11/29/17. <I> **** Actions Taken **** SOP-HHGP-PM was removed from the files in Work Control since it was superseded on 11/29/18. IS Management team has been informed. No further actions are needed or required. CR initiated for trending purposes only.
391495 | CR | 20190327 | CAQ | C | DEA-FN-SPARE, PPM 10.2.13, and PMID 26037 deficiencies | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02132084-01 it was identified that during a review of past work orders that the lubricant used could not be verified to be the correct one (Chevron SRI-2) which was used during the performance of current PM. Doubled shielded bearings should be installed so it is â€œlike for likeâ€ if it gets installed in the plant. This CR is to document these issues. â€¢ PPM 10.2.13, Approved Lubricants identifies for the EPNâ€™s listed for the PMID 26037-01 and 02 DEA-FN-SPARE (DEA-FN -11, DEA-FN-21, & DEA-FN-31) that lubrication is not required; motor bearings are double shielded. Discussion and research by system engineering identified that the spare fan does not have double shielded bearings and requires lubrication every 6 months with Chevron SRI-2. PPM 10.2.13 needs to be revised to add this specific motor or PM work instructions changed to indicate correct lubricant to be used. â€¢ See EDMS for motor information document â€¢ Additionally PMID 26037-01 DEA-FAN- SPARE, DEA-FN SPARE LUBRICATION-3 year PM (Ref 307520) & 26037-02 DEA-FAN- SPARE, ROTATE SPARE DEA FAN ROTORS-6 month PM (Ref 307520) have you perform the same maintenance at different intervals. â€¢ Recommend assignments to system engineering to provide direction on the following: â€¢ unverified lubricants used â€¢ Installation of double shielded bearings or not â€¢ Whether PPM 10.2.13 should be updated or the work instructions â€¢ Determine if PMID 26037-02 can be retired (SMS 390964) <I> **** Actions Taken **** Discussed with Manager, system engineer, contacted MCR and initiated CR | 02-00-DEA-M-FN/11,02-00-DEA-M-FN/21,02-00-DEA-M-FN/31
391497 | CR | 20190327 |  | 3 | CID 34092- Received incorrect stem from vendor (R24) |  |  |  | N | NO | <D> **** Detailed Description **** While attempting to perform pre-outage task to machine a new stem nut for HD-V-18D it was discovered that the pitch and lead of the new stem are incorrect. The CID description has a â€˜note to vendorâ€™ that states the Pitch should be Â¼ â€œ and the lead should be Â½â€. The actual pitch and lead are 1/3 and 1/3. Stem was purchased on PO 352781. <I> **** Actions Taken **** Machinist notified supervisor.
391498 | CR | 20190327 |  | 4 | PWC-SEW-12 has low flow on right side | N | N |  | N | YES | <D> **** Detailed Description **** While performing safety eyewash checks it was observed that PWC-SEW-12 has low flow on the right side of the eyewash. <I> **** Actions Taken **** Staged temporary eywash, wrote CR and informed CRS. | 02-00-PWC-SEW-12
391499 | CR | 20190327 |  | 4 | Tripping hazard exiting the TSC |  |  |  | N | NO | <D> **** Detailed Description **** Exiting the TSC through door N-18 RCA/TSC ACCESS, a tripping hazard was discovered. Approximately 7/16th of an inch difference in height between the tile and the chipped painted concrete floor. Other tripping hazards are in that same area. painted concrete floor. Other tripping hazards are in that same area. <I> **** Actions Taken **** Notified Supervisor and generated CR.
391500 | CR | 20190327 | CAQ | C | POC Procedure SWP-IRP-01 missing requirement to send minutes |  |  |  | N | NO | <D> **** Detailed Description **** POC Procedure SWP-IRP-01 Step 2.11.10 does not require Quality to receive copies of meeting minutes even though it is specified by the OQAPD (Rev 54), Appendix III, Section 2.1.8.d <I> **** Actions Taken **** Notified the POC Admin and Quality Dept
391501 | CR | 20190327 |  | 4 | Unusual behavior of evap pond leak detection | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The Evap Pond leak detection pipe for Pond 1A was found to exhibit unusual behavior during a regular walk-down. The leak detection collection pipe was full at a level higher than the water within Cistern-1 while the leak detection pump was observed running. This behavior is new within approximately the last week and is possibly due to overtopping the leak detection pipe during recent water movement or some ice damage in the system. This issue is internal to the pond system which contains clean wastewater from the potable water backwash; no water is leaking to the environment. <I> **** Actions Taken **** Walk-down performed with F&CE system engineer. Consulted electrician who installed leak detection system components. Leak detection system behavior will continue to be investigated/trended and Pond 1A inspected when water levels can accommodate a more thorough inspection. Recommend for trending.
391502 | CR | 20190327 |  | 3 | PeopleSoft Payroll Advice Print failure |  |  |  | N | NO | <D> **** Detailed Description **** The Payroll Advice Print program failed with the message 'value too large for column PS PY EARNS WRK ERNCD'. <I> **** Actions Taken **** Research has uncovered a flaw in the logic where an invalid value was assigned. Will apply fix asap. <N> Fix was applied 3/27/19 and verified to correct issue. No more actions needed. Recommend NCAQ 4 to ITMGMT.
391503 | CR | 20190327 |  | 4 | PPC data points X113 and X108 have no data | N | N |  | N | YES | <D> **** Detailed Description **** While attempting to establish a real time plot for performance of OSP-ELEC-M703, there was no data on points X113 and X108. Both points come from MUX-3 which was recently repaired and put back in service. The real time plot is not used to certify any pounded step in the surveillance. Analog data will be used for performance of the surveillance. <I> **** Actions Taken **** Notified CRS. Documented lack of data points on surveillance cover sheet. <N> **** Equipment Description **** PPC-MUX-3, MCR, RW 501'
391504 | CR | 20190327 | CAQ | C | Recieved 4.418.J1 NOBLE GAS RAD ALERT. | Y | N |  | N | YES | <C> Added WO 02128123 to the cross reference panel and checked the Completion required box. <D> **** Detailed Description **** Recieved 4.418.J1 NOBLE GAS RAD ALERT WITH CMS-RIS-12A/1 alarming at 2.06e-06. A look back at the history on ENW -CGS-X469 shows a slow rise in activity from 3/20/19 and then a faster rise starting on 3/27/19 at about 0400. There is not a corresponding on CMS-RIS-12B. There is no perceptable change to Indentified leakage, unidentified leakage, RRC-P-1A/B seal parameters, containment pressure or temperatures noted. Chemisty has been requested to take a sample of conatinment. CRS informed. <I> **** Actions Taken **** Wrote this AR. Followed ARP. Informed CRS. Requested chemistry sample. eDNA trend attached to EDMS. Monitoring will continue. <N> Chemistry reports that containment sample for noble gas activity was less than minimum detectable | 02-00-C-TK-1,02-00-CMS-RIS-12A
391505 | CR | 20190327 |  | 4 | OG-RF-20A did not start as expected | N | N |  | N | YES | <D> **** Detailed Description **** OG-RF-20A did not start with an indicated start signal (all three lights out) on GY-TIC-17. The local RMS was in AUTO. The other two compressors were running and maintaining glycol temperature at ~42F for the time I was in the arear (1.5hrs) with an Offgas dryer regeneration in progress (higher heat load). <I> **** Actions Taken **** Wrote CR and notified SM <N> **** Equipment Description **** W452 | 02-00-OG-RF-20A
391506 | CR | 20190327 |  | 4 | GY-TIC-17 not controlling correctly | N | N |  | N | YES | <D> **** Detailed Description **** During walkdown of the glycol system the glycol temperature indicating controller, GY-TIC-17, was not functioning correctly, this has been previously identified. This CR is to capture what was observed during the walkdown to assist in troubleshooting efforts/review compressor performance. During this time an OG dryer was regenerating which places an additional heat load on the glycol system. It was observed on the local temperature indicator that glycol temperature was ~41F. The controller was indicating 34.5F which should have started two compressors (C was lead) however no compressors were running and none of the indicating lights were out (indicating a start signal). During this time the start contactor for the lead compressor would randomly cycle momentarily. When this cycling would occur the controller temperature indication would simultaneously jump up to ~37F and back to 34.5F. <I> **** Actions Taken **** Initiated CR and notified SM After a few minutes of this random behavior the lead compressor started and the controller temperature stabilized at ~37F with local tank temperature indicating ~42F. Approximately 2 minutes later the second and third compressors received a start signal (all three lights extinguished) but only OG-RF-20B started. The system stabilized with OG-RF-20B and 20C running and a start signal to 20A with no compressor start (CR 391505). It was observed that the static pressure of OG-RF-20A was ~45 psig. I retrieved a contact temperature probe and took temperature and pressure measurements for reference. See EDMS for data. Cross referenced existing WR. <N> **** Equipment Description **** W452 | 02-00-GY-TIC-17
391507 | CR | 20190327 | CAQ | D | HPCS-GEN-DG3 north bearing oil level is low | Y | N |  | N | YES | <D> **** Detailed Description **** HPCS-GEN-DG3 north bearing oil level is low, please add oil. The normal level is in the middle of the sight glass and the low specification is the bottom of the sight glass. Oil level is just above the bottom of the sight glass. <I> **** Actions Taken **** Informed the backshift craft supervisor. | 02-00-HPCS-GEN-DG3
391508 | CR | 20190327 | CAQ | C | OPRM-CH-2 growth rate stuck at 3.200 | Y | N |  | N | YES | <D> **** Detailed Description **** On the PPC overview screen, OPRM-CH-2 growth rate indication is stuck at a value of 3.200. On the N9 screen, the channel fluctuates between 1.000, which is the expected value for steady state conditions, and 3.200. Further investigation in the OPRM summary screen for OPRM-CH-2 indicates the value is coming from cell 11 which constantly indicates 3.200. Maintenance was performed on APRM-CHS-2 today. Review of computer point HSD2.PRNM OPR2C11G indicates this value had been fluctuating as expected prior to the maintenance. Request maintenance investigate and repair as necessary. <I> **** Actions Taken **** Notified CRS. <N> **** Equipment Description **** MCR, RW 501' | 02-00-APRM-CHS-2
391509 | CR | 20190327 |  | 4 | Eye Wash Station #14 missing FME cover |  |  |  | N | YES | <D> **** Detailed Description **** The right hand side eye wash station spray head is missing it's cover and the left hand cover has a broken retainer strap. Eye Wash Station #14 is located in the DG3 room. <N> **** Equipment Description **** DG 3 Room
391510 | CR | 20190327 |  | 4 | Ladder bracket seismis restraint wing nut is stripped |  |  |  | N | YES | <D> **** Detailed Description **** The bottom ladder rack located in the DG3 room on the West wall has a stripped wing nut on the right hand side bracket preventing the ladder from being secured per the guidance on the wall sign. <N> **** Equipment Description **** DG 3 Room on the West wall
391511 | CR | 20190327 |  | 3 | TS 3.3.1.3 still in books and electronic licensing database |  |  |  | N | NO | <D> **** Detailed Description **** While investigating operability of OPRM-CH-2 per CR 391508, determined that TS 3.3.1.3 is still in all the copies of the technical specifications in the MCR. Additionally, when utilizing the electronic version of the technical specifications, section 3.3.1.3 still appears in the document. However, there is no corresponding technical specification basis for the section. Review of the list of effective pages in the electronic technical specifications indicates TS 3.3.1.3 should have been removed after implementation of the PRNM upgrade. All hard copies of the Technical Specifications need to be updated, as well as the electronic copy of technical specifications. <I> **** Actions Taken **** Discussed with CRS. <R> The cleanup LAR was submitted under GO2-18-057, NRC acceptance review is complete, expected date is 6/13/19. All prior to PRNM TSs are being removed in this LAR. The LAR is being tracked via 00375749-16. No further action is needed under this AR.
391512 | CR | 20190327 |  | 3 | DG3 Electronic Log Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Electronic DG3 Run Logs do not contain all of the notes found in the paper logs from SOP-DG3-START for the DG-ENG -1C LUBE OIL LEVEL reading. Additionally the log reading shows up red as an out of spec when it shouldn't while running. The log reading has the standby spec only and not the running spec. When the running spec is logged, the program thinks it is an OOS and displays it as a red reading. There are no notes in the electronic log that clarify that there are different specs.
391513 | CR | 20190328 |  | 3 | Step 7.3.68 of OSP-ELEC-M703 needs revision |  |  |  | N | NO | <D> **** Detailed Description **** Step 7.3.68 of OSP-ELEC-M703 (HPCS Monthly DG run) needs to be revised. As currently written, it has the operator check the lube oil level on the engine while it is idling, and then has the operator compare the level to that taken in step 7.1.2. The problem is that in step 7.3.68 the engine is idling, while in step 7.1.2 it is off. Therefore, the part of the step where the operator is tasked to compare the two oil levels to determine if the engine is using oil does not make sense, since oil levels will always be different in this case. The step should either compare idling oil level to idling, or shutdown to shutdown. Please revise. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** HPCS DG 3
391514 | CR | 20190328 |  | 4 | Bldg 9 Palouse HVAC unit cycling continously | N | N |  | N | NO | <D> **** Detailed Description **** Bldg 9 Palouse external HVAC unit surging/cycling on and off coninously (10-15 times per minute). This occurs over a 30 minute period multiple times per day. Facilities needs to repair. <N> **** Equipment Description **** FACILITIES BLDG 9 PALOUSE EXTERNAL HVAC DUAL FAN
391520 | CR | 20190328 |  | 4 | CAS-C-1B maintaining lower pressure than normal | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1B needs unloader adjusted. During previous maintenance CAS-C-1A dschg check was leaking by which prevented adequate adjustment of CAS-C-1B unloader. | 02-00-CAS-C-1B
391521 | CR | 20190328 |  | 4 | 2 Pieces of M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** 2 Pieces of M&TE have been Rejected. Calcode #45187 Fluke DC/AC Current Probe- model 80i-1010 Passed Calibration but now Rejected- Unreliable DEF #6978A written. Calcode #0063364 Starrett Dial Indicator- model 196A1Z was NOT used during Calibration cycle. Rejected- No Data Available. DEF #6979A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391523 | CR | 20190328 | CAQ | D | Accumulator trouble alarm HCU 3027 | Y | N |  | N | YES | <D> **** Detailed Description **** trouble alarm due to water level <I> **** Actions Taken **** drained water / alarm clear | 02-00-CRD-TK-125/3027
391524 | CR | 20190328 |  | 4 | 6 Pieces of M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** 6 Heise Pressure Calibrators- model PTE-1/XT found OOT & adjusted within specs. All had been Suspended 6/21/17- Batteries Removed. Not used during this time. Their EPROMS could likely have lost it's Calibration Constants. Calcode #0068154. DEF #6980A written. Calcode #0068155. DEF #6981A written. Calcode #0068156. DEF #6982A written. Calcode #0068159. DEF #6983A written. Calcode #0068200. DEF #6984A written. Calcode #0068201. DEF #6985A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391525 | CR | 20190328 | CAQ | C | Incorrect EPN listed on AED ELC E503-2A |  |  |  | N | NO | <D> **** Detailed Description **** E503-2A (Rev 24) has an incorrect EPN listed as the local starter compartment to CAS-C-1C. CAS-DISC-2P6C is the fused disconnect to CAS-C-1C to isolate power to CAS-42-C/1C (CAS-C-1C LOCAL STARTER COMPARTMENT) and CAS-C-1C; however AED ELC E503-2A (Auxilliary one line diagram) shows this power going through CAS-42-C/1A (CAS-C-1A LOCAL STARTER COMPARTMENT). As CAS-C-1A is powered from E-MC-7A, this implies a separate energy source, which was verified to be incorrect via E528-47A (Rev 13) and E555-CAS-42-C/1C. The EPN on the drawing should be CAS-42-C/1C. <I> **** Actions Taken **** Verified correct power supplies to CAS-C-1C and clearance boundaries continue to be sufficient with qualified individuals.
391526 | CR | 20190328 |  | 4 | Security gate track issue | N | N |  | N | YES | <D> **** Detailed Description **** As part of an extent of condition walk down of the vehicle trap gates following WR 29147558 issue. Overall the gates are working as designed with the exception of one. The gate in the mentioned WR needs to have a new track system installed due to the round roller guide on the ground being smashed over years of heavy loads being driven over it. The track is currently imbedded in concrete. Recommend replacing to a V style guide like the other adjacent gates. For additional information contact x2141. <I> **** Actions Taken **** CR/WR generated | 02-00-SEC-GATE-26
391527 | CR | 20190328 |  | 3 | IDC drinking water exceeds level for di(ethylhexyl)phthalate |  |  |  | N | NO | <D> **** Detailed Description **** Routine Compliance samples for Pesticides were collected at both Industrial Development (92023F) wells on February 28, 2019. Analysis at Anatek Laboratories on March 18, 2019 showed that one of the fifty analytes tested on well #2 (SO2) exceeded the Trigger Level of 0.6 ug/L. The result of di(ethylhexyl)phthalate by EPA Method 525.2 at well #2 was 0.750 ug/L. The maximum containment level for this analyte is 6.0 ug/L. <I> **** Actions Taken **** Discussed results with Environmental and Regulatory Programs. E&RP discussed results with WA DOH. DOH said we didnâ€™t have to sample or take corrective action at this time. Recommending AR assignment to Environmental and Regulatory Programs
391528 | CR | 20190328 |  | 3 | Revision needed for PPM 1.3.64 |  |  |  | N | NO | <D> **** Detailed Description **** Step 3.10.1 of PPM 1.3.64 references Clearance Order Briefing Checklist (Form 26604). This needs to be revised to say Complete a clearance order prejob brief. This form has been superseded by Form 26888. Form 26604 should be cancelled. <I> **** Actions Taken **** Wrote AR.
391533 | CR | 20190328 |  | 3 | E-DISC-AC/1 & E-DISC-AC/2 need to be closed | N | N |  | N | YES | <D> **** Detailed Description **** E-DISC-AC/1 & E-DISC-AC/2 are the new local fused disconnect switches for Elevator 4 `Machine Room AC Units, WRA-AC-1 & WRA-AC-2 located on the 467 RW elevation in the corridor. WO 02137366-06 MT-ELEV-4: CHARGE HVAC SYSTEM (EC 12277) is complete and the clearance order was lifted. The clearance order did not cover closing the two disconnects listed. Currently there is no document that provides operations a line up for these disconnects. Task 06 will be closed with a work request generated to apply trim charge if required. Disconnects E-DISC-AC/1 & E-DISC-AC/2 need to be closed in order observe operation of the new units and apply trim charge if required. <I> **** Actions Taken **** Discussed with operations initiated CR and WR <N> **** Equipment Description **** 467 RW elevation in the corridor . Due date moved out to allow time for EC 12277 to be revised to include these changes. . E-DISC-AC/1 & E-DISC-AC/2 disconnects are added to PPI SOP -HVAC/RW-LU, which was revised and issued on 7-17-19. As the procedure addresses this issue, this AR-CR can now be closed. . | 02-00-E-DISC-AC/1,02-00-E-DISC-AC/2
391534 | CR | 20190328 | CAQ | D | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065705 Proto Torque Wrench- model 6018AB 300ft/lb found OOT- Rejected- Can't adjust . Per PPM 1.5.4 section 4.4.3 (a-c) Torque Wrench had acceptable post use verification @ +/- .06%. DEF #6977A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391537 | CR | 20190328 | CAQ | D | Received S1-7 ground when AR-CB-P1A trip fuses installed | Y | Y |  | N | YES | <D> **** Detailed Description **** Received 125 VDC BATTERY B1-7 GROUND (H13-P800.C5 6-7) alarm. The ground was a severe positive ground (between 0 and 1k ohms positive on the S1-7 gound meter on H13-P800). The alarm was received coincident with installing the tripping fuses for AR-CB-P1A when racking the breaker back in following maintenance (WO 02120617). The AR-CB-P1A tripping fuses were removed and the ground meter immediately returned to normal and the alarm was reset. <I> **** Actions Taken **** Notified the CRS and SM. Submitted CR and WR. The trip fuses for AR-CB-P1A were removed and the ground was reset. | 02-00-AR-CB-P1A
391538 | CR | 20190328 | CAQ | C | Fresh CFD resin is leaching more chloride than normal | N | Y |  | N | NO | <D> **** Detailed Description **** Several lots of new CFD resin is leaching more chloride than ususal. This is producing elevated reactor chlorides when a fresh CFD pre-coat is placed into service. The chloride levels produced are above normal but within the allowable limits as contracted to the vendor. <I> **** Actions Taken **** Requested that OPS place new precoats on the hold pump for 2 hrs before placing into service. This is helping to reduce the reactor chloride spikes. Also, the resin vendor was contacted to discuss the problem. The vendor indicated that they have found UV chlorides in the raw materials used to make the resin. The UV chlorides were not detected in their QA test methods and thus adequate rinse time was not achieved for the lots of resin that we received. The vendor has updated their test methods and are confident that future resins recieved will not have the chloride issues. No further actions are needed.
391540 | CR | 20190328 |  | 4 | Two CW halogenations were not able to be performed | N | N |  | N | NO | <D> **** Detailed Description **** Two CW halogenation treatments were not able to be performed because of work associated with the dehalogenation skid project. The work for the dehal project was brought forward. As a result, the operator controls for the blowdown flow control were modified before a procedure change could be made. <I> **** Actions Taken **** Procedure writers are working on updating the controls for the blowdown flow control. No chemistry actions are required.
391541 | CR | 20190328 |  | 3 | Multiple RW elevator emergency calls to MCR (in error) |  |  |  | N | YES | <D> **** Detailed Description **** RW elevator emergency push button has been mistakenly depressed on several occasions. This PB is in line with the floor call buttons and the buttons are arranged lower than the previous car. Request a cover (permanent not magnetic â€“ stainless steel car) be installed to prevent inadvertent actuation of this switch. This switch call the CR emergency line at 2222. A temporary cover is not a good option nor would be declaring a temporary cover permanent since the cover would likely be displaced during normal use. Riveted or screwed in place low profile cover would be best option. | 02-00-MT-ELEV-4
391542 | CR | 20190328 |  | 4 | Turbulent conditions TMU-P-1B around 09:30 observed | N | N |  | N | YES | <D> **** Detailed Description **** During support of weekly fish basket study at TMU pumphouse craft identified turbulent conditions (and intermittent) noise/vibrations ~ every two minutes local to TMU-P-1B. This was observed with both the fish baskets installed and removed. Craft stated that noise did not seem apparent on Wednesday, however local conditions at TMU-P-1B were turbulent. <I> **** Actions Taken **** Reviewed current system lineup with craft from field conditions. TMU-P-1A and TMU-P-1B are in service with TMU-P-1C secured. There is a note in SOP-TMU-OPS regarding if TMU-V-72 (min flow) valve is open that turbulent conditions exist at the pump. Performed initial review of M620 loigic for TMU-V-72 and with system flow GT ~6650 TMU-V-72 should appear to logically be closed. Per review of M507-1, the surge arrestor valve (TMU-V-1) also ties into this line downstream of the TMU-RO-2A, and TMU-RO-2B. * Reviewed Computer point L002 and TMU make up on average shows changing ~ 6000 gpm from ~0130 this morning to 0930 timeframe for info. * Contacted SSS for if there was any reason TMU-P-1B was in service as opposed to TMU-P-1C. <N> See screenshot of local conditions from video on EDMS tab. | 02-00-TMU-P-1B
391543 | CR | 20190328 |  | 3 | (Non EN/CGS) Commercial Customer |  |  |  | N | NO | <D> **** Detailed Description **** (Non EN/CGS) Commercial Customer Calibration 6 NEW assets were recieved and set up with an incorrect prefix. <I> **** Actions Taken **** Asset number changed to reflect the correct prefix. The corrected certificates and stickers were sent to the customer and the customer was notified via email.
391545 | CR | 20190328 |  | 4 | Safety Near Miss - Handrail Obstructing Walkway | N | N |  |  | NO | <C> CAP Reviewed CR and moved to CR-SRO for OPS review. <D> **** ANONYMOUS CR - Detailed Description **** The handrail just inside the protected area is a safety hazard. As I entered the protected area I ran into the handrail and was nearly injured. The handrail is in the middle of the walkway immediately outside the double doors. It is difficult to see until you are upon it. Someone is going to get hurt. There has got to be a better solution. <I> **** Actions Taken **** Initiated CR
391547 | CR | 20190328 |  | 3 | License Reactivation doumentation incomplete |  |  |  | N | NO | <C> CR Priority/Severity changed to NCAQ â€“ 3 at the request of MRT (4.02.2019) <D> **** Detailed Description **** Two licensed Operators reactivation paperwork documentation for time on shift was incomplete as required IAW PPM 1.3.1, attachment 6.7. These reports have been cosistently added to reactivation paperwork for Objective Quality Evidence (OQE) purposes. The two subject personnel did not propely log in and out of eSOMS IAW eSOMS user guides. Improper login prevents the summary data from being provided to the report function in eSOMS. Evaluate eSOMS login process for improvements and trending. Repeat Issue, reference AR 373686, dated 11/9/2017. <I> **** Actions Taken **** CR Initiated.
391548 | CR | 20190328 |  | 4 | TDAS X413 data could not be obtained. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02132959-01, data for TDAS point X413 could not be obtained. All values during loop check were 0. <I> **** Actions Taken **** Notified Supervision and CRS. Continued with surveillance. Wrote CR and WR per step 7.6.12b. <N> **** Equipment Description **** 501RW MCR
391549 | CR | 20190328 |  | 4 | NET3-KVM-SW/2 Password expired early |  |  |  | N | YES | <D> **** Detailed Description **** NET3-KVM-SW/2 password was discovered to have expired early, requiring update to a new password. Investigation of configuration found it was set to 60 days, which does not align with the EC (13492) which states 90 days. The other KVM devices on the network are set to 90 days. This needs to be updated to 90 days in alignment with the EC. This does not affect Operations, these devices are only used by Computer Engineering for system administration. This is not a reportable condition. <I> **** Actions Taken **** Wrote CR and Generated WR | 02-00-NET3-KVM-SW/2
391550 | CR | 20190328 |  | 4 | AS-BLR-1 failed to start. | N | N |  | N | YES | <D> **** Detailed Description **** AS-BLR-1 (Aux Boiler) failed to start while investigating WR 29147601 for a previous failure to start. During the current start attempts the pilot ignition occurred but, were immediately followed a â€œLow atomizing air pressureâ€ alarm and a â€œSafety Shutdownâ€ occurred. AS-PS-8 was monitored during one of the start attempts and no movement was observed. SA-V-205 was warm to the touch indicating that it was energizing. The media Selection Switch was verified set to AIR per the ARP. Recommend installing a test gauge on AS-PI-8 line to investigate cause of low atomizing air alarm and subsequent trip. <I> **** Actions Taken **** Informed supervisor and wrote CR/WR. <N> **** Equipment Description **** T 441 G4/4.5 | 02-00-AS-BLR-1
391552 | CR | 20190328 |  | 3 | QA Missed Opportunity |  |  |  | Y | NO | <D> **** Detailed Description **** A missed opportunity review performed under AR 388333-02 confirmed that Quality Services had the opportunity to elevate or bring to the attention of Operations Management the steady trend of failures in Licensed Operator Requalification (LORQ). Continuous monitoring activities followed the steady trend but failed to act on the trend prior to the 2018 Annual Exam cycle. Subsequently, annual exam failures resulted in an NRC Finding. . See EDMS for AR 388333 for the complete Missed Opportunity Screening Report. Quality recommends assignment of this CR to AR-Quality. Enablers of Excellence missed include Verification/Validation and Worker Practices. <I> **** Actions Taken **** Informed QA Manager and initiated CR.
391553 | CR | 20190328 |  | 3 | IER Response-Administrative Errors (asgn numbers) |  |  |  | N | NO | <D> **** Detailed Description **** During data review for the M&T Training self-assessment an administrative error in Columbia's response to L2-17-9, "Weaknesses in Maintenance Technical Fundamental Skills Adversely Affecting Plant Operations" was identified. One referenced AR number in the response Rec 4A and four AR numbers in Rec.4B do not match up to the actual AR assignments in portal J. <I> **** Actions Taken **** Documented in self-assessment, discussed with training management.
391554 | CR | 20190328 | CAQ | C | Improper approval of CAQ Assignment 380257-09 |  |  |  | N | NO | <D> **** Detailed Description **** Corrective Action assignment (380257-09) did not get approved in accordance with SWP-CAP-01, 4.6.2. a. 3) DOCUMENT Owed to Group Managerâ€™s approval (e.g. in the closure notes or via an assignment route list). Recommend Assign to C/SYSENG to resolve. <I> **** Actions Taken **** Contacted department by email and voice messages, wrote CR.
391555 | CR | 20190328 | CAQ | C | Improper extensions of CAQ Assignment 388941-03 |  |  |  | N | NO | <D> **** Detailed Description **** Corrective Action assignment (388941-03) did not get Approved for 2 Extensions in accordance with SWP-CAP-01, 4.11.2. a. IF the corrective action assignment is for a severity A or B AR-CR, THEN PERFORM the following: 1) DOCUMENT the extension justification, including an assessment of the risk, in the In-Progress Notes tab of the assignment. 2) REQUEST due date extension approval as follows: a) IF first extension request, THEN OBTAIN approval from Owed to Group Manager. b) IF second extension request, THEN OBTAIN approval from: (1) Owed to Group Manager, and (2) Plant General Manager Recommend Assign to C/MMGR to resolve. <I> **** Actions Taken **** Contacted department by email, wrote CR.
391556 | CR | 20190328 |  | 3 | Different OMM component listed in Asset Suite for EDR-HX-1 |  |  |  | N | NO | <D> **** Detailed Description **** The OMM listed in Asset Suite for EDR-HX-1 (CVI OMM 921 -00,1) appears not to agree with the heat exchanger installed in the plant. The installed heat exchanger is a shell and tube heat exchanger, yet the OMM only specifies a plate and frame heat exchanger which differs in physical configuration. This issues has been discussed with the EDR heat exchanger system engineer. . This is not a plant equipment issue. This is only a documentation issue. <I> **** Actions Taken **** Initiated AR-CR. . Informed system engineer of submission of AR-CR.
391557 | CR | 20190328 |  | 3 | Missed Opportunities for Formal Training |  |  |  | N | NO | <D> **** Detailed Description **** This deficiency was identified during the Maintenance and Technical Training Comprehensive Self-Assessment. There are some examples where Columbia has over utilized informal training, resulting in missed opportunities in employing the systematic approach to training. Examples include, the recently completed Human Performance sessions deemed necessary due to recent Area for Improvement, briefings for Foreign Material Exclusion and Configuration Control, and the recent successful practice session for valve work that did not consider the Just in Time Training (JITT) process. In most cases, training time has been used to complete these tasks and the tasks should be evaluated using the systematic approach to training to ensure the informal training is meeting the needs of the station. <I> **** Actions Taken **** Included in self-assessment report and discussed with training management.
391559 | CR | 20190328 |  | 3 | Columbia's SAT Knowledge has Declined |  |  |  | N | NO | <D> **** Detailed Description **** This was identified during the Maintenance and Technical Trng Self-Assessment. During multiple interviews with non -training station personnel at varying levels and multiple organizations, it was determined that the individuals did not understand their role in the systematic process. This knowledge gap has led to not understanding the performance analysis process, the importance of the criticality when performing management observations of training, a low number of Living Accreditation Self Evaluation Reports (LASERs) for technical training. A potential contributor is the elimination of Curriculum Review Committees (CRC) which reduced the opportunities for direct incumbent and line management engagement resulting in at least one program operating in reactive mode following CRC elimination. <I> **** Actions Taken **** Documented in self-assessment and discussed with training management.
391560 | CR | 20190328 |  | 3 | Missed Reinforcement of Management Expectations in Training |  |  |  | N | NO | <D> **** Detailed Description **** This was identified during the Maintenance and Technical Trng Self-Assessment. During the assessment, there were two observations during one electrical lab activity that identified a lack of reinforcement of management expectations. In the activity, the supervisor and instructor did not refer to the standard documented in the lab guide. Also, during the same activity, insulated tools were not used while performing work in the electrical panel. Although this was a mock-up and there was no actual safety concern, this may send the wrong message to the students that insulated tools are not required for this working in these conditions. <I> **** Actions Taken **** Documented in self-assessment report and discussed with training management.
391561 | CR | 20190328 |  | 4 | Security HGUs need maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security HGUs are not functioning as designed. Contact security for additional information. <I> **** Actions Taken **** Notified security and I&C management. Initiated CR/WR | 02-00-SEC-HK-4,02-00-SEC-HK-5
391562 | CR | 20190328 |  | 3 | e520-8 converted to PDF in error |  |  |  | N | NO | <D> **** Detailed Description **** E520-8 was designed as an XL spread sheet to aid in grouping and searching functions. The latest revision converted it to PDF format which is not nearly as useable for grouping similar items. The AR 346782 which was the change document driving the last change has the correct XL sheet attached to the EDMS. Suggest convert back to XL to enhance the searching and grouping functions as originally designed during project construction.
391563 | CR | 20190328 |  | 4 | E-M-M2/F10 tripped during normal operation | N | N |  | N | YES | <D> **** Detailed Description **** A main-2 transformer alarm was caused by E-M-M2/F10 as it had tripped on a normal group 4 start. Actions in 7.4.11 of ABN-TRANSFORMER were performed and the trip was reset per the CRS. The fan started normally. There were no abnormal sounds or other indications that there may be obvious degredation of the unit. There was a scaffold present but was not permitted to be used to get closer to the fan per a posted sign. It should be mentioned that this fan had issues a year or so back and it was worked. <I> **** Actions Taken **** Informed CRS and performed ABN actions. | 02-00-E-M-M2/F10
391564 | CR | 20190328 |  | 3 | CBD-FT-1 IMDS needs updating for new installation. |  |  |  | N | YES | <D> **** Detailed Description **** While performing WR 29146384 we discovered the IMDS was outdated for the newer software in GE Panametrics ultrasonic flowmeter model DF868. Found WOT 02000891 had previously addressed the changes but had not been implemented. <I> **** Actions Taken **** talked with supervision, created word document to update IMDS. | 02-00-CBD-FT-1
391565 | CR | 20190328 |  | 4 | Asset Suite does not reflect installed equipment MS-RMS-RV/X |  |  |  | N | NO | <C> Trend to CR 390472 <D> **** Detailed Description **** This is a legacy configuration documentation issue only and does not affect the proper operation of plant equipment. Asset suite panel D034, â€œInstallation Historyâ€ DOES list the correct switch Model CR2940UB203F1 for EPNs MS-RMS -RV/1A, 1B, 1C, 1D, 2A, 2B, 2C, 2D, 3A, 3B, 3C, 4A/C, 4B/C, 4C/C, 4D/C, and 5C/C. However, this model number does not reflect the optional OEM contact adder deck installed in these locations as was confirmed via walkdown, associated EWD drawing review, and discussion with the OEM. The adder deck increases the available number of switch contacts necessary for installation in these locations (physical plant configuration correct). This discrepancy is being addressed under AR OBS 390472 for the selection and approval of a replacement switch as the original is obsolete. The WO planner and WWM associated with WOs 02136023, 02136022, 02135237, 02136021, 02136020, and 02136019 have been notified of the spare parts impact. Supply Chain Services has been notified of the need for additional piece parts to support these work activities as scheduled (PO 354066 issued). <I> **** Actions Taken **** Notfied Supervisor, WWM, WO Planner, SCS <N> **** Equipment Description **** MS-RMS-RV/1A MS-RMS-RV/1B MS-RMS-RV/1C MS-RMS-RV/1D MS-RMS-RV/2A MS-RMS-RV/2B MS-RMS-RV/2C MS-RMS-RV/2D MS-RMS-RV/3A MS-RMS-RV/3B MS-RMS-RV/3C MS-RMS-RV/4A/C MS-RMS-RV/4B/C MS-RMS-RV/4C/C MS-RMS-RV/4D/C MS-RMS-RV/5C/C
391578 | CR | 20190328 |  | 4 | HSSF Transformer Making Unusual Noise | N | N |  | N | YES | <D> **** Detailed Description **** During peformance of cathodic protection surveilance, it was noticed that the green High Voltage Transformer in the Northwest Corner of the HSSF gated area was making an unusually loud buzz/arcing noise. The noise didn't appear to be a usual transformer humming noise. Also noticed some wetness around the bottom corners of the Transformer. Can't tell if it may be leaking something, or if it's residual snow melt from the storms we've recently had. No identifiable EPN, but it did have a sticker with the following codes (P/N?): CP0337004821, 000L6P08W73A <I> **** Actions Taken **** Notified Supervisor, took picture, Notified shift manager, wrote CR for trending <N> **** Equipment Description **** Green High Voltage XFMR in the NW corner of the HSSF
391579 | CR | 20190328 | CAQ | B | Unexpected actuation of HPCS-V-15&HPCS-V-1 during surveillan | Y | N |  | N | NO | <C> CR Severity changed to B assigned to AR-MMGR at the request of MRT (4.02.2019) RISK: Medium. CAUSE: Clear. Document and Correct â€“ Document Causes and create Corrective Actions. <D> **** Detailed Description **** Unexpected actuation of HPCS-V-15&HPCS-V-1 during surveillance (0213594901 ISP-HPCS-Q901) When craft was hooking up test equipment (digital multi meter) to HPCS-LS-1A valves HPCS-V-15 and HPCS-V-1 actuated. The Craft that was part of this surveillance noticed that this valve line up happened prematurely to when this actuation should have occurred during this surveillance. The craft at the switch recognized that the mini grabber test lead when stacked (connected to each other) essentially jumpering out the Level switch (completing the circuit). <I> **** Actions Taken **** The craft stopped immediately and contacted the CRS, SM and their supervisor. The craft supervisor CRS and SM evaluated the risk of the event and recognized that the actuation was within the scope of the surveillance, le switch would not have been affected or damaged by the â€œjumperâ€ and agreed on a back out strategy. The surveillance (ISP-HPCS-Q901) had the proper steps to restore the level switch and all unneeded steps in the surveillance where N/Aed with SM approval. Switch is restored, statement where taken and this CR was initiated. <N> Technicians in the field failed to verify that the leads were properly connected to the DMM, which were stacked on each other. The technicians in the field did not verify the integrity of their leads by checking resistance,which would have required the leads to be properly connected. The condition of the leads resulted in the acutation when it was put into use. Behaviors associated with this event have been corrected and event was shared with the shop. No further actions required. This event was reviewed as a potential PCSC Event, referencing PPM 1.3.81. The technicians had CRS/PSRO permission to perform the scheduled activity in accordance with the briefed procedure (ISP-HPCS-Q901). The component actuation was expected, only premature due to test equipment errors. IAW PPM 1.3.81, this error has been determined to not be a PCSC event. AGR 4/3/2019. This event did not constitute a risk to safe operations or equipment condition. See EDMS for more information.
391580 | CR | 20190328 |  | 4 | CAS-DPI-25B reading higher than normal | N | N |  | N | YES | <D> **** Detailed Description **** CAS-DPI-25B reading higher than normal. This reading is usually reading around 2-3" and now is reading from 9-12". <I> **** Actions Taken **** Contacted MCR and issued this AR/WR | 02-00-CAS-DPI-25B
391581 | CR | 20190328 |  | 4 | HSSF Barrier Ropes Degraded |  |  |  | N | NO | <D> **** Detailed Description **** The rope used to barrier off areas around the HSSF Facility are degraded and need replaced. In performance of a cathodic protection surveilance, we found a danger sign on the ground. The sun damaged rope it was attched to had been cut by the signs tie wraps. The rope barriers need maintenanced with new rope. <I> **** Actions Taken **** Notified supervisor, notified control room, took picture, wrote CR <N> **** Equipment Description **** Rope barriers around the gated HSSF Facility
391582 | CR | 20190328 |  | 3 | Microsoft patch issue, deployment delayed |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Microsoft patch KB4489886 has been removed from the control room workstation deployment scheduled for 3/28/19 10:30 PM, due to the patch causing issues opening multiple documents in SharePoint. See CR# 391436 â€œUnable to open multiple documents at once in SharePointâ€ Recommend NON-CAQ 3. <I> **** Actions Taken **** Notified IS Duty Officer. Removed patch from control room deployment.
391583 | CR | 20190328 | CAQ | D | Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-2603 due to high water level <I> **** Actions Taken **** Followed ARP. | 02-00-CRD-TK-125/2603
391584 | CR | 20190329 | CAQ | D | ROD ACCUMULATOR TROUBLE alarm on CRD-HCU-3003, high water | Y | N |  | N | YES | <D> **** Detailed Description **** ROD ACCUMULATOR TROUBLE alarm on CRD-HCU-3003 due to high water level. <I> **** Actions Taken **** Cleared alarm per SOP-CRD-HCU, informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-HCU-3003
391585 | CR | 20190329 |  | 3 | CW-P-2 secured | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of the shiftly chemistry data log it was noted that CW-P-2 was not operating. This pump is supposed to continuously operate to control flow through the CW coupon station on 441' TB. Cause unknown, however, it is possible that the bypass was throttled during/after sampling at the coupon station. <I> **** Actions Taken **** The pump was restarted and the control room and chemistry supervision were notified of the abnormality. <N> PPM 12.9.10 is performed when changing corrosion coupons which is a quarterly PM (PMID 19596). The PM was last completed on 3/14/19 and samples are taken from CW-P-2 three times/week. CW-P-2 can be sensitive to tripping due to low suction pressure which is caused by the bypass valve being closed too far and starving the pump. Chemistry verifies that the pump is running every shift. Short losses of the pump have very little effect on the coupons performing their long term sample. | 02-00-CW-P-2
391586 | CR | 20190329 |  | 3 | 12.13.40 procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Several minor changes could be made to 12.13.40 to make it flow better. The procedure works as is, however, it could be better. <I> **** Actions Taken **** Created a marked up copy of the procedure and sent it to the procedure owner/ chemistry specialist.
391592 | CR | 20190329 |  | 3 | Update ABN-LEVEL for mode 4 and 5 abnormal level response |  |  |  | N | NO | <D> **** Detailed Description **** Update ABN-LEVEL for mode 4 and 5 abnormal level response to support use of ECCS pumps on unplanned RPV level drop greater than normal makeup capability. EOPs do not specifically cover mode 4 and 5 events and the current ABN does not address needed actions for response to unplanned RPV level losses GT the PPM 3.2.7 level control strategies. For R24, ECCS initiation capability is required but operations will not wait until RPV level reaches aut <I> **** Actions Taken **** Discussed with EOP lead. EOPs expected to be issued for R25 will cover mode 4 and 5 scenarios. This procedure change will provide a bridging strategy between now and R25 for a forced, maintenance, or refuel outage. Specifically, ABN-LEVEL changes need to combine actions of 4.1.6 and 4.1.8, add steps for mode 4 & 5 when level loss is greater than normal makeup capability of PPM 3.2.7. â€¢ Isolate suspected drain pathways â€¢ Inject via SOP-HPCS -INJECTION â€¢ Inject via SOP-LPCS-INJECTION â€¢ Inject via SOP-RHR-INJECTION
391593 | CR | 20190329 |  | 4 | SEC-CCTV-13 requires maintenance | N | N |  | N | YES | <D> **** Detailed Description **** SEC-CCTV-13 requires maintenance. Contact Security for more information | 02-00-SEC-CCTV-13
391594 | CR | 20190329 |  | 3 | MELTRIC WELD RECEP RETROFIT HRA/CA |  |  |  | N | NO | <D> **** Detailed Description **** WO 02087819-04 implement RIE 327158-change out house weld receptacles to new safety enhanced version (MELTRIC). Weld receptacle #2 RHR B HRA RB 441 L.1/8.5 is a HRA and a CA. This area is above RHR B pump on the deck. Depending on if the leads need to be reduced down this task could be 2-3 craft in the HRA/CA for up to 6 hours or more. With ALARA /dose concerns for this task, it would be best to make a "pig tail adapter" that could be staged for outage. This would take 1 craft 10 minutes max in the HRA/CA to plug in and would minimize dose that is unnecessary. A better plan could be in place for the future to replace this weld receptacle if needed <I> **** Actions Taken **** notified supervision, initiate cr, initiate wr <N> **** Equipment Description **** weld receptacle 2 RHR B 441 L.1/8.5
391595 | CR | 20190329 |  | 3 | Fix PM's that come out in READY status,WO's listed below |  |  |  | N | NO | <D> **** Detailed Description **** Fix PM's model WO's for the WO's listed 02133437-01, 02133449-01, 02133453-01 These WO's come out in the READY status (which is corret) Some tasks missing FMR hold, missing 15.2.39 not attached..Need to ensure models and tasked WO's are correct. <I> **** Actions Taken **** added 15.2.39 to WO 02133437-01, added FMR hold to WO's 02133449-01, 02133453-01. <N> When code was originally added to background hold codes for the PMs, the request was only made for 'SRO','RO' and 'WD' holds to be included. Modifications to the batch program will include all unreleased hold codes as part of the backgrounding process. . The work is being performed under CR 00391089.
391596 | CR | 20190329 | CAQ | D | CRD-FI-4A low flow | Y | N |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was observed that CRD -FI-4A had low flow of less than 0.12 GPH. Operator rounds require flow of equal to or greater than 0.12 GPH. <I> **** Actions Taken **** Notified CRS and wrote CR | 02-00-CRD-FI-4A
391597 | CR | 20190329 | CAQ | D | Rod Accumulator Trouble for CRD-HCU-5443. | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble, H13-P603.A7,6-7, alarm for CRD-HCU-54-43 due to moisture. OPS 2 cleared the alarm per SOP-CRD-HCU. | 02-00-CRD-HCU-5443
391598 | CR | 20190329 |  | 3 | Potential RC-1 and RC-2 work risk reduction |  |  |  | N | NO | <D> **** Detailed Description **** During WO 02138372 performance an RPS test box was installed to prevent the half SCRAM which work on CRD-LT -13A would otherwise cause; this avoided the risk of a full SCRAM caused by the failure of an RPS-B instrument or power supply. During the work on MS-LT-61A the risk of working on live wires (24V DC) was accepted to avoid de-energizing CRD-LT -12A. The station accepted the risk of mishandling a live lead during de-terming, taping, and re-terming. If the RPS test box had been used to prevent the half SCRAM caused by de-energizing the single power supply to both MS-LT-61A and CRD-LT-12A the risk of mishandling live leads would have been mitigated. <I> **** Actions Taken **** During the work on MS-LT-61A the station also accepted the risk of having an RC-1 half outboard/MSIV isolation. The risk to the station is that a failed instrument or power supply could cause a full outboard/MSIV isolation; which in turn causes a loss of containment cooling requiring a manual SCRAM. A jumper installed across MS-RLY-K104 contacts T2-M2 would mitigate the risk of a full outboard isolation. To use a jumper would require pre-planning; specifically the installation of sockets on the relay bases. The use of MS-RMS-S84 would mitigate the risk of a full MSIV isolation. An entry into a TSAS would be required for either action.
391599 | CR | 20190329 | CAQ | D | Broken hinge on EBU cover. | N | Y |  | N | YES | <D> **** Detailed Description **** While performing WO# 02133453, PPM 15.2.39. On E-BU -C121/441/1x1 we noticed that the top hinged cover was broken. The spot welds on the cover no longer connected the top cover to the hinge. This condition does not affect the operability of the emergency light, but should be corrected in the near future. <I> **** Actions Taken **** Initiated CR, and informed supervision, and also documented the condition in the work order. | 02-00-E-BU-C121/441/1X1
391600 | CR | 20190329 |  | 3 | Failure to source check GEM-5 at Bldg 356 (in-processing) |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The GEM-5 that is used for Passive Whole Body Monitoring for incoming outage workers in Bldg 356, was apparently not source checked prior to use for the week beginning 3-25-2019. This is a violation of HPI-12.93 (3.7 & 5.3). Additionally, the daily Operational Status Checks were apparently not performed the rest of the week. This is a violation of HPI-12.93 (3.6 & 5.2). <I> **** Actions Taken **** Inquired of supervision whether the weekly source check and daily Operational Status Checks had been done after being prompted by a Rad Support Specialist. There was no evidence of these required actions being taken for operation of the GEM-5. The eSoms logbook was reviewed as well as the current & historical version of the Stationary Equipment Source Check Log (form 26492). Aditionally, the local daily signoff card on the GEM-5 had no initials on it for the week. RP Supervision requested that I initiate this AR/CR. <N> **** Equipment Description **** This GEM-5 is located inside Bldg 356. Note: This instrument was calibrated 3/20/2019 and as part of the calibration, a post calibration source check is performed. This post calibration source check was successful.
391601 | CR | 20190329 |  | 3 | SOP-SO-START Procedure Enhancement | N | N |  | N | NO | <D> **** Detailed Description **** SOP-SO-START Step 5.4.10 references SOP-H2/CO2-OPS, Section 5.14 for draining Main Generator Liquid Detectors. SOP -H2/CO2-OPS has been revised since this step was written and the appropriate section is now 5.17. Recommend changing SOP-SO-START to reflect this revision. <I> **** Actions Taken **** Informed MCR, Wrote CR. . Crew processed an editorial change in APPW per SWP-PRO-02.
391602 | CR | 20190329 |  | 4 | EDR-DM-9 post BWPC at 11 psig on hold | N | N |  | N | YES | <D> **** Detailed Description **** EDR-DM-9 was backwashed and precoated per procedure. No issues, 2 bags of resin were used. DP was not looked at immediately following. After the precoat was complete the filter was placed in service in 'recycle' mode within about 15 minutes. DP stabilized at about 11 psig per EDR-DPIS-27 in the RWCR while in recycle having processed no water otherwise. Usually it is at 0 for several hours. This is unusual. CR for trending. | 02-00-EDR-DM-9
391603 | CR | 20190329 |  | 3 | safety issues with RW 487 new breaker area |  |  |  | N | NO | <D> **** Detailed Description **** New breaker test area power requirements need to be expedited. Need 480 power receptacle in the breaker area, need overhead 120V drop down outlets for test equipment and High bay led lighting install. (While installing 480 power, need clean 480 power in the relay shop right next to it should also be installed. Breaker area is in the process of being constructed and items listed need to get priority. There is temporary power installed, but it reguires cords to be strung for lighting, test equipment, power tools and 480 test plug. this makes it very hard to comply with extension cord requirements, a hinderance to completing work and tripping hazards. Craft are putting extra efforts on focusing on safety issues which is taking away from there focus for worker fundimentals on equipment. <N> **** Equipment Description **** RW 487 breaker area (and relay shop)
391604 | CR | 20190329 |  | 4 | Severe degradation of CW basin netting | N | N |  | N | YES | <D> **** Detailed Description **** CW basin netting is severely degraded. See attached photos. There are significant FME concerns with the netting in this condition. Netting is falling into the basin and entering the CW system. The open hole also allows birds to enter. Recommend replacing netting as soon as possible. <I> **** Actions Taken **** Notified CRS <N> **** Equipment Description **** CWPH Basin ***General Notes*** The netting at the Circ Water Basin is not for FME purposes, The netting is there for personal safety reasons.
391605 | CR | 20190329 |  | 3 | Williams Electricians Replaced 8' light tubes unnecessarily |  |  |  |  | NO | <C> CAP Reviewed, moved to OPS for review. <D> **** ANONYMOUS CR - Detailed Description **** Williams electricians installed several 8' light tubes in the RX 471' and 501' RX building that had already been identified as having bad ballists, thus wasting perfectly good light tubes and time & money. The regular Energy Northwest electricians already knew that these fixtures were no good and replacing them with LED compatible ones is planned. This is IBEW Local 77 work that was assigned to contractors on overtime and unfortunately, was only partially effective and somewhat wasteful, even without figuring in that the contractors were scheduled for overtime without much, if anything, to do that doesn't tread on the regular EN electricians. The work order task used was 0213032501. <I> **** Actions Taken **** Initiated CR. Initiating grievance.
391606 | CR | 20190329 | CAQ | D | CRD-LS-613A FIL-2 Shield wire termination | Y | N |  | N | YES | <D> **** Detailed Description **** On GG-25 the Shield and Ground are stacked instead of utilizing both sides of the termination block. <I> **** Actions Taken **** At step 4.47.3 of 0213837201 had Supervisor *1 and noted in the comment section below the step. | 02-00-CRD-LS-613A
391607 | CR | 20190329 | CAQ | C | SRM channel B failed PMT following replacement of HVPS | Y | Y |  | N | YES | <D> **** Detailed Description **** On 3/28/2019 HVPS PS21 for SRM Channel B (SRM-EMSQ-600B) was replaced by WO 02109358.the HVPS failed again at Step 7.10.10 of ISP-SRM-X302 during performance of ISP fro PMT WO 02109358-01. <I> **** Actions Taken **** Operations was notified. CR writen to document and generated new WR | 02-00-SRM-EMSQ-600B
391608 | CR | 20190329 |  | 4 | TOA-FN-2A tripped on high exhaust temperature | N | N |  | N | YES | <D> **** Detailed Description **** ON 3/29/19 DAYSHIFT, RECEIVED TURBINE GENERATOR BUILDING FAN TOA-FN-2A EXHAUST TEMPERATURE GT 140F ALARM (TGHV.2A 1-1). THIS RESULTED IN AN AUTOMATIC TRIP OF TOA-FN-2A. Investigation revealed TOA-V-21A (steam supply AOV) was open with its control switch in close. TOA-TIS-24A was indicating ~ 140F. Outside ambient temperature was 55F to 60F. TOA-V-21A was previously documented as not closing - even with its control switch in close by WR 29147696. Heating steam was secured to the west side of the Turbine Bldg. per SOP-COLDWEATHER-OPS and TOA-FN-2A was restarted to return Turbine Bldg. HVAC to a 4 TOA fan / 3 TEA fan lineup. Suspect issue with TOA-V-21A mechanical binding or TOA-TIS-24A. <I> **** Actions Taken **** Notified the CRS and Shift Manager. Submitted CR & WR for documentation. Heating Steam secured to Turbine Building west side and TOA-FN-2A restarted. | 02-00-TOA-V-21A
391609 | CR | 20190329 | CAQ | C | (NRC) SW EJ Tie Rods Appear Loose | Y | N |  | N | YES | <D> **** Detailed Description **** SW-EJ-1A, -1B and -2 are bolted to the discharge of SW-P -1A, -1B and HPCS-P-2, respectively. They are flexible metal joints to absorb the vibration energy and thermal expansion between the SW piping and pump nozzles. Each EJ has four tie rods. Some of these tie rods are loose when rotated by hand . SW-EJ-1A: both tie rods on the North side have a gap. ~3/32" on the upper tie rod and ~1/8" on the lower tie rod. All nuts on these tie rods are more than hand-tight. The upper bar on the south side has no loosenes or gap, but the outer nut on the pump side is only hand-tight. SW-EJ-1B: There is slight rotation on the East side upper tie rod. All nuts are more than hand -tight. SW-EJ-2: Both upper and lower tie rods on the North side are loose, with about a 1/6" gap. The upper tie rod is loose on the South side, again with a ~1/16" gap. All nuts are more than hand-tight. <I> **** Actions Taken **** Verified condition. Contacted Engineering for questions on seismic impact. | 02-00-SW-EJ-1A,02-00-SW-EJ-1B,02-00-SW-EJ-2
391610 | CR | 20190329 | CAQ | D | Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-4207. Alarm was high water level. <I> **** Actions Taken **** Followed ARP. | 02-00-CRD-TK-125/4207
391611 | CR | 20190330 |  | 4 | TOA-FN-1A Belts All Broken | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FN-1A has all its belts broken. This loss of Turbine Building HVAC flow brought in P601-A3 drop 3-6 for Leak Detection Turbine Building Temp High alarm. Please replace the belts. <I> **** Actions Taken **** TOA-FN-1A has been secured. | 02-00-TOA-FN-1A
391615 | CR | 20190330 | CAQ | D | Oscillograph Started Alarm | N | N |  | N | NO | <D> **** Detailed Description **** Received 4.800.C4 4-3 Oscillograph Started Alarm. Plant controllers and equipment response was normal. TRS: 239/239/239KV. TRB: 118/118/118KV. J7 500KV Neutral Ground O.C. was tripped and reset. Cause was Lower Monumental -McNary line tripped single pole and reclosed. No damaged equipment. No RAS initiated. 230 KV and 115 KV not affected.
391616 | CR | 20190330 |  | 4 | DEH-AC-IR/TRIP has a loose bare end wire inside | N | N |  | N | YES | <D> **** Detailed Description **** There is a loose bare-ended wire inside the enclosure for the DEH air conditioning controller; appears to have become disconnected from the back of the control module and could be energized. Please investigate and repair as necessary. <I> **** Actions Taken **** informed CRS, wrote AR and WR coordinated with maintenance (electrical) to make exposed wire electrical safe (taped off wire). The exposed wire safety hazard has been addressed. It is unclear what function the wire serves. The unit is running propelry with no adverse indications. | 02-00-DEH-AC-IR/TRIP
391617 | CR | 20190330 |  | 3 | RWCU-V-44 issues for R-24 |  |  |  | N | YES | <D> **** Detailed Description **** RWCU-V-44 is documented to be leaking approximately 100 gpm per AR 390846.During the R-24 outage, the preferred letdown path is RWCU to the main condenser per PPM 3.2.7. P&L 4.13 states that if not in an emergency RWCU letdown to the condenser with RWCU-V-44 open is not advisable. The other option is to send RWCU letdown to radwaste tanks, which for long periods of time is not a good option due to radwaste processing issues during the outage. Also, the R -24 water plan is not out for review yet, but could pose a problem if letdown is directed elsewhere. Please provide to operation a plan to letdown during the outage. <I> This is not new issue - see CR 390846 for initial issue IOD. This issue addresses the plan for plant operations with the known condition. | 02-00-RWCU-V-44
391618 | CR | 20190330 | CAQ | C | HPCS-RLY-51V/B red target was in; reset ok | Y | N |  | N | YES | <C> CR reopened to cross reference additional W0 02126101, marked completion required box, then taken back to complete <D> **** Detailed Description **** Noticed the red target was dropped on HPCS-RLY-51V/B, which is the overcurrent time delay voltage restraint relay for the HPCS Diesel. Informed the CRS and the target reset ok. OSP-SW/IST-Q703 was in progress at the time of discovery; unknown if this relay target was related to that. <N> WR 29147830 initiated to replace the realy during the next 4 year PM. | 02-00-HPCS-RLY-51V/B
391619 | CR | 20190330 |  | 3 | OSP-SW/IST-Q703 step needs re-written |  |  |  | N | NO | <D> **** Detailed Description **** Currently, step 7.5.11 reads: Quick connect fitting downstream of SW-V-703 REMOVED. New step should read: Quick connect plug downstream of SW-V-703 INSTALLED. This change would align this procedure to the I&C step of 7.5.1c <I> **** Actions Taken **** Informed CRS
391620 | CR | 20190330 |  | 4 | T1 sump high level alarm - no lights at breaker or switch | N | N |  | N | YES | <D> **** Detailed Description **** Need to check T1 sump, FD-P-12, fuses at MC-2P3D due to no lights on breaker or on pump switch in RWCR. High level alram came in at end of day shift. | 02-00-FD-P-12
391649 | CR | 20190331 | CAQ | D | Oscillograph Started Alarm with TR-B trouble alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm and TR-B TROUBLE C4.2-5. Plant controllers and equipment response was normal. TR-B trouble alarm immediately cleared.Reference AR Startup and Backup voltages are as follows: E-TR-S A: 239 B: 239 C: 239 E-TR-B A: 118 B: 118 C: 118 The following sensors were tripped and are reset: J8, J9, and J15. Cause was Midway-Benton #2 230KV relay off then on. No damaged equipment reported. Relaying involved unknown single pole or multiphase. No RAS initiated.
391650 | CR | 20190331 | CAQ | D | Oscillograph start alarm when CW-P-1B started | Y | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.drop 4-3 alarm when CW-P-1B was started. The alarm was due to sensor J12 (SM8 Undervoltage). The J12 sensor reset. E-TR-S and E -TR-B voltages are 239/240/239 kV and 118/118/117 kV. All plant controllers and equipment exhibited normal operation
391651 | CR | 20190331 |  | 4 | CW-V-1B lost indication for 15 minutes | N | N |  | N | YES | <D> **** Detailed Description **** While starting CW-P-1B, CW-V-1B green light took about 3 minutes to extinguish (as expected), the red light did not come on for 15 minutes (should have come in within seconds) . The valve operated as expected verified locally. <I> **** Actions Taken **** WR written. <N> **** Equipment Description **** CWPH | 02-00-CW-V-1B
391652 | CR | 20190331 |  | 4 | FD-P-12 line fuses (all three) found to be cleared | N | N |  | N | YES | <D> **** Detailed Description **** While investigating the reason FD-P-12 wouldnâ€™t run for AR# 00391620, the Electricians found all three line fuses were cleared in MC-2P3D. There was no apparent reason this would have occurred. There are no obstructions or anything that would interfere with the operation of FD-P-12 inside Sump T1 that can be seen through the small access door on top of the sump. The Electricians replaced all three bad lines fuses and now the sumps high level alarm is clear and the pump appears to work fine. <I> Placed item on weekend issues list. | 02-00-FD-P-12
391653 | CR | 20190331 |  | 4 | Lack of plan for FDR-TK-22 resin removal | N | N |  | N | NO | <D> **** Detailed Description **** See write up in EDMS <I> **** Actions Taken **** Added item to plant concerns list and informed the Station key personel to address the issue <N> Cross referenced WO 02138607 is scheduled to be worked on 04/02/19.
391654 | CR | 20190331 |  | 4 | MCR unable to make off-site calls through XO Communciations | N | N |  | N | NO | <D> **** Detailed Description **** Outbound off site phone calls from the MCR were getting dropped to dead air due to Telco Carrier XO Communications call routing issue between 5:45pm to 6:00pm. <I> **** Actions Taken **** Contacted the MCR at approx 6:40pm and spoke with Steve, asked if he would make a few test calls while I traced the calls in Avaya to see where they were failing. He called my cell phone back, and I saw the call go through just fine in the system, he then tried his cell phone, and also was able to get through okay. Issue seemed to be resolved before this testing. Recommend NCAQ-4 Note - cell phone referenced was a company CISCO phone and not a personal cell phone. Outbound phone call service restored with no action taken. <N> Verified ENS line was functional by making and then receiving an ENS call with NRC headquarters operations officer. Confirmed with IS duty officer that the momentary issue did not affect crash line either.
391655 | CR | 20190331 | CAQ | D | RHR-P-2B Discharge Pressure Trending Up | Y | Y |  | N | YES | <C> Trend to CR 390620 <D> **** Detailed Description **** RHR-P-2B discharge pressure is slowly rising, reference point X076, which is reading 347 psig. The Annunciator Response Procedure, 4.601.A2 drop 5-6, for RHR B Pump Discharge Pressure High/Low alarms at 455 psig and has steps to lower pressure by venting through the RHR heat exchanger vents. CR written for trend. <I> **** Actions Taken **** Wrote CR. | 02-00-RHR-P-2B
391656 | CR | 20190401 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm | N | N |  | N | NO | <D> Received Oscillograph Started, H13-P800.C4.4-3, alarm Plant controllers and equipment response was normal. Reference AR 00391656 Startup and Backup voltages are as follows: E-TR-S A: 240 B: 240 C: 240 E-TR-B A: 119 B: 118 C: 117 The following sensors were tripped and are reset: J7 500KV Neutral Ground Overcurrent. <N> BPA reports the following a. Cause was Momentary relay Rock Creek/Wautoma. b. Relaying involved a single pole c. No damage d. Line auto reclose. e. no outage f. 500KV i. 0246
391657 | CR | 20190401 |  | 3 | Corrections for ABN-CR-EVAC | N | N |  | N | NO | <D> **** Detailed Description **** The following issues were found in ABN-CR-EVAC and should be corrected in the next revision: . 1. Each attachment is listed twice in the Table of Contents. . 2. The flow chart lists actions for â€œTGSSâ€. This should be changed to â€œEOSSâ€ to match elsewhere in the procedure and flow chart. . 3. Step 7.11.10.e specifies to close RCIC-V-63 but does not explain how. This is necessary because there is no RMS on the RSD for RCIC-V-63. . 4. Step 7.18.4.y specifies to verify RHR-V-53B and RHR-V-23 are closed but does not explain how. This is necessary because there is no RMS on the RSD for either RHR-V-53B or RHR-V-23. . 5. Steps 7.18.4.w and 7.19.10 lists actions for EPNs â€œRRC -RPT-3Aâ€ and â€œRRC-RPT-3Bâ€. These EPNs should be corrected to â€œRRC-CB-RPT/3Aâ€ and â€œRRC-CB-RPT/3Bâ€ respectively. . 6. In Attachment 7.23, correct â€œBeltineâ€ to â€œBeltlineâ€ in horizontal axis. <I> **** Actions Taken **** Recommend condition report be directed to AR-OPSPROC to correct procedure. <N> CR is incorrect about RCIC-V-63, RHR-V-53B, and RHR-V-23. They are on the RSD panel controls.
391693 | CR | 20190401 | CAQ | D | CRD-HCU-3027 3 alarms in 30 day period (water) |  |  |  | N | YES | <D> **** Detailed Description **** The subject HCU alarmed 3 times within 30 days for same condition (2/28/19, 3/8/19 and 3/28/19), which constitutes a Reactivity Management Level 5 Concern. Reference PPM 1.3.79, Degraded Reactivity-Related System Performance (5 -4) HCU Accumulator Alarm trend for CRD that meets standard for scheduling maintenance (CGS std: 3 or more accumulator alarms in a 1 month period caused by the same condition) This is not an operability concern. <I> **** Actions Taken **** Notified System Engineer. <N> **** Equipment Description **** R -522- - -L5/8.4 ... Disregard this AR, it is a duplicate of 382995, which is being worked in R24 under 02109735. See individual CR for IODs. | 02-00-CRD-HCU-3027
391697 | CR | 20190401 | CAQ | C | Three Engineering Assignments not closed In IAW SWP-CAP-01 |  |  |  | N | NO | <D> **** Detailed Description **** Three assignments in Severity "B" CR 380257, "Reactor Scram Main Transformer Trip" were not closed by the Owed to Group Manager in accordance with SWP-CAP-01, step 4.6.2.3, as follows: 380257- 09, assignment type â€œCAIâ€, closed by the SEEIC supervisor . 380257- 17, assignment type, â€œRCâ€, closed by the DESENG Manager . 380257- 20, assignment type â€œDCâ€, closed by the DESENG Manager . The Owed to Group Manager is SYSENG. <I> **** Actions Taken **** Documented the procedure non-compliance in this CR and informed involved parties. Assignments 380257-17, 20 have been reclosed correctly at the time of this CR initiation. Assignment 380257-09 has closed IAW SWP-CAP-01 on 4/2/19. Thumbs Down write-up submitted, procedure adherence has been coached at D-15 meetings on 4/2/19. <N> Verification/Validation: The proper The proper procedure (SWP-CAP-01) necessary to successfully complete the task of closing the Corrective Action assignments was not reviewed, verified, or validated. . . Supervisor Oversight: Challenges that would have prevented correct closure of the corrective action assignments were not identified and resolved. the guidance in SWP-CAP-01 was not reviewed or applied. . . Worker Practices: Error Prevention Tools (EPT) such as STAR, Task Preview, and Take 2 were not rigorously applied.
391699 | CR | 20190401 |  | 4 | Oil Spill in Deschutes Parking Lot |  |  |  | N | NO | <D> **** Detailed Description **** A small oil spill was discovered in the South Deschutes parking lot. Approximately 1 gallon of oil spilled to impervious surface. Spill appeared to come from a personal vehicle no longer on site. <I> **** Actions Taken **** Contacted F&CE for spill cleanup. Spill is not reportable. No further action is needed. <N> E&RP verified spill has been cleaned up.
391701 | CR | 20190401 |  | 3 | HIPAA Violation |  |  |  | N | NO | <D> **** Detailed Description **** On Saturday, 3/30/19, a previous EN employee informed a current EN employee that they had requested personal Access Authorization records and mistakenly received two confidential/personal documents of the current employee (with SSN on each). The personal records request occurred in January 2019. <I> **** Actions Taken **** Informed Supervision, HR, and initiated this CR. Access initially reviewed and discussed with occupational health and they indicated it was not a HIPAA violation. However, additional evaluation is assigned to be conducted to review further.
391702 | CR | 20190401 | CAQ | C | (QA) WO Not Routed to QC for Review |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) WO 02111387-15 for RFW-HX-6B R24 maintenance work activity was not routed to QC for Initial Review as required per MI.1.22A. Issue was identified by Craft Foreman and QC during discussions related to separate WOTs 02111387-01 & 14. Quality Control contacted Maintenance Planning, â€œQCIâ€ soft applied on the work task and QC review was completed & approved. <I> **** Actions Taken **** Notified Quality Services QC Supervisor, Maintenance Planner, and Williams Craft Foreman. <N> **** Equipment Description **** WOT at Ready Status for R24. No work performed.
391703 | CR | 20190401 |  | 3 | Inconsistent definition of SPV (Procedures) |  |  |  | N | NO | <D> **** Detailed Description **** This is a documentation issue only. Procedures SYS-2-24 and SYS-2-17 do not match the most recent definition of a Single Point Vulnerability (SPV), which is a subset of critical components whose failure will directly result in a turbine trip and/or reactor scram. Recommend revision to SYS-2-24 and SYS-2-17 to reference the most recent SPV definition found in EGM-1-9.
391704 | CR | 20190401 |  | 3 | Inconsistent definition of SPV (System Manuals) |  |  |  | N | NO | <D> **** Detailed Description **** This is a documentation issue only. Many of the System Description Manuals (MAN SYS SDxxxxxx) do not match the most recent definition of a Single Point Vulnerability (SPV), which is a subset of critical components whose failure will directly result in a turbine trip and/or reactor scram. Recommend revision to the System Description Manuals to reference the most recent SPV definition found in EGM-1-9 and to reference the â€œEquipment Reliabilityâ€ Team Site for a listing of the relevant system single point vulnerabilities.
391706 | CR | 20190401 | CAQ | D | CMS-P-1401 shows step change in vibration | Y | Y |  | N | YES | <D> **** Detailed Description **** The data for several points shows an increase at 89.4 Hz and 119.8 Hz. The spectral data for the motor axial point, Point MOA, indicates the greatest change from previous data sets. Amplitudes are high at 0.92 IPS-Pk. The frequency is at 3X Operating Speed (89.4 Hz). Based on the increase in the axial direction and the frequency seen, there maybe issues with the motor to pump coupling. Recommendation is to take another set of vibration data ensuring proper placement of the sensor and normal pump operation. <I> **** Actions Taken **** Submitted WR to get another vibration data set. Notified FIN manager and supervisor. | 02-00-CMS-P-1401
391708 | CR | 20190401 |  | 3 | ESD Near Miss at MPF |  |  |  | N | NO | <D> **** Detailed Description **** On 3/29/19, employee had a near miss while attempting to lock the MPF revolving door. Using situational awareness, the employee waited until all people had finished using the revolving door before starting to place the revolving door in the position to lock it. While having eyes on the task and looking up to place the door in the correct position, a person located outside the building used the revolving door which almost caught the employee's arm in the door while in the process of preparing to lock it. The employee was able to quickly move out of the way of the moving door to avoid any injury or first aid damage. This is a task that is performed twice-daily without previous incident. Past success by staff without incident may have led to lack of identification of hazards. <I> **** Actions Taken **** Employee's management was notified next business day of near miss. Industrial safety was consulted and confirmed that this is NOT a "significant" near miss based on the facts and that NO first aid was required. As such, no event investigation is necessary under GBP-ESD-03. Corrective Actions to be taken: Work with ENOC facilities to obtain a wedge for a revolving door that can be used to prevent this type of risk in the future when unlocking and locking the revolving door. Brief staff who perform this task on risk and lessons learned. Further I will educate my staff on appropriate process for reporting a near miss. <N> Reassigned owed to group by request from Owed to group manager. Was AR-VPEBS moved to AR-VPESD.
391709 | CR | 20190401 |  | 4 | Service Air header to the RWCU deminâ€™s will not depressurize | N | N |  | N | YES | <D> **** Detailed Description **** Near the end of the RWCU-DM-1B backwash section, the air pressure as read on SA-PI-71 is not decreasing. SA-V-23 and/or SA-F-69 appear to be plugged. Air not depressurizing from the filter at its normal rate when drain valve SA-V-23 is opened two turns, IAW SOP-RWCU -DEMIN, Step 5.5.7y. This is becoming a frequent problem when doing backwashes on the cleanup demins. <I> **** Actions Taken **** inform Shift Supervision | 02-00-SA-F-69
391710 | CR | 20190401 |  | 3 | cam-ptz-379 wiring wrapped around hoist | N | N |  | N | NO | <D> **** Detailed Description **** cam-ptz-379 blue cable located on the 548 reactor at m5/4 .1 is wrapped around mt-hoi-21. <I> **** Actions Taken **** contacted david strecker telcom architecture supervisor my supervisor and wrote this cr <N> **** Equipment Description **** 548 reactor m5/4.1
391711 | CR | 20190401 | CAQ | C | Electronic RP Survey information not sent to records |  |  |  | N | NO | <D> **** Detailed Description **** The monthly electronic download of RP VSDS Surveys record failed to complete successfully. The barriers identified the failure quickly as the process had anticipated and planned for, allowing IS to quickly troubleshot and prevent a backlog survey data transmit failures. <I> **** Actions Taken **** Notified RP-Supervision and IS. IS currently evaluating cause. <N> Per IS Analyst, all RP surveys were sent to records on the afternoon/evening this condition was discovered.. There are currently, as of 5/1/19, no unsent RP surveys in the system. The AR assignment closed received review and approval by an IS supervisor for closure
391712 | CR | 20190401 |  | 3 | PCSC Committee Meeting Attendance |  |  |  | N | NO | <D> **** Detailed Description **** April PCSC Committee Meeting was conducted on 4/1/2019, 1130 in GSB1. Two members were missing form maintenance department, I&C shop technician and mechanical shop technician. Invitations and Agenda were sent well in advance. <I> **** Actions Taken **** CR Initiated.
391713 | CR | 20190401 |  | 4 | Detached Transmitter Bldg 17 Exterior North Face | N | N |  | N | YES | <D> **** Detailed Description **** On the external North Face of Building 17, at the East end, a conduit is in place. Extending from the junction box is a transmitter reading "Centurion Wireless Technologies, Inc. Linear Directional CAF94569" and is hanging from the wire, no longer attached to the wall. <I> **** Actions Taken **** CR Created <N> **** Equipment Description **** Bldg 17, external north face, east end
391714 | CR | 20190402 | CAQ | D | Received H13-P814 drop 3-1 NOBLE GAS RAD ALERT alarm. | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02128123, then taken back to complete <D> **** Detailed Description **** Received H13-P814 drop 3-1 NOBLE GAS RAD ALERT alarm. CMS -RIS-12A channel 1 is above ALERT level at 2.11E-06 and steady. CMS-RIS-12B channel 1 is at 2.32E-06 and steady and well below its ALERT level. The ALERT level is set approximately 5 times lower on alarming channel. <N> Reference T19-CMS-RIS-12A-001. | 02-00-CMS-RIS-12A
391730 | CR | 20190402 |  | 4 | HP dose over the goal for March |  |  |  | N | NO | <D> **** Detailed Description **** HP received 517mrem against a goal of 473mrem in the month of March. Emergent work in March was the reason for going over our dose goal. <I> **** Actions Taken **** Wrote CR <N> Details of March 2019 dose has been uploaded into EDMS.
391731 | CR | 20190402 | CAQ | D | E-SM-1 unit 11 is missing parts | N | N |  | N | YES | <D> **** Detailed Description **** E-SM-1 unit 11, cubicle for E-CB-CDTP, is missing several parts. The MOC assembly pantograph channel and linkage is not installed. The MOC switches and the connecting rod between the switches and channel are present. As all the MOC switch contacts are spares, these components are not required for E-CB-CDTP operation. However, the cubicle does not meet the design configuration and the missing parts should be procured and installed. | 02-00-E-SM-1
391734 | CR | 20190402 |  | 4 | Ice Machine in GSB 441' Lunchroom does not work |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Ice machine in the GSB 441' lunchroom does not make ice. Ice machine stopped making ice following filter maintenance and troubleshooting filtered water pressure. This maintenance occurred week of 25 March. <I> **** Actions Taken **** No action has been taken except creation of this condition report. Repairs or troubleshooting require a qualified and knowledgeable worker. <N> **** Equipment Description **** GSB 441' Lunchroom
391737 | CR | 20190402 | CAQ | D | M&TE Rejected |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calccode #45417 White Box Hygrothermograph- model CT485AL found OOT. Used at 487' Chem Lab. EFIN Eval: a. All equipment used have a Cal check performed. If room temperature was outside tolerances, the check would reveal that situation. No Impact. b. If room was actually at indicated temp, Lab personnel would have noticed. 80Deg F vs 72DegF. No Impact. DEF #6968A written. Rejected- Unable to adjust. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391738 | CR | 20190402 |  | 4 | Multiple lockouts of RW elevator. | N | N |  | N | NO | <D> **** Detailed Description **** Multiple lockouts of the RW elevator have occured over several days due to personnel holding open the door manually, instead of using the "door open" push button located inside the elevator. This requres operator action to reset the fault on the computer motherboard located in the RW elevator machinery room. Reccomend postind signs inside the elevator and on each floor indicating that the button in the elevator must be used to hold open the door. <I> **** Actions Taken **** Reset elevator fault and notified supervisor. <N> **** Equipment Description **** RW
391739 | CR | 20190402 |  | 4 | E-RLY-81T1, DWG needs updating, 2 issues |  |  |  | N | NO | <D> **** Detailed Description **** E-RLY-81T1 was replaced 5/14/45 with a new model per WO 02040881-01 and the new UTC 533351 was installed in Portal J. 1st issue is the drawings were not updated and need to be updated with the new model #. 2nd issue is the current process we use missed documenting (drawings) model changes. Need to look at current process and understand why and how we will correct missing these types of documentation. <I> DOC AS 309072-01 aleady exists tracking completion of the drawing updates associated with WO 02040881 completion. Additionally, WOT 02040881-01 clearly pointed to AR EVAL 309072 for post installation drawing updates.
391740 | CR | 20190402 | CAQ | D | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0052390 White Box Hygrothermograph- model CT485-AL found OOT & adjusted within specs. Used at 487' Chem Lab. EFIN Eval: Local display was OOT. Chart IN Tolerance. Chart is the function required. No Impact. DEF #6969A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391741 | CR | 20190402 | CAQ | C | Operations Logs missing log entries for downpower actions |  |  |  | N | NO | <D> **** Detailed Description **** Operations Logs during the downpower on 3/23/19 are missing key entries for downpower commencement, work completion, and rampup commencement. Downpower on 2/16/19 was also missing downpower commencement entry. These types of entries are required in accordance with PPM 3.1.10. Key downpower times are needed for reporting of plant downpowers to INPO and the NRC, per Section 3.3 of the INPO CDE Data Element Manual, INPO-04-004. The times for these actions in February and March will be approximated. <I> **** Actions Taken **** Initiated CR. Times have been approximated. Section 4.9 contains the required log entries - the level of detail to support the authors requests are not currently required. The procedure should be updated with the specific logging needs to meet these offsite reporting requirements as required.
391742 | CR | 20190402 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0066432 Hytorc Hyd. Torque Wrench- model Avanti- P7 found OOT & adjusted within specs. Not used during Calibration cycle. DEF #6987A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391745 | CR | 20190402 |  | 3 | Unclear when to lift clearance. |  |  |  | N | NO | <D> **** Detailed Description **** D-PSR-V-03-ISOL-001 was found to be hanging with work apparently complete and the clearance ready to lift. Guidance is needed to determine if this is ready to lift. <I> **** Actions Taken **** CR written. <N> **** Equipment Description **** RHR-A pumproom
391748 | CR | 20190402 |  | 3 | Cal Code 0063399 OOT - Keithley 248 HV Power Supply | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Keithley 248 High Voltage Power Supply (0063399) out of tolerance for the -5000 VDC Accuracy (Negative â€“ No Filter) test when tested to the manufacturers specification for DC Voltage accuracy of Â±(0.01% of reading + 0.05% of range). This has had Limited Specifications on this Keithley 248 for DC Voltage Accuracy of Â±(0.01% of reading + 0.1% of range) with the Output Filter On. This limitation (as well as DC Current Accuracy of Â±(0.05% of Reading + 5ÂµA) with the Output Filter On) has been in place since this Keithley 248 was put into service in 2003. See EDMS for email with options recommended by Cal Lab. <I> **** Actions Taken **** Notified Tool Crib and Maintenance.
391749 | CR | 20190402 | CAQ | D | floaters in E-B2-1 battery for tracking/trending | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** floater material has been previously identified as not affecting the operability of the battery. this CR is being generated to track and trend the number of cells with floaters. All floaters identified appear to be made up of the same material and appear to be similar. the following cells were identified 5,7,9,11,12,15,16,17,21,23,27,39,41 -46,67,70,74,76,93,139,140,142,150,168,174,178,182,185,186, 187,189-191,195,198,199,204,219,224,225,228, and 231. <I> **** Actions Taken **** notified CRS and supervision write CR/WR, <N> **** Equipment Description **** E-B2-1 Battery room 1
391750 | CR | 20190402 |  | 3 | PPM 10.25.170 Maintenance & Repair Limitorque SMC-03 and 04 |  |  |  | N | NO | <D> **** Detailed Description **** Procedure PPM 10.25.170 Maintenance & Repair of Limitorque Vlave Operators - Model SMC-03 and 04 incorrectly identifies part numbers. Part #'s on Pg 75 for the motor outline does not align with Part #'s on Pg 104 (figure 6 Motor Removal) . Pg 104 FIgure 6 (Attachment 9.7) had the incorrect part #'s: 1) O-ring Part # (31) should be Part # 81 2) O-ring Part # (30) should be Part # 80 ** This CR is administrative and does not impact plant equipment. (Procudure revision). <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
391751 | CR | 20190402 | CAQ | D | RHR-RV-88B- temperature not recorded during testing of spare |  |  |  | N | NO | <D> **** Detailed Description **** While performing closeout review of TSP-RV/IST-R701 it was discovered that the pre-test temperatures were not recorded per step 3 of attachment 9.3. It was thought that the temperature did not need to be recorded because it is a Crosby valve and the previous step mentions not needing a temperature taken for tests below 150 deg. The task to test this pre-outage spare was returned to working and a new test will be performed. <I> **** Actions Taken **** Discussed with PSRO. Did not credit work order as SAT. Asked the testing be reperformed with the required data documented.
391752 | CR | 20190402 |  | 3 | TMU-SR-1 was not representative March composites |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The TMU composite sampler, TMU-SR-1 was not representative from 3/19 through 3/21/19 because PWC-P-5 was turned off per WR 29147637. The samplers are an ODCM table 6.3.1-1 and EFSEC 332 requirement. The ODCM requirements were tracked in eSOMS on sheet O19-PWC-P-5-001. This CR written to drive reporting of these sample deviations in the annual REMP report only, no additional action needed. Request assignment to AR-ENLAB. <I> **** Actions Taken **** Requested Chemistry to take grab samples from 3/19 through 3/21/19. Wrote CR.
391753 | CR | 20190402 |  | 4 | B.5.B fire truck air compressor | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** Found B.5.B supplemental air compressor (continuously keeps air brakes pressurized while in standby) was found not plugged in. After use of the truck, compressor was attempted to be plugged back in and it made an odd noise and failed to start. Left compressor unplugged. This does not impact the use of the B5B truck, it just takes longer (~3 to 5 minutes) for the factory air compressor to build pressure up to release the brakes. <I> **** Actions Taken **** Generated CR. <N> **** Equipment Description **** B5B truck
391754 | CR | 20190402 |  | 4 | Unable to locate 8" to 4" adapter for FLEX-P-2 | N | N |  | N | YES | <D> **** Detailed Description **** Operations was unable to perform SOP-LHGP-PM in support of WO#02134446 due to inability to locate the FLEX-P-2 Discharge Adapter (8â€ to 4â€ with Storz conn.). Section 3.3 of SOP-LHGP-PM lists the adapterâ€™s location as FLEX-TRLR -2. The adapter was unable to be located on FLEX-TRLR-2 or anywhere in Bldg. 600 including the B.5.b Pumper truck. OSP-FLEX-A106, Flex Equipment Storage Inventory, does not list the adapter as part of the inventory. <I> **** Actions Taken **** Informed CRS/SM | 02-CM-FLEX-P-2
391756 | CR | 20190402 |  | 4 | Task cannot be worked as written | N | N |  | N | NO | <D> **** Detailed Description **** During walk down of work order 02128119-01, paint has been identified behind all four base plates approximately Â¼â€ to 3/8â€ below edge of plates. Due to location and access to base plates removing paint required cannot be achieved 100%, per PPM 10.2.33 (7.4.1 section a). Recommend evaluation to determine if the supports can be removed to allow adequate grout installation per the procedure. As grout cannot be installed in the current configuration. <I> **** Actions Taken **** Contacted Planning, Management and Work Control.
391757 | CR | 20190402 |  | 4 | Inadequate flow during Condenser In-Leakage Testing | N | N |  | N | YES | <D> **** Detailed Description **** During test setup of Condenser In-leakage testing (WO 02131337) insufficient flow was observed from the Â¼â€ O.D PSR(1005)-1S line connecting AR-V-1IN to the OG sample line (less than 10 SCFM). The insufficient flow may be the result of an obstruction in the sample line or an off -normal position of the sample isolation valve AR-V-10. Recommend purging the line of potential obstructions and ensuring AR-V-10 is in the full-open position to allow Condenser In-Leakage testing to continue. | 02-00-AR-V-1IN
391758 | CR | 20190402 |  | 3 | Wyse thin client devices not functioning as expected | N | N |  | N | NO | <D> **** Detailed Description **** Wyse thin client devices not functioning as expected, device configuration needs to be validated and tested. <I> **** Actions Taken **** Notified Supervisor, wrote CR to document as found configuration.
391759 | CR | 20190403 |  | 4 | TO-TK-2 filter basket needs changed out | N | N |  | N | YES | <D> **** Detailed Description **** TO-TK-2 filter basket needs changed Excessive oil leakage from strainer basket housing This issue has already been documented in 2 other W/R 's ( 1 cancelled, 1 H/APPR) The oil leakage has only gotten worse since originally written up in SEPTEMBER <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TO-TK-2, TG 471 E | 02-00-TO-TK-2
391760 | CR | 20190403 |  | 4 | TOA-FL-1A at End Of Roll | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FL-1A at End Of Roll <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TOA-FL-1A TG 501E | 02-00-TOA-FL-1A
391761 | CR | 20190403 |  | 3 | Suggest stop payment for MT-ELEV-4 contract due to failures | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-4 has had multiple faults on a daily basis since installation. Equipment operators have reset the brake failure alarm several times each shiift and the alarm now immediatly comes in on the first attempt to move the car. Suggest contract for the elevator be revieved for failure to perform as promised and stop payment until fixed. This fault has been written up many times and no action has come from it. <N> The elevator contractor has already been paid for the installation so withholding payment is not an option at this point. The warranty clause is the method of gaining satisfaction on the performance of the elevator and is being addressed by the project manager of the elevator installation. | 02-00-MT-ELEV-4
391774 | CR | 20190403 |  | 3 | CBD-FT-1 CVI MANUALS NEED UPDATING FOR NEW INSTALL |  |  |  | N | YES | <D> **** Detailed Description **** WR 29146384 INSTALLS NEW CBD-FT-1. CVI MANUALS NEED UPDATING FOR NEW UNIT. <I> **** Actions Taken **** Notified supervision. Obtained new manuals from vendor supplied CD rom and uploaded to edms documents of this CR <N> Per the CID 60112346 description, there is a drawing in addition to an O&M manual. | 02-00-CBD-FT-1
391776 | CR | 20190403 |  | 3 | Enhancement to HPI-8.2 |  |  |  | N | NO | <D> **** Detailed Description **** 29CFR1910.134 Appendix A requires respirator fit tests to be performed with the individual in the standing position. HPI-8.2 does not have this requirement. Please revise HPI-8.2 to include this requirement. <I> **** Actions Taken **** Rad Support organization notified of gap - procedure change requested.
391778 | CR | 20190403 |  | 4 | CT-1C level High | N | N |  | N | YES | <D> **** Detailed Description **** During rounds on 4/3 dayshift, CW-CT-1C level was +13 inches, greater than the action level of +12 inches to write a CR. <I> **** Actions Taken **** Initiated CR | 02-00-CW-CT-1C
391779 | CR | 20190403 |  | 3 | I&C surveillance did not have proper reviews in EWP |  |  |  | N | NO | <D> **** Detailed Description **** W/O 02137541-01 & 02137542-01 for performance of ISP-SEIS -M202 did not have the correct review steps captured in order to notify Operations when their review of the ISP was required during the EWP workflow process. Looking at the two work orders in Asset Suite the box for review was not checked, even though the model work order has the correct review box checked. Previous work orders for performance of ISP-SEIS-M202 prior to the new EWP software update did not have a similar issue. <I> **** Actions Taken **** Notified CRS, wrote CR for Tracking, & informed EWP help of the issue.
391782 | CR | 20190403 |  | 4 | CAS-C-1B run meter indicates 36 hrs less than previous read | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1B run meter indicates 36 hours less than the previous reading. Reading taken on 4-3-2019 was 94859.25, reading taken on 3-31-2019 was 94895.25, and reading taken on 3-27-2019 was 94786.91. Which indicates numbers were not transposed. <I> **** Actions Taken **** Informed CRS, write CR/WR | 02-00-CAS-C-1B
391783 | CR | 20190403 |  | 4 | TOA-FL-1A is at end of roll. | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FL-1A is at end of roll. End of roll alarm is in. <I> **** Actions Taken **** CRS informed, write CR/WR | 02-00-TOA-FL-1A
391785 | CR | 20190403 | CAQ | D | RHR-B System Pressure Up Slow | Y | Y |  | N | YES | <C> CR reopened to cross reference additional WR 29147391, then taken back to complete <D> **** Detailed Description **** See EDMS. RHR-B system pressure has risen from 110 psig to 350 psig from 3/21/19 to 4/3/19. OSP-RHR/IST-Q703 (RHR-B quarterly surveillance) was performed on 3/21/19 and RHR -P-2B was secured at 18:53 on that date. | 02-00-RHR-P-2B
391786 | CR | 20190403 | CAQ | D | RHR-MO-73A - Actuator won't engage into motor mode | Y | N |  | N | YES | <D> **** Detailed Description **** After the motor replacement on RHR-MO-73A, the actuator wouldn't go back into motor mode and appears to be stuck in manual. During the initial operator removal for the motor replacement , the actuator wouldn't go into manual mode. The rotor was found seized to the stator (the failure drove the motor replacement). After the forces were relieved, and the motor was replaced, the operator went into manual mode, but now won't go back to motor mode. <I> **** Actions Taken **** Notified supervisor, work control, engineering, mechanics, planning . Engineering came to the field to validate the situation, and recommend a full overhaul of the actuator. <N> **** Equipment Description **** RHR-A HX Room | 02-00-RHR-MO-73A
391787 | CR | 20190403 |  | 3 | PDIS History Function not working correctly for Building 88 |  |  |  | N | YES | <D> **** Detailed Description **** Retrieving MCR.CGS data from History does not work correctly from the Network Operations & Security Center. The functions work correctly from the I&C workstation in the Control Room, so we do not see evidence of operations being affected. This CR should go to Computer Engineering for further investigation. <I> **** Actions Taken **** Tried rebooting both PDIS-COMP-DATA1 and PDIS-COMP-HIST1. But that did not correct the issue. Tried deleting the history files. But that did not correct the issue. | 02-00-PDIS-CPU-HIST1
391788 | CR | 20190403 |  | 4 | BRE-37 UPS not functioning as designed |  |  |  | N | YES | <D> **** Detailed Description **** A UPS at BRE 37 found out of spec while performing maintenance. This does not affect normal operation. <I> **** Actions Taken **** Notified Security. Recommend closing to cross-referenced WR for repair. <N> **** Equipment Description **** BRE 37
391789 | CR | 20190403 | CAQ | D | Communication failure to siren C2 | N | Y |  | N | YES | <D> **** Detailed Description **** During the weekly siren poll test C2 did not respond. Further individual communication tests over the next hour continued to show no response. All other sirens remain fully functional. <I> **** Actions Taken **** Notified EP and dispatched techs to repair the siren. Upon arrival, the communication was back working with no indication as to the problem. Recommend NCAQ-4 to trend. Cross reverenced to WR 29147667 to replace the antenna and feed cable. <N> **** Equipment Description **** Siren C2 Franklin County
391791 | CR | 20190403 |  | 3 | Interference ID'd in EC 17469- Install Oilers on RRC-M-P/1B |  |  |  | N | NO | <D> **** Detailed Description **** An interference was identified in the approved design change EC 17469. Each of the three (3) oilers have a 1/8â€ vent port that would have been blocked by the structural support for the oilers. . This CR was initiated because this interference potentially impacts the R24 fast track project to install constant level oilers on RRC-M-P/2B. Note that EC 17469 has not been installed in the plant and this CR does not affect any plant equipment. . This issue was identified by Design Engineering while researching a separate question associated with the design package. A Field Change Request (FCR) and possible calculation revision are currently in progress. . This issue was discussed with the Design Supervisor, Work Planner, Civil/Structural Engineer, Welding Engineer and the Mechanical Designer. A voice message was left with the Project Manager. Please route this CR to AR-CMC for resolution. <I> **** Actions Taken **** This issue was discussed with the Mechanical/ Civil Design Supervisor, Work Planner, Civil/Structural Engineer, Welding Engineer, and the Mechanical Designer. A voice message was left with the Project Manager. Initiated this CR <N> FCR 17469R000B has been issued to correct this non -consequential design error. No further actions are required. The parent AR-CR is now closed. .
391793 | CR | 20190403 |  | 3 | CVI-OMM 666-00,7 needs to be updated for current parts |  |  |  | N | NO | <D> **** Detailed Description **** RFT-LOC-1A/1B CVI-OMM 666-00,7 has outdated information, gasket number 180 does not exist in the current document, however part number 0007-2501-750 (180) from Westfalia is required for installation is in our system under CID 645 and is in the new manual received from the vendor in a digital format and should be evaluated by engineering to validate parts and replace the current CVI OMM due to the missing parts and the clarity of the document. See EDMS for new document <I> **** Actions Taken **** Notified engineering supervisor, my supervisor and wrote this CR
391796 | CR | 20190403 |  | 4 | Fire Alarm system in DG1, DG2 & DG3 rooms |  |  |  | N | NO | <D> **** Detailed Description **** The photoelectric detectors located in the diesel rooms need to be changed to the Siemens OP-121. Eliminate the need to build a scaffold every year for cleaning heads. <I> **** Actions Taken **** Generated CR/WR, notified engineering and supervision on the need for a Work Order to change the existing heads to Siemens OP-121, to eliminate the need to build scaffolds in order for the electricians to remove the existing heads for cleaning. OP-121 has a self check system and would only require it to be changed out when the OP-121 LED changes from flashing green to flashing yellow. . AR type EVAL needed for proposed configuration change? <N> **** Equipment Description **** Located in all Diesel Rooms (DG1, DG2 & DG3)
391797 | CR | 20190403 |  | 3 | OSP-FLEX-A106 Procedure Change |  |  |  | N | NO | <D> **** Detailed Description **** OSP-FLEX-A106 step 7.1.10 says to write a CR if any tamper seals were found broken. However, there is no mention to reinstall seals following inventory in the listed attachments. For those cabinets or boxes required to be sealed please add a step to reseal. <I> **** Actions Taken **** Informed Supervision
391798 | CR | 20190403 |  | 4 | MT-HOI-40 stuck in undesirable condition | N | N |  | N | YES | <D> **** Detailed Description **** MT-HOI-40 (RX 548' hatch crane) is currently stuck with its hook below the RX 471' elevation. MT-HOI-40 will move East and West along its rails, and the Hoist will lower the hook, but the Hoist will not raise the hook. Power was verified available, as evident by ability to move in all other directions. With the hoist stuck in its current configuration, R-DOOR-R106 (King Kong Door) cannot be opened (Due to Secondary Containment interlocks). With the outage closly approaching there will likely be needs/desires to OPEN R-DOOR-R106; please expedite this repair. NOTE: there is no load on the hook and the hook is approximately centered in the hatch; therefore, not in close proximity to any equipment located in the RX 441 railroad bay. Also, the handle to the local disconnect (on the hoist itself) spins freely and no longer appears to be attached. <I> **** Actions Taken **** Informed MCR. verified no load on hook, and hook not in close proximity to equipment. <N> **** Equipment Description **** RX 458 Maintenance fully raised the hoist. The hoist is no longer inhibiting the ability to close hatch A1. | 02-00-MT-HOI-40
391799 | CR | 20190403 |  | 3 | PWC-P-8, tube connection leak outside BLDG40. | N | N |  | N | YES | <D> **** Detailed Description **** During the investigation of chemical residue outside of wellhouse 40. It was found to be coming from a poly tube compression fitting. This line is from PWC-P-8 and is routed inside underground conduit from the flocculator bldg to Wellhouse. The metal coduit is corroded and requires replacement. This will require ground excavation, conduit and poly tube replacement. See pictures in EDMS. <I> **** Actions Taken **** The tubing is being repaired temporarily on WR#29147484. The intent of this cr & WR# is for the permanent replacement of the underground tubing run and conduit. <N> E&RP walked down the spill referenced in CR 391799 â€œPWC-P-8, tube connection leak outside BLDG40â€. There is sodium hypochlorite (NaOCl) in the tube. It was determined that the contaminated soil needs to be excavated and placed in a drum for later sampling to evaluate volume spilled to the environment. Additionally, containment should be placed under the leaking connection to contain future leaks that occur before permanent repair. | 02-00-PWC-P-8
391800 | CR | 20190403 |  | 4 | MT-HOI-40 Failed | N | N |  | N | YES | <D> **** Detailed Description **** While using MT-HOI-40 on the 548â€™ RX it failed to raise the hook. It would allow the hook to lower but not raise. The hook was lowered to the lower floor and placed in a safe configuration. The crane is powered from MC-8C-B, cubicle E-DISC-8CB3BL, receptacle 8CB/3BL. <I> **** Actions Taken **** Contacted Operations, Work Week Manager. To eliminate future issues, request Engineering evaluation to either wire the crane into direct power or add an additional power source with a disconnect. Right now, the only way to shut the power off is to go to the MCC and turn the switch off. Another issue that has occurred in the past, is that this meltrix receptacle is sometimes being used by another department as a power source. To use the crane this power source has to then be removed to plug the crane power supply in to operate. If the crane had it's own power supply this would not be an issue. <N> **** Equipment Description **** MT-HOI-40 Maintenance was able to raise the hoist fully and is no longer inhibiting the ability to close hatch A1.
391801 | CR | 20190403 | CAQ | D | CRD-HCU-4259 Rod Accumulator Trouble High Water Level | Y | N |  | N | YES | <C> CR reopened to add completion required check mark to referenced WO/WR per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** Received "Rod Accumulator Trouble" alarm on CRD-HCU-4259. Ops2 reports the alarm is due to high water level; that he has drained the water, and the alarm is clear. Following water drainage HCU pressure was slightly below 1000psig and per SOP-CRD-HCU the N2 pressure was raised. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** RX 522 A review of CRD-HCU-4259 determined that this HCU has alarmed 3 times since 12/1/18. (CRs 387442, 389834, 390861) | 02-00-CRD-HCU-4259
391802 | CR | 20190404 |  | 3 | HP Tech took over Fire Brigade Duties for RMC Laborer |  |  |  |  | NO | <C> ANON CR reviewed by CAP, moved to OPS for review. This CR was graded as a 4/T at CRG but moved to a 3/EMERP at EP managers request. <D> **** ANONYMOUS CR - Detailed Description **** On 3/20/2019 during dayshift, an HP Tech was asked and then proceeded to take over Fire Brigade Duties for the assigned RMC Laborers due to the Laborers being shorthanded and not having enough man-power to perform their assigned tasks outside the protected area fence without pulling the assigned Fire Brigade Laborer from their duties. <I> **** Actions Taken **** Initiated CR for tracking purposes.
391803 | CR | 20190404 |  | 4 | WO0200097706 PMT UNSAT FOR LIGHTING ON mt-cra-1 | N | N |  | N | YES | <D> **** Detailed Description **** Closed breaker and used the remote to turn on lights, crane moves fine but the lights donâ€™t work. Lights need further investigation so you can use the remote control to turn on lights. Work order 0200097706 (TT) MT-CRA-1: VERIFY LIGHT OPERATION <I> **** Actions Taken **** Wrote this CR to document issue | 02-00-MT-CRA-1
391804 | CR | 20190404 | CAQ | C | unknown/ foreign substance in DCW level glass | Y | N |  | N | YES | <D> **** Detailed Description **** Unknown/ foreign substance in DCW level glass DG-ENG-1A1 DCW expansion tank DCW-LG-10A1 <I> **** Actions Taken **** Informed SSS, MCR <N> **** Equipment Description **** DG1 DG 441 Similar substance also identified in DCW-TK-1A2 sight glass but to a much lesser degree. DG-2 and DG-3 DCW expansion tank sight glasses did not exhibit any similar unknown substances. | 02-00-DCW-LG-10A1
391806 | CR | 20190404 |  | 4 | 2 Pieces of M&TE OOT | N | N |  | N | NO | <D> **** Detailed Description **** 2 Pieces of M&TE were found OOT & adjusted within specs. Neither were used during Calibration cycles. Calcode #C011928 Ectron TC Test Set- model 1100CF. DEF #6989A written. Calcode #0062494 Dresser Sensor- model HQS-1 25in. DEF #6990A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391807 | CR | 20190404 |  | 4 | 3 Pieces of M&TE Rejected | N | N |  | N | NO | <D> **** Detailed Description **** 3 Pieces of M&TE were Rejected. None were used during Calibration cycles. Calcode #43477 Starrett Depth Mic- model 449BZ-6R. DEF #6991A written. Calcode #0052384 White Box Hygrothermograph- model CT485-AL. DEF #6992A written. Calcode #0068309 Mitutoyo Dial Caliper- model 505-743 8". DEF #6993A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391813 | CR | 20190404 |  | 4 | TOA-FL-1B at End of Roll | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FL-1B at End of Roll. Recommend filter changeout. | 02-00-TOA-FL-1B
391814 | CR | 20190404 |  | 3 | PPM 11.2.7.3 needs a Minor Revision | N | N |  | N | NO | <D> **** Detailed Description **** PPM 11.2.7.3 (HRA,LHRA,VHRA Controls) Attachment 10.1 lists LHRA/VHRA Door Guard Duties/Responsibilities. Each responsibility is numbered 1 through 8, except that there is no number 3 listed. With there being no #3, the list should be 1 through 7. <I> **** Actions Taken **** Notified Supervision via e-mail Initiated Condition Report
391816 | CR | 20190404 |  | 3 | Enhancement to PPM 10.25.137 |  |  |  | N | NO | <D> **** Detailed Description **** PPM 10.25.137, which calibrates SW-MO-PCV/15A and 15B, needs enhancement. This CR relates to CR 391248 (SW-PCV -15B is Leaking By in the Indicated Closed Position). Additional steps are required to verify that valve is in Closed (full bypass) position when it receives a 20 mA signal to close. This style of valve does not have a positive hard stop to verify the closed position. Recommend running SW pumps during calibration and using a Midas meter to verify no flow through pipe in the closed position. <I> **** Actions Taken **** Discussed proposed change with valve engineer.
391817 | CR | 20190404 |  | 3 | SOP-RHR-SDC contains a CAUTION with an undefined term |  |  |  | N | NO | <D> **** Detailed Description **** Section 5.10 of SOP-RHR-SDC contains a caution regarding excessive radiation exposure to prevent failure of RHR pumps if operating with a â€œdegraded core conditionâ€. This caution relates to {R-9677} FSAR commitment however there is no threshold value for coolant activity level given in procedures that could be used to determine if a â€œdegraded core conditionâ€ exists. This has caused confusion in task training during LORQ simulator instruction. Please define. <I> **** Actions Taken **** Wrote CR from operator feedback during simulator instruction.
391818 | CR | 20190404 |  | 4 | Cycle 19-2 Non-Licensed Operator Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** Two Non-Licensed Operators failed the Cycle 19-2 requalification exam. The first was a fully qualified operator. Qualificaitons have been removed pending remediation. The second was a non-qualified operator in -grade. No qualification removal was required. Remediation and re-examination will be conducted in accordance with TDI-02 and TDI-10 <I> **** Actions Taken **** Conducted a review of the exam Documented exam results Developed remediation plan
391819 | CR | 20190404 | CAQ | C | Work order 02107551-03 RWCU-MO-1 lost weld/ASME records |  |  |  | N | YES | <D> **** Detailed Description **** (R24 Pre-Outage/Outage) WO #02120340-04/47 (RWCU-MO-1). After being sign by ANI on 1/09/19; ASME Plan No 2-3026, WR 2-13673 and WR 2-13674 for WO #02120340-04/4 have been lost. This document was created by Code Programs,and signed by QC and ANI, as evidenced by their respective hold codes (WR, QCI, ANI) being lifted, and and their respective review hold codes (CPR, QCR) being placed. This does not affect installed RWCU-MO-1. <I> **** Actions Taken **** A search of William files where the walkdown was located, Document Control and a query to QC did not result in finding the documents. <N> **** Equipment Description **** (R24 Pre-Outage/Outage) . Weld records and ASME Plan have been recreated, re-reviewed / re-signed by QC & AHII and given to affected work group for use.
391823 | CR | 20190404 |  | 3 | R 24 Outge project in P6 corrupted |  |  |  | N | NO | <D> **** Detailed Description **** The R 24 Outage Project in Primavera's P6 software became corrupted on 4-3-19 at approximately 10:15. Over 1000 logic ties were created between activities that had no reason to have logic between them. The problem was discovered while "Time Scheduling" the project. The calculation failed due to loops. While researching the cause of the loops (caused by bad logic) the scheduler found many logic ties that were not created by any scheduler. The only thing being done during this period was Maxavera ran scheduled job S2 updating P6 project NO01 (Online schedule) from Syntempo. I noticed when I clicked on the icon to pull up the Time Schedule dialog box the screen dimmed P6 showing that something was happening with the project or P6 that had to finish before I could continue. I did the Time Schedule when what ever was running finished and this is when the loops were discovered <I> **** Actions Taken **** Contacted other Outage scheduler along with supervision. Contacted IS for support on what happened and how to recover. <N> **** Equipment Description **** This is for a business side software and not plant equipmen t.
391825 | CR | 20190404 |  | 3 | Procedure Enhancement SOP-RPS-OPS |  |  |  | N | NO | <D> **** Detailed Description **** Restore the ability to transfer RPS-A while keeping RWCU in service by opening the RWCU-V-4 disconnect; this method requires entry into the associated PCIV TSAS, but does not represent the loss of a safety function since RWCU-V-1 remains operable (although this method defeats the RWCU-V-4 closure on SLC initiation it was determined acceptable in AR-CR 350903). Also restore the ability to transfer RPS-B while keeping RWCU in service by first installing a jumper in the RWCU -V-4 disconnect (although this method defeats NSSSS manual initiation it was determined acceptable in AR-CR 350903) and then opening the disconnect for RWCU-V-1.
391827 | CR | 20190404 |  | 3 | Quarterly CORC Caution Tag Audit (WO 02132645) |  |  |  | N | NO | <D> **** Detailed Description **** Quarterly CORC Caution Clearance Audit 10CFR50.59 The Quarterly CORC Caution Tag Audit (WO 02132645) has documented the caution clearances that have been hanging for GE 30 days. There are 8 new Caution clearances added to this total since the last audit: C-AUX-BOILER -002, C -CAS-V-278A -001, C-CBD-V-42 -001, C-DW-FI-1 -001, C-FPC -FIC-15B -001, C-RHR-V-73A -002A, C-RRA-FN-8 -001, C-TMU -P-1C -001 . Request Technical Services/Systems Engineering Manager (or designee) to determine whether a 50.59 review is required. <I> **** Actions Taken **** Wrote CR.
391828 | CR | 20190404 |  | 3 | Quarterly CORC Danger & Local Tag Audit (WO 02132643) |  |  |  | N | NO | <D> **** Detailed Description **** Quarterly CORC Danger & Local Clearance Audit 10CFR50.59 The Quarterly CORC Danger & Local Tag Audit (WO 02132643) has documented the danger & local clearances that have been hanging for GE 30 days. 15 new clearances have been added to this total since the last audit; D-COND-V-79/80 -002, D-COND-V-79/80 -002A, D-CW-FN-1 -001A, D-E-CB-LP3AK/1 -002, D-PSR-V-03-ISOL-001, D-RFT-LOC-1B -008, L-CO-P-2A -001, L-HS-V-T1O -001, L-HS-V-T1N -001, L-HS-V-T2M -001, L-MT -CRA-1 -004, L-MT-ELEV-4 -004, L-MT-HOI-7 -003, L-WOA-HC -1/N -002, L-WOA-HC-1/P -001, . Request Technical Services/Systems Engineering Manager (or designee) to determine whether a 50.59 review is required. <I> **** Actions Taken **** Wrote CR.
391830 | CR | 20190404 |  | 3 | PPM 15.1.18 - FP Suppression System Valve Alignment Update |  |  |  | N | NO | <D> **** Detailed Description **** Fire protection valve FP-V-CO2/909, normally locked open, should to be added to PPM 15.1.18 Fire Suppression System Valve Alignment. Fire Protection Valves FP-V-C02/900, FP -V-C02/910, and FP-V-C02/942 should be corrected from C02 to CO2. This update aligns PPM 15.1.18 with drawing M515 -3. . This assignment should be routed to Maintenance Procedure Writers, the procedure sponsor. . This is an administrative issue that does not affect the FP CO2 Suppression system. <I> **** Actions Taken **** Intiiated CR to create action. <N> Incorporated into PPM 15.1.18 Rev 019.004.
391831 | CR | 20190404 |  | 4 | R24 lessons learned - pre-outage breaker testing |  |  |  | N | NO | <D> **** Detailed Description **** This AR is to capture lessons learned from pre-outage breaker testing. Numerous ARs have been generated in the last several months to document breaker deficiencies encountered during pre-outage testing in support of R24. The failed breakers were sent back to the vendor for repair and will return just prior to R24 impacting other preparatation activities. The preoutage testing should start sooner in the cycle such that the work weeks are not overloaded with breaker work in the few months prior to the outage. Several delays were encountered due to the lack of elevator reliability. There have been several delays due to M&TE issues - more specifically the Primary Injection Test Set (PITS). <I> **** Actions Taken **** Initiated AR to capture lessons learned <N> **** Equipment Description **** W487 breaker shop . Due to hardened grease concerns with our Westinghouse DHP and DS breakers there is more than normal breaker scope for R-24. When combined with the quality issues from the vender and some ancillary issues such as the RW elevator being out of service, this has created some challenges to the official pre-outage window for completion of breaker setups. No change to the work management process is recommended at this time though. In the event it is determined that there is a heavy load of breaker work in future outages, there is nothing that prevents the station from scoping the setup activities for those jobs ahead of the official pre-outage window. This is a similar strategy to how we plan to do MSIV actuator refurbishments, all it takes is scoping a breaker setup activity at a T-20 meeting and/or coding it as GSA D work and performing it as shop resources allow.
391832 | CR | 20190404 |  | 3 | CC-185 Out of Tolorence Standard 31848 |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** CC-185 Out of Tolorence Standard 31848. Recommend assign to AR-CALSERV Cat 3 <I> **** Actions Taken **** CR entered
391834 | CR | 20190404 | CAQ | D | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065076 Proto Torque Wrench- model 6006C 80ft/lb found OOT & ajdusted within specs. Per PPM 1.5.4 section 4.4.3 (a-c) Torque Wrench had acceptable post use verificationS @ +/- .06%. Def #6994a Written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391835 | CR | 20190404 |  | 3 | TSP-RV/IST-R701 inconsistences |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During the review of TSP-RV/IST-R701, Testing of IST Program Safety/Relief Valves, Major Revision 014. Attachment 9.3, IST Relief Valve Test Record for relief valve RHR-RV-88B Step 3 which is a â€œpoundedâ€ (#) step was N/Aâ€™d. CR 391751 was written to document the issue. An extent of condition was performed to investigate the use of N/A for Step 3 of Attachment 9.3. Step 2 which is a â€œpoundedâ€ (#) step of Attachment 9.3 states: Temperature stability was equal to or less than 10Â°F variation for the 30 minutes prior to testing: Not required for Crosby air and water valves at less than 150Â°F. However, ambient and media temperatures shall be with 10Â°F of each other. Can be interpreted that if a Crosby valve is tested that it is at ambient temperature and ambient and media temperatures are within 10 degrees of each other. Seven work orders were reviewed and three out of the seven had N/A for Step 3 of Attachment 9.3 with no review issues from Operations or Maintenance. Therefore step 3 does not apply. â€¢ Does the relief valve in question need to be retested when the N/A was interpreted as acceptable by other reviewers? â€¢ Additionally there is confusion with step 3 which states (See TSP-RV/IST-R701 Attachment 9.1 for temperature criteria). Attachment 9.1 lists the ambient and media temperatures. The confusion is if the ambient and media temperatures are within 10 degrees of each other and if it is; there is a number of relief valves that will not meet that criteria with the values listed; which would have you writing a CR every time. The procedure needs to be changed to clarify these issues due to lack of clarification and the inconsistencies filling out the paperwork as to what is acceptable and what is not. â€¢ Recommend assignment to procedure sponsor <I> **** Actions Taken **** Discussed with Supervisors, Engineering, and craft. Initiated CR
391836 | CR | 20190404 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0060909 Fluke Dig. Multimeter- model 8842A found OOT & adjusted within specs. Not Used in the OOT Ranges. DEF #6997A written. No Action Required. <I> **** Actions Taken **** None Trending purposes
391839 | CR | 20190404 | CAQ | C | RDCS system has been place into MRule (a)(1) status |  |  |  | N | NO | <D> **** Detailed Description **** This AR CR is being written in accordance with SYS-4-22 as the RDCS system has been placed into Maintenance Rule status (a)(1). This status is in reference to 10CFR50.65 (a)(1). . The MRule performance monitoring program identified that the RDCS system had 4 Functional Failures (FF) which exceeded the performance criterion of < = 2 FF. Also there has been 16 soft lockups of the system with the performance criteria of < = 12. Reference AR assignment 00313942-82-01 for more details. . In accordance with the Columbia M-Rule guidance document, System Engineering Instruction SYS-4-22, these failures associated with the RDCS system were evaluated and presented to the System Engineering Manager who approved changing the status to (a)(1), reference AR 313942-82-01 assignment. The appropriate Performance Improvement Plan needs to be developed outlining any Corrective Actions, Goals and Monitoring plan to return RDCS system to satisfactory health and (a)(2) status. Refer to System Engineering Technical Instruction SYS-4-22 for detailed guidance for this evaluation. . AR CR to be assigned to AR-ER as Cat.C to create assignment for the development of a Maintenance Rule (a)(1) performance improvement plan.
391841 | CR | 20190404 |  | 3 | SOP-COND-START procedure clarification |  |  |  | N | NO | <D> **** Detailed Description **** SOP-COND-START sections 5.4, 5.5, & 5.6 have the condensate booster pumps isolated for the first one started. Step . The step says verify condensate not feeding the RPV. It is actually concerned with verifying it is not therequired feed pathway. SOP-COND-START Step 5.4. 6a should say â€œVERIFY isolating COND-P-2A will not cause a loss of feed to the RPVâ€. Same change for 5.5.8.a for 2B and 5.6.8.a for 2C. <I> **** Actions Taken **** Contacte
391843 | CR | 20190404 |  | 4 | IMDS for CRD-FCV-2A needs to be validated. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of WO# 02101714-10 Bench cal and pressure check; technicians discovered a possible error in the stop adjustment numbers and need to have engineering evaluate the numbers on the IMDS. <I> **** Actions Taken **** communication with valve engineer, initiate CR on IMDS potential error (this CR), initiate CR to add instructions to adjust stop limits in the diagnostic task, document in the work order package. <N> The stop adjustment numbers in question in this CR are correct as stated in EC 15866. It has been communicated that the adjustments may be slightly different as the provided adjustment numbe change is small (between 0.020 and 0.060 inches). The finial adjustment number will be provided so that the IMDS of the new CRD-FCV-2A can be updated under AR 309191-04.
391844 | CR | 20190404 |  | 3 | Work order instructions need update upon completion of CR |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Work order instructions need update upon completion of CR 391843. Planning will need to update the work instructions for WO# 02101714-15. Instructions needed to adjust stop limits during the diagnostic testing, total added time to job will be ~1hr. <I> **** Actions Taken **** Contact system engineer, CR initiated for the incorrect IMDS 391843, initiate CR for adding work instructions to task 15, document in the history panel of the work performed.
391845 | CR | 20190404 | CAQ | C | Legacy Issue identified with zone dose calculation |  |  |  | N | YES | <D> **** Detailed Description **** A legacy issue with CMR 3522 (against 0740-004-441C) was identified. This issue involves both the basis for the normal equipment radiation exposure rate and the the arithmetic in the calculation. The result overestimates the amount of dose equipment received in the conservative direction. No action needed from shift, engineering should investigate and fix calculations and involve license renewal . <I> **** Actions Taken **** Generated CR, notified shift. <N> **** Equipment Description **** HPCS Fan: R447'3" at M5 / 4.1 | 02-00-RRA-FN-4
391846 | CR | 20190404 | CAQ | C | Non-conservative process heat rise used for thermal life | Y | N |  | N | YES | <D> **** Detailed Description **** A review of current qualification for limitorque MOVs attached to high temperature process piping was conducted based on current industry OE. This evaluation identified that the heat rise used in the thermal life calculations for Limitorque MOVs was non-conservative for high temperature process lines. To verify actual temperatures, thermography was taken on a representative valve which determined that the actual heat rise at the motor is approximately 13 deg. F higher than previously assumed and the temperature at the limit switch compartment is approximately 7 deg. F higher than previously assumed. . The additional heat rise identified by thermography has a slight impact on the qualified life of the MOV's EQ components but does not impact the current qualification of these components. . Recommend action to plant programs engineering to document the actual heat rise on the Limitorque MOVs associated with process temperatures and update the qualification documents as applicable. <I> **** Actions Taken **** Initiated EQ Evaluation 17668 to determine impact on qualified life. No impact to current qualification was identified. | 02-00-MS-MO-16,02-00-MS-MO-19,02-00-MS-MO-67A,02-00-MS-MO-67B,02-00-MS-MO-67C,02-00-MS-MO-67D,02-00-RCIC-MO-63,02-00-RCIC-MO-76,02-00-RCIC-MO-8,02-00-RFW-MO-65A,02-00-RFW-MO-65B,02-00-RWCU-MO-1,02-00-RWCU-MO-4,02-00-RWCU-MO-40
391847 | CR | 20190404 |  | 4 | CW ortho-phosphate below target | N | N |  | N | NO | <D> **** Detailed Description **** Residual ortho-phosphate for 4/1/19 was below the lower target of 5.0 ppm. Test result was 4.0 ppm. CW blow down had been increase significantly to reduce cycle and caused the drop in residuals. <I> **** Actions Taken **** Chemical addition to the CW system was increased and by the next testing cycle the residual was back within target range. No further action is required. This CR is for trending only.
391851 | CR | 20190404 |  | 4 | FP-P-3 leakoff exceeding capacity of pit | N | N |  | N | YES | <D> **** Detailed Description **** FP-P-3 leakoff exceeding capacity of pit. The leakoff is directed by Tygon hose to a pit in the CWPH floor. This pit seemingly has no outlet, causing it to overflow onto CWPH floor and travel as far as the East end of the building where it is now flowing out of the building. Recommend re-routing/ adding tygon hose and sending water to adjacent CW pit <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** FP-P-3 CWPH | 02-00-FP-P-3
391852 | CR | 20190404 |  | 3 | Lighting out in 522 RX and DG3 | N | N |  | N | YES | <D> **** Detailed Description **** During housekeeping tour WO 02123752-01 several lighting discrepencies were found. Reference attached pictures in Data Glance under this WO to see a list of lights that are out. <I> **** Actions Taken **** CR generated. list of lighting issue left with area supervisor. <N> **** Equipment Description **** 522 and DG3 for lighting issues **************** WO referenced is incorrect. The WO that has the pictures is 02132752-01. Pictures copied to word document and attached to the EDMS of this AR.
391853 | CR | 20190405 |  | 3 | Procedure Change Needed for OSP-ELEC-S701 |  |  |  | N | YES | <D> **** Detailed Description **** Page 33 of OSP-ELEC-S701 states, â€œNOTE: Steps 7.3.74 through 7.3.82 may be performed concurrently.â€ Step 7.3.79, verifying DO-TK-3A full (running the transfer pump), must be completed before step 7.3.80, Recording DO -TK-1A level, since DO-TK-1A is supplying DO-TK-3A. <I> **** Actions Taken **** Notified MCR and OPS Procedure Supervisor <N> **** Equipment Description **** OSP-ELEC-S701
391860 | CR | 20190405 | CAQ | D | SFS-STORM-003 Indicates Yellow | Y | N |  | N | YES | <C> CR reopened to cross reference additional WR 29144437, then taken back to complete <D> **** Detailed Description **** SFS-STORM-003 Indicates Yellow on the display screen of SFS-CP-ISFSI/TMS. Indicates 1 Fault for RTD #2. | 02-00-SFS-STORM-003
391861 | CR | 20190405 | CAQ | D | SFS-STORM-022 Indicates Yellow | Y | N |  | N | YES | <C> CR reopened to add additional WR 29144327, AR 00384375, and AR 00383899 to the cross reference panel and check the Completion required box on the WR, then taken back to complete <D> **** Detailed Description **** SFS-STORM-022 Indicates Yellow on the display screen of SFS-CP-ISFSI/TMS. Indicates 2 Faults at RTDâ€™s #1 and #2. | 02-00-SFS-STORM-022
391862 | CR | 20190405 | CAQ | D | SFS-STORM-025 Indicates Yellow | Y | N |  | N | YES | <C> CR reopened to cross reference additional WP 02135153 and marked completion required box, then taken back to complete <D> **** Detailed Description **** SFS-STORM-025 Indicates Yellow on the display screen of SFS-CP-ISFSI/TMS. Indicates 1 Fault at RTD #3. | 02-00-SFS-STORM-025
391863 | CR | 20190405 | CAQ | D | SFS-STORM-043 Indicates Yellow | Y | Y |  | N | YES | <D> **** Detailed Description **** SFS-STORM-043 Indicates Yellow on the display screen of SFS-CP-ISFSI/TMS. Indicates 1 Fault at RTD #3. | 02-00-SFS-STORM-043
391864 | CR | 20190405 |  | 4 | CAS-AR-1A/1B/1C all have loose strongbacks on access covers. | N | N |  | N | YES | <D> **** Detailed Description **** The Access covers for all three CAS Air Receivers are loose. Some of the fasteners are not even hand tight. This is usually caused by failure to Re-tighten the strong backs After the Receiver is repressurized. (The Work Package may not have a step for that). All 6 of the strong backs can be re-tightened as is without any Tagout. This is quick simple job that even the EOs are qualified to perform. <I> **** Actions Taken **** Contacted the Control Room | 02-00-CAS-AR-1A
391865 | CR | 20190405 |  |  | SFS-STORM-045 Status Indicates Yellow |  |  |  | N | YES | <D> **** Detailed Description **** SFS-STORM-045 (Cask #45) status indicates yellow. | 02-00-SFS-STORM-045
391866 | CR | 20190405 | CAQ | D | CRD-HCU-3023 accumulator.trouble | Y | N |  | N | YES | <D> **** Detailed Description **** Received "ROD ACCUMULATOR TROUBLE" (H13-P603.A7 drop 6-7) for CRD-HCU-3023 accumulator. Alarm was due to moisture, the alarm is now clear. <I> **** Actions Taken **** OPS 2 responded per ARP | 02-00-CRD-HCU-3023
391867 | CR | 20190405 |  | 4 | PPCV system failed. | N | N |  | N | YES | <D> **** Detailed Description **** PPCV system failed. Received a message from user SYSTEM on PPCV "%QMAN-E-NODISCKSPACE, disk space not available for queue manager to continue". Need to investigate and repair <I> **** Actions Taken **** Computer technictian try a couple reboot but fail to resolve the issue. | 02-00-PPC-COMP-8715
391868 | CR | 20190405 |  | 3 | Procedural Enhancement SOP-CW-OPS, redundant steps |  |  |  | N | NO | <D> **** Detailed Description **** The procedure for initiating Circ Water blowdown was recently revised to accommodate the new Dehalogenation skid EC 16616. Section 5.8 of SOP-CW-OPS now contains redundant steps. Step 5.8.1 is redundant to step 5.8.2. Step 5.8.1 says to perform PPM 12.2.9 and step 5.8.2 says â€œVERIFY total residual halogen concentration is LE 0.10 ppm in two separate samples taken at least 15 minutes apart, AND pH has been verified to be between 6.5 and 9.0â€ which is already done in 12.2.9 steps 8.4.5 & 8.4.6 and is how you do this. Recommend deleting step 5.8.2 of SOP-CW-OPS as it is redundant and confusing.
391872 | CR | 20190405 |  | 3 | (NRC Identified) Housekeeping in RHR A following Maintenance |  |  |  | N | NO | <D> **** Detailed Description **** The NRC resident identified multiple housekeeping issues in the RHR-A pump room following maintenance. There are multiple zipties on the ground, wrench adrift, pole under ladder, and sump covers not restored to normal. <I> **** Actions Taken **** CR written and working with responsible individuals to address these housekeeping issues.
391873 | CR | 20190405 |  | 4 | External DMZ systems unavailable |  |  |  | N | NO | <D> **** Detailed Description **** External DMZ systems unavailable due to network maintenance at the TEC data center on DC-TEC. The systems were unavailable on 4/5/19 between ~1:18 PM and ~2:25 PM. The systems affected include Horizon/View remote access, Exchange Outlook Web Access, Outgoing SMTP email, www, PeopleSoft careers. Recommend NON-CAQ 4 <I> **** Actions Taken **** Notified IS Duty Officer. Verified physical links. Verified route tables.
391874 | CR | 20190405 |  | 3 | SOP-CRD-HCU Section 5.13 Procedure Change |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.13.17 h â€œSnoop Check CRD-V-111/HCUâ€ should be a standalone step. Snoop checking CRD-V-111/HCU should always be performed and should not be part of a conditional step. <I> **** Actions Taken **** Informed Supervision
391875 | CR | 20190405 |  | 4 | TSW-F-1A (TSW lube water) is stuck in Backwash cycle | N | N |  | N | YES | <D> **** Detailed Description **** TSW-F-1A (lube water filter to the TSW pumps) is stuck in it's backwash cycle. The filter has been in backwash for GT 24hrs. Cycling the control switch to OFF and then back to AUTO did not improve the situation. The green backwash light is lit at TSW-CP-F/1A and the backwash valve was verified to be OPEN locally. TSW-F-1A D/P is ~ 0.3 PSID, well below the level that would prompt the control panel to go into backwash mode. <I> **** Actions Taken **** Informed MCR. Attempted to reset logic by cycling control switch. <N> **** Equipment Description **** CWPH | 02-00-TSW-F-1A
391876 | CR | 20190405 | CAQ | C | AED M515-1 depiction of FP-M-P/2A(B) cooling water piping |  |  |  | N | YES | <D> **** Detailed Description **** The AED M515-1 depiction of the small bore FP cooling water supply piping to the FP-M-P/2A and FP-M-P/2B upper bearing oil coolers is not accurate. As drawn, the source of the FP cooling water supply to each motor is the motor rather than the pump. This is an administrative issue only - there is no associated impact up the physical plant or the continued operation, function, or qualification of any SSC. Recommend nonCAQ resolution to Design & Drafting for administrative correction of the AED M515-1 depiction. <N> This discrepancy was noted while reviewing drawings associated with AR EVAL 374127. | 02-00-FP-M-P/2A,02-00-FP-M-P/2B
391877 | CR | 20190405 |  | 3 | Procedural Enhancement SOP-CW-OPS |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.8.1 of SOP-CW-OPS requires performance of PPM 12.2.9 even if it isnâ€™t required. PPM 12.2.9 is the Circulating and Plant Service Water Halogenation Surveillance and is only performed if you are going to manually halogenate CW. It also provides for post-halogenation sampling. Step 5.8.1 says â€œIF the continuous Halogenation/Dehalogenation process is not being placed in service, AND the Plant is in Mode 1, 2, or 3, THEN VERIFY one of the following has been completed up to initiating blowdown. (N/A the one not used.) -PPM 12.2.9 -PPM 12.2.9A The problem is that if CW blowdown is secured for some other reason (like to support I&C calibrating a CW flow meter) and then CW blowdown needs to be reestablished, the step does not give any latitude. Recommend a conditional statement be added: â€œIf Halogenation was not performed, mark this step as N/A.â€
391878 | CR | 20190405 | CAQ | D | Recieved Accumulator trouble alarm HCU 50-39 | Y | N |  | N | YES | <D> **** Detailed Description **** Recieved Accumulator troble alarm HCU 50-39 due to high water level <I> **** Actions Taken **** OPS2 drained the water and cleared alarm | 02-00-CRD-TK-125/5039
391879 | CR | 20190405 |  | 3 | COND-DM-1A & COND-DM-1F no Low Level Relaxes | N | N |  | N | NO | <D> **** Detailed Description **** Upon taking the watch, I noticed that there were no Low Level Relaxes performed on COND-DM-1A & COND-DM-1F and both CFD's were well past the Low level Relax D/P limit. This significantly dereases the usable lifespan of the CFD by reducing the amount of relaxes allowed to be perfomed on the CFD before it must be Backwashed and Precoated. <I> **** Actions Taken **** CR Written Superision Notified Training in the form of a Night Order Suggested <N> **** Equipment Description **** COND-DM-1A & COND-DM-1F . Feedback and coaching was provided to the proper individuals. Will trend this following the outage.
391884 | CR | 20190406 |  | 3 | Trailer with untreated wood stored in RB truck bay |  |  |  | N | NO | <D> **** Detailed Description **** The TCP for the CVAN in the RB truck bay was incorrectly evaluated for the TB truck bay (TCP 18-0190). The new permit required hourly fire tour. The FM will need to evaluate if continous fire tour is required. (TCP 19-0040) <I> **** Actions Taken **** Created new TCP 19-0040 closed old TCP 18-0190 . The trailer has 2 by wooden decking that does not appear to be treated. Per FCEI-2.2.1 4.1.2.b. : Where more than 20 pounds of untreated/uncoated wood is temporarily used in â€œFP Vital Areas,â€ it must be continuously attended or have a continuous fire tour. Trailer deck is approximately 7' wide by 38' long. Approximately 1000 lbs of wood.
391885 | CR | 20190406 |  | 4 | RFW-VBI-1A/XS/TE green "ABOVE MIN RPM" LED not lit | N | N |  | N | YES | <D> **** Detailed Description **** RFW-VBI-1A/XS/TE green "ABOVE MIN RPM" LED not lit. When compared to RFW-VBI-1B/XS/TE, all other indications are comparable. <I> **** Actions Taken **** Informed CRS/SM, wrote this CR and WR. | 02-00-RFW-VBI-1A/XS/TE
391886 | CR | 20190406 |  | 3 | SOP-RRC-START needs enhancement. |  |  |  | N | NO | <D> **** Detailed Description **** SOP-RRC-START needs enhancement. The following should be added as a new precaution and limitation: Core reactivity will change when placing ASD controllers RRC-M/A-R676A and RRC-M/A-R676B in AUTO on RRC-M/A-R675 Master Controller following a runback of both RRC pumps to 30 Hz or 15 Hz. Following the runback, RRC-M/A-R675 Hz demand will already be at the desired setpoint, and RRC -M/A-R676A and RRC-M/A-R676B Hz demands will already be within + 3 Hz deviation of RRC-M/A-R675. When placing RRC -M/A-R676A or RRC-M/A-R676B in AUTO, the DEV/BIAS (Hz) indication on RRC-VD-R673 for the applicable pump will change from 0.00 to the bias that was in effect prior to the RRC pump runback. The PUMP Hz DEM and ACTUAL Hz for the applicable pump will also change accordingly. . The following should be added as a note between steps 5.8 and 5.8.1: Core reactivity will change when placing RRC-M/A-R676A or RRC-M/A-R676B in AUTO following a runback of both RRC pumps to 30 Hz or 15 Hz. The DEV/BIAS (Hz) indication on RRC -VD-R673 for the applicable pump will change from 0.00 to the bias that was in effect prior to the RRC pump runback. The PUMP Hz DEM and ACTUAL Hz for the applicable pump will also change accordingly. <I> **** Actions Taken **** Discussed with AOM-Crews, informed CRS/SM, wrote this CR. . This issue has been observed in the plant following RRC pump runbacks and validated in the simulator.
391887 | CR | 20190406 |  | 3 | ARP 4.602.A6 needs enhancement. |  |  |  | N | NO | <D> **** Detailed Description **** ARP 4.602.A6 needs enhancement. The following should be added as a note to drop 5-8, FEEDWATER PUMP TRIP LIMIT, between step 6 and step 6.a, and also to drop 6-1, REACTOR LEVEL LOW LIMIT, between step 5 and step 5.a: Core reactivity will change when placing RRC-M/A-R676A or RRC-M/A-R676B in AUTO. The DEV/BIAS (Hz) indication on RRC-VD-R673 for the applicable pump will change from 0.00 to the bias that was in effect prior to the RRC pump runback. The PUMP Hz DEM and ACTUAL Hz for the applicable pump will also change accordingly. <I> **** Actions Taken **** Discussed with AOM-Crews, informed CRS/SM, wrote this CR. . This issue has been observed in the plant following RRC pump runbacks and validated in the simulator.
391888 | CR | 20190406 | CAQ | D | ROD ACCUMULATOR TROUBLE on CRD-HCU-3823 due to high water. | Y | N |  | N | YES | <D> **** Detailed Description **** ROD ACCUMULATOR TROUBLE on CRD-HCU-3823 due to high water level. <I> **** Actions Taken **** Cleared alarm per SOP-CRD-HCU, informed CRS/SM, wrote this CR and WR. | 02-00-CRD-HCU-3823
391889 | CR | 20190406 |  | 4 | red handle valves error likely situation |  |  |  | N | YES | <D> **** Detailed Description **** While performing isp-ms-q901 step 7.1.7a. and c. close high side (19) and low side (17) isolation valves noticed they were not painted red. mi-2.2 step 4.4.1c. states red handle valves are tied directly to reactor level or presure sensing lines. these valves have a potential for causing a half or full reactor scram signal. recomend getting them both painted red before the next performance of isp-ms -q901. <I> **** Actions Taken **** talked with supervisor wrote this cr <N> **** Equipment Description **** e-ir-h22-p004 | 02-00-MS-LIS-24A
391890 | CR | 20190406 | CAQ | D | RHR-MO-73A Failed to stroke during the PMT | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of the PMT of RHR-MO-73A under WO#02137236-09 (per 10.25.74), the MOV failed to stroke for the rotation check. It was found to have no control power. Control room was notified, and an attempt to reset the thermals was done. This re-established the control power, but the MOV still failed to go closed or open. MOV was verified to have control power at all applicable Limit switch term points. Work was stopped so that a troubleshoot plan to check the MCC cubicle (E-MC-7BB5D) could made. <I> **** Actions Taken **** Notified the control Room, Supervisor, wrote a CR to document the condition. | 02-00-RHR-42-7BB5D,02-00-RHR-MO-73A
391891 | CR | 20190406 |  | 4 | TSW-F-1A stuck in 'backwash' mode | N | N |  | N | YES | <C> Duplicate of AR391875 <D> **** Detailed Description **** TSW-F-1A stuck in 'backwash' mode Investigate and repair as necessary <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TSW-F-1A CWPH | 02-00-TSW-F-1A
391892 | CR | 20190406 | CAQ | D | BUS 73 GND alarm, H13.P800.C1.6-6 | Y | Y |  | N | YES | <D> **** Detailed Description **** Received BUS 73 GND alarm, H13.P800.C1.6-6. MC-7A ground indicating lights are out, E-TR-7/73 neutral ground lights are out and the ground resistor bank is hot, and E-RLY -50N/T7/73 is dropped out. Attempted to reset the ground and it immediately tripped. It has been raining sporadically over the last couple of days. Reference CR 389044 for a similar previous event. <I> **** Actions Taken **** Informed CRS/SM, wrote this CR and WR. | 02-00-E-TR-7/73
391893 | CR | 20190406 | CAQ | C | CCH-CR-1A trip on low suction pressure | Y | Y |  | N | YES | <D> **** Detailed Description **** CCH-CR-1A tripped on low suction pressure approximately 5 minutes after initial start up. It was noticed that control vane was about 75% open, the 7R relay had repositioned during the trip, and suction pressure on CCH-PI-6A was about 18" HG. A second attempt to start the chiller yeilded the same results. <I> **** Actions Taken **** Control room informed and CR initiated | 02-00-CCH-CR-1A
391894 | CR | 20190406 |  | 4 | Unable To Complete PMT on RHR-MO-73A | Y | N |  | N | YES | <D> **** Detailed Description **** Unable to complete PMT on RHR-MO-73A under WO# 02137236-09. Issues around RHR-MO-73A failing to stroke for the rotation check resulted in delays (see AR/CR#00391890 and WR#29147902). After troubleshooting WR was established to proceed, OPS was unable to support the Troubleshoot Plan due to an emergent issue with a ground alarm on bus 73 (see AR/CR#00391892 and WR#29147905). We were pulled from the PMT task to support the emergent ground alarm issue. We are also going to loose our temp lift due to running into shift change. <I> **** Actions Taken **** Supervision notification/coordination to switch from the primary task to the emergent task. Wrote CR to track the PMT on RHR-MO-73A. | 02-00-RHR-MO-73A
391895 | CR | 20190407 |  | 4 | W 501' light outside MCR needs ballast replaced | N | N |  | N | YES | <D> **** Detailed Description **** W 501' light outside MCR needs ballast replaced. Lamp above the SAM is not illuminated. Replaced bulbs no change. Left new bulbs installed. 4' flourescent tubes. 4th lamp from west hallway end. <I> **** Actions Taken **** replaced bulbs - no impact non-essential lighting | 02-00-E-CB-LP7EC/15
391898 | CR | 20190407 |  | 4 | Generator Condition Monitor Chart Paper EOR | N | N |  | N | YES | <D> **** Detailed Description **** Generator Condition Monitor chart paper is at EOR. <I> **** Actions Taken **** Called ext. 8714 and left a message as instructed on the front of the equipment. Initiated this CR. Made appropriate OPS log entries. | 02-00-TG-ID-1
391899 | CR | 20190407 |  | 3 | Corrections to SWP-PRO-02 |  |  |  | N | NO | <D> **** Detailed Description **** SWP-PRO-02 states in Step 5.3.3 "IF preparing a Procedure Change Notice (PCN), THEN PROCEED to Section 1.1." There is no Section 1.1. Section 5.3 addresses PCN's. Attachment 8.1 , under the "Major Revision" column, states "...Implements recommendations or conclusions as a result of a Follow-up Assessment of Operability (FAO)." FAO's were replaced by POD's many years ago. <I> **** Actions Taken **** No immediate actions necessary. Found while processing a PCN. . Correction - Section 5.5 of SWP-PRO-02 addresses PCN's, not 5.3.
391900 | CR | 20190407 |  | 3 | Employee Directory |  |  |  | N | NO | <D> **** Detailed Description **** Some contract employees are listed in the directory, however some are not. It would seem that anyone issued a pager should be listed in the directory. This is not always the case. Being able to contact workers pre outage and during the outage is time sensitive. <I> **** Actions Taken **** Wrote CR
391904 | CR | 20190408 |  | 4 | Three RP Techs removed from training |  |  |  | N | NO | <D> **** Detailed Description **** Three RP Technicians were removed from training with less than 24 hours notice. This request was approved by the PGM as required by GEN-TQS-01. Training personnel and affected individuals were notified. <I> **** Actions Taken **** Requested and received PGM approval. Notified training personnel and affected individuals. <N> Due to three HPTs calling in sick, three HPTs were pulled from training to support high risk work.
391905 | CR | 20190408 | CAQ | D | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0063399 Keithley Hi Volt Power Supply- model 248 found OOT & will need adjustment. EFIN Eval: Not used in the OOT Range. DEF #6988A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391924 | CR | 20190408 | CAQ | D | (NRC) RHR A Pump Room Sump Covers | N | N |  | N | YES | <C> CR reopened and grading changed by MRT from non-CAQ 4/TR to CAQ D/TR. <D> **** Detailed Description **** On an NRC plant walkdown, it was discovered the sump covers in the RHR A pump room are misaligned. NRC informed the CRS who informed the Shift Manager and SSS. <I> **** Actions Taken **** Initiated CR due to NRC identified equipment issue. <N> **** Equipment Description **** RB 422' RHR-A Pump Room | 02-00-FDR-SUMP-R1
391926 | CR | 20190408 |  | 3 | R24 Preoutage LL - Scrub preoutage ground device work scop |  |  |  | N | NO | <D> **** Detailed Description **** Need to have a scrub of breaker setups and ground device setup preoutage tasks prior to preoutage scope freeze. In R24 preoutage, there were some ground device set up activiities coded for preoutage that were setting up the device to early. We have a small number of ground devices and need to move them from one cubicle to another during the the electrical bus windows. This sequence needs to be established before the preoutage Milestone scope freeze and validate that the correct work items are coded UCR G. This is a lessons learned for outage management. to establish actions in the preoutage preparations. Ref: WO 02115597 -33,35 Task 33 was complete but was not needed until will into R24. A new task was generated. <I> **** Actions Taken **** none applicable. <N> A sub-assignment was added to the R25 pre-outage milestone PO.21 "Pre-Outage Work Activities Integrated into the Work Management Process" to accomplish a scrub prior to pre-outage scope freeze. Reference AR 377345-21-14.
391927 | CR | 20190408 | CAQ | C | Weld record misplaced |  |  |  | N | NO | <D> **** Detailed Description **** W.O 02111977-06 was printed and issued with the Weld record misplaced. <I> **** Actions Taken **** Initiated a CR, Notified the weld Engineer and QC.. .Further review indicates both the weld record and the ASME plan was lost. <N> Weld Record 2-13492 and ASME Plan 2-2988 have been re-produced, re-reviewed and re-signed by QC and the ANII. Re-produced documents have been given to WPS.
391929 | CR | 20190408 |  | 3 | Do not use Asset Suites to review work order instructions |  |  |  | N | NO | <D> **** Detailed Description **** If a person opens work instructions via Asset Suites (AS) whlie a technician has the work open in EWP on the iPad, the work instructions become invalidated. Once this happens the Tech has invalidated work instructions that cannot be opened until the supervisor re-validates the work instructions in Data Glance. This will cause delays in work due to slow down of the Tech to get the work re-validated. It also can have the potential to wipe any documentation of work performed if the supervisor clicks "Replace" instead of "Append". Any employee having need to review work orders needs access to Data Glance at a minimum Review ability. Also need a site wide communication to review work orders utilizing Data Glance instead of AS. The problem mentioned does not happen when work instructions are viewed via Data Glance. Also need a site wide communication stating to "not use AS to review work instructions. Only use Data Glance to review work instructions." Only Planners and those executing work orders should use AS to review work orders. All others should use Data Glance. <I> **** Actions Taken **** Informed PSO management of the issue. Maintenance Component Managers have been informed. Initiated this CR which the # will be given to IS and PSO <N> Briefing on this topic was complete at the Outage Meeting on 4/17/19. In addition, an email communication was sent to Distribution C on 4/17/19 addressing this topic and directing individuals to view WOs in DataGlance rather than asset suite. No further actions needed.
391931 | CR | 20190408 |  | 3 | Sudden unexplained drop in TMU Flow. | N | N |  | N | YES | <D> **** Detailed Description **** Sudden unexplained drop in TMU Flow. Current flowrate is about 9000 gpm. Previous flowrate was about 15000 gpm. Step changed occurred about 1208, 8 APR 19. TMU-LIC-2A controlling at about 22%. TMU-LI-2A denotes 444.6â€™ in a band of 443â€™ â€“ 445â€™. CW Blowdown removed previous shift. <I> **** Actions Taken **** CRS notified and SM. CRS referenced ABN-TMU. TDAS Point L002 for TMU Flowrate. | 02-00-TMU-LIC-2A
391932 | CR | 20190408 |  | 3 | Condensate Motor Pump UTC 538492 Not Fitted in plant |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** CID 8632 Condensate Motor Pump UTC 538492 was installed in R-23 however it is not showing as installed (fitted) in the plant. This would also indicate that any in storage PMâ€™s remain active for this UTC. <I> **** Actions Taken **** Communicated with the maintenance manager this CR was being created
391933 | CR | 20190408 |  | 3 | Recently installed RHR-P-2A Storage PM Not Deactivated |  |  |  | N | NO | <D> **** Detailed Description **** The RHR pump WO 02033672 storage PM not deactivated didnâ€™t include the step to deactivate the in storage PM as required by the limitation on use.
391934 | CR | 20190408 |  | 3 | Cat ID 538492 but does not identify which pump by UTC |  |  |  | N | NO | <D> **** Detailed Description **** MR 260931 issued for pre-outage preparation currently identifies only the Cat ID 538492 but does not identify which pump by the specific UTC and there are 2 of the same pump in the warehouse. This will leave the pump selection to the warehouse personnel without the UTC identifying which pump is called for. This is potentially an error likely situation not identifying the specific pump for installation similar to the pump mix up for RHR. <I> **** Actions Taken **** Initiated CR <N> 538492 may be the UTC number (not the CID number as indicated in the AR CR write-up). MR 260931 is for CID 8632.
391935 | CR | 20190408 |  | 3 | Evaluate if actions taken complied with CFR 26.75 |  |  |  | N | NO | <D> **** Detailed Description **** Columbia recently took administrative action against an employee following a positive fitness for duty test result only. These results were above the cutoffs in CFR26.163(b )(1) but below the 15,000ng/mL limit referenced in CFR26 .185. These actions were taken prior to a meeting with the medical review officer. These actions were premature and against CFR 26.75. Per CFR 26.75 sanctions (a) A licensee or other entity may impose more stringent sanctions, except as specified in paragraph (h) of this section. (h) A licensee or other entity may not terminate an individual's authorization and may not subject the individual to other administrative action based solely on a positive test result from any initial drug test, â€¦., unless other evidence, including information obtained under the process set forth in Â§ 26.189, indicates that the individual is impaired or might otherwise pose a safety hazard. The licensee or other entity may not terminate an individual's authorization or subject an individual to any other administrative action under this section based on the results of validity screening or initial validity testing performed at a licensee testing facility indicating that a specimen is of questionable validity. CFR26.185 (j) Review for opiates, prescription and over-the-counter medications. (1) If the MRO determines that there is no legitimate medical explanation for a positive confirmatory test result for opiates and before the MRO determines that the test result is a violation of the FFD policy, the MRO or his/her designee, who shall also be a licensed physician with knowledge of the clinical signs of drug abuse, shall determine that there is clinical evidence, in addition to the positive confirmatory test result, that the donor has illegally used opium, an opiate, or an opium derivative (e.g., morphine/codeine). This requirement does not apply if the laboratory confirms the presence of 6-AM (i.e., the presence of this metabolite is proof of heroin use), or the morphine or codeine concentration is equal to or greater than 15,000 ng/mL and the donor does not present a legitimate medical explanation for the presence of morphine or codeine at or above this concentration. The MRO may not determine that the consumption of food products is a legitimate medical explanation for the presence of morphine or codeine at or above this concentration
391936 | CR | 20190408 |  | 3 | Actions taken against individual need to be evaluated and co |  |  |  | N | NO | <D> **** Detailed Description **** Columbia recently took administrative action against an employee following a positive fitness for duty test result only. These results were above the cutoffs in CFR26.163(b )(1) but below the 15,000ng/mL limit referenced in CFR26 .185. Case studies of this exact same situation have been documented to show that drugs were not used and levels coincided with diet and medicine The conclusion from these case studies is that this situation should be a negative result when there is no clinical evidence of abuse, and the concentrations are less than 15,000 ng/mL. Reference SAMHSA Medical Review Officer Guidance Manual for Federal Workplace Drug Testing Programs page 5-6 for recommended actions in these situations and Medical Review Officer Case Studies #3. Can be found on The Substance Abuse and Mental Health Services Administration website (SAMHSA) The actions taken against this individual need to be evaluated and compared to state and federal standards. Cross reference CR# 00391935
391939 | CR | 20190408 |  | 3 | Spare conduit for CCVT Project Appears to be Broken | N | N |  | N | NO | <D> **** Detailed Description **** Note: This is a spare conduit with no active circuits installed. The spare conduit to be used in the CCVT project to run the CCVT cables appears to be broken/was found with sand and small rocks inside. After several attempts to clear, sand continues to enter the conduit. It is estimated that ~ 110lbs of sand has already been removed from the conduit. Estimate location of breach is approximately 50 feet north of the Trenwa. Area needs to be excavated and conduit repaired in order to continue the CCVT cable installation. <I> **** Actions Taken **** NDE performed Bore scoping however they were limited to less than 20' due to equipment limitations. Attempted sand and small rock removal. <N> **** Equipment Description **** Spare conduit run the Trenwa running between M2 and it's we st firewall and north towards the Hand Hole HH-E51/by the /by the MODs.
391941 | CR | 20190408 |  | 4 | PPC-COMP-8715 DP20 failed | N | N |  | N | YES | <D> **** Detailed Description **** During investigation of CR 391867 per WR 29147893, it was discovered that DP20 was in OVFL status on PPC-COMP-8715. Stop-Start of the card did not resolved the OVFL, it returned in just a couple mins of run time and MUX-8 didn't restore at all. . PPC continues to be out of service due to this failed card. . This is not a reportable condition. . DP20 in PPC-COMP-8715 needs to be replaced and the failed card RMA'd to the vendor. <I> **** Actions Taken **** Notified SM, generated CR and WR | 02-00-PPC-COMP-8715
391942 | CR | 20190408 | CAQ | D | ABN-HVAC entry due to MCR temperature GT 78F | Y | Y |  | N | NO | <D> **** Detailed Description **** CCH-CR-1A tripped shortly after it was started for troubleshooting. ARP 4.826.P1.8-4 EMERG C.R. CHILLER A TROUBLE restored MCR cooling via WCH by placing CCH-P-1A control switch to OFF. While performing the ARP, control room temperature rose to 78.4F and ABN-HVAC was entered. Control room temperature rapidly returned to LT 78F with the restoration of WCH cooling. <I> **** Actions Taken **** Entered ABN-HVAC, restored MCR temperature LT 78F, and submitted a CR.
391943 | CR | 20190408 | CAQ | C | Rx Bldg 606 Ultraviolet Detector Trouble Alarm | N | N |  | N | YES | <D> **** Detailed Description **** On FCP-1 drop 14-1 Rx Bldg 606 ultraviolet trouble alarm came in. No fire or welding activities were present on the 606. The alarm is in a high contamination area of the RX bldg 606 for ALARA considerations the alarm was not reset. This issue has been documented previously in CR 375989, 376118, 376239, 379793, and 382277. <I> **** Actions Taken **** Wrote CR Informed CRS . FP-UVD-19B trouble alarm came in. This is non-essential fire detection equipment. Entry into a HRA/C-zone is required to reset. Did not reset the alarm. | 02-00-FP-UVD-19B
391945 | CR | 20190408 |  | 3 | Transient Comustible Permit for the TB-471 found in RB-522 | N | N |  | N | NO | <D> **** Detailed Description **** During operator rounds, OPS2 discovered TCP 17-0137 attached to equipment in a location other than that specified on the permit. The permit was issued for a non -FP vital area was discovered in a FP vital area. Upon investigation, it appears that the permit was attached to the equipment while it was staged in the TB, and not removed when the equipment was later placed in the RB. There are valid RB TCP's on the equipment for the staging area in the RB. <I> **** Actions Taken **** Walked down the equipment to ensure that it was properly permitted for the RB. Notified the CRS, and initiated this CR.
391946 | CR | 20190409 |  | 4 | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0068310 Mitutyo Dial Caliper- model 505-743 8" found OOT & Rejected. Not used during Calibration cycle. DEF #6999A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391947 | CR | 20190409 |  | 4 | Main Transformer TR-M3 Trouble alarm received in MCR | N | N |  | N | YES | <D> **** Detailed Description **** 4.800.C4 drop 3.1 alarmed in the Main Control Room <I> **** Actions Taken **** Dispatched OPS4. Alarm was due to "Cooler Group 2 Failure" and was reset with no further issues. This AR is for trending purposes | 02-00-E-TR-M3
391949 | CR | 20190409 | CAQ | D | 2 Pieces of M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** 2 Pieces of M&TE were found OOT & adjusted within specs. Calcode #0063335 Dresser Sensor- model HQS-2 300in. Not used in the OOT Range. DEF #6995A written. Calcode #0063866 Agilent Function Generator- model 33250A. Not used in the OOT range. DEF #6996A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
391955 | CR | 20190409 |  | 3 | SOP-RCC-LU needs to be updated |  |  |  | N | NO | <D> **** Detailed Description **** RCC-V-211, RCC-V-650, RCC-V-651, RCC-V-652, RCC-V-653, RCC-V-654 and RCC-V-655 are closed and capped in the plant and are shown as closed and capped on M607-2. SOP-RCC-LU says that these valves should be closed only. SOP-RCC-LU needs to be updated.
391957 | CR | 20190409 |  | 4 | EC 14635 Native Files Missing |  |  |  | N | NO | <D> **** Detailed Description **** Some of the native files for EC 14635 were missing. There were also cases where the native file did not match what was put in to the EC. The A/E working on this EC was contacted to locate the missing or incorrect files. In a few instances, the files were found but for the rest it meant recreating the files. Our processes were not followed, the processes state that native drawing files are to be stored on our Design Work in Progress folder or provided to EN Design/Drafting leads per DES-2-1, DDS-3, DES-2-15 and in the Standard Design Process Toolbox on Sharepoint. Our processes also state that manual drawings scanned in to AutoCAD are to be scanned to .CAL format. In this EC, some of the files were imported in to AutoCAD as PDF, which makes the file unusable for us. <I> **** Actions Taken **** ENW and A/E personnel were cycled to locate missing files and ENW personnel were cycled to recreate and verify files (rework). All files have been reconcilled, recommend this AR CR to be trended.
391959 | CR | 20190409 | CAQ | C | RWCU system flow rate exceeds RWCU HX design capacity | Y | N |  | N | YES | <D> **** Detailed Description **** The RWCU total system flow rate is much higher than the system and RWCU heat exchangers design flow rates due to leakage past RWCU-V-44. The RWCU heat exchangers are designed for 133,000 lbm/hr of system flow (per their TEMA sheets in OMM 02G33-09,10). Testing performed under WO 02138812 confirmed that the flow rates shown on B010GPM (RWCU Return to Feedwater) are correct. For many years these flow rates were assumed to be incorrectly high and therefore the demineralizer flow rates were used to set total system flow. Demineralizer flow rates do not take into account bypass leakage through RWCU-V-44. B010GPM typically reads about 435 gpm right now which is equivalent to 184000 lbm/hr (for comparison 133000 lbm/hr is 315 gpm return flow). This is 138% of design flow. Between 2003 (oldest EDNA data available) and January 2016 flow was usually run at about 470 gpm on EDNA point B010GPM. This is equivalent to 199000 lbm/hr or 150% of design flow rate. This has contributed to increased FAC in the RWCU piping and damage seen in the RWCU HXs (e.g. AR 330811 Missing tie rods, AR 331161 Eroded nozzles) in R22. The continued operation with RWCU system flowrates above design flow needs to be addressed. Assign to NSSS engineering. | 02-00-RWCU-HX-1A,02-00-RWCU-HX-1B,02-00-RWCU-HX-1C
391962 | CR | 20190409 |  | 3 | Procedure enhancement for ISP-EFC-B108 |  |  |  | N | NO | <D> **** Detailed Description **** Typo on page 103 of 103. See EDMS <I> **** Actions Taken **** Wrote CR <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
391963 | CR | 20190409 | CAQ | C | Using RWCU Demin flows cause Thermal Power Calc Errors |  |  |  | N | NO | <D> **** Detailed Description **** The RWCU Demineralizer flow rates (EDNA Point B021 and B024) are used in the Reactor thermal power calculation instead of RWCU suction or return flow rates (B009 and B010). For many years the suction and return flow rates were assumed to be incorrectly high and therefore the demineralizer flow rates were used in the thermal power calculation to determine RWCU system flow rate. Testing performed under WO 02138812 confirmed that the flow rates shown on B010GPM (RWCU Return to Feedwater) are correct and that due to leakage past RWCU-V-44, the demineralizer flow rates are erroneously low. The assumption made many years ago that the supply and return flow rates were inaccurate was incorrect. Need to evaluate changing the thermal power calculation to use the RWCU supply or return flow rate as the input to the thermal power calculation. Using demineralizers flow rates introduces potential non -conservative errors into the thermal power calculation. This will also simplify taking demineralizers out of service and make the calculation more accurate since the thermal power calculation will no longer be impacted by bypass flow and will not require dummy values to be inserted. Recommend assignment to Reactor Engineering. <I> Not a DNC. This is a recommended enhancement to existing calculation methodology to incorporate different data points for RWCU flow in the thermal power calculation. Our current thermal power calculation is valid. As described in the IOD for CR 390846, substitute values for RWCU-DM-1A and RWCU-DM-1B flow have been entered (0.1 mlb/hr) to PPC and TDAS to account for RWCU-V-44 leakage.
391965 | CR | 20190409 |  | 4 | Work order tasks cancelled. |  |  |  | N | NO | <D> **** Detailed Description **** This CR is to document that work order tasks 02118809-01 (INSPECTION OF SCR/ZENER DIODES/CAPACITORS IN RPS-MG-1 SET), and 02118810-01 (INSPECTION OF SCR/ZENER DIODES/CAPACITORS IN RPS-MG-2 SET) are being cancelled. The work cannot be performed as written without the potentially damaging the internal SCR/Diodes of the motor generator sets. WR 29147923 was initiated to perform an inspection of RPS-MG-1â€™s SCR/Diodes and forward the relative information to engineering.
391966 | CR | 20190409 |  | 3 | eWP tasks taken to Finished, Instructions not signed off |  |  |  | N | NO | <D> **** Detailed Description **** Some support type tasks were taken to FINISHED status but upon review it was discovered that the work instructions had not been signed off by the performer(s). This is contrary to SWP-PRO-01 for work instructions. The examples discovered were support tasks assigned to Operations for work orders where the main task was for Maintenance. Examples are listed on the Xref panel. 4 tasks were related to draining and refilling DCW for DG2 engines. In some cases the instructions required a peer verfication signature for parts that was also not signed off. Other evidence exists that the work was performed, just not properly documented and verified per the task work instructions. <I> **** Actions Taken **** Reviewed the work tasks in eWP and Asset Suite. Notified the Ops Crew AOM. Reminders were previously sent out to ops crew supervisors regarding eWP WOT processing.
391968 | CR | 20190409 |  | 4 | SRD set points Change not documented correctly |  |  |  | N | NO | <D> **** Detailed Description **** While conducting SA-387308 it was identified, RWP SRD set point temporary changes are documented using PPM 11.2.9.31. Since 10/2018 at least one instance were the set point was changed was documented in the eSOMS log rather than the RWP Log as prescribed by procedure. <I> **** Actions Taken **** Notified RP Supervision
391969 | CR | 20190409 |  | 3 | Evaluate the need for recorder TIP-XR-1 |  |  |  | N | YES | <D> **** Detailed Description **** Per PPC bridging study the plant uses original TIP system SSCs. However, the latest FSAR section 7.7.1.6 states that analog data is available for driving a recorder. The recorder TIP-XR-1 appears to be abandoned in place. There is no indication the recorder is functioning and no maintenance history is associated with it. The recommendation is to evaluate if the recorder is still needed and determine if it can be tested/calibrated. If recorder is no longer needed and is abandoned in place, an FSAR amendment needs to be processed and all associated design document needs to be updated. <I> **** Actions Taken **** Discussed the issue with system, computer, and reactor engineering. Reference EDMS for pictures, FSAR and other design documents. <N> **** Equipment Description **** main control room | 02-00-TIP-XR-1
391970 | CR | 20190409 | CAQ | D | EDNA points for SW-LI-1A and 1D show data not expected. | Y | N |  | N | YES | <C> CR reopened to cross reference additional WR 29147940 and mark completion required box, then taken back to complete <D> **** Detailed Description **** While monitoring and trending, it was noted that EDNA points L068 and L070 for SW-LI-1A and 1D appear to show incorrect data. With both SW pumps 1A and 1B secured, pond levels should be equalized and reading similar levels. Calibrated SW-LT-1B and 1C for spray pond B are showing ~13.2 ft while SW-LI-1A and 1D for Spray pond A are reading 13.1 and 13.8 ft respectively. Local level indicators at the ponds will also show accurate pond levels that align with readings from SW-LI-1B and 1C. Contacted the control room to confirm indication readings in EDNA matched the control room indication. Local indications can also be checked to aid the MCR in determining the pond levels and to meet SR 3.7.1.1. <I> **** Actions Taken **** notified SM and supervisor | 02-00-SW-LT-1A,02-00-SW-LT-1D
391972 | CR | 20190409 |  | 3 | Fire Protection pump replacement is not like-for-like |  |  |  | N | YES | <D> **** Detailed Description **** The replacement pump for FP-P-2A, 2B, and 1, was requested to be a like-for-like replacement by Specification Number 15614. The new pump differs from the existing pump in dimensions and materials. Due to these differences an evaluation is required. Reference: PO 352590, PO 353273, CID 34448 (motor/pump combo). <I> **** Actions Taken **** Components Supervisor, Minor Mods Supervisor, Critical Spares Project Manager, Buyer, and System Engineer notified. AR EVAL 392069 initiated by AR-SECOMP. <N> The fire protection pump is currently being built at the Ruhrpumpen facility in Monterrey, Mexico. ENW has not received any of these pumps at our warehouse. Pump engineer identified differences in the new pump drawings when comparing them to the documentation in PortalJ for the installed pumps. Fomer Pump Engineer did a procurement specification deviation noting the differences but did not communicate to the station that this would not be a like for like replacement. Pump engineer is working with vendor to resolve the differences. | 02-00-FP-P-1,02-00-FP-P-2A,02-00-FP-P-2B
391973 | CR | 20190409 |  | 3 | OSP-SLC/IST-Q701 and PMID 17131 needs revision and clarifica |  |  |  | N | NO | <D> **** Detailed Description **** OSP-SLC/IST-Q701 step 3.8 reference PMID 23618 and 23619 (Retired) needs to be deleted. Need to validate if online motor testing (Baker testing) is still required and if it is, what it is done under. Need to revise the electrical support instructions for PMID 17131-01, 02 and 03 to state clearly and accurately what is being performed. Need to validate that 17131-01 electrical support is not needed and the support task deleted. Validate 17131-02 is for vibration data and clarify instructions. Validate 17131-03 is for check valve testing (and vibs ?) and clarify instructions.
391974 | CR | 20190409 | CAQ | D | SLC TANK LEVEL HIGH/LOW locked in after sparge | Y | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02131014 then taken back to complete <D> **** Detailed Description **** SLC TANK LEVEL HIGH/LOW, H13-P603.A8.5-8, alarm is locked in following SLC sparge. SLC-LI-601 indicates 5000 gal, TDAS indicates 4889 gal, and local indication indicates 4900 gal. All these indications are close to previous readings. <I> **** Actions Taken **** Informed CRS/SM, wrote this CR and WR. | 02-00-SLC-LS-600
391981 | CR | 20190409 |  | 4 | Building 9 (Palouse) Reverse Osmosis unit flow is low |  |  |  | Y | YES | <D> **** Detailed Description **** Building 9 (Palouse) Reverse Osmosis unit flow is low. Both hot and cold filtered water flow is low. <I> **** Actions Taken **** Wrote CR/WR <N> **** Equipment Description **** Building 9 (Palouse) Reverse Osmosis unit
391982 | CR | 20190409 |  | 3 | Improvements needed for OCC focus on ind safety performance |  |  |  | N | NO | <D> **** Detailed Description **** DG-2 Safety System Window: The OCC team briefings inconsistently discussed industrial safety when this was part of the established agenda. While there were some effective discussions on industrial safety, the overall aggregate performance did not reflect the importance of safety first being a station focus area. As leaders, the topic is well understood and a known item on the agenda and it is expected that some level of effort would be placed on preparing to discuss this focus area and could also be forward looking vice focusing on shift performance. (TE1d. Team members demonstrate collective ownership for overall station performance, including improving the effectiveness of the entire organization â€” not just their responsible area). This was part of a snapshot self-assessment AR 391475 <I> **** Actions Taken **** Contacted PSO and discussed with OCC SOD/SOM Recommend to PSO non-caq 3
391983 | CR | 20190409 |  | 3 | Enhance OCC critique protocol |  |  |  | N | NO | <D> **** Detailed Description **** DG-2 Safety System Window: Observations of end of shift OCC critiques found an inconsistent standard in the approach of how these critiques are performed. One shift critiqued their own performance for the shift and did so by asking each individual to discuss their own performance as well as the teamâ€™s performance. A different shift designated a critique lead for the last briefing of the day and did not purposefully seek all members input like the other shift. They critiqued their briefing performance and not necessarily their shift performance. This is a missed opportunity to align the OCC performance around a common approach and engage all OCC members to challenge their performance. . Additionally, one of the observed positives was the SOM/SOD turnover sheets which contained key lessons learned as well as shift critiqued items. It is recommended that the key information (lessons learned and OCC critique information) be shared with the oncoming shift and established as part of the OCC standard protocol (LE.7.c Leaders reinforce positive behaviors and results as well as provide candid feedback on performance gaps and development areas). <I> **** Actions Taken **** Notified PSO. Discussed with SOD/SOM. Recommend assignment to PSO non-caq 3
391984 | CR | 20190409 | CAQ | D | ROD ACCUMULATOR TROUBLE alarm on CRD-HCU-0223, high water | Y | N |  | N | YES | <D> **** Detailed Description **** ROD ACCUMULATOR TROUBLE, H13-P603.A7.6-7, alarm on CRD -HCU-0223 due to high water level. <I> **** Actions Taken **** Cleared alarm per SOP-CRD-HCU, informed CRS/SM, wrote this CR and WR. | 02-00-CRD-HCU-0223
391985 | CR | 20190409 |  | 3 | Ensure OCC key positions have identified primary and backup |  |  |  | N | NO | <D> **** Detailed Description **** DG-2 Safety System Window: The DG-2 safety system window OCC activation was identified as an opportunity to demonstrate OCC performance and execution in preparedness of R24. Overall, engagement and teamwork appeared strong. However, there were a few resource examples that did not reflect excellence. On nightshift, one shift did not have an Emergent Issues Manager and the second night, a key manager was not present due to sickness. While these absences did not appear to hamper overall OCC performance given the limited work scope, it is expected adequate resources are pre-established in case the primary OCC representative could not support. In this instance, the SOD filled the role of OCC Maintenance Manager and appeared to effectively fill this role but it also presents a risk of not providing the expected effective oversight role for the entire OCC team (LE2a. Leaders fill key positions with well-qualified, prepared candidates who have the behaviors, necessary technical expertise, and experience to be successful). This is focused on the organizationsâ€™ commitment to support OCC roles ahead of time with appropriate backups as per R-24 expectations. <I> **** Actions Taken **** Contacted PSO. Discussed with SOD. Recommend assignment to PSO non-caq 3
391986 | CR | 20190409 | CAQ | C | RHR-MO-73A - Trouble Shooting | Y | N |  | N | NO | <D> **** Detailed Description **** Trouble shooting activiites identiified the wires were rolled on RHR-MO-73A. This was identified during maintenance activities of replacing the failed motor. The failed motor was identified in CR 387795. The valve was also found to be in the backseat. <N> Wires were rolled during motor starter coil replacement under work order 02118444 in December 2018, per MOV engineer.
391990 | CR | 20190409 |  | 4 | LP3 Inlet Steam C2 Fail alarm | N | N |  | N | YES | <D> **** Detailed Description **** MCR received DEH Trouble, H13-P820.B1,2-5 alarm due to LP3 Inlet Steam C2 Fail alarm. On the Reheater Temp Input Selection page, LP#3 C2 Status Fail is highlighted in Red. The temperature has failed high at 795Â°F. The selected temperature is C1 at 512Â°F. Error message h3 mALM LP3 INLET 2. Suspected MS-TE-115C1 failure. <I> **** Actions Taken **** CRS notified. DEH Trouble alarm remains locked in. Notified Engineering and responsible I & C Tech. Suspect MS-TE-115C2 failure and not MS-TE-115C1 failure. | 02-00-MS-TE-115C
391993 | CR | 20190409 |  | 4 | ESD Injury with self-administered first aid |  |  |  | N | NO | <D> **** Detailed Description **** Employee tripped on excess gravel on road at corner of Hill and Port of Benton while crossing street leaving meeting at APEL facility and returning to MPF facility. Eyes were on path and hands were free. Employee fell forward and put hands out to brace self from fall. Classified as an injury due to abrasions. <I> **** Actions Taken **** Employee immediately notifed manager and self-administered first aid. No CEO notification required under GBP-COM-06. Employee also notified Industrial Safety and OH. At OH request, employee was also assessed by OH. An Incident Report and CR were also completed by COB.
391994 | CR | 20190409 |  | 4 | TSW-F-2B Motor Running Hot, High Vibration | N | N |  | N | YES | <D> **** Detailed Description **** TSW-F-2B motor running hot, high vibration, likely damaged motor bearings. Filter was switched to off under direction of CRS. <I> **** Actions Taken **** Informed CRS, shut off motor under CRS direction. | 02-00-TSW-F-2B
391995 | CR | 20190410 |  | 3 | Too many steps required to close LC task |  |  |  | N | NO | <D> **** Detailed Description **** 02136152 -05 LC D-RPS-EPA-3A3C -002 could not be set to FINISHED as excpected in DATAGLANCE. The task had to be AUTHORIZED, set to WORKING, FIELD WORK COMPLTE, etc. The control room communication is set to '1'. This type of issue will cause significant delays during the outage if not corrected. <I> **** Actions Taken **** Took the extra steps to close the task, initiated this CR to help improve the work control process <N> WO 02136152-05 is a job Type is â€˜COâ€™ (CLEARANCE ORDER: HANG OR LIFT) and in DataGlance the user would normally be able to set the WO straight to FINISHED, but this option is not allowed if the Control Room Communication is set to â€˜1â€™, which set on the Asset Suite Nuclear Panel. CORC and/or SRO review this field prior the task hold being released. . This WO task 02136152-05, although it is a support task, has the Control Room Communication set to â€˜1â€™, meaning that it is â€œHIGH IMPACT â€“ Only PSRO/OPS may take to 48â€ and Requires a QAR Record. The software is working as designed. . Tony Pace created and distributed Night order 426 to the operating crews.
391996 | CR | 20190410 |  | 3 | 16.11.6 PRM filter shows increased activity. | N | Y |  | N | NO | <D> **** Detailed Description **** The analysis of the weekly 16.11.6 PRM filters showed an increase in Co60 activity and identified short half life isotopes. The isotopic results were well below the limits of 16.11.6 Attachment 10.3. <I> **** Actions Taken **** Notified CRS, Email sent to specialist and supervision for data review.
391997 | CR | 20190410 | CAQ | D | SW-LI-1D Reads Excessively High | Y | N |  | N | YES | <D> **** Detailed Description **** SW-LI-1D indicates SW-A Spray Pond level and it is indicating 14 ft 3 inches. Local indication is 13 ft 3 inches. The instrument data sheet says the accuracy should be within 3 inches. SW-LI-1D is fed from SW-LS-1D1. | 02-00-SW-LS-1D1
392001 | CR | 20190410 |  | 4 | Driver distracted by smartphone usage | N | N |  | N | NO | <D> **** Detailed Description **** Individual was distracted while operating personal vehicle. Driver was in far left lane of security check point during a very high traffic time this morning. Driver appeared to be using their smartphone device to scroll/read through a document or possible social media site. Vehicle was driven at least 100â€™ during this time placing other employees at risk of potential injury and property at risk of damage. This action is in violation of ISPM-19 and Washington State RCW codes. 3.7 Vehicles Operated on Energy Northwest Property â€¢ 3.7.4 The driver SHALL obey all traffic rules, laws, and signs Washington State RCW 46.61.672 â€œ(1) A person who uses a personal electronic device while driving a motor vehicle on a public highway is guilty of a traffic infractionâ€¦â€ <I> **** Actions Taken **** Generated CR for trending. Unable to provide coaching.
392004 | CR | 20190410 |  | 3 | Enhance TSP-DG1-B502 by adding a step for OSP-ELEC-M101. | N | N |  | N | NO | <D> **** Detailed Description **** Enhance TSP-DG1-B502, DG1 Load Testing, by adding a step to perform OSP-ELEC-M101, DO-TK-3A OPERABILTY. TSP-DG1-B502, step 1.2 says it satisfies OSP-ELEC-M701, but it doesn't have a step for OSP-ELEC-M101. <I> **** Actions Taken **** Notified Supervisor
392013 | CR | 20190410 |  | 3 | ESP-EPA-3A3C-S901, 3B3D, 3E3F need to be revised. | N | N |  | N | NO | <D> **** Detailed Description **** ESP-EPA-3A3C-S901, ESP-EPA-3B3D-S901, ESP-EPA-3E3F-S901, need to be revised. OPs has changed how they do business, they no longer remove the keys from the switches. The keys are left in the switches and have covers placed on them. Need to delete the statements to remove the keys and put steps in for Ops to remove the covers and reinstall the covers when the task is complete. Steps 5.2.1, 7.1.115, 7.1.116, 7.2.115, 7.2.116 and 7.3.2 all have statements on keys/removing them that need revision. <N> An assignment has been created under the Maint. Procedure revision data base. No further procedure revision assignments are needed within Asset Suite. EDMS has a link to the assignment within the Maint. Procedure revision data base.
392014 | CR | 20190410 |  | 3 | RFT-LOC-1B coating, pump, and bearing failure | N | N |  | N | YES | <D> **** Detailed Description **** During the disassembly it was identified that the lower bearing had failed and the driver keyway had been rounded off. This issue is believed to be caused by a failure of the gear pump. After removal of the gear pump the gears appear to have debris in the gears due to not being able to rotate the pump, but cannot be evaluated till disassembly of the pump. See pictures in EDMS <I> **** Actions Taken **** Wrote this CR notified engineering and my supervisor. Please evaluate upgrading this model of conditioner. <N> **** Equipment Description **** RFT-LOC-1B | 02-00-RFT-LOC-1B
392016 | CR | 20190410 |  |  | Develop Action Plan for Minimizing PMs in 2nd Half of Grace | [5 empty] | <D> The goal for the station is to achieve top quartile performance for both Critical PMs in 2nd half of grace and total (Critical and Non-Critical) PMs in 2nd half of grace. The goal of this AR is to develop a plan that will minimize the number of PMs in the 2nd half of their grace period to help the station achieve our goal. This plan needs to be sustainable.
392018 | CR | 20190410 |  | 3 | Procedure enhancement to OSP-SLC/IST-Q701 | N | N |  | N | YES | <D> **** Detailed Description **** Details in EDMS. All changes are in RED and have a comment box. OSP-SLC/IST-Q701. <N> **** Equipment Description **** OSP-SLC/IST-Q701.
392020 | CR | 20190410 |  | 3 | procedure enhancement 1.3.76 | N | N |  | N | NO | <D> **** Detailed Description **** page 46 step 5 references note 4. There is no note 4. Please fix. See EDMS <I> **** Actions Taken **** wrote CR
392023 | CR | 20190410 | CAQ | D | (QA) QC rejection of ASME item for RWCU-V-4 | N | N |  | Y | NO | <C> As per the MRT this has been changed from Non-CAQ 4 to CAQ D/T. <D> **** Detailed Description **** (QA) QC identified an unsatisfactory condition while performing ASME parts acceptance for work order 02120341 task 14. ASME plan 2-3020 ASME material traveler calls for an ASME III Class 1 item Cat ID 25123651. Cat ID 25123651 (studs) that was presented to QC shows it to be ASME III Class 2 therefore conflicting with the ASME plan. The ASME PIC signature acceptance for the item had been performed for Cat ID 25123651 in the ASME traveler. <I> **** Actions Taken **** Notified the ASME PLE, Crane Supervisor, QC Level III and the Planner of the above condition. <N> **** Equipment Description **** Material verification is for shop work activity not plant installed component. ***General Notes*** Corrective actins have been taken. individual has been coached, parts have been validated, and correceted. no further actions are required to address this issue.
392025 | CR | 20190410 |  | 3 | RCA restriction not placed on employee as per procedure HPI- | N | N |  | N | NO | <D> **** Detailed Description **** RCA restriction not placed on employee as per procedure HPI-12.96. Employee reporting medical radiotherapy reported to Rad Support and provided needed information. The Rad support failed to place RCA restriction on employee as per HPI-12.96 step 4.7.3. Employee was prevented from any RCA entry by DLR sequester by RAD support/RER during this time. (4/4/19) <I> **** Actions Taken **** Notified RP Supervision
392026 | CR | 20190410 |  | 3 | Procedure Enhancement to 10.25.19 - Terms and Splices | N | N |  | N | NO | <D> **** Detailed Description **** During 2019 Block Training, The following was fed back to me as the instructor: Page 83 Step 3.1.1: 3-phase motor leads - Why do we need to re-label the leads? Page 91 Step 2.6.1: Double Verification - What is the definition? Page 79 Step 1.3.10e: Reviewer â€“ Should he be qualified in ELEV? Page 82 Step 2.11.1: Reviewer vs. Reviewed by â€“ Shouldnâ€™t they be worded differently? Page 79 Step 1.3.8: Shift Manager â€“ Whose responsibility is it to get the signature? Page 79 Step 1.3.10: Prepared by â€“ Is it the responsibility of the planner to prepare the Determ/Reterm Data Sheet? Page 84: Difference in forms â€“ I.E. the Determ/Reterm form in the procedure is different than the one used in eWP Pages 84, 93, 96: Difference between Determ/Reterm / PWTI / CTI â€“ Who decides what form to use? Page 92 Step 2.10: PWTI â€“ Why is only one QC signature required? <I> **** Actions Taken **** Provided feedback to the EL shop in March, notified supervisor, initiated CR to drive needed improvements in the procedure. Recommend dispositioning to Maintenance. <N> an assignment has been created under the maint. procedure revision data base. No assigment needs to be created for the procedure revision within Asset Suite. A link has been created within the EDMS of this AR to the assigment created within the maint. procedure revision data base.
392030 | CR | 20190410 |  | 3 | Enhancement to SOP-DG1-STBY, SOP-DG2-STBY, and SOP-DG3-STBY | N | N |  | N | NO | <D> **** Detailed Description **** SOP-DG1-STBY, SOP-DG2-STBY, and SOP-DG3-STBY all require that if starting air header pressure is GE 206 psig to reduce pressure to 190 â€“ 195 psig (See steps 5.1.2 and 5.1.3 for SOP-DG1-STBY and SOP-DG2-STBY, and steps 5.1.3 and 5.1.4 for SOP-DG3-STBY). ISCR 349623 evaluated and approved revising the DSA PCV setpoint from a setpoint of 190 psig to a new setpoint of 180 psig. Per discussion with the DG system engineer a change to the DG standby procedures should be made to reduce air header pressure to 180 â€“ 185 psig in lieu of the currently directed 190 -195 psig. <I> **** Actions Taken **** Discussed with DG system engineer. <N> Procedure should also be enhanced to include steps to more precisely control pressure. For example there are no steps in the procedures that govern how to maintain pressure if pressure drifts above the prescribed band but is not GE 206 psig. Although this is unlikely to occur the procedure should be enhanced to give the Operator better guidance.
392031 | CR | 20190410 |  | 3 | (QA) ARMA - Maintenance Performance | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) Area Requiring Management Attention â€“ Maintenance Performance. Quality â€™s rating of Maintenance performance is Yellow (needs improvement) for the current monitoring period (February 1 â€“ April 30, 2019) based largely on continued human performance errors and resulting events. Supervisory oversight and other Management issues also continue to impact department performance. Maintenance was also rated Yellow in the previous monitoring period that ended January 31, 2019 due, in part, to human performance errors. Since the performance rating remains Yellow for two consecutive periods without an improving trend, Quality is initiating an Area Requiring Management Attention with an expectation for timely resolution and improved performance. Refer to EDMS for additional details. <I> **** Actions Taken **** Discussed with Quality Supervisor, Quality Manager and Maintenance Manager.
392032 | CR | 20190410 |  | 3 | Procedure Modification | N | N |  | N | NO | <D> **** Detailed Description **** HPI-8.2 needs modification to some steps. See EDMS documents for specific details. <I> **** Actions Taken **** Documentation provided to RP Supervision of the needed modifications.
392033 | CR | 20190410 | CAQ | C | Incorrect Closure of CR 389079 | N | N |  | N | NO | <D> **** Detailed Description **** CR 389079-08 action to perform OPIT was not submitted to Corrective Action Program for approval (e.g. in the closure notes or via an assignment route list) per SWP-CAP-01, section 4.6.1(g). <I> **** Actions Taken **** Contacted CAP supervision, notified owed to group and initiated CR. Recommend CAQ/C to Engineering to obtain OPIT approval and document reason for non-compliance.
392034 | CR | 20190410 |  | 4 | Unsat Licensed Operator 19-2 Simulator Evaluation | N | N |  | N | NO | <D> **** Detailed Description **** A Licensed Operator had unsatisfactory performance on the Cycle 19-2 Evaluated Scenario administered on 4/9/19. Remediation will be IAW TDI-02 and TDI-08. Recommmend Severity level 4.
392039 | CR | 20190410 |  | 3 | OI-54 wording needs clarified for License Activation | N | N |  | N | NO | <D> **** Detailed Description **** Section 6.3 under section â€œFor RO Hoursâ€ Reads â€œUpdate to PQD LO001607 for SRO licenses via E-Tar.â€, but should state RO. Section 6.4 Operators returning to shift from a day shift position, License Class or Matrixed to another department. Because of confusion by ILC students, and all of the trainers over here I think it would be clearer if it was titled â€œInitial License activation, or Operators returning to shift from a day shift position, License Class or Matrixed to another department.â€Section 6.4 Reads â€œWill fill out the Form â€œLicense Reactivation Record Sheetâ€ Attachment 6.6.1 or â€œIncident Advisor Certification Record Sheetâ€ Attachment 6.6.2 per PPM 1.3.1â€ Should read â€œWill fill out the Form â€œLicense Reactivation Record Sheetâ€ Attachment 6.7 or â€œIncident Advisor Certification Record Sheetâ€ Attachment 6.8 per PPM 1.3.1â€ <I> **** Actions Taken **** Contacted Ops Procedure writers and Scheduler
392042 | CR | 20190410 | CAQ | C | IMDS update needed for MS-RIS-610A | N | Y |  | N | NO | <D> **** Detailed Description **** The Downscale Trip Setpoint tolerance on MS-RIS-610A IMDS Revision 30 has a different tolerance than the same setpoint on the IMDSs for MS-RIS-610B,C & D. Setpoint calc E/I-02-93-1281 states that â€˜the lower process limit for the â€œLOWâ€ alarm is zero, indicative of a failed sensor. There is no functional requirement for an upper process limit. Hence, the â€œLOWâ€ alarm should be set as close as possible to the lower limit to avoid nuisance trips of the â€œLOWâ€ alarmâ€™. This means that there is no recommended tolerance for the Downscale Trip Setpoint. . Instrument Setpoint Change Requests (ISCR) 1356, 1357 & 1365 were reviewed and it was found that the changes made on revision 27 of the IMDS for MS-RIS-610A inadvertently applied a tolerance of +/-10% to the Downscale Setpoint. A review by Design Engineering concurred that since the setpoint itself was not changed, just the tolerance, this would be a clerical error. A redlined markup of the IMDS as well as the ISCRs are attached to the EDMS folder. Procedure ICP-MS/PRM-Q401, Table 7.2c of step 7.2.37 lists the correct tolerances. Additionally, procedures ICP -MS/PRM-Q401 & ICP-MS/PRM-Q402 both have the correct tolerances for the LO Alarm/Downscale Trips for MS-RIS -610B,C & D. <I> **** Actions Taken **** Discussed issue with Maintenance I&C Supervisor, Design Engineering Supervisor and Design Engineer; redlined the changes and uploaded supporting documents in the EDMS folder. | 02-00-MS-RIS-610A
392044 | CR | 20190410 |  | 3 | Update TSW-TC-11 OMM and TSW-TE-11 IMDS | N | N |  | N | NO | <D> **** Detailed Description **** This is a documentation issue only. CVI OMM 42B-00,73 and AED IMDS TSW-TE-11 were not updated to reflect installation of the new temperature controller TSW-TC-11 after implementation of EVAL 5962 under WO 01075951. Recommend update of 42B-00,73 and IMDS TSW-TE-11 to match installed plant equipment. Additionally, recommend that the impacted components remove CVI OMM 42B-00,73 from the equipment documents panel (D078) and add CVI OMM 42A-00,237,2. Due to obsolesce and control issues with the original Bailey controller, TSW-TT-11, TSW-TE-11, and TSW-TC-11 were replaced with a single Fisher 4166K type controller in 2006. An independent temperature transmitter was no longer required with the new Fisher controller and documentation was appropriately updated to reflect TSW-TT-11 was permanently removed from the plant.he new temperature element for TSW-TE-11 was provided with the new Fisher temperature controller (TSW-TC-11); however, a separate EPN was retained for the temperature element.
392045 | CR | 20190410 |  | 3 | R24 generator clearance requirement change (Siemens Concern) | N | N |  | N | NO | <D> **** Detailed Description **** The main generator clearance provides an 18 inch air gap in the isolated phase bus for main generator work in R24. Siemens recently changed their requirements for clearance for main generator inspections requiring a second air gap protection during backfeed. The existing generator clearance has only a single air gap for the duration of the main generator work including backfeed. As an interim action the main generator clearance will need to be revised to provide a second air gap during station backfeed. An engineering evaluation (calculation) will need to be performed and approved by Siemens to provide justification for the single air gap during backfeed if possible and demonstrate adequacy of a second air gap. . CGS is in compliance with industry standards and Washington state code with respect to clearance and grounding requirements but the Siemens concern needs to be addressed for R24 and for future outages. . The requirements for the calculation are contained in Siemens Field Service Procedure FSP1201 which is available for review as necessary. <I> **** Actions Taken **** Discussed with Siemens, Project management, engineering and Operations. Initiated CR to document condition and drive resolution.
392048 | CR | 20190410 |  | 3 | Incorrect reference to ISPM-7 in PPM OI-12 | N | N |  | N | NO | <D> **** Detailed Description **** OI-12 referrences ISPM-7 for ground requirements. ISPM-7 no longer exists and trhee ground requirements were moved to ISPM-20. Revise OI-12.
392049 | CR | 20190410 |  | 4 | Met tower delta T differences between A & B | N | Y |  | N | NO | <D> **** Detailed Description **** Starting in late November a step change between MET A and MET B approx. 0.2 degree delta T occurred and over the last quarter the deviation between A & B slightly increased this can potentially impact stability class. For the last quarter stability class deviation between the two instrument loops (A & B) were 48% within expectation and 49% were off by 1 stability class and the other 3% is off by GE 2 stability classes. Env. Services will continue to monitor meteorological performance for stability class between instrument loops for A & B. Recommend this is a trending CR only. <I> **** Actions Taken **** Discussed issue with system engineer and EP personnel. <N> Discussion with environmental engineer revealed that this trending of MET tower parameters is to support the Radioactive Effluent annual report.
392050 | CR | 20190410 |  | 4 | Individual Using Unauthorized Notes on a CBT Exam | N | N |  | N | NO | <D> **** Detailed Description **** On 4/09/2019 an individual from Org 84000 was observed using unauthorized notes while taking a CBT Exam. <I> **** Actions Taken **** Individual was exited from the exam and directed to their employer. Employer and Training Management were notified.
392052 | CR | 20190410 |  | 4 | SEC-XD-9 calibration out of limits. | N | N |  | N | YES | <D> **** Detailed Description **** Weekly check for SEC-XD-9 failed calibration. <I> **** Actions Taken **** Informed supervisor, security, and generated work request. | 02-00-SEC-XD-9
392053 | CR | 20190410 |  | 4 | MT-HOI-TRN/1 hoist drum making grinding noise | N | N |  | N | YES | <D> **** Detailed Description **** MT-HOI-TRN/1's hoist drum was making a rotating, grinding noise when hoisting up. Initially, the sound was heard only while under load, but the sound increased in volume and went on to occur even while not under load. Lubrication issue with hoist rope, sheaves, or bearing housing suspected. Outage in-processing qualification for Pendant Controlled Cranes (MEBR) suspended until crane can be inspected further and source of noise determined. <I> **** Actions Taken **** Placed crane in a safe condition. Notified Training Management, Outage In-Processing, and Site Rigging Coordinator. Initiated CR. <N> Mechanical Maintenance is coming up with a plan to have Mechanics look at the issue this week. | 02-00-MT-HOI-TRN/1
392054 | CR | 20190410 |  | 3 | Missed Sales Tax and Incentive on Turbine Services Contract | N | N |  | N | NO | <D> **** Detailed Description **** The additional funding request for the turbine project field services contract last November did not include sales tax and incentive. Due to the amount of the contract, this is a substantial sum of money. As a result, the turbine project must request more funding for these items. <I> **** Actions Taken **** RxMM Management and Asset Management was notified. The overall turbine budgets were scubbed for potential reductions to offset. Presentation to PHC-SC is scheduled on April 15th. Asset management states they are performing extent of condition reviews on other projects. Other discussions included breaking contract sales tax and incentive costs out as separate budget line items to increase visibility.
392055 | CR | 20190410 | CAQ | D | (NRC) DG-RLY-87/DG2 Reset Rubber Cap Missing | Y | N |  | N | YES | <D> **** Detailed Description **** NRC Identified - The rubber cap on the reset lever is missing on DG-RLY-87/DG2. Please replace. <I> **** Actions Taken **** wrote CR | 02-00-DG-RLY-87/DG2
392057 | CR | 20190410 | CAQ | C | NRC - Observations of DGs | Y | N |  | N | NO | <D> **** Detailed Description **** See EDMS for details of observation. <I> **** Actions Taken **** Informed NRC resident inspector of planned actions.
392058 | CR | 20190410 | CAQ | D | CRD-HCU-3855 high level alarm | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-3855 high level alarm. Trending <I> **** Actions Taken **** Drained moisture per SOP and made a log entry in eSoms | 02-00-CRD-HCU-3855
392059 | CR | 20190410 | CAQ | C | Received 812.R1.10-2 alarm | Y | N |  | N | YES | <D> **** Detailed Description **** DC MOTOR MCC ROOM COOLER FLOW LOW alarm. SW-FI-41 indicates 18 gpm. Alarm setpoint is LE 16 gpm, min op value is 12 gpm. | 02-00-SW-FI-41
392060 | CR | 20190411 |  | 4 | ASD Glycol Indicate Less Than 5Mohm, Filter Changes Required | N | N |  | N | YES | <D> **** Detailed Description **** GY-CI-10A1 indicating 4.86Mohm, GY-CI-10A2 indicating 4.7 0Mohm, GY-CI-10B2 indicating 4.56Mohm, ASD glycol system filters GY-F-10A1, GY-F-10A2, and GY-F-10B2 changes are required. <I> **** Actions Taken **** Informed CRS, initiate CR/WR | 02-00-GY-F-10A1,02-00-GY-F-10A2,02-00-GY-F-10B2
392061 | CR | 20190411 |  | 4 | ASD 1A/2 Coolant Leakage Between Hose and Pipe | N | N |  | N | YES | <D> **** Detailed Description **** ASD 1A/2 coolant leakage near floor between hose and copper pipe. Black, gummy substance collecting on the floor beneath hose/pipe connection. Glycol collectiong on and can be wiped from the connection. Previous AR 372559 WR 29139281 has been closed but the leak is still present. <I> **** Actions Taken **** Informed supervision, initiated AR/WR | 02-00-RRC-IMD-ASD1A/2
392062 | CR | 20190411 |  | 3 | Procedure Enhancement SOP-RWCU-START, Quick Restart |  |  |  | N | NO | <D> **** Detailed Description **** In the RWCU quick restart procedure for Modes 1,2&3, the procedure directs fully opening RWCU-V-44. Normally RWCU -V-44 only needs to be cracked open to support removal of RWCU Demins from service; in fact, RWCU-V-44 doesnâ€™t even open enough to indicate dual (the red OPEN light never illuminates) when removing or restoring RWCU Demins. SOP -RWCU-START, section 5.3 Reactor Water Cleanup System Quick Restart, Steps 5.3.5.a and 5.3.7.a directs â€œVERIFY RWCU -V-44 OPEN (RWCU Demin Bypass).â€ Not only is this unnecessary, but it causes excessive RWCU flow which causes elevated temperatures and a thermal transient and possible High Temperature Alarms if one takes too long. It is also an error likely setup because this valve then needs to be almost shut again and if one shuts it for a few seconds too long, the valve goes fully closed and the RWCU pump trips on low flow. Recommend changing Steps 5.3.5.a and 5.3.7.a to read: â€œThrottle RWCU-V-44 open five secondsâ€.
392065 | CR | 20190411 |  | 4 | CF-P-13 abnormal - metalic rubbing noise | N | N |  | N | YES | <D> **** Detailed Description **** CF-P-13 (EDR and FDR filter Precoat pump) is making an abnormal noise. The noise sounds similiar to light metalic rubbing, perhaps impeller is beggining to come in contact with casing while at speed. CF-P-13 is still producing normal flow rate of ~350 gpm while precoating the FDR filter. Note: failure of this pump would result in the inability to change out the EDR and FDR filters and prevent any water processing in the RWCR. This pump is somewhat of a single point vulnerability - reccomend elevating the investigation/repair. CF-P-13 is used about once a day. No abnormal vibrations or heat could be felt on the pump motor or casing. <I> **** Actions Taken **** Informed MCR. Verified normal flow rate while precoating the FDR filter. No abnormal vibraitions or heat could be felt. <N> **** Equipment Description **** Behind RWCR | 02-00-CF-P-13
392066 | CR | 20190411 |  | 4 | 2 Pieces of M&TE OOT | N | N |  | N | NO | <C> CR reopened to add severity. <D> **** Detailed Description **** 2 Pieces of M&TE were found OOT & adjusted within specs. Neither were used during Calibration cycles. Calcode #0063994 Fluke Temp. Probe- model 80PK-26. New Sensor replaced broken one in set. DEF #7000A written. Calcode #0065620 Ashcroft Sensor- model HQS-2 -15/+30psig. DEF #7001A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
392067 | CR | 20190411 | CAQ | D | M&TE OOT | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0066333 Votes Infinity Data Acquisition Switch Unit- model 85004 found OOT. Sent out for Repair. MOV Eng Eval: The OOT related to the current input measurements only affects the MN185 current probes measurements which are not a set-point type measurement (i.e. motor running current). Therefore, the acceptance criteria for thrust, torque and limits were not impacted.. No additonal testing or actions are required. DEF #6986A written. <I> **** Actions Taken **** None Trending purposes only.
392068 | CR | 20190411 | CAQ | D | Entered ABN-HVAC due to MCR Temperature GT 78F | Y | Y |  | N | YES | <D> **** Detailed Description **** Entered ABN-HVAC due to MCR temperature GT 78F. Running CCH-CR-1A for surveillance testing, dispatched OPS-2 to investigate. CR written to document condition per LCS. <I> **** Actions Taken **** Reported that CCH-CR-1A was running at full load, 16 inches of suction pressure on CCH-PI-6A. | 02-00-CCH-CR-1A
392070 | CR | 20190411 |  | 4 | M&TE Suspended. | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0065821 Hytorc Hyd. Torque Wrench- model Stealth 14 was Not used during Calibration cycle. Suspended until further Eval can be done. DEF #7002A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
392072 | CR | 20190411 |  | 3 | Ordered part is missing the relay | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While cleaning out Building 13 to make room for more parts found a Fisher E/P that is missing the relay. Unable to use in this condition MR# 00221397 WO# 02046429. <I> **** Actions Taken **** Returning said E/P to warehouse
392076 | CR | 20190411 |  | 4 | RX SW Elevator Out of Service | N | N |  | N | YES | <D> **** Detailed Description **** Reactor Building SW elevator doors sticking, and will not open without assistance on at least two floors (441', 471'). <I> **** Actions Taken **** Informed MCR and hung retractable belt barriers. Credited elevator fire doors are closed and performing the fire barrier function. | 02-00-MT-ELEV-2
392077 | CR | 20190411 |  | 3 | Certain special characters lead to login issues for eSOMS | N | N |  | N | NO | <D> **** Detailed Description **** eSOMS, as well as other web based applications using LDAP for user authorization/authentication can have errrors when certain special characters are present in user passwords. Some examples include <, >, & though this list is not all inclusive. <I> **** Actions Taken **** Opened a case with the vendor (ABB). Checked other applications for this issue and found that Syntempo also has this issue.
392078 | CR | 20190411 |  | 4 | Level 1 Procedure Filing Error in the TSC | N | N |  | N | NO | <D> **** Detailed Description **** While performing the weekly audit of the procedures that were filed the previous week in the TSC, it was discovered that PPM 1.20.3 was misfiled under PPM 1.20.2. <I> **** Actions Taken **** The filing error was corrected and both PPM 1.20.2 and 1.20.3 were verified to be the current revisions. IS Management team has been informed and the individual that performed the filing has been coached. No further actions are needed or required. CR initiated for trending purposes only.
392085 | CR | 20190411 | CAQ | D | B5B Portable BATTPACK | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** It was dicovered that the "quick connect" connection to the B5B battery suitcase was disconnected. The positive and negative cables that come from the charger, connect to the battery on the outside of the suitcase and then are taped to secure in place. It was found that the taping had slipped and pulled apart over time. After reporting this discrepancy, the connection was repaired per supervisor direction. However this finding lead to the WO (0213373-01) being stopped and unable to complete due to a prerequsite that the battery has been on float for 48 hours. This damage could have potenially taken place due to the poor placement of this battery. which is on the top shelf in a tight space. A more sufficient location for this battery and its charger would be on a small rack near the receptacle that it is being feed from. <I> **** Actions Taken **** cr report to supervision reported to engineering <N> **** Equipment Description **** B5BPORTABLE BATTPACK
392088 | CR | 20190411 |  | 3 | (QA) PO.39 requirements and deliverable misaligned | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) The requirements for pre-outage milestone closure are provided in PPM 1.20.1 â€œRefuel Outage Preparation and Milestonesâ€ but those requirements cannot be satisfied for PO.39 at the time of milestone closure. The definition of Refueling Outage R24 Milestone PO.39 â€œRadiological ALARA Planning Completeâ€ states that radiological planning defines the dose projection for the outage, and how, where, and when that dose will be received. R24 radiological plans identify how and where dose is received, but not when. A projection of when dose will be received is not feasible at PO.39 closure because the outage schedule available at milestone closure does not provide sufficient information. Note: The Milestone Numbers were changed in PPM 1.20.1 Rev. 18 and those numbers are effective for R25 Milestones. The R24 Milestone Numbers are reflected in Rev. 17. Insights: â€¢ Radiation Protection develops an outage daily dose projection as part of milestone PO.44 â€œRadiation Work Permits Approved, High Risk Plans Developed and Final Dose Estimate Completeâ€. This dose projection satisfies the requirement to identify when dose will be received. â€¢ Outage management scheduled a post R24 outage revision to PPM 1.20.1 to incorporate this deficiency and other changes in preparation for R25. <I> **** Actions Taken **** Discussed this issue with the Outage Manager. This is a Deficiency identified in Quality Surveillance SR-19-11. Recommend assignment to AR-OTMG. <N> **** Equipment Description **** N/A
392094 | CR | 20190411 | CAQ | C | Spare MSRVs springs out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** The five spare MSRVs that are being rebuilt at NWS for use in R24 were found with springs below the free height tolerance (the total height of the spring is below the manufacturer tolerance). The springs will need to be replaced or accepted as-is with engineering evaluation for effects of blowdown. These S/N valves previously passed their relief setpoint tests prior to being removed and stored as spares. The spring datasheets are attached in the EDMS. Valve S/Ns: N63790-03-0046 N63790-03-0134 N63790-03-0135 N63790-03-0137 N63790-03-0138
392096 | CR | 20190411 |  | 4 | RRC-M-P/1A Upper Oil Reservoir Level Indication | N | N |  | N | YES | <D> **** Detailed Description **** On around 2/12/19 and 4/2/19, the RRC-M-P/1A upper oil reservoir level indication rose one inch from 0.6 inches to 1/6 inches. This appears to occur when the motor speed exceeds 1,800 rpm. The level indication dropped to its previous value on around 3/5/19 when the motor speed was reduced. In addition, this similar behavior was observed during the last cycle during coast down. Looking at the cycle before that, the reservoir level stayed near the 1.6 inch mark and the motor stayed near 1,800 rpm. This was during the breaker to breaker run and before motor speed was reduced due to ARTS-MELLLA. Only the 1A upper reservoir level indication exhibits this dramatic of a level change with higher motor speed. The other three RRC motor oil reservoir levels will change with motor speed, but by only a few tenths of an inch. This is an indication only issue that is unique to this reservoir and is being reported for trending purposes only. The level floats are calibrated every refueling outage and the 1A upper float has always been shown to be functioning correctly. All indications and alarms are functional. In addition, this behavior hasnâ€™t affected the ability of RRC-M-1A to perform its required functions. | 02-00-RRC-LS-1A
392098 | CR | 20190411 | CAQ | C | OG-V-803K normal position conflict |  |  |  | N | NO | <D> **** Detailed Description **** This is a documentation issue only. OG-V-803K is shown as normally closed on M535-1 and the D031 panel; however, the normal lineup as shown in SOP-OG-LU, and 12.2.2 is normally open. Discussed lineup with Chemistry and determined that this valve is normally left open to purge the Off-Gas Vial Sample Rack when it is not in use. Recommend resolution by Design Engineering to confirm appropriate configuration and update documentation accordingly. | 02-00-OG-V-803K
392099 | CR | 20190411 |  | 4 | Unexpected cooler behavior on E-TR-M2 | N | N |  | N | YES | <D> **** Detailed Description **** A E-TR-M2 alarm was received for cooler group 2 failure or off positon. ABN-TRANSFORMER 7.4.11 was used. Cooler groups 1, 3, 4 were found on with cooler group 2 fans/pump off. All contacts on cooler 2 were de-energized and NOT tripped. This happens periodically for unknown (but speculated upon) reasons and has been CRâ€™d in the past. The group 2 cooler control was taken off and at that instant group 3â€™s relays de-energized. Due to this unexpected event the operator informed the CRS; the SSS and a second EO came to assist. After a discussion of the events, it was concluded that it was possible that the cycle-off temp for group 3 had been very close to the setpoint and interference may have caused group 3 to cycle off when the switch was turned. The ABN was continued, the group 2 contacts were reset, then the panel was reset and the alarm cleared with group 2 running and 3 off. CR for trending. <I> **** Actions Taken **** Informed CRS. | 02-00-E-TR-M2
392100 | CR | 20190411 | CAQ | C | Discrepancies with OSP-FLEX-A106 | N | Y |  | N | YES | <D> **** Detailed Description **** There were several discrepancies noted while performing OSP-FLEX-A106. See attached document for full comments. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** FLEX
392101 | CR | 20190411 | CAQ | D | Fire Hydrants 2T, 2I, 2S not working correctly | N | N |  | N | YES | <D> **** Detailed Description **** Performing 15.1.12 found FP-HT-2S , and FP-HT-2T barrel draining very slow, FP-HT-2I operates very hard. all hydrants function and are all non saftey related | 02-00-FP-HT-2I,02-00-FP-HT-2S,02-00-FP-HT-2T
392102 | CR | 20190411 |  | 3 | (NRC)Procedures Differ for DG Governor Oil Levels |  |  |  | N | NO | <D> **** Detailed Description **** NRC identified that DG governor oil levels are referenced differently in our procedures, reference: â€¢ In SOP-DG3-STBY step 5.1.8 Governor Oil Level is called out as Â¼â€ to Â½â€ above the line in the sightglass â€¢ SOP-DG-GOV-OIL talks about oil level being approximately Â¼â€ above the sightglass â€¢ SOP-DG1-STBY step 5.1.6 has governor oil between the top of the sightglass and 0.25â€ below the top of the sight glass. â€¢ OPS 2 logs, FORM 27153 has governor oil level approximately Â¼â€ above the midline on the sight glass . These procedures are all reference slightly different oil levels or reference points. Please consolidate the procedure requirements. <I> **** Actions Taken **** Discussed with NRC, no operability concern for the DGs. <N> Governor actuator oil levels should be maintained at 1/2 inch above the line in the sight glass during standby and above the line in the sight glass during operation. See EDMS for email to Shift manager.
392103 | CR | 20190411 | CAQ | D | Received H13-P800C.5 drop 6-7 battery B1-7 ground alarm | Y | N |  | N | YES | <C> CR reopened to cross reference additional WR 29147794, then taken back to complete <D> **** Detailed Description **** Received H13-P800.C5 drop 6-7 125 VDC BATTERY B1-7 GROUND alarm. Ground is approximately 50K ohms. No abnormalities on bus S1-7 voltage or current. After 14 minutes ground returned to infinity and alarm was reset. Operators were dispatched to investigate with nothing abnormal noted. <I> **** Actions Taken **** Foloowed ARP and when ground indication returned to the infinity position reset ground per ARP | 02-00-E-B1-7
392105 | CR | 20190411 |  | 3 | PCR - PPM 1.10.1 and 1.3.82 |  |  |  | N | NO | <D> **** Detailed Description **** In PPM 1.3.82 there are multiple reporting requirements for NERC/WECC in Attachment 9.2. PPM 1.10.1 does not have all of these reporting requriements. I recommend that in PPM 1.10.1 we reference PPM 1.3.82 for the reporting of issues to NERC/WECC. Examples are 1 hour report to NERC/WECC for physical and cyber attacks is not on page 14 of PPM 1.10.1 for cyber incidents. <I> **** Actions Taken **** Discussed with OPS procedures, wrote CR. <N> This CR is being clossed to AR 388688- which is handling updates to PPM 1.10.1.
392106 | CR | 20190411 |  | 3 | Concrete fractures during anchor installation WO 02136475-02 | N | N |  | N | NO | <D> **** Detailed Description **** Concrete anchors were being drilled out and installed for the CCVT foundations per EC 17406. During the time of installation the foundations began to develop cracks in the body of the concrete foundation. The holes that were drilled meet the requirements listed in PPM 10.2.23. <I> **** Actions Taken **** Verified the concrete break tests met the compressive strength requirements. Notified the project manager and engineering. Generated a CR. <N> **** Equipment Description **** There are three foundations total, 1 of the 3 is fractured on the corner. . Concrete repairs have been completed. Engineering performed a follow-up field walk down and inspected the concrete and verifed that the repairs were completed. .
392107 | CR | 20190411 |  | 4 | FLM camera tour identified several issues. | N | N |  | N | YES | <D> **** Detailed Description **** Due to increase in the Plant water usage rate, a camera tour was performed and identified that BS-V-54B, HD-V-18D and HV-V-31G have a noticiable increase in leak rate. These leaks are already coded as S5 in the Fluid leak program. <I> **** Actions Taken **** Notified the CRS and SM. Work orders are already in place for the permanent repairs in R24. | 02-00-BS-V-54B,02-00-HD-V-18D,02-00-HV-V-31G
392108 | CR | 20190411 |  | 4 | SEA-DPS-3 failed to bring in Low Flow alarm | N | N |  | N | YES | <D> **** Detailed Description **** SEA-DPS-3 failed to bring in the SEA-FN-3 Low Flow alarm when SEA-FN-3 was secured. The Alarm tile lights were tested and verified to be good. Several minutes were waited to ensure it was not merely a delay issue. SEA-FN-3 low flow alarm is located on E-CP-SBHV/1 (GSB 456). SEA -FN-3 shaft was verified stopped, Mechanical agitation was applied to SEA-DPS-3 but failed to rendure the expected alarm response. <I> **** Actions Taken **** Informed MCR. Verified SEA-FN-3 did secure, as evidence by red to green light indications and 0 rpm shaft rotation. <N> **** Equipment Description **** GSB 456 | 02-00-SEA-DPS-3
392109 | CR | 20190412 |  | 4 | Security XD 4 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security XD 4 in the PAAP is not operating by design and needs maintenance. Equipment taken out of serivice. <I> **** Actions Taken **** CR/WR initiated. Security supervision notified. Equipment taken out of service. | 02-00-SEC-XD-4
392110 | CR | 20190412 |  | 4 | GSB PAP ARGOS Out Of Service | N | N |  | N | YES | <D> **** Detailed Description **** ARGOS HP-EQ-42783 located at the RCA exit point of the GSB is out of service due to "low background counts" on body detector 10a. <I> **** Actions Taken **** Placed monitor out of service, contacted RP Supervision and initiated WR. <N> **** Equipment Description **** GSB PAP RCA Exit | 02-00-HP-EQ-42783
392111 | CR | 20190412 |  | 4 | WOA-FL-1 EOR Alarm in | N | N |  | N | YES | <D> **** Detailed Description **** Following filter replacement the end of roll alarm remains locked in. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** RW 487' | 02-00-WOA-FL-1
392112 | CR | 20190412 |  | 4 | WPWH-DISC-7E3E will not CLOSE | N | N |  | N | YES | <D> **** Detailed Description **** WPWH-DISC-7E3E will not CLOSE. WPWH-DISC-7E3E is currently Danger Tagged OPEN (Danger tag is hanging on Cubicle door - NOT the handle). This discrepency was found while attempting to cycle WPWH-DISC-7E3E when hanging its Danger tag, Per OI-12 and/or 1.3.64. Please investigate/repair before tag lift is scheduled (~ 36hours from 4/12). WPHW -DISC-7E3E powers the Hot water heater on the RW 487. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RW487 | 02-00-WPWH-DISC-7E3E
392113 | CR | 20190412 |  | 3 | Typo on EWD-15E-042 | N | N |  | N | NO | <D> **** Detailed Description **** EWD-15E-042 contains a typo that needs corrected. at quadrent 7C on drawing is says MS-LT-61D. this should be MS-LT-61B. This mistake was intruduced in rev 6. CVI- dwg 02H22-05,87 correctly shows that it is MS-LT-61B <I> **** Actions Taken **** contacted engineering anad obtained concurrence from EFIN htat this is a typo and wrote CR
392116 | CR | 20190412 | CAQ | C | E937-3 Correction | N | N |  | N | NO | <D> **** Detailed Description **** E937-3 says HT-H-7FX is for FP-LT-TK100. It should say that it is for PWC-LT-100.
392117 | CR | 20190412 |  | 3 | Troxler Gauge Brought On Site Without HP Support Scheduled | N | N |  | N | NO | <D> **** Detailed Description **** On 4/12/2019, a work group contacted Radiological Operations to support soil compaction testing with a troxler gauge, which contains radioactive sources (Cs-137 and Am-Be) . This activity creates dose rates in excess of 1.6 mrem/hr outside of the protected area fence, which requires continuous radiological support. This activity was not scheduled with HP resources or support, and no scheduled activity related to soil compaction testing or troxler gauge use could be identified. Unscheduled support prior to an outage puts an undue strain on HP resources and could impact our ability to support actually scheduled work. <I> **** Actions Taken **** Discussed issue with Rad Ops Supervisor and HP Lead Technician. Resources shuffled to support soil compaction testing.
392118 | CR | 20190412 |  | 3 | Yakima power outage impacted more equipment than planned | N | N |  | N | NO | <D> **** Detailed Description **** On 4/12/2019, the scheduled power outage to the General Services Building (GSB/Yakima Building) interrupted power to Radiological Operations' RCA egress monitors (all four WBCMs and both gamma-sensitive Portal Monitors), four out of six TES access computers, one SAM-12, and both RCA turnstiles. This outage was not planned to impact any of these items. At the same time, lighting and power was not interrupted to all of the Rad Ops general assembly area as originally planned. Interrupting power to sensitive contamination monitors without properly powering them down could affect the monitor software or the integrity of the detectors and electronics. <I> **** Actions Taken **** Discussed with Rad Ops Supervisor. Ran temporary extension cords to provide power to some egress equipment and one turnstile. <N> Recently updated Facilities drawing 0271EP001 determined to be inaccurate for the receptacles in this immediate area. As-found drawing mark-up obtained and will be forwarded to the Facilities department for revision.
392119 | CR | 20190412 |  | 4 | PMA-AC-51 compressors. | N | N |  | N | YES | <D> **** Detailed Description **** Upon PM inspection as part oof PMA-AC-51 (WO 02108858), it was identified that the top portion of the two compressors to the units are becoming corroded/rusted and should be replaced in the near future prior to hot weather to ensure operation through the summer. <I> **** Actions Taken **** Generated CR for seperate WR. This could be FIN minor Maintenance within the next 4 weeks prior to R24. | 02-00-PMA-AC-51
392120 | CR | 20190412 |  | 4 | PMA-FN-51 belt needs replaced. | N | N |  | N | YES | <D> **** Detailed Description **** As part of PM checks on PMA-AC-51, to it was identified that the belt on warrants replacement on PMA-FN-51. Recommend belt replacement via WR with unit currently tagged out for maintenance in conjunction with WO 02108858. <I> **** Actions Taken **** Generated CR. Will contact Control Room to pursue this WR being added to the existing clearance for the PM work order. | 02-00-PMA-FN-51
392121 | CR | 20190412 |  | 3 | Procurement Specification AED SPC 15614 R000 | N | N |  | N | NO | <D> **** Detailed Description **** Procurement Specification AED SPC 15614 R000 (FIRE PROTECTION PUMP & MOTOR ASSEMBLY PROCUREMENT SPECIFICATION 15614 - NFPA & UL CERTIFIED) indicates specification number 15614 on the first 5 pages of the uploated document but indicates specification number 15216 on the remaining pages of the uploaded document. Additionally, a total of 46 pages are indicated (e.g., page 1 of 46) on page 1 of 46 through page 3 of 46 but the pages after that indicate a total of 44 pages (e.g., page 4 of 44) and the last page of the uploaded document is page 43 of 44 (possibly missing the last page of the document). AED SPC 15216 is a different Procurement Specification document entirely (not affected by this AR CR condition). . This is an administrative issue only - no impact/effect upon any existing installed plant equipment.
392122 | CR | 20190412 |  | 4 | Fluorescent Lamps found stored in corner |  |  |  |  | NO | <D> **** ANONYMOUS CR - Detailed Description **** Fluorescent lamps were found leaning in a corner which is a hazard. This house keeping hazard was observed after lighting was assigned to electrical site support contrators. It is possible that the standard was not properly relayed to whomever stored these lights. This discrepancy was immediatly reported to supervision. <I> **** Actions Taken **** stored lamps properly CR Written <N> **** Equipment Description **** 501 RX ANON CR Generated, moved to OPS for review.
392123 | CR | 20190412 | CAQ | D | 3 sections of floor coating on RW 525' have cracking | Y | Y |  | N | YES | <D> **** Detailed Description **** While working o RW 525' area craft identified a small section of the floor coating to contain some cracking where the floor meets the wall. <I> **** Actions Taken **** Contacted Operations/Engineering. Operations will add pictures and further details based on that identified. Per discussion with Operations, three small sections were identified. Per history, the paint is a credited floor barrier per 1.3.57 and Barrier Impairmenent will apply until the coating is addressed by the Work Control Process. This item as of now is expected to require a Barrier Impairment with Hourly Fire tour impacts. 3 sections of cracking/damage were observed. One section on either side of the doorway to room C510. And one section directly across from the doorway located behind portable air sniffers. Pictures have been attached. . Walked down the AR CR condition as requested by the Shift Manager. It is the flexible toe board along the wall that was run into/over by something (e.g., a cart wheel or a barrel edge) causing it to flex more than the flexible epoxy coating painted on it could tolerate. It is the flexible toe board along the wall and the coating on the flexible toe board that is damaged, not the underlying concrete floor slab. Further, the existing coating on the concrete under the AR CR subject cracked coating appeared to remain intact. Additional photos and movies are attached to the AR CR EDMS. <N> **** Equipment Description **** Radwaste 525' Floor Coating
392124 | CR | 20190412 |  | 3 | Sliding door at building 167 is challenging to open | N | N |  | N | NO | <D> **** Detailed Description **** When trying to access materials inside building 167 workers were challenged with opening the door. The door required multiple workers to open the door. Once the door started to move it rolled better. <I> **** Actions Taken **** Door was closed and workers notified supervision to initiate CR for resolution.
392125 | CR | 20190412 |  | 4 | 15.1.12 - Fire Main Header and Hydrant Inspection | N | Y |  | N | YES | <D> **** Detailed Description **** During performance of section 7.7.8 for the flush of the last 5 hydrants specifically done today (tested ~ 33 in total from Tuesday through today) FP-HT-2E, FP-HT-2D, FP -HT-2C, FP-HT-2P, FP-HT-2M several intemittent flow variations in were observed. Specifically FP-HT-2E was initially opened for ~ 1 minute until clear, then upon closing the FP-HT-2E, it was observed the flow had just started to fluctuate (Hose monster used). The hydrant was checked ~ 10 times throughout the day to check, and at times variations in flow were observed. For FP-HT-2D was flushed and the flow was observed with lower flow for this hydrant flush using the hose monster. FP-HT-2C was flushed with the diffuser but appeared to be somewhat normal however the hose moster was not used. FP-HT-2P flow fluctuated during the flush with hose monster. FP-HT-2M, flow fluctuated during this flush with hose monster. Installed a pressure gauge on other port during flush, pressure remained constant around 145 psi. FP-HT-2E as stated was checked again, captured video of fluctuations and pressure gauge remained constant at 145, changed hose to 4" and 4" hose monster and GPM gauge showed 2300 with strainer removed. <I> **** Actions Taken **** Discussed with Control Room, contacted FP per the step 3.4 of PPM 15.1.12. Note, video put on the following location: S:\Maintenance\Fire Protection\Hydrant Flow Fluctuation/IMG 0649.MOV | 02-00-FP-HT-2E
392126 | CR | 20190412 | CAQ | D | Relay reset lever missing cap | Y | N |  | N | YES | <C> Duplicate of CR392129 <D> **** Detailed Description **** NRC identified that E-RLY-27/8/2 on SM-8 is missing the plastic cap from the end of its reset lever. Other similar relays in the vicinity have their caps intact. This does not affect operation of the relay or of its reset lever. <I> **** Actions Taken **** SM was informed of condition by NRC resident, SSS walked down identified relay and others in the area. | 02-00-E-RLY-27/8/2
392127 | CR | 20190412 | CAQ | C | (NRC) Timeliness of Repair | N | N |  | N | NO | <C> CR reopened to add completion required check mark to referenced WO 02118025 per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** The NRC resident inspector noted that CR 288285 / WR 29106637 written for a material deficiency on ROA-CB-FN1A breaker trip indication in 2013 has not been repaired. A review of the associated WO 02046067 shows that the WO is at the planning stage with no schedule for repair yet established. No safety concern was communicated though the timeliness of the repairs was commented on. <N> the material deficiency was previously identified. The NRC observation is regarding timeliness of the resolution of the material deficiency. . Reviewed CR and WP with outage schedulers and UC. Determined that work can be done on-line and bundled with the next overhaul of that breaker (PMID 10308-04/05) in Jan 2020. UC changed WP to daily from outage and scheduled in Jan 2020 with associated work noted above. No additional additional action reequired.
392128 | CR | 20190412 | CAQ | D | NRC Identified: SW-P-1B oil seeping from motor flange | Y | N |  | N | YES | <D> **** Detailed Description **** The NRC identified oil seeping from the bottom flange on SW-P-1B's motor. Specifically the oil was coming from the dark blue 8-12" tall midsection (between pump and motor) flange surface that mated to the top of the pump case (4-5' off the ground). The residue was cleaned up by an operator. The quantify of oil was small enough it could not be measured and was cleaned up with a single small towel. The leakrate is low enough that it also cannot be measured, but given a period of time it will likely occur in the future. <I> **** Actions Taken **** Informed CRS. <N> An oil drop was also wiped up from the RTD well to the lower motor oil resevoir. Oil drop appears to have collected due to weepage. | 02-00-SW-P-1B
392129 | CR | 20190412 | CAQ | D | (NRC) E-RLY-27/8/2 Relay Reset | Y | N |  | N | YES | <D> **** Detailed Description **** The NRC resident inspector noted that the E-RLY-27/8/2 relay reset does not have a plastic/rubber tip on the end similar to other relays in SM-8. No safety concern was communicated. | 02-00-E-RLY-27/8/2
392130 | CR | 20190412 |  | 4 | (NRC) RPS-MG-1 Room Lighting | N | N |  | N | NO | <D> **** Detailed Description **** The NRC resident inspector noted that some light fixtures mounted in the RPS-MG-1 room have chains attached to them with the other ends of the chains attached to cable trays or other fixtures in the room. Similar chain installation may were observed elsewhere on some light fixtures elsewhere in the RW 467â€™ vital island. The inspector was curious of the purpose of the chain. No safety concern was communicated. <I> No photos were attached to the AR CR EDMS but the observed chains for the subject W467' vital island area overhead light fixtures are likely tethers installed where necessary for QC 2 over 1 purposes - reference PPI ENG CIVES-6 (DESIGN REQUIREMENTS FOR NONSAFETY-RELATED ITEMS IN SEISMIC CATEGORY I AREAS) section 6.3. Following discussion with the Shift Manager, confirmed via field walkdown that the subject chains are QC 2 over 1 tethers for their associated light fixtures. Photos are now attached to the AR CR EDMS.
392131 | CR | 20190412 | CAQ | D | Received H13-P800.C5 drop 6-7 125 VDC BATTERY B1-7 GROUND. | Y | N |  | N | YES | <C> CR reopened to cross reference additional WR 29147794, then taken back to complete <D> **** Detailed Description **** Received H13-P800.C5 drop 6-7 125 VDC BATTERY B1-7 GROUND alarm. Ground is approximately 50K ohms. No abnormalities on bus S1-7 voltage or current. After 7 minutes ground returned to infinity and alarm was reset. Received same alarm previous day 4/11/19 at 1505. See AR 392103 and WR 29148023. | 02-00-E-B1-7
392132 | CR | 20190412 | CAQ | D | H13-P611 Panel GG-16 Terminal Crimp | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02138373-01, the crimp on terminal GG-16 panel side was found with insulation not inside crimp on ring lug per 10.25.19. <I> **** Actions Taken **** Discussed with Supervision, continued with inspections. Wire appears to be functioning correctly. Wrote CR and WR to document. <N> **** Equipment Description **** H13-P611 MCR
392133 | CR | 20190412 |  |  | A RFT thrust bearing temperature perturbation |  |  |  | N | YES | <D> **** Detailed Description **** Operational decision making issue evaluation 386522 in response to B RFT high vibrations requires a once per shift check of the thrust bearing temperatures(EDNA pts W005 ,W006,W008,W009) on the A/B RFTâ€™s. On 4/9 a slight downward perturbation was noted on the A RFT with a return to normal temperatures over about 3 hours. This perturbation has occurred daily about the same time over the last 3 days, each time with a larger drop in temperature <N> **** Equipment Description **** A RFT thrust bearing | 02-00-RFT-TI-37A
392134 | CR | 20190412 |  | 3 | A RFT thrust bearing temperature perturbation | N | N |  | N | YES | <D> **** Detailed Description **** Operational decision making issue evaluation 386522 in response to B RFT high vibrations requires a once per shift check of the thrust bearing temperatures(EDNA pts W005 ,W006,W008,W009) on the A/B RFTâ€™s. On 4/9 a slight downward perturbation was noted on the A RFT with a return to normal temperatures over about 3 hours. This perturbation has occurred daily about the same time over the last 3 days, each time with a larger drop in temperature. | 02-00-RFW-P-1A
392135 | CR | 20190412 | CAQ | D | HPCS-C3-2 has a suspected blown fuse | Y | N |  | N | YES | <D> **** Detailed Description **** While performing operator rounds on the HPCS diesel it was observed that the air blowdown flow from DSA-DY-2 was very weak and diminishing compared to normal. The pressure downstream of DSA-DY-2 at DSA-PI-9C was reading 0 psi. The two air receivers were reading 250 psi at DSA -PI-8 and 255 psi at DSA-PI-7. After returning an hour later it was noted that one of the compressors was running and charged up the the air receivers to 265 psi at DSA-PI-8 and 267.5 psi at DSA-PI-7. The pressure downstream of DSA-DY-2 at DSA-PI-9C was 250 psi. At the end of the day the pressure downstream of DSA-PI-9C was observed to be low again at 40 psi. The air receivers were at normal pressure of 255 psi and 257.5 psi. HPCS-C3-2 battery charger for the lister diesel battery was showing less that 0 amps. It is suspected that HPCS-C3-2 has a blown fuse. Reference AR 225790 for posibly checking lister diesel battery voltage. <I> **** Actions Taken **** Wrote CR and notified CRS | 02-00-HPCS-C3-2
392136 | CR | 20190412 |  | 3 | EC MALT 14851 is implemented but at EXPIRED status |  |  |  | N | YES | <D> **** Detailed Description **** EC MALT 14851 (REPLACE NSR ITE WCH-CB-7E4E MCCB, OBSOLETE) was physically implemented during R23 via WOT 02077504-01 but the PMT task (WOT 02077504-03) was not completed at that time as intended and has yet to be completed. By automated process, EC MALT 14851 went from ACTIVE to EXPIRED status on 03/23/19. For resolution, EC MALT 14851 must be unexpired and WOT 02077504-03 must be completed so that the modification can be advanced to MODIFIED status and beyond. Please assign resolution to AR-MODS. Will need assistance from AR-EFIN (Responsible Engineer). <I> EC MALT 14851 was administratively unexpired 04/16/19. | 02-00-WCH-CB-7E4E
392137 | CR | 20190412 | CAQ | D | R-DOOR-R103 door will not close if closed slowly | Y | Y |  | N | YES | <D> **** Detailed Description **** It was observed that R-DOOR-R103 door will not close if closed slowly. The limit switch at the top of the the door (that leads to the override keylock switch and red light box) will not allow the door to close all the way if the door is closed slowly by hand. If you travel in and out of the door like normal then the door will close all the way. <I> **** Actions Taken **** Notified CRS and wrote CR | 02-00-R-DOOR-R103
392138 | CR | 20190412 |  | 3 | Unable to Determine new OPS-3 Log |  |  |  | N | NO | <D> **** Detailed Description **** New OPS-3 log states to log the throttle position of the condensate booster pump oil cooler TSW outlet valve. This can not be determined without operating the valve. Log needs to be modified. <I> **** Actions Taken **** informed SSS and CRS <N> **** Equipment Description **** OPS-3 electronic logs
392139 | CR | 20190412 |  | 3 | EC MALT 12510 is implemented but at EXPIRED status |  |  |  | N | YES | <D> **** Detailed Description **** EC MALT 12510 (INSTALL ULTRASONIC FLOW METER ON THE 6"DW(3)-1S PIPE) appears to have been plant implemented via WO 02095007 as of 01/28/19 but the modification went from ACTIVE to EXPIRED status by automated process on 03/30/19. . For resolution, EC MALT 12510 must be unexpired so that the modification can be advanced to MODIFIED status and beyond per DES-2-22, DES-2-23, and DES-2-25. Please assign resolution to AR-EFIN. <I> EC MALT 12510 was administratively unexpired 04/16/19. | 02-00-DW-FE-123,02-00-DW-FI-1,02-00-DW-FI-123,02-00-DW-FT-1
392140 | CR | 20190412 |  | 3 | All GEM 5s Alarmed at the Protected Area Egress |  |  |  | N | NO | <D> **** Detailed Description **** Removal of Troxler Gauge from Protected Area causes GEM 5s at PA Egress to Alarm. HP received a phone call from Security stating that 2 Gem 5s were in fault and the third one showed someone was contaminated. HP responded and found that the vendor was removing the Troxler Gauge from site through the trunstiles. The close proximity of the Troxler Gauge alarmed all the Gem 5s. HP instructed the vendor to take the Troxler Guage out of the security bldg. The Gem 5s reset and personnel were able to exit the PA. After taking with security the Troxler Gauge was scheduled to come through the trap on a vehicle but not as soon as the vendor/work group wanted so the Troxler Gauge was brought in through the personnel access into the PA. HP was not aware of this and was not aware that they were taking it out of the PA via the tunstiles. <I> **** Actions Taken **** Reported to PA egress, had the source removed from the area, reset the Gem 5s, discussed with security the circumstances of how things transpired, Notified HP Supervision and Initiated this CR. <N> Causes and actions for this event will be documented and resolved under AR-39117. No further actions required under this AR.
392141 | CR | 20190412 | CAQ | D | Door R-104 Will Not Latch | Y | Y |  | N | YES | <D> **** Detailed Description **** NRC identified that the latch for door R-104 is sticks and not fully engaging the plate. | 02-00-R-DOOR-R104
392143 | CR | 20190412 | CAQ | D | Leaks identified on CCH-CR-1A | Y | Y |  | N | YES | <D> **** Detailed Description **** During performance of WR 29148008 two areas were identified as testing positive for leaks. The mating surface around the circumference of the float chamber and around the king valve. See EDMS for picture. <I> **** Actions Taken **** Generated CR notified SM and WWM, planning is working on a WO to repair | 02-00-CCH-CR-1A
392144 | CR | 20190413 |  | 4 | RW 487' Men's Restroom |  |  |  | N | YES | <D> **** Detailed Description **** HP-EQ-63090 at the RW 487' Men's Restroom is not working due to Low Beta Counts on one detector and has been taken out of service. <I> **** Actions Taken **** Wrote AR / Work Request . Noted problem in HP turnover log. . <N> **** Equipment Description **** RW 487 Men's Restroom
392145 | CR | 20190413 |  | 4 | E-TR-M2 Fan 10 overloads tripping | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-M2 Fan 10 overloads tripped twice within an hour, causing MCR alarm and local Cooler Group 4 Failure alarm. It was successfully reset, and the fan restarted after the first one, but after the second the decision was made to monitor via temp log. Recommend investigate and repair. <I> **** Actions Taken **** Informed MCR, generated AR/WR. . See cross-referenced CR's. There is a degrading trend on main transformer cooler group problems. | 02-00-E-TR-M2
392152 | CR | 20190413 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. The alarm was due to the J15 sensor [230KV undervoltage]. The J15 sensor has been reset. E-TR-S and E-TR-B voltages are 239/238/238 kV and 119/118/118 kV respectively. BPA Munro reports that at 0901 the Potholes - Sand Dunes 230 KV line relayed off and on. Neither 230 kV nor 115 kV near grid was involved. This outage did not affect service power to CGS from either 230 kV or 115 kV power supplies. No damage or RAS in place. All plant controllers and equipment exhibited normal operation. <I> **** Actions Taken **** Informed CRS/SM
392153 | CR | 20190413 |  | 4 | Hydraulic oil leak in MPF parking lot from sweeper machine |  |  |  | N | NO | <D> **** Detailed Description **** During parking lot sweeping activities, one of the vendor machines developed a hydraulic oil leak. A small amount of oil was leaked. No human performance issues identified. <I> **** Actions Taken **** Removed equipment from service. Notified E&RP, supervisor and manager. Qualified employee cleaned up spill, E&RP will make designation for waste.
392154 | CR | 20190413 |  | 3 | TSP-THERM-C101 Procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Per discussion with SNEs, copy and paste NOTE from the tope of page 22 of TSP-THERM-C101 to just prior to step 10.1.11 on page 12. While in FFTR, step 10.1.11 will be performed and a comment will be made that the plant has entered FFTR on the surveillance cover sheet to satisfy step 10.1.11.f .(2). <I> **** Actions Taken **** Discussed with SNEs. Email documenting the conversation sent to all Ops personnel who might perform or review TSP -THERM-C101.
392156 | CR | 20190413 | CAQ | D | E-CB-B/7 open indication light socket is broken. | Y | N |  | N | YES | <D> **** Detailed Description **** E-CB-B/7 open indicating light socket will not recieve a light bulb. Found no bulb in the socket on rounds and attemped to relamp. It appears that the contacts for the bulb base have been pulled forward in the socket. Perhaps when the original burned out bulb was extracted? The light sockets on SM-7 are scheduled for replacement in R-25. Please determine if a repair is required before then. This indicator is located on the breaker cubicle door. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** RW 467 | 02-00-E-CB-B/7
392157 | CR | 20190413 | CAQ | D | TSC Mens Bathroom Urinal Flush valve stuck open | N | Y |  | N | YES | <D> **** Detailed Description **** TSC mens bathroom urinal flush valve stuck open, PWC-V-290 was closed to stop overflow. This isolated water to both Mens and Womens bathroom in TSC. PWC-V-290 has a 1/16' steady stream packing leak. <I> **** Actions Taken **** Infromed CRS/SM Costco for configuration for PWC-V-290. | 02-00-PWC-V-290
392158 | CR | 20190413 | CAQ | D | Rod Accumulator Trouble Alarm for CRD-HCU-3027 | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-3027 was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear.[ | 02-00-CRD-HCU-3027
392159 | CR | 20190413 |  | 4 | PWC shock suppressor leaking R572 | N | N |  | N | YES | <D> **** Detailed Description **** After restoration of PWC from E-CB-5B1B replacement a PWC leak was found on the R572. Leak was several drips per minute onto a staged temp power box. Please fix this so that RB air wash can be put in service before weather get to point of needing air warsh. Picture placed into EDMS <I> **** Actions Taken **** PWC-V-114 and 119 CSTCO'd closed. Informed CRS and OPS2. Asked SM to add to weekend issues list. | 02-00-PWC-PIPE-MISC
392161 | CR | 20190414 |  | 4 | TMU-C-1A Low Oil Level | N | N |  | N | YES | <D> **** Detailed Description **** The oil level in TMU-C-1A is low, well below the threads of the oil fill cap, see EDMS for Photos. TMU-C-1B was placed in Auto and TMU-C-1A in Standby. Please add oil <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** TMU Pumphouse | 02-00-TMU-C-1A
392164 | CR | 20190414 | CAQ | D | Yellow plastic tarp covering crane bay on RB 606 | N | Y |  | N | NO | <D> **** Detailed Description **** Yellow plastic tarp covering crane bay on RB 606. SOP-DOOR/HATCH-OPS and 1.5.18 both state that the A1 hatch is part of the severe accident response for the hardened containment vent final integrated plan. It should remain open when plant needs do not require it to be closed. If this is part of a credited air flow path wouldnâ€™t this extend to the RB 606 which has most of the normal reactor building exhaust flow on it. If the reactor building exhaust fans were lost in a severe accident then the plastic tarp would block air flow going from the RB 606 toward the SGT fans or if those were also lost would not allow complete natural ventilation of the reactor building. <I> **** Actions Taken **** Wrote CR Informed SM <N> AR-EVAL 00392197 has been initiated and cross referenced.
392165 | CR | 20190414 |  | 4 | Reactor building NW stairwell on the 606 is blocked off |  |  |  | N | NO | <D> **** Detailed Description **** Reactor building NE stairwell on the 606 is blocked off for alara and contamination concerns. It is unclear if this has been evaluated for as blocking off an emergency egress route from the 606 in the event of an emergency. Recommend opening up the stairwell route and placing warning signs to not use stairs unless in the event of an emergency. <I> **** Actions Taken **** Wrote CR Informed SM . It is actually the NW stairwell that is blocked, not the NE. Per ISPM-18, 3.4.2 When erecting barriers of any type, the boundaries should be well planned. Emergency egress routes, access to power shutoffs, etc., should only be restricted when absolutely necessary to prevent personnel entry into the hazardous area. Alternate means of egress from the area should be considered.
392166 | CR | 20190414 |  | 4 | Scaffolding placed over SLC piping does not have eng evaluat |  |  |  | N | NO | <D> **** Detailed Description **** Scaffolding placed over SLC piping does not have a signature indicating that an engineer has evaluated the scaffolding for being within 12 in of the safety related SLC piping and valves. Recommend documenting engineering evaluation on scaffolding tag. <I> **** Actions Taken **** Wrote CR Informed SM
392167 | CR | 20190414 | CAQ | D | Oil observed at HPCS-P-1 lower drain plug | Y | N |  | N | YES | <D> **** Detailed Description **** Oil found around the HPCS-P-1 lower drain plug. Oil level in the bullseye is within specification (between min and max). No constant visible oil leakage from lower drain plug was observed. <I> **** Actions Taken **** Wiped up oil. Informed CR. | 02-00-HPCS-P-1
392168 | CR | 20190414 |  | 4 | E-TR-1/11 pressure low. | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-1/11 is at 0 psig. The normal operating range is 0 - 4 psig. Please add nitrogen. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 471W | 02-00-E-TR-1/11
392169 | CR | 20190414 |  | 4 | E-LP-3C-B handle broken | N | N |  | N | YES | <D> **** Detailed Description **** the access cover handle is broken for LP-3C-B. during tag audit, i attempted to open the LP and the handle fell off in my hand. the interior parts of the lock are not visible thru the hole, and it appears the door may be locked shut still. i applied a reasonable amount of force to the panel to try and open it to no avail. the panel is located on the border of the BPA excavation/work area under the MODS. <I> **** Actions Taken **** informed SSS and MCR initiated CR/WR | 02-00-E-LP-3CB
392170 | CR | 20190414 |  | 3 | Recommend PPM 1.5.18 enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Recommend adding guidance to PPM 1.5.18 concerning the installation and control of the RB 606' south equipment hatch plastic cover due to the HCV impact and the fact that this cover is not accounted for in Extended Loss of AC power (ELAP) Beyond Design Basis External Event (BDBEE) calculation, ME-02-18-12. This cover should controlled with restrictions similar to those of hatch A1 position. It is also recommend that SOP-HVAC/RB-START, SOP-HVAC/RB -OPS, PPM 10.3.21, and PPM 10.3.22 be enhanced to reflect this information.
392171 | CR | 20190414 | CAQ | D | Debris in SW A pond | Y | Y |  | N | NO | <D> **** Detailed Description **** Two small clear pieces of plastci were floating in SW. pond A. <I> **** Actions Taken **** Initiated CR <N> **** Equipment Description **** SW A pond
392172 | CR | 20190414 |  | 4 | Locked in alarm on System Cabinet 1 in Comm Room | N | N |  | N | YES | <D> **** Detailed Description **** Locked in alarm " Zone 7 FAIL" on System Cabinet 1 in Comm Room. the alarm was reset and then reappeared a few seconds later. <N> **** Equipment Description **** Zone 7 Fail alarm on system cabinet 1 in the comm room
392173 | CR | 20190414 |  | 4 | E-TR-M3 Cooler Group 2 Failure Alarm | N | N |  | N | YES | <D> **** Detailed Description **** Upon investigation none of the three fans or oil pump were running. None of the Motor overloads were clearly tripped. However, the overload for FAN 6 (52F-6) was found slightly askew, see EDMS for photo. Per ABN-TRANSFORMER the overloads were all reset, the overload for FAN 6 reset with the same tactile sensation as the other overloads (the switch may just be misaligned). The alarm was attempted to be reset but remains locked in. A temporary log was established to verify transformer temperature and additional alarms. Investigate and Repair. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** Transformer Yard | 02-00-E-TR-M3
392176 | CR | 20190415 |  | 4 | WOT 02106853-01 not completed by scheduled late date |  |  |  | N | NO | <D> **** Detailed Description **** WOT 02106853-01 (HPSCHDDLR PROC, DLR LOG IN) was not completed prior to the late date of April 13, 2019. The work order was initially scheduled in January, and the work was completed at the time; however, the work package was not closed out in DataGlance. The work package rode the schedule for approximately 3 months, but it did not appear on the schedule reports reviewed by Rad Ops personnel. Rad Ops did not recognize that the work package was from January, and instead believed that it was incorrectly scheduled. This allowed the package to go overdue.â€ <I> **** Actions Taken **** None taken - work could not be performed. <N> CR edited at the request of initiator.
392178 | CR | 20190415 |  | 3 | RECORDS SUBMITTED WITHOUT SIGNED TRANSMITTAL |  |  |  | N | NO | <C> Changed to non-CAQ as per the MRT. <D> **** Detailed Description **** RECORDS WERE SUBMITTED TO RECORDS CONTROL BY WILLIAMS PLANT SERVICES WITHOUT A SIGNED TRANSMITTAL. PLEASE FOLLOW SWP -REC-02 SECTION 4.3.2 FOR THE SUBMITTAL PROCESS. <I> **** Actions Taken **** NOTIFIED MY SUPERVISOR. SENDING RECORDS BACK TO WILLIAMS PLANT SERVICES FOR CORRECTION AND RE-SUBMITTAL. <N> Williams Plant Services. Documents have been resubmitted in accordance with SWP-REC -02.
392179 | CR | 20190415 |  | 4 | Procedure 10.25.141B update |  |  |  | N | NO | <D> **** Detailed Description **** Need to update procedure 10.25.141B step 7.1.2 page 7 to correct equipment catagory "manually operated". <I> **** Actions Taken **** CR initiated and completed procedure change request with markup. <N> PCN 19-0008 implemented for rev 006.002
392187 | CR | 20190415 |  | 3 | ODMI for FPC-V-172 |  |  |  | N | YES | <D> **** Detailed Description **** The purpose of this CR is to track the ODMI for FPC-V-172, the actions required from the ODMI, and closure of the ODMI. This is an administrative CR only, since the original CR documenting a diagnostic anomoly was trended to the work management process. However, per request from station management, an ODMI is now required for this condition. Please assign as a 3 to AR-SECOMP. <I> **** Actions Taken **** ODMI distributed to Shift Manager for review and signature. Assignments made under this CR. | 02-00-FPC-V-172
392188 | CR | 20190415 | CAQ | C | Emergency Notification Primary system , Communicator | N | Y |  | N | YES | <D> **** Detailed Description **** Communicator, the system used for Emergency Notification to employees, was updated by the vendor on April 11th 2019. Since that time, the paging notification does not function. The SCC is aware and is using the backup Communicator server. <I> **** Actions Taken **** Notified Motorloa that the paging service is not functioning. Notified EP and the SCC that testing is being conducted. . Notes modified to remove individuals name. <N> **** Equipment Description **** Emergency Preparedness Department to notify all ERO members of callouts, Actual events, Senior Mgmnt, and on the fly m essages to the ERO members.
392189 | CR | 20190415 |  | 4 | 3 Pieces of M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** 3 Pieces of M&TE were found OOT and None were used during Calibration cycles. #44830 Hytorc Hyd. Torque Wrench- model 1XLCT. Adjusted within specs. DEF #7003A written. Calcode #45321 Hytorc Hyd. Torque Wrench- model 2XLCT. Adjusted within specs. DEF #7004A written. Calcode #0068189 RAD Dig. Battery Torque Wrench- model DB-RAD 3000-2. Rejected - Can't adjust. DEF #7005A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
392191 | CR | 20190415 |  | 3 | SOP-CN-START needs enhancement. |  |  |  | N | NO | <D> **** Detailed Description **** SOP-CN-START needs enhancement. Section 5.1 of SOP-CN-START has steps that are misnumbered. 5.1.1 thru 5.1.6 then it should be 5.1.7 but starts over again at 5.1.1 thru 5.1.7. Steps should be labeled 5.1.7 thru 5.1.13 <I> **** Actions Taken **** Contacted supervision and issued this CR.
392192 | CR | 20190415 | CAQ | C | CMS-P-1401 Diaphragm found cracked | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02114149-01 CMS-P-1401 Pump Rebuild the existing diaphragm was found to be cracked when removed. See EDMS for picture. Diaphragm was replaced per the CVI and work instructions. â€¢ Request assignment to system engineer to determine if preventative maintenance frequency needs to be increased for PMIDâ€™s 971-03 and 970-03. Current frequency is two years. <I> **** Actions Taken **** Notified the MCR and initiated CR | 02-00-CMS-P-1401
392193 | CR | 20190415 |  | 3 | Model work orders need revision CMS-P-1401/1301 |  |  |  | N | NO | <D> **** Detailed Description **** Model work orders for CMS-P-1401 PMID (971-03 REBUILD PUMP) (971-04 REPLACE PUMP/MOTOR ASSEMBLY) & CMS-P-1301 PMID (970-03 REBUILD PUMP) need to be revised. â€¢ The use of the PV parts sheet needs to be incorporated in the precautions/limitations of the work instructions; currently nothing drives you to use it (error likely situation). A caution note concerning the energy (120V) that is still in the SR. Instructions in the electrical determ/retem tasks to install and remove voltage rated plastic for mechanics. â€¢ Step 4.4 PERFORM Step 4.1 of the enclosed â€œPump rebuild Instructionsâ€ from CVI OMM 441-00,10,2 Appendix D (Doc P -9484). Page 22 â€“ 30 electronically. There needs to be notes that address the following steps in the CVI: â€¢ CVI 4.12.1 and 4.12.2 references Loctite 271 not 242. Loctite 271 is used â€¢ CVI 4.14.1 RTV not used step 4.14.2 installs alternate seal CMS-P-1301 PMID (970-03 REBUILD PUMP) â€¢ Doesnâ€™t have the part number for the rod connecting alignment tool P/N A99995 in the Prerequisites like the work order for CMS-P-1401. â€¢ Material request-the Paste and the catalyst (20651) silicone sealant (92902502) need to be unreserved, we donâ€™t use anymore we use as an alternate method if required. The rod connecting alignment tool is ordered every time. There should be a step to return it or unreserved it if you canâ€™t find the tool in the special tool storage area as stated in the prerequisites. â€¢ Recommend assignment to maintenance planning <I> **** Actions Taken **** Provided feedback to planning initiated CR
392194 | CR | 20190415 |  | 4 | Lost DLR |  |  |  | N | NO | <D> **** Detailed Description **** Individual Employee ID number C1832U reported to HP his DLR was lost. DLR was apparently lost offsite. <I> **** Actions Taken **** Notified HP supervision, Documented loss on form 14872, initiated a Conditon Report. A replacement DLR was issued.
392196 | CR | 20190415 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0068598 Proto Torque Wrench- model 6006C 80ft/lb found OOT & adjusted within specs. New- Never Used. DEF #7006A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
392198 | CR | 20190415 |  | 4 | New designs should include ball valve locking devices |  |  |  | N | NO | <D> **** Detailed Description **** OI-12 and PPM 1.3.64 require all ball valves that are danger tagged to be locked in their required positions. Because most ball valves in columbia did not include locking devices in their original design, resources must be spent on labor costs and temporary locking devices instead. There is ample OE where valve mispositions have occurred with ball valves due to them being bump hazards (this includes potentially dangerous mispositions of danger tagged valves). Recommend all future Engineering Design Changes incorporate "ball valve locking devices" in their design to save resources and mitigate potential mispositioning events in the future. To clarify, this CR recommends the change be incorporated in FUTURE designs only, and does not attemp to comment on existing ball valves already installed in the plant. <N> Engineering Design Guideline "CGS Specific Design OE and Considerations" has been revised to include direction to incorporate ball valve locking devices within new design changes installing new ball valves to mitigate PCSC (Plant Component Status Control) issues and support tagging efforts. No further actions necessary.
392203 | CR | 20190415 | CAQ | C | RECORDS NOT SUBMITTED IAW GBP-REC-04 |  |  |  | N | NO | <D> **** Detailed Description **** RECORDS WERE SUBMITTED TO RECORDS CONTROL BY OPERATIONS WITHOUT FOLLOWING THE RECORDS SUBMITTAL PROCESS FOR CONFIDENTIAL RECORDS. THE RECORDS TRANSMITTAL WAS NOT FILLED OUT PROPERLY AND THE RECORDS WERE NOT FLAGGED AS CONFIDENTIAL. ALSO THE RECORDS WERE DELIVERED VIA MAILROOM AND HAD BEEN LEFT UNATTENDED IN THE OUTGOING MAIL SLOT FOR AN UNDISCLOSED AMOUNT OF DAYS. THIS IS NOT IN ACCORDANCE WITH GBP-REC-04 SECTION 4.7. <I> **** Actions Taken **** NOTIFIED MY SUPERVISOR AND APPLICABLE INDIVIDUALS WITH OPERATIONS FOR CORRECTIONS TO BE MADE.
392204 | CR | 20190415 | CAQ | C | SW-V-171B Acceptance tag does not match ASME plan |  |  |  | N | NO | <D> **** Detailed Description **** During prefabrication of the replacement SW-V-171B under WO 02076390-02 it was noticed the valve acceptance tag does not match the ASME plan requirements, specifically the year addenda. The plan calls for 74/S75 where the acceptance tag is listed 71/W73.The valve was NOT PICâ€™d all prefabrication besides the welding of the valve was completed in the 02 task, the remainder of the welding will be completed in the installation task 01 following Engineering acceptance of the valve. This does not affect the valve function as it is not currently installed. <I> **** Actions Taken **** Notified Code Programs, generated CR for documentation.
392205 | CR | 20190415 | CAQ | C | ACUMEN GNF-A ECP Open Problem Report Notification (20190410) |  |  |  | N | YES | <D> **** Detailed Description **** ACUMEN is in parallel testing, so core monitoring system design functions and operability are not impacted. GNF ACUMEN software error notice attached to EDMS. ACUMEN error 2019-014, Post System-Detected Scram Start-Restart With Bad Rod Positions not Working ACUMEN error 2019-013, VIEW ALL Instance Predictor Report Displays Wrong Thermal Limits and PCRAT <I> **** Actions Taken **** Recommend Category C to AR-RXFUEL to incorporate interim actions in procedure changes to be implemented by EC 17398. See EMDS for recommended interim actions. . Users notified by e-mail. See EDMS. | 02-00-PPC-SOFT-ACUMEN
392208 | CR | 20190415 |  | 3 | Potential CFR/NRC commitment violations found in SWP-FFD-01 |  |  |  | N | NO | <D> **** Detailed Description **** Regarding administrative action that was taken against an employee following a positive fitness for duty test result only. Reference CRâ€™s 391935/391936. Several potential procedure violations for SWP-FFD-01 have been identified including SHALL actions that are required to be taken in order to comply with Code of Federal Regulations (CFR) or NRC commitments. Step 4.1.10a. states EN or contractor management personnel who knowingly DISREGARD the requirements of the FFD Program and/or this procedure are subject to corrective action. I have attached applicable pages in the EDMS docs. Reference SWP-PRO-01 for definition of SHALL. Three separate points are listed below. Point 1 Actions were not taken per Figure 1 pages 16-17: Referral to the SAE, Determination of Fitness and Obtain negative test under observed conditions prior to receiving access. . Point 2 Shall statements in section 4.5.1 were not performed: Section 4.5.1 states The actions and sanctions referenced herein are minimum actions and sanctions (1) Energy Northwest employees shall be referred to the EAP for assessment and referral and (2) This assessment, counseling, and treatment shall receive review and approval by an Energy Northwest-approved treatment specialist. Point 3 Step 4.5.2c was not followed, no other evidence was provided: 4.5.2 Actions on Initial Positive Test Results: Except as specified below, all actions and sanctions listed in Figure 1 shall be based upon confirmed positive test results only. c. Action as above for initial positives for the other substances in Figure 2 may be taken when, and only when, other evidence indicates an individual is impaired or might otherwise pose a safety hazard. Other evidence can include, but is not limited to, those behaviors or incidents listed in Attachment 8.2, Behavior and Job Performance Warning Signs.
392209 | CR | 20190415 |  | 3 | Swollen Li-ion batteries identified in the MCR. |  |  |  | N | NO | <D> **** Detailed Description **** 2 cicso phone batteries were identifed as disteneded. This is an idication of overheating, overcharging, or internal degredation and possible fire hazard. The guidance for LI -ION battery disposal that was found states to tape the leads and place in a waste container. Contacted E&RP and we were asked to deliver the swollen batteries to them. Request that GBP-ENV-17 be updated to include a section detailing station policy about disposal of Li-ion batteries that may be degraded. Recomend that the CISCO phone batteris be surveyed to see if there are any other distended batteries. Request that 2 additional spare batteries be sent to the Main contol room to replace the 2 sent for disposal. This issue does not impact any SSC and is not plant equipment. <I> **** Actions Taken **** Removed the batteries from service. Taped the connections. Utilized an EO to transport the batteris to E&RP individual at Deschutes/1-177 for disposal as requested.
392210 | CR | 20190415 |  | 4 | MT-CRA-1 will not bridge | N | N |  | N | YES | <D> **** Detailed Description **** MT-CRA-1 will nbot Bridge in either direction. The trolley and both hooks function as designed. <I> **** Actions Taken **** Cycled the 480 Volt Disconnect to attempt to reset the system to no avail. Lowered the load to the floor and removed all rigging from the small hook and raised the hook to upper limit. <N> **** Equipment Description **** TG 501" | 02-00-MT-CRA-1
392212 | CR | 20190415 | CAQ | D | Clean and evaluate leakage on bushings inside of term box | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02107738 and marked completion required box, then taken back to complete <D> **** Detailed Description **** E-TR-B has an active oil leak (identified in AR-CR 00361129) from the low voltage bushings and the Low voltage terminal box should be cleaned up and evaluated for leakage in R24. The purpose of this CR is to obtain a work request so this work can be scoped into R24. At the time of this cleaning it is recommended that a drain valve be installed on the doghouse to drain the oil from the terminal box for the transformer when the transformer out of service for this maintenance. This valve will be used to evaluate the leakage similar to the doghouse drain valves that are installed on each main transformer. AR-OSCR 392211 was initiated to scope both WRs into R24. This CR has no impact on E-TR-B because oil level on the transformer is within the transformer operating level. | 02-00-E-TR-B,02-00-E-TR-B-SPARE
392214 | CR | 20190415 | CAQ | D | Received 4.800.C5 drop 6-7 125 VDC BATTERY B1-7 GROUND | Y | N |  | N | YES | <C> CR reopened to cross reference additional WR 29147794, then taken back to complete <D> **** Detailed Description **** Received 4.800.C5 drop 6-7 125 VDC BATTERY B1-7 GROUND. Indication was approximately 75% on the way toward infinty from the 25Kohm mark . No work was in progress at the time. Ground was reset and stayed clear. The only S1-7 work was investigation of AR-CB-P1A about 1 hour earlier. <I> **** Actions Taken **** Reset alarm. Monitoring. | 02-00-E-RLY-64X/B4
392215 | CR | 20190415 |  | 4 | ISP-CRD-Q404 02138373-02 record |  |  |  | N | NO | <D> **** Detailed Description **** ISP-CRD-Q404 02138373-02 record is only in data glance and was performed 4/12/2019. I had to review 02129302 on 4/15/19 which is a work order being credited by the performance of 02138373-02. I looked at portal and the QAR for the work package only contains the 01 task. No QAR exists for the 02 task which is the task that is crediting the completion of the work. <I> **** Actions Taken **** Informed supervision The QAR QAR for 02138373 will show up after the I & C supervisor reviews it.
392216 | CR | 20190415 |  | 3 | RWP can be modified after termination |  |  |  | N | NO | <D> **** Detailed Description **** When an RWP is brought to completed status it becomes a record and should not be modified. However, there is an option on the R210 panel for completed RWPs that says "Unprotect HP logbook". This option allows adding, removing or modifying logbook text. We evaluate whether this is acceptable and correct it if not. <I> **** Actions Taken **** Wrote CR
392217 | CR | 20190415 |  | 4 | NET3-COMP-EPO hung on logout | N | N |  | N | YES | <D> **** Detailed Description **** NET3-COMP-EPO is stuck on logout for several accounts. This is related to the issue documented in CR 374547 and AR Eval 376954. To restore locin capabilities for the hung users, the system needs to be rebooted. Services are functioning normally, only Computer Engineering user access is impacted. . This does not affect Operations. This is not a reportable condition. . Recommend Trend/Repair to Computer Engineering <I> **** Actions Taken **** Generated CR and WR | 02-00-NET3-COMP-EPO
392218 | CR | 20190415 |  | 4 | R24 LL 0.075 rem recieved against estimate of 0.032 rem |  |  |  | N | NO | <D> **** Detailed Description **** ALARA task 02048833-07-01 to build scaffold to RHR-MO-23 received 75 mrem against an estimate of 32 mrem. A cause of this was that the work order had been sequenced such that shielding would be installed to reduce dose rates prior to the scaffold installation, but the work was performed before the shielding was installed. WO 02048833 is a scheduled R24 work order, but the scaffold was allowed to be built pre-outage. This was a mistake since the associated shielding could not be hung during plant operations . The lack of shielding caused work to take place in greater than planned dose rates. While no holds or restrictions were violated in the RWP or work order, RP planning, RP operations and the carpenters all missed opportunities to question the work schedule versus the sequence on the work order. <I> **** Actions Taken **** Wrote the CR <N> Briefed and provided coaching to the ALARA planning group on the need to ensure an intrusive evaluation of pre-outage scaffolding is completed prior to installation.
392219 | CR | 20190415 |  | 3 | Vendor notification of End-of-Life (EOL) for ePO software | N | N |  | N | YES | <D> **** Detailed Description **** Per vendor notification, the ePO software version 5.3 running on NET3-COMP-EPO and NET4-COMP-EPO reached End-of-Life (EOL) on March 31, 2019 and is no longer a supported version. . This does not impact operations. This is not a reportable condition. . Recommend a 3 to Computer Engineering. <I> **** Actions Taken **** Generated CR | 02-00-NET3-COMP-EPO,02-00-NET3-SOFT-EPO/SERVER,02-00-NET4-COMP-EPO,02-00-NET4-SOFT-EPO/SERVER
392220 | CR | 20190415 | CAQ | C | MS-RIS-610A display failed. | N | Y |  | N | YES | <D> **** Detailed Description **** MS-RIS-610A display failed. The failure is similar to previous failures of MS-RIS-610's. <I> **** Actions Taken **** Using computer point X169 for data recording, informed CRS/SM, wrote this CR and WR. | 02-00-MS-RIS-610A
392221 | CR | 20190415 |  | 4 | Two unsat licensed operator 19-2 simulator evaluations |  |  |  | N | NO | <D> **** Detailed Description **** Two Licensed Operators had unsatisfactory performance on the Cycle 19-2 Evaluated Scenario administered on 4/15/19. Remediation will be IAW TDI-02 and TDI-08, therefore recommend severity level 4.
392225 | CR | 20190416 |  | 3 | CBT program vulnerable to exploitation |  |  |  | N | NO | <D> **** Detailed Description **** There is no password security on the CBT program, and the login id is just the employee id number. An employee could easily accidentally or intentionally log in with another employee's id number and take (or fail) CBTs. Some of these can cause a loss of plant access or loss of other quals, and could significantly impact personnel required for plant operations. Recommend prompt action to close this vulnerability. <I> **** Actions Taken **** Discussed with Shift Manager, generated AR. . Currently no evidence the CBT system is or has been intentionally or accidentally used as described in this CR. <N> While there are CBTs in Plateau with exams (i.e., Safeguards Access, Basic Safety as examples), the badge affecting CBTs such as BOP/FFD, General Protected Area Access, and Radworker CBTs are in NANTEL which require unique username and password, which prevents accidental test taking by another user.
392228 | CR | 20190416 | CAQ | C | FP Piping Configuration Control | N | N |  | N | YES | <D> **** Detailed Description **** While performing required PMs on FP Sprinkler Systems Mechanical Maintenance identified severe degradation of sprinkler system drain piping. . Upon review of the as-built piping and drawing 217-00,135; the in-plant as built piping does not match the drawing. Configuration control has been lost on this piping at some point. This CR is to align the field piping with the drawing. . FP recommends removing drain piping from drawing 217-00,135 as sprinkler drain piping is open to atmosphere and is only utilized in performance of surveillances and/or PMs. Piping downstream of drain angle valves attached to wet -pipe alarm check valves or pre-action/deluge deluge valves should be removed from the drawing to allow for better routing of the piping to accommodate drainage. . Drain piping does not affect functionality of the suppression systems. . Contact FP System Engineer Roy Burson x4117 for additional information. . Spoke with design and design drafting, CR should be routed to AR-DMC. <I> **** Actions Taken **** Spoke to Design Engineering, Design Drafting Engineering and Mechanical Maintenance. <N> **** Equipment Description **** FP-V-W2/020 - 4" ALARM VALVE,WET SYSTEM #2 - T -445- - -G1/8.1 - . FP-V-W3A/040 - 4" ALARM VALVE, WET SYSTEM #3A - T -445- - -G1/8.6 - . FP-V-W3B/060 - 4" ALARM VALVE,WET S YSTEM 3B - T -445- - -G1/8.5 - . FP-V-W5/100 - 6" ALARM VALVE, WET SYST. 5 - T -445- - -G1/8.8 - . FP-V-D53B/361 - DELUGE SYS 51 - 4" DELUGE VALVE - T -444- - -G1/8.0 - . FP-V-D53A/341 - DELUGE SYS 53A - 4" DELUGE VALVE | 02-00-FP-V-D53A/341,02-00-FP-V-D53B/361,02-00-FP-V-W2/020,02-00-FP-V-W3A/040,02-00-FP-V-W3B/060,02-00-FP-V-W5/100
392229 | CR | 20190416 | CAQ | C | Replacement relay failed initial bench test |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During intial set up and bench test of control relay Cat ID # 68604340 some of the contacts failed to change state upon energizing the relay. This Cat ID requires an eight hour warm up time before testing. After the eight hour burn in time the relay was cycled 50 times per work instructions and the contact resistances checked. Some of the contacts failed to change state. The relay was ordered under MR 225635 under WO# 02112991-06. <I> **** Actions Taken **** Failed the relay and notified supervision <N> **** Equipment Description **** Replacement relay. Failed the bench test
392234 | CR | 20190416 |  | 3 | Risk of service impact for hosted apps from vendor updates |  |  |  | N | NO | <D> **** Detailed Description **** hosted/cloud applications are at risk for service impacts and/or interruptions due to vendor patches and/or upgrades that are performed without an allowance for EN to test the changes prior to implementation. <I> **** Actions Taken **** Generated CR to capture the issue. Notified IS Leadership. <N> Recommend CAT 3 to ITMGMT
392236 | CR | 20190416 |  | 4 | R-Door-R-404 does not shut without manual action (helb) | N | N |  | N | YES | <D> **** Detailed Description **** Door R-404 will not shut when released from 1/2 open swing. the knob must be rotated to fully close the door and this is a posted HELB barrier <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-R-DOOR-R404
392237 | CR | 20190416 |  | 4 | Main 3 transformer gas analyzer alarm light lit | N | N |  | N | YES | <D> **** Detailed Description **** Transformer Main 3 gas analyzer alarm light is lit. | 02-00-E-AY-TR/M3
392238 | CR | 20190416 | CAQ | D | FP-P-2A Seal water pressure low | N | Y |  | N | YES | <C> CR reopened to cross reference additional WR 29149888, marked completion required box, then taken back to complete <D> **** Detailed Description **** Seal water pressure low on FP-P-2A | 02-00-FP-P-2A
392239 | CR | 20190416 |  | 3 | EC MALT 10986 R003 is implemented but at EXPIRED status |  |  |  | N | YES | <D> **** Detailed Description **** EC MALT 10986 R003 (E-TR-B ALARM RELAY) appears to be implemented or partially implemented but the modification went from ACTIVE to EXPIRED status in Portal J by automated process on 07/30/2018. Additionally, there does not appear to be any existing ENG assignment tracking implementation and closeout of this modification package - the parent AR EVAL 261653 is COMPELTE status and never had an ENG assignment. . For resolution, EC MALT 10986 R003 needs to be unexpired, reviewed to verify it is fully plant implemented, and advanced to MODIFIED status and beyond per DES-2-22, DES-2-23, and DES-2-25. Please assign resolution to Electrical Design Engineering. <I> **** Actions Taken **** Requested that EC MALT 10986 R003 be administratively unexpired in Portal J. | 02-00-E-RLY-47/27/TRB,02-00-E-RLY-47N/27/TRB
392241 | CR | 20190416 |  | 3 | Individual Attempted To Access an Area W/O Appropriate Acces |  |  |  | N | NO | <D> **** Detailed Description **** Individual attempted to access an area that they did not have access to. No access was gained. <I> **** Actions Taken **** Security Management was notified. Verified no access was gained. Escorted the individual outside the PA IAW SWP -SEC-15.
392243 | CR | 20190416 |  | 3 | Scope of WOs 02078190, 02114480 not planned for R24 |  |  |  | N | NO | <D> **** Detailed Description **** WOs 02078190 (loss of 50-51 rod positions ending in 0) and 02114480 (loss of 14-07 rod positions ending in 2) were scoped in to R24 but have not been planned. Request the scope be planned. Background: Positions 10, 20, 30, 40 of CRD-ROD-5051 were noted to be missing during R22. WO 02078190 was scoped in to R23 but deferred during R23 (AR OSCR 366090) due to not being appropriately planned (loss of position indication suspected to be due to connector but inspection/replacement tasks were at canceled status). The WO was then scoped in to R24 and coded R24DP but its scope does not appear to be included in any other WO. Similarly positions 02, 12, 22, 32, 42 of CRD-ROD-1407 have been missing intermittently since R23 (during 2/16/19 down-power all positions were noted to be working). WO 02114480 was coded R24DP but only the PIP replacement was planned (WO 02114218) without any inspection/corrective work planned. This inspection and corrective work was requested of planning twice. Once in October 2018 and again in January 2019 (ref. emails in EDMS). Impact: The loss of the specific rod positions is not insignificant but due to both rods 14-07 and 50-51 being edge rods, the operational impacts can be minimized. <I> **** Actions Taken **** Discussed issue with reactor maintenance. They are able to perform the desired work scope.
392244 | CR | 20190416 |  | 4 | Confidential Information found on Microfilm |  |  |  | N | NO | <D> **** Detailed Description **** Confidential Information was found on microfilm while researching legacy information for current scope of work. This is a legacy issue for a record filmed in 2007 that was not flagged as confidential at the time. <I> **** Actions Taken **** Informed IS Management. The roll of film was removed from the general area, placed in the vault, and marked as confidential.
392245 | CR | 20190416 |  | 4 | spare CW motor Cat ID 65002945 heater circuit not working. |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During the inspection of Spare CW motor at Warehouse 2/4 (aka bldg 188) we noted that there was no voltage present at the heater junction box on the motor. It appears as the circuit breaker is not tripped and that there is still power at the receptacle where the heater is plugged in. It is suspected that the male plug is faulty. The heater is currently fed from a 120volt / 30 amp single pole breaker. <I> **** Actions Taken **** notified supervisor and generate WR/CR <N> **** Equipment Description **** Spare CW Motor located at Warehouse 2/4, site 4 Cat ID 65002945, UTC 365356
392246 | CR | 20190416 |  | 4 | C-FP-DISC-3C7CL-001 Caution Tag Needs Updating |  |  |  | N | NO | <D> **** Detailed Description **** Upon Clearance Review per PPM 1.3.9, Clearance C-FP-DISC -3C7CL-001 referenced LIft Instruction on Caution Tag WO 02084217 was cancelled. Clearance instructions have not been updated. Per PPM 1.3.9, Section 4.9.3(c) VERIFY Danger Tags and Caution Tags which have been installed GT 1 year have appropriate closure mechanisms identified. Caution Tag is place since 2016. <I> **** Actions Taken **** Notified EFIN Supervisor and OPS Work Control <N> C-FP-DISC-3C7CL-001 was lifted on 4/5/19. No further actions needed. Recommend close to trend.
392247 | CR | 20190416 |  | 4 | Spare Condensate Pump Motor not unpackaged/available for PM |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** WO#02130225-01 has Condensate pump motor Cat ID 8632 UTC 541368 located at warehouse 2/4 (site 4) required to perform semiannual inspection and testing, but the motor has not been completely unpackaged from shipment. maintenance cannot be performed until new/refurbished motors are staged and accessible. <I> **** Actions Taken **** notified supervisor write CR/WR <N> **** Equipment Description **** Spare Condensate pump motor Site 4 warehouse 2/4
392248 | CR | 20190416 | CAQ | C | Room C510 shop presents a fire hazard to SR circuits | Y | N |  | N | NO | <D> **** Detailed Description **** The RW 525â€™ Room C510 I&C instrument shop contents presents a fire hazard to safety-related circuits. This is the only office/shop in the plant that has safety-related circuits/cable trays in the overhead without automatic fire suppression. Its walls were installed under PDC 84-1202 with a statement that if combustibles accumulated, then fire protection features would be pursued. There is a file in EDMS that goes into detail on this topic and suggests corrective actions, so assign to Maintenance I&C. Room R510 is being placed on hourly fire tour. <I> **** Actions Taken **** Discussed with various parties. See file in EDMS. Fire Prevention Evaluation permit 19-0019 was prepared. Research on whether a CR was warranted was started as part of self-assessment AR 384793-10.
392250 | CR | 20190416 |  | 3 | Simulator PIs |  |  |  | N | NO | <D> **** Detailed Description **** Benchmark the industry for Simulator PI data. <I> **** Actions Taken **** None
392251 | CR | 20190416 | CAQ | D | Typographical Error in ODCM LEP |  |  |  | N | NO | <D> **** Detailed Description **** Bases 6.2.2.6-2 of the ODCM is being changes as part of implementation of License Amendment 251. In preparing that change it was discovered that the List of Effective pages (LEP) for the ODCM listed a B 6.2.2.6-3 which does not exist. <I> **** Actions Taken **** Discussed with Licensing Supervisor. Ame 48 of the ODCM was in WordPerfect (WP). Ame 48 contained a 3rd page for B 6.2.2.6. Ames 49 & 50 of the ODCM represent the WP to WORD conversion. In the conversion, B 6.2.2.6 was reduced from 3 pages to 2 due to differences in font and spacing. Although the LEP is not considered a technical portion of a licensing basis document, SWP-LIC-03 was reviewed. There is no prohibition to correcting this error in the LEP outside of the LDCN process. The risk of error in replacing the new pages is greater if the LEP is not corrected. Recommend Delta to Regulatory Affairs
392254 | CR | 20190416 | CAQ | C | Preaction system drain valves not shown on drawing. |  |  |  | N | NO | <D> **** Detailed Description **** While researching the clearance for WR 29146660, it was found that that the loop drain valves for Preaction systems 65 and 66 are not shown on drawing M515-2. FP-V-P65/19 and FP-V-P66/27 are both listed in SOP-FP-LU, albeit with different noun descriptions (loop drain vs supply drain). They have different field configurations, one with a plug and one with a chicago fitting. These are the only two preaction systems with the loop drain valves, since no other preactions systems have piping between the supply valve and the clapper valve. Request the following resolution: 1. Change both descriptions in SOP-FP-LU to read "loop drain". 2. Add the valve to Detail F on M515-2, downstream of the sprinkler isolation valve, but before the lines for valves D and U. The new valve could be labeled on Detail F as valve S, as there is currently not a valve S listed on the Detail F valve list. 3. Update the Detail F valve list to show the new S valve category along with the two valves with their respective system. <I> **** Actions Taken **** Walked down all preaction system isolation and clapper valve configurations.
392256 | CR | 20190416 |  | 4 | MT-HOI-40 Is Non-Functional | N | N |  | N | YES | <D> **** Detailed Description **** During material transfer activities using MT-HOI-40, the hoist became non-functional for lifting purposes --- the hook will respond to LOWER commands. The hook was raised to full up position and the hoist was placed in the safe storage location. There is no load or rigging on the hoist hook. . Loss of MT-HOI-40 will impact pre-outage activities for material transfers into the reactor building. There are currently two material containers in the R441' railroad bay that are awaiting transfer to R501'. Additionally, pre -outage activities starting 29-Apr-19 will require the use of MT-HOI-40. <I> **** Actions Taken **** Submitted CR. Submitted WR. Informed FIN manager. | 02-00-MT-HOI-40
392257 | CR | 20190416 | CAQ | D | SFS-CASK-3 and 25 RTD's reading low | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of ICP-SFS-A301 RTD's on cask 3 and 25 were reading low or burnout causing a warning (Yellow indication) on the master recorder. This does not fail the procedure, but the RTD's need fepaired/replaced <I> **** Actions Taken **** Informed CRS/supervisor and created CR/WR for tracking Recommend additional information be provided to assist with tracking / trending (photo and/or specific EPN). <N> **** Equipment Description **** ISFSI pad 1 & 2
392258 | CR | 20190416 |  | 4 | Undocumented power strip and power cord E-CP-C91/P605 Bay 2 | N | N |  | N | YES | <D> **** Detailed Description **** During a walkdown of E-CP-C91/P605 in support of EC 17398 (ACUMEN), an extra power connection was observed on SS-2A located E-CP-C91/P605 Bay 2 not found on the drawings. Additionally there is an extra surge strip on the bottom shelf of Bay 2 that is not in use. The power cord was traced to a bundle of tie-wrapped other power cords. It was not possible to determine if the extra plug belongs to the surge strip. If it does, then this appears to be a case of daisy chaining. . Recommend that the power cord be traced to determine if its a daisy-chain. Also recommend that the unused power strip get removed. <I> **** Actions Taken **** Notifiied Operations and generated CR. This is non-safety related equipment associated with E-PP -US/A. <N> **** Equipment Description **** E-CP-C91/P605 Bay 2
392260 | CR | 20190416 |  | 4 | Spare Condensate Motor UTC 538493 not accessible for testing |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** semi-annual inspection and testing cannot be performed until shipping/packaging material is removed from Spare Condensate Pump Motor (CAT ID 8632, UTC 538493). This Motor is located at Building 74 and still wrapped in shrink wrap. <I> **** Actions Taken **** Notified Supervisor and generate CR/WR <N> **** Equipment Description **** Spare Condensate Motor CAT ID 8632 UTC 538493
392261 | CR | 20190416 |  | 3 | (Non EN/CGS) CC-186 calibration report incorrect |  |  |  | N | NO | <D> **** Detailed Description **** (Non EN/CGS) CC-186 calibration report incorrect - did not affect as-left data. Corrected copy issued, customer complaint initiated. Customer notified, recommend assign AR-CALSERV CATEGORY 3 <I> **** Actions Taken **** Corrected copy issued, customer complaint initiated. Customer notified, recommend assign AR-CALSERV CATEGORY 3 <N> Correction issued to customer. Supervisor to evaluate.
392262 | CR | 20190416 | CAQ | C | Spare RHR Motor in Bldg 74 not identified in WO 02130225 |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** There is a spare RHR motor staged in Bldg 74 that does not have lubrication in the bearing reservoirs and the space heater is not connected. This motor is not identified in the semi-annual work order to maintain spare motors. this CR is written to drive the addition of this motor to the PM list and to get heaters connected as well as oil into the bearing reservoirs. <I> **** Actions Taken **** notified supervisor generate CR/WR <N> **** Equipment Description **** Spare RHR Cat Id 8639 UTC 552836 SEQ-N8406-071017 Building 74
392263 | CR | 20190416 | CAQ | D | Siren C2 post testing revealed additional problem | N | Y |  | N | YES | <C> Reopend the CR due to accidentally canceling it. <D> **** Detailed Description **** Siren C2 has been experiencing an intermittent communication issue, typically in the morning. A failed antenna connector was replaced and successfully tested under WR 29147667. Additional testing the next morning revealed an additional problem with the siren transceiver board. <I> **** Actions Taken **** Notified EP. The siren board has been replaced and successfully tested. Siren C2 is fully functional. Additional testing will be performed in the morning. Recommend closing to cross-referenced WR. <N> **** Equipment Description **** Siren C2
392264 | CR | 20190416 |  | 4 | Level Indication on CF-TK-4 is not reading right | N | N |  | N | YES | <D> **** Detailed Description **** The level indicator for CF-TK-4 is reading 918 gals when the tank is empty. Visually no level in the tank. This is the hydrobromic acid for the halogenation system. <I> **** Actions Taken **** A load of bromide to refill the tank is scheduled for 5/1/19. The level indication must be working by this date to provide OPS the level they will need so that they can authorize the tank to be filled. <N> **** Equipment Description **** CF-TK-4 - Hydrobromic acid tank CWPH
392265 | CR | 20190416 | CAQ | D | Standby plant public announcement (PA) amp failed | N | Y |  | N | YES | <D> **** Detailed Description **** The standby amplifier for the plant PA zone 7 failed. This is the service water area and outside the protected area. Note: This is a backup amplifier and does not affect normal PA operability. <I> **** Actions Taken **** Dispatched techs to fix the standby amp. <N> **** Equipment Description **** 525 Comm room
392267 | CR | 20190416 |  | 3 | Received H13.P840.A5 drop 8-6 STANDBY AIR COMP ON. | N | N |  | N | YES | <D> **** Detailed Description **** Received H13.P840.A5 drop 8-6 STANDBY AIR COMP ON. CAS-C-1C auto started with CAS-C-1B running. CAS-PI-1 101 psig and up slow, dispatched OPS3 CAS-C-1B CJW outlet temperature was high at 155F (normally around 100F), comparable CAS-C-1C CJW outlet temperature was at 80F. CAS-C-1B unloaded light was also illuminated. Placed CAS-C-1C to RUN and CAS-C-1B to STOP per SOP-CAS -OPS. H13.P840.A5 drop 8-6 STANDBY AIR COMP is clear. Possible air leakage in CAS-C-1B air compressor or CJW blockage | 02-00-CAS-C-1B
392268 | CR | 20190416 |  | 3 | Unknown Waste found in Dumpster next to Bldg. 94 |  |  |  | N | NO | <D> **** Detailed Description **** During a routine walkdown of the Cooling Tower Area, Environmental and Regulatory Programs (E&RP) discovered a plastic chemical sprayer in the dumpster next to Bldg. 94 with an unknown liquid in it. The container was not labeled and had approximately 1 gallon of liquid in it. Disposing liquids in a dumpster is not in compliance with state and federal law and is prohibited by station procedures (e.g. GBP-ENV-17). Unless the owner of the container is found to identify the contents, E&RP will have to send a sample off for analysis which can be expensive. <I> **** Actions Taken **** Discussed with E&RP Manager, tried to determine liquid in container. Removed container and packed in a drum in Bldg. 117. Uploaded pictures in EDMS Docs. <N> Williams Plant Services. Container and liquid has been desginated by E&RP as HW19 -035. The liquid is designated as non-regulated; it has been solidified and disposed of in accordance with state and federal regulations.
392273 | CR | 20190417 | CAQ | C | Foreign Material - rope in spent fuel pool | Y | Y |  | N | NO | <D> **** Detailed Description **** While performing inspection of fuel pool locations in preparation for R-24 the refuel bridge operators identified a small piece of rope on top of a spent fuel bundle approximately Â¼â€x 1â€ long. The rope was located at E-59. <I> **** Actions Taken **** Documented the identification in the work order. A recovery plan will be made with FME coordinator approval prior to R-24. <N> The Rope has been retrieved per the FME procedure PPM 10.1.13 , no further actions are required. Closed with concurance from the Maint. Programs supervisor.
392280 | CR | 20190417 | CAQ | C | OQAPD Section 18.2.4.g references an activity not applicable |  |  |  | N | NO | <D> **** Detailed Description **** OQAPD Section 18.2.4.g references an activity not applicable to Energy Northwest. Energy Northwest is a Part 72 General Licensee and as such is obligated to the General Licensee requirements spelled out in 10 CFR 72. 13(a) & (c). OQAPD Section 18.2.4.g references security plan requirements in 10 CFR 72 Subpart H as an activity for which quality audits are performed. However, 10 CFR 72. 13(b) indicates that this section of Part 72 is only applicable to Specific Licensees (which EN is not). Physical Security Plan activities required for a Part 72 General Licensee are described in 10 CFR 72.212(b)(9). In research of this error, it was determined that this was an oversight when the OQAPD first implemented Part 72 quality requirements in 2000 (per LDCN-OQAPD-00-050) in Rev 34 of OQAPD-01. <I> **** Actions Taken **** Discussed this matter with Quality department management.
392281 | CR | 20190417 |  | 4 | Lighting in the TB 471' Heater Bay | N | N |  | N | NO | <D> **** Detailed Description **** There is poor lighting in the TB 471' heater bay. This is a This is a safety concern. The lighting should be done shortly after shutdown. The dose rates will be significantly lower after shutdown. <I> **** Actions Taken **** (1) Informed supervision. (2) Wrote this CR <N> **** Equipment Description **** Lighting TB 471' Heater Bay.
392282 | CR | 20190417 |  | 4 | Caution Tag C-SS-PC-4F -001 has no closure mechanism |  |  |  | N | NO | <D> **** Detailed Description **** Upon tag review per PPM 1.3.9, Caution Tag C-SS-PC-4F-001 referenced WO 02115914 closure task 03 (To Lift Clearance Order) was taken to FINISHED but Verification Field shows Tag is still hung. There is no clear closure mechanism for this Caution Tag. Per PPM 1.3.9, Section 4.9.3(c) VERIFY Danger Tags and Caution Tags which have been installed GT 1 year have appropriate closure mechanisms identified. This Caution Tag is 645 days old. <I> **** Actions Taken **** Notified EFIN Supervisor and OPS Work Control See Xref WO 02115914-03 Added LC C-SS-PC-4F-001 to WO task 02118822-02; the HC task to repair SS-PC-4F in R24.
392286 | CR | 20190417 |  | 3 | Ballast rock for transformer yard was incorrect | N | N |  | N | NO | <D> **** Detailed Description **** During the backfill process of WO# 02134675-04 it was identified that more ballast rock was needed in order to finish the task. An MR, material request, was initiated but the rock was not here on site yet. A different ballast rock was down at the warehouse that was pulled from after MRâ€™s were given to the warehouse staff. Upon placement of this rock in the transformer yard it was identified that it was the wrong material. <I> **** Actions Taken **** Work was stopped and placed in a safe condition and contact with the transformer yard coordinator was made. A clear path forward was made to continue and a CR was generated. <N> Williams Plant Services.
392287 | CR | 20190417 |  | 4 | Flammables cabinet #02-0027 lock ineffective |  |  |  | N | NO | <D> **** Detailed Description **** Flammable liquid storage cabinet #02-0027 located on RW 487' outside chemistry lab has a damaged latch mechanism. Door will latch closed but locking is ineffective. Refer to PPM 1.3.10C section 3.7.13 for site cabinet requirements. <I> **** Actions Taken **** Discovered during chemical inventory. After locking cabinet, latch was challenged to verify locked and was still able to be opened with lock mechanism engaged. <N> **** Equipment Description **** Rad Waste 487' Chem Lab hallway.
392290 | CR | 20190417 |  | 4 | RW 507 gymnasium abmysmal light conditions | N | N |  | N | NO | <D> **** Detailed Description **** The RW 507 gymnasium is so dimly lit in certain areas, you need a flashlight to read words on paper. Since Jan 1st 2019 there at least 20 CRâ€™s in the database that concern poor lighting throughout the Power Block. Some of these CRâ€™s state that the poor lighting condition is an industrial safety concern or it was identified by the NRC. I donâ€™t know how many CR's regarding the same subject constitutes a trend but on face value, it appears that this is a trend. <I> **** Actions Taken **** Contacted HP Supervision, initiated CR. <N> **** Equipment Description **** RW 507 gymnasium
392291 | CR | 20190417 |  | 3 | B88 L&I Elevator Inspection Power Disconnect Issues | N | N |  | N | YES | <D> Recent L&I inspection of the B88 elevator had issues with the method of connections to the shunt trip circuit breaker. 1. Elevator power is monitored by the fire alarm panel. The monitoring relay is connected to the LOAD side of the power disconnect. The location needs to be changed to be on the LINE side of the disconnect. This way, when testing the disconnect, the fire alarm panel will not receive the supervisory alarm for the loss of power. 2. The two fixed temperature heat detectors connected to the shunt trip circuit breaker for the power disconnect must be tested annually and replaced every 15 years. These detectors are not connected to the fire alarm panel, but serve to provide a means to disconnect power prior to the application of fire sprinkler water. These detectors are spot-type, 115 VAC power. They are nonrestorable heat detectors. Once heated and activated, they cannot be reused. The L&I inspector suggested annual removal of the detector, shorting out the 115 VAC circuit, and proving the shunt trip works. . Recommend that this AR be assigned to AR-TEFP to initiate actions to test the B88 heat detectors, replace the detectors now, set up an annual test for the detectors and also set up a method to accomplish the 15 year replacement of the detectors. <I> 1. Work Request written to change the location of the elevator power monitoring connection. 2. Work Request written to test the two heat detectors in B88. <N> B88 Elevator Power Shunt Trip Heat Detectors (two) CR found at INPROG, moved to OPS for review.
392294 | CR | 20190417 |  | 3 | AED C878D and AED C897 incorrectly depict DG4 |  |  |  | N | YES | <D> **** Detailed Description **** Civil drawings AED ARC C878D and AED ARC C897 both inaccurately depict DG4. The DG4 trailer is depicted in a north-south orientation while it actually exists in the field in an east-west orientation. Additionally, the wrong EPN is depicted for DG4 on both drawings. The correct EPN for DG4 is E-GEN-DG4, not E-DG-4. EPN E-DG-4 exists in Portal J / MEL but is a NONEQUIP duplicate of correct EPN E-GEN-DG4. Please update/correct AED C878D and AED C897. Suggest NONCAQ resolution to Mechanical Design & Drafting. <N> This discrepancy was noted while performing document reviews associated with AR EVAL 332405. | 02-00-E-DG-4,02-00-E-GEN-DG4
392295 | CR | 20190417 |  | 3 | Injury Reported a Year After Occurance |  |  |  | N | NO | <D> **** Detailed Description **** An employee informed occupational health that their doctor had insrtucted them to inform the company of a medical condition that had potentially occured a year ago during fire brigade training. Occupational health notified supervision and industrial safety of the information. <I> **** Actions Taken **** Supervision, occupational health, industrial safety, department manager and shift management informed. The employee was given the paperwork to get permission for work release. IRL #19-004 was generated in response to the situation.
392296 | CR | 20190417 |  | 4 | Radio in the remote shutdown room found inoperable | N | N |  | N | YES | <D> **** Detailed Description **** Radio in the remote shutdown room found inoperable While doing preventive maintenance on the radio desk set in the remote shut down room the radio transmitter was found inoperable. The phones verified operable. <I> **** Actions Taken **** Notified the MCR, EP and SCC. Recommend closing to the cross-referenced WR Non-essential communication equipment. <N> **** Equipment Description **** Remote shutdown room.
392297 | CR | 20190417 |  | 4 | 2019 LNI elevator inspection report - PEC east | N | N |  | N | YES | <D> **** Detailed Description **** Inspection report from Labor and Industries notes required actions. Response due 7/4/2019. A copy of the inspection report is uploaded in EDMS docs. <N> **** Equipment Description **** PEC east elevator, conveyence ID 7836
392299 | CR | 20190417 |  | 4 | Near Miss incident |  |  |  | N | NO | <D> **** Detailed Description **** On the morning of 4/17/19, An employee was walking from her car to the south entry of the MPF building where she works. Part of the asphalt ramp that transitions from the parking lot to the sidewalk had a piece missing. She stepped on the area of the transition that had the missing piece and fell. She reports that she has no injuries what so ever. She correctly reported the incident to her manager and the MPF Property Coordinator has been contacted and shown the part of the transition that has a missing piece. The Property Coordinator and the Facilities Craft/Maintenance Supervisor for the MPF both agree that Energy Northwest (EN) does not own that parking lot as it is owned by the owner of the Main building. Therefore, EN would not own the transition either. The property coordinator has sent notification to the owner of the Main building of the missing piece in the transition. <I> **** Actions Taken **** Employee reported the situation to management, manager notified VP. Industrial safety was notified Builidng property coordinator was notified and also the property owner was notified(EN does not own the south parking lot )
392300 | CR | 20190417 | CAQ | D | E-V-S/3 minor oil leak needs contained | Y | N |  | N | YES | <D> **** Detailed Description **** During a walkdown of the transformer yard a leak was identified on one of the E-TR-S drain cooler drain valves. The purpose of this CR is to get a bucket installed under the valve and to try to tighten the plug on the valve. <I> **** Actions Taken **** Notified SSS to install something under the valve. | 02-00-E-V-S/3
392301 | CR | 20190417 |  | 3 | Evaluate a standalone RHR flushing procedure. |  |  |  | N | NO | <D> **** Detailed Description **** Currently we use SOP-FPC-ASSIST-ALT sect 5.6 and 5.7 to flush sections of RHR and FPC systems. The use of these sections are for placing RHR on FPC assist mode. Making a standalone procedure would eliminate the work around of a procedure intended for something else, which would save dose, extra planning (tag outs) and will prevent errors from occurring.
392302 | CR | 20190417 |  | 4 | Monthly Chemical Storage area inspection discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** The monthly inspection of Mechanical Maintenance chemical storage areas discovered the following discrepancies: Chemicals found outside of flammable liquid storage cabinet in GSB shop. <I> **** Actions Taken **** Notified appropriate personnel to resolve. All discrepancies resolved, no further action required.
392304 | CR | 20190417 |  | 4 | Reactor Building SW elevator is non-functional | N | N |  | N | YES | <D> **** Detailed Description **** Reactor Building SW elevator has been removed from service due to intermittent service issues <I> **** Actions Taken **** removed the elevator from service, contacted mechanical maintenance and the elevator vendor | 02-00-MT-ELEV-2
392305 | CR | 20190417 |  | 3 | Shielding package 97-003 in FPC HX room needs recount |  |  |  | N | NO | <D> **** Detailed Description **** WO 02100590, periodic review of temporary shielding, indicates that the FPC Heat exchangers and pumps have shielding installed. It appears that the shielding on the pumps was removed. Per shielding coordinator, a recount of the currently installed temporary shielding on the heat exchangers should be performed in order to verify that the information for package 97-003 is accurate. <I> **** Actions Taken **** Initiated this CR at the request of the shielding coordinator.
392306 | CR | 20190417 |  | 4 | 2019 LNI Elevator Inspection Report -Bldg 88 Okanogan | N | N |  | N | YES | <D> **** Detailed Description **** Inspection report from Labor and Industries notes required actions. Response due 7/4/2019. A copy of the inspection report is uploaded in EDMS docs. <N> **** Equipment Description **** Bldg 88 Okanogan
392307 | CR | 20190417 |  | 4 | 2019 LNI Elevator Inspection Report - PEC West | N | N |  | N | YES | <D> **** Detailed Description **** Inspection report from Labor and Industries notes required actions. Response due 7/4/2019. A copy of the inspection report is uploaded in EDMS docs. <N> **** Equipment Description **** PEC West Elevator Inspection ID 688418, Conveyance ID 7666
392308 | CR | 20190417 |  | 4 | 2019 LNI elevator inspection report - Reactor Bldg NE | N | N |  | N | YES | <D> **** Detailed Description **** Inspection report from Labor and Industries notes required actions. Response due 7/4/219. A copy of the inspection report is uploaded in EDMS docs. <N> **** Equipment Description **** Reactor Bldg Elevator, Inspection ID 687542, COnveyance ID
392309 | CR | 20190417 |  | 4 | Shield package 95-005 is damaged | N | N |  | N | NO | <D> **** Detailed Description **** Shielding package 95-005, RW 487 Neutron Source Storage is damaged. The Borofloat Glass "window" on top appears to have dropped from its position and needs to be repaired. Picture is attached in EDMS. <I> **** Actions Taken **** Initiated this CR and informed Rad Support supervisor and Shielding Coordinator. Generated Work Request. <N> **** Equipment Description **** Neutron Source Storage on RW 487'
392310 | CR | 20190417 |  | 4 | 2019 LNI Elevator Inspection - Rad Waste Building Elevator | N | N |  | N | YES | <D> **** Detailed Description **** Inspection report from Labor and Industries notes required actions. Response due 7/4/2019. A copy of the report is uploaded in EDMS docs. <N> **** Equipment Description **** RAD Waste Bldg Elevator - Insp. ID 687547, Conv. ID 2949 This conveyance has been inspected and no apparent deficiences were noted. There is no need for further aciton .
392311 | CR | 20190417 |  | 3 | Data Glance: Test equipment loading issue |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of WO: 02110249 Digital Multi Meter (Fluke 187) M&TE number 0063195 (cal Due Date 1-23-20) could not be entered into the Ipad during work out closure. The test equipment was validated by the tool crib to be the correct M&TE number and valid since 2003. It appears the issue is with data glance not recognizing the test equipment. <I> **** Actions Taken **** Supervision notified, and CR generated. <N> **** Equipment Description **** DMM fluke 187 M&TE # 0063195 1-23-20.
392313 | CR | 20190417 |  | 4 | Relamping in RB 522 South pipe space | N | N |  | N | YES | <D> **** Detailed Description **** RB 522 South pipe space in conmpletely dark. Second CR wrote due to no lights in room. We enter the room multiple times a week which make this more of a safety issue . Previous CR Number is 00391324 W/O 29147692. <I> **** Actions Taken **** Needs relamped. This room is a HRA so a Alara brief is required to enter. <N> **** Equipment Description **** Permanente Lighting
392314 | CR | 20190417 |  | 3 | Spill outside Bldg. 17 |  |  |  | N | NO | <D> **** Detailed Description **** A small spill of epoxy occurred outside of Bldg. 17 near a C-Van. Environmental and Regulatory Programs (E&RP) was alerted to the spill, completed a walkdown and discovered the waste from the spill in a dumpster outside Building 17. The process for notifying E&RP when a spill occurs (GBP-ENV-18) and disposal of the waste (GBP-ENV-17) was not followed. Spills are only to be cleaned up by qualified personnel and disposed of properly. It is unclear who cleaned up the spill and if they had the proper qual to do so. At this time, the material is unknown and may require testing for appropriate disposal. <I> **** Actions Taken **** E&RP completed a walkdown and determine the spill is not reportable. Waste was removed from the dumpster and transferred to Bldg. 117 for further analysis. Discuss issue with E&RP Manager and Supervisor, wrote this CR.
392315 | CR | 20190417 |  | 4 | COND-V-31 Spool Piece Location Discrepancy / Wasted Man-hrs |  |  |  |  | YES | <D> **** ANONYMOUS CR - Detailed Description **** Maintenance requested support in the RCA caged area located in Warehouse 5 (Bldg 80) to find and transport the Spool Piece for COND-V-31 to the Plant. After getting the location from the warehouseman, the Spool Piece was not to be found. A phone call to a more knowledgeable maintenance person revealed that the Spool Piece was actually stored on the RW 437'. The work instructions, procedure, and warehouse records have discrepancies which include the following locations: Warehouse 5, RW 467' Tool Crib, and the RW 437'. This resulted in a minimum of 6 hours of wasted man-hours. <I> **** Actions Taken **** Initiated this AR/CR. <N> **** Equipment Description **** COND-V-31 Spool Piece ANON CR generated, moved to OPS for review. | 02-00-COND-V-31
392316 | CR | 20190417 | CAQ | C | 16.11.6 PRM filter elevated activity for 2nd week | Y | Y |  | N | NO | <D> **** Detailed Description **** The 16.11.6 surveillance of reactor effluent air has found an elevated level of Co-60, as well as the short lived isotopes Tc-99 and Na-24 for a second consecutive week (first sample identified in CR 00391996). The increase in Co-60 activity may be attributable to R24 preparation activities, but the presence of the short lived isotopes is indicative of primary coolant leaking into the reactor building, and is believed to have begun between sample collection period of 4/2/19 and 4/9/19. The 16.11.6 air sampling filters are collected weekly and from 4/9/19 to 4/16/19, the observed Tc-99 and Na-24 concentration in air increased by a factor of 5.4x and 2.5x respectively. These activities do not currently challenge the effluent concentration limits for ODCM 6.2.2.1. An occurrence similar to this was last identified in CR 00360057 on 11/7/17. <I> **** Actions Taken **** Wrote this CR. Spoke with systems engineering.
392317 | CR | 20190417 |  | 4 | 2019 LNI Elevator Inspection Report - MPF Elev. #1 |  |  |  | N | YES | <D> **** Detailed Description **** Inspection report from Labor and Industries notes required actions. Response due 7/4/2019. A copy of the inspection report is uploaded to EDMS docs. <N> **** Equipment Description **** MPF Elev. #1, Inspections ID 696726 Conv ID 3727
392320 | CR | 20190417 |  | 3 | Additional Tech Memo Changes Required |  |  |  | N | NO | <D> **** Detailed Description **** The Hardened Containment Vent (HCV) Phase 2 project identified that the EOP/SAG Bases document, Technical Memo (TM)-2120 required revision to support EOP and SAG changes. TM-2120 has been revised in August 2018 to support the needed EOP/SAG changes required to meet the HCV Phase 2 requirements. The SAG is now being updated by Operations per PPM 1.2.7 (EOP/SAG Program Maintenance). However, additional Technical Memos were recently identified for revision that would augment the required changes. This additional TMs provide guidance to the TSC Electrical Engineer (TM-2113), TSC Mechanical Engineer (TM-2115), TSC Operations Manager (TM-2118), and TSC Core Thermal Engineer (TM-2117). As some of these changes are quite extensive, it is recommended that Reactor Fuels create an action plan (timeline) to support the implementation of these additional guidance documents. Recommend severity 3 assignment to AR-RXFUELS. <I> **** Actions Taken **** Discussed with Operations and Licensing personnel to ensure that the augmenting changes were not part of the Operations informed changes already provided in TM-2120â€™s revision. Confirmed that Operations is in the process of updating the SAGs.
392321 | CR | 20190417 |  | 3 | Revision needed |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Revision and CORC review needed for work order 02118305-01; CN-V-707 needs to be open in order to supply air to CN-PCV- 9 so we can adjust CN-PCV-9 to 35 psi per work instructions. CN-V-707 is normally closed unless ops is inerting. See attached picture in work order notes for ops procedure number. <I> **** Actions Taken **** Initiate CR Communicated with PSRO Informed WWM and Supervison.
392322 | CR | 20190417 |  | 4 | Text box obscured part of step 3.2.9, PPI.PPM.13.10.5 Rev 13 |  |  |  | N | NO | <D> **** Detailed Description **** PPI PPM 13.10.5, Rev 013, was issued with part of step 3.2.9 obscured by a text box containing a note on page 5. The page did not display correctly when opened in Word 2010; however, when the revision Procedure Native was opened in Microsoft Word 2016, the page displayed correctly. When the automated process created the Procedure PDF for the revision, the page printed with the text box shifted over part of the text. Note, Caution, and Warning Boxes in procedures can be created using Procedure Macros to avoid this issue. SWP-PRO-03 includes guidance on formatting these boxes. <I> **** Actions Taken **** Notified supervision. Corrected the image in Asset Suite / Share Point based on Procedure Sponsor's review. The procedure will be redistributed and filed in the field on 4/18/19.
392323 | CR | 20190417 |  | 4 | Quorom not met for 04-08-19 WW T+1 Meeting |  |  |  | N | NO | <D> **** Detailed Description **** The quorum was not met for the 04-08-19 Work Week T+1 Meeting held on Wednesday, April 17. All required departments were represented at the meeting. However, WCI-4 requires 3 of 7 Department Managers (no delegates) from either Maintenance, Operations, PGM, System Engineering, PSO, RP, or SCS to be present. The attendees did not meet that requirement. This CR is being generated to document for trending purposes only. No further action is required. <I> **** Actions Taken **** The decision was made to continue the T+1 meeting and generate the CR for documentation purposes.
392324 | CR | 20190417 |  |  | MSIV parts inspection found unacceptable conditions |  |  |  | N | YES | <D> During inspection of parts for MSIV's, a dent and scratch in the plug and defect in the stem were observed. The scratch spanned the seating surface and is a potential leak path <I> Informed supervision. recommend aquiring new parts and returning damaged to flowserve | 02-00-MS-V-28C
392326 | CR | 20190417 | CAQ | D | MSIV parts inspection found unacceptable conditions |  |  |  | N | NO | <D> **** Detailed Description **** During inspection of parts for MSIV's, a dent and scratch in the plug and defect in the stem were observed. The scratch spanned the seating surface and is a potential leak <I> **** Actions Taken **** Informed supervision. recommend aquiring new parts and returning damaged to flowserve <N> Plug and stem are being returned and placed on hold status. recommend trend.
392329 | CR | 20190417 | CAQ | D | FPC-LIT-21B Cable Broke During Surveillance | N | Y |  | N | YES | <D> **** Detailed Description **** During performance of 10.27.116, the transmission cable connection inside of TB-R554 broke while establishing the test setup. Recommend removing broken connector and replacing with new. This does not affect the "hardline" or "repairable head." <I> **** Actions Taken **** Placed work in a safe condition, notified supervisor and CRS. | 02-00-FPC-LIT-21B
392330 | CR | 20190417 |  | 3 | Inefficiencies when people switch complanies |  |  |  | N | NO | <D> **** Detailed Description **** When personnel switch companies but remain employed on site (for example temporary EN to BHI or Planetforward to BHI) they are required to re-inprocess. I understand that there are regulations which require some of the process, but the station should assess whether this in being done in the best, most efficient manner. Under current practices an employee has a badge one day and has to have a new PHQ the next day in order to regain access. The implacts the employee, the employee's department, in-processing and security. Recommend some benchmarking on how other stations comply with this regualtion. <I> **** Actions Taken **** Wrote the CR <N> Individuals granted UA/UAA are logged through the vendor supplied software which is the Security Screening Information System (SSIS). When the badge is produced the company is hard coded in to the badge ID., and pushes to the Personnel Access Data System (PADS) automatically. The proper way to change information in PADS without performing a manual update is to make a permanent change to the badge ID record then the requirement to have the correct company associated with the badge (an NRC requirement) is to issue the individual who changed companies a new badge. The example being provided in this case involves the supervisor who had full knowledge ahead of time that his employee was changing companies and failed to read the procedure or conduct prior planning so that the employee could be re-badged which only takes a few minutes in access authorization if the proper planning and reference to the procedure is followed. It was suggested to the supervisor to make a phone call or expand the team and get help. This is a very simple process which aligns Access Authorization with NRC rules, and was not followed. When the supervisor raised the issue they were instructed to call the manager of Access Authorization but also chose not to call or expand the team. There is no need to benchmark this process because the 18 plants that use SSIS follow this same process to ensure alignment with the rules this benchmarking had already been completed.
392333 | CR | 20190417 |  | 4 | Several BS Non-Return Check Valves indicate dual-position. | N | N |  | N | YES | <D> Performed WO# 02070383 at 100% RX Power, The following valves indicated dual-position and PPM 10.2.200 will need to be performed on them during R24. BS-V-5A, BS-V-7A, BS-V-8A, BS-V-8B, BS-V-8C, BS-V-8D, BS -V-8E, BS-V-8F, BS-V-10A, BS-V-10B, BS-V-10C, BS-V-10D, BS-V-10E, HD-V-33A, HD-V-33B. <I> Informed CRS/SM Wrote WR 02070383. | 02-00-BS-V-10A,02-00-BS-V-10B,02-00-BS-V-10C,02-00-BS-V-10D,02-00-BS-V-10E,02-00-BS-V-5A,02-00-BS-V-7A,02-00-BS-V-8A,02-00-BS-V-8B,02-00-BS-V-8C,02-00-BS-V-8D,02-00-BS-V-8E,02-00-BS-V-8F,02-00-HD-V-33A,02-00-HD-V-33B
392339 | CR | 20190417 | CAQ | C | Staff unable to call in for "Call in Drill" 4/16/2019 | N | Y |  | N | YES | <D> **** Detailed Description **** A "Call in Drill" was initiated at 1900 on 4/16/2019. It was reported that some staff members recieved a busy signal, or a ring and then the call would drop. After multiple attempts, staff were able to call in and report. <I> **** Actions Taken **** Trouble ticket was opened with Motorola. They indicated that after the upgrade of the incoming lines to the Communicator system on 4/11/2019, they have been working with their carriers to resolve issues with the 800 numbers. They recommended we use our backup Communicator system until they have the issues resolved. <N> **** Equipment Description **** Remotely hosted server. | FW-00-SOFT-COTS-COMM NXT
392340 | CR | 20190417 |  | 4 | Near Miss - incorrect procedure opened on iPad |  |  |  | N | NO | <D> **** Detailed Description **** While performing a surveillance, the technician in the main control room inadvertently had the wrong procedure pulled up in EWP. The crew was assigned to perform 2 surveillances, one after the other, and had both surveillances assigned to them in EWP. The discrepancy was identified during communication with the crew in the field. No manipulation of equipment in the field had been performed. <I> **** Actions Taken **** Stopped work, contacted supervisor and CRS and informed shop manager.
392341 | CR | 20190417 |  | 4 | Phone Jack CB1206C not working. | N | N |  | N | YES | <D> **** Detailed Description **** Phone jack CB1206C extension #2687 on T471â€™ near Instrument Rack 82 does not function. This phone jack is needed for communications with the control room during surveillance testing. <I> **** Actions Taken **** Initiated CR and a WR to have the phone jack repaired. This is non-essential communication equipment. <N> **** Equipment Description **** CB1206C T471' B0/5.9
392342 | CR | 20190417 |  | 4 | HP-EQ-42809 unequal sheave sizes |  |  |  | N | YES | <D> **** Detailed Description **** The sheave size on the motor is smaller than the sheave size on the pump. The belt runs near the bottom of the sheave on the pump. With a little belt wear the belt may start running on the bottom of the sheave instead of on the sides. The sheaves should be made equal with a belt size to match. The current belt rides correctly in the motor sheave. It may be easiest to change the sheave on the pump to match the sheave on the motor, no change in belt size would be required. <I> **** Actions Taken **** notified supervisor and wrote cr <N> **** Equipment Description **** HP-EQ-42809 is a mobile unit mounted on a hand truck.
392343 | CR | 20190418 |  | 3 | One of 4 Div 1 integrated tests not deferred from R24 |  |  |  | N | NO | <D> **** Detailed Description **** OSP-ELEC-B701 not deferred for R24 as expected results in missed opportunity for outage excellence. OSP-ELEC-B701 (Manual and Auto Transfer, STARTUP TO BACKUP XFMR) is the last of four integrated testing surveillances normally performed in series that result in significantly cycling plant equipment and power components. TSTF 425 (Tech Spec Task Force) has allowed for extending surveillance intervals that support maintaining station reliability while reducing or enhancing overall station risk. Three of the four integrated surveillances were identified and evaluated for extension. However, OSP-ELEC-B701 was not. This surveillance will de-energize SM-7. This is the only activity in R24 that will result in a loss to SM-7 and its associated buses. <I> **** Actions Taken **** As a result, the expected savings in resources and direct impacts to various groups including OPS, I&C, HP, and Security, in preparation for a bus loss and restoration associated with integrated testing will not be fully realized for R24. The Shutdown Safety Plan will require update to include this test. Defense in Depth (DID) will remain Green overall. OSP-ELEC-B701 is not written as a stand-alone surveillance and will require revision or alternate instructions established. A large number of affected components are normally prepared and positioned by the other three integrated testing surveillances When performed in series, no additional preps are needed as OSP-ELEC-B701 is normally the last to be performed. As the other three have been moved to a four year periodicity, additional preparations are now required and may present a challenge to the operating crews. See EDMS for examples. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
392344 | CR | 20190418 |  | 4 | 3 Pieces of M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** 3 Pieces of M&TE were found OOT. None were used during Calibration cycles. Calcode #0060613 Hytorc Hyd. Torque Wrench- model XLT-5. DEF #7008A written. Calcode #0064637 Hytorc Hyd. Torque Wrench- model 2XLCT. DEF 7009A written. Calcode #0065106 Ind. Scientific Gas Monitor- model iTX. Rejected- Unable to get parts DEF #7010A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only
392345 | CR | 20190418 |  | 3 | eSoms will not print Ops turnover info for SM |  |  |  | N | NO | <D> **** Detailed Description **** When attempting to run an eSoms Turnover report for "Shift Manager shift turnover checklist", the report failed to generate. Instead a "SAP BusinessObjects OpenDocument" login window appears and will not recognize the eSoms password. Login failure message. = Account information not recognized: Enterprise authentication could not log you on. Please make sure your logon information is correct. (FWB 00008).
392355 | CR | 20190418 |  | 3 | Duplicate or incorrect qualification groups assigned |  |  |  | N | NO | <D> **** Detailed Description **** The report for manager/supervisor missed 2019 Q1 training showed several individuals who appeared on the report twice. Investigation showed these 7 individuals are assigned both a manager and a supervisor qualification group, MTAH and MTAI. Further investigation showed there are 21 with the title of manager who have not been assigned the manager qualification group, MTAI, but still assigned the supervisor qualification group, MTAH. TPD-3 gives definitions that describe the supervisor and manager qualification groups. One general manager was still assigned a manager qualification group - per TPD-3, general managers do not need to be assigned a qualification group. As part of the promotion process, qualifications for those being promoted need to be reviewed to ensure their qualifications match their job description and associated training is provided. There are not currently any qualification or training issues associated with the individuals mentioned. <I> **** Actions Taken **** Spoke with Training Support Manager. Attached reports used to gather data to EDMS
392358 | CR | 20190418 |  | 3 | 2019 Q1 Manager/Supervisor missed training |  |  |  | N | NO | <C> Request from initiator to re-open and assign to AR-ORGEFF. <D> **** Detailed Description **** A pilot session and 6 continuing training sessions were given for MT000716, Overtime Management, and MT000717, SOER 10-2 Drain Down event. All managers and supervisors were to have attended MT000716, and Nuclear managers and supervisors were to have attended MT000717. There were 39 who did not attend MT000716 and 38 who did not attend MT000717. <I> **** Actions Taken **** Spoke with Training Support Manager Uploaded missed training reports to EDMS
392359 | CR | 20190418 |  | 4 | E-TR-M2 Cooler Group 2 failure | N | N |  | N | YES | <D> **** Detailed Description **** Cooler Group 2 fans 4 & 5 tripped and was reset succesfully. May be a reoccuring event. <I> **** Actions Taken **** Initiated CR, Informed MCR <N> **** Equipment Description **** Transformer yard | 02-00-E-TR-M2
392361 | CR | 20190418 |  | 3 | Revision to PPM 3.1.6A is needed |  |  |  | N | NO | <D> **** Detailed Description **** PPM 3.1.6A page 63 incorrectly calls out COND-FT-201B. The correct EPN should be COND-DPT-201B. See EDMS for markup. <I> **** Actions Taken **** Notified Maintenance Programs Supervisor. Initiated CR. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
392362 | CR | 20190418 |  | 3 | OG-RF-20C Suction/Discharge pressure D/P low | N | N |  | N | YES | <D> **** Detailed Description **** OG-RF-20C Suction/Discharge pressure D/P is low out of spec, at 25 PSID. Per PPM 3.1.10, the low spec is 30 PSID. This discrepancy has been identified multiple times in the recent months (ref. WR 29144923, 10-4-18 and WR 29146425 ,1-3-19). Both of these WR have been canceled due to the completion of WO# 02103313. Unfortunately, WO 02103313 did nothing more than inspect the OG-RF-20A(B)(C) units, with no actual maintenance/adjustments performed. WO 02103313 did not give specific values for what acceptable D/P for Suction and Discharge pressure should be. The issue still exists and nothing has been done to address it. This is a longstanding, repeat, equipment discrepancy â€“ if the equipment discrepancy cannot be remedied by maintenance, perhaps a re-evaluation of the acceptable D/P band should also be considered. Note: this issue exist for OG-RF-20A and 20B, as well. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RW 452 | 02-00-OG-RF-20C
392363 | CR | 20190418 |  | 3 | Incorrect approvals on rigging certificates |  |  |  | N | NO | <D> **** Detailed Description **** Recent rigging certificates (ME000650) required for site support contractor rigging qualifications (CNAX, CNAY) have been signed and approved by an SSC staff member. This is in contradiction to Qual Directory section 1.2 which stipulates the Site Rigging Coordinator as the approving authority for any rigging qualifications. This certificate is the final barrier to qualification and signifies the Site Rigging Coordinator's approval for the individual to rig on site, not just that the individual has completed all prerequisite training. <I> **** Actions Taken **** Notified Site Rigging Coordinator and Site Support Contractor. Initiated CR.
392364 | CR | 20190418 |  | 4 | good catch documentation |  |  |  | N | NO | <D> **** Detailed Description **** This CR is for documentation purposes. During a field walk down of WO# 02084844-16 while performing a Take 2 of the Work area, Williams Electricians found the nearest phone. The craft recognized that the phone was in an area earlier explained as a high dose area by supervision. The craft electricians routed an auxiliary line and staged a phone in the low dose area. This behavior has the potential to save several MR on a very dose conscious task. This task is worked under RWP 30004381. <I> **** Actions Taken **** Craft supervisor recognized the crew an offered positive recognition for displaying the desired behaviors. An observation was logged into DEVON WAY to share lessons learned, and acting on a request from ALARA, documented in this CR so this information can be added in future tasks with the similar conditions.
392367 | CR | 20190418 |  | 3 | Guest Network outage |  |  |  | N | NO | <D> **** Detailed Description **** Guest network outage due to software issues. Software issue not allow device to respond correctly. <I> **** Actions Taken **** Information services rebooted device and working to bring it back up. No further actions required. Not reportable under 10 CFR 73.54 SWP-CSW-28
392369 | CR | 20190418 | CAQ | D | M&TE OOT | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0065664 Fluke Insulation Tester- model 1507 found OOT & adjusted within specs. Not used in the 20 Ohm range. DEF #7011A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
392371 | CR | 20190418 | CAQ | D | CIA-PS-39B out of tolarance. | Y | N |  | N | YES | <D> **** Detailed Description **** CIA-PS-39B out of tolarance, while performing ISP-CIA-Q902. As found and as left are foumd in table 7.3a of surveillance WO#02134705-01. <I> **** Actions Taken **** adjusted to within tolerance per ISP-CIA-Q902. | 02-00-CIA-PS-39B
392372 | CR | 20190418 |  | 4 | TOA-FN-1A outboard vane linkage disconnected. | N | N |  | N | YES | <D> **** Detailed Description **** While walking down TOA-FN-1A in preparation for placing TOA-DPIC-1A in AUTO for WR 29123490 investigation it was noticed that the outboard vane damper linkage was disconnected with all parts present and no sign of failure. Please remove bolt from damper linkage and reconnect to actuator linkage. See pictures in attributes screen of new work request. <I> **** Actions Taken **** Informed FIN mechanical supervisor. <N> **** Equipment Description **** T 501 F4/5.0 | 02-00-TOA-FN-1A
392374 | CR | 20190418 |  | 3 | 10.27.114 and 10.27.116 require revisions |  |  |  | N | NO | <D> **** Detailed Description **** FPC-LIT-21A and FPC-LIT-21B channel calibrations (PPM 10.27.114 and 10.27.116) require a TDR be performed from the MCR for the entire cable system, then the channel calibration requires the cable is disconnected at the junction box at the RB 606â€™ level and perform a TDR on the level probe (only) and the cable back to the MCR; based on vendor recommendations. Request engineering evaluate the need to disconnect the cable and perform the additional TDR. Past pictures show that breaking the connection at the 606â€™ level is causing galling of the connectors and over time the level probe will need to be replaced. Not performing the additional TDR will save money (in not needing to replace the level probe or repairing a broken connector, see CR 392329) and the dose received working on the RB 606â€™. (This is also the highly contaminated area at this time and routinely performed at the busiest time with work on the RB 606â€™).
392376 | CR | 20190418 | CAQ | C | PPM 1.5.4 not aligned with SWP-CAP-01 |  |  |  | N | NO | <C> CR changed from non-CAQ to CAQ C/CALSERV by MRT. <D> **** Detailed Description **** PPM 1.5.4 Section 4.10, OOT M&TE, Paragraph 4.10.4 directs that an M&TE Deficiency Report shall be initiated in a timely manner typically less than 5 working days for simple evaluations or within 5 working days after an EFIN, Supervisor, or User completed Deficiency Report. Following completion and evaluation of the Deficiency Report and repeat of testing if applicable (4.10.4a - c) Step 4.10.4d. directs to initiate CR per SWP-CAP-01. The timeframe for initiation of the CR can be 5 days or more following finding the M&TE OOT. SWP-CAP-01 Paragraph 4.1.3 directs to initiate AR-CR no later than end of shift and 4.1.4 within 24 hours. Recommed SWP-CAP-01 be aligned with how 1.5.4 is currently written for CR initiation following completion and evaluation of the OOT M&TE Defeciency Report. <I> **** Actions Taken **** Initiated this CR. <N> 22-May-2019 cjc - Extended due date to allow time for all concerned parties to come to a common consensus on how/when CR's should be initiated for EN OOT M&TE.
392384 | CR | 20190418 |  | 4 | Implement temporary power for PRM-SR-2 |  |  |  | N | YES | <D> **** Detailed Description **** A means of providing temporary power to the heat trace and air sampling components of PRM-SR-2 must be determined to allow compensatory sampling at PRM-SR-2 during the DIV-B outage of R24. WR-29148154 was submitted to request this work, but additional determination by engineering is necessary to confirm the exact requirements to implement temporary power to the heat tracing and air sampling pumps for the reactor building effluent air. The distance of PRM-SR-2 from the effluent air collection point (179 ft) is such that it requires heat traced lines in order to maintain representative sampling. These requirements are evaluated in NE-02-16-04 and CVI 1220 -00,2. The heat tracing prevents condensation from building on the interior of the sample line and causing entrapment of particulates, tritium, and iodine before they reach the sample collection point. The new stack monitor sampling line was designed with an active and standby heat tracing to ensure heat trace continuity, but both lines are powered by DIV-B and will not function during the DIV-B outage. If temporary power is not supplied to the heat tracing on PRM-SR-2, the ODCM RFO 6.1.2.1 compensatory sampling measures will be completely unrepresentative of emissions leaving the reactor building stack. The calculations reported in CVI 1220-00,2 estimated a 0.05% radio-iodine transport efficiency through this line to the sample collection point without heat tracing. This is a huge deviation from the FSAR commitment to ANSI/HPS N13.1-1999, which requires a sample transmission design efficiency of greater than 50%. The transport efficiencies of particulates and tritium will be similarly impacted to a lesser extent. <N> What kind of Temporary Configuration Change is being requested? Reference SWP-CM-02. Is an AR type EVAL needed (vs an AR type CR) or does one already exist? Was this a miss for R24 outage planning (i.e., should this be an R24LL)? | 02-00-PRM-SR-2
392386 | CR | 20190418 |  | 4 | EC 16616 missing drawings |  |  |  | N | NO | <D> **** Detailed Description **** A review of EC 16616 Rev 0 in EDMS was found to be missing drawings E528-16 and E528-16A. The signed original drawings were located. This equipment has not been accepted and is not in operation. Recommend action to AR-CMC to add the drawings to the design package. <I> **** Actions Taken **** Discussed with involved parties and located signed original drawings. Notified Engineering and wrote CR. <N> Two missing electrical drawings are uploaded into EDMS.
392387 | CR | 20190419 |  |  | BS and HD valves indicate Dual Position. |  |  |  | N | YES | <D> During the performance of WO 02070383 the listed valves indicate Dual Position. Ref. 10.2.200. <I> Wrote one CR and WR for each. Completed WO 02070383. PortalJ created error and failed to generate WR with this AR submittal. I approved then cancelled this CR and will regenerate another CR. | 02-00-BS-V-10A,02-00-BS-V-10B,02-00-BS-V-10C,02-00-BS-V-10D,02-00-BS-V-10E,02-00-BS-V-5A,02-00-BS-V-7A,02-00-BS-V-8A,02-00-BS-V-8B,02-00-BS-V-8C,02-00-BS-V-8D,02-00-BS-V-8E,02-00-BS-V-8F,02-00-HD-V-33A,02-00-HD-V-33B
392388 | CR | 20190419 |  | 4 | BS and HD valves have Dual Position indication. | N | N |  | N | YES | <D> **** Detailed Description **** During WO 02070383 the listed valves indicate Dual Position. Ref. 10.2.200. <I> **** Actions Taken **** Wrote one CR for all and a WR for each valve. | 02-00-BS-V-10A,02-00-BS-V-10B,02-00-BS-V-10C,02-00-BS-V-10D,02-00-BS-V-10E,02-00-BS-V-5A,02-00-BS-V-7A,02-00-BS-V-8A,02-00-BS-V-8B,02-00-BS-V-8C,02-00-BS-V-8D,02-00-BS-V-8E,02-00-BS-V-8F,02-00-HD-V-33A,02-00-HD-V-33B
392389 | CR | 20190419 |  | 3 | Procedure enhancement TSP-DG2-X501. |  |  |  | N | NO | <D> **** Detailed Description **** The steps in Section 7.0 of TSP-DG2-X501 are not in sequential order after the first three steps. Currently step 7.1.3 is followed by 7.1.1. Change steps in procedure so they are sequential.
392391 | CR | 20190419 | CAQ | C | FO-TK-1 diesel quality is unknown. | Y | N |  | N | YES | <D> **** Detailed Description **** Total DG fuel volume has been below the minimum specification of 160,000 gal since 4/5/19. This cannot be corrected until CSP-DO-C101 is complete to ensure the fuel in FO-TK-1 meets DG quality requirements. The sample for CSP-DO-C101 was performed on 3/27/19 and offsite results have not been received as of 4/19/19. Typically these are received within 14 days of sampling. <I> **** Actions Taken **** I recommend chemistry department follows up with Herguth Labs to determine the results of the sample. <N> **** Equipment Description **** FO-TK-1 diesel | 02-00-FO-TK-1
392392 | CR | 20190419 | CAQ | D | DC Pump Failure | Y | N |  | N | NO | <D> **** Detailed Description **** When starting DG2 in support of OSP-ELEC-M702 the DC PUMP FAILURE annunciator was received (4.DG2 drop 10-2). DP-P- 3B1 and 3B2 were verified running with pressure at 56# (no abnormal conditions). When DG2 was taken to rated speed the annunciator cleared. <I> **** Actions Taken **** Informed CRS, inititated CR for trending
392393 | CR | 20190419 |  | 3 | New RRC Pump1A Sleeve Final PT Exam O/S Tolerance at Vendor |  |  |  | N | NO | <D> **** Detailed Description **** The new RRC Pump 1A Sleeve final PT exam did not pass again and was outside acceptable tolerances. The stellite weld overlay is performed by one sub-vendor and PT'd along the way, this is followed by a finished grinding process. At final PT, a linear indication with dimensions 9/16" x 3/16" was discovered on the overlay. Linear indications > 1/16" are not acceptable. This is a repeatable issue: Reference CR 389745. <I> **** Actions Taken **** Notified Supervision up to VP OPS Notified Component Engineering up to VP Engineering Recieved NCR 200184452 from Vendor Requested Recovery Plan from Vendor Requested Vendor to determine root cause prior to performing any additional stellite weld overlay Recieved % complete of FY19 and FY20 Payment Milestones from Vendor and communicated to Supervision and Asset Management. FY19 funding will not be affected but the full amount of FY20 pull forward to FY19 could be affected.
392394 | CR | 20190419 |  | 3 | Dehalogenation Tank Pad grout cracking & separated from pad | N | N |  | N | NO | <D> **** Detailed Description **** New grout was poured on the Dehalogenation chemical tank pad to provide sloping toward the containment basin. After less than 24 hours, portions of the grout was peeling, cracking and would not adhere to the tank pad. PM and Design engineering were notified. <I> **** Actions Taken **** PM and Engineering walked down the area and documented the condition noting the broken and peeling grout had been removed. Engineering is evaluating options to replace/repair or remove the existing grout from the pad. Recommend assigning to Design Engineering to determine path forward. <N> The mortar has been installed satisfactorily as noted in assignment 01. No further actions are required. The parent AR is now closed.
392395 | CR | 20190419 |  | 3 | SOP-ELEC-DIV2-TEMPPOWER |  |  |  | N | NO | <D> **** Detailed Description **** Due to the new NLI buckets being installed in the Class 1 Safety Related MCCs the temporary power SOPs (SOP-ELEC -DIV1-TEMPPOWER , (SOP-ELEC-DIV2-TEMPPOWER) will need to be revised. The NLI disconnect switches have two sets on contacts, one on either side of the disconnect switch. Because the contact configuration the disconnect is required to be closed to have temporary power installed. This revision must be in place to support the R24 SM8 outage. <I> **** Actions Taken **** Marked up Sop-ELEC-DIV2-TEMPPOWER and sent it Ops procedures writer for revision.
392397 | CR | 20190419 | CAQ | D | Transformer TR-B Trouble alarm on N2 psi high | Y | N |  | N | YES | <D> **** Detailed Description **** Main Control Room received alarm 4.800.C4 drop 2-5 "TRANSFORMER TR-B TROUBLE". The control room entered ABN -TRANSFORMER and dispatched OPS4 to investigate. <I> **** Actions Taken **** OPS4 investigations found the alarm was due to Nitrogen Pressure high at 5 psig as read locally. OPS4 used step 7.3.5 in ABN-TRANSFORMER to clear the alarm. This CR was written for trending purposes | 02-00-E-TR-B
392398 | CR | 20190419 |  | 3 | Corporate eDNA history data unavailable after eDNA upgrade |  |  |  | N | NO | <D> **** Detailed Description **** After completion of the corporate eDNA upgrade, some history data is unavailable. The following services are unavailable. ENW.HISTMANL ENW.HISTORY ENWBU.HISTORY Main service for ERDS is functioning. Real Time and history data are available for CGS and CGSHS. See email in EDMS for Comp Eng insight. <I> **** Actions Taken **** Notified IS Leadership and Computer Engineering. Recommend NCAQ 3 ot ITMGMT.
392399 | CR | 20190419 |  | 4 | Computer point X209 stuck at 85% | N | N |  | N | YES | <D> **** Detailed Description **** Computer point X209, APRM B Flux level, which is fed from MUX 06, is stuck at 85%. APRM B indicates normally on the back panel and operator displays. This appears to be a computer point issue only and does not affect operability of the APRM. <I> **** Actions Taken **** Discussed with SM and Computer Engineering. Request computer engineering investigate and repair. | 02-00-TDAS-MUX-6
392400 | CR | 20190419 |  | 4 | BPA 115kV Transmission Line Structure with FME | N | N |  | N | NO | <D> At approximately 1700 today while driving home I noticed FME in the form of a bird's nest or a tumble weed on BPA's 115kV transmission line structure on the crossarm. The FME is approximately 20 to 30" in diameter. No transmission lines are located directly below FME so the risk to the plant is low. The location of the FME is the third transmission structure east of Route 4 (Hanford 500 road) towards the river on the BPA Benton -White Bluffs line. BPA will be responsible for FME removal. <I> Contacted the Main Control Room, immediate supervisor and System Engineer <N> Approximately 900' East of Route 4 towards the river betwee n access road to Site 1 and Site 2 ENW.
392401 | CR | 20190419 |  | 4 | (NRC) Div 1 and 2 DG day tank room lights out | N | N |  | N | YES | <D> **** Detailed Description **** The NRC resident identified one of the four overhead lights is out in each of the division one and division two DG day tank rooms.. <N> **** Equipment Description **** DG1 Day Tank Room 441' DG2 Day Tank Room 441'
392402 | CR | 20190420 |  | 4 | Received HSSF Nitrgen tank alarm | N | N |  | N | YES | <D> **** Detailed Description **** Found the 487 HSSF HMI pannel with alarm NT PIT300 -PRES STAT HH indicated. This is the NITROGEN TANK PRES TX DATA OVER RANGE as described in CI-14.4. The nitrogen tank pressure is currently indicating 120.4 PSIG. The alarm cleared when acknowledged. HWC is currently in service and normal operation. CI-14.4 directs that this CR be written. <I> **** Actions Taken **** Notified CRS, supervision, and wrote CR. | 02-00-HSSF-CAB-CHEM/LAB
392403 | CR | 20190420 |  | 3 | Improper storage of Universal Waste (50 fluorescent tubes) |  |  |  | N | NO | <D> **** Detailed Description **** Discovered two cardboard boxes that contained a collective total of 50 used fluorescent (4 foot) light tubes improperly stored within the RCA at the HP PAP. They were not labeled as Universal Waste and were not being stored in a proper Universal Waste Sorage or Accumulation Area. This is in violation of GIH-8.1.4. <I> **** Actions Taken **** Surveyed all 50 Fluorescent light tubes and the two cardboard boxes out of the RCA as clean. Notified the electricians to transfer them to their designated used light cage located in the GSB Clean Shop. They responded and transported them within 2 hours. Informed RP Supervision and initiated this AR/CR.
392404 | CR | 20190420 |  | 3 | SOP-H2/CO2-OPS 5.17.1-2-3 procedure enhancement | N | N |  | N | YES | <D> **** Detailed Description **** This is requesting a change to steps 5.7.1-h, 5.7.2-h and 5.7.3-h. Specifically this is requesting the 20 ml volume be changed to 5 ml. This is because while draining H2-LS-6B about 6 ml or so came out. But no gas was seen, so the steps were repeated and about the same volume came out again. It wasn't for another 10-15 cycles of draining (all about the same volume) until gas came out and the amount of oil was not substantial. It appears the effective volume within the pipe that drains per the procedure doesnt get more than 6-8 ml on this switch. So per the procedure additional draining isn't requred; it has an opportunity to continue to back up. End result is this would bring in a level switch alarm over a long period of time. About 90ml of oil was drained from H2-LS-6B. <I> **** Actions Taken **** Informed CRS. <N> **** Equipment Description **** SOP-H2/CO2-OPS
392405 | CR | 20190420 | CAQ | D | sw-v-171A too difficult to operate by hand | Y | N |  | N | YES | <D> **** Detailed Description **** Recover from coldweather ops was being performed when SW -V-171A had to be taken closed. Conclusion was it is too difficult to operate by hand, even with 2 people. It was closed (from full open) no more than a turn. Request maintenance to lube/inspect valve. <I> **** Actions Taken **** Informed SM. <N> **** Equipment Description **** Located on SW-B sprayring entrance. | 02-00-SW-V-171A
392406 | CR | 20190420 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 238 B: 239 C: 238 E-TR-B A: 119 B: 119 C: 118 The following sensors were tripped and are Reset: J7 Sensor - 500KV Neutral Ground Overcurrent BPA reports the following: a. Cause was Grand Coulee/Hanford 500KV line tripped to lockout. b. Relaying involved a multiphase pole that did not reclose. c. No damaged equipment d. Locked out e. No emergent outage needed f. No 230kv or 115kv involved g. No line equipment outage needed h. No affect on the 230kv or 115kv grid i. 1354 j. 500KV k. No RAS initiated l. Grid frequency change temporarily lowered to 59.95 Hz. <I> **** Actions Taken **** Initiated CR. Notified CRS. Contacted Dittmer.
392408 | CR | 20190420 | CAQ | C | Unusual indication exhibited by IRM-DET-2H | Y | Y |  | N | YES | <D> **** Detailed Description **** IRM-DET-2H indication is not a consistant indication. The 6 other functional IRMs flux indication are steady. Please see images attached to EDMS. It has been noted that manipulation of IRM-RMS-9D has caused the indication to settle back out to a stable value. Suspect that IRM-DET-2H may be degraded and need repalcement. <I> **** Actions Taken **** Wrote this CR. Informed supervision. | 02-00-IRM-DET-2H,02-00-IRM-RMS-9D
392409 | CR | 20190420 |  | 4 | SA-MON-1 Calibration drift. | N | N |  | N | YES | <D> **** Detailed Description **** SA-MON-1 has been reading -5 to -3 for the last several shifts. Suspect zero drift since the IMDS says 0, +5 to -0. Please T/S and cal as necessary. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** EW 467 | 02-00-SA-MON-1
392410 | CR | 20190421 |  | 4 | Door C511 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Door C511 needs maintenance. The door is hard to unlock, possibly an issue with the core. <I> **** Actions Taken **** CR/WR generated. <N> This is the normally locked door to the I&C shop on RW 525. This door has no credited barrier functions. | 02-00-W-DOOR-C511
392411 | CR | 20190421 | CAQ | D | sw-v-171a | Y | N |  | N | YES | <C> This CR is a duplicate of CR392405. This will be closed to that CR. <D> **** Detailed Description **** Valve has been very hard to open and close for years. We had to use unorthorised machanical means to close it this year for ops. Valve should be rebuilt or replaced <I> **** Actions Taken **** notified my supervisor. <N> **** Equipment Description **** sw-v-171a and the spray ponds. The word unauthorized, should have been unorthadox, mechanics coordinated with operations to lube and cycle the valve
392412 | CR | 20190421 |  | 3 | Unable to perform WO#02118305-01 as written |  |  |  | N | YES | <D> **** Detailed Description **** Unable to perform WO#02118305-01 due to valve lineup issues and needing to be revised. Work order steps need revision to keep CN-V-707 closed during removal of AS-TC-1. Additionally, we are questioning using SOP-CN-CONT-INERTING just to manipulate CN-V-707. This requires N/A-ing the majority of the procedure (including multiple prerequisites) which can be an error likely situation. <I> **** Actions Taken **** Discussed with OPS and supervisor, wrote this CR. <N> Conflict between work instructions and procedure has been resolved. No furthering actions required. | 02-00-AS-TC-1,02-00-CN-V-707
392413 | CR | 20190421 |  | 4 | Damaged sprinkler box near CN-TK-1 | N | N |  | N | NO | <D> **** Detailed Description **** The control room received a report of a sinkhole forming near the sidewalk between CN-TK-1 and the fuel oil polisher building. Investigation determined that the hole appears to be caused by a cracked lid on an abandoned in place sprinkler control valve box. The crack was allowing the soil and gravel to drop down into the box, causing the appearance of a sinkhole. There are no other apparent soil stability issues beyond this localized spot. This condition does not impact CN-TK-1 or any of the buried fuel oil tanks. This does, however, present a safety risk. A person walking through that area could step on the broken lid and cause it to collapse, potentially resulting in an injury. Recommend removing the box and filling the void with sand/gravel. <I> **** Actions Taken **** An orange cone was placed on the spot to prevent someone from inadvertently stepping onto this spot and injuring themselves. <N> **** Equipment Description **** Gravel covered area between CN-TK-1 and fuel oil polisher building.
392414 | CR | 20190421 |  | 4 | AMS-3 #C00876 for OSC/TSC is due for cal. 4/23/2019 | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The CAM (Constant Air Monitor) that is located at the HP AAP and is used for the TSC/OSC during ERO drills and potential emergencies, is due for calibration on 4/23/2019. CAM's are not normally "free released" due to their internal inaccessible surfaces being potentially contaminated with radioactive material. This particular one is always kept and credited for availability outside the RCA at the HP AAP. It is normally calibrated outside by I&C outside of the RCA. The cal due date has been kept in RP's turnover and is of growing concern. <I> **** Actions Taken **** Initiated this AR/CR. Other notifications to resolve this concern have been previously made. <N> **** Equipment Description **** AMS-3 #C00876 located outside the RCA at the HP AAP
392415 | CR | 20190421 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm Startup and Backup voltages are as follows: E-TR-S A: 238 B: 239 C: 237 E-TR-B A: 119 B: 119 C: 118 The following sensors were tripped and are reset: J15 BPA reports the following: a. Cause was due to issues on the line between Midway and Rocky Ford and could not supply any further information and the present time <I> **** Actions Taken **** Notified CRS
392416 | CR | 20190421 |  | 3 | SOP-RPS-OPS PCN for number correction required |  |  |  | N | NO | <D> **** Detailed Description **** SOP-RPS-OPS numbering is in error. Following step 5.2.22 is a second 5.2.1-5.2.9 instead of 5.2.23-5.2.31. <I> **** Actions Taken **** After hours PCN has been initiated per SWP-PRO-02.
392417 | CR | 20190421 | CAQ | C | OSP-CCH/IST-M702 log readings out of reference again |  |  |  | N | NO | <D> **** Detailed Description **** CCH-CR-1B Operability Data Sheet has mulitiple readings outside the reference values. CR 376212 was written to request Engineering evaluate the reference values to change them if needed. Evaluating the logs for the last 13 times this surveillance has been completed reveals that the three log readings that are out of reference on the recent performance of the surveillance have been very consistently out of reference on all of the last 13 times the surveillance was complete. The log readings are: Refrigerant High/Condenser Pressure per CCH-PI-7B, Condenser Water Outlet Pressure per SW-PI-42B, and Condenser Water Outlet Temperature per SW-TI-69B. Recommend these reading be evaluated to determine whether or not the chiller is performing as expected or the reference values need to be changed. <I> **** Actions Taken **** CRS was informed of the readings per the surveillance.
392418 | CR | 20190421 |  | 4 | Security CCTV 46 |  |  |  | N | YES | <D> **** Detailed Description **** Security CCTV recieved multiple trouble alarms without cause. After a short period of time the alarms returned to normal. <I> **** Actions Taken **** Generated CR for trending purposes. | 02-00-SEC-CCTV-ISFSI/46
392419 | CR | 20190421 |  | 3 | H2 Leakage alarm recieved in Main Control Room. | N | N |  | N | YES | <D> **** Detailed Description **** Main Control room recieved Alarm 4.800.C3.10-6, "H2 LEAKAGE AT IBD/EXCITER". OPS 3 dispatched to invesitgate and found channel 4 reading 95% LEL at TG-H2IS-1. Alarms 1 and 2 were flashing and alarm 3 was in solid locally.After reseting alarm, indication indicated drift and appears to have settled out at about 35% LEL. Alarms 1 and 3 flashing. <I> **** Actions Taken **** Performed steps in ARP 1-4, step 5 not required. MCR performed step 6 and notified Engineer. Performed step 7 and 8 estabishing a temporary log. Checked Exciter and MG area with a H2 meter and found 0% LEL. Verified all Seal Oil parameters normal at SO skid. H2 pressure also normal. <N> **** Equipment Description **** TG 471W | 02-00-TG-H2IS-1
392420 | CR | 20190421 |  | 3 | PPM 11.2.6.4 is in need of a Revision |  |  |  | N | NO | <D> **** Detailed Description **** PPM 11.2.6.4 (Damaged, Lost, or Off-Scale Dosimetry Devices) is in need of a Revision. The First step 3.1.1 under LOST DLR directs you to perform (2) different tasks in one step and causes confusion. Several parts of this procedure are confusing and do not flow well and makes it hard to perform this task without past knowledge of performing tasks associated with Lost or Damaged Dosimetry. <I> **** Actions Taken **** -Notified Supervision -Initiated Condition Report
392421 | CR | 20190421 |  | 4 | PWC-V-512 leaking worse | N | N |  | N | YES | <D> **** Detailed Description **** PWC-V-512 now has no ability to throttle, much less stop any flow whatsoever. during transition to warm weather ops, we initiated flow to SW pond B. when attempting to shut PWC-V-512 there was no reduction in flow throughout the entire range of operation. flow was approx 70 gpm full open, and still 60-70 gpm with PWC-V-512 full "shut" <I> **** Actions Taken **** backed out of procedure and re-isolated PWC makeup informed MCR initiated CR/WR | 02-00-PWC-V-512
392422 | CR | 20190421 |  | 4 | Ice Machine Is Not Working (GSB 441') |  |  |  | N | NO | <D> **** Detailed Description **** Ice Machine in the Lunch Room does not make ice. <I> **** Actions Taken **** Initiated Condition Report & Work Request Notified Supervision <N> **** Equipment Description **** GSB 441' Lunch Room
392423 | CR | 20190421 |  | 3 | Unable to Perform OJT (HP001550) |  |  |  | N | NO | <D> **** Detailed Description **** Qualified OJT/TPE HP Trainer was unable to perform OJT to fellow HP Technicians due to Portal J differences in the Training Region and the Non Training Region. CR#00392420 addresses that the procedure used for this OJT Qual Card needs Revised. An example of an issue is that in the HO11 Panel in TES, there is a drop down (check box) under Personnel HP Status for ALT. Alarm Device Required and in the Training Region, it is titled Case Color. Unsure if the Training Region gets system updates that coincide with the Non Training Region of PortalJ. <I> **** Actions Taken **** Initiated Condition Report Notified Supervision <N> The OJT data/scenario should have been validated by RP or the Trainer prior to providing the training. The â€œTrainingâ€ region of Asset Suite is not meant to be an exact copy of Production. IT can support and coordinate a â€œrefreshâ€ of the training region data when needed, however, they do not keep production and training data in sync due to specific data being set up at times that is needed for training.
392424 | CR | 20190422 |  | 4 | Rolled gasket on north side exciter door | N | N |  | N | YES | <D> **** Detailed Description **** The gasket for one of the two doghouse doors on the main gnerator exciter housing is rolled and needs to be repaired or replaced. With the generator in operation, significant airflow can be felt issuing from the door. <I> **** Actions Taken **** Notified SM. <N> **** Equipment Description **** Main generator exciter doghouse north west door, T501
392425 | CR | 20190422 |  | 4 | PWC-SV-301 has a leak from the top cover of valve. | N | N |  | N | YES | <D> **** Detailed Description **** PWC-SV-301 has a leak from the top cover of valve. There is a solid stream leak from cap into valve pit. This is located in pit south of CW-CT-1A. Recommend fixing concurrently with PWC-V-512. <I> **** Actions Taken **** Wrote this CR and informed MCR | 02-00-PWC-SV-301
392426 | CR | 20190422 | CAQ | D | FP-PI-D58 reading pegged high. | N | N |  | N | YES | <D> **** Detailed Description **** FP-PI-D58 is reading GT 300 psig pegged high. This is the header pressure for E-TR-M2. Pressure should read LE 20 psig above system pressure. ( ~ 150 psig ). Please bleed down pressure/replace gauge as necessary. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 441 NE | 02-00-FP-PI-D58
392428 | CR | 20190422 |  | 3 | Procedure editorial change request |  |  |  | N | NO | <D> **** Detailed Description **** Procedure editorial change request SOP-CFD-BW/PC . Recent changes include steps that are erroneously given drum timer steps. Pics in EDMS <I> **** Actions Taken **** emailed procedure group, they requested an AR for tracking <N> **** Equipment Description **** Procedure change
392431 | CR | 20190422 |  | 4 | WO 02110491-01 Procedure Had to be Added by Crew |  |  |  | N | NO | <D> **** Detailed Description **** WO 02110491-01 for OSP-EDR/IST-Q702 did not have the surveillance procedure populate in the iPad. The Print or P box had to be checked in eWP for the procedure to be available on the iPad. Please update the MWO for this. <I> **** Actions Taken **** Wrote CR for trend.
392432 | CR | 20190422 |  | 3 | R24LL Late identification work creates significant rework |  |  |  | N | NO | <D> **** Detailed Description **** WO 02139017 (REPLACE 230 KV NON-CERAMIC INSULATORS ) and 02139018 (REPLACE 500KV LINE INSULATORS) was added to R24 scope (ref AR/OSCR 00389703) . This will require a complete re-write of the 500KV and 230 KV clearance sequences due to BPA policy for their lineman work not being allowed within a shared tagging boundary. This work is based on a 20 year replacement cycle and could have been identified before P07 initial scope milestone. <I> **** Actions Taken **** Additionally, 6 BPA work activities requiring planning, operations work control and scheduling resources associated with risk evaluation and scheduling have been created since March 2019 and added as DR24 daily scope, challenging R24 readiness. These activities should have been identified earlier in the planning process. For future outage planning and scheduling , need earlier identification of BPA work. scope
392437 | CR | 20190422 |  | 4 | HP-EQ-42809 Pump Needs to be Replaced | N | N |  | N | YES | <D> **** Detailed Description **** Performing WOT 02110200-01, the required flow on the sample cart was not able to be achieved. The max flow obtained was 72slpm, and the required max flow is 120slpm. Based on the last performance of this calibration, it appears the pump capacity has been degrading for the last couple years. <I> **** Actions Taken **** Recommend replacing the sample pump. | 02-00-HP-EQ-42809
392438 | CR | 20190422 | CAQ | D | cctv 46 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** cctv 46 at the ISFSI needs maintenance. Contact security at ext. 2185 for further details <I> **** Actions Taken **** Comp measure initiated, CR/WR generated | 02-00-SEC-CCTV-ISFSI/46
392443 | CR | 20190422 |  | 3 | SOP-H2/CO2-OPS Section 5.10.6 minor error |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.10.6 states â€œIF the Generator casing is to be purged of hydrogen, THEN FOLLOW the instructions outlined in Section 5.115.10.â€ This is a word error with referencing sections. In the last revision a new section was added which did not update this reference correctly. This step should read â€œâ€¦outlined in Section 5.11â€ <I> **** Actions Taken **** Informed Supervision
392444 | CR | 20190422 |  | 3 | 10.2.13 does not list lubricant for new Radwaste Chiller |  |  |  | N | NO | <D> **** Detailed Description **** PPI PPM 10.2.13 needs to be revised to show the lubricants used on the new Radwaste Chiller WCH-CR-51A. Additionally, it should be verified that lubricants will be onsite for upcoming WCH-CR-51A annual maintenance. <I> **** Actions Taken **** Discussed issue with Maintenance. <N> **** Equipment Description **** WCH-CR-51A ***General Notes*** This AR does not need an assignment for the Proceudre revision due to the assignment being created within the Maint. Procedure revision data base. a link to the Maint. Procedure revision data base has been put into the EDMS of this AR.
392447 | CR | 20190422 |  | 3 | Procedure enhancement SOP-FPC-ASSIST-ALT |  |  |  | N | NO | <D> **** Detailed Description **** There are flow restrictions specified in SOP-RHR-SDC to prevent cavitation on RHR-V-48B. When operating in FPC assist mode per SOP-FPC-ASSIST-ALT, the system is operated outside of those specified limits. Engineering reviewed and determined this was acceptable and a part of the design for FPC assist modifications. FPC-RO-5A/5B raise the backpressure on RHR-V-48B which make these limits not applicable in FPC assist mode. Procedures are accurate as written, however, an enhancement in warranted to alleviate future questions. Recommend revising SOP-FPC-ASSIST-ALT to add a P&L: â€œThe cavitation limits on RHR-V-48B specified in SOP-RHR-SDC do not apply in FPC ASSIST mode of operation. This is due to the pressure drop across FPC-RO-5A/5B.â€ <I> **** Actions Taken **** Engineering confirmed this is technically accurate. Initiated CR.
392450 | CR | 20190422 | CAQ | D | (NRC) FPC-LIS-2A reads low | N | Y |  | N | YES | <D> **** Detailed Description **** FPC-LIS-2A reads lower than all other skimmer surge tank level indicating switches. Upon walkdown, FPC-LIS-2A was reading approximately 30%. All other FPC skimmer surge tank level indicating switches were ready approximately 35% Per the IMDS, there is a +/- 1.5% tolerance at all calibration points. This level switch feeds into the control logic that closes COND-V-42 on high skimmer surge tank level. FPC-LIS-2B is wired in series and will still close COND-V-42. Recommend calibrating FPC-LIS-2A. <I> **** Actions Taken **** Wrote this CR. | 02-00-FPC-LIS-2A
392451 | CR | 20190422 |  | 3 | Nine Canyon Wind Project Safety Inspection |  |  |  | N | NO | <D> **** Detailed Description **** Industrial Safety performed an unannounced safety inspection at the Nine Canyon Wind Project on Monday, April 22, 2019. One finding is noted below. Four recommendations were also identified and are noted in the report entered into EDMS. â€œThe inspection sign-off sheet for the bridge crane in the high bay shop has inconsistent entries. There is no entry for the crane pre-use inspection prior to the on/off load of the T-15 gear box in January 2019. Organize the inspection folder and assure pre-use inspections are performed on the crane prior to operation. Ref. ISPM-5, seciton 3.3.2.â€ <I> **** Actions Taken **** Communicated the informaiton to the project lead person and documented the inspection.
392453 | CR | 20190422 |  | 4 | Near Miss at Checkpoint |  |  |  |  | NO | <C> Reviewed ANON CR for SCWE content and forwarded to SRO. Reopened to edit attributes (CRG Review). <D> **** ANONYMOUS CR - Detailed Description **** After clearing the checkpoint in lane #2 vehicle in lane #1 did not yield to lane #2. I had to brake to avoid collision. <I> **** Actions Taken **** Could not coach individual. Vehicle exceeded speed limit towards parking lot.
392456 | CR | 20190422 |  | 3 | ABN-CR-EVAC Minimum Vessel Temperature Curve Update |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing ABN-CR-EVAC for the Fire PRA, I noted that the Minimum Vessel Metal Temperature vs Reactor Vessel Top Head Pressure Non-Critical Cooldown Table Curve contained in the procedure as Attachment 7.23 is from October 12, 1999. This older curve does not appear to reflect a shift to the right for the curve reflected in Tech Spec Figure 3.4.11-2. As such, the 35 degrees F Reference Transition temperature (RTT) shift along the reactor vessel beltline for the 33.1 Effective Full Power Years (EFPY) is not reflected in the older curve. Recommend assignment to Operations Procedures to review the need to update ABN-CR -EVAC with an updated curve reflecting the RTT shift. <I> **** Actions Taken **** Contacted the Operations Procedure Supervisor for a peer check and initiated this AR.
392457 | CR | 20190422 |  | 4 | TDAS X413 Out of Tolerance Low | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02132960-01, step 7.6.2, TDAS X413 data was found out of tolerance low on all but one reading. <I> **** Actions Taken **** Per step 7.6.12b, informed Supervision and Operations. Wrote CR and WR request. Continued with surveillance. <N> **** Equipment Description **** 548Rx
392459 | CR | 20190422 | CAQ | D | CW-PHE-1 incorrect D030 equipment status |  |  |  | N | YES | <D> **** Detailed Description **** This is a documentation issue only. On the D030 panel CW -PHE-1 has a status of REMOVED and DEFUNCT, however, this component is currently installed in the plant and does not meet the definition of REMOVED as described in MUGM-01. Recommend update of the D030 to reflect that CW-PHE-1 is ACTIVE and currently installed in the plant. <I> The equipment status was changed from REMOVED to ACTIVE as directed per this CR and I validated against the drawings to ensure that this equipment was spared in place. . Procurement Engineering has been notified to correct the UTC from indicating that this equipment has been removed. . No further action â€¦ Dave <N> CW-PH-1 was replaced by CW-PHE-1 in 1994 (WO 00DE37). CW -PH-1 does not have an EPN in Portal J and it is possible that CW-PHE-1 was instead erroneously included with those components being removed from the plant in the equipment minor revision under EC 08803831AE. | 02-00-CW-PHE-1
392460 | CR | 20190422 |  | 4 | MT-ELEV-4 Fault | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-4 suffered a "Brake Did Not Lift" fault. Reset using system fault reset P/B. The elevator worked as expected following reset. CR written for trending. <I> **** Actions Taken **** Informed MCR. Reset fault. | 02-00-MT-ELEV-4
392461 | CR | 20190422 |  | 4 | eDNA not available from the EP network | N | Y |  | N | NO | <D> **** Detailed Description **** Workstations in the EP centers are unable to use eDNA after the eDNA upgrade on 4/19/2019. Recommend Non-CAQ - Severity 4 <I> **** Actions Taken **** EP firewall rules for eDNA were updated to include the new eDNA servers' IP addresses. eDNA functionality has been verified in EOF.
392462 | CR | 20190423 |  | 4 | Pipe guard for PWC-V-513 full of water. | N | N |  | N | YES | <D> **** Detailed Description **** The pipe guard that PWC-V-513 is down in is filled with water and is approximately six inches above the handle of the valve operator. Suspect that the pipe line is broken. <I> **** Actions Taken **** Initiated CR <N> **** Equipment Description **** South of fence and SE of Cooling Tower 1A. | 02-00-PWC-V-513
392471 | CR | 20190423 |  | 3 | (NRC) Security does not have keys to FLEX buildings |  |  |  | N | NO | <D> **** Detailed Description **** The NRC resident identified that security does not have key to obtain access to either FLEX storage building (BLDG 82 and 600). Evaluate whether security should have the key to obtain access to these buildings. <I> **** Actions Taken **** Wrote this CR <N> Security Operations had meetings with Operations and Engineering in early 2018 regarding FLEX building access. After benchmarking other sites throughout the industry it was determined that Columbia was in line with other stations regarding FLEX equipment key access. It was also determined that other stations maintain control of the FLEX building keys in other locations than Security very similar to Columbia. Columbia Security has specific roles if there was a need to utilize FLEX equipment. Opening the buildings is not a required step or need in that role. Security Operations plays a valuable role in supporting the use of FLEX equipment based upon the situation or need. Access to the FLEX equipment storage buildings is and will remain controlled by Engineering and Operations for equipment accountable and inventory needs. â€“ M. Sullivan Security Operations Manager.
392474 | CR | 20190423 | CAQ | D | Elevated RX water chlorides | N | Y |  | N | NO | <D> **** Detailed Description **** Reactor water chlorides were sampled at 0805 by the online ion chromatograph that showed Chloride concentration at 1.58 ppb. This exceeds the good practice value of LE1 ppb, but is below the action level 1 limit of GE 3ppb per SWP -CHE-02 Table 6.1.13. COND-DM-1A was backwashed and placed in service at 0015. Only RWCU-DM-1B is in service to clean up the chloride as RWCU-DM-1A remains out of service for maintenance. Increased sampling is in progress to monitor cleanup. <I> **** Actions Taken **** Notified supervision and OPS. Increased sampling frequency, Wrote CR <N> CR reopened to correct Owed to Group.
392481 | CR | 20190423 |  | 4 | As Found Time RPS-RLY-K4/MG2 | N | N |  | N | YES | <D> **** Detailed Description **** As Found Time RPS-RLY-K4/MG2 was out of tolerance As-Found was 2.8 seconds tolerance range is 1.9.to 2.1 seconds. Relays was adjusted per PPM . As-Left is 2.03 seconds. Relay is SAT <I> **** Actions Taken **** Notified supervisor & ops. CR for trending. <N> **** Equipment Description **** RPS-MG2 | 02-00-RPS-RLY-K4/MG2
392483 | CR | 20190423 | CAQ | C | CAS-V-286A/B/C drawn incorrectly on M510-1. |  |  |  | N | NO | <D> **** Detailed Description **** Investigation of CAS-C-1B failure (WR 29148110) has led to discovering that CAS-V-286A(B)(C) is drawn wrong on M510-1 as verified by the technical manual and sytem operation. Per M501, the three way valve port that closes when energized has the dot. On the drawing, the dot needs to be changed on all 3 valves from the port on the left to the port on the bottom. <I> **** Actions Taken **** Discussed and verified with supervisor and system engineer.
392487 | CR | 20190423 |  | 4 | Unusual odor coming out of the backside of SH-5 Cubicle 6 | N | N |  | N | YES | <D> **** Detailed Description **** While putting away my arc flash gear in the cage behind SH-5, I noticed an unusual odor in the area. It smelled like something was warm/overheating. My first impression was maybe a ballast was going bad in one of the lights in the area (there were a couple flickering). I asked my colleague to verify if something smelled hot. She agreed something in the area smelled as if it was hot. We surveyed the area and both agreed the smell seemed to be coming from the vent on the backside of cubicle 6 (Aux Cabinet) of SH-5. Looking through the vent with flashlights, there were no obvious signs of anything being warm. There were some spots on the floor under the connections where it looked like something may have dripped at some point in time. Might be worth checking those connections during the upcoming outage. <I> **** Actions Taken **** Generated CR for trending and evaluation, notified control room, emailed supervisor Fire Brigade leader walked down the area and no abnormal odors were noticed. He also inspected through the vents with a flashlight and saw no noticeable indications of damage or overheating. <N> **** Equipment Description **** Backside of AUX Cubicle 6 | 02-00-E-SH-5
392488 | CR | 20190423 |  | 4 | TDAS Mux P/S's need to be replaced. | N | N |  | N | YES | <D> **** Detailed Description **** While performing voltage checks for maintenance three TDAS Mux 5 v power supplies were found to have low dc voltage outputs with high maAC ripple. They need to be replaced before they fail. <I> **** Actions Taken **** Notified supervision, and Computer engineering and wrote this CR/WR. <N> **** Equipment Description **** MCR | 02-00-TDAS-MUX-10,02-00-TDAS-MUX-11,02-00-TDAS-MUX-4
392489 | CR | 20190423 |  | 4 | PPC Card DP20 locked up | N | N |  | N | YES | <D> **** Detailed Description **** Recieved a text notification that CTP on PPC had failed. Investigated and found DPU Card DP20 in OVFL status. <I> **** Actions Taken **** Wrote CR and WR. <N> TDAS is primary. This condition had no impact on CTP on the TDAS comuter system. No loss of CTP indication. | 02-00-PPC-COMP-8715
392492 | CR | 20190423 |  | 3 | Work order 02110461-01 improvements and lessons learned |  |  |  | N | NO | <D> **** Detailed Description **** See EDMS. Summary: Bottom line is reducing the time (allowing us to use demin water to supplement) will lower dose (3.1mrem collected today). We add it to the CSTâ€™s all the time, as we are currently, making â€˜more contaminated water' should not be a concern in this volume. Water level can be seen in the scuppers outside the hi-rad boundary. The hi-hi switch closes about 1â€™3â€ below floor level. This number appears accurate based off todays performance of this WO. <I> **** Actions Taken **** WO improvement <N> **** Equipment Description **** WO improvement
392493 | CR | 20190423 |  | 4 | PWC-SV-301 gasket leakage | N | N |  | N | YES | <D> **** Detailed Description **** PWC-SV-301 gasket leakage , approx 1/2 gallons per minute. Leakage drains out the bottom of the box/ pit that the piping is located in (South valve pit outside CWPH fence) <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** South valve pit | 02-00-PWC-SV-301
392495 | CR | 20190423 |  | 4 | FLEX-P-2 trailer wiring harness will not release brakes | N | N |  | N | YES | <D> **** Detailed Description **** FLEX-P-2 trailer wiring harness applies the brakes when connected to the dump truck. When this happens you have to remove the wiring harness to be able to move the trailer to the CWPH basin. This needs to be addressed since this is not a normal condition. <I> **** Actions Taken **** Notified my supervisor the main control room and initiated this condition report. FLEX-P-2 has been deleted as flex equipment and as an EPN from the PortalJ system. <N> **** Equipment Description **** Building 600
392496 | CR | 20190423 |  | 4 | PWC-V-512 PMT leaking threads | N | N |  | N | YES | <D> **** Detailed Description **** 02119693-04 PMT PWC-V-512 Threads leaking, drips almost a full stream. video in media of above WO | 02-00-PWC-V-512
392497 | CR | 20190423 | CAQ | C | FLEX fire truck air compressor inoperable | N | Y |  | N | YES | <D> **** Detailed Description **** During recent activities that required the removal of the fire truck out of building 600 it was observed that the air pressure was zero. This required the truck to idle for about 5 minutes inside the building before air pressure was sufficient to move the truck. Upon returning the truck to the required configuration it was noted that the compressor was inoperable and made a humming noise and did not start. <I> **** Actions Taken **** Notified my supervisor the main control room and initiated this CR <N> **** Equipment Description **** Building 600 in the top compartment of the fire truck
392498 | CR | 20190423 |  | 4 | RPS-MG-2 Tripped after attempting to starting | N | N |  | N | YES | <D> **** Detailed Description **** While Performing SOP-RPS-Start Section 5.2 step 5.2.2.c; I depressed and Held the RPS-RMS-MG2/Start pushbotton, I observed the Motor Off light Extingush and the Motor On light illuminate, I also waited for MG-2 to come up sto speed. After which I observed VAC increase to aproximately 119 VAC. I released the Start button. Aproximately 10 seconds after releasing the start button, I observed the Motor On light extinguish and the Motor Off light illuminate and was able to hear the MG-2 start to ramp down. <I> **** Actions Taken **** Stopped the Evolution. Contacted Supervision. CR/WR Generated. | 02-00-RPS-MG-2
392501 | CR | 20190424 |  | 4 | Supplemental worker brought cell into the turbine building |  |  |  | N | NO | <D> **** Detailed Description **** A supplemental worker brought his cell phone into the turbine building. The cell phone was placed in airplane mode and was being used as a camera only to photo document a technical inspection of the LP rotor. <I> **** Actions Taken **** The worker was immediately coached on the the restriction of cell phones in the plant and he immediately removed the phone from the plant. In a follow up discussion, the worker reported that he did not recall reading or hearing about the restriction during in-processing. He has routinely used his cell phone at other nuclear power plants, in airplane mode, as a camera. He now understands the cell phone restriction. This issue was discussed with all of the contractor's personnel during the next day's D15. No further action is required.
392503 | CR | 20190424 |  | 3 | Drawing M517 has incorrect EPN for Demin Valve DW-V-100/74 |  |  |  | N | NO | <D> **** Detailed Description **** Drawing M517 calls out valve DW-V-200/74 at column lines K.1/12.5. That is not a valid EPN in D030 panel of Portal J DW-V-100/74 is a valid EPN in Portal J and is located at K.1/12.5 on Radwaste 437' elevation. Drawing needs to be updated to reflect the correct EPN. <N> **** Equipment Description **** RW-437' K.1/12.5
392506 | CR | 20190424 | CAQ | D | Accumulator trouble alarm on CRD-HCU-2259. | Y | N |  | N | YES | <D> **** Detailed Description **** Accumulator trouble alarm H13-P603.A7 drop 6-7 for CRD -HCU-2259 due to high water level. The water was drained per SOP-CRD-HCU and the alarm is clear. The last work request for this HCU was due to high water level and was written on 12/30/18 (#29146344). | 02-00-CRD-HCU-2259
392507 | CR | 20190424 |  | 3 | Cabinet Lamps behind control room panels |  |  |  | N | YES | <D> **** Detailed Description **** Cabinet Lamps behind control room panels are either burnt out or broke while performing I/C surveilances on nights and weekends. This causes an error likely situation. The replacement lamps are not stored in the control room for easy replacement when needed. Also the supervisors on nights and weekends might not know how to or where to get them. Also Hp involement may be needed if they can't fit into the sam.Recommend creating a PM that checks these panels quarterly or monthly to replace or fix the lighting issues. <I> **** Actions Taken **** Talked with my manager the previous electrical manager and wrote this cr <N> **** Equipment Description **** control room panel lamps
392508 | CR | 20190424 |  | 4 | Personal Vehicle Damaged in Parking Lot |  |  |  | Y | NO | <D> **** Detailed Description **** A contract employee's personal vehicle was damaged in the Deshutes south parking lot on 4/23/19. The issue was reported to the supervisor on 4/23/19. The CR was not issued that day due to being offsite for mgr/super meeting. This CR issued as required by ISPM-1. This was a personal vehicle and it is not known what vehicle caused the damage. Security and Site Safety has been notified. Form 23174 completed and distributed as required. <I> **** Actions Taken **** See Description.
392509 | CR | 20190424 |  | 3 | Procedure enhancement for a MSIV failure |  |  |  | N | NO | <D> **** Detailed Description **** At reduced power levels, a single MSIV closure would result in a pressure rise and the need to lower power to LT 75% per SOP-MSIV-OPS. Direction to perform the power reduction and to reference ABN-CORE for the OPRM enable region entry, PCIV tech spec, etc. should be added to a new section in ABN-PRESSURE. Assign to AR-OPSCE. <I> **** Actions Taken **** Discuss with Ops Mgmt and crew E.
392510 | CR | 20190424 |  | 4 | PWC-V-426 in Building 40 is leaking | N | N |  | N | YES | <D> **** Detailed Description **** PWC-V-426 in building 40 is leaking <I> **** Actions Taken **** Notified the CRS and wrote a CR. | 02-00-PWC-V-426
392512 | CR | 20190424 |  | 3 | (QA) RPM approval not obtained for RWP |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Radiation Work Permit (RWP) 30004451 â€œR24 DW NDE N2 NOZZLES INCLUDING ALL SUPPORT WORK *LHR*â€ was not approved by the Radiation Protection Manager as required by PPM 11.2.8.2, Radiation Work Permit Preparation and Use. PPM 11.2.8.2 requires RPM approval for RWPs when the collective total effective dose equivalent (TEDE) for the job or individual task is estimated to be equal to or greater than 5 person-rem. The estimated TEDE for RWP 30004451 at the time of approval was 5.139 person-rem. RWP 30004451 was approved by a Craft-HP Supervisor, but not routed to the RPM for review and approval. Insight: ALARA Review Checklist (Asset Suite panel TIMH220) item 25 â€œJOB/TASK TEDE > OR = 5 PERSON REM?â€ was incorrectly answered â€˜noâ€™, leading to incorrectly marking item 24 â€œIS RPM APPROVAL REQUIREDâ€ as â€˜noâ€™. <I> **** Actions Taken **** The RPM approved RWP 30004451 on 4/17/19 after Quality identified this issue. This is a Deficiency identified in Quality Surveillance SR-19-12. Recommend assignment to AR-RADPL. <N> **** Equipment Description **** N/A
392513 | CR | 20190424 |  | 3 | (QA) RWP current and approved dose estimates different |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The Total Effective Dose Equivalent (TEDE) listed in the â€˜Current Estimateâ€™ and â€˜Approved Estimateâ€™ fields in the RWP Additional Details (Asset Suite panel TIMH211) are different for three RWPs. This difference was noted in the following RWPs: â€¢ 30004338, R24 DW MINOR MAINTENANCE/ SETUP/ SURVEILLANCES *LHR** â€¢ 30004363, R24 DW SNUBBER INSPECTION/TEST DW *LHR** â€¢ 30004451, R24 DW NDE N2 NOZZLES INCLUDING ALL SUPPORT WORK *LHR* The â€˜Current Estimateâ€™ is the sum of the estimated doses for each task on the RWP. PPM 11.2.8.2, step 4.1.15 requires â€œENTER the total RWP dose of all of the RWP assigned ALARA tasks in the H211 Panel â€“ Approved Estimate fieldâ€. . Insight: The Current and Approved estimates should match to ensure RPM approval for RWPs with approved estimates >5 person-rem. <I> **** Actions Taken **** Discussed this issue with the Radiological Support Supervisor. This is a Deficiency identified in Quality Surveillance SR-19-12. Recommend assignment to AR-RPOPS. <N> **** Equipment Description **** N/A . CR canceled and reopened at the authors request to add description.
392514 | CR | 20190424 |  | 3 | (QA) Outage Radiological HRP missing required information |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The HRP for RWP 30004258, R24 WW/RX DIVE INSPECTION (DIVERS) ***LHRA/HIGH RISK***, does not satisfy the requirement of PPM 11.2.2.12, Radiological Risk Assessment and Management, Attachment 9.2, Condition 1 for underwater work and surveys. Condition 1 requires â€œReference PPM 11.2.13.1, Section, Survey of Items Underwater, to ensure HP Technicians perform underwater survey for removal of items from the Spent Fuel Pool, Reactor Cavity, Equipment Pool, or Wetwell.â€ PPM 11.2.13.1 is not referenced in the HRP and no instructions are provided for surveying items removed from the wetwell. Insight: Previous HRPs are typically used to background new HRPs, leading to the potential to miss requirements added since the previous plan was created. <I> **** Actions Taken **** Discussed this issue with the Radiological Support Supervisor . This is a Deficiency identified in Quality Surveillance SR-19-12. Recommend assignment to AR-RADPL. <N> **** Equipment Description **** N/A
392520 | CR | 20190424 |  | 4 | Unable to locate shield package 96-071 |  |  |  | N | NO | <D> **** Detailed Description **** While performing shielding evaluation (Work order 02100590) on TG 501 turbine deck, package 96-071 (AR System Rad Monitor) could not be found. The work order instructions say that 222 pounds of lead putty was installed on the rad monitor in 1996. It is possible that it was removed during R23 and not replaced. <I> **** Actions Taken **** At the request of the Shielding Coordinator, initated this CR. More investigation can be performed during R24 when dose rates are lower. <N> Shield package 96-071 was located. No further action required.
392521 | CR | 20190424 | CAQ | D | Fume Hood Air Flow Low | N | Y |  | N | YES | <C> CR reopened to cross reference additional WP 02150929, marked completion required box, then taken back to complete <D> **** Detailed Description **** HEPA filter requires replacement due to high D/P. HEPA filter D/P for fan TEA-FN-52 at SR-3 is HOOS. <I> **** Actions Taken **** CR and WR written. Supervision and MCR/SM/CRS informed. | 02-00-TEA-FN-52
392522 | CR | 20190424 |  | 4 | 2019 L&I Elevator Inspection MPF elevator #2 conveyance 3733 |  |  |  | N | YES | <D> **** Detailed Description **** Inspection report from Labor and Industries notes required actions. Response due 7/18/2019. A copy of the inspection report is uploaded in EDMS docs. <I> MPF elevator #2 is not located at CGS. <N> **** Equipment Description **** MPF elevator #2 conveyance ID 3733
392523 | CR | 20190424 |  | 4 | 2019 L&I Elevator Inspection Turbine Bldg conveyance 2950 | N | N |  | N | YES | <D> **** Detailed Description **** Inspection report from Labor and Industries notes required actions. Response due 7/18/2019. A copy of the inspection report is uploaded in EDMS docs. <I> No immediate safety issues regarding continuing to use the elevator. <N> **** Equipment Description **** Turbine Bldg elevator conveyance ID 2950
392524 | CR | 20190424 |  | 4 | 2019 L&I Elevator Inspection Reactor Bldg SW conveyance 2948 |  |  |  | N | YES | <D> **** Detailed Description **** Inspection report from Labor and Industries notes required actions. Response due 7/18/2019. A copy of the inspection report is uploaded in EDMS docs. <I> No immediate safety issues regarding continuing to use the elevator. <N> **** Equipment Description **** Reactor Bldg SW elevator conveyance ID 2948
392526 | CR | 20190424 |  | 3 | (QA) Hazard communication signs not properly displayed |  |  |  | Y | NO | <D> **** Detailed Description **** A Confined Space warning sign on one circulating water valve vault cover is held in-place by a rock that partially obscures the wording (the sign is not otherwise adhered or secured). On a different vault, there are 2 signs stacked together held upside down by a rock (confined space and asbestos warning). Another valve vault cover does not have any hazard sign. . See EDMS for photographs. <I> **** Actions Taken **** Notified Industrial Safety. This deficiency was observed during Quality Continuous Monitoring activities. <N> **** Equipment Description **** N/A
392528 | CR | 20190424 |  | 3 | (QA) Partially obscured rad material signs on sea-van |  |  |  | Y | NO | <D> **** Detailed Description **** Partially obscured radiation tri-foils and the words radioactive material were visible on a sea-van located adjacent to Building 94 (storage building in the cooling tower area). It appears that these symbols were painted over and/or covered with a different label at one time. No other radioactive material labels or markings were observed on the sea-van. . See photographs in EDMS. <I> **** Actions Taken **** Notified Radiological Operations. This deficiency was identified during Quality Continuous Monitoring activities. <N> **** Equipment Description **** N/A
392529 | CR | 20190424 |  | 3 | (QA) Chemical hazard labels not visible |  |  |  | Y | NO | <D> **** Detailed Description **** The chemical hazard labels on two of four temporary acid storage containers located near SAT-TK-2 were not visible without close inspection. These containers are located within inches of the sulfuric acid tank berm and are turned such that the chemical hazard labels face the berm. . See photographs in EDMS. <I> **** Actions Taken **** Notified the Chemical Control program owner. This deficiency was identified during Quality Continuous Monitoring activities. <N> **** Equipment Description **** N/A
392533 | CR | 20190424 |  | 3 | R24 Lessons Learned- MSRV Refurbishment Timeliness |  |  |  | N | NO | <D> **** Detailed Description **** The MSRVs that are being installed in R24 did not start refurbishment until April 2019. The teardown and discovery of problems had to be evaluated in a rush to allow time for refurbishment, reassembly and testing. This work needs to be performed well in advance of the outage so that the valves are ready and can be returned to site with adequate time. If all goes well, the valves will be ready to ship to the site about two weeks before the outage. If additional problems are encountered during rebuilding and testing, the valves may not be here before the start of the outage. Recommend assignment to Maintenance for incorporation into R25 contracts and planning for MSRV refurbishment.
392535 | CR | 20190424 |  | 4 | GMA-AC-2, small refrigerant leak on circuit 2A | N | N |  | N | YES | <D> **** Detailed Description **** while performing WO 02110948 to inspect the GMA-AC-2 air conditioning unit it was noted a small leak on GMA-C-2A mixing valve connection. <I> **** Actions Taken **** finished PM to clean and inspect the rest of the unit, Notified supervision. Iniatiated AR and WR to perform repairs. Pictures taken and uploaded into WO 02110948 | 02-00-GMA-AC-2
392536 | CR | 20190424 |  | 3 | R24LL Missed communication opportunities to clear Turb Bldg |  |  |  | N | NO | <D> **** Detailed Description **** This CR does not affect any plant system or component. A High Risk Work Plan (HRWP) requirement to ensure ALL unnecessary personnel were clear of the turbine building during a lift of C-Vans was missed. A walk down of the Turbine Building was performed to clear the area prior to the heavy lift. The individual performing the area walk down was not familiar with all potential work areas of the turbine building and, as a result, did not contact one person in the Relief Valve Maintenance area. Additionally, other means of communication also failed to ensure all persons in the area were cleared prior to the lift. Including: 1). The High Risk evolution was discussed in the 0615 Morning Meeting 2). Operations made a Plant PA announcement prior to the lift. Recommend TREND. <I> **** Actions Taken **** Future HRWP walkdowns will be performed by individuals familiar with the work areas of the turbine building and familiar with the activity being performed. Also, operations will be requested to make an announcement 15 to 30 minutes prior to the actual lift of the need to leave the building.
392537 | CR | 20190424 | CAQ | C | Reuse MSRV springs that are below minimum recommended height |  |  |  | N | YES | <D> **** Detailed Description **** During MSRV rebuilding at an off-site facility, the free height of the springs for the five valves were found to be below the minimum recommend by the manufacturer (see AR CR 392094). Two of these springs have been replaced and evaluated per EC-EVAL 17706. The remaining three springs could not be replaced since suitable replacement springs were not available. The springs with free heights below the recommended value are being reused in the following valves. These valves will be used in the following locations during R24: MS-RV-3A, S/N N63790-03-0137, WO 02116256 MS-RV-2A, S/N N63790-03-0138, WO 02116157 MS-RV-1S, S/N N63790-03-0134, WO 02082938 The valves were tested for setpoint operability prior to removal from the plant (see WO 02076248 and WO 02006407) and were found to be within the acceptable setpoint tolerance and the valves were functioning normally. The valves will be refurbished and retested prior to installation in the plant. There is no indication that the spring height being below the recommended value has any impact on valve operation based on as-found and post maintenance testing. The valves will be retested no later than 2 outages (approx. 4 years) after installation to confirm the setpoint is correct as required by ASME code. Failure of the setpoint will require refurbishment. The valves are refurbished every 8 years per the PM program regardless of setpoint performance. The non-conformance will be re-evaluated when the valves are removed for their next planned PM refurbishment. | 02-00-MS-RV-1D,02-00-MS-RV-2A,02-00-MS-RV-3A
392538 | CR | 20190424 | CAQ | D | Received ROD ACCUMULATOR TROUBLE, for CRD-HCU-4259. | Y | N |  | N | YES | <C> CR reopened to add completion required check mark to referenced WO/WR per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** Received ROD ACCUMULATOR TROUBLE alarm H13-P603.A7 drop 6-7 for CRD-HCU-4259. The alarm was due to high water level, the HCU was drained per SOP-CRD-HCU and the alarm is clear. This HCU has alarmed due to high water level 4 times previous to this instance since 12/4/18. Ref. WR 29145884, 29147055, 29147500 & 29147876. Piston resealing was attempted on 2/14/19 per WR 29147055. <I> **** Actions Taken **** Notified the CRS. Submitted CR and WR. | 02-00-CRD-HCU-4259
392539 | CR | 20190424 |  | 3 | 115KV Set 2 open phase alarm came in followed by Set 1 | N | N |  | N | YES | <D> **** Detailed Description **** 115KV Set 2 open phase alarm came in at 13:40. 115KV Set 1 open phase alarm came in at 14:00. At the time TR-B was unloaded. After each alarm the voltage was verified on all three phases of the backup transformer and all indications appeared normal. All control room indications for TR-B were verified in accordance with the annunciator response procedure. Alarms were verified on the RW 525 comm room on D003 for OPDS-RMS-3/3L had an alarm reading â€œopen phase alarmâ€. D004 for OPDS-RMS-3/3N also read â€œopen phase alarmâ€. Read locally inside of OPDS-BLDG-B the alarm for both set 1 and set 2 indicated â€œopen phase C alarmâ€. The alarms were acknowledged locally but did not reset. Contacted system engineer to assist with trouble shooting alarms. <I> **** Actions Taken **** Wrote CR Informed CRS Informed system engineer | 02-00-E-TR-B
392540 | CR | 20190424 | CAQ | C | RBM B output 6 did not bring in computer point. | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of ISP-RBM-S402 (WO 02135288-01) at step 7.4.6j for output 6, the ROD BLOCK computer pt. A543 did not come in as expected. The activity control panel 2 NN indication did come in as expected. <I> **** Actions Taken **** Stopped, informed supervision and CRS. Initiated this CR to document. This is a known condition ref. CR 348526. After concurrance it was decided to move on and write this CR.
392541 | CR | 20190424 |  | 3 | (R24 LL) Some DAILY WO's Should be in Outage |  |  |  | N | NO | <D> **** Detailed Description **** Following the release of Rev 0 for the R24 schedule it was noted that several DAILY work orders should have been included in the R24 schedule. These WOâ€™s were to be completed post R24 during the startup and were done at 20% and 50% power levels (i.e. OCC still manned and R24 schedule still in effect). These work orders are done routinely when coming out of an outage and should have been included in R24 scope. The WOâ€™s when they auto generate are automatically coded to DAILY and must be manually recoded to the outage. These were missed. Some had a UCR H code which means they were post outage work. However, the outage code was DAILY and never transferred into the outage network to schedule. Recommend Severity 3 to AR-OTMG. <I> **** Actions Taken **** The station should identify a process or method of identifying and coding work like this that is routinely done after outage but before transitioning to the DAILY schedule to prevent a repeat of this oversight. Examples of this type of work are walkdowns done by FIN to check for steam leaks, NDE checks at 20% on the TR-S, and Calibrate Line Protective relays (BPARLYSET1 and BPARLYSET2). See cross reference for WO numbers with specifics. <N> The action items assigned in the CR have been completed and address the issue for this CR. This CR is now complete.
392543 | CR | 20190424 | CAQ | D | HPCS B3-2 Battery Float Voltage Out of Tolerance | Y | N |  | N | YES | <C> CR reopened to add completion required check mark to referenced WO/WR per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** While performing 10.25.5H Monthly Battery Test, the HPCS B3 -2 battery float voltage was found outside of the acceptance criteria. The Float Voltage Criteria is 13.4 -14.0 VDC. The battery was found at 12.83 VDC with 0.03 amps float current. Last month the battery was at 13.70 VDC with 0.17 amps float current. <I> **** Actions Taken **** Validated the readings with a second DMM. Notified supervisor and consulted engineering. Wrote CR to document the condition. Informed the CRS/SM. <N> **** Equipment Description **** DG3 | 02-00-HPCS-B3-2
392544 | CR | 20190424 |  | 3 | (QA) Incomplete Task Preview for QL 1 Coatings Activities |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The Task Preview for Work Order Task (WOT) 02120897-06 failed to identify issues that were left unresolved and caused the Quality Control (QC) Inspection of the preparation and Quality Level (QL) 1 coatings application to be rescheduled to the following day. The issues were identified prior to the start of QC inspections by Quality Assurance (QA) and would have failed inspection criteria had work continued to the QC Hold Points. (See EDMS for details) <I> **** Actions Taken **** Notified Maintenance Craft Supervisor and Quality Management, generated AR-CR. Issues identified were associated with shop work materials and have no effect on SSCs, were not yet part of a formal QC inspection, and no defects were identified with Quality Level 1 coatings materials. This is a deficiency identified during pre -audit activities for Special Processes Audit AU-SP-19
392545 | CR | 20190424 | CAQ | D | DG-BO-DG4/A&B Batteries showing signs of corrosion | N | Y |  | N | YES | <D> **** Detailed Description **** While performing 10.25.5H Monthly Battery Test, Corrosion was noticed on the positive post of the DG4A battery, and on the hold down brackets of DG4B battery. <I> **** Actions Taken **** Took pictures. Notified supervisor and consulted engineering. Wrote CR. Informed CRS/SM. Attached pictures to CR <N> **** Equipment Description **** dg4 | 02-00-DG-B0-DG4/A,02-00-DG-B0-DG4/B
392546 | CR | 20190424 |  | 3 | R24LL: No compensatory actions at PRM-SR-2 for DIV-2 outages | Y | Y |  | N | YES | <D> **** Detailed Description **** During a DIV-B power outage, ODCM RFO 6.1.2.1 compensatory actions cannot be performed per PPM 12.5.35A at PRM-SR-2. Both the active and backup heat tracing for the sample line to PRM-SR-2 are powered through DIV-B, and without heat tracing the air sampling at this location is no longer valid; see NE-02-16-04 and CVI 1220-00,2. . Procedure PPM 12.5.35A has provisions to take compensatory samples at PRM-CAB-2 on RB 606 using the old stack monitoring equipment, however, the equipment used to perform this sampling is slated for removal in EC 0000016611 â€œremove existing stack monitor,â€ and the equipment is in a degraded state for performing 12.5.35A. Flow transmitter PRM-FIT-1 on RB 606 has been retired. This flow transmitter was previous used during the performance of 12.5.35A at PRM-CAB-2, so additional compensatory actions have to be implemented to use this location. . A means for maintaining a functional sampling line to PRM -SR-2 during DIV-B power outages must be implemented to perform the ODCM required particulate, iodine, and tritium sampling of the reactor building effluent during future DIV-B outages. <I> **** Actions Taken **** Making preparations to sample at PRM-CAB-2 on RB 606 during upcoming R24 DIV-B outage. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817. | 02-00-PRM-CAB-2,02-00-PRM-SR-2
392547 | CR | 20190424 |  | 4 | Move RB 606 Johnson Informer to Save Dose |  |  |  | N | NO | <D> **** Detailed Description **** CR 382226 was written to recommend moving the RB 606 Johnson Informer, which Ops 2 takes temperature readings on, to a location that can be read from the 606 Kelly Building. It was noted that this change will save dose, time, and cost as no anti-c's will have to be worn during outages to read the RB 606 temperature. No change occured from the CR because it was not known who controlled the location of the Johnson Informer. Ops Dose Champion has now reached out to engineering and licensing but no requirement is known for requiring the specific location for the Johnson Informer. Please relocate the Johnson Informer from the NW side of the RB 606 to a position visible from the Kelly Building using this CR/WR. <I> **** Actions Taken **** Discussed with Ops Dose Champion and wrote CR/WR to move the Johnson Informer. Is an AR type EVAL needed to make this configuration change? <N> **** Equipment Description **** RB 606 NW side by old stack monitor.
392548 | CR | 20190424 | CAQ | D | E-B0-2B specific gravities low after discharge test | N | Y |  | N | YES | <C> CR reopened to cross reference additional WR 29148272, then taken back to complete <D> **** Detailed Description **** Performing steps 7.1.31, 7.1.32, and 7.1.33 of ESP-B02B -B101 to measure battery cell specific gravities. Not every cell has a GE Specific gravity 1.195 and the average is LT 1.205. <I> **** Actions Taken **** Notified CRS/Shift Manager, Craft Spervisor notified. Work Request generated to place E-B0-2B on equalize | 02-00-E-B0-2B
392549 | CR | 20190424 | CAQ | D | ISFSI PAD MPC #27 HAS HOLE IN LOWER AIR INTAKE SCREEN. | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** ISFSI PAD MPC #27 HAS HOLE IN LOWER AIR INTAKE SCREEN. The screen is at position 270 deg. The hole is approximately 1 inch x 1 inch in area. <I> **** Actions Taken **** Wrote this CR. Notified shift manager. <N> **** Equipment Description **** ISFSI Pad.
392550 | CR | 20190424 | CAQ | D | White powder, which may be corrosion, found on MPC 32 screen | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** White powder, which may be corrosion, found on MPC 32 screen. This can be seen at azimuth 0 deg and 270 deg. <I> **** Actions Taken **** CR written, shift manager notified. <N> **** Equipment Description **** MPC # 32, ISFSI Pad.
392551 | CR | 20190424 | CAQ | D | Siren C19 degraded but functional | N | Y |  | N | YES | <D> **** Detailed Description **** Number 2 amp failed in siren C19. The siren is comprised of 10 amps and the other 9 amps are working as designed. <I> **** Actions Taken **** Notified EP and replaced the failed amp. The siren is now fully functional. Close NCAQ4. <N> **** Equipment Description **** Site C19 Franklin County
392552 | CR | 20190424 |  | 4 | Core Business Meeting DRB Quorum not met |  |  |  | N | NO | <D> **** Detailed Description **** The Design Review Board for EC 17398 Acumen Project did not meet the required quorum necessary to support the review and approval of the design change. Operations and System Engineering Managers were not in attendance and a delegate was not sent to support the meeting. The meeting has been rescheduled to 4/30/19, but is at risk of not meeting design and project milestone dates if the meeting is missed again. The delays may result in work currently scheduled in the Fall to be rescheduled in order to meet work management milestones. Recommend closure to trend. <I> **** Actions Taken **** Recorded any comments those in attendance had and rescheduled meeting to next available time. Initiated CR.
392553 | CR | 20190424 |  | 3 | Flaw in internal Peoplesoft view |  |  |  | N | NO | <D> **** Detailed Description **** The Oracle view PS-ENW-HR-PERS-VW is queried by external systems to identify active employees. A certain data anomaly involving a recent hire has exposed a bug in this view that prevented this person from being correctly identified. <I> **** Actions Taken **** HR was contacted and the data was modified to allow the view to correctly present the persons profile. A separate action will be required to correct the view.
392554 | CR | 20190424 | CAQ | D | ISFSI CCTV 46 | N | N |  | N | YES | <D> **** Detailed Description **** Not operating as intended <I> Contact security for more details. Not reportable. Compensatory measures are in place. | 02-00-SEC-CCTV-ISFSI/46
392555 | CR | 20190424 |  | 4 | WOA-FL-1A ROLL FILTER FELL OFF ROLL | N | N |  | N | YES | <D> **** Detailed Description **** WOA ROLL FILTER FELL OF ROLL AND NEEDS TO BE ROLLED BACK UP AND PLACED BACK INTO PROPER LOCATION. <I> **** Actions Taken **** WROTE CR, CONTACTED MECH TO FIX | 02-00-WOA-FL-1
392558 | CR | 20190425 |  | 3 | Computer Point X224-09 Frequent Alarm - Filling Alarm Typer | N | N |  | N | YES | <D> **** Detailed Description **** Computer Point X224, from RPS-RLY-K12B, is coming in and clearing frequently. This is filling up the alarm typer and is a nuisance to the MCR. Please investigate and repair. <I> **** Actions Taken **** Verified RPS-RLY-K12B is normal (not chattering), wrote CR to address. . There are several X224 points: X224 TDAS DIGITAL WORD 224 X224-08 TURB TCV FAST CLOSURE CHANNEL B1, GDS INPUT X224-09 NMS TRIP RPS B1, GDS INPUT X224-10 CONDENSOR LOW VACUUM TRIP CHANNEL B2 X224-11 CRD SCRAM DISCH VOL HIGH LEVEL B2, GDS INPUT X224-12 RPS B1 TRIP, GDS INPUT Point X224-09 is causing the frequent alarms on the typer. | 02-00-TDAS-COMP-8715
392562 | CR | 20190425 |  | 3 | 2019 M&TT Comp: Improper use of OJT Waiver Process |  |  |  | N | NO | <D> **** Detailed Description **** In 2018, an I&C post-training evaluation identified an improper use of the OJT waiver process. This issue was addressed through the Maintenance Training Advisory Group and SELF AR actions. While the actions appear to have corrected the issue, feedback from the 2019 Maintenance and Technical Training Comprehensive Self-Assessment was that this issue should have been entered into the CAP. Training agrees with the feedback. <I> **** Actions Taken **** Notified Training leadership. Recommend Severity 3 to AR -TRNMT.
392563 | CR | 20190425 |  | 3 | SLI 2-30/PQD Alignment and Assignments |  |  |  | N | NO | <D> **** Detailed Description **** 1) Lack of clarity in SLI-2-30 with regard to responsibilities in maintaining the PQD. 2) Lack of clarity in SLI-2-30 with regard to managing the Qualification assignments.3) Inconsistent assignment of Qualifications in PQD. Recommend assign AR/CALSERV <I> **** Actions Taken **** CR Issued
392564 | CR | 20190425 |  | 3 | Metal piece found inside RCC-F-1 Station | N | N |  | N | YES | <D> **** Detailed Description **** During the change out of the RCC-F-1 filters on 4/25/19 a piece of metal was found on one of the filters. Pictures will be attached in EDMS. <I> **** Actions Taken **** Notified CRS, chemistry supervision, chemistry specialist and system engineer. | 02-00-RCC-F-1
392565 | CR | 20190425 |  | 3 | SOP-FPC-DEMIN and SOP-FPC-SPC need enhancement |  |  |  | N | NO | <D> **** Detailed Description **** SOP-FPC-DEMIN and SOP-FPC-SPC need enhancement <I> **** Actions Taken **** Informed CRS/ SM, sent proposed changes via e-mail to OPS procedures group
392566 | CR | 20190425 | CAQ | D | LPCS Rm Cooler Flow Low/Temp High, H13-P812.R1,7-1, alarm. | Y | N |  | N | YES | <D> **** Detailed Description **** Received LPCS Room Cooler Flow Low/Temperature High, H13 -P812.R1,7-1, alarm. OPS 2 reports the LPCS Pump Room Local Temperature is 81Â°F and SW-FI-25 denotes 60 gpm. OPS 2 adjusted RRA-CC-5 flowrate per OSP-SW-C101. SW-FI-25 currently denotes 68 gpm. The alarm is clear. <I> **** Actions Taken **** Notified the CRS. Reference Tech Spec 3.5.1. | 02-00-SW-FI-25
392567 | CR | 20190425 |  | 4 | HD-LIC-5A21 found with low level and zero demand | N | N |  | N | YES | <D> **** Detailed Description **** During system monitoring and trending, preseparator drain tank HD-TK-5A normal level controller HD-LIC-5A21 was fouind with low leve and zero demand to the level control valve. At ~97.2% power the controller was found fluctuating around-5.3" to-5.4", well below the controller setpoint. With zero demand indicated, the associated level control valve (HD-LCV-5A21) should be going full closed to raise level, so this is indicative of valve issue. HD-LIC-5A22 was noted to be off-scale low with zero demand. AR CR 00389180 identified a similar issue with HD-LIC-5B21 on 1/23/2019 and investigation per WR 29147221 found a leaking positioner bellows seal. <I> **** Actions Taken **** Notified Operations. <N> **** Equipment Description **** Main Control Room | 02-00-HD-LIC-5A21
392569 | CR | 20190425 |  | 3 | PPM 12.14.12 missing step |  |  |  | N | NO | <D> **** Detailed Description **** PPM 12.14.12 step 6.3.6 F-7 was inadvertantly deleted in the last revision. It needs to be put back in to correctly perform the RCC filter replacement the step shoud read CLOSE RCC-V-656 AND replace pipe cap. <I> **** Actions Taken **** Informed Chemistry supervision and procedure sponsor
392574 | CR | 20190425 | CAQ | C | Incorrect Portal J MEL location for SW-FE-36B & SW-FI-36B | Y |  |  | N | YES | <D> **** Detailed Description **** Portal J MEL currently indicates that EPNs SW-FE-36B and SW-FI-36B are on W525' elevation at/near column line H5/10.3. If correct, this would be in the W525' A HVAC room (room C507). The actual location for SW-FE-36B and SW-FI-36B is on W525' elevation in the B HVAC room (room C508) at/near L6/11.1. Please update Portal J MEL accordingly to indicate the correct/actual room and column line location for these EPNs. <I> This same issue also exists for EPNs SW-V-784A and SW-V-784B (root valves for SW-FI-36B & SW-FS-36B). Please also correct Portal J MEL for EPNs SW-V-784A and SW-V-784B. | 02-00-SW-FE-36B,02-00-SW-FI-36B
392575 | CR | 20190425 | CAQ | D | (NRC) E-IR-21 Missing a Latch | Y | N |  | N | YES | <D> **** Detailed Description **** During a walkdown of the SW A pumphouse it was reported that the hinged electrical box cover for PRA-RMS-FN/1A on E -IR-21 is missing a screwed latch. The upper right latch is missing. The remaining 4 latches are installed and at least hand-tight. <I> **** Actions Taken **** Investigated and verified remaining latches were at least hand-tight. Checked remaining boxes on IR's located in both SW pumphouses. | 02-00-E-IR-21
392577 | CR | 20190425 |  | 4 | COND-PI-3CG does not indicate seal water pressure | N | N |  | N | YES | <D> **** Detailed Description **** During a walkdown of the Condensate system, it was discovered that Condensate pump seal water pressure for COND-P-1C as indicated on gauge COND-PI-3CG read 0 psig. CR 00367091 was iniated on 06/07/2017 but no work request was initated. <I> **** Actions Taken **** Documented indication of 0 psig for gauge COND-PI-3CG on walkdown form for monitoring and trending purposes and initated CR. <N> **** Equipment Description **** T -441- - -F1/14.4- | 02-00-COND-PI-3CG
392578 | CR | 20190425 |  | 4 | Telex base station antenna broken | N | N |  | N | YES | <D> **** Detailed Description **** One of the Telex antennas on top of the 606 Kelly building is broken and needs to be replaced. Note: A temporary antenna is mounted in the window that can be used until the building antenna is fixed. <I> **** Actions Taken **** Notified Reactor maintenance. Recommend closing this CR to the cross-referenced WR to replace the antenna. NCAQ-4. <N> **** Equipment Description **** Kelly building 606
392579 | CR | 20190425 |  | 3 | RWCR Lighting has 4 Bulbs Flickering | N | N |  | N | NO | <A> Work request was created to change the light bulbs - CR can close <D> **** Detailed Description **** RWCR has 4 bulbs flickering and is missing 9 Bulbs. Please fix. <I> **** Actions Taken **** Wrote CR <N> **** Equipment Description **** W467-RWCR
392581 | CR | 20190425 |  | 4 | PWC-P-8 has lost suction again. | N | N |  | N | YES | <D> **** Detailed Description **** PWC-P-8 (Chlorine injection pump) appears to have lost suction again. Attempting to prime was not successful. The pump has crystallized hypochlorite around the suction and discharge fittings, which may indicate bad seals. Please repair or replace this pump. <I> **** Actions Taken **** Notified chemistry, wrote CR. <N> **** Equipment Description **** Flocculator building | 02-00-PWC-P-8
392582 | CR | 20190425 | CAQ | C | SW-FE-23C and SW-FE-36B has legacy drawing errors | N | N |  | N | YES | <D> **** Detailed Description **** SW-FE-23C and SW-FE-36B has legacy piping isometric drawing errors and needs to be corrected. . This condition is an administrative drawing issue only â€“ there is no impact upon continued operation, functionality, or qualification of the physical plant. . For SW-FE-23C isometric drawing (CVI ISO 317-00,36,2) indicates that the (Item 33) 1/2â€ diameter stainless steel nipples are threaded on one end (T.O.E) to each of the orifice flanges, however in the field the 1/2â€œstainless steel nipples are not threaded on either end â€“ they are actually socket welded on both ends which is acceptable (proper) per AED SPC 1. In addition, the isometric drawing shows a seal weld type at each orifice flange for (Item 33), which is incorrect (is actually socket welded as indicated before) and will need to be updated. . For SW-FE-36B isometric drawing (CVI ISO 215-00,14377,1) indicates that the (Item 26) orifice flanges are raised face (RF), however in the field the orifice flanges are actually flat faced (FF) which is acceptable (proper) per AED SPC 1. Also SW-FE-36B isometric drawing page 2 (CVI ISO 215-00,14377,2), indicates that the (Item 46) 1/2" diameter stainless steel nipples are T.O.E at each of the orifice flanges, however in the field the 1/2" stainless steel nipples are not threaded on either end - they are actually socket welded on both ends which is acceptable (proper) per AED SPC 1. Additionally, the isometric drawing shows a seal weld type at each flange (Item 26), which is incorrect (is actually socket welded as indicated before) and will need to be updated. . In each case of the nipples being threaded on one end, AED SPC 1 and their applicable subsystem designation specifies that joints 2â€ and smaller are to be socket welded which is reflected in the field. Per AED SPC 1, flanges for 2â€ & smaller flow orifices are to be ANSI 300# FF (flat faced) which is reflected in the field. <I> **** Actions Taken **** Performed plant walkdown for verification with design drafting and my supervisor and called the Shift Manager. Pictures uploade to EDMS. <N> The changes required per AR assignment 01 have been made and incorporated per EC 17505. The drawings have been updated. No further actions are required. The parent AR is now closed. . | 02-00-SW-FE-23C,02-00-SW-FE-36B
392583 | CR | 20190425 |  | 4 | R-Door-R209 requires maintenance | Y | N |  | N | YES | <C> CR reopened to edit severity. <D> **** Detailed Description **** R-Door-R209 Dog latch is not functioning as designed. The latch freely spins causing the door not to secure properly which in return due to it being an air lock door is not allowing R-Door-R210 to open. <I> **** Actions Taken **** CR/Wr Generated Request maintenance to investigate This issues does not impact the barrier capability for the door. This is a security related issue only. The secondary containment interlock and the barrier function of the door remains operable / functional. | 02-00-R-DOOR-R209
392584 | CR | 20190425 |  | 4 | Improper Disposal of Universal Waste | N | N |  | N | NO | <D> **** Detailed Description **** During a facility walkdown, a light fixture containing a fluorescent lamp was discovered inside a dumpster near building 75. Per GBP-ENV-17, fluorescent lamps must be managed as universal waste and canâ€™t be disposed of in a dumpster. <I> **** Actions Taken **** Removed lamp from the dumpster and transported to the Universal Waste Storage Area. Notified E&RP Manager and wrote CR.
392585 | CR | 20190425 | CAQ | C | Environmental Protection Plan Non-Conformance Identified |  |  |  | N | NO | <D> **** Detailed Description **** Environmental & Regulatory Programs (E&RP) found that a notification of proposed changes to the Columbia Generating Station National Pollutant Discharge Elimination System (NPDES) Permit (No.WA002515-1) was not submitted to the Nuclear Regulatory Commission (NRC) as required. The requirement is from the Columbia Generating Station Environmental Protection Plan (EPP), Section 3.2 Reporting Related to the NPDES Permit and State Certification. <I> **** Actions Taken **** Discussed with E&RP Manager and Licensing Manager.
392586 | CR | 20190425 |  | 4 | Broken fill head light on SERDS Delaying resin transfer |  |  |  | N | NO | <D> **** Detailed Description **** On Thursday April 24, 2019 in preparation for a bead resin transfer, it was noted that the lfill head light on SERDS was not working. Upon investigation it was found that the bulb had burned out. Operations was notified that the transfer could not be conducted without being able to see inside the disposal container to track resin slurry level, thereby assuring the container would not be over filled, resulting in a resin spill. Operations promptly stopped the planned transfer. <I> **** Actions Taken **** The vendor was contacted and two bulbs were ordered and delivered on 4/25/19. Unfortunately, the wrong bulbs were received. The correct bulb was found and is being expressed here, to be delivered on 4/26/19. The vendor's Director of Engineering was contacted and he committed to investigate why the incorrect item was sent and why a different bulb than what is used in the Energy Northwest SERDS was sent. <N> The correct fill head light has been received from the vendor and replaced. No further action required.
392587 | CR | 20190425 | CAQ | C | (NRC) FLEX Equipment | N | Y |  | N | NO | <D> **** Detailed Description **** NRC resident identified that FLEX-VEH-5 (Fork Lift) was missing from Bldg 600 during an inspection. The same inspection also identified that although equipment was obviously identifiable, a clear EPN label could not be found for the following: B5B-P-1, FLEX-VEH-3, FLEX-CAB -2/TK-F1, FLEX-CAB-2/TK-F2. <I> **** Actions Taken **** Notified CRS and documented findings in this CR. The vehicle was documented as checked out on 4/9/19 (on bldg 600 checkout board) and was verified still parked in that location. The guidance on PPM 1.5.18 is not clear on how to properly track removal of non-LCS FLEX equipment. CR 392596 was generated to document the procedure gap. All FLEX keys associated with this equipment and the buildings were verified properly checked in. There is no DNC. <N> Reassgined from Ops to AR-PPROG - per J Twomey and J Jones
392588 | CR | 20190425 |  | 3 | Negative trend at Columbia re: Managing Universal Waste | N | N |  | N | NO | <D> **** Detailed Description **** Multiple issues were discovered during a walkdown of the Universal Waste Storage inside the GSB: 1. There are boxes of waste lamps that either donâ€™t have the appropriate labels or the labels donâ€™t have the appropriate markings on them. One box contained sodium-vapor lamps which is mislabeled â€œUniversal Waste â€“ Mercuryâ€. Sodium-vapor lamps exhibit the Department of Transportation (DOT) hazard of â€œDangerous When Wet;â€ the storage and shipping containers of these lamps need to be segregated from other lamps, moved to Bldg. 118, and labeled Dangerous When Wet in accordance with GBP-ENV-17. 2. Some of the containers are quickly approaching the one year regulatory deadline for shipment and should be transported to the warehouse immediately for shipment. 3. Good/unused lamps should be removed from the universal waste storage area. It is not the best practice to store product with waste. 4. The universal waste storage area is cluttered and doesnâ€™t meet good housekeeping practices â€”Lamps are sticking into the walkway and could cause an injury. This area routinely doesnâ€™t adhere to station procedures and is not compliant with state regulations. Recommendations: See cross reference CRs related to this issue. It is recommend that the area supervisor walks this area down, corrects the multiple deficiencies, and provides additional training/coaching to generators of universal waste. <I> **** Actions Taken **** Notified E&RP supervision; initiated CR. <N> **** Equipment Description **** GSB Universal Waste Storage Area
392589 | CR | 20190425 |  | 4 | Dessicant dryer on E-TR-M2 is flashing yellow | N | N |  | N | YES | <D> **** Detailed Description **** The dessicant dryer on E-TR-M2 is flashing yellow, indicating an issue. Please investigate and repair. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** Transformer yard | 02-00-E-TR-M2
392590 | CR | 20190425 |  | 4 | Turbine project injury to low back while handling L-0 blades | N | N |  | N | NO | <D> **** Detailed Description **** Yesterday, while handling LP rotor blades, a craftsman felt soreness in his low back. He asked his foreman for a change in assignment and continued working. Upon arriving at work this morning, he informed his foreman that his back was still hurting. They notified their supervision of the condition this morning. <I> **** Actions Taken **** Siemens initiated a incident report and contacted their occupational health provider. The worker was given direction for self care and returned to work. Follow up with the employee is scheduled. The Siemens project manager notified the EN turbine project manager immediately. The EN project manager made notifications to EN Industrial Safety, Occupational Health, the RxMM Manager and the Operations Shift Manager IAW ISPM-1. Coaching was provided to the worker and his foreman regarding the late reporting of the incident. The EN project manager reinforced the Station's expectations at the end of day project status meeting.
392591 | CR | 20190425 |  | 4 | (NRC) Sulfur Smell in Cable Spreading Room from FP Drain | N | N |  | N | YES | <D> **** Detailed Description **** A formerly clear tygon hose is routed from FP-V-P65/19 to a floor drain in the cable spreading room. There is a sulfur odor emanating from the open end of this hose. The hose is black with sediment/corrosion products, with a white layer on top. There is no water leaking into the cable spreading room. There is a hose tag on the hose. <I> **** Actions Taken **** Verified conditions, inspeected area. | 02-00-FP-V-P65/19
392592 | CR | 20190425 |  | 2 | Tagging Error while installing temp power for E-TR-TC/1 |  |  |  | N | NO | <D> **** Detailed Description **** Crew was installing temporary power to E-TR-TC/1 (Tool Crib) WO 02112636. In asset suite M105 panel a clearance order requirement is listed. Working this task along with SOP-ELEC-BOP-TEMPPOWER procedure clearance O-E-TR -TC/1TPWR-002 was in place but never signed onto by the crew members performing the work. <I> **** Actions Taken **** Stoppped work. Notified CRS,SM and work week manager. Will conduct an IRB per SWP-IRP-03. <N> WIlliams Plant Services Event investigation is complete. No corrective actions in addition to the immediate corrective actions implemented are required.
392593 | CR | 20190425 |  | 4 | RFW pump bias adjusted IAW action level in ODMI | N | N |  | N | YES | <D> **** Detailed Description **** The ODMI titled â€œRFT B Vibes Trouble â€“ RFW-VBI-XE/P1B (Pump Axial Displacement), ALERT at 15 milsâ€ contains action statements for indication that reaches 16 mils and 17 mils in the normal direction. At 16mils RFW pump bias was increased from 110 rpm to 160 rpm on 23Apr2019. [This was performed per PPI PPM 4.840.A1, Drop 7-5, Step 4. This was the first action taken and more is afforded by this ARP.) Additionally, a Management Call was conducted to satisfy the first part of the 17 mils action. The second action required at 17 mils is to â€œReview status of WR 29145527 to prepare for implementationâ€. This WR was performed in Nov2018; however, there was difficulty removing the thrust probe cover and probes were not inspected. The WR generated from this CR will be to make another attempt to get the cover removed and gather vital information needed to understand the health of the probes and the true pump axial position. This CR is for trending purpose to document where we are in the ODMI action levels and to provide a WR for accessing the probes. <I> **** Actions Taken **** discussed with systems and components supervisors | 02-00-RFW-P-1B,02-00-RFW-VBI-XE/P1B
392594 | CR | 20190425 |  | 4 | Unauthorized entry through airlock door inside the RCA |  |  |  | N | NO | <D> **** Detailed Description **** A work group was processing through an airlock door inside the RCA. The first person presented the badge and proceeded into the airlock the second person also presented their badge to the card reader but failed to acknowledge a green light for entry. The unauthorized person had the area checked on their access card but was not activated in the system. <I> **** Actions Taken **** Security came and escorted the individual out of the area. Provided coaching to the individual. <N> Williams Plant Services
392595 | CR | 20190426 | CAQ | D | Chemistry Index (C.I.) exceeds 1.0 | N | Y |  | N | NO | <D> **** Detailed Description **** COND-DM-1A was taken off-line for Backwash & PreCoat on 4 -26-19 @ 2030. COND-DM-1A is in the 2 hour hold pump phase when on-line SP-1(Rx Water) sample was taken. Chlorides were 1.59 ppb which makes C.I.= 1.24. <I> **** Actions Taken **** Verified results with SP-1 grab sample Chlorides=1.63 ppb. Will perform 4 hour grab samples until SP-1 Chlorides are below 1.0 ppb. Which in turn will make C.I.=1.0. This CR is for trending purposes.
392596 | CR | 20190426 |  | 3 | PPM 1.5.18 lacks detail on tracking FLEX / B5b equipment |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.5.18, Managing B.5.b and FLEX equipment unavailability, is lacking detail on equipment tracking section 5.1. OSP-FLEX-A106 note before section 9.4.1 states "Flex equipment removed from its normal storage location in accordance with PPM 1.5.18...is still considered to be properly stored...". PPM 1.5.18 has no guidance on how to address this.
392597 | CR | 20190426 | CAQ | D | Buzzing noise from DLO-42-8AA5A | Y | N |  | N | YES | <D> **** Detailed Description **** DLO-P-11B1 was momentarily turned off and then back on, per step 7.3 of OSP-ELEC-W102. Upon restarting DLO-P-11B1 a very prominent buzzing could be heard from the NLI disconnect bucket (DLO-42-8AA5A) on E-MC-8AA. The buzzing was intermittent. DLO-P-11B1 did successfully start and ran normally, but the buzzing was definitely unusual. Recall that there have been issues with several of the NLI bucket starter coils. This may be an indication of pending failure. See also CR 381705 WR 29143358 for similar issues. <I> **** Actions Taken **** Wrote CR and informed CRS <N> MCC bucket replaced with new NLI bucket 07/2015 (02035907) Part 21 coil replaced 04/2018 (02116389) | 02-00-DLO-42-8AA5A
392603 | CR | 20190426 | CAQ | D | B0-2B battery parameters not within spec | Y | Y |  | N | YES | <D> **** Detailed Description **** This CR is written to comply with LCS 1.8.6.1.O.1. B0-2B remains inoperable after performance of ESP-B02B-B101, 24 month battery discharge testing. Plan remains to use installed charger to raise voltage to normal levels. Ref L18-ESP-B02B-B101 -001 <I> **** Actions Taken **** Wrote CR | 02-00-E-B0-2B
392604 | CR | 20190426 | CAQ | D | Failed/Drifting LPRM | Y | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02109790-05, then taken back to complete <D> **** Detailed Description **** LPRM-DET-56/17A is Failed/drifting. This was discovered during a shiftly check of the MON run and is likely due to coast down. <I> **** Actions Taken **** Entered ABN-LPRM, bypassed the LPRM and informed SNE. | 02-00-LPRM-DET-56/17A
392605 | CR | 20190426 |  | 3 | (NRC) ABN-ASH procedure revision |  |  |  | N | NO | <D> **** Detailed Description **** ABN-ASH mis-identifies the location of FLEX-VEH-3 and 4. FLEX-VEH-3, International Dump Truck, is actually located in Bldg 600 vice 82 and FLEX-VEH-4, International Flatbed Truck, is actually located in Bldg 82 vice 600. <I> **** Actions Taken **** Wrote CR
392607 | CR | 20190426 |  | 4 | Transformer N2 Cooler Fan Noise | N | N |  | N | YES | <D> **** Detailed Description **** North side bottom left fan is making excessive noise recommend inspect and replace. Picture attatched <I> **** Actions Taken **** Initiated CR and notified control room. . This has been an issue since 9/12/16. WO 02128872 is being planned for the 7/29/19 work week. Temperature may be very hot then. WO 02104980 was completed to replace the motor on 4/18/17. However the problem remains. | 02-00-E-TR-N2
392608 | CR | 20190426 |  | 4 | PW Chlorine Concentration Low | N | N |  | N | YES | <D> **** Detailed Description **** Chlorine concentration 0.92, has been trending down since 4/22/2019. <I> **** Actions Taken **** Notified chemistry and control room. | 02-00-PWC-AY-1
392609 | CR | 20190426 | CAQ | D | Essential Fluorescent lighting in control room | N | Y |  | N | YES | <D> **** Detailed Description **** light 8FDA/1C has 1 lamp replacement needed and light 8FDA/1A has 2 lamps that need to be replaced. lights are in control room and will require scaffold. <I> **** Actions Taken **** cr wr <N> **** Equipment Description **** 8FDA/1C 8FDA/1A
392611 | CR | 20190426 |  | 3 | (NRC) Inconsistent Descriptions for FLEX Fuel Transfer Pumps | N | Y |  | N | NO | <D> **** Detailed Description **** FLEX-P-F5, -F6, -F7 and -F8 are gasoline engine powered fuel transfer pumps. They are described in PASSPORT, ABN -ASH, OSP-FLEX-A106 and SOP-FLEX-EQUIPMENT-REFUEL. For the most part these sources agree on the fuel service for the pumps. However, for two pumps there are discrepancies: 1. FLEX-P-F6 is described as a transfer pump for the B-11 gas tank on PASSPORT. Page 11 of SOP-FLEX-EQUIPMENT-REFUEL states it is for gasoline. Page 10 of OSP-FLEX-A106 states it is labeled "For Diesel Transfer." Pages 32 and 37 of SOP-FLEX-EQUIPMENT-REFUEL state it is for Diesel transfer. Page 52 of ABN-ASH states it is for the underground diesel tank. 2. FLEX-P-F7 is also described as a transfer pump for the B-11 gas tank in PASSPORT. Page 19 of OSP-FLEX-A106 also states it is labeled for Gas Transfer. Page 11 of SOP -FLEX-EQUIPMENT-REFUEL states it is for Diesel. Pages 32 and 37 of SOP-FLEX-EQUIPMENT-REFUEL state it is for gasoline. ABN ASH page 52 also states it is for gas. Actual fuel service for each of these pumps needs to be validated, and appropriate procedures and labels updated as necessary. <I> **** Actions Taken **** Validated procedure references. This is NOT an equipment issue; equipment checked "YES" to allow entering EPN's to facillitate future searches.
392615 | CR | 20190427 | CAQ | C | Increased Reactor chlorides following CFD precoat. | N | Y |  | N | NO | <D> **** Detailed Description **** CON-DM-1C was placed in service at 0400. A SP-1 sample taken at 0430 indicated 2.02 ppb Chlorides. The previous chloride sample taken at 0010 was 1.10 ppb. Increased sampling is already in place as the good practice value for RX chlorides is LE1 ppb, This sample was still below the action level 1 limit of GE3 ppb per SWP-CHE-02 table 6.1.13. This CR is for trending. The chemistry index is 1.41. <I> **** Actions Taken **** Notified CRS and email supervision. increased monitoring is in place.
392616 | CR | 20190427 | CAQ | D | CBD-FR-10 failed down scale | N | Y |  | N | YES | <D> **** Detailed Description **** CBD-FR-10 failed downscale at approximately 0505 on 4/27/19 CBD-FI-1A indicates approximately 2100 GPM. Circ water blowdown was established approximately 2 hours prior to this failure at 2100 GPM. <I> **** Actions Taken **** Informed CRS and SM | 02-00-CBD-FR-10
392617 | CR | 20190427 | CAQ | D | DG4 Coolant Leak | N | Y |  | N | YES | <D> **** Detailed Description **** During step 7.1.1 (pre-start checks) of OSP-FLEX-M704 on 4/27, there was a coolant leak discovered on a flex connection at the diesel. This connection was dropping at approximately 1 drop every 16 seconds. Further inspection noted that under the diesel had a large quantity of coolant and the radiator bullseye was empty, vice the required 1/2 full. Coolant still remained in the reservoir on top of the diesel, but not enough to meet the pre-start check requirements. Possible that other leaks not identified at this date created the larger pool underneath the diesel. Pictures are attached to this CR to show the condition. <I> **** Actions Taken **** Informed supervision. Initiated CR. Informed CRS. <N> **** Equipment Description **** South of Diesel buildings | 02-00-E-DG-4
392618 | CR | 20190427 | CAQ | C | Oxygen concentration is going up in the wetwell | Y | N |  | N | YES | <D> **** Detailed Description **** 0xygen concentration is going up in the wetwell as indicated on CMS-SR-13, level has gone from 1.69% on 04/24/19 to 1.85 % on 04/27/2019 following CMS-SR-14 being returned to service. EDNA points X456 and X359 show WW/DW O2 levels slightly going up. <N> Oxygen, not 0xygen | 02-00-CMS-SR-14
392619 | CR | 20190427 | CAQ | D | E-C0-1A 'AC ON' light bulb out | Y | Y |  | N | YES | <D> **** Detailed Description **** E-C0-1A 'AC ON' light bulb out Recommend having electrical maintenance replace bulb <I> **** Actions Taken **** Informed MCR | 02-00-E-C0-1A
392620 | CR | 20190427 |  | 4 | EDR-V-393A will not close. | N | N |  | N | YES | <D> **** Detailed Description **** EDR-V-393A did not go closed at the end of the resin transfer from EDR-TK-1 to the resin drying system IAW SOP -RW/EDR-OPS section 5.14. . EDR-V-393A will not go closed with the control switch when taken to closed either. Their is a previous AR/WR addressing the fact that the valve indicates intermediate when closed. <I> **** Actions Taken **** Notified supervisor. | 02-00-EDR-V-393A
392621 | CR | 20190427 |  | 4 | Received DEH warning alarm | N | N |  | N | YES | <D> **** Detailed Description **** STEAM CHEST RIGHT HAND TEMP DEV HIGH alarm. TG-TE-SCSRH indicates 795F (indicates failed input status). No turbine drain or main steam extraction line drain valves repositioned. Feedwater Heater operations remain normal. | 02-00-TG-TE-SCSRH
392622 | CR | 20190427 |  | 4 | FPC-FCV-15A indicates closed with 574gpm flow. | N | N |  | N | YES | <D> **** Detailed Description **** FPC-V-15A indicates closed with 575 gpm through the demineralizer ( on the SFP ), and an 8 psig demand signal. Suspect a limit switch adjustment may be needed or a contoller calibration. Please T/S, adjust, repair as needed. Note: Checked light bulb to verify it wasn't the cause. <I> **** Actions Taken **** Checked open indication light bulb for proper operation and notified supervisor. <N> **** Equipment Description **** RW 467 | 02-00-FPC-FCV-15A
392623 | CR | 20190427 |  | 4 | Housekeeping need for Transformer Yard oil absorbants |  |  |  | N | NO | <D> **** Detailed Description **** The Transformer yard is in need of a flammable proof container to dispose of oil soaked absorbants. All of our inservice transformers have variying levels of oil leakage, which generates oil soaked absorbent waste. A small, stratigically located, oil absorbant waste can would greatly enhance the houskeeping efforts in the transformer yard. Because the transformer yard requires special qualifications and controlled key for entry, the flam can should be placed OUTSIDE the transformer yard, in close proximity to the East mangate. <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** oil absorbant, waste can. Locate outside of EAST man-gate
392624 | CR | 20190427 |  | 4 | Houskeeping need for CWPH oil absorbant waste |  |  |  | N | NO | <D> **** Detailed Description **** Because of the chronic "operational" leakage from various CWPH equipment (SAT-P-1A(B) diaphram pumps, FP-P-2A(B) motor bearings, and FP-ENG-1), there is a consistent generation of oil soaked absorbants. The nearest flamable oil absorbant waste container is located in bldg 33 , and would require transporting oily waste in the OPS vehicle. This is a significant hinderance to changing out the oily absorbants. A flam proof oily wast container in the CWPH will significantly imporve the housekeeping efforts of the CWPH. <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** CWPH
392625 | CR | 20190427 |  | 4 | CF-TK-41 gravity drain line appears to be clogging | N | N |  | N | YES | <D> **** Detailed Description **** CF-TK-41 is currently being gravity drained (100 gal per day), due to the failure of CF-P-41A(B) and CF-P-42A(B) - reference AR#389393. The time to gravity drain 50 gals is now taking ~ 30 minutes. Previously, adding 50 gals would only take ~ 15 min. The size of the stream from the gravity drain hose is visibly smaller than in the past. CF-TK-41 level is at ~ 1500 gallons. This should be plenty of product to create sufficient head for gravity draining. Strongly reccomend we elevate the priority on identifying the status of the apparent clogging of both the Chemical feed pump suctions and the Gravity drain lines, before we are left with no way to add corrosion inhibitors to the CW system. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** CWPH | 02-00-CF-TK-41,02-00-CF-TK-42
392626 | CR | 20190427 |  | 4 | RWCU-FCV-33 PMT Testing |  |  |  | N | YES | <D> **** Detailed Description **** During PMT testing for RWCU-FCV-33, control room was requested to demand 100% full open using RWCU-RMC-606 and observe proper operation at RWCU-FCV-33. When demanded to 100% open, valve position and feedback indicated approximately 70% open and verified by measuring current at RWCU-E/P-1 and found 15 mA input. Expected input to RWCU -E/P-1 with RWCU-RMC-606 at 100% full open demand is approximately 20 mA. PMT testing verified RWCU-FCV-33 opens to 100% with 1.5 inches of travel using test equipment. Further investigation is required. <I> **** Actions Taken **** Contacted supervision, control room, wrote CR. <N> **** Equipment Description **** RW 501 MCR | 02-00-RWCU-RMC-606
392627 | CR | 20190427 |  | 4 | RWCU-V-241A is very difficult to operate. | N | N |  | N | YES | <D> **** Detailed Description **** While lifting a DT C/O on RWCU-DM-1A it was very difficult to open RWCU-V-241A from the valve gallery. Opening the valve required assistance from a mechanic on the other side of the valve gallery wall. Max leverage was applied with the valve operator in the valve gallery and D/P was verified to be 0 psig. This valve has been worked on in the past to repair leakby. <I> **** Actions Taken **** Obtained supervisor assistance to prevent damage to the reach rod/coupling. <N> **** Equipment Description **** RW 467 | 02-00-RWCU-V-241A
392628 | CR | 20190427 |  | 4 | PWC-V-453 is stuck OPEN | N | N |  | N | YES | <D> **** Detailed Description **** PWC-V-453 is stuck OPEN, as evidence by the surface wash arm slowly rotating, while PWC-P-122 (surface wash pump) is OFF and the Flocculator is in a standby status. The back flow through the surface wash arm was slowly draining PWC -TK-100 and filling PWC-FU-1 to the point of overflow, to the storm drain. AR# 207990 identified a very similiar issue that ended up being a failed spring inside PWC-V-453. Please investigate/repair. PWC-V-453 has been isolated from PWC-TK-100, by CLOSING PWC-V-451 (PWC-P-122 suction), to prevent further undesired draining of PWC-TK-100. Note: a 2A Sub Master Key is required for entry into Bldg. 33 <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** BLDG 33, Note: a @A Sub Master Key is required for entry. | 02-00-PWC-V-453
392629 | CR | 20190427 |  | 4 | NA step to support recovery of RWCU |  |  |  | N | NO | <D> **** Detailed Description **** NA step to support recovery of RWCU. Need to NA step 5.15.1e to allow due to the condition of the RWCU logic timer at position one. Performing a backwash per step 5.15.2 will restore the system to normal lineup <I> **** Actions Taken **** Discussed issue with SM and got his approval for NA.
392630 | CR | 20190427 |  | 4 | E-TR-M2 Cooler Group 4 alarms do not clear | N | N |  | N | YES | <D> **** Detailed Description **** Responding to Main 2 Transformer Trouble alarm, found Cooler 4 Failure or Off Position and Loss of Oil Flow Pump 4. Performed actions from ABN-TRANSFORMER, section 7.4.11 but alarms would not clear when reset on step 7.4.11d. Fan 10 was initially found not running (due to 52F-10 breaker tripped), and procedure successfully started cooler group 4 fans and pump (verified by switch and shaft). <I> **** Actions Taken **** Verified fans and pumps running. Notified CRS of condition. | 02-00-E-TR-M2
392631 | CR | 20190427 | CAQ | D | Received Rod Accumulator Trouble Alarm. | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm 4.603.A7 drop 6-7 for CRD-HCU-3059 due to high water level. Drained accumulator and cleared alarm. <I> **** Actions Taken **** Drained accumulator and cleared alarm. | 02-00-CRD-HCU-3059
392632 | CR | 20190428 | CAQ | D | Received Rod Accumulator Trouble Alarm. | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm 4.603.A7 drop 6-7 for CRD-HCU-2203. Alarm was due to high water level in accumulator. Drained and cleared alarm. <I> **** Actions Taken **** Drained accumulator. | 02-00-CRD-HCU-2203
392637 | CR | 20190428 | CAQ | D | Spray Pond A Hi/Lo Level Alarm | Y | N |  | N | YES | <D> **** Detailed Description **** H13-P840.A5.7-2 â€œSpray Pond A Level High/Lowâ€ alarm is locked in with normal SW-A spray pond levels and no SW pumps running. Indicated level on SW-LI-1A is 13.5 ft. Local indicated level is 433â€™1â€. Request the level switch for the alarm be adjusted/calibrated to not be in alarm at normal levels with no pumps running. | 02-00-SW-LS-1A1
392638 | CR | 20190428 | CAQ | D | RPS-RLY-K4D buzzing sound. | Y | N |  | N | YES | <D> **** Detailed Description **** RPS-RLY-K4D has a buzzing sound from the soleniod. This sound was not present in the previous days. The relay is energized (normal position). There is no known reason this relay is in immediate danger of failing. <N> **** Equipment Description **** MCR | 02-00-RPS-RLY-K4D
392639 | CR | 20190428 |  | 4 | <10 yellow CIA N2 bottles on wall rack | N | N |  | N | NO | <D> **** Detailed Description **** <10 yellow CIA N2 bottles on wall rack in Rx bldg truck bay 9 bottles on rack, logs call for 10 or more. Recommend bringing n more yellow N2 bottles <I> **** Actions Taken **** Informed MCR emailed Chadd Bliss . MR submitted requesting 9 new/full CIA bottles. See XRef panel <N> **** Equipment Description **** Yellow N2 bottles in rx bldg truck bay
392640 | CR | 20190428 |  | 3 | Procedural Enhancement SOP-RHR-SDC |  |  |  | N | NO | <D> **** Detailed Description **** SOP-RHR-SDC step 5.2.7 inappropriately says to place a Danger Tag on RHR-RMS-FCV/64B, even though the switch is not being used as a boundary because the valveâ€™s disconnect is danger tagged open. An Equipment tag should be used for RHR-RMS-FCV/64B instead. OI-12 step 6.13.3 says â€œIn Danger clearances C/S are normally Equipment tagged unless the C/S is being used as a clearance boundary. When used as a clearance boundary C/S are red tagged and the required control switch position (not Information) is placed in the Placement Configuration field. A Job Hazard Analysis is also required when using a C/S as a clearance boundaryâ€. This comment also applies to following steps of SOP-RHR -SDC: 5.1.7, 5.8.13, 5.9.13, 5.10.2, 5.11.2.
392641 | CR | 20190428 |  | 3 | Procedural Enhancement to SOP-FPC-ASSIST-ALT |  |  |  | N | NO | <D> **** Detailed Description **** SOP-FPC-ASSIST-ALT step 5.2.19 refers you to the wrong procedure if the pump trips. It says â€œIF RHR-P-2B trips, THEN RESTART RHR-P-2B per SOP-FPC-ASSIST-ALT, if the pump is available.â€ It should refer to SOP-FPC-ASSIST-RESTART instead.
392642 | CR | 20190428 |  | 3 | SOP-RHR-SDC refers to OPDRVs =>R24 issue |  |  |  | N | NO | <D> **** Detailed Description **** SOP-RHR-SDC step 5.2.17.a refers to â€œOPDRVâ€ requirements per PPM 3.4.1. Recently OPDRV requirements have been deleted and are now under a new program of Water Inventory Control. Recommend the step be updated as required. This comment also applies to step 5.1.17 and P&L 4.32.
392643 | CR | 20190428 |  | 3 | TSP-THERM-C101 revision | N | N |  | N | NO | <D> **** Detailed Description **** Step 10.1.11.a needs a sign off line added. Please incorporate this change with AR 00392154 changes.
392644 | CR | 20190428 |  | 3 | SOP-CAVITY-FILL enhancement | N | N |  | N | NO | <D> **** Detailed Description **** Precaution and limitation 4.2 states the FPC temperature limit for a loss of a single FPC loop is 155F. FSAR Table 9.1-6 states the temperature limit for the loss of one FPC loop is 175F. The FSAR was revised in 2013 and it is likely this infrequently used SOP was not updated. <I> **** Actions Taken **** Documented discrepancy with this CR
392645 | CR | 20190428 |  | 3 | Remove LCS Table 1.7.1-1 Note 7 | N | N |  | N | NO | <D> **** Detailed Description **** Remove Note 7 from LCS Table 1.7.1-1 which is for the RB 606 area temperature. The stack monitor is no longer on the RB 606 and there should be no specific location required for taking the RB 606 general area temperature. <I> **** Actions Taken **** Discussed with engineering, email attached.
392646 | CR | 20190428 | CAQ | D | DO-F-3 leaking fuel oil (HPCS DG) | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02104159, then taken back to complete <D> **** Detailed Description **** DO-F-3 is leaking fuel oil, and drops of fuel oil are present on the filter sleeve. See pictures in EDMS. Please investigate and repair. <I> **** Actions Taken **** Notified SMgt, wrote CR. Directed Ops 2 to wipe up the fuel oil and to continue to monitor. <N> **** Equipment Description **** HPCS DG, east side Verified with Ops 2 that this is a very small leak with the formation of a few drops of fuel oil on the filter casing. | 02-00-DO-F-3
392647 | CR | 20190428 |  | 3 | PPM 3.3.1 Enhancement | N | N |  | N | NO | <D> **** Detailed Description **** Section 5.4.2.a states that RPV PRESS HI is 1121# for an ATWS/ARI initiation. ARPs 4.603.A7 and A8 drop 3-1 ATWS -ARI TRIP identify this set point is 1120#. The 1120# value is supported by the IMDS for MS-PS-45A/B/C/D. Recommend updating PPM 3.3.1 to reflect the correct nominal value of 1120#. <I> **** Actions Taken **** Documented discrepancy in CR for correction.
392648 | CR | 20190428 |  | 4 | SAM-12 (HP-EQ-42813) Out of Service | N | N |  | N | NO | <D> **** Detailed Description **** SAM 12 at HP PAP out of service due to screen being blank. Instrument seems to work otherwise. This leaves only one SAM-12 in service <I> **** Actions Taken **** Wrote Work Request <N> **** Equipment Description **** GSB HP PAP
392649 | CR | 20190428 |  | 4 | SCS TRENDING TROUBLE ALARM | N | N |  | N | YES | <D> **** Detailed Description **** SCS Trending Trouble Alarm - IO PANEL Mux 4A MR16G <I> **** Actions Taken **** Security Supervision Notified. Security Equipment Coordinator Notified, Safeguards Specialist Notified. | 02-00-SEC-MUX-4A
392650 | CR | 20190428 | CAQ | C | (NRC Identified) SW-PCV-15B Position Indicator | Y | Y |  | N | YES | <D> **** Detailed Description **** The NRC noted that there is a paper scale taped to the position indicator on SW-PCV-15B. Engineering should evaluate whether the paper scale is needed and if so then request a permanent scale to replace the paper scale. SW -PCV-15A did not have a taped paper scale. Picture is attached to EDMS. | 02-00-SW-PCV-15B
392651 | CR | 20190428 |  | 4 | Unattached SSC Label found | N | N |  | N | NO | <D> **** Detailed Description **** A SSC label was found adjacent to DO-LITS-10A by the NRC resident incpector. See attached picture. <I> **** Actions Taken **** Label request submitted
392652 | CR | 20190428 | CAQ | D | HPCS-V-26 has slow packing leak | Y | N |  | N | YES | <C> CR reopened due to accidental cancellation. CR reopened for notes to be added by Reg Affairs, then taken back to closed <D> **** Detailed Description **** The valve parts around the packing follower for HPCS-V-26 are rusty, and there is a drop of water hanging from the valve, indicative of a slow leak. Please investigate and repair. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RB 422 HPCS room <R> NRC Identified. | 02-00-HPCS-V-26
392653 | CR | 20190428 | CAQ | D | HCU 34-23 high accumulator water level alarm | Y | N |  | N | YES | <D> **** Detailed Description **** HCU 34-23 had a high accumulator water level alarm. This CR is for trending. <I> **** Actions Taken **** Drained HCU water; notified SMgt, wrote CR. <N> **** Equipment Description **** RB 522 | 02-00-CRD-HCU-3423
392654 | CR | 20190428 |  | 4 | CAMERAS NEEDED TO BE CLEANED INSIDE PA | N | N |  | N | NO | <D> **** Detailed Description **** Cameras needed to be cleaned inside the PA: CCTV01 -CCTV03T-CCTV11T- CCTV12- CCTV12T- CCTV13- CCTV13T- CCTV42- CCTV45- CCTV46 <I> **** Actions Taken **** CAS generated list, notified supervision, CR/WR generated <N> **** Equipment Description **** LIst of cameras are located inside the Protected Area. Notify supervision prior to work.
392655 | CR | 20190428 | CAQ | D | Blue dot light out in RW 525 stair vestibule | N | N |  | N | YES | <C> CR reopened to cross reference additional WR 29147677, marked completion required box, then taken back to complete <D> **** Detailed Description **** A blue dot light fixture on RW 525, in the stairway vestibule, has both bulbs out. Please relamp. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 525 stairway vestibule Blue dot light is a normal emergency egress lighting ballast fixture per PPM 10.25.64, Non-essential.
392656 | CR | 20190429 | CAQ | D | Blue dot fixture lamps out RB SW A5 | N | N |  | N | YES | <D> **** Detailed Description **** There is a blue dot light fixture in RB stairwell A5 at the approximate 512' level that has both lamps out. Please relamp. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RB A5 stairwell at approx 512' elevation. Per PPM 10.25.64 blue dot lamps are normal emergency egress and are non-essential.
392657 | CR | 20190429 |  | 3 | (NRC Identified) CCH-CR-1A and CCH-CR-1B Control Panel Clips | Y | Y |  | N | YES | <D> **** Detailed Description **** The panel doors for CCH-CR-1A and CCH-CR-1B controls have installed restraints/clips that are not engaged. The panel doors are closed and latched via a door latch. A review of component drawings did not provide a level of detail that could confirm the need for the restraint clips to be engaged. Recommend engineering evaluate the need for the door clips. The panel doors do not provide a HELB function and are not referenced in PPM 1.3.57. See EDMS for picture. | 02-00-CCH-CR-1A,02-00-CCH-CR-1B
392658 | CR | 20190429 |  | 4 | PTZ 35 needing maintenance | N | N |  | N | YES | <D> **** Detailed Description **** PTZ 35 has occasional distorted picture. <I> **** Actions Taken **** CAS identified issue. Notified supervision, CR/WR generated <N> **** Equipment Description **** Located inside the PAAP.
392659 | CR | 20190429 | CAQ | D | (NRC Identified) DO-P-2 RMS Control Panel Top Clips Missing | Y | N |  | N | YES | <D> **** Detailed Description **** A DO-P-2 RMS panel labelled CS-DO DIV 3-P-2 located in the Div 3 diesel fuel oil storage tank room has restraining clips on the top of the panel that are missing. Other clips on the side are engaged. See EDMS for pictures of missing clips on top and engaged clips on side. | 02-00-DO-P-2
392660 | CR | 20190429 |  | 3 | (NRC Identified) RPS-MG-1 and RPS-MG-2 Control Panel Thermog | Y | N |  | N | NO | <D> **** Detailed Description **** The NRC questioned why the RPS-MG-1 and RPS-MG-2 panel (E -CP-C72/S001A and E-CP-C72/S001B thermography windows are different. See pictures in EDMS. Thermographic inspection windows were installed for E-CP-C72/S001A under WO 01141057 in 2008 and E-CP-C72/S001B under WO 01141056 in 2013.
392661 | CR | 20190429 |  | 3 | (NRC Identified) SW-V-2B Flange Bolts | Y | N |  | N | YES | <D> **** Detailed Description **** The NRC noted a difference between SW-V-2A and SW-V-2B flange bolted connections. There are 24 fasteners installed on SW-V-2B on the south flange connection nearest SW-P-1B. 22 of the fasteners are a threaded bolt while the 2 located at the top of the flange are a stud/nut arrangement. This configuration does not exist on SW-V-2A. WO 02052516 installation of SW-V-2B following removal for ASME inspections references a difference in torqueing these top 2 fasteners as â€œturn-of-the nutâ€ method as compared to the remaining 22 fasteners. No other design information or historical work orders were found specific to this arrangement. Engineering should assess the SW-V-2B fastener installation to ensure its adequacy and initiate a new CR if the installation is not per design. See EDMS for pictures. | 02-00-SW-V-2B
392662 | CR | 20190429 | CAQ | D | HCU 34-23 accumulator trouble | Y | N |  | N | YES | <D> **** Detailed Description **** HCU 34-23 accumulator trouble due to high water level. <I> **** Actions Taken **** Followed ARP and cleared trouble alarm. | 02-00-CRD-HCU-3423
392663 | CR | 20190429 | CAQ | D | MW 67 JBT | N | N |  | N | YES | <D> **** Detailed Description **** CAS receieved a high alarm rate on the JBT for MW 67. <I> **** Actions Taken **** Compensatory Measures initiated, CR/WR, No Electrical Support onsite at the time. Security Supervision Notified. | 02-00-SEC-MW-ISFSI/67AT
392671 | CR | 20190429 |  | 4 | Reckless driving on access road |  |  |  | N | NO | <C> CR reopened to edit severity level. <D> **** Detailed Description **** At approximately 0530 while driving down the access road, I was passed by a dark Harley Davidson motorcycle (partial plate # 620) at a very high rate of speed. The motorcycle then crossed the double yellow line (in the 30mph zone) into the oncoming traffic lane and passed 2 vehicles before merging back into the north bound lanes. <I> **** Actions Taken **** Generated AR for trending.
392675 | CR | 20190429 | CAQ | D | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0068257 Fluke True RMS Multimeter- model 287 found OOT & adjusted within specs. EFIN Eval: Card 1- ALL except Usage #21, Function and/ or range not used. Usage #21 WO #02138372-01 The delta was below area of interest. Card 2- ALL function and/ or range not used. No Plant Impact. DEF #7007A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
392679 | CR | 20190429 |  | 3 | (R24LL) Pre-outage task impact on 2 week no fly zone |  |  |  | N | NO | <D> **** Detailed Description **** As of 4/29/19, there are 200 pre-outage tasks remaining to be complete prior to R24. This is also Day 1 of the 2 week no fly zone. Some of these pre-outage tasks were known impacts to the 2 week no fly zone, however, many have either been added or rescheduled into this 2 week period which will result in less time for the shops to prepare for R24. Need to evaluate this as part of the station critique. Assign as severity 3 to AR-OTMG. <I> **** Actions Taken **** Discussed w/Outage Mgmt team
392681 | CR | 20190429 | CAQ | C | EWD-1E-059 Minor Correction |  |  |  | N | NO | <D> **** Detailed Description **** EWD-1E-059 at G-6 location has a light bulb labeled â€œDS32â€. The light bulb should actually be labeled DS23 as per local inspection of the labeling on H13-P609 and step 5.2.9 of SOP-RHR-SDC-BYPASS.
392682 | CR | 20190429 |  | 3 | Lessons learned, DG-SV-1B1/1B2 taper pins degraded. |  |  |  | N | NO | <D> **** Detailed Description **** During the implementation of work orders 02092281 and 02092282 for the replacement of DG-SV-1B1, and DG-SV-1B2, the taper pins were degraded and required replacement which caused delays with work completion. This issue became critical path for DG2. <I> **** Actions Taken **** Generated this CR to document the degraded condition, which in turn, caused delays, lessons learned during the DG2 window, and create sub-assignment for planning to integrate your recommendations into future w/o's. <N> The model WOs need to be revised to purchase the parts to replace the taper pin and the trip cam, the instructions for the mechanics should be revised to direct drilling the solenoid shaft for installation of the new trip cam and taper pin. The trip cam part number is 8246101 (CATID 58619183), the taper pin part number is 103563, a CATID needs to be created for this EMD part number to ensure a class 1 taper pin is on hand for future replacements.
392684 | CR | 20190429 |  | 3 | Spare transformers need attention | N | N |  | N | YES | <D> **** Detailed Description **** The spare transformers in the warehouse wire yard have degraded storage conditions. Of the 3 smaller transformers, 2 of the oil leak containment basins have signifcant amounts of water in them, but the 3rd is completely dry. This may indicate a leak in the one that is dry. The leak containment around the large transformer is collapsed and would not contain a leak. The N1 spare has a large birds nest built on it and the grounding wire between the phases has become disconnected from some of the phases. The nest and ground wire were originally documented in CR381117 in June of 2018. <I> **** Actions Taken **** Notified supervision Generated this CR <N> **** Equipment Description **** Spare transformers located in the Wire lay down yard at the warehouse
392685 | CR | 20190429 | CAQ | D | ContainmentT particulate rad detectors show elevate level | Y | N |  | N | YES | <D> **** Detailed Description **** ContainmentT particulate rad detectors shown elevate level. CMS-RIS 12A/2 indicated from 4E-12 to 1E-10 uCi/cc CMS-RIS-12B/2 indicated from 1E-12 to 7.5E-11 uCi/cc Both detector study out at < 1E-10 uCi/cc. The on ly activity in progress is the reduction cooling to the containment drywell to support CRA-FN 2A2 outage. Need to investigate and resolve the issue if exist. <I> **** Actions Taken **** SM/CRS and Chemist are informed. A request to chemist is to draw a sample then evaluate. | 02-00-CMS-RIS-12B
392686 | CR | 20190429 |  | 4 | Lock and cable stolen from RW 487' cage |  |  |  | N | NO | <D> **** Detailed Description **** The RW 487â€™ Supply cage for Chemistry and RP had a lock and a cable placed on it to keep supplies from going missing un-accounted for. The lock and the cable were removed and have been taken. This is evidence of the issues the supply cage has had with missing supplies. <I> **** Actions Taken **** Notified MCR, Chemistry and RP supervision <N> New lock and cable have been ordered. No further action required.
392687 | CR | 20190429 | CAQ | D | LCS 1.7.1.A.2 Exceeded temperature limit. | Y | Y |  | N | NO | <D> LCS 1.7.1.A.2 Exceeded temperature limit on CMS-TE-24 RPV head area. The temperature exceeded the limit about 1 hour after securing CRA-FN-2A2 which was about the time frame expected. Engineering performed EC 17705 already which predicts all environmentally related equipment within the drywell above the 572â€™ elevation which may experience intermittent high temperatures would be qualified for >60 years if exposed to a constant ambient service temperature of 170Â°F. Intermittent temperature excursions up to 170Â°F are inconsequential. <I> Informed shift manager entered the LCS and established the new temporary temperature limit of 170Â°F and gave a new temporary log to verify temperature less than 170Â°F every 4 hours to CRO1, and referenced EC 17705.
392688 | CR | 20190429 |  | 3 | TSW-TIC-14A does not control in AUTO mode. | N | N |  | N | YES | <D> **** Detailed Description **** TSW-TIC-14A does not control RFT-1A lube oil in Automatic. Investigated notification from the MCR of lowering lube oil temp .on the A RFT . Local LO temp. was about 94F as read locally on RFT-TI-3G/1A. TSW-TIC-14A setpoint and proccess variable were consistent with TSW-TIC-14B. (See attached pics.). TSW-TIC-14A air output signal was showing about 25% (95% open on the control valve). TWS-TIC-14B air output was at 85%, (only 25% open on the control valve). Per MCR direction, performed a transfer of TSW-TIC-14A from AUTO to HAND and raised air output to 85% ( 25% open ) to match TSW-TIC-14B air output. RFT-1A lube oil temp. returned to normal at about 106F. Please T/S, repair as necessary to restore auto control to TSW-TIC-14A. <I> **** Actions Taken **** Notified MCR of local indications. Per MCR direction, took manual control of TSW-TIC-14A and restored lube oil temp. to NOT. MCR is initiating a CT to indicate that the controller must be operated in HAND. <N> **** Equipment Description **** E-IR-16 TG 441E | 02-00-TSW-TIC-14A
392689 | CR | 20190429 |  | 4 | Housekeeping B-75 Concrete pad. Dumping Ground |  |  |  | N | NO | <D> **** Detailed Description **** The concrete pad outside of B-75 has become a dumping ground for many departments. This area is not for garbage disposal and limited wood is allowed per Fire Marshall and Neil Requirements. All departments need to dispose of their own trash and pallets cradle to grave. Accumulation of garbage and crates needs to be outside the RCA and in appropriate areas. This also limits the unloading area for material deliveries.
392690 | CR | 20190429 |  | 4 | CW-CT-1A high level, at 12.5" | N | N |  | N | YES | <D> **** Detailed Description **** CW-CT-1A distribution plenum is High out of Spc. Current level is 12.5". Per PPM 3.1.10 (OPS logs), the high spec. is 11". Please schedule deck cleaning of CW-CT-1A <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** CW-CT-1A | 02-00-CW-CT-1A
392692 | CR | 20190429 |  | 4 | Housekeeping tour: Lighting discrepancies | N | N |  | N | NO | <D> **** Detailed Description **** Reactor bldg. 522 has 5 ballasts that are having lighting issues. The lights are dimly lit, and are flickering constantly. Reference attached pictures in WO 02132753. SW pumphouse A has 3 lights that are out in the Crane Bay, also reference above work order for location of lighting discrepancies. <I> **** Actions Taken **** CR written to document the lighting issues. Area owner groups emailed housekeeping list, and WR generated as part of the CR. <N> **** Equipment Description **** SW pump house A and Reactor 522
392694 | CR | 20190429 |  | 3 | R24LL) Work on or Near Protected Equipment |  |  |  | N | NO | <D> **** Detailed Description **** There are 32 items in the Outage schedule that require work on or near protected equipment during the outage (see EDMS list). The responsible groups need to complete the appropriate form to ensure they are ready to perform this work. An asgn on this CR will drive those actions. As a lesson learned, the need for ensuring the form is completed needs to be incorporated into the outage milestone after Rev. 0 of the Shutdown Safety Plan has been issued. Assign as Sev. 3 to AR-OTMG <I> **** Actions Taken **** Discussed w/OpsWM
392695 | CR | 20190429 |  | 3 | SOP-HWC-START- new section for Immediate restart |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** SOP-HWC-START does not have a section to allow for the immediate restoration of the HWC system after a spurious trip, due to plant transients (such as a loss of Cond booster pump, or transient in Cond/RFW system like COND-V -76 opening). HWC out of service time can have significant impact on Columbia's Chemistry Performance Index. The current procedural guidance for "rapid" restoration is not rapid by any means. It requires verifications of manual valves, in difficult to reach locations, who's position should not be in question, if the HWC system was previously in service. Please see EDMS for proposed new section to SOP-HWC-START - changes in Red, starting on Pg. 22. (Note: the attached proposed change does not include changes to formating and table of contents, etc.) <I> **** Actions Taken **** Informed Engineering of new proposed change <N> **** Equipment Description **** SOP-HWC-START enhancement
392698 | CR | 20190429 |  | 4 | 2019 L&I Elevator Inspection APEL High Bay E conveyance11880 |  |  |  | N | YES | <D> **** Detailed Description **** Inspection report from Labor and Industries notes required actions. Response due 7/18/2019. A copy of the inspection report is uploaded in EDMS docs. <N> **** Equipment Description **** APEL High Bay East elevator conveyance ID 11880
392699 | CR | 20190429 |  | 4 | Initial Training Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** An individual in the HP Technician initial training program failed an exam for HP001932, Radiological Risk Management. <I> **** Actions Taken **** Notified RP Supervision. Following remediation, the individual successfully passed a second exam.
392700 | CR | 20190429 |  | 4 | Individual Using Unauthorized Material on a CBT Exam | N | N |  | N | NO | <D> **** Detailed Description **** On 4/10/2019 an individual from Org 84000 was observed using unauthorized material while taking a CBT Exam. <I> **** Actions Taken **** Individual was exited from exam and directed to their employer. Employer and Training Management were notified. <N> Williams Plant Services
392701 | CR | 20190429 |  | 3 | WO 02113213-01 Requirement screen inaccessible. |  |  |  | N | NO | <D> **** Detailed Description **** WO 02113213-01 and -02 Requirement screens inaccessible. Error message states the following: Your transaction was unable to complete processing due to an application program failure. If problem persists, report this to your application support group. <I> **** Actions Taken **** Checked this on another computer with same results. Please fix process.
392702 | CR | 20190429 |  | 4 | Lamp falure during WO# 02131875 01 | N | N |  | N | YES | <D> **** Detailed Description **** HID lamp failed to come back on after the quarterly test was performed. Due to height a lift is needed to access. Due to scaffolding in place it is not accessable with a lift. <I> **** Actions Taken **** Iniciated CR/WR, notified supervision and CRS <N> **** Equipment Description **** ELP-7AC/3 fixture number 9 | 02-00-E-ELP-7AC
392703 | CR | 20190430 | CAQ | D | Security MW 01 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security zone MW 01 is not operating by design and needs maintenance. Compensatory measures initiated. Contact 2185 for details. <I> **** Actions Taken **** Security supervision notified. Shift manager notified. CR/WR initiated. Compensatory measures initiated. | 02-00-SEC-MW-1RA
392704 | CR | 20190430 | CAQ | D | High Reactor Chlorides | N | Y |  | N | NO | <D> **** Detailed Description **** COND-DM-1F was placed in service at 1730 on 4/29/19. A sample of SP-1 taken at 0044 on 4/30/19 indicated 1.13 ppb chlorides. A backup grab sample taken at 0125 indicated 1.12 ppb chlorides. This sample is below the action level 1 limit of GE 3 ppb per SWP-CHE-02 table 6.1.13. Chemistry index is at 1.05. Initiated 4 hour sampling to monitor cleanup as the good practice value for SP-1 chlorides is LE 1 ppb. This CR is for trending purposes. <I> **** Actions Taken **** Notify CRS and supervision. Intiated 4 hour sampling. Wrote CR
392705 | CR | 20190430 |  | 4 | West gate on Transformer yard found unlocked |  |  |  | N | NO | <D> **** Detailed Description **** West gate on Transformer yard found unlocked while hanging protection scheme. Gate was shut, lock was locked on fencing. locked gate and verified no one was inside, let myself out other gate. <I> **** Actions Taken **** discussed with CRS who recommended a cr . Discussed with Security Sgt who stated no abnormal reports or activity had been observed in the transformer yard this shift.
392706 | CR | 20190430 |  | 4 | SOP-WARMWEATHER-OPS impact of degraded equipment |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of WO 02109628-01 the following items were identified as part of step 4.2: No issues were identified affecting nuclear safety. Issues affecting generation: CW-P-1C is currently operating under ODMI 357 and is expected to operate under this ODMI following R24. TMU-LCV-2A has exhibited abnormal operation Ref. WRs 29143710, 29143479. TMU-P-1C is cautioned tag under C-TMU -P-1C-001 after spuriously tripping with no apparent cause. CR 00387042. E-TR-N2 has a failed fan. The fan is scheduled to be repaired the week of 7/30/19 during the heat of the summer. WO 02128872 ASD Building HVAC Multiple work requests identify that the ASD building temperature GT the Operationâ€™s Log specification of 80F. Ref WRs 29144424, 29144423, 29123500, 29123429, 29123428. These issues present an increased risk to generation during hot weather operations. <I> **** Actions Taken **** Informed SM.
392707 | CR | 20190430 | CAQ | D | RCC-V-72A indicates intermediate when it should be open | Y | Y |  | N | YES | <D> **** Detailed Description **** RCC-V-72A indicates intermediate (both red and green lights illuminated on H13-P813) when the valve should be full open (CRA-FN-2A1 and / or CRA-FN-2A2 running). This occurred after replacement of CRA-FN-2A2 started bucket (CRA-42-7B5B) per WO 02035819. RCC-V-72A indicated intermediate prior to stopping CRA-FN-2A1 and closing in CRA-42-7B5B for recovery of CRA-FN-2A2. RCC-V-72A appears to be physically open based on drywell temperature and RCC flow parameters returning to normal following re-start of CRA-FN-2A2. Note: this valve was previously documented as not indicating full closed by WR 29142707. <I> **** Actions Taken **** Notified the CRS and SM. Submitted CR and WR. | 02-00-RCC-V-72A
392712 | CR | 20190430 |  | 4 | Received H2 water chemistry trouble alarm | N | N |  | N | NO | <D> **** Detailed Description **** H2 water chemistry trouble received 4.840.A3 drop 7-6, sent OPS3 to investigate. OPS3 reports that there was supply facility trouble alarm in and clear with normal indications on P500 panel. Chemistry reports that there are no new alarms on HSSF-CAB-CHEMLAB. .
392716 | CR | 20190430 | CAQ | D | Security CCTV 46 | N | N |  | N | YES | <D> **** Detailed Description **** CCTV 46 is not functioning as designed. Please contact Security at extension 2185 for further details. <I> **** Actions Taken **** Compensatory measures posted, Security Supervision notified, CR/WR generated for Electrical support. | 02-00-SEC-CCTV-ISFSI/46
392717 | CR | 20190430 |  | 4 | TSW-F-2A packing leakage onto equipment below. | N | N |  | N | YES | <D> **** Detailed Description **** TSW-F-2A packing is leaking. Currently there is a catch funnel keeping water off of TSW-M-F/2B, but the damage to TSW-M-F/2B was already done, see WR 29147939. This leakage was corrected on 8/27/18 under WR 29144330, but the leakage has increased again. Please correct the leakage problem. See pictures in attributes screen of the work request. <I> **** Actions Taken **** Informed supervision and wrote this CR/WR. <N> **** Equipment Description **** P450 W0/1.0 | 02-00-TSW-F-2A
392718 | CR | 20190430 |  | 3 | ME-02-90-46 out of date | N | N |  | N | NO | <D> **** Detailed Description **** ME-02-90-46 is out of date in several ways, none of which affects the ability of RWCU-RV-1 to perform its design function. The calc still has analysis for RWCU-RV-2, which has been removed from the plant. The calc refers to RWCU-RV-1 as a 1 x 1 relief valve while the installed relief valve is Â¾â€ x 1. The calculation uses the wrong specific heat on page 5.006, which results in a conservative error of requiring a relief capacity of 27 gpm. The correct relief capacity requirement is 12 gpm, as is listed on page 2.000. Since the installed capacity is listed as 37 gpm, correcting this error increases margin. Since the calc was issued, the relief valve was replaced with a higher capacity relief valve, 82 gpm at 70F versus the 37 gpm capacity listed, which is also a conservative error. Suggest revision to the calc.
392721 | CR | 20190430 |  | 4 | B81 MPF Fire Alarm Trouble Signal Reported | N | N |  | N | YES | <D> **** Detailed Description **** On 4/29/19, Monday, at about 1325 hours the SCC called to report a TROUBLE signal was transmitted to SCC Monaco D21 and MOON Security. Investigation by Telecom Technician found that the MXL Fire Alarm Panel recorded a Trouble signal detailed: 001 Class A Loop Trouble. Visual inspection of the MMB3 mother board in Panel 1 and the PAD3 modules in Panel 2 as well as the TRI relays in Panel 2 did not show any red or amber lights. Fire alarm panel was reset and the Trouble cleared. Panel reset has held for about 22 hours now. This appears to be a non-disclosed Trouble and there is no further actions that can be taken. See EDMS for EMail discussions with Telecom and System Engineer. <I> **** Actions Taken **** Visual check of all components and relays. No red or amber LED indicating lights observed. Reset the Fire Alarm panel without further issues. <N> **** Equipment Description **** B81 MPF Fire Alarm Control Panel
392722 | CR | 20190430 |  | 3 | CMS Parts Unavailable to Support R24 Outage Work |  |  |  | N | NO | <D> **** Detailed Description **** This CR does not affect proper function of installed plant equipment. OEM replacement CMS-LS-1 (CMS-LT-LS/1), CMS -LS-2 (CMS-LT-LS/2), CMS-LS-2 (CMS-LT-LS/2), and CMS-LS-2 (CMS-LT-LS/2) drywell level switches (flood detection) were ordered under CID 38155 on an advance procurement PO 352776 (issued 8/28/2018) to support outage WO 02108241, 02108269, 02108270, and 02108479. CGS has worked closely with the manufacturer to help resolve continued parts shipment delays (no firm shipment commit date). Additionally, the OEM has been unable to provide PO required documentation necessary to approve and environmentally qualify the new replacement switches for application in the CGS drywell. The subject R24 work orders are driven by a 68 month Equipment Qualification (EQ) PM (PMID 958-02, 956-02, 957-02, 955-03) to replace the installed (obsolete) level switch sensor heads. Equipment Qualification Engineering has performed a preliminary review of the qualified life for the existing switches and a PM extension of at least one fuel cycle is feasible. . Recommend an OSCR and SMS PM extension be issued to remove the CMS drywell level switch sensor head replacement activity (under WO 02108241, 02108269, 02108270, and 0210847) from R24 outage scope due to lack of parts. Note: Calibration of the installed level switches is still due 05/12/2019 under the respective tasks for the same PMIDs (Work order scope may require re-work). . See AR CR EDMS for additional background information. <I> **** Actions Taken **** Notified Procurement, Procurement Engineering Supervisor, EQ Engineering, System Engineering <N> **** Equipment Description **** CMS-LS-1 CMS-LS-2 CMS-LS-3 CMS-LS-4 CMS-LT-LS/1 CMS-LT-LS/2 CMS-LT-LS/3 CMS-LT-LS/4 | 02-00-CMS-LS-1,02-00-CMS-LS-2,02-00-CMS-LS-3,02-00-CMS-LS-4,02-00-CMS-LT-LS/1,02-00-CMS-LT-LS/2,02-00-CMS-LT-LS/3,02-00-CMS-LT-LS/4
392724 | CR | 20190430 |  | 4 | Declared Prohibited item at Security Checkpoint |  |  |  | N | NO | <D> **** Detailed Description **** At approx 0955 an un-badged contractor arrived at the Security Checkpoint. When instructed to exit the vehicle for a visitor search the individual declared to the officer that he had a handgun in the vehicle. The Security Officers took possession of the firearm and notified Supervision. Benton County Sheriff was notified and declined to respond to site. The Point of contact stated that a prohibited item email had been sent to the contracting company, however the information was not passed on to this particular individual. Access to the station was denied. <I> **** Actions Taken **** Security Supervision, Shift Manager, and Benton County were notified. The point of contact was contacted, and visitor access was denied for the day. CR generated. <N> **** Equipment Description **** Security Checkpoint
392727 | CR | 20190430 |  | 3 | New Procedure needed for Temporary PCs during Outages |  |  |  | N | NO | <D> **** Detailed Description **** Each outage Operations requests to install additional PC work stations in the MCR to support the additional work load. This has been done previously using AR EVAL and Temporary Modificiation process. Rather than doing a temporary mod each outage we should have a Procedure that directs the installation and removal of the temporary PCs to satisfy the requirements in SWP-CM-02. <I> **** Actions Taken **** Discussed with Engineering and Ops AOM Initiated CR
392729 | CR | 20190430 |  | 3 | DW leak approx 60 dpm from DW-CE-2A | N | N |  | N | YES | <D> **** Detailed Description **** DW leak approx 60 dpm from where DW-CE-2A connects into the DW/SW/RHR 'A' system. The ball valve that isolates the CE from the system has no EPN, but has approx 60 drops/ min stem/packing leakage to the floor. Approx 15 feet off the floor of the 548 RHR 'A' HX room, SW corner <I> **** Actions Taken **** Informed SSS, MCR <N> Should consider adding the DW isolation valves for DW-CE-2A (and DW-CE-2B) to the Portal J / MEL and applicable station documentation (e.g., procedures and drawings). Reference CVI DWG 218-03,7183. | 02-00-DW-CE-2A
392731 | CR | 20190430 | CAQ | D | Computer Point L108 Found Out of Tolerance | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02136554-01, step 7.2.21, computer point L108 was found out of tolerance low at the 0 SCFM point (0-7425) at -1306 SCFM. All other data points were in tolerance. <I> **** Actions Taken **** Per step 7.2.22b, notified Supervisor and Operations. Wrote CR/WR to document. <N> **** Equipment Description **** 525 RW
392732 | CR | 20190430 |  | 4 | T-DOOR-T205 TG471 hallway door is damaged | N | N |  | N | YES | <D> **** Detailed Description **** T-DOOR-T205, the TG471 west side hallway door has become badly damaged from scaffold cart hitting the lower inside hinge area; the door skin is cracking at the hinge. as of now it will close but if the condition worsens it may not function properly. This door is not a Plant Fire Door or a HELB Barrier, but it does have a Security latch on it on the hallway side of the door. See pictures on the EDMS screen <N> Cross referenced WR 29148350. | 02-00-T-DOOR-T205
392738 | CR | 20190430 | CAQ | D | FP-P-2A/2B splash guards | N | Y |  | N | YES | <D> **** Detailed Description **** Splash guards for FP-P-2A and 2B not installed correctly and are leaning.(NRC find) <I> **** Actions Taken **** Informed MCR, initiated CR <N> **** Equipment Description **** Splash guard | 02-00-FP-P-2A,02-00-FP-P-2B
392739 | CR | 20190430 |  | 4 | Circ Water Basin Inlet Netting | N | N |  | N | YES | <D> **** Detailed Description **** There are holes in the Circ Water Basin netting. (NRC find) <I> **** Actions Taken **** Informed MCR and initiated CR Cross referenced WR 29148351. <N> **** Equipment Description **** Netting over Circ Water Basin inlet
392741 | CR | 20190430 | CAQ | D | Received Rod Accumulator Trouble Alarm for CRD-HCU-5427 | Y | N |  | N | YES | <C> CR reopened to cross reference additional WP 02082590. marked completion required box, then taken back to complete <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-5427 due to moisture. TREND | 02-00-CRD-HCU-5427
392742 | CR | 20190430 | CAQ | D | TIP purge secured for GT 24 hours | Y | Y |  | N | YES | <D> **** Detailed Description **** The TIP purge was isolated on 4/28/2019 to support TIP drive E work. SOP-TIP-PURGE requires a CR to be generated if the purge is isolated for more than 24 hours. <I> **** Actions Taken **** None <N> **** Equipment Description **** TIP purge system This was an expected condition based on TIP-DET-3E replacment on-going. Moisture build-up in the tubes can be removed with a complete purge upon completion of detector replacement | 02-00-TIP-DRVE-1E
392743 | CR | 20190501 | CAQ | D | E-CB-N1/3 failed to rack out with the remote racking tool | Y | Y |  | N | YES | <D> **** Detailed Description **** E-CB-N1/3 failed to rack out with the remote racking tool. After investigation, it appeared that it was rubbing on a metal edge on the right side of the cabinet. Manual racking was successful. <I> **** Actions Taken **** Manually racked out after investigation. | 02-00-E-CB-N1/3
392744 | CR | 20190501 |  | 4 | 3 Pieces of M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** 3 Pieces of M&TE found OOT & adjusted within specs. None were used during Calibration cycles. Calcode #C012249 Temp. Calibrator- model 3605. DEF #7015A written. Calcode #0063321 Nucon Press. Detector- model PD-C. DEF #7016A written. Calcode #0065288 Hytorc Hyd. Torque Wrench- model HY-1MXT. DEF #7017A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only. <N> CR reopened to edit severity.
392745 | CR | 20190501 | CAQ | D | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065246 Fluke High Volt Probe- model 80PK-40 As founds passed. Now Rejected- Open Insulation @ Banana Connector. DEF #7018A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
392746 | CR | 20190501 | CAQ | D | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #C011757 Fluke Dig. Multimeter- model 8060A found OOT & adjusted within specs. Not used in the OOT Range at 100 mV AC. No Plant Impact. DEF #7019A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
392775 | CR | 20190501 |  | 3 | EWP - Task Authorization and closeout |  |  |  | N | NO | <D> **** Detailed Description **** 02134902-08 HC D-RWCU-V-213A-001 - could not be authorized or taken to finished. The 'authorize' option was greyed out in Operations View. <N> The WO was able to be authorized and taken to finished last night. It looks like when Ops tried to authorize it yesterday morning, there was still an RWP Hold. After that, the CR was written at 0526. At 0559 the RWP Hold was released. I am not sure that they attempted to authorize following the release of the hold. No further action needed.
392776 | CR | 20190501 | CAQ | D | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065604 Heise Pressure Calibrator- model PTE-1 found OOT & adjusted within specs. Not used at the 10VDC Range. DEF #7020A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
392777 | CR | 20190501 |  | 3 | Drawings not updated after modifications |  |  |  | N | NO | <D> **** Detailed Description **** This is not an equipment issue, it is a actual plant to paper plant configuration issue. Modifications that spared out MOC switch S3 were performed to the E-CB-N1/2, E-CB -S/2, and E-CB-S/3 switchgear cubicles. The mods required wiring changes such as moving leads from switch S3 to switch S2. The switch was also mechanically detached from the MOC assembly by removing a link between switches S2 and S3. The associated drawings for the breakers have not been updated. Recommend assignment to AR-DESDFTE.
392778 | CR | 20190501 |  | 4 | DLR ran through the x-ray |  |  |  | N | NO | <D> **** Detailed Description **** On 5-1-19 an individual ran their DLR through the x-ray machine coming into the PAAP. The individual had removed their jacket and when doing so had folded their jacket with the badge in it, when it passed the x-ray thatâ€™s when they had noticed that the DLR went through. <I> **** Actions Taken **** Coaching on the proper practice to keep the DLR on you at all times. <N> Williams Plant Services.
392780 | CR | 20190501 |  | 4 | broken cover screw on light fixture in RHR-HX-1A room | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Type V8 fixture in RHR-HX-1A room has a broken screw. There are supposed to be four screws that hold the existing fixture in place, however, only three are holding at this time. The light fixture is to be replaced, per WO# 02130025-01, with LED style which are heavier than the existing incandescent type V8. The mounting box will need to be replaced to so that all four mounting holes can help support the new LED fixture. The light fixture is fed from E-PNL-3DA-C-7. <I> **** Actions Taken **** Notified Supervision and generate CR/WR non-essential lighting. <N> **** Equipment Description **** V8 fixture at RX 548 J3/9.4
392784 | CR | 20190501 |  | 4 | Ingersollrand forklift tilt bleedoff |  |  |  | N | NO | <D> **** Detailed Description **** While unloading a vendors truck with the Ingersollrand forklift the forks started to bleed off. <I> **** Actions Taken **** The workers stopped the unloading process and tagged the forklift out. Project supervision turned this over to Facilities for inspection.
392785 | CR | 20190501 |  | 3 | PO 351873 L/I 3 CID 37626-1 Received Damaged from Vendor |  |  |  | N | NO | <D> **** Detailed Description **** During the receiving process of PO 351873 L/I 3 CID 37626-1 It was discovered to be damaged due to poor packaging from the vendor. A screw used to fabricate the shipping crate came in contact with the Valve Seat and scored/Scraped the surface of the item which may effect it's function. Vendor has been notified and OSDD 15742 has been created to document and track resolution. Reccomend item be looked at by valve team to evaluate useability prior to sending back to vendor. <I> **** Actions Taken **** Notified Vendor. OSDD 15742 created to document and track resolution. Pursuing repair or replacement. Requesting valve team Support to support.
392786 | CR | 20190501 | CAQ | D | Security CCTV 46 | N | N |  | N | YES | <D> **** Detailed Description **** SEC-CCTV-46 is not working as designed. <I> **** Actions Taken **** Contacted electricians for support and generated CR/WR. Compensatory measures are in place. | 02-00-SEC-CCTV-ISFSI/46
392787 | CR | 20190501 |  | 3 | (NRC) CWPH area confined space signs in degraded condition | N | N |  | N | NO | <D> **** Detailed Description **** confined space DANGER signs located at the multiple manhole entry points are in degraded condition. Some have been temporarly attached to the covers with tape others are almost illegible. recommend permentaly adhearing signs that are in good condition and replacing illegible signs with a quality metal sign. <I> **** Actions Taken **** initially multiple signs were held in position with a rock, OPS4 replaced the rock with tape
392789 | CR | 20190501 |  | 3 | Tag EPN does not match equipment it is hung on |  |  |  | N | NO | <D> **** Detailed Description **** When hanging C-WELDRCPT-R24-001, tag 913 was supposed to be hung on E-DISC-PPF10/2/9/1. When the EO hanging tags was at the receptacle, another caution tag was found already hanging on the disconnect switch. The EPN on the tag is E-CONN-F10/2/9/1/WELD and is associated with clearance C -MT-ELEV-2TPWR-001. This component is an electrical disconnect used for temporary power during outages. It consists of a box containing the disconnect switch with a weld receptacle on the bottom. The disconnect is labeled E-DISC-PPF10/2/9/1. There is no label in the field with the EPN E-CONN-F10/2/9/1/WELD. <I> **** Actions Taken **** Suspended hanging C-WELDRCPT-R24-001. Notified SM, and Ops Crew Manager. <N> Operations conducted a stand down with all operating crews. No further action will be required and will included in department trending
392790 | CR | 20190501 | CAQ | D | ISFSI Cask 29 fault on ISFSI Display | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of OSP-SFS-D101 on 5/1/2019, Cask 29 shows a fault. This requires a WR written for the cask and fault. <I> **** Actions Taken **** Informed MCR. Initiated CR/WR | 02-00-SFS-STORM-029
392793 | CR | 20190501 |  | 4 | DES-2-5 does not align with new SDP |  |  |  | N | NO | <D> **** Detailed Description **** DES-2-5 Preparation and Approval of Equipment Modification Specifications gives direction to process Equipment Modification Specifications under DES-2-1, DES-2-7, and DES-2-10 which are under the old design process. This procedure should be updated to reflect the new Standard Design Process per IP-ENG-001 and ENG-DES-50 Interface Procedure for IP-ENG-001 Standard Design Process. <I> **** Actions Taken **** Spoke to design lead and determined procedure was expected to be cancelled under new design process. Recommend action to Design Engineering to cancel procedure. <N> Duplicate of the issue being corrected by AR-CR 388083. Close this AR-CR to AR-CR 388083.
392794 | CR | 20190501 | CAQ | C | RWCU-V-4 S5 packing leak. | Y | Y |  | N | YES | <D> **** Detailed Description **** Investigation of increased reactor building activity per WR 29148233 revealed an S5 packing leak from RWCU-V-4. RWCU -V-4 is having the stem replaced under WO 02120341-14, which will repack the valve. Just need to ensure that the task is not cancelled. <N> **** Equipment Description **** RB 522 RWCU pump room mezz . This CR was reopened by Licensing request to update the RWCU V 4 OCC3 document. See email from licensing for the request. Update completed. SDM 7/8/19 | 02-00-RWCU-V-4
392798 | CR | 20190501 |  | 4 | Door T-109 knob failure | N | N |  | N | YES | <D> T-109 door is the main entrance to the Turbine from the 441 corridor west end. The knob will not rotate counter clockwise and is hard to rotate clockwise from the corridor side. Furthure damage will occur during outage if not fixed. <I> SSS notified, CR written, Sgt. notified. <N> Door T-109, 441 west corridor entrance to Turbine.
392799 | CR | 20190501 |  | 4 | Monthly Chem Inspection OPS4 Truck |  |  |  | N | NO | <D> **** Detailed Description **** The OPS4 pickup is a designated chemical storage location. During monthly inspection found a container of hand sanitizer laying on its side and small amount of leakage. Also found several AA size batteries that were visibly degraded/expired. Both items above were found in the glove box. <I> **** Actions Taken **** Removed and disposed of the batteries in a battery recycle bin. Removed the hand sanitizer and set in upright/secure location. Cleaned up small amount of sanitizer that had spilled. Findings documented on inspection form 26615 and routed to Ops AOM. No further actions are necessary.
392800 | CR | 20190501 |  | 3 | 02073782 not worked as scheduled |  |  |  | N | NO | <D> **** Detailed Description **** WO 02073782 COND-42-3C3C TEST AND INSPECT STARTER was not worked as scheduled do to risk evaluation concerns. This work deenergizes the Auxiliary Oil Pump for COND-P-2A. The initial Risk evaluation identified the PMT as High risk Nuclear if done with the pump on line. The inspection itself was deemed low risk nuclear. Consequently the work was scheduled for 4/30/19 and the PMT was scheduled for 5/10/19, when COND-P-2A would be removed from service as part of the shut down for R-24.. This CR should be assigned to Ops-WM to provide clarification the extent to which risk determination needs to consider coincidental circumstances. It should also be used to identify any desired PMID changes (UCR F vice UCR M). See EDMS for full description. <I> **** Actions Taken **** Rescheduled the work to occur after COND-P-2A is removed from service as a no risk solution.
392801 | CR | 20190501 |  | 3 | Evaluate use of basic rigging certificate as prerequisite |  |  |  | N | NO | <D> **** Detailed Description **** The use of the basic rigging certificate (ME000650) as a prerequisite to various specialty rigging qualifications is error likely. The certificate does not expire, nor does it turn red when individual qualifications within basic rigging (MEDX or CNAX) are not refreshed. This CR is to drive evaluation of a better structure for the associated qualifications to remove the human element of certificate removal. Ideally, the system automatically pulls the certificate when any of the supporting training goes red. <I> **** Actions Taken **** Notified Training leadership and Site Rigging Coordinator. Initiated CR. * Recommend owed-to AR-TRNMGT as Severity Level 3
392802 | CR | 20190501 |  | 3 | PPM 10.25.209 and main xfmr cooler rep WOs have wrong EPNs |  |  |  | N | YES | <D> **** Detailed Description **** Section 2 and Figure 2 of PPM 10.25.209 needs updated with correct valve EPNs for the cooler groups on the main transformers. The procedure should be updated along with the WOs for the cooler replacements which also has the incorrect labels for each valve. Reference SOP-ELEC -500KV-LU for the correct valve EPNs. Reference WOs 02115677 (scheduled for R24) 02115678 (Scheduled for R24) 02115669 (Scheduled for R24) <I> **** Actions Taken **** 1) WOs should be updated to show the correct EPNs listed on valves in field so the work can be completed. 2) Procedure should be updated to reflect the correct valve EPNs. | 02-00-E-TR-M1,02-00-E-TR-M2,02-00-E-TR-M3
392803 | CR | 20190501 |  | 3 | Condensate pump expansion joints | N | N |  | N | YES | <D> **** Detailed Description **** During external inspection PM WO 02113404-01 COND-EJ -2A/2B/2C under WO 02113404 it was identified that COND -EJ-2A and COND-EJ-2C have portions that have partially collapsed inward with evidence of surface cracking and may warrant replacement prior to the Planned 6 YR PM replacement WOs. <I> **** Actions Taken **** Generated CR. Recommend further review by Engineering/manufacturer based on current as found conditions. Updated EDMS with Pictures taken during the inspection. | 02-00-COND-EJ-2A,02-00-COND-EJ-2C
392804 | CR | 20190501 | CAQ | D | Possible Test Equipment Problem | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02136554-01, could not obtain 226 SLPM during flow test. Only able to get approximately 120SLPM. Suspect test equipment problem. <I> **** Actions Taken **** Informed Supervisor and Operations. Turned test equipment flow meter into Calibration Lab to be calibrated.
392805 | CR | 20190501 |  | 3 | Wiring to E-P-M1/P1 failure analysis results | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02140218 it was discovered that one of the phases for E-P-M1/P1 was grounded. This cooler trip was identified under AR-CR 390870. A failure analysis was conducted by the materials group and the failure was identified to be associated with rubbing were due to vibration and that this type of vibration can occur in sharp conduit bends on long free spans. The installation was reviewed and it appears this condition is similar to the failures of transformer wiring in 2000 (PER 200-2578) and 2003 (203-2578) in which a wire for the CTs for main transformers went to ground and caused a reactor SCRAM. The wiring for the CTs on the main transformers is similar to the wiring installation that was on the old transformers in which two transformer trips occurred on different units. The purpose of this CR is to document the condition and to perform field inspections of each conduit fitting for the main transformers to determine if rubbing is occurring inside of the other conduits starting with CT wiring since it is the same type of wire as the cooler groups. This can be a very simple inspection because during the warranty repairs ABB is going to tighten each conduit fitting and this could be incorporated into their work with minimal impacts if determined to be a priority based on past experience. See EDMS for report from J. Lasalle on failed wiring to pump motor. Reference: PER 200-1043 PER 203-2578 <I> **** Actions Taken **** This installation could impact the other Main Transformers | 02-00-E-TR-M1,02-00-E-TR-M2,02-00-E-TR-M3
392806 | CR | 20190501 | CAQ | C | Clearance C-RHR-V-73A-003A should have had a 50.59 review |  |  |  | N | NO | <D> **** Detailed Description **** It was determined that Clearance C-RHR-V-73A-003A should have had a 50.59 review prior to installation, during completion of action 390192-05 to review C-RHR-V-73A-003A. This clearance is for configuration control for opening RHR-42-7BB5D and for clearing the RHR-A OOS alarm by removing RHR-RLY-80/V73A when RHR-V-73A stuck open and received a ground on MC-7BB (CR 387795). The removal of the relay to clear the RHR-A OOS alarm is a temporary alteration to support operations and should have had a 50.59 review prior to installation. The clearance was removed on 3/31/19, therefore this temporary alteration no longer exists. <I> **** Actions Taken **** Discussed with 50.59 SME and supervisor
392807 | CR | 20190502 | CAQ | C | E-CB-N1/3 Stab finger Nonconformity | Y | Y |  | N | YES | <C> CR reopened by decision of the MRT. Change to SECOMP. <D> **** Detailed Description **** After the completing WO 0212643401 E-CB-N1/3 INVESTIGATION, the operator racking out E-CB-N1/3 notice it lurch out a bit at the end of its stroke (breaker was racked in and out 4 time for the investigation). E-CB-N1/3 was pulled out of the cubical SM-3 and inspected, it was noticed that a finger on one of the stabs was not in conformity with the others. (UTC 430488, MODEL 50-DHP-VR350 ) <I> **** Actions Taken **** Supervision, CRS, SM, WWM and the back shift on call engineer was notified. This CR was written to document issue. Photo in WO 0212643401 E-CB-N1/3 INVESTIGATION <N> **** Equipment Description **** TB471' SM-3 | 02-00-E-CB-N1/3
392808 | CR | 20190502 | CAQ | D | MW 01 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** MW 01 is not functioning as designed and requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Compensatory measures initiated. Security Supervision notified. CR/WR generated. | 02-00-SEC-MW-1RA
392809 | CR | 20190502 |  | 4 | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065145 Mitutoyo Dial Caliper- model 505-675 6" was found OOT. Not used during Calibration cycle. Rejected- ID jaws bent/ chipped. Dial lock broken. DEF #7022A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
392832 | CR | 20190502 |  |  | Door T-109 knob failure | N | N |  | N | YES | <D> T-109 door is the main entrance to the Turbine from the 441 corridor west end. The knob will not rotate counter clockwise and is hard to rotate clockwise from the corridor side. Furthure damage will occur during outage if not fixed. <I> SSS notified, CR written, Sgt. notified. <N> Door T-109, 441 west corridor entrance to Turbine. | 02-00-T-DOOR-T109
392833 | CR | 20190502 |  | 3 | E-EXC-1, Main exciter should be ventilated during shutdown |  |  |  | N | YES | <D> **** Detailed Description **** CR 392419 documented an H2 leakage alarm received in the main control room. The alarm was from TG-H2IS-1 channel 4 and indicated hydrogen was detected in the exciter doghouse. Operations inspected and determined there was no H2 in the doghouse, engineering later walked down the doghouse and verified there was no leakage. Operations established a once per shift check to monitor the doghouse for hydrogen and OSCR 392442 was processed to add inspection and calibration of TG-H2IS-1 into the R24 scope to ensure the monitor was functional coming out of the outage. . With TG-H2IS-1 channel 4 not functioning there is no continuous monitoring of H2 in the exciter doghouse. The main generator radial lead seals are a known source of potential H2 leakage into the doghouse and will be replaced with the OEM recommended seal in R24 to prevent future leakage. The radial lead seals are currently not leaking but after turbine trip as the rotating element comes to a stop the centrifugal forces applying pressure to the seal and maintain the seal will not be present and the seals may relax allowing hydrogen to leak into the doghouse enclosure. With TG-H2IS-1 out of service this condition would potentially go unmonitored. Recommend opening the exciter doghouse north and south doors closest to the generator and placing a fan at one side blowing air through the opening prior to tripping the main generator to ensure the area is properly ventilated. <I> **** Actions Taken **** Discussed with supervisor and operations, initiated CR to document condition and track recommended actions | 02-00-E-EXC-1,02-00-TG-H2IS-1
392834 | CR | 20190502 |  | 3 | OSP-FLEX-A101 procedure needs to revised |  |  |  | N | NO | <D> **** Detailed Description **** After discussing with Tim Hancook, it was made clear that the 1 year performance of OSP-FLAX-A101 does satisfy the 6 month requirment to run the pump. The 6 month run is not required by the LCS and was only established to agree with industry best practice. Please add statement to purpose section specifying that performance of the 1 year section does take crewdit for the 6 month requirment. <I> **** Actions Taken **** Wrote CR
392835 | CR | 20190502 |  | 4 | MT-CRA-1 | N | N |  | N | YES | <D> **** Detailed Description **** There are approximately one dozen drops of oil beneath the trolley. The crane had been sitting in the same location since the end of shift yesterday. <I> **** Actions Taken **** Contacted the Turbine Project Manager and initiated this CR. <N> **** Equipment Description **** 501 Turbine Building | 02-00-MT-CRA-1
392838 | CR | 20190502 |  | 3 | Procedure update for RPS-42-MG2/MS1 and MG1/MS1 replacement |  |  |  | N | NO | <D> **** Detailed Description **** During the RPS-MG-2 maintenance window the motor starter RPS-42-MG2/MS1 was replaced, but the overloads were not properly set. This resulted in a trip of the MG when restarted (see CR 00392498). The work instructions for replacement of RPS-42-MG2/MS1 do not contain steps to verify that the overload is set to 110% per E528-47A. Steps need to be added in the work instructions to ensure that overloads are properly set per design for motor starters RPS-42-MG1/MS1 and RPS-42-MG1/MS2 whenever the starters are replaced or components of the starters are replaced. <I> **** Actions Taken **** None <N> The TOL dial was already reset to 110% during the EFIN activities in the field per E528-47A. This CR is generated for future reference so if the 42 is replaced again, or a coil or TOL that there are steps to verify that the TOL is set correctly before buttoning up and attempting to start the MG.
392839 | CR | 20190502 |  | 4 | RRA-FN-30 was found off. | N | N |  | N | NO | <D> **** Detailed Description **** RRA-FN-30 was found off. When going out into field to hang D-RRA-FN-30 -004, RRA -FN-30 was found off with control switch in OFF, reason unknown. <I> **** Actions Taken **** Informed CRS and hung tags Contacted HP regarding this fan and air sampler. HP indicated this sampler is no longer used. Recommend evaluating this fan for permanent removal from service. <O> Contacted HP regarding this fan and air sampler. HP indicated this sampler is no longer used. Recommend evaluating this fan for permanent removal from service. . AR EVAL 392942 created and xref.
392843 | CR | 20190502 |  | 3 | Circuit #12 in HT-HTP-FP/6 has 2 EPN's on the prints. |  |  |  | N | NO | <D> **** Detailed Description **** 322-00,34,12 says the EPN for circuit #12 in HT-HTP-FP/6 is HT-CB-FP6/A. E937-10 says the EPN for circuit #12 in HT -HTP-FP/6 is HT-CB-FP6/12. Locally this circuit breaker is labeled â€œAâ€ because it is the circuit breaker for the alarm circuit. HT-CB-FP6/A does not exist in Portal J. HT-CB -FP6/12 does exist in Portal J. 322-00,34,12 and E937-10 need to have the same EPN for circuit #12 in HT-HTP-FP/6. Also, if it is decided that this EPN is HT-CB-FP/6/12 then the label needs to be changed on circuit #12 in HT-HTP -FP/6.
392844 | CR | 20190502 |  | 3 | Fire procedures not being revised . |  |  |  | N | NO | <D> **** Detailed Description **** Many PPM's need to be revised, Red lined copies were submitted and changes were made on some , but not the changes asked for in the red line copies . CR 387713 was written , changes were made and implimented ( Not what was asked for ) without the worker looking at the revision
392845 | CR | 20190502 |  | 4 | (Non EN/CGS) ASSET RETURNED WITH OLD CAL LABEL (COMMERCIAL) |  |  |  | N | NO | <D> **** Detailed Description **** (Non EN/CGS) ASSET 776-13-01-003A RETURNED TO CUSTOMER WITH OLD CALIBRATION LABEL In-Depth Evaluation: CUSTOMER EMAILED 05/02/2019 THAT CALIBRATION STICKER WAS NOT CURRENT <I> **** Actions Taken **** RESPONDED TO CUSTOMER EMAIL THAT NEW STICKER WILL ARRIVE WITH NEXT SHIPMENT
392848 | CR | 20190502 | CAQ | C | 15.1.16 PM Work orders auto advancing to Closed Status. |  |  |  | N | NO | <D> **** Detailed Description **** During review of previous PM WOs against PPM 15.1.16, PMID 16370-01, for Suppression System Checks it was identified that after the H/Ops Reviews are being completed to verify all requirements have been completed, the WOTs in Dataglance are advancing to Closed status as part of the work flow. Typically these WOTs will stay in the completion tab of Dataglance or the Supervisor review bin to document work package completion prior to getting statused past Finished status after the H/OPS status. All recent surveillances have had the proper Operations reviews however the addiitional assigned reviewer Field and Fire Marshall review (Including the FMR soft hold) of the previous performance prior to performing the next upcoming performance has not been documented. No issue with sucessful completion of past performances from an Operations Review standpoint or formal PM completion dates. <I> **** Actions Taken **** Generated CR. Recommend assignment to Dataglance team to review PM Model WO 00DGB3 for how sequenced in Dataglance. Note, the last WO listed on the Xref tab had the FMR hold removed in Asset Suite to support going to Complete status and a hard copy cover sheet with the Assigned Reviewer and the FMR was submitted to records with the required signatures. <N> Note, PM WO 02113168-01 for the current PM Work order for perforance of 15.1.16 is Field work complete as of today. . Due date moved to 08/31/19 to allow testing of code changes. . Due date extended to 10/30/19, this program change is now ready for testing. Delay in testing was due to the PM Generation Batch program not working and ensuring the previous change to the TIDWOBAK program was not associated with the issue.
392849 | CR | 20190502 | CAQ | C | update EWD15E-047A |  |  |  | N | YES | <D> **** Detailed Description **** Engineering update EWC-15E-047A to add OL on all 3 phases of RPS-42-MG2/MS1 | 02-00-RPS-42-MG2/MS1
392850 | CR | 20190502 |  | 3 | EPNs not cross-referenced to EMS |  |  |  | N | NO | <D> **** Detailed Description **** This is an administrative issue only. It was discovered that a number of Equipment Modification Specification (EMS) documents were lacking the appropriate EPN cross reference. The EPN cross reference is used by Procurement Engineering to determine if there are any relevant EMS changes that need to be considered during procurement and/or substitution evaluations. Recommend the appropriate EPN cross references get added to the affected EMS documents. See EDMS for a list of ISSUED EMS that contain no EPN cross references.
392853 | CR | 20190502 |  | 3 | DES-2-5 enhancement |  |  |  | N | NO | <D> **** Detailed Description **** This is a documentation issue only. DES-2-5 currently does not contain any guidance to ensure EPN cross references are added to new EMS documents. The EPN cross reference is used by Procurement Engineering to determine if there are any relevant EMS changes that need to be considered during procurement and/or substitution evaluations. See EDMS for a suggested markup of DES-2-5.
392854 | CR | 20190502 |  | 3 | Planning update models for WO 02105274 and sister component |  |  |  | N | NO | <D> **** Detailed Description **** Componant has three OL's. Add drawings E528-47A (see note 6) to WO's. Ensure steps are added to set OL to 110 (not in the OL/starter procedure. Work was performed and failed PMT, OL tripped. Had to rehang tags and set OL to 110. OE/previous history shows that the same thing happened perviously per WO 02005022-01. The two MG motors/fly wheels draw too nuch current so the OL's need to be set at 110 so they do not trip. There was not any thing in the instructions to ensure the OL were set at 110. The procedure is a generic type procedure which has you have the OL's at 100, so the instructions should have you set the OL's at 110 for these specific EPN's. E528-47A has a note which states OL setting is at 110.
392857 | CR | 20190502 |  | 3 | Radioactive Sealand Container Requires Repair |  |  |  | N | NO | <D> **** Detailed Description **** Empty Framatome Sealand shipping container #9280010 has a 24â€ split seam along one side of its top edges. RP was contacted and concurred with the action taken to temporarily seal the split. The container currently resides in a temporary RMA outside the power block south of Building 62. The seam must be properly repaired before the container can be used to ship radioactive material off site. <I> **** Actions Taken **** 1. RP Contacted 2. Container has been temporarily repaired
392858 | CR | 20190502 |  | 4 | E-LP-5AC-27 Frequent Trip | N | N |  | N | YES | <D> **** Detailed Description **** The OPS production office printer and Production Manager computer are powered from E-LP-5AC circuit 27. This circuit breaker has tripped 3 times in the first 2 hours of nightshift. <I> **** Actions Taken **** Moved the Electrical production computers 120 VAC plug to a different ciruit. Moved the temporary cooler 120 VAC plug in the GSB lunchroom to a different circuit. | 02-00-E-LP-5AC
392859 | CR | 20190502 |  | 3 | Skype for Business Not Working in OPS Production Center |  |  |  | N | YES | <D> **** Detailed Description **** Several of the computers in the production center cannot sign into Skype For Business. This is a necessary tool for communication in the outage and needs to be corrected. <I> **** Actions Taken **** Informed control room that we cannot communicate via Skype. <N> **** Equipment Description **** Skype For Business Application in the OPS Production Center
392860 | CR | 20190502 |  | 4 | E-DISC-7CA5BR disconnect will not close. | N | N |  | N | YES | <D> **** Detailed Description **** E-DISC-7CA5BR is a spare disconnect and will be used for temporary power for MT-HOI-19C for R24. See WO 02112540. Disconnect would not close after several attempts when performing SOP-ELEC-BOP-TEMPPOWER step 5.11. 6a to check phase rotation. Recommend maintenance lube disconnect. | 02-00-E-DISC-7CA5BR
392861 | CR | 20190502 |  | 4 | Scaffold T471 West Blocks Lights; Leaves Area Under it dark |  |  |  | N | YES | <D> **** Detailed Description **** Scaffolding installed for WO 02112120 leaves are under it dark (T471 west around the H2 compressor). Safety first. request lighting be installed in the area. <I> **** Actions Taken **** wrote CR . Added this to the production priority list. <N> **** Equipment Description **** scaffolding installed t 471W
392862 | CR | 20190502 |  | 4 | East and West Transformer Yard Gates Unlocked |  |  |  | N | NO | <D> **** Detailed Description **** During night shift OPS4 logs, found both east and west gates of transformer yard unlocked. Found no workers inside the transformer yard and locked gates. This also occurred on 4/30/2019 (CR 392705). This needs to be addressed prior to outage when the transformer yard is more heavily relied upon for risk management. <I> **** Actions Taken **** Walked down transformer yard to look for workers and locked up gates. Notified Shift Manager.
392863 | CR | 20190503 | CAQ | D | CRD-HCU-2603 trouble alarm due to high water level | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble alarm H13-P603.A7 6-7 for CRD-HCU-2603. Alarm due to high water level and was drained per SOP-CRD-HCU to clear alarm. This HCU accumulator is on the list for online replacement due to multiple high water alarms (WO 02140415). Piston re -sealing per SOP-CRD-HCU was performed on 1/23/19 due to previous alarms on 12/26/18 & 1/22/19. <I> **** Actions Taken **** Notified the CRS and Shift Manager. Submitted CR and WR to document issue. | 02-00-CRD-HCU-2603
392864 | CR | 20190503 |  | 4 | ARP holder for P603 A-7 bottom had a failure |  |  |  | N | YES | <D> **** Detailed Description **** Plastic ARP holder for P603 A-7 lower shelf had a failure when the ARP binder was being returned to its normal resting place following an accumulator trouble alarm. Recommend either repairing ARP holder or fabrication of a new ARP holder. <I> **** Actions Taken **** Generated WR <N> **** Equipment Description **** Binder holder left hand side of P603
392872 | CR | 20190503 |  | 3 | VT-2 inspection needs evaluation | N | N |  | N | NO | <D> **** Detailed Description **** During recovery of RWCU-DM-1A a VT-2 inspection of 5 welds per WO 02134902-04 was required. Operations performed SOP-RWCU-DEMIN, section 5.15 to recover the demin and pressurize it to NOP and NOT to support these inspections, however 2 of the welds will not be subjected to reactor pressure (X1-1 and X1-2). These two welds are not subject to reactor pressure during normal operation of the demineralizer as this line is an air line for performing backwashes. The Shift Manager has amended the VT-2 examination data sheet to reflect that X1-1 and X1-2 will not be observed at this time and this CR has been generated to document the decision and request an ASMI engineer evaluation to determine the alternate means with which these two welds will be tested. PPM 8.7.3.A, P&L 3.3 states that areas of interest which are required to be pressure tested and VT-2 examined which are not subject to normal operating conditions during the pressure test require a separate pressure test by an alternate means. If a VT-2 test is required then this CR should drive WO instructions to test these joints using an alternate method. <I> **** Actions Taken **** CR written.
392873 | CR | 20190503 |  | 3 | SOP-ELEC-DIV2-TEMPPOWER Procedure update | N | N |  | N | NO | <D> **** Detailed Description **** Change step 5.27.11 to say "Inform CAS Operator that E-IN-4 will be powered by the battery momentarily while transferring power source. Power will not be lost in this process." <I> **** Actions Taken **** Wrote CR to clarify procedure for security to streamline temp power process.
392874 | CR | 20190503 |  | 4 | E-MC-7E GFIP bulb pushed into socket. | N | N |  | N | YES | <D> **** Detailed Description **** While on OPS 2 rounds, observed burned out light bulb ( 24E ) in GFIP for E-MC-7E. When an attempt was made to extract the bulb, it slipped back flush into the socket. Attempted to extract using duct tape, but the bulb slipped back further out of reach. ( about 1/16 " into socket ). Please remove bulb and repair socket if necessary. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** RW 487 E-MC-7E is non-safety related. Load sheds on an FA signal. | 02-00-E-MC-7E
392879 | CR | 20190503 |  | 3 | SOP-CW-OPS procedure enhanement |  |  |  | N | NO | <D> **** Detailed Description **** make step 5.10.1.h-k contiotional based using a Godwin pump. These steps are not required or desired. Also add step to 5.17 to verify inital setup has been completed per section 5.10.
392880 | CR | 20190503 |  | 3 | R24LL WO Godwin pump install needs I/C support task added |  |  |  | N | NO | <D> **** Detailed Description **** Need to add I/C support task to Godwin pump install WO 02111561 to set up ph and flow instruments per SOP-CW-OPS section 5.10 <N> Tasks added per assignemnt 02. No further actions
392881 | CR | 20190503 |  | 4 | RRC-TR-ASD/B/2 Pressure High Out of Spec | N | N |  | N | YES | <D> **** Detailed Description **** Pressure indicated for RRC-TR-ASD/B/2 read 4.2 psig with a maximum of 4 allowable per Operator Rounds. Previous night reading was 3.5 psig. <I> **** Actions Taken **** None | 02-00-RRC-TR-ASD/B/2
392882 | CR | 20190503 |  | 4 | ASD Resistivity Low for all four channels | N | N |  | N | YES | <D> **** Detailed Description **** ASD resistivity has crossed threshold per Operator Rounds and require filter change. 1A2: 4.39 MOHM, 1B1: 4.97 MOHM, 1A1: 4.58 MOHM, 1B2: 7.37 MOHM <I> **** Actions Taken **** Notified CRS | 02-00-GY-F-10A1,02-00-GY-F-10A2,02-00-GY-F-10B1,02-00-GY-F-10B2
392892 | CR | 20190504 |  | 4 | RPS Test Box Lamp Did Not Extinguish | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02134832-01, step 7.1.35a, the RPS Test Box lamp was not extinguished. <I> **** Actions Taken **** Per step 7.1.35b, recoreded issue on cover sheet and continued with surveillance. Per Precaution s and Limitations 4.8, wrote this CR to document. <N> **** Equipment Description **** 501 RW MCR
392893 | CR | 20190504 |  | 3 | WO 02115117 error, potentially impacting 1st 72hrs of R24 | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** WO 02115117 - Task 06, is scheduled for 5-13-19. Step 4.7 and 4.8 are believed to erroneously direct the operator to manipulate OPDS-RMS-3/3L. During Task prievew/walkdown it was identified that the correct EPN should be OPDS-RMS -3/3N. This appears to be a Copy/Paste error as OPDS-RMS -3/3L is manipulated in steps 4.5 and 4.6. These OPDS switches are located in the RW 525 Communications room, 2B submaster and Shift Manager permission required for entry. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RW 525 Comm room. 2B Sub Master key required for entry. Email sent to Ops Work Control to review and correct as needed.
392894 | CR | 20190504 |  | 3 | Recommend enhancement to PPM 1.3.84 |  |  |  | N | NO | <D> **** Detailed Description **** Recommend adding SOP-MSR-OPS P&L 4.2 information to PPM 1.3.84 Section 4.6, reactivity manipulations list. Per SOP-MSR-OPS transferring MSR 2nd stage excess steam from RFW-HX-6A/6B to the main condenser may result in a 1-2% power increase due to the feedwater temperature reduction.
392895 | CR | 20190504 | CAQ | D | ROD ACCUMULATOR TROUBLE on CRD-HCU-1823 due to hi water | Y | N |  | N | YES | <D> **** Detailed Description **** ROD ACCUMULATOR TROUBLE on CRD-HCU-1823 due to hi water level. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR, cleared alarm per SOP-CRD-HCU | 02-00-CRD-HCU-1823
392896 | CR | 20190504 |  | 3 | OUTAGE IMPACT-1.3.5 Trip Report file needs to be migrated |  |  |  | N | YES | <D> **** Detailed Description **** When histograms and real time plots were migrated from the corporate computers to PPC/TDAS, the PPM 1.3.5 scram trip report was not migrated. The old link to the trip report file as listed in the IA/STA turnover sheet no longer works (The EDNA view file is on \\domain1\dfs\UserDBApps\User Applicati ons\PDIS). Request computer engineering migrate the trip report file over to PPC/TDAS or restore the link off the corporate computer to support the upcoming scram for the outage. <I> **** Actions Taken **** Notified CRS. . Called Computer Engineer. Verified the trip report is still available on the coroporate LAN at T:\User_Applications\PDIS\ScramRpt.rtv | 02-00-PPC-COMP-8715
392897 | CR | 20190504 |  | 3 | Typographical errors in SOP-RFT-SHUTDOWN |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.6.8 incorrectly refers to SS-PCV-1A when it should refer to SS-PCV-1B (ref. M502-3). <I> **** Actions Taken **** Initiated CR
392898 | CR | 20190504 |  | 4 | SB offices are not being cooled, Request Engineering assist. |  |  |  | N | YES | <D> **** Detailed Description **** Production area in the GSB is not benefitting from the temporary air conditioning units installed. It appears the incoming air is overcoming any cooling of the area. Request engineer assistance in evaluating operating the SB ventilation in a different manner. Option one is to secure all ventilation, supply, exhaust and recirc fans. This would not remove the exhaust heat being discharged to the ceilings or provide the already poor exhaust from the bathrooms. Option two is to just secure the recirc and supply fans and leave the exhaust fans running. This removes the heat and provides bathroom ventilation. Option three would be to provide manipulation of the intake and recirc dampers for the Supply and recirc fans. Bring in more cool air at night and recirc during the heat of the day. This would do very little for dayshift after it started heating up. Please evaluate & provide assistance <I> **** Actions Taken **** Discussed with production supervisor the three option decided to expand the team and request engineering assistance. I belive OPTION 2 is the best bet. <N> **** Equipment Description **** SB HVAC
392899 | CR | 20190505 | CAQ | C | Loss of position indication CEP-V-4B | Y | N |  | N | YES | <D> **** Detailed Description **** While securing venting the wetwell per SOP-CN-CONT-VENT, the RO took the switch for CEP-V-4B to close per step 5.1.10.d.3 The OPEN indicating light went out, but the closed light never turned on <I> **** Actions Taken **** Engaged shift supervision. Position was verified CLOSED per GDS as well as locally | 02-00-CEP-V-4B
392900 | CR | 20190505 |  | 3 | RWCR Operator performed BW/PC on CFD, but missed 2 hour hold |  |  |  | N | YES | <D> **** Detailed Description **** The Radwaste Control Room Operator Performed a Backwash and Precoat on Cond-DM-1E. It was placed in service per the procedure. The Operator forgot about an Email, (the Schedule for CFD BW/PC), that instructs a 2 hour hold period prior to placing the CFD in service. The CFD was to be left in recirc on its hold pump for two hours in an attempt to mitigate the effects of the Low Quality Resin we are currently using. This resin has elevated Chlorides. The Vedor is working on the issue. Not performing the 2 hour hold can add more Chlorides to the system. <I> **** Actions Taken **** Contacted The Main Control Room and Chemistry. . The additional two-hour hold time is on the precoat sheet, but is not in SOP-CFD-BW/PC. | 02-00-COND-DM-1E
392901 | CR | 20190505 |  | 4 | E-CP-GEN/AUX drop 1-5 bulb broken in socket | N | N |  | N | YES | <D> **** Detailed Description **** While testing annunciators it was observed that a bulb was broken off in its socket at E-CP-GEN/AUX drop 1-5. Reference AR 334105 WR 29123254 for a similar issue. <I> **** Actions Taken **** Notified CRS and wrote CR. | 02-00-E-CP-GEN/AUX
392905 | CR | 20190505 |  | 3 | Evaluate SOP-CAVITY-FILL P&L4.2 for correct temperatures | N | N |  | N | NO | <D> **** Detailed Description **** SOP-CAVITY-FILL P&L 4.2 appears to contain a typo and an outdated temperature value. The temperature value in the second bullet may be outdated (reference SOP-FPC-OPS P&L 4.2 which states the temperature limit for 1 loop of FPC to be 175 degrees F). The Cavity Fill procedure still lists this limit as 155 degrees F, which was changed to 175 degrees back in 2016. The first bullet in SOP-CAVITY-FILL contains a typo: the temperature is listed as "150'F" vice 150 degrees F. <I> **** Actions Taken **** Notified production SRO and initiated this CR.
392906 | CR | 20190505 |  | 3 | MT-MTS-6B/3D administrative control | N | N |  | N | YES | <D> **** Detailed Description **** EC 17480 installed MT-MTS-6B/3D which requires administrative control and locking the switch in the E-MC -6B position during normal plant operation and is not required to be administratively controlled when shutdown. A lock goes through a hole in the sheet metal vice both the sheet metal and the handle. The lock can be negated by simply forcing the handle down without removing the lock. Drill a hole in line with the hole on the handle to place a lock. 2 similar transfer switches have holes drilled that prevent shifting the transfer switch unless removing the lock. The other 2 transfer switches have slightly more clearance for drilling holes. 1 switch has a provision to lock in either position by way of holes CGS drilled in addition to the center factory provided hole for placing a lock in the center â€œoffâ€ position, the other switch has 1 additional hole drilled besides the factory provided one. <I> **** Actions Taken **** Informed supervision so the current configuration can be evaluated and corrected if required, see pictures in EDMS file of all 3 transfer switches. | 02-00-MT-MTS-6B/3D
392907 | CR | 20190505 | CAQ | D | SEC-PAAP-IRE is not functioning as designed. | N | N |  | N | YES | <D> **** Detailed Description **** SEC-PAAP-IRE is not functioning as designed. Request Elect. Maintenance to investigate. Contact Security at 2185 <I> **** Actions Taken **** Compensatory measures initiated. CR/WR Generated | 02-00-SEC-IDS-PAAP/IR/E/M
392908 | CR | 20190505 |  | 4 | Loop cal of RWCU-RMC-606 could not be performed as written |  |  |  | N | YES | <C> CR reopened due to accidental cancellation. <D> **** Detailed Description **** During performance of loop cal of RWCU-RMC-606, (02142978 -03) could not perform because of locked in low pressure alarm, <I> **** Actions Taken **** Informed Ops, Maintenance & WWM, obtained Planner support to rev package and completed loop cal <N> **** Equipment Description **** W501 L0/13.5 | 02-00-RWCU-RMC-606
392909 | CR | 20190505 |  | 3 | RWCU-FCV-33 was sticky during loop cal | N | N |  | N | YES | <D> **** Detailed Description **** When stroking valve during loop cal, 02142978-03, RWCU -FCV-606 was sticky while opening and RWCU-RMC-606, controller spiked from 65% to 100% momentarilly on output indicator of the controller <I> **** Actions Taken **** informed ops, maintenance and WWM, need engineering to evaluate <N> **** Equipment Description **** W501 L0/13.5 | 02-00-RWCU-FCV-33,02-00-RWCU-RMC-606
392910 | CR | 20190505 | CAQ | D | Received P800.C4.2-5 XFMR TR-B TROUBLE alarm. | Y | N |  | N | YES | <D> **** Detailed Description **** Received P800.C4.2-5 XFMR TR-B TROUBLE alarm. OPs-4 reports the alarm is HI TANK PRESSURE 63P-H and TR-B pressure indicates ~5psig. <I> **** Actions Taken **** Reduced pressure per ABN-TRANSFORMER, alarm is clear | 02-00-E-TR-B
392911 | CR | 20190505 | CAQ | D | E-TR-7/73 pressure low. | Y | N |  | N | YES | <D> **** Detailed Description **** E-TR-7/73 pressure is about -0.1 psig. Please add Nitrogen to restore to normal band. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** RW 467 | 02-00-E-TR-7/73
392912 | CR | 20190505 |  | 3 | RPV Disassembly (PPM 10.3.21) minor editorial |  |  |  | N | NO | <D> **** Detailed Description **** Step 6.5.8.b directs verifying that the draining of the reference legs for RFW-DPT-17 and MS-LT-27 have been completed per 10.27.39. The reference section of 10.27.39 is Section 7.1, but it should read Section 7.8 of 10.27.39. <I> **** Actions Taken **** Wrote CR
392913 | CR | 20190505 |  | 4 | Grab sample Greater than 10% From Meter/Recorder For SP-27A | N | N |  | N | YES | <D> **** Detailed Description **** The grab sample for SP-27A is greater than 10% different than both the meter or recorder but still within 20%. Request I&C adjust Cond. element to match grab sample results. <I> **** Actions Taken **** CR and WR written. MCR/CRS/SM and chemistry supervision informed. | 02-00-S-CE-27A
392914 | CR | 20190505 |  | 3 | (R24 LL) Inconsistent Guidance on Removal of CRD Backfill |  |  |  | N | NO | <D> **** Detailed Description **** In PPM 3.2.1 Normal Plant Shutdown step 5.6.6 directs removal of the continuous backfill system from service per PPM 10.27.64. In OSP-RCS-C102 RPV Non-Critical Cooldown Surveillance step 7.3 directs removal of the continuous backfill system.Recommend the removal of backfill be removed from OSP-RCS-C102 so we avoid multiple procedures directing the same action and PPM 3.2.1 for plant shutdown is the overarching procedure. <I> **** Actions Taken **** wrote CR to drive procedure change - change not required before R24.
392915 | CR | 20190506 |  | 4 | (NRC) Sightglass Reading on DCW-TK-1B2 Close to Minimum Spec | Y | N |  | N | YES | <D> **** Detailed Description **** DCW-TK-1B2 is the coolant expansion tank for DG-ENG-1B2. Coolant level is read on a sightglass DCW-LG-10B2. The reading is required to be from +2 to +6 per the OPS 2 Diesel rounds. It currently appears to be at or near the minimum. It has been logged at +2 for the past 6 shifts. We need to refill DCW-HX-1B2 per SOP-DG-DCW. <I> **** Actions Taken **** Verified by field walkdown. Checked DG1 and DG2 DCW tank levels. | 02-00-DCW-TK-1B2
392916 | CR | 20190506 |  | 4 | Security MD-04 | N | N |  | N | YES | <D> **** Detailed Description **** Sec-MD-04 is not working as designed <I> **** Actions Taken **** Generated CR/WR, Contacted Shift Manager and Workweek Manager for support. | 02-00-SEC-MDET-4
392917 | CR | 20190506 |  | 3 | 3 of 4 VESDA Smoke Detector Power Supplies at Design Status |  |  |  | N | YES | <C> Changed from CAQ to non-CAQ in the MRT on 5/7/19. <D> **** Detailed Description **** FP-E/S-ISD/1, -ISD/2, -ISD/3 and -ISD/4 are all installed in the plant. VESDA is active. ASSETSUITE shows FP-E/S -ISD/1,-ISD/3 and -ISD/4 at "DESIGN" status and FP-E/S -ISD/2 at "ACTIVE" status. EC 16066 was accepted by OPS 2/25/19. This was discovered while researching a question from the NRC. This is a documentation issues vs an equipment issue, but Equipment Issue was marked "yes" to allow tying this CR to the correct EPN's. <I> **** Actions Taken **** No further immediate actions required. | 02-00-FP-E/S-ISD/1,02-00-FP-E/S-ISD/3,02-00-FP-E/S-ISD/4
392918 | CR | 20190506 | CAQ | C | (NRC) Enclosure Doors Not Fastened on VESDA Power Supplies | N | Y |  | N | YES | <D> **** Detailed Description **** FP-E/S-ISD/1, -ISD/2, -ISD/3 and -ISD/4 are power supplies for the VESDA system. The metal power supply enclosure boxes appear to have holes for sheet metal screws to hold the hinged door shut. None of the enclosures have retaining screws installed. The question is should the doors be captured closed? The -ISD/1 and -ISD/3 are fully closed. Due to some spring in the sheet metal doors, -ISD/2 and-ISD/4 are not fully closed. <I> **** Actions Taken **** Walked down in the field. Attached pictures to the EDMS of this CR. | 02-00-FP-E/S-ISD/1,02-00-FP-E/S-ISD/2,02-00-FP-E/S-ISD/3,02-00-FP-E/S-ISD/4
392919 | CR | 20190506 |  | 3 | ABN-TRANSFORMER Procedure Revision |  |  |  | N | NO | <D> **** Detailed Description **** ABN-TRANSFORMER Step 7.3.5.b.6) states 'Verify 63X light is extinguished (panel TR-B/T99941)." It should say 63XA vice 63X. There is no 63X light in panel TR-B/T99941. <I> **** Actions Taken **** Informed MCR. Wrote CR.
392920 | CR | 20190506 |  | 3 | (NRC) Question About Display on VESDA Control Panels | N | Y |  | N | YES | <D> **** Detailed Description **** FP-CP-ISD/1, -ISD/2, ISD/3 and ISD/4 have various LEDs on the front panel display. There was a question on what it means if there is an amber LED illuminated above the green "OK" LED on each panel. FP-CP-ISD/1 amber LED came on and off periodically, FP-CP-ISD/2 had just the green OK LED lit, FP-CP-ISD/3 has one amber LED above the "OK" lit and FP-CP-ISD/4 also had no amber LED lit above the lit green OK LED. Did NOT generate WR's at this time - request FP Engineering response on expected LED status on these panels. <I> **** Actions Taken **** Walked down, took photos and uploaded to EDMS. | 02-00-FP-CP-ISD/1,02-00-FP-CP-ISD/2,02-00-FP-CP-ISD/3,02-00-FP-CP-ISD/4
392921 | CR | 20190506 | CAQ | D | (NRC) DSA-V-714 Handle and Lock Nut are Loose | Y | N |  | N | YES | <D> **** Detailed Description **** The handwheel and lock nut which retains it are loose on the stem of DSA-V-714. The lock nut will not easily come off the stem, so there appears to be no concern that the handwheel will come off and impact any other SSC. <I> **** Actions Taken **** Walked down, verified other similar DSA valves nearby had handwheels and locknuts secured. | 02-00-DSA-V-714
392922 | CR | 20190506 |  | 3 | Incorrect ASSETSUITE Description for DSA-V-714, DSA-V-713 |  |  |  | N | NO | <D> **** Detailed Description **** Per the ASSETSUITE D030 "Name" field for DSA-V-714, it states "PS-34 Root Isolation." Per AED MED M512-1, DSA-V -747 is the DSA-PS-34 Root Isolation. DSA-V-714 is actually the root valve for hydraulic unloader DSA-V-724A. Likewise ASSETSUITE states DSA-V-713 is the DSA-PS-35 Root Isolation. It actually is the root for hydraulic unloader DSA-V-724B. <I> **** Actions Taken **** No further immediate actions required.
392923 | CR | 20190506 |  | 4 | Camera Cleaning |  |  |  | N | YES | <D> **** Detailed Description **** Cameras needed to be cleaned <N> **** Equipment Description **** Cameras needed to be cleaned inside the PA: PTZ 29 | 02-00-SEC-PTZM-1
392932 | CR | 20190506 |  | 3 | SOP-COND-SHUTDOWN needs a revision for COND drain. |  |  |  | N | NO | <D> **** Detailed Description **** OP-COND-SHUTDOWN was revised following R23 for lessons learned following the system draining for AR 339670-09. The procedure still references a precaution 3.4 which was removed in the latest revision of the procedure on pg 27 in a note above 5.9.15. It is unclear if this was intentional or if the level indicator is still allowed to be used and the precaution was inadvertently deleted. If this level indicator is not supposed to be used the procedure does not provide an alternate method of level indication at very low hotwell levels. Also 5.9.15 has a strike through it indicating it may have wanted to have deleted the entire step. <I> **** Actions Taken **** Wrote CR
392934 | CR | 20190506 |  | 4 | Faucet and toilet need repair at TSC. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The sink faucet in the ladies restroom and a toilet in the mens restroom need repaired. According to one witness the ladies restroom sink faucet has limited flow and water instead wants to escape through the handle connection. In the mens restroom the far toilet handle is difficult to flush and needs repaired. <I> **** Actions Taken **** Wrote CR. Generated work request. <N> **** Equipment Description **** See description above.
392938 | CR | 20190506 |  | 3 | AUX Boiler pH low - Action level | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The 5-5-19 Aux Boiler sample showed it was in spec for sulfites (corrosion inhibitor indication), but was just under the limit for pH (9.92) the lower limit is 10. Per SWP-CHE-02 it is an Action level. The Action is to restore chemical parameters as soon as possible. Chemistry will need to add NaOH for pH adjustment to maintain optimal corrosion control. The chemical addition can only be performed when the boiler is running. The add will be planned for the next run. <I> **** Actions Taken **** Notified Operations, Chemistry Supervision and System specialist.
392940 | CR | 20190506 |  | 3 | ABN-TRANSFORMER references a 63X light vs actual 63XA on N1, | N | N |  | N | NO | <D> **** Detailed Description **** ABN-TRANSFORMER steps 7.1.6.b.6 and 7.3.5.b.6 (For the Normal transformers) both reference the "63X" light. This light is labeled on the transformer alarm panels as "63XA". This CR is to be added on to the CR written for the same purpose on the Backup transformer (CR 392919) <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** ABN-TRANSFORMER
392941 | CR | 20190506 |  | 3 | Procedure R24 Enhancement to Cavity Fill |  |  |  | N | NO | <D> **** Detailed Description **** Recommend following improvements to Sect 5.5 Vessel Flood Up Using Main Condensate in SOP-COND-OPS. Add new step to â€œVerify COND-V-670 (Cond Supply to CRD) is tagged closed .â€ Add this new step before current step 5.5.1. . Also, add new step following Step 5.5.2.p to say â€œAdjust COND-LIC-1 or -2 as required to control Main Condenser Hotwell level within the desired band.â€
392943 | CR | 20190506 |  | 3 | Temporary Power installation issue | N | N |  | N | YES | <D> **** Detailed Description **** Switching CAS to alternate power supply fed from E-MC-5A in section 5.27 E-IN-4 was running on the battery and not being supplied by AC power. Supervision contacted and procedure was backed out of E-IN-4 was validated to be operating normally after backing out and restoring. The AC input was not available when attempting the transfer one possible cause is cleared fuse(s) installed in SEC-DISC -5A4C. <I> **** Actions Taken **** Contacted Engineering and supervision <N> Temp power being installed per SOP-ELEC-DIV2-TEMPPOWER, Sect 5.27. IN-4 left in normal configuration. | 02-00-SEC-DISC-5A4C
392948 | CR | 20190506 |  | 3 | Record Copy Not Controlled And Protected | N | N |  | N | NO | <D> **** Detailed Description **** A couple of aperture cards (record copy image of a drawing) were removed from the vault for a customer and one of them was not returned to the vault the same day which resulted in the record not being controlled and protected in accordance with ANSI-N45.2.9. It appears that the records were removed from the vault on 4/25/19 and it was discovered by the microfilm reader machine in the old Document Control area on 5/1/19 by another individual who promptly returned it to a RIM staff member. <I> **** Actions Taken **** Refiled the aperture card in the vault. <N> THe individual that provided support to the customer was coached on 5/9/19 and in order to strengthen the control of records, the Vault Sign-In Log has been updated with 3 new colums as follows: 1) Description/Count of Records Removed from Vault 2) Records Removed (RIM Initials) 3) Records Returned (RIM Initials). No further actions are required.
392949 | CR | 20190506 |  | 4 | incorrect EPN label on E-BU-SWS28/1 light fixture | N | N |  | N | NO | <D> **** Detailed Description **** while performing work to post Fire Impairment and stage portable lanterns for WO#02111307-05, electricians found fixture E-BU-SWS28/1 in the stairwell at the RX 606' dungeon. The label on the fixture Read "E-BU-SW28/1" fed from E-LP-6BA-E/2. According to EWD 46E-410, The fixture fed from this circuit is E-BU-SWS28/1. The Fire Impairment and lantern were staged and a label request will be generated to replace the existing label when EBUs get restored. <I> **** Actions Taken **** Notified Supervisor, Generate CR/WR and complete a label request form. <N> **** Equipment Description **** E-BU-SWS28/1 RX 576 dungeon
392950 | CR | 20190506 |  | 3 | Worker Back Injury Later Classified as OSHA Recordable | N | N |  | N | NO | <D> **** Detailed Description **** The worker back injury initially reported under CR 392590 on 25-APR-19 has been classified as an OSHA recordable injury by the worker's employer today, 06-MAY-19. <I> **** Actions Taken **** The contract tech rep notified his management chain and Industrial Safety. The Industrial safety rep notified Occupational Health. An event investigation has been initiated. This CR should remain open to capture the event investigation outcome.
392953 | CR | 20190506 |  |  | Security hydraulic arm failed during operation |  |  |  | N | YES | <D> **** Detailed Description **** Security barrier arm failed while being raised. No workers were in the area when this occurred. Damage unknown. Request facilities access and repair as needed. <I> **** Actions Taken **** Facilities notified, CR/WR generated, Supervision notified <N> **** Equipment Description **** Vehicle trap area | 02-00-SEC-GATE-26
392954 | CR | 20190506 |  | 3 | Cyber PM WO advances to late due date |  |  |  | N | NO | <D> Cyber PM WO for quarterly worked advanced to the late due date. Work had been completed for both a monthly and quarterly WO , but monthly WO was closed instead of the quarterly WO. <I> Validated work order tasks had been completed and then proceeded to close out the WO. Coaching provided and received by the individual who had made the error. . Found this CR at INPROG. Advanced to APPROVED.
392956 | CR | 20190506 |  | 4 | Red PI- Training Staffing | N | N |  | N | NO | <D> **** Detailed Description **** The EN Performance Indicator (PI) for Training Staffing is red for April 2019. This is due to having a vacancy for greater than 6 months. <I> **** Actions Taken **** PI is estimated to return to yellow in May 2019 as a new employee has started in May. This CR serves as a data point, recommend 4/Trend.
392957 | CR | 20190506 |  | 3 | Unable to complete temp power installation MT-HOI-19C | N | N |  | N | YES | <D> **** Detailed Description **** Work order 02112540-01 cannot be completed as scheduled. MT-DISC-3DA2CR disconnect cannot be closed when the plant is in mode(s) 1-3. Reference SOP-ELEC-BOP-TEMPPOWER step 5.11.8 sub step A. <I> **** Actions Taken **** Notified operations, work control and initiated this CR. <N> **** Equipment Description **** C561 AZ186/R42
392959 | CR | 20190506 |  | 4 | CW Scale Control Chem PMP CF-P-41A not pumping | N | N |  | N | YES | <D> **** Detailed Description **** Based on trending of the inventory in TK-41, CF-P-41A is not pumping. This was a new pump installed 5/2/19. Chemical samples test for residuals on 5/6/19 show levels below target concentrations which supports the inventory trend. <I> **** Actions Taken **** Change sheet was sent to the control room to change to manual feed of 60 gals/shift from TK-41 to the TSW weir. Chemistry Supervision informed of the residual levels and the move back to manual feed. <N> **** Equipment Description **** CWPH - CF-P-41A
392960 | CR | 20190506 | CAQ | D | Security hydraulic arm failed during operation | N | Y |  | N | YES | <D> **** Detailed Description **** Security barrier arm failed while being raised. No workers were in the area when this occurred. Damage unknown. Request facilities access and repair as needed. <I> **** Actions Taken **** Facilities notified, CR/WR generated, Supervision notified <N> **** Equipment Description **** Vehicle trap area Vehicle trap arm failed to the lowered position.
392962 | CR | 20190506 |  | 3 | CSP-DO-M101 needs to be updated | N | N |  | N | NO | <D> **** Detailed Description **** step 7.5.3 needs to be updated to reflect the current extention for the Herguth Labs. The new extention is X3049. The lab can still be reach through the main number listed in step 7.5.3 <I> **** Actions Taken **** Wrote CR. Informed Chem Supervision.
392963 | CR | 20190506 | CAQ | C | Discrepancies in FSAR Chapter 6 for Penetrations X-117/118 | N | N |  | N | NO | <D> **** Detailed Description **** FSAR Figure 6.2-39 labels two different valves as RHR-V-73A (one motor operated and one manual valve). Review of M521-1 suggests the manual valve should likely be RHR-V -173A. Additionally, Table 6.2-16 indicates that penetrations X-117/118 are included in Figure 6.2-51 (see page 6.2-95 of the FSAR). The correct figure for X-117/118 is Figure 6.2-39. Note that Figure 6.2-39 splits out a portion of the system drawing onto Figure 6.2-51. Recommend corrective action to fix the discrepancies identified above, as well as to do additional checking of overall accuracy/consistency of data presented pertinent to the RHR system contained on Figures 6.2-39, 6.2-51 and Table 6.2-16. There is no immediate regulatory significance of the noted discrepancies. <I> **** Actions Taken **** Briefed Reg Affairs management and wrote this CR.
392964 | CR | 20190506 | CAQ | B | SWP-SEC-12 Procedure Violation (HU Error) | N | N |  | N | NO | <C> Risk: Medium Cause: Clear Severity: B/NUCSEC document and correct. . This was changed at the MRT to requiring an investigation template to document what oversight is being provided by the leadership team. <D> **** Detailed Description **** A green badge driver conducting a delivery exited a running vehicle to enter a building in the PA. <I> **** Actions Taken **** Security personnel were on hand to respond to the vehicle and retrieve the driver. The vehicle was turned off and the individual was escorted offsite. Security Supervision notified. CR Generated. <N> The cause is that a vendor failed to comply with SPIP-SEC-06 section 4.1.2.h when they left their vehicle unattended and running inside the Protected Area (PA). As part of entering the PA instructions are given by a Nuclear Security Officer per SPIP-SEC-06 section 4.2.2.u â€œConfirm driver understands requirement to remove keys from vehicle while unattended in the Protected Area.â€ This action was conducted in this event and driver failed to adhere to requirements. Additionally, the driver was asked why they did not adhere to the requirements and they stated it was their first delivery onsite inside the PA and they just went in bldg 88 to get directions on where to park for delivery. Driver also stated it was common practice for the company to leave vehicle at idle and that he reverted to his old routine. CA have been reviewed and have been completed within CAP requirements, no further actions required.
392965 | CR | 20190506 |  | 4 | Declared Prohibited Item at Security Checkpoint | N | N |  | N | NO | <D> **** Detailed Description **** At approx. 1345 a Declared Prohibited item (2 Boxes of Alcohol)) was brought to the Security checkpoint by G.L.S. Delivery. The Alcohol was going to a different business on his route. Access was denied and the driver was coached not to bring alcohol when delivering to ENW. CR was generated. Benton County was contacted and did not respond. Shift Manager & Security Management notified. <I> **** Actions Taken **** Access was denied, CR was generated. Benton County was contacted and did not respond. Shift Manager & Security Management notified.
392967 | CR | 20190506 |  | 4 | MT-DISC-6BA1DL disconnect will not close. | N | N |  | N | YES | <D> **** Detailed Description **** MT-DISC-6BA1DL operation is required to supply temporary power to MT-HOI-18. See WO 02079277-39. Disconnect would not close to check phase rotation. Recommend maintenance lube disconnect. <I> **** Actions Taken **** Notified MCR and submitted CR | 02-00-MT-DISC-6BA1DL
392968 | CR | 20190506 |  | 3 | Lessons learned for outage/daily scheduling. |  |  |  | N | NO | <D> **** Detailed Description **** Work orders 02134618 (ESP-B11-Q101 QUARTERLY BATTERY TESTING 125 VDC E-B1-1) and 02134625 (ESP-B21-Q101 QUARTERLY BATTERY TESTING 250 VDC E-B2-1) were both scheduled in the work week of 05/06/19. These same surveillances are required prerequisites for 02111921 (ESP-B11-B101 24 MONTH BATTERY TEST) scheduled for 05/13/2019, and 02124385 (ESP-B21-F101 60 MONTH BATTERY TEST) scheduled for 05/15/19. Opportunities exist for scheduling PMâ€™s that can satisfy outage prerequisites. <I> **** Actions Taken **** Generated CR to document lessons learned. <N> The surveillances have been scheduled w/their respective WOs in outage. This was an oversight by Maintenance during the DR24 review for WOs that needed to be added to outage scope No further action required.
392969 | CR | 20190507 |  | 4 | TS Surveillance Procedure Incorrectly Coded as Low Risk |  |  |  | N | NO | <D> **** Detailed Description **** WOâ€™s 0211113801, PERFORM PPM ISP-CIA-Q901 â€“ CC and 0213766801 PERFORM PPM ISP-CIA-Q901 â€“ CFT are on the schedule to be performed. The IMPACT statement by the PSRO correctly states that per PPM 1.3.76 this procedure should be a MEDIUM risk - "7. Activity, if performed incorrectly, would prevent a SSC from performing its Safety Function." However, WO 02111138 and its MWO 00DJZ2 were incorrectly coded "L" for Low Risk on the Nuc panel and in the schedule. WO 021376680 and its MWO 02135507 are correctly coded "M". <I> **** Actions Taken **** Recoded WO's to correct risk level. Notified Craft Supervisor and WWM.
392970 | CR | 20190507 |  | 3 | RWCU-V-33 Rebuild Missing Task to Fill Piping |  |  |  | N | NO | <D> **** Detailed Description **** During the restoration of WO 02119802 it was identified that a task should have been created to ensure the piping between RWCU-V-32 and RWCU-FCV-33 was full. The performance of SOP-RWCU-OPS section 5.6 to re-open RWCU-V -32 has the potential to cause RWCU-V-1 and RWCU-V-4 to isolate on high blowdown flow if any air exists in the piping post maintenance. This issue was identified while performing this portion of the SOP. Recommend adding a task to ensure the piping is full prior to opening RWCU-V -32. <I> **** Actions Taken **** Notified MCR, OCC, and submitted CR <N> Work has been completed. Note added to WO documenting AR content for reference in future planning.
392975 | CR | 20190507 | CAQ | D | Quorum not met - Management CR review |  |  |  | N | NO | <D> **** Detailed Description **** Quorum was not met for Management CR review conducted on 5/6/19. Operations personnel were not in attendance. Per PGM the meeting was held. <I> **** Actions Taken **** This CR is to document an approved deviation from SWP-CAP -06. Recommend CAQ - D as no further actions are necessary.
392978 | CR | 20190507 |  | 4 | 3 Pieces of M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** 3 Pieces of M&TE found OOT & adjusted within specs. NONE were used during Calibration cycles. Calcode #0064142 Hytorc Hyd. Torque Wrench- model Avanti 1. DEF #7024A written. Calcode #0066011 Cementex Insulated Torque Wrench- model 50250TW38I 50-250". DEF #7025A written. Calcode #0066012 Cementex Insulated Torque Wrench- model 50250TW38I 50-250". DEF #7026A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
392984 | CR | 20190507 |  | 3 | CF-TK-41 and 42 need flushing / cleaning. | N | N |  | N | YES | <C> CR reopened as per MRT to evaluate compatability issue. Changed to 3/CHEM <D> **** Detailed Description **** CF-TK-41 and CF-TK-42 have a sludge layer that floats on the surface of the product. This sludge extends far enough below the surface to get drawn into the tank outlet lines and eventually the chemical feed pumps which causes clogging and loss of pump suction. Currently CF-TK-41 outlet piping is clogged to the point of the gravity drain path not providing enough flow to maintain desired chemistry levels in the circ water / TSW systems (see WR 29148287). The current tank level in CF-TK-41 is 1098 gallons which should provide enough pump suction head for the pumps to operate, but the sludge in the piping is inhibiting free flow. Work order 02129874 had been created to clean out CF-TK-41 and CF-TK-42, but was cancelled because a feed and bleed process â€œwas being successfulâ€. In reality this was never the case. Ever since receiving some bad batches of chemicals maintenance has been battling with the clogging of the chemical feed pump suction lines and it continues to this day. Both chemical tanks need to be drained and cleaned as well as all of the pump suction lines. It also appears that there is a compatibility issue with the chemical product and the stainless steel piping. Please investigate and clean out these chemical storage tanks. <I> **** Actions Taken **** Discussed with supervisor and wrote this AR/WR. <N> **** Equipment Description **** O 449 | 02-00-CF-TK-41,02-00-CF-TK-42
392985 | CR | 20190507 | CAQ | C | Malfunction on IDS 24/25 | N | N |  | N | YES | <D> Malfunction on IDS 24/25 <I> Placed comp. IDS 24/25, notified supervision, Notified electricians, CR/WR generated <N> CR found at INPROG, reviewed and sent on to SRO. Work was conducted and completed prior to CR/WR being initiated. Security zone has been corrected and returned to security no compensatory measures in place at this time. No further action required. | 02-00-SEC-IDS-E/S/24/25/26
392988 | CR | 20190507 | CAQ | C | RHR-M-P/2A lower oil bearing level - abnormal fluctuations | Y | Y |  | N | YES | <D> **** Detailed Description **** RHR-M-P/2A lower motor bearing oil level is fluctuating abnormally while RHR-P-2A is running. This was discovered while performing the quarterly RHR-P-2A survielance. Lower bearing oil level was fluctuating approximately 1/4", but maintaining in the "operating band". Normally, upper and lower motor bearing oil levels change with pump start/stop, but they normally remain steady during pump operation. See EDMS doc for video. Note: RHR-P-2A room is normally a High Rad Area. <I> **** Actions Taken **** Informed MCR. Verified Lower motor bearing oil level remained in "operating band". <N> **** Equipment Description **** RHR-P-2A pump room. Rx 422 | 02-00-RHR-M-P/2A
392989 | CR | 20190507 |  | 3 | TOA-DPIC-2A PM Changed to 10 years | N | N |  | N | YES | <D> **** Detailed Description **** TOADPT2ALCI445 LOOP CAL needs to be changed back to a 24 month cycle <I> **** Actions Taken **** Notified Supervisor | 02-00-TOA-DPIC-2A
392990 | CR | 20190507 |  | 4 | TOA-DPIC-2A | N | N |  | N | YES | <D> **** Detailed Description **** Walked down WR 29143283 and after investigation determined PM TOADPT2ALCI445 needs to be performed with potential corrective maintenance. <I> **** Actions Taken **** Notified Supervisor | 02-00-TOA-DPIC-2A
392991 | CR | 20190507 |  | 4 | RHR-RV-25B & C-new valves not tested |  |  |  | N | NO | <D> **** Detailed Description **** After testing rotational spares, to be installed in R24, it was discovered that that these thermal relief valves have to be replaced or the rotational spare needed to be disassembled, inspected and then tested prior to installation per TSP-RV/IST-R701 step 6.3.1. The tested valves were not new or refurbished. <I> **** Actions Taken **** Contacted Supervisor and Planning to revise work orders to re-perform testing on new valves. No further action is required. <N> Work instructions have been updated as requested. No further actions required.
392994 | CR | 20190507 |  | 4 | TOA-DPIC-1A | N | N |  | N | YES | <D> **** Detailed Description **** Walked down WR 29123490 and after investigation determined PM TOADPT2ALCI443 needs to be performed with potential corrective maintenance. <I> **** Actions Taken **** Notified Supervisor | 02-00-TOA-DPIC-1A
392995 | CR | 20190507 |  | 3 | Pre-Filters could not be located at WH1. |  |  |  | N | NO | <D> **** Detailed Description **** Asset Suite shows 22 available for CATID 34584. A demand was placed for quantity of 3. Warehouse storekeeper was not able to locate them in the storage area shown in Asset Suite. <I> **** Actions Taken **** Generated CR. Reference WO 02111132-01 <N> Found filter in an adjacent location.
392996 | CR | 20190507 |  | 3 | PPM 16.11.2 needs revision |  |  |  | N | NO | <D> **** Detailed Description **** This does not affect plant operation. PPM 16.11.2 steps 6.8.4, 6.9.4, and 6.10.4 require the use of a â€œcorrected postâ€ and â€œcorrected priorâ€ reading for the effluent monitors during startup/shutdown and power change operations greater than 15%. The guidance given to determine this value is complicated, and includes four â€œnotesâ€ and two calculations. Changes to the effluent monitoring equipment has made it possible to significantly simplify this process. This procedure can be performed as written, but these instructions should be clarified and revised to reduce the likelihood of error during performance, as this is a rarely performed evolution . Recommend assignment to chemsitry effluent specialist. <I> **** Actions Taken **** Spoke with chemistry supervisors and technicians about procedure, ODCM requirements, and related equipment IDMS.
392997 | CR | 20190507 |  | 3 | TOA-DPIC-1A PM Changed to 10 years | N | N |  | N | YES | <D> **** Detailed Description **** TOADPT2ALCI443 LOOP CAL needs to be changed back to a 24 month cycle <I> **** Actions Taken **** Notified Supervisor | 02-00-TOA-DPIC-1A
393001 | CR | 20190507 |  | 4 | Ultrasonic Tank in the RW 467 Decon | N | N |  | N | YES | <D> **** Detailed Description **** The Ultrasonic Tank on Radwaste 467 needs to be repaired before R24 outage. The heater does not currently work and needs to be repaired for the ultrasonic tank to work properly. This ultrasonic tank is used during the outage to decontaminate highly contaminated valve parts, tools and equipment. <I> **** Actions Taken **** Initiated CR and Work Request <N> **** Equipment Description **** Radwaste 467' Decon Facility
393003 | CR | 20190507 |  | 4 | PM CHANGE PROCESS NOT FOLLOWED |  |  |  | N | NO | <D> **** Detailed Description **** Per PPM 1.5.13, when changes in the scope of a PM need to be made, an SMS-AR is created to document the approvals and the changes. In AR 377850, PM scope changes were requested, which is outside the PM change process since the AR is not an SMS AR. Scope changes were made to the model work orders of 360 PMs, which made the MWOs not be in alignment with the current PMRQ scope. Also the changes were made without ensuring that the appropriate approvals were obtained prior to the change being made. <I> **** Actions Taken **** Notified supervisor and manager. Recommend Engineering create an SMS-AR so that approval for the changes and be obtained and appropriate changes to the PM scope can be made. <N> AR SMS 00393035 has been created to change the PM scope for ITE Gould AC NSR MC starters as required. AR CR 00393003 should be trended
393004 | CR | 20190507 |  | 3 | 10.24.109 cancelled with no new reference |  |  |  | N | NO | <D> **** Detailed Description **** 10.24.109 was cancelled without a new reference document to calibrate CMS-LS-1 thru 4. IMDS calls out 10.24.109 as the calibration reference. Either 10.24.109 needs to be re -instated or the correct reference is required on the IMDS. <I> **** Actions Taken **** spoke with system engineer wrote CR <N> 10.24.109a covers the information documented in this AR. No further actions required.
393005 | CR | 20190507 |  | 4 | Cathodic System Loss of DC alarm in. | N | N |  | N | YES | <D> **** Detailed Description **** H13-P821 board W drop 6-4 Cathodic System Loss of DC at Well No. 2 Pump house. | 02-00-CP-RECT-DW2
393006 | CR | 20190507 |  | 3 | Bent piping up stream of TO-V-641 | N | N |  | N | NO | <D> **** Detailed Description **** While performing oil samples per WO 02133564-01 TO-TK-2 the craft noticed that the 3/8â€ piping up stream for the valve was bent. This is believed to be from the force needed to hold the Â½â€ pipe and twist the cap off to obtain the oil sample. Recommend that it be evaluated to increase the size of the pipe into the flange to Â¾â€ and change the valve to a ball valve for sampling. There is no operational impact currently, but if the 3/8â€ piping was to break during operation oil would leak out with no way of stopping it. See pictures in EDMS <I> **** Actions Taken **** Generated CR for documentation and evaluation to upgrade and complete during the Outage . The bend in the EDMS pictures has no impact on piping integrity. Recommend that two wrenches are used to remove the pipe cap - one on the pipe (immediately adjacent to the cap) and one on the cap.
393008 | CR | 20190507 |  | 4 | GRA-FN-1 has dual indication while running. | N | N |  | N | YES | <D> **** Detailed Description **** After starting GRA-FN-1 the red run lamp came on as expected, but the green off lamp remained energized. Looking at EWD-89E-057, contact 8-9 would be stuck closed resulting in this condition. Also, none of the lamps work at the local disconnect. The bulbs were checked good. See attributes screen for picture. Please investigate and correct. <I> **** Actions Taken **** Informed supervisor and wrote this AR/WR. <N> **** Equipment Description **** G441 D1/2.8 | 02-00-GRA-FN-1
393009 | CR | 20190507 |  | 4 | E-EQ-B1/11 battery needs demin added to 75% of cells |  |  |  | N | NO | <D> **** Detailed Description **** during quarterly inspection of spare batteries per 10.25. 5F, it was noted that cells 1-6 electrolyte levels are above the low-level mark, but the levels are very close to the low level mark. 10.25.5F does not allow for water addition unless the electrolyte level is actually below the low level mark. This CR is generated to facilitate adding water to E-EQ-B1/11 to ensure levels do not drop below the low level mark. <I> **** Actions Taken **** Generate CR/WR Notifiy Supervisor <N> **** Equipment Description **** E-EQ-B1/11 Bldg 19
393013 | CR | 20190507 |  | 3 | DSA-DY-1A, Replacement dryer has internal corrosion. |  |  |  | N | NO | <D> **** Detailed Description **** During inspection of the new replacement dryer CID 58709196, it was observed during the internal inspection that moderate corrosion and rust was present. See EDMS for pictures. Request engineering to evaluate condition for use and possible coating of the internal surface. <I> **** Actions Taken **** Notified engineering, obtained pictures and generated CR. <N> **** Equipment Description **** spare dryer, not installed in the plant.
393015 | CR | 20190507 | CAQ | D | R-209 door from RW487' elevator into Radwaste side | Y | N |  | N | YES | <D> **** Detailed Description **** The door handle from the inside of door R-209 (487' Elevator from Rx bldg into Radwaste spins freely and does not open the door). You have to push really push inward manually when the latch is in the normal position then turn up in order the for the mechanism to engage and unlock the door from the inside. Sometimes the round handle from the outside (Radwaste side) will become essentially locked and the only way it it becomes free is if someone is on the inside messing with the door latch. <I> **** Actions Taken **** Contacted Operations and informed Operations personnel of current configuration of door. Inserted a blurry video (showing the latch free spinning) and an picture as well. | 02-00-R-DOOR-R209
393016 | CR | 20190507 | CAQ | D | Loose connections on CEP-V-4B | Y | N |  | N | YES | <D> **** Detailed Description **** This CR is being requested by engineering for trending: CEP-V-4B had a loose fuse clip and a loose termination on TB1-29. More information is available in WR 29148410 <I> **** Actions Taken **** Informed CRS | 02-00-CEP-V-4B
393017 | CR | 20190507 |  | 4 | MCR kitchen sink is plugged | N | N |  | N | NO | <D> **** Detailed Description **** The MCR kitchen sink is plugged and over flows onto the floor. <I> **** Actions Taken **** Stopped using the sink <N> **** Equipment Description **** RW 501.
393019 | CR | 20190507 |  | 3 | OSP-RCS-C105 procedure change |  |  |  | N | NO | <D> **** Detailed Description **** Recommend changing step 7.8 to read Verify associated technical specification entry for WIC in step 7.7; if no entry exist Notify CRS immediately
393020 | CR | 20190507 | CAQ | D | ARE-CR-51 not running with disc shut and cooling demand | N | Y |  | N | YES | <D> **** Detailed Description **** ARE-CR-51 not running with disc shut and cooling demand No cooling to TSC/ OSC <I> **** Actions Taken **** Informed MCR * EP informed of this condition. 1733 5/7/19 | 02-00-ARE-CR-51
393024 | CR | 20190507 |  | 3 | Typo within procedure 10.25.53 |  |  |  | N | NO | <D> **** Detailed Description **** Upon reviewing WO 02111297.01. In the QC requirement box IP02 â€“ 10.25.53, Attachment 9.4 (parts) and on step 4.1.3 the step refers you to attachment 9.4. When you refer to 10.25.53 step 7.2.12. step D and E refers you to attachment 9.4, Step 7.2.14.F also refers you to attachment 9.4. On page 30 of 34 is attachment 9.3, on page 31 is attachment 9.5. It has been noticed that procedure 10.25.53 has a typo within the attachments. There is no attachment 9.4 in procedure 10.25.53, attachment 9.5 in the procedure needs revised to say attachment 9.4 as it is the correct form to be used. <I> **** Actions Taken **** Contacted planning and wrote CR <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
393026 | CR | 20190507 |  | 4 | Radwaste Elevator not working | N | N |  | N | YES | <D> **** Detailed Description **** The Radwaste Building elevator is not working. Operations Department has exhausted their troubleshooting and potential remedies without success. Request vendor support to troubleshoot and repair the elevator to support the outage. <I> **** Actions Taken **** Notified CRS <N> **** Equipment Description **** Radwaste Bldg elevator
393027 | CR | 20190507 |  | 4 | MT-ELEV-4 (radwaste) elevator fault, would not reset | N | N |  | N | YES | <C> This CR is a duplicate of CR 393026 <D> **** Detailed Description **** MT-ELEV-4 has fault "hoistwell safety string open" currently in. It will not reset on any of the 3 resets on the pixel controller. The outter door on that level was opened using the key and the inner door following. The elevator is at exactly 525 elevation, not above or below. The doors were taken back full closed and the fault would still not reset. In the help button on the pixel controller, it displays "Hoistwell safety string open, SAFH input, the pit stop, the buffer switches, or the up or down terminal switches is open, refer to page 3 of the prints." <I> **** Actions Taken **** CRS informed, ropes pulled. | 02-00-MT-ELEV-4
393028 | CR | 20190507 | CAQ | C | Unable to perform ISP-RWCU-Q402 | Y | N |  | N | I DONT KNOW | <C> As per MRT, this was changed from nonCAQ to CAQ Change to CAQ C/MNTPLAN <D> **** Detailed Description **** Unable to perform ISP-RWCU-Q402 due to open WO 02140138; work order 02140138 is intended to be used as the fix for the broken terminal strip. In order to perform as installed Q402 will need to be revised to reflect the change made in WR 29147070 as initiated by CR 389903. <I> **** Actions Taken **** Contacted SM WO 02111154-01 halted by SM CR initiated <N> Procedure has been revised and issued to allow performance of surveillance. WR will repair terminal.
393029 | CR | 20190508 | CAQ | D | WO: 02111138-01 Presure switch found out of tolerance | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02111138-01 Switch CIA-PS-39A was found out of calibration limit tolerance. Switch was 1 PSI out of tolerance, and was adjusted back into acceptable calibration limits (159-161PSI) <I> **** Actions Taken **** Switch was adjusted back into calibration limits. CR written for tracking purposes, | 02-00-CIA-PS-39A
393030 | CR | 20190508 |  | 3 | OMI-5.5 is outdated and inconsistent with OCC-01 |  |  |  | N | NO | <D> **** Detailed Description **** OMI-5.5, Outage Emergent Work and Issues Management is an "Active" instruction in Asset Suite however it contains outdated titles and is inconsistent with the guidance provided in OCC-01, Outage Control Center Norms. The instruction should be canceled since OCC-01 is the higher level document and contains the appropriate guidance for emergent issues management. <I> **** Actions Taken **** Discussed the matter with the Shift Outage Manager and direction was given to continue to follow OCC-01 instead of OMI-5.5
393037 | CR | 20190508 |  | 3 | EWP page 1 of work instructions was blank â€œlocked upâ€ |  |  |  | N | NO | <D> **** Detailed Description **** On work order 0213736701 page #1 was locked up and I had to close the work instructions and reopen them. See attached picture. <N> This work order is now complete. Need more information to understand why it got locked up. It could have been an individual workstation issue. No issues appear with work order. No action needed.
393043 | CR | 20190508 |  | 3 | R24 Contingency Wedge for RHR-V-4C shipping date moved |  |  |  | N | NO | <D> **** Detailed Description **** CATID 37625 wedge shipping date slipped to June 7, 2019 which is outside of the scheduled window. This CR is to document the OCC-03 decision on outage scope and additional actions as required by the OCC. Purchasing has been significant amount of contact with the vendor from the first time the date slipped. This wedge is a contingency part for going internal to the valve and does not impact the current scope. <I> **** Actions Taken **** Significant amount of vendor contact has taken place. SECOMP will take this CR. This CR does not affect installed equipment.
393048 | CR | 20190508 | CAQ | C | Potential RWCU RHX Tube leaks | N | N |  | N | YES | <D> **** Detailed Description **** WO 02137234 identified a demineralizer bypass flow of about 120 gpm. This flow is seen on total system flow but not on the demineralizer flow. The RWCU-V-44 was suspected of significant leakage. Testing under WO 02143179 identified leakage at 60 gpm. This would indicate a possible 60 gpm tube to shell leak in the RHXs. Leakage would be internal to the HX and both sides are Reactor water, so no external leakage exists. The HX are maintaining adequate system temperatures but the impact on continued operation of the HX and HX health needs to be assessed. | 02-00-RWCU-HX-1A,02-00-RWCU-HX-1B,02-00-RWCU-HX-1C
393050 | CR | 20190508 |  | 4 | PWC-SEW-10 reduced flow to left side eye wash | N | N |  | N | YES | <D> **** Detailed Description **** PWC-SEW-10 reduced flow to left side eye wash Possible foreign material inside sprayer, reducing flow Eyewash still functional, just reduced flow to one side <I> **** Actions Taken **** Notified MCR | 02-00-PWC-SEW-10
393051 | CR | 20190508 |  | 4 | Received Annunciator 4.840.A1 Drop 3-3 TURBINE A SEALING STE | N | N |  | N | YES | <D> **** Detailed Description **** Received Annunciator 4.840.A1 Drop 3-3 TURBINE A SEALING STEAM PRESSURE LOW Alarm. SS-PI-1A was indicating ~3-3.5 psig. Dispatched OPS 3 to investigate. OPS 3 reported SS -PI-4A indicated 2.7 psig. OPS 3 made adjustment to SS -PCV-1A per ARP and alarm is now clear. SS-PI-1A now indicates 4.5psig and SS-PI-4A indicates ~3.9-4.0 psig. <I> **** Actions Taken **** Informed CRS/SM | 02-00-SS-PCV-1A
393053 | CR | 20190508 | CAQ | C | LOST ASME PLAN 2-3024 |  |  |  | N | NO | <D> **** Detailed Description **** AFTER REVIEWING PRINTED MASTER PACKAGE WO 02109790. IT WAS NOTICED THAT THE ASME 2-3024 IN THE WO HAD NO QC SIGNATURES OR RED STAMP INCLUDED ON IT. THEREFORE I CONTACTED QC EFRAIN IZAGUIRRE AND AFTER A LONG DISCUSSION IN REGARDS TO THE ROUTING PROCESS AND TRANSITION FROM HARDCOPIES TO EWP/DATAGLANCE THAT THERE HAS BEEN SEVERAL QC STAMPED ITEMS THAT HAVE BECAME MISPLACED/LOST BETWEEN ROUTING TO QC AND WOPP. THEREFORE THE ROUTING OF THE ASME DOCUMENT MUST BE REROUTED THROUGH PLE & QC FOR ORIGINAL SIGNATURES. <I> **** Actions Taken **** A NEW COPY OF THE ASME 2-3024 WAS PRINTED AND REROUTED FOR APPROPRIATE SIGNATURES FROM PLE & QC. <N> **** Equipment Description **** N/A
393056 | CR | 20190508 |  | 4 | PM task completion incorrectly credited |  |  |  | N | YES | <C> As per CRG discussion and request of engineering rep, this CR is being trended. There is actually no issue. Engineering CIC to discuss with the CR author. <D> **** Detailed Description **** COND-EJ-2A and COND-EJ-2C have PMs to replace the expansion joints every 6 years. These two joints were last replaced in 2011 and 2010 respectively. When they were due to be replaced in 2017, the work orders were canceled, but the PMs were credited. The canceled work orders referenced AR371815. AR371815 did not give direction to cancel the work order or extend the PM frequency. The PM should not have been credited. <I> **** Actions Taken **** AR Written <N> **** Equipment Description **** T -432- - -D4/13.8- | 02-00-COND-EJ-2A,02-00-COND-EJ-2C
393058 | CR | 20190508 |  | 3 | Effects of WR 29147070 not fully scoped out |  |  |  | N | NO | <D> **** Detailed Description **** CR-389903 identified a broken terminal while performing ISP-RWCU-Q402. WR 29147070 moved the test terminal on 2 -13-19 and Notes of CR stated no further action needed as once terminal was fixed, then wires would be relanded. Yesterday CR-393028 was written as the surveillance again could not be performed. The surveillance was changed to identify the temporary test terminal in order to perform the channel functional test. No action has been taken to determine other procedures and possible work orders that may be affected by the change in test terminals. ISP-RWCU -B302 that is the channel calibration is scheduled to be performed on 6-3 during the outage. AED-EWD-19I-001 and CVI-DWG-02H13-05,72,5 currently have the original position for the test terminals with no indication of the actual field configuration. <I> **** Actions Taken **** Engineering is coming up on the 90 days (85 currently) when determination needs to be made on either a Temp Mod or EC. Because WR 29147070 is such a low priority, thought needs to be given to ensure complete actions are taken so affected drawings and surveillances match the field configuration.
393060 | CR | 20190508 | CAQ | D | Loose Connection on fuse for CEP-SPV-3B | Y | N |  | N | YES | <D> **** Detailed Description **** Loose Connection on fuse for CEP-SPV-3B was found when lifting Caution Clearance: C-CEP-V-4B. Tag Serial Number 925 E-FUSE-IR62/TB1F4. CEP-SPV-will energize if switch is taken to operate. Recomend perfoming thermography on the fuse to verify that this is not a high resistance connection. <I> **** Actions Taken **** Ssupervision Notified CR/Wr Generated <N> **** Equipment Description **** Fuse for CEP-SPV-3B at IR 62 /TB1F4
393061 | CR | 20190508 | CAQ | C | (QA) LPRM PMT VT-2 Leakage Task Not Routed To QC for Review |  |  |  | Y | NO | <D> **** Detailed Description **** (QA WOT 02109790-19 not routed to QC for initial review as required per MI.1.22. During search for the Original hard copy of ASME Plan 2-3024 considered to be lost (Reference CR 393053) it was discovered that the applicable LPRM VT-2 Visual Examination Data Sheets had not been reviewed. The work order task was at Ready status and will require QC and ANII review to support ASME work activities for ASME Plan 2-2034. <I> **** Actions Taken **** Notified QS Supervision and RX Planner. Initiated CR and Planner proceeded to add QCI hold for Initial Review required by QC. Documents will be processed, reviewed with QC and ANII signatures for work package submital and approval. <N> **** Equipment Description **** R24, No field work started.
393063 | CR | 20190508 |  | 3 | Unable to complete temp power for 400CFM portable compressor |  |  |  | N | NO | <D> **** Detailed Description **** Work order 02114004-01 could not be completed as scheduled. This is a pre-outage task that was scheduled to complete in the pre-outage timeframe but will go into the outage when E-EP-F10/4 of the GSB basement and the main disconnect on T471 are powered up and the final bump test can be performed (mode 4 or 5). This could potentially impact the current outage schedule and allotted resources. E-EP-F10/4 IN THE BASEMENT of GSB basement and the main disconnect on T471. <I> **** Actions Taken **** Notified Operations,PM and work control.
393064 | CR | 20190508 |  | 3 | Revise PPM 1.5.21 |  |  |  | N | NO | <D> **** Detailed Description **** Step 6.3.2 should read: â€œProtect systems used to satisfy step 6.3.1 per PPM 1.3.83.â€ Step 6.4.2 should read: â€œProtect systems used to satisfy step 6.4.1 per PPM 1.3.83.â€
393065 | CR | 20190508 |  | 4 | WOA-FI-1 full of debris, not indicating | N | N |  | N | YES | <D> **** Detailed Description **** WOA-FI-1 spring is full of debris, and indicates pegged high even when WOA-V-60 is shut (should have been 0gpm). Flow should be 5gpm per SOP-WARMWEATHER-OPS. With SSS concurrence, WOA-V-60 was throttled open until flow was just visible in sight glass. Recommend repair/replace WOA -FI-1, and throttle WOA-V-60 to 5gpm indication. <I> **** Actions Taken **** Informed SSS, generated AR/WR. | 02-00-WOA-FI-1
393066 | CR | 20190508 |  | 3 | WO 02129668-02 Taken to Finished Without SRO Review | N | N |  | N | NO | <D> **** Detailed Description **** WO 02129668-02 for TSP-RV/IST-R701 was signed in on 1/14/19 at 0949 and task is now at finished with no SRO review. Additionally, page 21 has a sign off for the performer and test supervisor that is blank. Please review and resubmit for SRO review. <I> Shop task 02129668-02 Has been reset to working and the Review Required flg checked . Maintenance needs to bring the completed surveillance package to the PSRO for review and closeout. MWO was also updated.
393068 | CR | 20190509 |  | 3 | RFW-LCV-10A/B steam leak reduced after stroking | N | N |  | N | YES | <D> **** Detailed Description **** RFW-LCV-10A/B was stroked to verify proper operation per WR 29148386 at 2300 5/8/19. After stroking the LCVs, the steam leak was much reduced. The original assessment of the source of the leak was a body to bonnet leak. The leak should be re-evaluated for a potential packing leak. See EDMS for pictures and video. Historical pictures can be found in S:\Operations\CROPS\RFW-LCV-10 steam leak pictures\ | 02-00-RFW-FCV-10
393069 | CR | 20190509 | CAQ | D | DG-ENG-1A1 needs oil addition | Y | N |  | N | YES | <D> **** Detailed Description **** During the 24 hr run oil level was logged at midnight per the surveillence. Minimum lube oil sump level is 3.75" BELOW the FULL mark on the dip stick. Level was found to be 4.5" BELOW the FULL mark. CRS was informed. A oil addition needs to be performed to restore level to the normal band. Note that the engine was at rated load during this measurement. | 02-00-DG-ENG-1A1
393070 | CR | 20190509 | CAQ | D | CRD-HCU-0635 high water level | Y | N |  | N | YES | <D> **** Detailed Description **** Received ROD ACCUMULATOR TROUBLE alarm H13-P603 (6-7) for CRD-HCU-0635. Alarm was due to high water level and excess water was drained per SOP-CRD-HCU. The alarm is clear. <I> **** Actions Taken **** Submitted CR and WR. Notified CRS and Shift Manager. | 02-00-CRD-HCU-0635
393071 | CR | 20190509 |  | 4 | E-CB-LP5NA/9 found tripped open. | N | N |  | N | YES | <D> **** Detailed Description **** During a walk down for WO 02079546-25, E-CB-LP5NA/9 was found in a tripped free condition. <I> **** Actions Taken **** Informed Work Execution Center. | 02-00-E-CB-LP5NA/9
393072 | CR | 20190509 |  | 3 | Drawing for ARE-CR-51 is incorrect |  |  |  | N | NO | <D> **** Detailed Description **** While investigating the replacement of ARE-CR-51, it was identified that the drawing EWD-89E-070 incorrectly identifies the compressor and fan ratings. The drawing needs to be updated with the nameplate data from calc E/I -02-90-01 rev 1, or the new nameplate data from the new motor if it is different. This is only a drawing issue and does not affect the plant equipment in the field. The new motor and CatID match the calculation values. <I> **** Actions Taken **** Initiated CR. <N> There is a local 100 amp breaker inside the unit cabinet that is upstream of the line fuses and turns off power to everything in the unit. The drawing in the EDMS shows this breaker as optional and this unit does have the option. Look at the drawings included in the EDMS and correct EWD-89E-070.
393073 | CR | 20190509 |  | 4 | CM-11 Out of Service | N | N |  | N | YES | <D> **** Detailed Description **** HP-EQ-63088 located at the AAP is out of service, displaying UNIT FAULT / LOW GAS FLOW RATE. <I> **** Actions Taken **** Tagged equipment out of service and initiated a CR/WR and notified HP supervision <N> **** Equipment Description **** HP AAP.
393074 | CR | 20190509 |  | 4 | 2 Pieces of M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** 2 Pieces of M&TE found OOT and were NOT used. Calcode #0068112 RAD Dig. Battery Torque Wrench- model DB -RAD 500-2. DEF #6211A 6/16/17 had Suspended it until R24. Adjusted within specs. DEF #7028A written. Calcode #0068303 Mitutoyo Dial Caliper- model 505-742 6" was Rejected- Not Repairable. DEF #7029A written. No Action Required. <I> **** Actions Taken **** None Trending purposes
393077 | CR | 20190509 |  | 3 | OSP-FLEX-A106 unable to be completed | N | N |  | N | NO | <D> **** Detailed Description **** OSP-FLEX-A106, Att 9.9 was unable to be completed for the following reasons: (1) FLEX-VEH-5 is not located in Bldg 600 as described. (2) FLEX-CAB-1/TKF1 and 2 are not labeled with tank volumes and there is no way to accurately check level in the tank. Same applies for FLEX-CAB-2/TKF1 and 2. An operator tried to remove the bung from one of the tanks in FLEX-CAB-1 and the tank appeared to be under pressure as the tank started venting into the building. The bung was retightened and supervisor was informed. For future purposes, i would recommend documenting on the tank how much fuel is added to each one, then seal the tank. As long as the tank stays sealed, we could say the volume is still there for the purpose of our surveillance. <I> **** Actions Taken **** Informed Supervision. Wrote CR.
393078 | CR | 20190509 |  | 3 | Received RECIRC B SYSTEM VIBRATION HIGH alarm (RRC-P-1B) | N | N |  | N | YES | <D> **** Detailed Description **** Received H13-P602.A6.2-8 RECIRC B SYSTEM VIBRATION HIGH alarm two times (alarm was able to be reset locally both times). Investigation revealed RRC-VBI-P1B/XE red alarm light flashing and indicating @ 46 mils on both occurrences. RRC-P-1B thrust bearing temperatures are normal as are RRC-P-1B motor oil levels. RRC-P-1B is operating at 61.9 Hz (flowed-out with RRC-P-1A biased higher at ~ 62.5 Hz). Reactor power currently at 92%. NOTE: both alarms were received shortly after adjusting (lowering) TMU makeup flow (to lower CW bay level in preparation for plant shutdown). This resulted in some variation in TSW and RCC temperatures and might have contributed to these alarms. This vibration indicator was also documented as alarming on 03/08/19 by WR 29147494. <I> **** Actions Taken **** Submitted CR & WR to document the issue. Notified CRS and Shift Manager. | 02-00-RRC-VBI-P1B/XE
393080 | CR | 20190509 |  | 4 | R24LL L-BS-DV-3A2 -002 hung per the schedule, lifted. |  |  |  | N | NO | <D> **** Detailed Description **** L-BS-DV-3A2 -002 was hung per WOT 02112767-03 (HC) as scheduled for 5/9/19. This work starts 5/21/19. Unfortunately work under O-BS-V-10A/R24 -001 is done first and the two clearances conflict (WOT 02110992-07 determs the QSV 5/13/19). Both use IR-V-IR3/V17 as an isolation. <I> **** Actions Taken **** L-BS-DV-3A2 -002 was processed and L-BS-DV-3A2 -003 will now be used for the work.
393081 | CR | 20190509 |  | 4 | PWC-P-4B failed to start | N | N |  | N | YES | <D> **** Detailed Description **** PWC-P-4B failed to start during performance of SOP -WARMWEATHER-OPS section 6.1 step 6.1.2n and 6.1.2u. <I> **** Actions Taken **** informed MCR and wrote CR. Request investigate and repair. | 02-00-PWC-P-4B
393082 | CR | 20190509 |  | 4 | ROA-HV-1 has clogged nozzles. | N | N |  | N | YES | <D> **** Detailed Description **** Upon start up of ROA-HV-1 air wash, it was noted that there are approximately 45 clogged air wash nozzles that need to be cleaned up for proper operation of the ROA-HV-1 air wash. <I> **** Actions Taken **** Wote CR. Informed supervision. | 02-00-ROA-HV-1
393083 | CR | 20190509 |  | 3 | DG load testing (24 hour run) procedure enhancements |  |  |  | N | NO | <D> **** Detailed Description **** Procedure TSP-DG1-B502 performs load reject testing as part of the 24 hour run procedure. The section providing guidance for load reject testing indicates voltage and frequency should return to nominal values (60 Hz and 4160 volts) following the load reject which is not the expected response. Load reject testing is performed by paralleling the diesel generator to the grid, loading the diesel generator to rated load for both real and reactive power then opening the output breaker and assuring the diesel generator does not trip on over speed or exceed a specific frequency and voltage. When parallel to the grid there is droop in both the voltage regulator and the governor control system to allow the controls to share load. The droop setting is typically between 3% and 5%, the governors and voltage regulators at Columbia are typically set just above 3%. For a 3% droop the diesel generator frequency following a full load reject should be 3% higher than 60 Hz or approximately 61.8 Hz. Voltage should be approximately 3% higher than the nominal 4160 and may be additionally elevated due to the grid voltage being higher than 500 KV. . Procedures for all three divisions should be revised to reflect the expected response so operations is not challenged to justify a frequency or voltage that is different than what is described in the procedure. <I> **** Actions Taken **** Discussed with OPS in the DG room following the full load reject, discussed with supervisor and initiated CR to recommend procedure changes. Procedures to be changed are TSP-DG1-B502, TSP-DG2-B502 and TSP-DG3-B502
393084 | CR | 20190509 |  | 4 | Portal J - Unreasonable performance issue |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Portal J is preventing Users from opening Word docs attached to WOs (An example would be trying to open Master Template work instructions for a PMT task.). After clicking the icon to open an attached Word Doc., a pop up window tells the user the Program will be Closed. Clicking the OK button or the upper right X, of the pop up window, both result in Portal J Closing. Once re-logged in, subsequent attempts to open the exact same attached Word doc. are usually successful. Opening additional word docs, often results in the Program Closing again. This discrepancy is occurring with MANY Portal J users. Whether preparing for the Outage or Online work, this issue is causing significant delays in task preparation/execution. Portal J is the backbone of Columbiaâ€™s Work Process/Implementation program, the frustration and time delays being created by this â€œglitchâ€ are unacceptable. <I> **** Actions Taken **** informed Supervision. Verified and Validated this is a station wide problem, not isolated to an individual user. <N> **** Equipment Description **** Portal J glitch . The Assetsuite application continues to have these sporadic abends when dealing with JAVA and Microsoft Office. The answer we receive from the vendor (Assetsuite Application - ABB) is that we are using software that is no longer supported (outdated). We are currently in the middle of the Assetsuite upgrade project which will bring the software up to the latest revisions. We are hoping this will resolve these issues, but if not, we will be able to address the issue with the vendor (ABB). . Recommend closing CR and Trend.
393091 | CR | 20190509 |  | 4 | TG-ID-1 is out of paper. | N | N |  | N | YES | <D> **** Detailed Description **** TG-ID-1 Condition monitor is out of paper. This is a Rustrack recorder. Please reload. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 471W | 02-00-TG-ID-1
393092 | CR | 20190509 |  | 3 | EC-17099 did not identify all impacted PPMs and WOs |  |  |  | N | NO | <D> **** Detailed Description **** During a walk down for upcoming maintenance on Radwaste Chiller WCH-CR-51A it was discovered that PPM 10.2.13 was not revised for the new chiller that was installed on 10 -9-19 per EC-17099 (CR-392444). Need markups from Engineering on lubricants to be used, in order to update the work instructions and PPM, order new lubricants if needed and have CAT IDs assigned. <I> **** Actions Taken **** Recommend informing all impacted groups when plant components are replaced with new models. <N> Reassigned this AR from AR-CMC to AR-MNTPROC for the processing and completion of the remaining open assignment. AR-MNTPROC (K Jerrow) agreed to this change on 8/20/19 @ 10:05am.
393096 | CR | 20190509 |  | 4 | TSC alternate acces area AC unit failing. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The AC unit for the TSC alternate access HP area fails to produce cool air. The unit quit working on 5/08/2019. The unit was turned off then back on and yielded cold air. Currently the unit is on but is not producing cold air. Request HVAC specialist investigation. The unit is located on the roof of the alternate access area and differs from the chiller used to cool the actual TSC emergency response area. <I> **** Actions Taken **** Wrote CR. Wrote work request. <N> **** Equipment Description **** AC unit located on roof of TSC alternate access building.
393097 | CR | 20190509 |  | 3 | PPM 9.2.1 contains inconsistent requirements ICA creation |  |  |  | N | NO | <D> **** Detailed Description **** PPM 9.2.1 contains inconsistent requirements for creation of a new Special Nuclear Material Item Control Area. Section 4.1.7 of PPM 9.2.1 requires that the new Item Control areas are established by the â€œNuclear Material Custodian, in consultation with the Manager, Security Operations, the Nuclear Material Manager, and the Nuclear Material Records Coordinatorâ€ while section 6.1 specifies that additional temporary ICAs may be approved by the Nuclear Material Custodian, the Nuclear Material Manager and the Radiation Protection Manager. This is an inconsistent approval requirement that is specified for the creation of new temporary ICAs. Section 4.1.7 should be revised to specify that the approvals only apply to establishment of new permanent ICAs. This is a deficiency identified during a snapshot self-assessment under AR 388874.
393099 | CR | 20190509 | CAQ | C | WO# 02035959-01 lost work package |  |  |  | N | NO | <D> **** Detailed Description **** The original "Master" and associated hard copy documents for R24 Outage WO# 02035959-01 (CIA-42-8B7D bucket replacement) have been lost. These documents had been reviewed by the QC department and included terminations sheets from EC 14761. One other document lost was the "Replacement Parts" sheet (Attachment 1) original, which included parts already installed in the bucket during the bench test. The hard copy appears to have been misplaced between late last year and early this year. <I> **** Actions Taken **** The applicable documents have been recreated from the EC and a copy of Attachment 1 has been created from the scanned copy in Task 02 (Bench Test). QC review will be obtained on the re-created documents. <N> Williams Plant Services
393100 | CR | 20190509 | CAQ | D | dg1 lube oil | Y | N |  | N | YES | <D> **** Detailed Description **** DG1 (1A1 1A2) engines were 4.5 inches below the full mark after the 24 hour run. This CR is created per SOP-DG -LUBEOIL step 5.1.3. to create a work request to fill DG1 1A1 and 1A2 <I> **** Actions Taken **** CR created to document low level - no actions in plant Sump levels checked again post shutdown indicate 3.25 inches below the FULL mark. <N> **** Equipment Description **** DG1 room | 02-00-DG-ENG-1A1,02-00-DG-ENG-1A2
393101 | CR | 20190509 |  | 4 | CW-P-2 tripped off | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of the shiftly chemistry log, Daily Chemistry Data, it was noted that CW-P-2 tripped off. This pump is intended to run continuously while the CW system is in operation. <I> **** Actions Taken **** CW-P-2 restarted,and informed chemistry supervisor/specialist. | 02-00-CW-P-2
393102 | CR | 20190509 |  | 4 | WOA-CB-FN1A light bulb base stuck in trip light socket. | N | N |  | N | YES | <D> **** Detailed Description **** WOA-CB-FN-1A light bulb seperated from the base in the trip light socket while extracting for replacement . Please repair. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** E-SL-53 TG 501E | 02-00-WOA-CB-FN1A
393103 | CR | 20190509 |  | 4 | PPC DP20 in OVFL (with RED ICE CUBES) | N | N |  | N | YES | <D> **** Detailed Description **** During system monitoring, PPCV was observed to have red ice cubes and high disk consumption. DP20 was found to be in OVFL. The system requires restart of either the DP20 or the whole PPC train to restore functionality. . This does not affect TDAS which is currently primary. Due to this PPC is not available as backup. This is not a reportable condition. <I> **** Actions Taken **** Notified MCR, generate CR and WR. TDAS is primary. No impact to core thermal power calculation. | 02-00-PPC-COMP-8715,02-00-PPC-CPU-VMS/WS
393104 | CR | 20190509 |  | 3 | SOP-RHR-SDC Slows Recovery of SDC |  |  |  | N | NO | <D> **** Detailed Description **** SOP-RHR-SDC-BYPASS in step 5.3.5 and 5.3.6 de-energizes RHR-V-53A or -53B OPEN to harden them versus a spurious closure. The current revision of SOP-RHR-SDC now requires requires an EO to manually operate RHR-V-53A/B if it cannot be operated from the MCR. Revision 27 of SOP-RHR-SDC (which we used R23) accommodated the hardening of RHR-V -53A/B by throttling with RHR-V-48A/B. Recommend that SOP-RHR-SDC be reverted to the wording of Revision 27 with the additional option of manually opening RHR-V-53A/B if needed in case it is stuck or tripped shut.
393105 | CR | 20190509 |  | 4 | REA-FN-3 Fow indicator shows ~1500 cfm (with unit OOS) | N | N |  | N | YES | <D> **** Detailed Description **** L-REA-FN-3-001 is hanging to support WO 02136710-01. This unit is OOS to support Pre-filter replacement. Unit will be returned to service as part of the system check, however this 1500 cfm should be considered as the PMT says to verify normal flow of ~4000 cfm. Previously the pre-filters indicated plugging with high DP. REA -DPIT-3A showed ~ .05" Water with unit out of service so DP across Pre-filter gauge appears correct with unit off. <I> **** Actions Taken **** Generated CR. Will follow up and account for flow static flow indication as part of the PMT. | 02-00-REA-FN-3
393106 | CR | 20190509 |  | 3 | RRC-P-1A new Pump Shaft Has 3 Indications O/S MFG Tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Three indications were discovered on the new Pump Shaft The new RRC-P-1A pump shaft has three indications on it outside of the manufacturer's tolerance. Indications occurred after the 2nd failed sleeve was removed due to two failures on the final PT exams causing the manufacturer to fail the sleeve and remove it from the shaft. <I> **** Actions Taken **** 1. NCR 200185194 has been written by the manufacturer with a suggested disposition to repair the shaft . 2. EN Engineering has been sent the NCR for disposition 3. PM is working with the vendor and Asset Managment to minimize and/or eliminate any impact to FY19 budget
393107 | CR | 20190509 |  | 4 | Delivered Sunbelt Manlift is Missing |  |  |  | N | NO | <D> **** Detailed Description **** A 60' Green sunbelt rental manlift was dropped off in the north gravel parking lot towards the Circ water tower side on 5/8/2019 . Indentifier number 355415 is on the manlift. <I> **** Actions Taken **** Multiple groups have looked for the manllift however it has still not been found. Security, Supervision & OCC has been notifed. <N> Update. Delvery date was 5/7/2019
393108 | CR | 20190509 |  | 3 | Replacement breakers failed degraded voltage testing | N | N |  | N | NO | <D> **** Detailed Description **** Two replacement circuit breakers will not close at the required degraded voltage. Both are CID 12554 and are to be used during R24. A vendor rep traveled to CGS to assist maintenance with the investigation and repairs but we were unable to correct the problem with available tools. It appears that both breakers will require a complete teardown to clean and relubricate internal components and correct noted minor misalignments that were observed. Per the vendor rep, the overhaul would require about a week and a half. This will impact the E-SH-6 window work as these breakers are to be used to replace E-CB-N2/6 and E-CB-S/6.
393112 | CR | 20190509 |  | 3 | Hot spot dose rates increased |  |  |  | N | NO | <D> **** Detailed Description **** During review of the hot spot log per WO 02110219 it was noted that HS-035 above the CRD vault, HS-043 RW 467 near the RWCU pre-coat tank and HS-051 on the EDR line above R-5 sump have increased dose rates since the last review. Actions need to be started to flush these hot spots. None of them are immediate significant contributors to dose or represent challnges to postings at this time. <I> **** Actions Taken **** Notified flushing coordinator
393113 | CR | 20190509 |  | 4 | TSW-HX-6E TSW flow / COND-P-2C Oil Temp | N | N |  | N | YES | <D> **** Detailed Description **** During OPS 3 rounds, COND-P-2C oil temp was noted to be 118F. The high spec is 120F. Last shift it was logged as 105F. TSW-FG-1C indicated almost 0 GPM. Last shift it was logged at 2 GPM. Suspect blockage in the TSW system due to small diameter piping and TSW-V-4E being throttled almost closed to maintain oil temperature in band. Recommend evaluating if there is a need for a strainer of some kind before the throttle valve to prevent recurrence. <I> **** Actions Taken **** Throttled TSW-V-4E back to 2 GPM. COND-TI-10C is 115F and down slow. Will continue to monitor. Informed MCR. <N> Flow adjusted. No further action required. Trend for now. If issue reoccurs, we may flush the system. | 02-00-COND-P-2C,02-00-COND-TI-10C,02-00-TSW-FG-1C,02-00-TSW-HX-6E
393114 | CR | 20190509 |  | 4 | Service building (GSB) Urinal Flush Valve Sticking | N | N |  | N | YES | <D> **** Detailed Description **** The left urinal in the men's room in the service building 441' has a sticky flush valve resulting in the urinal overlowing to the floor. The water was moped up and the urinal was taped off to prevent continued use. Please investigate and repair. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** GSB 441' Men's Room Left Urinal
393115 | CR | 20190509 |  | 4 | Error in signing H101's | N | N |  | N | NO | <D> **** Detailed Description **** Dayshift on 5/9/19, the CRS review of H101's was performed properly at 9:41am which meets TS requirements, however he signed in the RWCR spot which made it appear as if they had not been reviewed. The SM performed a final review and signed the H101's at 9:52PM. Since the CRS reviewed the H101's on time there is no missed surveillance and this CR is just to document the issue. <I> **** Actions Taken **** CR written.
393116 | CR | 20190509 | CAQ | D | Instruments found OOT during ICP-RHR-Q901 | Y | N |  | N | YES | <D> **** Detailed Description **** Under W/O 02113537-01 for performance ICP-RHR-Q901 - CFT, RHR-DPIS-12A and RHR-DPIS-12B trips were found OOT. RHR -DPIS-12A has an Admin Limit of 165 to 176â€ H2O with a setpoint of 174â€ H2O, as-found trip was 163â€ H2O. RHR -DPIS-12B has an Admin Limit of 165 to 176â€ H2O with a setpoint of 174â€ H2O, as-found trip was 179â€ H2O. Both RHR-DPIS-12A & 12B were calibrated and as-left trips are in tolerance. <I> **** Actions Taken **** Wrote CR & Notified Supervision.
393118 | CR | 20190510 |  | 4 | Rx S/D Support Task Improperly Rescheduled |  |  |  | N | NO | <D> **** Detailed Description **** WOT 02115591-69, SECURE CRD. BACKFILL (10.27.64), was originally scheduled at 0500 on 5/11/19. Sometime between 5/2 and 5/8, it was improperly tied to SOP-CST-DRAIN as a predecessor, and rescheduled to 1300 on 5/12. <I> **** Actions Taken **** Broke the tie to the predecessor and rescheduled the task to its proper place in the shutdown. CR written to capture lesson learned.
393119 | CR | 20190510 |  | 4 | SEC-XD-5 not functioning as designed | N | N |  | N | YES | <D> **** Detailed Description **** SEC-XD-5 is not functioning as designed. Contact security for more information. <I> **** Actions Taken **** Unit removed from service; CR/WR Generated | 02-00-SEC-XD-5
393120 | CR | 20190510 |  | 3 | MT-DISC-HOI/34A does not exist in Asset Suite |  |  |  | N | NO | <D> **** Detailed Description **** EWD-107E-007 shows the EPN MT-DISC-HOI/34A. This epn does not exist in Asset Suite. This CR is administrative only. Recommend review by Electrical Design Engineering.
393122 | CR | 20190510 |  | 3 | Outage Contingency Control Process Not Followed |  |  |  | N | NO | <D> **** Detailed Description **** Contingency controls for MT-HOI-35 were not adhered to, resulting in work being performed without authorization from the OCC. The WOT did not have an OM hold to ensure SOM/SOD approval prior to working, was not on the schedule to be worked, and was not appropriately communicated to the OCC. This event poses challenges to the organization's ability to control scope and schedule during the outage. . <I> **** Actions Taken **** 1. Generated CR. 2. Informed Operations to not make any further tag hangs and/or changes for this scope. 3. Returned the C3 Contingency to Ready status and placed an OM hold on the task. 4. Commenced an extent of condition investigation regarding the remaining contingencies to ensure they have the apporpriate holds on them. 5. Recommend other actions to PSO and Operations to determine the course of events and generate LLs to preclude repetition.
393123 | CR | 20190510 |  | 3 | EC 17345 Replace Lighting Changed W/O notice/Affecting R24 |  |  |  | N | NO | <D> **** Detailed Description **** EC 17345 REPLACE HID FIXTURES WITH LED FIXTURES has been revised without notice after all work orders for transformer yard lighting replacement have been planned and all parts received. Light fixtures were changed and no longer usable. Additionally there has been changes to mounting back plate prep and additional parts needed. This introduces a tremendous amount of re-work and the need for additional resources to re-plan and new materials ordered. Work is scheduled to begin 5/11/19 and the EC revision still needs to be issued. Summary: This affects R24 Transformer Yard Light Replacements. EC 17345 REPLACE HID FIXTURES WITH LED FIXTURES Revision 1 needs to be issued. Work Orders need revised to include prep details call out the correct parts and the correct parts ordered from the warehouse. Affected work orders totaling 25 LED replacement tasks. 02136055 TRANSFORMER YARD LIGHTING - LED RETROFIT (500KV WINDOW) 02135998 TRANSFORMER YARD LIGHTING - LED RETROFIT (230KV WINDOW) 02136027 TRANSFORMER YARD LIGHTING - LED RETROFIT (115KV WINDOW) <I> **** Actions Taken **** Contacted EFIN whifh is the group performing the EC revision. Contacted OCC
393124 | CR | 20190510 |  | 3 | Procedures disagree |  |  |  | N | NO | <D> **** Detailed Description **** SOP-RHR-SDC precaution 4.23 limiting thermal stratification by maintaining adequate core flow. This is not in agreement with PPM 3.2.1 precaution 4.6 that also describes adequate core flow. . This does not affect the plant shutdown. . Engineering to evaluate.
393125 | CR | 20190510 | CAQ | D | ISFSI Cask display 37 red. | Y | N |  | N | YES | <D> **** Detailed Description **** ISFSI cask 37 was red at beginning of shift and turned green after the printout was obtained. Temp. is elevated at 125.5 F as shown on the printout. <I> **** Actions Taken **** Notified supervisor. OPS 4 verifing screens are clear IAW OSP-SFS-D101 step 7.1.1. <N> **** Equipment Description **** ISFSI
393126 | CR | 20190510 |  | 4 | SAT-P-1B positioner leaking air and oil. | N | N |  | N | YES | <D> **** Detailed Description **** SAT-P-1B was found to be leaking air and oil from the bottom of the stroke positioner. Work request 29140940 was to replace the positioner, but was cancelled due to no leakage found. The leakage has been found. Please plan to replace or rebuild SAT-P-1B stroke positioner. See pictures in attributes screen. <I> **** Actions Taken **** Informed supervisor and wrote this AR/WR. <N> **** Equipment Description **** P 448 U0/4.0 | 02-00-SAT-P-1B
393127 | CR | 20190510 | CAQ | D | Slow DEH quad voter time during OSP-MT-W701 | N | Y |  | N | YES | <C> CR reopened to add completion required check mark to referenced WO 02112562 per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** During performance of OSP-MT-W701 solenoid valve A had a response time of 0.72 seconds. During the two subsequent tests the response time was 0.23 seconds both times. All other solenoids were less than 0.40 milliseconds during all three tests that were performed. <I> **** Actions Taken **** Wrote CR Informed CRS and SM | 02-00-DEH-SV-TRIP/A
393128 | CR | 20190510 |  | 3 | (QA) Williams Plant Service welders have not completed CBT |  |  |  | N | NO | <D> **** Detailed Description **** A number of Williams Plant Service welders have not completed the ME000694 CBT or at lease are not showing up In portal J against the qual. The ME000773 Forms shows as completed. The welding engineer uses the ME000773 form checklist as proof of completion befor adding the welders to the Welder Updat list .This was pointed out by Quality Audit of the welding program <I> **** Actions Taken **** Issued list of welder to WPS Removed welders from the Update list preventing them from any welding activites untill CBT is complete All these welder are ASME IX Code Compliant . This is a nonconformance to ENW traiining expectations. This CR need to Go to WPS to determin why the CBT's are not getting completer or entered during inprocessing and showing up in Portal J <N> Williams Plant Services. Current process for qualifying SSC Welders is: Craft typically test at local pipefitter union hall prior to arrival on-site. An EN welding engineer is overseeing their performance and verifies test coupons meet welding specifications. Once completed then the engineer signs ME000727. Once on-site they have to completed the welder orientation CBT and the welder qualification checklist with their GF. Based on a discussion with John LaSalle, his concern is that the welder, that is GREEN in PQD and on the welder qualifiaction roster, is not completing the welding CBT ME000694 which is indeed occuring. John said there is not a "HOOK" on form 26471 "Personnel Requirements Form" to ensure the welders and their supervison know to complete this CBT before performing any welding activities. The SSCO qualification is for SSC welders that will be on-site for 9-months or greater which implies that welders on-site for less than 9-months (RFO) would not be required to have this qualification. Initially it appears that three things need to be corrected to satisfy John's concerns: 1). ALL SSC welders should have SSCO regardless of their time-on-site. So the qualificaiton directory 3.6 (SSCO) needs to be revised removing the 9-month requirement. Once this has been done then there will be a "HOOK" that John said he needs to make sure welders are complting the CBT. 2). With this change John will need to update applicable MWP procedures so that they align with the qualification matrix. 3). Update Form 26471 adding in CGS Welder Orientation CBT (SSCO) (ME000694). . Extending the due date to 9/26/19 to allow time for identying the required actions to resolve this concern. Will need to work with the responsible welding engineer, training and security.
393131 | CR | 20190510 |  | 3 | 15.1.30 revision for hose Station change |  |  |  | N | NO | <D> **** Detailed Description **** As part of Mechanical Maintnenance 4.0 critique, it was identified that for efficiency/time/dose, for the non-5 year RB A-5 standpipe flush the connection should be from Reactor Building Hose Station FP-V-HS/RB13 on the 471' elevation. Currently the hose station used is Hose Station 12 on the 441', however that requires the craft to run several sections of hose up an additional 30 ft up to the 471' elevation to support flushing into the staged truck in the RX truck bay through the 471' hatch and then have to drain all the hoses back from 471' to 441' back following the flush. <I> **** Actions Taken **** Gnerated CR. This was previoulsy discussed between the Fire Protection Mechanical craft lead and Engineering for being ok for performing during the non 5 year performance. Assign to Procedure group. Essentially Section 7.1.1 of PPM 15.1.30 should reference FP-V-HS/RB13 as opposed to FP -V-HS/RB12 through all the applicable steps. s currently referenced. <N> **** Equipment Description **** PPM 15.1.30 and PMID 24058-01 for yearly RX Bldg Standpipe flush. This was added to the maintenance procedure database and has been started within APW. This will be tracked within the database as this is an enhancement. See EDMS for link to procedure database.
393133 | CR | 20190510 |  | 3 | Revise PMID 24058-01 to have additional Barrier Impairments |  |  |  | N | NO | <D> **** Detailed Description **** Recent performance of PPM 15.1.30 required an additional Barrier Impairment (BI 19-0151) for R-DOOR-R202 (471') to support the current practice of flushing the RX Bldg A-5 standpipe into the RX bldg Truck bay. Recommend Model WO for PMID 24058-01 be updated to include this BI as being prepared to support future performances. The other two Barrier Impairments inclusive of the one that prepares R-DOOR-R108 and R-DOOR-R109 to be opened, should be continued to be generated and reviewed in the event the water cannot be used, however with the water truck, opening of R-DOOR-R018 and R-DOOR-D109 is not required. <N> **** Equipment Description **** PMID 24058-1.
393136 | CR | 20190510 |  | 4 | LP HEATER 1C failed to indicate properly | N | N |  | N | YES | <D> **** Detailed Description **** LP HEATER 1C failed to indicate properly with the condition given (alarm not in with the low level condition). Need to investigate and resolve the issue. Did perform lamp test on P840.A2 3-5 and it look normal. <I> **** Actions Taken **** CRS/SM informed. | 02-00-HD-LS-1CL
393139 | CR | 20190510 |  | 4 | Rental PO of M&TE Did Not Reference Calibration PO |  |  |  | N | NO | <D> **** Detailed Description **** PO 00354083 utilized to rent Crane M&TE for R24 did not reference the Calibration PO in place with Crane, PO 00318189. <I> **** Actions Taken **** PO 00354083 to rent M&TE from Crane for R24 did not reference calibration PO 00318189 EN has in place with Crane (Crane is on our ESL) to provide the quality requirements needed to accept their calibrations. Procurement, Purchasing, QC Receiving, and Technical Services Program Manager were notified. Purchasing revised PO 00354083 to reference Calibration PO 00318189 and sent revised PO to Crane. Crane then re-issued calibrations with the correct PO referenced. The M&TE then went through the QC Receiving process and was then issued to the customer.
393140 | CR | 20190510 |  | 4 | Hydrogen Differential Flow Alarm received at HMI panel | N | N |  | N | NO | <D> **** Detailed Description **** During plant shutdown alarm ID HS HFLWDLT-STAT ALM, Hydrogen Differential Flow, was received. The alarm came in and cleared multiple times. <I> **** Actions Taken **** CRS and chemistry supervision informed. Alarm acknowledged on HMI.
393142 | CR | 20190510 |  | 3 | Procedure enhancement for CSP-INST-H201 |  |  |  | N | NO | <D> **** Detailed Description **** Prerequisite 3.1 of the procedure requires "Obtain permission and signature from the Shift Manager/Control Room Supervisor" This prerequisite is a hold-over from previous revisions of our surveillances that required the cover page to be signed. <I> **** Actions Taken **** Discussed the prerequisite with the CRS.
393143 | CR | 20190510 |  | 3 | Procedure enhancement for 12.5.44. |  |  |  | N | NO | <D> **** Detailed Description **** There is a formatting issue in 12.5.44 RCS Dissolved Hydrogen and Oxygen Monitoring. A section of the procedure, Termination of Cross Tie SP-8 to SP-1, on page 6 does not have its own section (5.5) as was intended. As such all future sections are also misidentified by having a lower section number than they should. <I> **** Actions Taken **** Specialist/supervisor informed.
393145 | CR | 20190510 |  | 4 | RFW-P-1A pulse input card fault RFW-P-1A on single CPU | N | N |  | N | YES | <D> **** Detailed Description **** RFW-P-1A indicates pulse input card fault and indicates on single cpu only. Main control room alarms currently in are PI-TR-PI-ERROR and PI-TR-DUELMODE. RFW-P-1A appears to still be responding as expected. <I> **** Actions Taken **** Notified CRS/SM and OCC. <N> Re-opened CR to allow RX startup tracking modifications. | 02-00-RFT-CP-COM2
393147 | CR | 20190510 |  | 3 | (R24LL) TG Hallway Doors | N | N |  | N | NO | <D> **** Detailed Description **** WO 02113307 task #01 directs craft to block open TG Hallway Doors. There is no task to notify Security prior this work being performed. There are signs posted on the doors that direct craft to contact Security before blocking or removing the door. We can reduce risk by adding a task in the WO to contact Security prior to beginning work. <I> **** Actions Taken **** Security Supervision Notified, Craft Supervision Notified, OCC Notiified. CR Generated <N> Task has been opened to MWO. No futher actions required.
393149 | CR | 20190510 |  | 4 | MS-TCV-115B and MS-TCV-116B will not indicate full closed | N | N |  | N | YES | <D> **** Detailed Description **** MS-TCV-115B and MS-TCV-116B will not indicate closed in the control room. MS-TCV-115B indicates full open. MS-TCV-116B indicated intermediate. Normal plant shutdown procedure 3.2.1 has a note that says if power is reduced to LT 400MWE and the MSR 2nd stage inlet isolation valves should be closed to reduce thermal transient to the MSR. Temperatures on DEH display indicate that the valves are not full shut. <I> **** Actions Taken **** Informed CRS/SM <N> Re-opened CR to allow RX startup tracking modifications. | 02-00-MS-TCV-115B,02-00-MS-TCV-116B
393150 | CR | 20190510 |  | 4 | FLM pre-outage steam leak walkdown at 65-55% power. |  |  |  | N | YES | <D> **** Detailed Description **** Completed FLM steam leak walkdown (pre-outage) per WO 02115216 and found the following new leaks: --HD-V-15D W3 packing leak at 5 dpm --MS-V-102B, W3 packing leak at 1 dpm --HD-V-2A27 S4 packing leak --RFW-V-709 W5 packing leak <N> **** Equipment Description **** TG | 02-00-HD-V-15D,02-00-MS-V-102B
393152 | CR | 20190510 |  | 3 | R24LL Regarding Emergent Need for CW Screen Cleaning. |  |  |  | N | NO | <D> **** Detailed Description **** On 5/10 while shutdown was in progress operations identified an emergent need for Circ Water screen cleaning for more than 7 shifts of 24 hour coverage. There was no work order in the schedule and no resource planned for covering this work, which is needed for every shutdown. Significant unplanned overtime costs and emergent planning required to support, in addition to resource reallocation required to support. <I> **** Actions Taken **** Arranged appropriate support, assured WO generated, assured OSCR written. Action recommended for outage management to create appropriate WO to add to the shutdown backbone schedule so itâ€™s a planned activity next outage. <N> This would have best been captured under W/O 02115591.
393153 | CR | 20190510 |  | 4 | Recieved 4.602.A13 drop 1-3 ASD1A/1 alarm |  |  |  | N | YES | <D> **** Detailed Description **** Recieved 4.602.A13 drop 1-3 ASD1A/1 alarm while lowering recirc pump speed. Local indication is alarm was caused by GTO GATE DRIVER new GTO alarm was 1FLT5 also 1FLT4 is previously identified. 1FLT5 initially was in and clear alarm was reset and about 5 minutes later alarm came back in and locked in. <I> **** Actions Taken **** Dispatched EO to address ARP. <N> **** Equipment Description **** ASD1A/1 drive . Re-opened CR to allow RX startup tracking modifications.
393154 | CR | 20190510 |  | 4 | BS-V-22A is Stuck OPEN | N | N |  | N | YES | <D> **** Detailed Description **** Motor Operated BS-V-22A will not CLOSE from the control room. Sent an operator to declutch and mannually close; unable to manually close BS-V-22A. <I> **** Actions Taken **** Discussed with Control Room and OCC <N> WO 02123280 is already within scope in R24 and is sufficient to resolve the problem identified in this CR. . Re-opened CR to allow RX startup tracking modifications. | 02-00-BS-V-22A
393155 | CR | 20190511 |  | 4 | DW-LCV-11 stuck open | N | N |  | N | YES | <D> **** Detailed Description **** DW-LCV-11 is stuck open. This is causing the condensate return tank to overflow. Until the valve is fixed, control will need to be by the bypass and will require more frequent monitoring by Operations. Recommend fixing the valve so more attention can be placed on the rest of the outage tasks. | 02-00-DW-LCV-11
393156 | CR | 20190511 |  | 3 | Approved OSP scope does not match planned instructions |  |  |  | N | NO | <D> **** Detailed Description **** AR OSCR 381118 was generated to repair the S5 body to bonnet leak on RFW-FCV-10B. The OSCR was approved at OSP with a 6-0 to â€œrepair the bonnet leak and add contingency tasks for full repair of valve (L5 Contingency).â€ WO 02129049-01 has three steps: verify the engineer and/or valve tech is present, verify the valve bonnet assembly is in alignment, and stroke the valve. The scope of the work that was planned does not align with the approved scope of the OSCR, as these three steps will not repair the bonnet leak. This CR is being written to document a difference between approved OSP scope, and what is planned. <N> WO02129049 Taks 07 ccovers the requirements for the rebuild of RFW-FCV-10B. No further actions at this time.
393157 | CR | 20190511 |  | 3 | Approved OSP scope does not match planned instructions |  |  |  | N | NO | <D> **** Detailed Description **** AR OSCR 389155 was generated to investigate the RFW-P-1B high pump thrust indication. The scope of the requested work was to investigate the instrument indications, with a contingency to investigate the pump thrust bearing if no issues are identified with the instrumentation. This scope of work was approved at OSP with a 6-0 vote. WO 02138514 was planned to calibrate/repair the vibration probes. No contingency task was planned or created. This CR is being written to document a difference between approved OSP scope, and what is planned. An assignment to outage management to review the process of communicating approved scope to planning is suggested. <N> Work instructions updated and back at approved status. No further actions required.
393158 | CR | 20190511 |  | 4 | XD4 Flow Warning |  |  |  | N | YES | <D> **** Detailed Description **** XD4 receiving multiple flow warning. Request I&C support to mitigate issue. Contact 2185 for more details. <I> **** Actions Taken **** Initiate CR/WR. Security supervision notified. OCC notified. | 02-00-SEC-XD-4
393159 | CR | 20190511 |  | 3 | MSRV SPVD Computer and printer problems during testing |  |  |  | N | YES | <D> **** Detailed Description **** During performance of WO 02110822-01 ISP-MS/IST-R101 MSRV SETPOINT VERIFICATION USING SPVD, the SPVD Computer froze when trying to print the as-found test results. This prevented recording of some of the test data (although the setpoints were still able to be recorded) and delayed testing approximately 30 minutes to 1 hour to reboot the computer and continue with the test. The printer was bypassed for the remainder of the testing and the test data was manually recorded. <I> **** Actions Taken **** Notified the control room and supervison of the delay. Bypassed the printer as allowed by procedure . Closing to cross referenced WR. Notified I&C. | 02-00-MS-CP-SPVD
393160 | CR | 20190511 | CAQ | C | Three MSRVs failed as-left set pressure tests | Y | N |  | N | YES | <D> During MSRV setpoint testing WO 02110822-01, all 10 valves being tested passed their as-found relief setpoint tests with setpoints within the -5% to +3% of nameplate setpoint range. Three valves were unable to be recertified to the TS required +/-3% of setpoint range (MS-RV-1B, MS-RV-1A, MS -RV-3B). These valves were tested 5 times total. MS-RV-1B final setpoint test was -3.49% of 1165psig nameplate setpoint, MS-RV-1A final setpoint was -5.45% of 1175psig nameplate setpoint, MS-RV-3B final setpoint was -5.61% of 1185psig nameplate setpoint after 5 tests. These all failed in the conservative direction meaning they would lift prior to reaching their nameplate lift setpoint. The unsatisfactory set pressure does not affect the ADS or air operated relief functions. Per ISP-MS/IST-R101 Step 6.1.4 "Any MSRV with Set Pressures not within TS SR 3.4.3.1 and 3.4.4.1 tolerances shall be adjusted, repaired or replaced, the cause of failure determined and corrected, and the valve shall successfully pass a retest prior to return to service." MS-RV-1B is already scheduled to be replaced with a refurbished valve in R24. Since CGS does not have the capability to adjust, repair, or retest these valves on site, it is recommended MS-RV-1A and MS-RV-3B be removed and sent offsite for repair. <I> Notified control room and OCC during setpoint testing <N> The valves all passed the as-found setpoint which is the test that determines past operability. They all would have performed their needed relief function during a real event. The recertification test is what allows them to continue to be used in the next cycle without any repair work. <R> REP/REGE assignments have been cancelled with Licensing Supervisor concurrence. | 02-00-MS-RV-1A,02-00-MS-RV-1B,02-00-MS-RV-3B
393162 | CR | 20190511 |  | 4 | RFW-RV-116A found leaking during system walkdown |  |  |  | N | YES | <D> **** Detailed Description **** At ~15% power during walkdowns RFW-RV-116A was found to be leaking. See EDMS Photos. This valve is scoped for R24 replacement via WO 02044023 so no WR generated. <I> **** Actions Taken **** Reviewed valve history and PMs. | 02-00-RFW-RV-116A
393163 | CR | 20190511 |  | 4 | MS-LS-24J leak and odor |  |  |  | N | YES | <D> **** Detailed Description **** During engineer pre-shutdown walkdown at 15% pwr, MS-LS-24J appeared to have a small steam leak or smoke and an odor of burnt electrical smell. Also, the EPN label on the component was damaged and illegible. <I> **** Actions Taken **** Informed EOC, discussed with peer and we checked that it is not on FLC list <N> **** Equipment Description **** Below BPVs, TG471 htr bay | 02-00-MS-LS-24J
393164 | CR | 20190511 |  | 4 | RFW-V-709 packing leak found during system walkdown |  |  |  | N | YES | <D> **** Detailed Description **** At ~15% power RFW-V-709 was found with a packing leak during system walkdowns at <25% power. See EDMS photo. <N> **** Equipment Description **** Column G.5/7.4 elevation 484.5 | 02-00-RFW-V-709
393165 | CR | 20190511 | CAQ | D | FP-V-352 Leaking | N | Y |  | N | YES | <D> **** Detailed Description **** While performing shutdown system walkdown, FP-V-352 has a packing leak, approximately 5 drops per minute. This is online work and should not be performed during R24. <I> **** Actions Taken **** Initiated CR. Minor leak does not adversely affect valve functionality. <N> **** Equipment Description **** Flocculator Bldg. | 02-00-FP-V-352
393166 | CR | 20190511 | CAQ | D | DEH Trip Tricon DO fault needs cleared | Y | Y |  | N | YES | <D> **** Detailed Description **** The Trip Tricon is in alarm due to a field fault on the slot 5 digital output module (load/fuse LED lit on 3603E module) . Recommend attempting to clear the fault via the engineering workstation DEH-COMP-4. This is also bringing in the DEH Trouble alarm. <N> Re-opened CR to allow RX startup tracking modifications. | 02-00-DEH-CHS-TRIP
393167 | CR | 20190511 | CAQ | D | FP-V-344 Leaking | N | Y |  | N | YES | <D> **** Detailed Description **** While performing shutdown system walkdown, FP-V-344 was observed to have a minor packing leak, approximately 2 drops per minute. This is online and should not be performed during R24. <I> **** Actions Taken **** Initiated CR. Minor leak does not adversely affect valve functionality. <N> **** Equipment Description **** Flocculator Bldg. | 02-00-FP-V-344
393170 | CR | 20190511 |  | 3 | Revise steps for ventilating main generator exciter housing |  |  |  | N | NO | <D> **** Detailed Description **** SOP-MT-SHUTDOWN step 5.1.25 should be revised to state, â€œIF the Main Generator rotor radial lead seal has a leak, THEN INITIATE action to ventilate the main generator exciter housing per SOP-H2/CO2-OPS.â€ The existing steps in SOP-MT-SHUTDOWN are redundant to SOP-H2/CO2-OPS and the two procedures provide slightly different guidance. The direction to â€œinitiate actionâ€ is more appropriate than â€œperformâ€ since actions to continue shutting down the turbine need to continue in parallel with ventilating the exciter. Also, consider if the steps from SOP-MT-SHUTDOWN to disconnect the power to the generator ground detection system and hang a caution clearance should be added to SOP-H2/CO2-OPS. Add direction provide appropriate signs for FME control and danger barrier for the open exciter doors. <I> **** Actions Taken **** Discussed with Control Room. Lessons learned from R24 shutdown.
393171 | CR | 20190511 |  | 3 | R24LL Update SOP-DW-ENTRY for EDR-V-601/602 checks |  |  |  | N | NO | <D> **** Detailed Description **** Add step to SOP-DW-ENTRY for initial entry specific for refuel outages to check EDR-V-601/602 closed. This is required for PPM 10.3.21 step 6.5.2.b and prevents a re -entry (dose savings). This was performed in R24 per task instructions during initial entry and worked well with entry sequence/eliminates and extra entry.
393172 | CR | 20190511 | CAQ | D | RRC-P-1B motor bearing oil low | N | Y |  | N | YES | <D> **** Detailed Description **** Received RECIRC B MOTOR BEARING OIL LEVEL LOW alarm P602-A6 drop 1-8 after the reactor was shutdown for R24. The lower bearing dropped to -1.2" and the upper bearing is at -0.6". please add oil during R24. | 02-00-RRC-P-1B
393173 | CR | 20190511 |  | 3 | (R24 LL) OSP-RPS-B401 PCR |  |  |  | N | NO | <D> **** Detailed Description **** OSP-RPS-B401 has placing the mode switch to refueling first, then back to shutdown to attempt to withdrawal a control rod. Recommend moving the control rod withdrawal check (step 7.14 and 7.15) to the beginning of the surveillance so we donâ€™t have to wait for the SDV to drain during the scram that occurs when we place the mode switch back to shutdown. This will save time during the shutdown.
393175 | CR | 20190511 |  | 3 | PPM 3.2.1 not aligned with SOP-MT-SHUTDOWN |  |  |  | N | NO | <D> **** Detailed Description **** PPM 3.2.1 step 5.3.4 has steps to remove the MSR 1st stage reheat by aligning HV-V-38A, 38B, 39A, & 39B; but does not have steps to complete the line up by shutting BS-V-1A, 1B, 2A, & 2B (Reference SOP-MT-SHUTDOWN section 5.1.9e) leading to a possible PCSC error. Recommend either aligning both 3.2.1 section 5.3.4 and SOP-MT-SHUTDOWN section 5.1.9, or having PPM 3.2.1 step to remove MSR 1st stage reheat per SOP-MT-SHUTDOWN. <I> **** Actions Taken **** Informed shift supervision, completed line up per SOP-MT -SHUTDOWN.
393176 | CR | 20190511 |  | 4 | COND-PI-65B stuck upscale again | N | N |  | N | YES | <D> **** Detailed Description **** COND-PI-65B has stuck upscale again. Reference previous CR 292090. This was found at ~20% power during system walkdown. <I> **** Actions Taken **** Reviewed component history. <N> **** Equipment Description **** T -450- - -F5/10.8- | 02-00-COND-PI-65B
393177 | CR | 20190511 |  | 4 | HP Turb Left Side Steam Chest insulation cracked and broken | N | N |  | N | YES | <D> **** Detailed Description **** During the R23 outage (in 2017), insulation on the Left Side Steam Chest near MS-V-GV/1 and MS-V-GV/3 deteriorated and required repair. New hard insulation was OSCRâ€™d (AR 366812) and installed under WO 02090289. This new insulation is cracking and spalling and some pieces have fallen off. The new damage does not appear to be steam impingement and no leaks were found in the area. <I> **** Actions Taken **** Informed EOC <N> **** Equipment Description **** Left side HP Turbine steam chest (south side), TG501 | 02-00-MS-DT-HP
393178 | CR | 20190511 |  | 4 | GREEN light not illuminated on NRCVs post SCRAM | N | N |  | N | YES | <D> **** Detailed Description **** During engineer post shutdown walkdown following SCRAM, three NRCVs were showing no indication for position. E-IR-4: BS-V-10C and BS-V-10D (to COND-HX-3B) E-IR-5: BS-V-10F (to COND-HX-3C) The indication for these NRCVs should be closed with only the green light illuminated. However, both red and green lights are extinguished. <N> **** Equipment Description **** TG 471 heater bay in overhead . Re-opened CR to allow RX startup tracking modifications. . cancelled by mistake. reopened and taken to complete | 02-00-BS-V-10C,02-00-BS-V-10D,02-00-BS-V-10F
393179 | CR | 20190511 |  | 3 | OSP-MT-W701 procedure enhancment |  |  |  | N | NO | <D> **** Detailed Description **** Step 7.1.10 has the operator evaluate if trip times are greater than 590 milliseconds but it is not clear that this is done before or after stroking the valves an additional 2 times. Please move Step 7.1.11 to before 7.1.10. <I> **** Actions Taken **** wrote CR.
393181 | CR | 20190511 |  | 3 | R24 LL I&C stage N2 bottle for SOP-SCW-SHUTDOWN sched wrong |  |  |  | N | NO | <D> **** Detailed Description **** 02115576-23 I&C stage N2 bottle and regulator should have been scheduled as a pre-outage task. This task is a predecessor for SCW Shutdown task as part of preps to open the MT-MG windows. The task was inappropriately scheduled for the day AFTER the SCW Shutdown task 02115576-26.
393182 | CR | 20190511 |  | 3 | sop-rhr-sdc |  |  |  | N | NO | <D> **** Detailed Description **** AR 207240 added a fill and vent evolution to SOP-RHR-SDC as a means to minimize the level drop when initially initiating SDC. this addition created a 30 - 45 minute delay in starting RHR after warming the system. this delay resulted in larger than desired differential temperature. enginerring should advise operations as to what more important, potential voids or low differential temperatures. in all cases, the system was not breached and any gases are solely due to heat up and aligning between RPV and RHR. <I> **** Actions Taken **** no action required.
393183 | CR | 20190511 | CAQ | C | Air observed during OSP-RHR-M102 (RHR B fill verification) | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Air was observed for 16.08 seconds from the RHR-V-622B vent path (RX 572, RHR B HX rm). Per OSP-RHR-M102, an AR should be generated to prompt Engineering evaluation if air is present for GT 6.1 Seconds. Air was also present at the RHR-V-741 (RX 501 SW valve rm) vent path for 2.28 Seconds, this also requires Engineering evaluation. Air was present from the RHR-V-633B vent path for only 4.19 Seconds, this does not require evaluation but is being included in the AR for informational purposes . Note, this fill verification was being performed in support of starting RHR B Shutdown Cooling. Part of SOP-RHR-SDC is to perform a flush of the RHR system with RPV water while the RHR B system is isolated from its' keep fill system. The presence of air was not entirely unexpected. The air present could be characterized as "slugs" of air. Engineering please perform Evaluation per OSP-RHR-M102. <I> **** Actions Taken **** informed CRS. <N> **** Equipment Description **** OPS-RHR-M102 presence of air afer SDC flush
393184 | CR | 20190511 |  | 3 | OSP-INST-H102 need updated |  |  |  | N | NO | <D> **** Detailed Description **** Several stations in eSoms still refer to TSP-SRM-W401 for information. This procedure was superceded by TSP-SRM-M401. <I> **** Actions Taken **** Administrative issue only.
393185 | CR | 20190511 |  | 4 | DG-3 Governor Oil LOOS | Y | N |  | N | YES | <D> **** Detailed Description **** DG-3 Governor Oil LOOS. Oil reads at the midline mark while low spec is 1/4" above midline to high out of sight on gauge for high spec. <I> **** Actions Taken **** Informed CRS, SSS. The indicator is actually reading >1/4" above the low level mark (approx 1/2"). The new DG3 governor gage glass is larger than DG1 and DG2 glasses, so the mid point is actually much higher on DG3. There is no degraded condition and the governor oil level is at the correct value. <N> **** Equipment Description **** D-3 HPCS Governor Oil gauge
393186 | CR | 20190511 |  | 3 | R24LL: SOP-ELEC-DIV2-TEMPPOWER Rev 11 needs corrections. |  |  |  | N | NO | <D> **** Detailed Description **** SOP-ELEC-DIV2-TEMPPOWER Rev 11 step 5.42.16 needs to be corrected from â€œremove caution tag on E-DISC-PPF10/2/7/1â€ to â€œremove caution tag from POWER CORD at weld receptacle powered from E-DISC-PPF10/2/7/1â€ as this is where the tag is located. Also, step 5.42.17 needs to be removed as there is not a caution tag hanging on E-42-8B10D. There was only a danger tag on it and it was removed in step 5.42.13. <I> **** Actions Taken **** Marked up procedure and delivered to OPS procedure group.
393187 | CR | 20190511 |  | 3 | (QA) Procedure Discrepancy PPM 10.2.14 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Maintenance Coating Program procedure PPM 10.2.14 contains a discrepancy regarding surface preparation prior to application of Carboguard 890N. Steps 1.3 and 1.4 of AP-54 on Page 53, indicate that 890N is to be applied over existing coating. The note referenced in step 1.4 at the bottom of page 53 states that coated surfaces are to be prepared to SP-6, which would remove existing coating. A procedure change is needed to specify a preparation method appropriate for coated surfaces, such as solvent wipe. . This issue was identified by QC during task preview activities and affects scheduled outage work including WOTs 02120897-05/06, 02120340-34 and 02136481-06/08. . <I> **** Actions Taken **** Notified Quality Services Supervisor, Project Manager, EOC and Engineering Coatings Program Owner.
393188 | CR | 20190511 |  | 4 | TSW-TCV-9 does not go full shut. | N | N |  | N | YES | <D> **** Detailed Description **** TSW-TCV-9 indicates 17.5% open with max output from the temperature controller. ( 23.5 psig ).. This is a 3-15 psig controller. Suggest loop cal. to determine if the valve or the controller is the culprit. Also note that there is flow noise with the inlet valve shut. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 471W. | 02-00-TSW-TCV-9
393189 | CR | 20190511 |  | 4 | TSW-V-28A does not isolate flow. | N | N |  | N | YES | <D> **** Detailed Description **** TSW-V-28A does not isolate flow when shut. With TSW-V-28A shut flow noise can be heard and the flow noise reduces when TSW-TCV-9 outlet isolation is moved in the shut direction. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 471W | 02-00-TSW-V-28A
393190 | CR | 20190511 |  | 4 | Squishing noise while slowly closing E-CB-N2/5 | N | N |  | N | YES | <D> **** Detailed Description **** While performing E-CB-N2/5 circuit breaker inspection under WO 02112084, electricians identified squishing noise while performing step 7.7.1 section e of ESP-CBN25-F101. This steep requires electricians to use a maintenance handle to slowly close the breaker. The nature of the noise seemed like something is either rubbing or tight. All other breaker tests have been SAT. <I> **** Actions Taken **** Informed EOC to track the issue <N> See video in the EDMS folder Based on the visual inspection perform on both the breaker and in the switchgear, there was no signs of ware paticles to indicate any metalic rubbing. This squishing sound is potentially from a rubber piece connected to the piston rod. This noise should not affect the design operation of the breaker | 02-00-E-CB-N2/5
393191 | CR | 20190511 |  | 3 | R24 LL: Update SOP-H2/CO2-OPS to be more efficient |  |  |  | N | NO | <D> **** Detailed Description **** Steps in SOP-H2/CO2-OPS say to verify SCW shutdown per SOP-SCW-SHUTDOWN. Update this step to say "verify SCW Pumps have been secured per SOP-SCW-OPS". This will allow Ops to move on more efficiently through the Main Generator shutdown process.
393192 | CR | 20190511 |  | 4 | small glycol leak from upper seal of filter for GY-F-10A1 | N | N |  | N | YES | <D> **** Detailed Description **** A small glycol leak from upper seal of filter was observed in GY-F-10A1. During walk down, a drip from handle was visible . Some moisture was noted in paper placed below filters as shown in pic attached in EDMS.Similar kind of leak was documented in CR 00386621 and WR 29145547 was completed by replacing Oring on 12/13/18. <I> **** Actions Taken **** Notified EOC and created WR to fix the leak. <N> **** Equipment Description **** VR 441 F1/18.7 . Re-opened CR to allow RX startup tracking modifications. | 02-00-GY-F-10A1
393194 | CR | 20190511 |  | 4 | R24: M2 Bushing Leaks - Gaskets Need Replaced | N | N |  | N | YES | <D> **** Detailed Description **** During the implementation to tighten the low-side bushing flange to tank connections on the Main transformer M2, Leaks continued around both east and west doghouse bushings and around the gaskets of each low-side bushings vent plugs. . Main Transformer M2 needs to have the bushings removed, replaced/and/or gaskets replaced. Also the vent plug gaskets on both bushings need replaced. This requires draining the oil down below the low-side bushings. BPA estimates the time will take three twelve hour day shifts from start to finish. <I> **** Actions Taken **** Notified, Supervision, OCC and BPA has been directed to mobilize equipment <N> Re-opened CR to allow RX startup tracking modifications. | 02-00-E-TR-M2
393195 | CR | 20190511 |  | 3 | broken rigid strap bolt | N | N |  | N | NO | <D> **** Detailed Description **** 3/4 inch conduit was being temporarily removed per work steps on cond-p-2a. A 1/4 inch bolt was old and broke. 02077541-01 <I> **** Actions Taken **** notified supervision CR <N> **** Equipment Description **** COND-P-2a conduit AM3C-210-001
393196 | CR | 20190511 |  | 3 | PCR: SOP-RHR-SDC-BYPASS |  |  |  | N | NO | <D> **** Detailed Description **** The RHR-V-8 bucket has been changed since the last time this procedure was completed. The bucket no longer clearly identifies the 5 amp fuses as N or P in step 5.2.6. (d,e) and 5.2.10 (b,c). This caused a delay while performing the procedure. Recommend changing the procedure from labeling the fuses as â€˜Nâ€™ and â€˜Pâ€™ to â€˜FU3â€™ and â€˜FU4â€™ respectively. Also the fuses are in a hard to reach place. Recommend purchasing extended length fuse pullers to easily access them. We used a 450V PPE glove to shield the worker from components they had to touch in order to squeeze their hand in and pull the fuses. <I> **** Actions Taken **** CR written <N> pictures attached
393198 | CR | 20190511 |  | 4 | TMU-RLY-63X/FIS/5C/8 repeated actuation | N | N |  | N | YES | <D> **** Detailed Description **** During walkdown of the TMU pumphouse, repeated actuation of TMU-RLY-63X/FIS/5C/8 could be heard. The observed frequency of actuation ranged approximately from once per 10 seconds up to three - four times per second. The frequent actuation of this relay is detrimental to the long-term reliability of this component. This relay is part of the prelube flow start permissive logic for TMU-P -1C. The corresponding flow indicating switch, TMU-FIS-5C, was also observed to read approximately 2.5 gpm, and periodically swing to an off-scale high reading. The leakby past TMU-V-18C (00387729) is a likely contributor to this issue. | 02-00-TMU-RLY-63X/FIS/5C/8
393199 | CR | 20190511 |  | 4 | TMU-PI-9 reading high | N | N |  | N | YES | <D> **** Detailed Description **** TMU-PI-9 was reading 200 psi (out-of-tolerance high). This pressure gauge is the local indicator for the TMU discharge pressure sensing line, which controls the opening of TMU-V-1. TMU-PI-9 is used for local indication and troubleshooting only, and has no history of calibration. TMU-PI-9 is a run-to-failure component. Recommend calibration or replacement of the pressure gauge. The corresponding pressure control switch, TMU-PS-9, appears to be functioning as intended. | 02-00-TMU-PI-9
393200 | CR | 20190511 |  | 3 | R24LL: MSIV LLRT missing logic tie |  |  |  | N | NO | <D> **** Detailed Description **** MSIV local leak rate testing is performed per TSP-MSIV-B801 with RPV water level being maintained below the main steam lines. However, the R-24 schedule has operations raise water level up to the RPV flange which is 80 inches above the main steam lines at the same time as the MSIV LLRT. There is a missing logic tie between SO-0SHD-0760 (TSP -MSIV-B801) and SO-0R606-1225 (Raise water level 2-6 inches below the RPV flange). These two outage tasks need to be performed in series, not parallel. The MSIV LLRT needs to be completed first.
393201 | CR | 20190511 | CAQ | D | SEC-PAAP-IRE Not Functioning as Designed |  |  |  | N | YES | <D> **** Detailed Description **** SEC-PAAP-IRE is not functioning as designed and requires maintenance. Request maintenance support. Contact 2185 for more details. <I> **** Actions Taken **** Security supervision notified. Initiate CR/WR. Compensatory measures posted. Notifications made to OCC. | 02-00-SEC-IDS-PAAP/IR/E/S
393204 | CR | 20190511 | CAQ | C | Outboard MSIVs Dry stroked during R24 | Y | N |  | N | YES | <D> **** Detailed Description **** The outboard MSIVs were dry stroked to complete surveillance OSP-MS/IST-Q701 during R24. Entry into the drywell and steam tunnel is required to perform this surveillance. Sufficient time was planned to complete the activity prior to the 12 hours from wetting expiring however, the drywell and steam tunnel were both locked and it took significant time to reopen them to proceed. The OCC was notified when access was not permitted. Engineering was notified and allowance was provided per SOP-MSIV-OPS to stroke the valves after the 12 hours from wetting expired. | 02-00-MS-V-28A,02-00-MS-V-28B,02-00-MS-V-28C,02-00-MS-V-28D
393205 | CR | 20190511 |  | 4 | Individual was issued wrong DLR |  |  |  | N | NO | <D> **** Detailed Description **** A wrong DLR was issued to SSC. The craftsman attempted to log into the RCA when he read on the computer screen someone elseâ€™s name. He stopped immediately and contacted his General Foreman to report the issue. HP was contacted and was able to issue out a new DLR to the individual. <I> **** Actions Taken **** General Foreman was contacted immediately and Supervison. Hp's also contacted to resolve the issue. <N> Williams Plant Services.
393206 | CR | 20190511 |  | 3 | Procedure change for SOP-ELEC-BKR-OPS |  |  |  | N | YES | <D> **** Detailed Description **** The instructions in step 5.22.3 and step 5.22.5 of SOP -ELEC-BKR-OPS needs to be changed to the instructions in step 5.23.5 which would allow the user to rack in a grounding device when directed to by PPM 10.25.141A or PPM 10.25.141B. The current procedure only allows the rack in of a grounding device when directed to by PPM 10.25.141A. Reference WO 02115599. <I> **** Actions Taken **** Notified CRS and wrote CR. | 02-00-E-EQ-GD/416/3000/M2
393207 | CR | 20190511 | CAQ | C | Error in wiring labels in 10.8.1 | N | N |  | N | NO | <D> **** Detailed Description **** While craft was performing WO #02119702-18 determing wires located in panel ZTB-4 on term points TB2-1 and TB2-2, the procedure 10.8.1 determ reterm sheet stated that the wire are label as 6-P67-P1 and 6-P67-N1, the wires out in the field is 6-D67-P1 and 6-D67-N1. <I> **** Actions Taken **** Craft stop work and notified Supervisor. EOC and OCC was notified, CR was written. Based upon field configuration and previous WO history for determination of Fire Protection zone 67 the wiring isin conflict. The EWD and procedure call out 6-P67-P1 and 6-P67-N1, however field wiring shows a 6-D67-P1 and 6-D67-N1. Previous work order history (WP #02087409-10) shows that the field configuration was used in the past with success. Request that the procedure/drawings be updated or the field wiring get new labels. Marked up procedure with OCC and EOC agreement. <N> **** Equipment Description **** 501' turbine No label request is needed, AR/CR was for tracking on Procedure enhancement to update the determ reterm sheet or to have engineering to verify the wiring in the field was correct or incorrect. At that time once it was determined then at the next outage either the labels will be corrected at that time, which we have the means to produce, or the procedure will be updated by then
393208 | CR | 20190512 |  | 4 | S-DOOR-S110 Degraded | N | N |  | N | YES | <D> **** Detailed Description **** The closing device for S-DOOR-S110 is failing. The door currently closes, but the closing device is loose which impedes door movement. <I> **** Actions Taken **** Wrote CR and ISPM-10 impairment 19-0019 | 02-00-S-DOOR-S110
393209 | CR | 20190512 |  | 3 | SOP-SCW-SHUTDOWN enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Add step 5.2.8 to isolate SCW demins to section 5.1 as well (operator good practice in case SCW drained at a later point.)
393210 | CR | 20190512 | CAQ | C | MS-V-28C 3 sec criteria TDAS closing time too fast | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of OSP-MS-IST-Q701 per WO 02111819, MS -V-28C 3 second criteria closing time with air isolated (Sect 7.24) was too fast. The action lo spec per OSP-MS/IST -Q701 is 2.66 seconds. The stopwatch time was 2.66 seconds, and the TDAS time was 2.610 seconds. The 3 second criteria closing time with air liined up (Sect 7.8) was also too fast. The action lo spec per OSP-MS/IST-Q701 is 2.66 seconds. The stopwatch time was 2.83 seconds, and the TDAS time was 2.640 seconds. MS-V-28C is scheduled for inspection and refurb in R24 per WO 02079277. <I> **** Actions Taken **** Informed CRS and production shift manager, wrote this CR and WR. | 02-00-MS-V-28C
393211 | CR | 20190512 | CAQ | C | In-correct data entered in TES |  |  |  | N | NO | <D> **** Detailed Description **** A workers dose margin was was entered incorrectly in TES. A contributor is that form 848 Dosimetry in-processing has data spaces which are unitless. <I> **** Actions Taken **** Corrected the margin in TES. Notified OCC RPM
393212 | CR | 20190512 |  | 3 | R24LL - SCW Clearance Schedule Logic |  |  |  | N | NO | <D> **** Detailed Description **** The SWC Clearance hang was scheduled incorrectly. The clearance requires an N2 bottle with a regulator to purge the SWC tank of the hydrogen blanket. Support task was not scheduled until 5/12 @ 0600 while clearance was scheduled for 5/11. I&C was able to respond and get the equipment for Ops. This staging task should have been scheduled during the pre-outage window. <I> **** Actions Taken **** Generated R24LL <N> WO 02146001 task 23 recoded as preoutage for R25. No furhter actions required.
393213 | CR | 20190512 |  | 4 | RCC-V-23A has a 20 DPM leak | N | N |  | N | YES | <D> **** Detailed Description **** RCC-V-23A, the discharge check valve for RCC-P-1A, has a leak out of the stem at approximately 20 drops per minute. Please repair. <I> **** Actions Taken **** Notified SMgt, requested laborers to install catchment, wrote CR. <N> **** Equipment Description **** RB 548 NE by elevator. | 02-00-RCC-V-23A
393214 | CR | 20190512 |  | 4 | Two employees had each others's assigned DLR's |  |  |  | N | NO | <D> **** Detailed Description **** Two employees with the same last name had DLR's which had been assigned to the other person. It is not known how this occurred. The employees are not in the same department. Neither employee entered the RCA during this time frame. <I> **** Actions Taken **** New DLR issued to one employee and the other had been restricted from RCA access to ensure that DLR.
393215 | CR | 20190512 | CAQ | C | Revise TS Table 3.3.5.1-1 note (e) | N | N |  | N | NO | <D> Revise TS Table 3.3.5.1-1 note (e) to delete reference to LCO 3.8.2 â€œAC Sources - Shutdownâ€. This change should have been included as part of the Tech Spec change to adopt TSTF-542, which was approved as Amendment 251. All the Mode 4 and 5 requirements are removed from TS 3.3.5.1. Thus, the reference to LCO 3.8.2 should also have been removed. The relevant Mode 4 and 5 instrumentation requirements are relocated to TS 3.3.5.2. The LOCA time delay relays are NOT included in TS 3.3.5.2. The ECCS initiation requirements in Mode 4 and 5 were revised from automatic initiation to manual initiation. As a result, the relays are not required to support the operability of TR-S in Mode 4 and 5. This was confirmed as part of the validation for the TSTF-542 amendment. This change should be included with the â€œTSTF-542 follow-upâ€ amendment and assigned to AR-LIC. <I> Discussed with Operations. <N> CR at INPROG, moved to APPROVED assigned to SRO for OPS review.
393216 | CR | 20190512 |  | 4 | Dragon Valve operator taken from EOP box for CRD-V-65 work | N | N |  | N | NO | <D> **** Detailed Description **** While connecting the drain line to CRD-V-65, the Dragon Valve operator was needed from the EOP tool box on the RB 522' North area. The operator was required to be left at CRD-V-65 for draindown operations. <I> **** Actions Taken **** Notified SSS and Production SRO, initiated the CR to document.
393217 | CR | 20190512 |  | 3 | Procedure enhancement SOP-SYS-FLUSH |  |  |  | N | NO | <D> **** Detailed Description **** I&C techs manipulate equalizing valves for excess flow check valves. Please put I&C letters under the initial blanks for these steps. <I> **** Actions Taken **** Informed Ian Bitner
393218 | CR | 20190512 |  | 3 | HD-LIC-1B replacement found faulty | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WO#02094544-01, one of the capacitors was found abnormally â€œlooseâ€ on the board while doing a visual inspection prior to installation. These components should be stationary and not exhibit this behavior. This could indicate a broken connection or poor solder joint. <I> **** Actions Taken **** Stopped work, informed supervisor and EOC, took video (see EDMS), and wrote this CR. <N> Condition has been restored. Work Order 02094544 completed. No further actions required. | 02-00-HD-LIC-1B
393219 | CR | 20190512 |  | 4 | CRD-V-65 Hose Leakage |  |  |  | N | YES | <D> **** Detailed Description **** While opening CRD-V-65 per WO 02077821-12 / 02073069-04, the fitting on the hose connected to the valve began leaking on the quick-disconnect side of the fitting. This problem occurred with two different hoses. Recommend replacement of this fitting or hoses with non-quick disconnect style fittings. <I> **** Actions Taken **** Closed CRD-V-65 to stop leakage, informed CRS, wrote CR. | 02-00-CRD-V-65
393220 | CR | 20190512 |  | 4 | Drain hose from CRD-V-65 leaking from quick disconnect |  |  |  | N | NO | <C> This is a duplicate of 393219. <D> **** Detailed Description **** After attaching the CRD drain hoses to CRD-V-65, the hose was found to be leaking from the quick disconnect end (not the O-Ring end). CRD-V-65 was shut, and another hose connected to drain. The second hose also leaked from the same quick-disconnect fitting. CRD-V-65 was closed and the work area was left to expand the team. <I> **** Actions Taken **** Notified SSS and Production SRO, initiated this CR.
393221 | CR | 20190512 |  | 4 | FDR-P-15A/15B level switches are failing. (For Sump T-4). | N | N |  | N | YES | <D> **** Detailed Description **** The level switches that control the start/stop of FDR-P -15A/FDR-P-15B are failing causing the pumps to always have one running. The level in T-4 sump is too low for them to always have one running. There is no High Level Alarm. If you turn off one pump the other starts. These pumps and switches are located in a High Rad Area During Operations. These should be fixed while we are shutdown. (See related AR/WR on FDR-P-15B discharge pressure). | 02-00-FDR-P-15A
393222 | CR | 20190512 |  | 4 | FDR-P-15B has low discharge pressure | N | N |  | N | YES | <D> **** Detailed Description **** than it should. This is the sump pump for T-4 sump. FDR -P-15B has 28psig discharge pressure and FDR-P-15A has 61psig. This is in a High Rad Area During Operation. This should be fixed while we are shutdown. (See related AR 00393221, CR 29148529, for the level switches controlling both pumps). | 02-00-FDR-P-15B
393223 | CR | 20190512 |  | 3 | R24 LL â€“ Incorrect Drawing Used to Provide Field Direction |  |  |  | N | NO | <D> **** Detailed Description **** While performing WO 02080035-07, the Craft identified 16 wires connected to the MS-V-164B Limit Switch Assembly however the Cable Termination Instruction (CTI) only identified 8 wires to determ. Upon research it was determined that the EWD drawings were used to provide the field direction on the CTIs to determ existing wires. The EWDs primarily provide functionality of circuits and do not necessarily show the complete configuration such as terminated spare wires. The connection wiring diagrams are the correct configuration control drawing that should have been used. <I> **** Actions Taken **** Discussed with the craft, craft supervisor and the EOC/CPM War Room. Processed EC16785R00B.FCR against the design change.
393224 | CR | 20190512 |  | 3 | Notified by vendor or potential part quality issue |  |  |  | N | NO | <D> **** Detailed Description **** This issue does not affect any installed equipment or equipment about to be installed during R24. CGS was notified by NLI that the CR120 relays currently supplied as part of CID 33799 have recently experienced a significant increase in failures during testing. GE sold the design and manufacturing to a new vendor. It was confirmed by the vendor that none of the materials purchased thus far under this CID are impacted and passed all performance testing. However, it is unclear if this issue impacts all CR120 type relays in manufacturing now, and it should be confirmed if this will impact all new relays. CGS has a large number of CIDs associated with this manufacturers model and part number. Recommend ensuring all new CR120 relays procured be evaluated for impacts. Email from vendor is attached in the EDMS. <I> **** Actions Taken **** Discussed with Procurement. Initiated CR.
393225 | CR | 20190512 |  | 3 | Long Term Storage of EOP Equipment |  |  |  | N | YES | <D> **** Detailed Description **** A EOP fitting was utilized to connect a hose between CRD -V-65 and a gravity drain. The fitting was degraded such that an internal o-ring was not properly providing a seal, which resulted in leakage. See CRs 393220, 393219, and 393216. Recommend evaluating periodic replacement of EOP equipment in long term storage. <I> **** Actions Taken **** Submited CR <N> **** Equipment Description **** EOP equipment in storage lockers
393228 | CR | 20190512 |  | 3 | FME covers left off of Hydrogen piping. |  |  |  | N | YES | <D> **** Detailed Description **** FME monitor was informed that Hydrogen piping on TG 441 west end associated with H2-V-49 and H2-V-8 had been 4 flanges broken open to support hydrogen clearances, but were not covered per PPM 10.1.13. One flange was covered correctly, one flange had an FME cover shoved into the pipe with duct tape wrapped around the flange to hold the FME cover in. This is inappropriet because the duct tape will leave a sticky residue on the flange surface. <I> **** Actions Taken **** The FME cordinator contacted OPS (Production manager on day shift of 5-12-19) OPS Production manager looked up Ops EO that conducted the work, and coached the individual via email. The FME cordinator ensured that the hydrogen piping was correctly covered with FME covers. No further actions required. FME cord. recomends a Non CAQ severity level 4 due to actions taken. Please code the CR with the following codes. D/MNT, C/OPS, FME <N> Shift manager coached the individuals involved. It was briefed during the Ops D15 at 0600 and email to all Supervisors for the HU event. CR can close with Ops actions taken | 02-00-H2-V-49,02-00-H2-V-8
393230 | CR | 20190512 | CAQ | D | Security IDS 24/25 | N | N |  | N | YES | <D> **** Detailed Description **** IDS 24/25 is not functioning as designed. Please contact Security at extension 2185 for further information. <I> **** Actions Taken **** Compensatory measures posted. CR/WR generated requesting Electrical Support. | 02-00-SEC-IDS-EVAL/24/25
393231 | CR | 20190512 | CAQ | C | Weld records altered and not routed through QC for review |  |  |  | N | NO | <D> **** Detailed Description **** In January of â€™19 weld records were altered/ created during the walk down for WO 02120347-01 and did not have a QCI hold placed on them for QC review. Worked with planning and QC added hold for review. This minor delay did not affect the schedule , as this was discovered prior to any work being started. <I> **** Actions Taken **** CR generated for documentation <N> Mechannical Shop.
393232 | CR | 20190512 |  | 4 | Late Scope Identificaiton prevented parts arrival in time. |  |  |  | N | YES | <D> **** Detailed Description **** Late Scope Identificaiton prevented parts arrival in time for R24. Ref WO 02134730, OSCR AR 385324, CR 370957, OSCR AR 393227 <I> Initiated OSCR 393227 to change scope from valve replacement to valve repair. Notifiedy OCC and EOC of the issue. <N> **** Equipment Description **** Turbine Bldg by SJAE B Need to investigate why this work was a late addition to the R24 scope when issue of leak was identified in 2017. DEW 5 -12-19 . â€¢ CR 370957 (COMP/NA) identified that MS-V-110B was leaking water at ~110 dpm on 9/4/17. â€¢ Associated WR 29138544 was flipped to WO 02134730 a year later on 9/12/18. â€¢ SELF assignment to review WO for inclusion created 9/28/18, â€œCOMPLETEâ€ 10/4/18 â€¢ OSCR 385324 was initiated on 10/3/18. â€¢ From the Attributes tab of the OSCR the OSCT meeting date was 10/17/18. From the Attributes tab of the OSCR the OSCR was approved on 1/28/19. â€¢ Planning assignment 04 created on 1/28/19 â€¢ Valve Material Request 239971 â€œAPPROVEDâ€ 2/14/19 â€¢ Planning assignment completed on 3/11/19 | 02-00-MS-V-110B
393233 | CR | 20190512 |  | 3 | R24LL: Cavity Fill |  |  |  | N | NO | <D> **** Detailed Description **** EDR-V-660 verified closed and EDR-V-603 verified open per SOP-CAVITY-FILL step 5.5. This would be more efficient if combined with PPM 10.3.21 when EDR-V-601 and EDR-V-602 are verified closed at step 6.5.2.b.
393234 | CR | 20190512 | CAQ | D | MS-V-28B and MS-V-28D Packing leaks during As-Found LLRT | Y | N |  | N | YES | <C> CR reopened to add completion required check mark to referenced WO/WR 02079278-01per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** During the As-Found LLRT testing of the MSIVâ€™s per TSP -MSIV-R801 (WO 02110152-01), minor packing leaks were identified at the stems of MS-V-28B and MS-V-28D. Both the B and D combined MSIV LLRTâ€™s passed their assigned admin leak rate values of 12.0 scfh. However, the packing should be verified to meet the required torque for the packing gland to preclude potential of steam leakage post R24. <I> **** Actions Taken **** Notified EOC/OCC/LLRT SRO <N> **** Equipment Description **** RB501' Steam Tunnel | 02-00-MS-V-28B,02-00-MS-V-28D
393235 | CR | 20190512 |  | 3 | (R24) Request FDR-SUMP-W2 temp. pump install |  |  |  | N | YES | <D> **** Detailed Description **** Request HP and laborer support to install a temporary sump in FDR-SUMP-W2. This is in support of SOP-ELEC-SH6-MAINT. Recommend adding a support task for this for future E-SH-6 outages. Refer to WO 02079546. <N> Temporary sump pump has been installed. No further action required. Tasks added to R25 SH6 overview WO 02151368 for future outages | 02-00-FDR-SUMP-W2
393237 | CR | 20190512 |  | 3 | Procedure Enhancement Required |  |  |  | N | NO | <D> **** Detailed Description **** PMM 10.25.105 provides instructions to electricians to perform inspection to motor control center (MCC) and switchgear. There has been continous, increasing failure rate of indication lights and light bases to the plant switchgears over the past 2 years. Therefore PPM 10.25.105 needs to be revised to allow electricians inspect indication lights and light sockets/base during the switchgear PM inspection and perform replacements as required. Mark-ups are provided and uploaded in the EDMS folder. <I> **** Actions Taken **** Had discussion with my supervisor <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
393238 | CR | 20190512 | CAQ | C | SDV Vent and Drain valves wonâ€™t open | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of PPM 8.3.361 the SDV V&Dâ€™s were noted to be OPEN per Prerequisite 3.4. The LSFT test PPM 8.3.361 proceeded normally until step 7.11 due to the SDV V&D valves not repositioning to OPEN; they remained SHUT. ARP was consulted power supplies were verified energized; fuses were verified to not have the red â€œblownâ€ indicator post popped. The scram reset buttons were depressed per the ARP, though all eight RPS Logic light on P603 were energized. CR 130644 documents a similar instance where a stuck valve caused CRD-V-10 and -11 to remain shut. | 02-00-CRD-V-10
393239 | CR | 20190512 |  | 3 | R24LL: Remove RPV Head schedule task duration too long |  |  |  | N | NO | <D> **** Detailed Description **** The schedule backbone task for removing the RPV head (SO -0R606-1260) has a schedule duration of 17 hours. Reactor Maintenance reports this task duration should be 12 hours. . Also, the backbone task for "Dryer/Rx Cavity Preparations" (SO-0R606-1280) has a 12 hour lag predecessor of entering mode 5 (SO-0R606-1270). This 12 hour lag should be about 7 hours. . Both of these schedule backbone tasks were pushing the Dryer Removal/Rx Cavity Flood backbone task (SO-0R606-1300) to start 13-May-19 0800 when we will likely be ready to start the dryer removal at 13-May-19 0000 hours. . Recommend a post-outage comparison be performed for the outage schedule backbone tasks actual start and finish times compared to the baseline backbone schedule start and finish times.
393240 | CR | 20190512 |  | 3 | MT-CRA-1 Aux Hoist Oil Level High Causing Leakage | N | N |  | N | YES | <D> **** Detailed Description **** Evidence of oil leaking from MT-CRA-1 was observed on the T501 west floor. On May 10th a Whiting Crane tech, here to support R24, inspected the trolley area and found the aux hoist gear box was over filled and oil was leaking from the shaft seals. As part of the previous MT-CRA-1 main hoist upgrade, the seals of the main and aux hoist gearboxes were replaced and the cases were filled to a level below the seals to prevent oil leakage. <I> **** Actions Taken **** Generating this CR to document the condition found. There is no negative impact to the operation of the crane other than continued leakage of oil until the level is below that of the shaft seals. The Whiting tech cleaned up oil found on the trolley. | 02-00-MT-CRA-1
393241 | CR | 20190512 |  | 3 | SAFETY CONCERN Disconnect for MT-HOI-35 only works forcibly |  |  |  | N | YES | <D> **** Detailed Description **** MT-DISC-HOI/34A has had problems closing for many years. Work Order 02080191 was written in January of 2016 to replace this disconnect. Having a defective 480 VAC disconnect that requires force or other unconventional methods to get it to close is a potential for an ARC FLASH. With Safety First being a staion focus area, to leave this disconnect in this condition without replacing it due to the outage schedule would go against our maintenenance Fundamentals. <I> **** Actions Taken **** Notified Maintenance Liason in the OCC <N> Work has been added to scheduled. No futher actions required. | 02-00-MT-HOI-35
393242 | CR | 20190512 |  | 4 | COND-RLY-62/CB2A AS FOUND TIME OUT OF TOLERANCE | N | N |  | N | YES | <D> **** Detailed Description **** During testing of COND-RLY-62/CB2A per PPM 10.25.207 (WO#02112099-01) the As found time was 53.11 seconds with a data sheet tolerance of 47-53 seconds. <I> **** Actions Taken **** Notified supervisor and PSRO. Adjusted time per PPM 10.25.207. As left time in tolerance at 50.83 seconds. Relay tested Sat with As left time in tolerance | 02-00-COND-RLY-62/CB2A
393243 | CR | 20190512 |  | 4 | RMC Laborer - Minor Skin Irritation |  |  |  | N | NO | <D> **** Detailed Description **** Two RMC Laborers reported minor skin irritation after handling a roll of herculite located in Bldg. 13. The irritation was limited to the forearms of both individuals. The irritation diminished over a period of two hours. Both individuals declined transport to urgent care. The roll of herculite was not located in the RMA and was later disposed of. Contact RMC Laborer office for additional details, x2142 or x2338. <I> **** Actions Taken **** The area of irritation was rinsed with warm water and soap. Bldg. 13 was walked down to locate the issue.
393244 | CR | 20190512 |  | 4 | COND-RLY-TK1/AOP1A AS FOUND TIME OUT OF TOLERANCE | N | N |  | N | YES | <D> **** Detailed Description **** During testing of COND-RLY-TK1/AOP1A per PPM 10.25.207 (WO#02112099-01) the As found time was 194.07 seconds with a data sheet tolerance of 171-189 seconds. <I> **** Actions Taken **** Notified supervisor and PSRO. Adjusted relay per PPM 10.25.207. As left time is 183.62 seconds. Relay tested Sat with As left time in tolerance. | 02-00-COND-RLY-TK1/AOP1A
393245 | CR | 20190512 |  | 4 | COND-RLY-TK2/AOP1A As found time out of tolerance | N | N |  | N | YES | <D> **** Detailed Description **** During testing of COND-RLY-TK2/AOP1A per PPM 10.25.207 (WO#02112099-01) the As found time was 10.85 seconds with a data sheet tolerance of 9.5 to 10.5 seconds. <I> **** Actions Taken **** Notified supervisor and PSRO. Adjusted relay per PPM 10.25.207. As left time is 10.22 seconds. Relay tested Sat with As left time in tolerance. | 02-00-COND-RLY-TK2/AOP1A
393246 | CR | 20190512 |  | 3 | BS-V-717A- bonnet steam cut | N | N |  | N | YES | <D> **** Detailed Description **** Disassembled valve for a body to bonnet steam leak and found pinched gasket. Bonnet gasket sealing surface is eroded. Bonnet should be replaced or valve should be cut out and replaced. See EDMS photos. <I> **** Actions Taken **** Contacted Component manager. Returned WO 02137368-01 <N> **** Equipment Description **** T 441 D8/9.4 | 02-00-BS-V-717A
393247 | CR | 20190512 |  | 4 | while performing 02119702-08 valve MS-V-718C bad | N | N |  | N | YES | <D> **** Detailed Description **** *1 MS-V-718C Found bad handle it spins, found capped off with no tubing connected for MS-PX-6A3. *2 MS-V-761 is for LPA not C section. <I> **** Actions Taken **** Notified supervisor <N> **** Equipment Description **** T501 DT-C | 02-00-MS-V-718C
393248 | CR | 20190512 |  | 3 | MSIV stroking delayed due to different locks on steam tunnel |  |  |  | N | NO | <D> **** Detailed Description **** MSIV stroking was delayed due to the steam tunnel gate being locked with 2 different keys (a padlock and the regular gate lock), adding approximately 45 minutes to locate the correct additional key and open the gate. Recommend not using extra locks if not necessary. <I> **** Actions Taken **** Informed supervisor, generated AR. <N> Ops manager issued the CR to track the work delay only. Added to R24 LL and closed per his direction
393249 | CR | 20190512 |  | 4 | Security Near Miss |  |  |  | N | NO | <D> **** Detailed Description **** Security had a near miss in the vehicle trap. The SAS operator operated the gate prior to being directed while a vehicle with a trailer was entering the PA. The operator was coached to standards and all squads will be briefed.
393250 | CR | 20190512 |  | 4 | Spilled Container In X-Ray Machine At PAAP | N | N |  | N | NO | <D> **** Detailed Description **** At approximately 1700 hrs. A craft supervisor sent his backpack through the x-ray machine at the entry portal. There was a stainless steel coffee mug that was full of coffee, the cover came off and coffee was spilled in the machine. The xray was put out of service for cleaning. <I> **** Actions Taken **** Supervisor was coached by Security as well as his supervisor about situational awareness and the expectations of no liquids allowed trough the machine. <N> WIlliams Plant Services.
393251 | CR | 20190512 |  | 4 | DEH actuator inspection at shutdown for R24 | N | N |  | N | YES | <D> **** Detailed Description **** Shutdown walkdowns entering R24 revealed there are a number of DEH actuators and actuator blocks associated with Main Turbine Valves that show evidence of very small leaks by wetted surfaces and beginning formation of droplets. Some have darkened oil suggesting the drops are slow to form and varnished from heat prior to dripping away. All leaks are too small to measure or quantify. Total cumulative volume of the leaks is negligible. This CR is written for trending purposes. <I> **** Actions Taken **** informed EOC and discussed with supervisor | 02-00-MS-V-160B,02-00-MS-V-163B,02-00-MS-V-163C,02-00-MS-V-164A,02-00-MS-V-164B,02-00-MS-V-164C,02-00-MS-V-165A,02-00-MS-V-165B,02-00-MS-V-165C,02-00-MS-V-166A,02-00-MS-V-166B,02-00-MS-V-166C
393252 | CR | 20190512 |  | 4 | Security X Ray 4 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security X Ray machine is not operating by design due to a coffee spill and needs maintenance. Contact security at 2185 for details. <I> **** Actions Taken **** Security supervision notified. Equipment taken out of service. CR/WR initiated. | 02-00-SEC-XR-4
393253 | CR | 20190512 | CAQ | D | IDS 16 17 Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** CAS received a malfunction on IDS 16 17. Compensatory measures were posted. Contact 2185 for more details. <I> **** Actions Taken **** Security supervision notified. Initiated CR/WR. Compensatory measures posted. OCC notified. | 02-00-SEC-IDS-E/S/16/17
393254 | CR | 20190512 |  | 3 | TSP-MSIV-B801 revision required |  |  |  | N | NO | <D> **** Detailed Description **** TSP-MSIV-B801 section 7.9 has independent verification steps for MS-V-603 closed and capped, and MS-V-604 closed (pg 50), but there are no steps to direct closing/capping those valves. Recommend inserting steps to close MS-V-604 and close & cap MS-V-603 after 7.9.10. Recommend revision prior to as-left LLRT. <I> **** Actions Taken **** Discussed with supervisor, closed MS-V-604, closed & capped MS-V-603, generated AR.
393256 | CR | 20190512 |  | 4 | Lube Oil Conditioner Room sump is half full | N | N |  | N | NO | <D> **** Detailed Description **** The level in the Lube Oil Conditioner Room sump has reached maximum limit per Operator Rounds and should be pumped out. <I> **** Actions Taken **** Notified SSS. <N> **** Equipment Description **** Lube Oil Conditioner/Oil Storage Room Sump
393258 | CR | 20190512 |  | 4 | (R24LL) CW screens continues to be a station problem |  |  |  | N | NO | <D> **** Detailed Description **** A proposed solution to the ever continuing battle with CW screens is removable gates in the walls between each of the CW basins downstream of the screens. This would enable the use of all 3 screens and basins to feed a single pump when the gates are removed. <I> **** Actions Taken **** Wrote AR-EVAL 393257
393259 | CR | 20190512 |  | 3 | M2 Cooler Group 1 Flow switch Paddle Found Broke Off | N | N |  | N | YES | <D> **** Detailed Description **** During the replacement of the flow switch on M2 cooler group 1 (WOT 02115678-01 E-TR-M2: REPLACE OIL FLOW INDICATORS), the removed flow switch was found with a broken off paddle. The paddle is lost in the cooler group and per the Factory rep, should be on the top of the heat exchanger. . Recommend a work order task to remove the top oil piping elbow and look into the heat exchanger visually and with a bore scope. . Also recommend a contingency task to replace the cooler group with the staged spare cooler group should be planned in the event that the paddle is not found and removed. Note: All flow switches are being replaced on M1. M2 and M3 transformers in R24. All of M1 flow switches have been replaced with all parts retrieved/no missing paddles. Three more flow switches remain to be replaced on M2 and all for on M3 as of this time (5-12-19 @ 1945). <I> **** Actions Taken **** Notified OCC and initiated the CR | 02-00-E-TR-M2
393261 | CR | 20190512 | CAQ | D | Locking mechism on FP-V-CO2/900 almost completely failed. | N | N |  | N | YES | <D> **** Detailed Description **** The locking mechaism is extrmemly bent and deformed and the metal portion on the moving side has a large visible stress fracture (it wiggled on this line as the lock was removed). Might need to use a chain and lock system in the future. <I> **** Actions Taken **** Informed supervisor. | 02-00-FP-V-CO2/900
393262 | CR | 20190512 | CAQ | C | (QA) D-1: ITR Not Performed Consistently |  |  |  | Y | NO | <D> **** Detailed Description **** D-1: Independent Technical Reviews (ITR) Not Performed Consistently Related Objective: Objective 2 Problem Statement: Only one Independent Technical Reviews (ITR) was completed since September 2017, which could challenge the ability to demonstrate compliance with OQAPD-01. OQAPD-01 states, Independent technical reviews shall include, but not be limited to, the following activities: unit-operating characteristics, Nuclear Regulatory Commission issuances, industry advisories, licensee event reports, other sources of unit design and operating experience information, including units of similar design, which may indicate areas for improving unit safety, plant operations, maintenance activities, and equipment modifications. While no frequency required is stated anywhere, the completion of only one ITR during the time period could be interpreted to not meet the intention of OQAPD-01. Examples of some items that could have had an ITR performed include: o CR 389753 â€œTR-S Lockout o CR 391261 â€œGNF Fuel Bundle Inspection Reportâ€ o CR 382832 â€œCOLR limits Non-conservative LDA OPC setpointâ€ o CR 380257 â€œReactor Scram Main Transformer Tripâ€ o CR 371655 â€œDG2 Failure to develop voltage or frequency on hot startâ€ <I> **** Actions Taken **** This issue was discussed with Quality Management and identified during the Quality 2019 Pre-NIEP SA-376427
393263 | CR | 20190512 | CAQ | C | (QA) D-4: No Procedure To Submit Audit Schedule to POC |  |  |  | Y | NO | <D> **** Detailed Description **** D-4: No Procedure/Instruction To Submit Audit Schedule to POC Related Objective: Objective 3 Problem Statement: The Operational Quality Assurance Program Description (OQAPD) requires the Plant Operations Committee (POC) to review â€œsummary reports of auditsâ€; however, there are no Quality procedures or instructions directing Quality to provide this to POC. Neither SWP -ASU-01 â€œEvaluations of Programs, Processes, and Suppliersâ€ and QSI-26 â€œQuality Audit Schedulingâ€ direct the internal â€œaudit scheduleâ€ to be given to the POC Chair or Coordinator at least semiannually, as required by the OQAPD. <I> **** Actions Taken **** This issue was discussed with Quality Management and identified during the Quality 2019 Pre-NIEP SA-376427
393264 | CR | 20190512 | CAQ | C | (QA) D-6: Seven Audit Reports Not Distributed IAW QAP-ASU-02 |  |  |  | Y | NO | <D> **** Detailed Description **** D-6: Seven Audit Reports Not Distributed IAW QAP-ASU-02 Related Objective: Objective 3 Problem Statement: Seven Quality audit reports were not distributed in accordance with QAP-ASU-02 â€œQuality Audit Reportsâ€. Five different audits were not in compliance with the 11/28/18 revision to QAP-ASU-02, which added a new requirement to distribute Quality audit reports to the POC Coordinator. AU-CSQ-18 dated 12/4/18, AU-CA-18 dated 1/2/19, AU-MN-19 dated 3/5/19, AU-EP-19 dated 3/14/19, AU -CL-19 dated 3/19/19, AU-SE-PADS-MRO-SAE-18 dated 9/17/18, and AU-CH-18 dated 11/8/18. Distribution list has now been updated and the seven reports were sent to the POC Coordinator. <I> **** Actions Taken **** This issue was discussed with Quality Management and identified during the Quality 2019 Pre-NIEP SA-376427. Issue has been corrected. <N> The reports in question were submitted to the POC Chairperson and the POC Admin. The standard distribution form has been updated now require distribution to all of those listed in the procedure. Coaching was provided to the Lead Auditors and the Quality Admin responsible for distribution was also made aware of the requirement. No further actions are needed to address this issue..
393265 | CR | 20190512 | CAQ | C | (QA) ESL not submitted to Records as required per SQI-7-2 |  |  |  | Y | NO | <D> **** Detailed Description **** D-8: ESL not submitted to Records as required per SQI-7-2 Related Objective: Objective 5 Problem Statement: ESL not processed and submitted to Records as required per SQI-7-2, Evaluation of Suppliers. Section 5.0 of SQI-7-2 states â€˜The ESLâ€¦ are processed in accordance with SWP-REC-01, Records Management and QAP -ASU-03 Quality Assurance Records. <I> **** Actions Taken **** This issue was discussed with Quality Management and identified during the Quality 2019 Pre-NIEP SA-376427
393266 | CR | 20190512 | CAQ | C | (QA) Technical Specialist Qualification Not Entered Into PQD |  |  |  | Y | NO | <D> **** Detailed Description **** D-9: Technical Specialist Qualification Not Entered Into PQD Related Objective: Objective 5 Problem Statement: Contrary to QAP-ASU-04, Personnel Indoctrination, Training, Qualification, and Certifications, the Technical Specialist assigned to BLACK & VEATCH Audit 18-A-05 was not added to Qual Group QAAG after completion of Form 27126. â€¢ QAP-ASU-04 Step 3.7.5 states, â€œForward the completed Form 27126 to Qualifications Management Services or department individual trained to enter qualifications into PQD and add the Qual Group QAAG to the Technical Specialistsâ€™ Qual group assignment.â€ <I> **** Actions Taken **** This issue was discussed with Quality Management and identified during the Quality 2019 Pre-NIEP SA-376427
393267 | CR | 20190513 |  | 4 | Knee-Knocker Turbine 501 East End | N | N |  | N | NO | <D> **** Detailed Description **** While on the Trubibne 501 Turbine deck, craft personnel mentioned they had wtnessed several near-misses already regarding what appears to be maybe a ladder storage rack located on the East End Turbine 501. The crafts concern was catching a knee on the lower portion of the rack. He specifically mentioned in past outages they had removed the lower portion of the rack for the duration of the outage. Recommend creating a WR to remove the lower rack. Reference pictures in EDMS folder. <I> **** Actions Taken **** Contacted OCC/EOC/Industrial Safety. Temporarily removed per WR 29148550. <N> **** Equipment Description **** Turbine 501 East End
393268 | CR | 20190513 | CAQ | D | DMA-FN-32 not running | Y | Y |  | N | YES | <C> This CR will be resolved by CR 393270. <D> **** Detailed Description **** DMA-FN-32 was found not running and without control power indicating lights. A reset of DMA-42-4A7D was performed to no avail. <I> **** Actions Taken **** Initiated CR. Informed MCR and OCC. <N> Cause is uncertain - Engineering recommends a severity B w/EQIT . Re-opened CR to allow RX startup tracking modifications. | 02-00-DMA-FN-32
393269 | CR | 20190513 | CAQ | D | SP-8 RX H2O meter and recorder greater than 20% delta | N | Y |  | N | YES | <D> **** Detailed Description **** SP-8 meter/recorder greater than 20% delta from calibrated cell grab sample. Meter and recorder will be deemed out of service until the cross check is less than 20%. Meter and recorder maintenance may be required. Chemistry is currently using calibrated cell grab samples once per shift to monitor SP-8 conductivity. <I> **** Actions Taken **** Informed chemistry supervision and wrote a CR. | 02-00-S-CIT-202,02-00-S-CR-24
393270 | CR | 20190513 | CAQ | B | DMA-FN-32 Breaker Suspected Fuses Blown | Y | N |  | N | YES | <C> Risk: Medium Cause: Unclear Severity: "B" with an IT required. <D> **** Detailed Description **** Investigating Control Room alarm for DG3 HVAC, discovered Drop 2.3 (DG Mixed Air Fan DMA-FN-32 Differential Low) in alarm. Breaker DMA-42-4A7D was found ON with no light indication on the breaker or E-CP-DGHV/3. With CRS direction, attempted to reset overloads with no change to condition. Cause is likely breaker fuses blown. <I> **** Actions Taken **** Attempted reset on overloads with CRS direction with no success. <N> Notes: This failure happened on 5/13/2019 when the plant was already in mode 5 and there were no Technical Specification entries required and no change in risk color based on the Shutdown Safety Plan of the station. | 02-00-DMA-42-4A7D
393271 | CR | 20190513 |  | 3 | SRD Dropped into Bellows During RPV Head Lift |  |  |  | N | NO | <D> **** Detailed Description **** During the RPV head lift, a self-reading dosimeter (SRD) became detatched from the thigh of the individual wearing it and fell into the bellows. The individual exited the area, and the SRD was immediately retrieved. <I> **** Actions Taken **** The individual was removed from the area, and the SRD was retrieved from the bellows. The coverage RP technician provided support for the removal of the SRD from the bellows. The individual was escorted to the RCA egress point and logged out of the RCA. A login restriction was placed on the individual pending further actions. <N> The tape came undone from the radworker's thigh where the SRD was located. No apparent radworker issues. A damaged/off-scale SRD form was filled out and the radworker was assigned the dose shown on the SRD. The radworker's restriction was lifted with concurrence from the OCC. Form 19086 has been completed and sent to records. No further action required.
393272 | CR | 20190513 |  | 3 | 15.3.7 vacuum Breaker frequency | N | Y |  | N | YES | <D> **** Detailed Description **** While performing 15.3.7 section 7.5 vacuum breaker inspection and maintenane for the A3 stairwell one of the vacuum breakers was found with the ball stuck on the seat which would have made it non functional. Vacuum Breaker FP-V-923 when removed had the ball stuck on the seat and could not be loosened by shaking or tapping on hand. The Vacuum breakers were replaced per the procedure however the frequency should be changed from every four years to every 2 years. <N> **** Equipment Description **** Fire protection stand pipe stairwell A-3 | 02-00-FP-V-923
393273 | CR | 20190513 |  | 3 | R24LL: SOP-COND-OPS Requires revision for cavity fill | N | N |  | N | NO | <D> **** Detailed Description **** After performing SOP-COND-OPS step 5.5.2.h, to raise hotwell level to 446 ft for cavity fill, an SRO walk down of TG bldg discovered a large quantity of water flowing from the HD-T-1 outlet off the gland steam condenser directly on the 441' TG bldg floor. This is due to the hotwell level being increased above the level of this piping. SOP-COND-OPS has the operators close and caution tag valves in step 5.5.2.a to prevent a similar condition. These bulleted steps need the addition of HD-V-21A and HD -V-22. Those valves are closed in the SOP-COND-SHUTDOWN procedure since the draining of the system back to the hotwell on shutdown would result in the same condition. With the water flowing, the valves could not be closed since they are directly under the flow path under the floor. A CSCO was generated to close HD-V-11 until the area can be accessed.
393274 | CR | 20190513 |  | 4 | Pipe leak next to main condenser down stream of HD-V-11 | N | N |  | N | YES | <D> **** Detailed Description **** Discovered a through wall pipe leak at the main condenser down stream of HD-V-11. The leakage can not be isolated. See EDMS. The leak is under the normal water level. <N> Re-opened CR to allow RX startup tracking modifications. | 02-00-HD-V-11
393275 | CR | 20190513 |  | 4 | Request flow detector installed near TMU-V-23. |  |  |  | N | YES | <D> **** Detailed Description **** Request flow detector installed near TMU-V-23. This was installed last outage and a change was made to SOP-CW-OPS to install it when we are using CW Basin Level with TMU-V -23. R24 has started and CW Basin Level control via TMU-V -23 will be required. TMU-V-23 has multiple issues with it currently and we will need additional ways to monitor flow until we can get it fixed or we will not to able to control CW Basin level in a desired manner. | 02-00-TMU-V-23
393276 | CR | 20190513 | CAQ | C | Substance identified floating on RPV water surface | Y | N |  | N | NO | <D> **** Detailed Description **** Following the removal of the RPV head at the beginning of R-24 a small area of an unidentified floating substance was identified. This substance was located on the east side of the RPV on the surface of the water/flange interface in the area where the studs are removed in preparation for the installation of the "cattle chute". Reports from the Radiation Protection personnel were that there was no abnormal dose rates identified in this area. It was also reported that this has been seen in previous outages, however internal OE search was not successful in identifying this issue or previous analyses. <I> **** Actions Taken **** OCC notified OE search conducted <N> **** Equipment Description **** MS-RPV-3
393278 | CR | 20190513 | CAQ | C | HSSF-CP-P2 Battery Needs to be Replaced | N | N |  | N | YES | <D> **** Detailed Description **** In preparation for the SH-6 outage, operations requested I&C replace the battery in HSSF-CP-P2, per SOP-ELEC-SH6 -MAINT under WOT 02079546-05. There was no support task, no MR, and no I&C resource allocation. After researching the task and buying the part, it was learned that the HSSF had already been tagged out to support WOT 02104439-01, which is not scheduled for almost 3 weeks. Given that the battery was never replaced, and that the HSSF will be deenergized for three weeks, it is possible the program data in the PLC will have been lost. <I> **** Actions Taken **** Worked with planning to create a task within 02104439 for I&C to replace the battery and verify program data upon restoration of power. Also working with outage scheduling to possibly move the work forward, so we don't get to the end of the outage before learing if there is a problem with HWC. | 02-00-HSSF-CP-P2
393279 | CR | 20190513 | CAQ | D | Clogged nozzle in the SWA Pond Spray Ring | Y | N |  | N | YES | <D> **** Detailed Description **** A single spray nozzle on the SSW B spray ring header in the SSW A spray pond was clogged, allowing less than full flow through the nozzle. This nozzle was located in the NE corner of the SSW A spray pond and photo uploaded into EDMS. EC EVAL 13729 has evaluated the plugging of SW spray nozzles and states a maximum of 10 plugged nozzles is acceptable. All other spray nozzles were SAT. <I> **** Actions Taken **** Notified SM <N> **** Equipment Description **** SSW B Spray Ring in the SSW A Spray Pond
393280 | CR | 20190513 |  | 4 | Seismic latch for 6 foot ladder broken RW 467 | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The seismic latch for the 6 foot ladder (Left Upper) on the RW 467 Vital Island next to Battery Room 2 door. The threaded portion that the wing nut threads onto to secure the seismic latch has sheared off. <I> **** Actions Taken **** Condition report initiated and Electrical supervision informed. <N> **** Equipment Description **** Siesmic Latch Mechanism for 6 foot ladder stored in the RW467 Vital Island
393282 | CR | 20190513 | CAQ | D | 501 West emd UV detector spurious alarms | N | N |  | N | YES | <D> **** Detailed Description **** Recieved multible spurious fire alarms on FP-UVD-11 no fire was identified. The turbine building crane was in operation during the reciept of these alarms. The left and right hand fault numbers were 0 for left and 0 for right. A 0 fault code indicates Dector discharge( low level UV). <I> **** Actions Taken **** Followed ARP | 02-00-FP-UVD-11
393283 | CR | 20190513 |  | 4 | TSW-RV-117E lifted then reset. |  |  |  | N | YES | <D> **** Detailed Description **** During TG bldg walkdown, TSW-RV-117E was observed to have lifted. It was later reset. This may be due to elevated TSW pressure with less cooling flow demand on the system. This is associated with a cooler on COND-P-2C. | 02-00-TSW-RV-117E
393285 | CR | 20190513 | CAQ | D | FME: Pen found and retrieved from cavity prior to flood up |  |  |  | N | YES | <D> **** Detailed Description **** A red pen was found on the shelf of the second cavity shield block at approximately 180 degree. The RPV head had been just been removed and the cavity had not been flooded up. <I> **** Actions Taken **** The pen was immediately retrieved from the shelf using long handled pickers. <N> **** Equipment Description **** NONE
393289 | CR | 20190513 |  | 4 | BLP pressure gauge unreadable due to FP leak | N | N |  | N | YES | <D> **** Detailed Description **** TO-PI-137 displays Bearing Lift Pump (BLP) pressure at LPC (MS-DT-1C) east end and is used to validate adequate pressure when on turning gear to prevent Main Turbine bearing damage. This gauge could not be read due to scum and debris caused by a Fire Protection piping leak (see CR AR 372443) completely obscuring the gauge. This pressure indication will be needed when Lube Oil Clearance is removed and the BLP is started. The pressure indicator is expected to be functional, it just needs to be cleaned. The difficulty is that the gauge is located about 18 inches below a floor grate that will require HP support to access. <I> **** Actions Taken **** informed turbine shack, walked down with laborers <N> **** Equipment Description **** TG501, LPC skirt east (Gov) end | 02-00-TO-PI-137
393291 | CR | 20190513 |  | 4 | Office Web Apps SharePoint (The Current) feature offline | N | N |  | N | NO | <D> **** Detailed Description **** The Office Web Apps feature of SharePoint 2013 (The Current) which provides a method of opening MS Office files (Word, Excel, PowerPoint, etc...) and provides file previews in SharePoint Enterprise Search went offline unexpectedly. <I> **** Actions Taken **** The SharePoint administrator was notified and began working to identify and resolve the condition. The feature remained offline for approximately 1.5 hours before the resolution was implemented and service was restored. The system is now functioning as intended.
393292 | CR | 20190513 |  | 4 | Corporate Laptop Identified in Power Block | N | Y |  | N | NO | <D> **** Detailed Description **** A corporate laptop associated with BPA work was located in the RW 525 communications room. Per GBP-IS-27, corprate laptops are not permitted in the power block and require additional labeling and evaluation. This laptop was NOT connected to any plant systems or components. <I> **** Actions Taken **** Work supervisor was contacted and informed of requirements, SM and cyber security contacted. CR initiated. <N> Cyber security reported to field, the laptop had been evaluated by cyber security and had an additional white label allowing use within the power block that was no identified by the operator who discovered the laptop and the worker was unfamiliar with the labeling requrements.
393293 | CR | 20190513 |  | 4 | Damaged flex conduit to BS-V-27 identified | N | N |  | N | YES | <D> **** Detailed Description **** During a walk down for WO 02120347 BS-V-29 prefabrication, damaged flex conduit was noticed that headed to BS-V-27. See pictures in EDMS <I> **** Actions Taken **** Generated CR | 02-00-BS-V-27
393295 | CR | 20190513 |  | 3 | Work Order Records not avail. to review for MTE Deficiency | N | N |  | N | NO | <D> **** Detailed Description **** Work Order Records not available to review for MTE Deficiency Report response. <I> **** Actions Taken **** Informed Tool Crib that W/Os not available to perform review of MTE report before due date (04-23-19). W/Os still not available 04-26-19. W/Os still not available 05-13-19. Wrote this CR.
393296 | CR | 20190513 |  | 4 | Multiple TOA airwash deficiencies. | N | N |  | N | YES | <D> **** Detailed Description **** The following disconnects could not be closed in, even with pressing on the disconnect door: TOA-42-2RA2C, TOA-42 -3A2A, TOA-42-2RA2D, and TOA-42-1E2C. Request nozzle cleaning for TOA-AW-1A. Once the other 3 are started, any needed WRs will be added to this AR/CR. <N> **** Equipment Description **** TG 501 | 02-00-TOA-42-2RA2C,02-00-TOA-42-3A2A
393297 | CR | 20190513 |  | 4 | MS-MO-V/104B Will Not Stroke | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Per WO # 02136291-05 valve was operated to stroke closed to open and would not move. valve was stroked in both directions and still would not move. Valve stem move slightly (less than 1/8") it seems to be stuck. this needs to be investigated. current was measured at bucket during stroke for less than one second. current was .9 amps but returned to zero almost immediatly. 497 Volts AC was measured. <I> **** Actions Taken **** notified electrical and mechanical supervision Initiate CR and WR <N> **** Equipment Description **** MS-V-104B MS-42-2R6C
393298 | CR | 20190513 |  | 3 | Records Submitted W/O Transmittal Attached | N | N |  | N | NO | <D> **** Detailed Description **** A record was submitted to records control Without a transmittal attached. Please refer to SWP-REC-02 SECTION 4.3.2 for the submittal process. <I> **** Actions Taken **** Notified my supervision. Sending Records back to Rad Material Control Supervision for corrections and resubmittal.
393299 | CR | 20190513 |  | 3 | Records Submitted without signed Transmittal | N | N |  | N | NO | <D> **** Detailed Description **** A Large stack of Records was sent to Records Control without a signed transmittal by Rad Protection. Please refer to SWP-REC-02 Section 4.3.2 for the submittal process. <I> **** Actions Taken **** Notified my supervision. Sending records back to Rad Protection for correction and re-submittal.
393301 | CR | 20190513 |  | 3 | (QA) 10.25.105 Inspection Requirements - Clarification | N | N |  | Y | NO | <D> **** Detailed Description **** QA) PPM 10.25.105 does not contain adequate clarification for when QC/PV inspection is required. To align with QAP -ASU-07 & QAP-ASU-10, section 4.1 of 10.25.105 needs to be reworded to specify that QC/PV Hold Points are applicable to work activities on Safety Related items only: see example for suggested wording. . PPM 10.25.105, Section 4.1 suggested wording: â€œQC/PV Hold Points are required for and applicable to QC-1 (safety related) MCC cubicles or QC-1 (safety-related) switchgear only. QC/PV Inspection Hold Points for work performed by Contractor Craft personnel must be addressed by QC personnel. Work performed by ENW Maintenance Craft personnel may be addressed by either QC or PV qualified personnel.â€ . <I> **** Actions Taken **** Notified Quality Services Supervisor, Planner and provided clarification in WOT 02077609-01 indicating â€œQC/PV Hold Points are required for and applicable to QC-1 (safety related) MCC cubicles or QC-1 (safety-related) switchgear onlyâ€. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
393303 | CR | 20190513 |  | 4 | Bus 21 ground | N | N |  | N | YES | <D> **** Detailed Description **** Bus SL-21 Ground alarm is in (4.800.C2 8-2). Ops 3 discovered the ground light indicators out at MC-2B and could not be reset. Furthermore, the ground light indicator housing was not fastened down completely. MC-2B powers MT-CRA-1 which could have an affect on the outage. <I> **** Actions Taken **** WR written. <N> **** Equipment Description **** TB471 | 02-00-E-MC-2B
393304 | CR | 20190513 |  | 4 | RFW-V-708, shows signs of excessive leakage. | N | N |  | N | YES | <D> **** Detailed Description **** During the investigation of RFW-V-709, it was noticed that RFW-V-708 appears to have a bad leak from the packing with the packing components rusted. Recommend adjustment or repack during the outage. | 02-00-RFW-V-708
393305 | CR | 20190513 |  | 4 | Received Annunciator P4.800.C4 Drop 6-1 MAIN TRANSFORMER OIL | N | N |  | N | YES | <D> **** Detailed Description **** Received Annunciator P4.800.C4 Drop 6-1 MAIN TRANSFORMER OIL LOW Alarm. Per ARP A MT TROUBLE should also be received concurrently w/this annunciator. Currently TR-M1, TR-M2, TR-M3 Trouble Alarms were aready in alarm prior to this alarm. An Operator was sent into field to verfiiy alarm and reported TR-M1, TR-M2 and TR-M3 Oil levels were all normal. <I> **** Actions Taken **** Informed CRS/SM | 02-00-E-TR-M1,02-00-E-TR-M2,02-00-E-TR-M3
393307 | CR | 20190513 |  | 3 | R24LL - Leakage past MS-V-1/2 Flange at DW upper bulkhead | N | N |  | N | NO | <D> **** Detailed Description **** Upon flood up, leakage was observed in the DW from the MS -V-1/2 bulkhead penetration, 2" Main steam (12 )-4 AED S822, detail D1101. This connection is removed and blanked above the DW bu;khead to allow for space frame removed and RPV dissassembly. A cap is placed over the blanked fitting with a gasket ans bolted down. This is a know leakage location and typically seals up when level is raised in the RX cavity. The station has seen this in R24 and previous outages, solution is to contninue flood up and monitor. Capture leakage as needed. Photos in EDMS. <I> **** Actions Taken **** Informed OCC. <N> Expected leakage considering past refueling outage OE. The source of the leakage is from a gasketed cover. The leakage will be monitored and is expected to reduce as level goes up. Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
393308 | CR | 20190513 |  | 4 | R24 TG 471 elevated dose rates | N | N |  | N | NO | <D> **** Detailed Description **** Received notification from Electricians and IC in regards to the Turbine Bypass valve area (TG 471) being higher than anticipated. Discussed with TG 471 RP technicians; general area dose rates are 7 to 13 mrem/hr due to a 65 mrem/hr contact reading on a pipe going thru the area. Radiological survey performed of area. WO(T)s affected by issue are 02111689 03 & 15, 02111690 13 & 02, 02111980 04 & 16, and 02111981 13 & 03. <I> **** Actions Taken **** Informed TG RP Supervisor, OCC RPM of the job hold up and situation. Task 24 created on WO 02111689 and shielding package developed. Shielding installation task released to Laborer Supervisor for installation. Shielding installed on four locations.
393312 | CR | 20190513 |  | 3 | BS-V-33 piping field vs. drawing discrepancies | N | N |  | N | NO | <D> During the field walk down of WO 02120349-02 it was identified that the piping configuration in the field does not match the drawing. The ISO shows a pipe nipple out of the 90 to a reducer then a pipe nipple to BS-V-33. In the field it is a reducing insert and contains no nipples. Also the leak to repair is listed in the wrong location and welds will need to be added to repair and remove Furmanite plug. <I> Generated CR and contacted OCC and EOC for resolution. <N> CR at INPROG, moved to APPROVED assigned to SRO for OPS review.
393315 | CR | 20190513 |  | 4 | HD-LS-1CL found full of water | N | N |  | N | YES | <D> **** Detailed Description **** when determing HD-LS-1CL. we found the switch housing and flex conduit full of water. WO# 02138025-08. <I> **** Actions Taken **** leak needs to be fixed so that the new switch dosn't suffer the same fate. <N> **** Equipment Description **** HD-LS-1CL
393317 | CR | 20190513 |  | 4 | Leak identified durring Cavity Flood-up. | N | N |  | N | YES | <C> Duplicate of 393307 <D> **** Detailed Description **** Leak identified durring Cavity Flood-Up. Duuring my inspection of the 572 Drywell elevation a flange attached to the drywell ceiling was leaking a pencil sized constant stream of water. After further investigation, the line was conmnected to a plackard labeled MS RPV Head Vent 2/7. <I> **** Actions Taken **** Notified Supervision Initiated CR/WR <N> **** Equipment Description **** MS RPV Head Vent 2/7 Leak at the Ceiling of the Drywell. Per CR 393307 this is epected leakage considering past refueling outage OE. Source of leakage is from a gasketed cover. The leakage will be monitored and is expected to reduce as level goes up.
393318 | CR | 20190513 |  | 3 | Stuck bolting on MS-HX-1B lower manways during removal | N | N |  | N | YES | <D> **** Detailed Description **** During removal of MS-HX-1B east and west lower reheat manway covers under WO 02111979-02 & 02111979-19, boilermakers experienced a stuck bolt on both ends. This is a common experience for of the MSR covers. Reference ARs 327863, 327864, 329710 (R22) 365897 (R23) to provide a few examples of similar occurrences (and there are many more from previous outages). Alternative fastening methods are available that will alleviate this challenge. Reference AR 278499 for further details and in progress RIE to address the issue. <I> **** Actions Taken **** Notified the OCC and Planning to revise the work package. Recommend taking action on a solution described in AR278499. <N> **** Equipment Description **** T501 D5/8.5-12.5 MOISTURE SEPARATOR REHEATER 1B Correction, the WO's for the stuck bolts are; 02111979-02 for MS-HX-1B West, one stuck bolt and 02111978-19 for MX-HX-1A East, two stuck bolts.
393320 | CR | 20190513 |  | 3 | Power loss to EDR-P-14B severely limiting RW | N | N |  | N | YES | <D> **** Detailed Description **** SH6 outage related Power loss to EDR-P-14B severely limiting RW ability to process and return water to CST's <I> **** Actions Taken **** Informed Electrical Outage PSRO <N> EDR-P-14B was deenergized as part of a planned SH-6 outage. This is addressed in SOP-ELEC-SH6-MAINT and it is a known condition. The impact is a loss of efficiency in processing EDR/FDR to return to the CST. This is due to the fact that it limits us to one sample tank vice 2. This slows down the rate at which we can sample water (1 batch at a time instead of 2). An enhancement to the procedure will be made to evaluate the need for Temporary power to EDR-P-14B during longer outages if desired. AR actions 01 and 02 complete. No additional actions required. | 02-00-EDR-P-14B
393325 | CR | 20190513 |  | 4 | TOA-AW-2B pad replacement and cleaning | N | N |  | N | YES | <D> **** Detailed Description **** All TOA airwash units have active model work orders to clean the pads, sumps, and nozzles, with the exception of TOA-AW-2B. Those 3 units had all of their airwash pads replaced. Model work order 01165605 was cancelled and therefore 2B has been neglected. The pads all need to be replaced, the basin cleaned, pump strainer replaced (WR 29144954), and nozzles flushed. The other 3 model work orders are currently being updated with information gleaned from last year's OE. Prioritize restoring the model work order for 2B. Also prioritize ordering more pads, as only 41 were in stock last time checked. Reference WO 01165606, 01165609, and 01165610. <N> **** Equipment Description **** TG 501 west | 02-00-TOA-AW-2B
393326 | CR | 20190513 |  | 4 | Level 1 Filing Not Completed in the MCR | N | N |  | N | NO | <D> **** Detailed Description **** The Level 1 procedure and drawing filing in the main control room was not performed today due to the complex evolution that was in progress. <I> **** Actions Taken **** The PSRO was contacted in regards to the filing and recommended that the filing wait until tomorrow. This CR is being initiated for trending purposes only.
393327 | CR | 20190513 | CAQ | D | As-Found Intermittent Operation Removed MS-RMS-RV/2A Switch | N | N |  | N | YES | <D> **** Detailed Description **** AR CR 385044 investigation drove replacement of MS-RMS -RV/2A (MS-RV-2A valve control switch) under Outage R24 WO 02135237. As found bench testing was performed by shop electricians on the removed General Electric MS-RMS -RV/2A switch (original plant equipment) on 5/13/2019. It was observed that the 3 position switch could be taken to, and remain in, an intermittent position between the â€œOFFâ€ and â€œAUTOâ€ positions. While in this intermittent position the switch contacts would not change state (off normal switch contact state logic configuration). The switch contact state returned to normal after the switch was manually transitioned out of the intermittent position to the full â€œOFFâ€ position. The switch was turned over to engineering for further failure analysis under AR CA 385044-04. . Additional switches are scheduled for replacement in R24 under WO 02136023, WO 02136022, WO 02136021, WO 02136020, and WO 02136019. This style of switch is installed in MS -RMS-RV/1A, 1B, 1C, 1D, 2A, 2B, 2C, 2D, 3A, 3B, 3C, 3D/C, 4A/C, 4B/C, 4C/C, 4D/C, 5B/C, and 5C/C. Recommend engineering review failure analysis and determine if extent of condition exists and/or if any follow-up actions are prudent (consider R24 scope add/delete). Reference AR CA 385044-05, â€œCA1.3 Review failure analysis and update EQITâ€. <I> **** Actions Taken **** Notified EOC, Supplied suspect switch to code programs for failure analysis, wrote CR to document as-found condition <N> This CR is closed to ar 384044-05 which was created to perform the failure analysis and update the EQIT and/or corrective actions based on the results. CR 393327 is redundant to 385044-05. | 02-00-MS-RMS-RV/1A,02-00-MS-RMS-RV/1B,02-00-MS-RMS-RV/1C,02-00-MS-RMS-RV/1D,02-00-MS-RMS-RV/2A,02-00-MS-RMS-RV/2B,02-00-MS-RMS-RV/2C,02-00-MS-RMS-RV/2D,02-00-MS-RMS-RV/3A,02-00-MS-RMS-RV/3B,02-00-MS-RMS-RV/3C,02-00-MS-RMS-RV/3D/C,02-00-MS-RMS-RV/4A/C,02-00-MS-RMS-RV/4B/C,02-00-MS-RMS-RV/4C/C,02-00-MS-RMS-RV/4D/C,02-00-MS-RMS-RV/5B/C,02-00-MS-RMS-RV/5C/C
393328 | CR | 20190513 |  | 4 | TOA airwash deficiencies (part 2) | N | N |  | N | YES | <D> **** Detailed Description **** Further problems with TOA airwash noted as follows: --TOA-V-92 leaks by, work with WR 29142714. --TOA-V-23A stuck shut (with air vented) --TOA-SPV-22A sticking and needs replaced --TOA-SPV-23A sticking and needs replaced --TOA-V-23B is binding mid position when closing. <I> **** Actions Taken **** Closed TOA-V-101 to prevent basin from draining through TOA-V-23B. <N> **** Equipment Description **** TG 501 | 02-00-TOA-V-23A,02-00-TOA-V-92
393329 | CR | 20190513 |  | 4 | PPC DP20 in OVFL (with RED ICE CUBES) | N | N |  | N | YES | <D> **** Detailed Description **** During system monitoring, PPCV was observed to have red ice cubes and high disk consumption. DP20 was found to be in OVFL. The system requires restart of either the DP20 or the whole PPC train to restore functionality. . This does not affect TDAS which is currently primary. Due to this PPC is not available as backup. This is not a reportable condition. <I> **** Actions Taken **** Notified MCR and created WR | 02-00-PPC-COMP-8715
393330 | CR | 20190513 | CAQ | D | Security CCTV11 | N | N |  | N | YES | <D> **** Detailed Description **** Security CCTV11 has minimal visibility. Needs cleaning support as soon as possible. call security at 2185 <I> **** Actions Taken **** CR/WR generated | 02-00-SEC-CCTV-11
393332 | CR | 20190513 |  | 4 | Monthly Chemical Storage area inspection discrepancies | N | N |  | N | NO | <D> **** Detailed Description **** The monthly inspection of Mechanical Maintenance chemical storage areas discovered the following discrepancies: Bldg 115 and 116 have lights out, excess combustibles found in bldg116 (painter tarps). <I> **** Actions Taken **** Notified appropriate personnel to resolve. All discrepancies resolved, no further action required.
393333 | CR | 20190513 |  | 4 | MD-LCV-1A | N | N |  | N | YES | <D> **** Detailed Description **** Water is leaking at the packing approximantly 30 drops per min. The valve should be repacked. <I> **** Actions Taken **** Reported the leak to my supervisor Rob Rhodes . <N> **** Equipment Description **** MDLC-V-1A Location seal water liquid tank , main condenser | 02-00-MD-LCV-1A
393334 | CR | 20190513 |  | 4 | DEH-LVDT-GV/4B signal deviation from 4A | N | N |  | N | YES | <D> **** Detailed Description **** The signal from DEH-LVDT-GV/4B, the backup LVDT for Main Turbine Governor Valve 4 (MS-V-GV/4), was noted to intermittently deviate from that of its redundant pair, DEH-LVDT-GV/4A, by up to 3% prior to and after shutdown. Visual inspection of the two LVDTs was performed by the main turbine system engineer who noted that the 4B core rod was slightly bent and that both LVDTs appeared to be misaligned. Recommend replacing both GV/4 LVDTs with new as part of MS-V-GV/4 overhaul (instead of reinstalling the old ones) and checking all GV/4 LVDT connections. See EDMS for photos and eDNA plot of governor valve position. <I> **** Actions Taken **** Discussed with main turbine system engineer, informed EOC | 02-00-DEH-LVDT-GV/4B
393335 | CR | 20190513 |  | 3 | E-TR-6/61 and E-TR-6/63 inspection and repair WOs | N | N |  | N | YES | <D> **** Detailed Description **** Contract 354196 was issued and signed between EN and contractor North American Substation Services LLC to perform transformer inspection and repairs to E-TR-6/61 and E-TR-6/63 under WO 02111305 and 02111307. The contractor showed up at the station around 1300 5/13/19 to drop of their equipment to be used during this work and met with me to go over the work scope and expectations. However contractor expressed to me that his supervisors did not give them the same work scope described in the signed contract and they could not perform any transformer inspection as described in EN PPM 10.25.062. This issue has been presented to EOC. I have asked the contractor to proceed with transformer repairs tomorrow morning 5/14/2019. E-TR-6/61 and E-TR-6/63 PM inspections will require to be performed in-house. <I> **** Actions Taken **** This issue has been presented to EOC. I have asked the contractor to proceed with transformer repairs tomorrow morning 5/14/2019. E-TR-6/61 and E-TR-6/63 PM inspections will require to be performed in-house. | 02-00-E-TR-6/61,02-00-E-TR-6/63
393338 | CR | 20190513 |  | 4 | Computer point L070 needs calibration | N | N |  | N | NO | <D> **** Detailed Description **** During WR 29147940, SW-LT-1D bubbler tube was rodded out and restored SW-LI-1D indication (14') to match local level indication (434'). Computer point L070 was reading 13.7. the computer point needs to be calibrated. <I> **** Actions Taken **** Wrote CR and WR <N> **** Equipment Description **** Computer point L070
393339 | CR | 20190513 |  | 4 | MS-V-739B stem pitted | N | N |  | N | YES | <D> **** Detailed Description **** During Repack WO #02106163-01 MS-V-739B Found valve stem pitted. pitting is even with the top of the stuffing box, if repacked ,cycling valve would start to destroy the packing. | 02-00-MS-V-739B
393340 | CR | 20190513 |  | 4 | information regarding nonroad engine not submitted to E&RP |  |  |  | N | NO | <D> **** Detailed Description **** During a site walk down by Environmental and Regulatory Programs (E&RP) staff on 5/13/2019, a temporary air compressor (Atlas Copco PTS 1600 Tier 4) was found staged outside of the CGS Circulating Water Pumphouse. Information regarding the temporary nonroad engine was not submitted to E&RP prior to arrival on site (reference: GBP-ENV-07, Air Quality). Based on online research of the equipment make/model, the engine size exceeds the 500 horsepower; a notification to the Energy Facility Site Evaluation Council (EFSEC) and WA Department of Ecology (Ecology) is required. <I> **** Actions Taken **** Notified E&RP Manager. E&RP emailed multiple departments to determine point of contact for the equipment. On 5/13/2019, E&RP submitted a notification of intent to operate nonroad engines to EFSEC and Ecology. <N> Per GBP-ENV-07, Air Quality (section 4.2) information regarding nonroad engines (ex: temporary pumps, generators, compressors) must be submitted to E&RP prior to equipment arrival on site regardless of engine size.
393341 | CR | 20190513 |  | 4 | Dose Rate Alarm in TB 471' Heater Bay |  |  |  | N | NO | <D> **** Detailed Description **** A Crane valve technician, working in overhead on a scaffold between Seal Steam Evaporator 1B and Feedwater Heater 6A, received a dose rate alarm. The electronic dosimeter dose rate alarm setpoint was 80 mrem/hr and peak dose rate when logging out was 113 mrem/hr. The HP tag on the scaffold indicated 20-60 mrem/hr general area and lists a hot spot of 65 mrem/hr. The scaffold tag was updated on 5/12/19. A post dose rate alarm survey has been performed. Survey # 20190513-42. Individual receiving dose rate alarm immediately exited the area and reported alarm to HP technician. <I> **** Actions Taken **** HP Supervision and Management were notified. Form 26443 was completed for RCA Access Restriction and Reinstatement. Discussion with HP Technician and Valve Technician completed with Radiation Protection Manager. RCA Access restriction lifted. <N> The CR was canceled and reopened to facilitate editing of the body of the CR. The dose rate on the hot spot had read 95mrem/hr and changed at RP's request to 65mrem/hr.
393342 | CR | 20190513 | CAQ | D | RHR-CB-P2A missing bolt | Y | Y |  | N | YES | <D> **** Detailed Description **** Prior to racking out RHR-CB-P2A a bolt was found on the floor inside the cubicle. The bolt likely is from the bottom cover of the breaker. See attached photos in EDMS. <I> **** Actions Taken **** Breaker is racked out and removed from cubicle with bolt and lock washer taped to the front. <N> **** Equipment Description **** SM-7 room. REGE/REP both canceled per SM IOD statement that it was no longer required <R> REP/REGE assignments have been cancelled with Licensing Supervisor concurrence. | 02-00-RHR-CB-P2A
393343 | CR | 20190513 |  | 4 | E-CP-LSP/PWA needs tamper seal. | N | N |  | N | YES | <D> **** Detailed Description **** E-CP-LSP-PWA, located in the CWPH electrical room, had to be entered for CW shutdown. This panel now requires a new tamper seal to be installed. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** CWPH | 02-00-E-CP-LSP/PWA
393345 | CR | 20190513 |  | 4 | TMU-V-23 has significant packing leak | N | N |  | N | YES | <D> **** Detailed Description **** TMU-V-23 has a significant packing leak, about 0.5 gallon per minute. Please adjust the packing on this valve. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** SWPH A | 02-00-TMU-V-23
393347 | CR | 20190513 | CAQ | D | DSA-C-2C shutting off early | Y | N |  | N | YES | <D> **** Detailed Description **** DSA-C-2C is shutting off at around 245 psig. It should be around 251 psig. Its currently our only compressor for raising DSA pressure for DG-3 during the SH-6 outage and it shutting off before clearing the alarm. | 02-00-DSA-C-2C
393348 | CR | 20190513 |  | 4 | M3 Cooler Group 2 Flow Indicator Paddle Broke Off | N | N |  | N | YES | <D> **** Detailed Description **** During replacement of the flow indicators on the M3 transformer, the flow indicator was found with the paddle broken off / missing. This cooler group is to be replaced on dayshift. The paddle remains within the cooler group, will be removed with the cooler group and does not need to be retrieved. All flow indicators on M1, M2 and M3 transformers have been replaced. Only two were found to be missing the paddles. One on M2 cooler group 1 which was recovered (AR CR 393259 â€œM2 Cooler Group 1 Flow switch Paddle Found Broke Offâ€ and this on M3 cooler group 2 which will be replaced. . This CR is to document the discovery and does not require any further actions. <I> **** Actions Taken **** Notified OCC | 02-00-E-TR-M3
393350 | CR | 20190513 |  | 4 | Damaged Insulator found on NONSEG BUS N1/X | N | N |  | N | NO | <D> **** Detailed Description **** Work order 02112120-01 - While performing inspection and cleaning per PPM 10.25.202 an insulator was found damaged at NONSEG BUS N1/X, Section D-22 â€œBâ€ phase. Engineering instructed for the insulator to be replaced as per PPM. <I> **** Actions Taken **** Notified Engineering
393351 | CR | 20190513 |  | 3 | R24LL: Revise SOP-COND-SHUTDOWN to remove RFW-V-65A/B Close |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate revising SOP-COND-SHUTDOWN to remove closing RFW -V-65A/B per step 5.8.7. <I> **** Actions Taken **** Dicsussed with Ops Outage Coordinator
393353 | CR | 20190514 | CAQ | C | RW 467 VESDA 3 Trouble Alarm | N | Y |  | N | YES | <D> **** Detailed Description **** Recieved RW 467 VESDA 3 TROUBLE alarm in the Main Control Room (FCP-3 drop 12-2). Local indication revealed an amber air flow indicator flashing on FP-CP-ISD/3. <I> **** Actions Taken **** Notified the CRS and Shift Manager. Submitted CR and WR to document the issue. <N> Due to load testing in the C210 battery room, doors C219 and C218 are propped open with the applicabe approved Barrier Impairment Permits. The VESDA detectors are air-sampling detectors designed to sample air in specific rooms. When doors are left open the detector senses to much airflow and will enter into a trouble confiugration. A trouble configuration would not prevent the detector from performing it's design function, detecting smoke in the event of a fire. Roy Burson 5-14-19 | 02-00-FP-CP-ISD/3
393354 | CR | 20190514 |  | 3 | Wrong CIDs associated with Model WOs for EJ Replacement |  |  |  | N | YES | <D> **** Detailed Description **** Condensate pump expansion joints COND-EJ-2A, COND-EJ-2B, and COND-EJ-2C have model work orders to replace the expansion joints. Each expansion joint has its own Catalog ID with different dimensions specified. However, each model work order references the Catalog ID for COND-EJ-2A (CID 24900). The work order to replace the expansion joint COND-EJ-2B in 2017, WO 00205327, used the 24900 CID. Each of these expansion joints have different dimensions and should reference their own CIDs. <I> **** Actions Taken **** Notified EOC and Planner of incorrect CIDs associated with work orders. <N> **** Equipment Description **** T -432- - -D4/13.8- Instructions and Model work order has been updated to reflect correct CAT ID. MR has been updated for future PM occurrences. No further actions required. | 02-00-COND-EJ-2A,02-00-COND-EJ-2B,02-00-COND-EJ-2C
393355 | CR | 20190514 | CAQ | D | WEA-SR-25 No Isok Control | N | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02115117 and mark completion required box, then taken back to complete <D> **** Detailed Description **** WEA-SR-25 displays the message "No Isok Control" <I> **** Actions Taken **** Informed chemistry supervision and system specialist and wrote a CR. | 02-00-WEA-SR-25
393356 | CR | 20190514 |  | 3 | Request for Night Shift Handicapped Parking Spaces |  |  |  | N | NO | <D> **** Detailed Description **** A contractor employeed asked me to initiate a CR because they were not familar with the process. This worker has worked at other plants and some provide temporary handicapped parking spaces for night shift workers. When night shift comes in the spaces are already full and the workers try to find a spot near the Security Access Building. <I> **** Actions Taken **** Wrote this CR and notified the worker of this CR number. <N> **** Equipment Description **** n/a
393357 | CR | 20190514 |  | 4 | E-SH-6 Broken Light Socket | N | N |  | N | YES | <D> **** Detailed Description **** While performing switchgear inspections on the spare cubicle in E-SH-6, two resistors for the open and close indication for the Breakers were found broken. The resistor model numbers are 449D187G24 and 449D187G34. They are Westinghouse brand. Work order 02077609-01. <I> **** Actions Taken **** Need Engineering review to determine replacement if required. Planning to create material request to procure material. <N> **** Equipment Description **** E-SH-6 . Main body of CR refers the socket as a resistor. Although it looks like a cast resistor it is the red/green indicating light socket. CAT ID 80000641. See WO 02118022 . Engineering recommends replacement.
393358 | CR | 20190514 | CAQ | C | Refuel Bridge will not move over to cavity | Y | Y |  | N | YES | <D> **** Detailed Description **** During preparations for Main Stem Line plug installation, it was discovered that the refuel bridge would not move over the cavity to assist in plug installation. There was no fault indication on the bridge controls of any issues. With permission from Shift Manager, locks were bypassed and work continues. <I> **** Actions Taken **** Notified OCC, discussed issue and path forward with Shift Manager, and set plan for troubleshooting and repair with PAR vendor to start after Separator transfer. Troubleshotting to start at 0800 on 5/14/2019 <N> **** Equipment Description **** Refuel Bridge | 02-00-NSSE-EQ-8
393359 | CR | 20190514 |  | 4 | drain manifold needed for CW system |  |  |  | N | NO | <D> **** Detailed Description **** EOs request a drain manifold to allow 6 @ 1.5" fire hoses in and one 2.5" fire hose out. The 1.5" inlet pipes could just be threaded 1.5" MPT that way caps could be used when on the TG 441 west side and only 3 inlets are needed. If 6 caps were included that would be best - that way no valves would be needed. <N> **** Equipment Description **** CW drain manifold
393360 | CR | 20190514 |  | 3 | ESP-B11-B101 Load test interupted due to laptop shutting off |  |  |  | N | YES | <C> At the direction of MRT, CR Priority and Severity changed to NON-CAQ and 3. <D> **** Detailed Description **** Laptop being used to run VOTES software in support of ESP -B11-B101 (W.O.# 02111921-01) was running off of its battery and did not have a power cord installed. Battery ran out of power causing test to be interupted. <I> **** Actions Taken **** Electrical Supervision informed, OCC informed, EOC informed. | 02-00-E-B1-1
393361 | CR | 20190514 |  | 4 | RFW-42-1A11D needs lubrication | N | N |  | N | YES | <D> **** Detailed Description **** RFW-42-1A11D needs lubrication, it is currently open and can't be closed. | 02-00-RFW-42-1A11D
393362 | CR | 20190514 | CAQ | D | Valves lack valve position indicating needle | N | N |  | N | YES | <C> MRT Change: CR Priority and Severity moved from 4/Trend Repair to CAQ D/Trend Repair. <D> **** Detailed Description **** MS-V-67A and MS-V-67C have no motor operator vpi as designed and the stem does not have a VPI needle. <I> This is not a DNC - only testing inconvenience. | 02-00-MS-V-67A,02-00-MS-V-67C
393363 | CR | 20190514 |  | 4 | HD-V-18D and BS-V-11A did not stroke fully. | N | N |  | N | YES | <D> **** Detailed Description **** During WO 02115591 to unbackseat valves, HD-V-18D fully closed and then on the open stroke it remained dual. BS-V-11A fully closed and then on the open stroke lost all indication. <I> **** Actions Taken **** Attempted additional operation of HD-V-18D with no full closed indication or full open indication only dual. Reset overloads for BS-V-11A and recieved full open indication. | 02-00-BS-V-11A,02-00-HD-V-18D
393364 | CR | 20190514 | CAQ | D | Broken valve position indication and lacks VPI on stem | Y | Y |  | N | YES | <D> Valves MS-V-19 and MS-V-20 have a indicator dial on the motor operator but on each of these valves it is broken. V- 20 lacks the back display that says % open, V-19 needle is pointing out of the indicating band in a indeterminate position. Both valves lack stem VPI soposition cannot be locally determined. <N> CR at INPROG, moved to SRO for OPS review. | 02-00-MS-V-19,02-00-MS-V-20
393365 | CR | 20190514 | CAQ | C | MS-V-160 Turbine Bypass Valves As Found Condition | Y | N |  | N | NO | <D> **** Detailed Description **** Pant washers on turbine bypass valves found installed incorrectly. Tabs not bent over. <I> **** Actions Taken **** Photographed condition, generated CR. <N> **** Equipment Description **** MS-V-160A MS-V-160B MS-V-160C MS-V-160D Condition documented in AR will be addressed with WO#02111981
393366 | CR | 20190514 |  | 3 | Required tasks not present for outage work |  |  |  | N | NO | <D> **** Detailed Description **** WO 02122003 EBUSISOPHASE: INSPECT ISOPHASE BUS, does not have a task to hang the required clearance. It appears the task was written, but then canceled. This has a significant impact to outage work for three different work groups, and for operations. Since there was no task, Operations did not have an opportunity to determine when would be the best time during the outage to secure IBD cooling. Also, It appears a scaffold task to access certain temperature switches in the turbine building was not created, making the switches unable to be accessed. <I> **** Actions Taken **** Spoke with planning to generate new tasks. Also walked down the T471 with Williams carpenters to show exactly where the scaffold needed to be built.
393369 | CR | 20190514 |  | 4 | Flash light found in N1/Y NONSEG BUS | N | N |  | N | NO | <D> **** Detailed Description **** Work order 02112119-01 - A flash light was found in the N1/Y NONSEG BUS on the 471â€™ elev. At D70-21 corner. <I> **** Actions Taken **** Notified Williams Manegement
393370 | CR | 20190514 |  | 4 | E-SH-6 maintenance outage findings | N | N |  | N | YES | <D> **** Detailed Description **** E-SH-6 maintenance outage findings: 1) E-SH-6, Cubicle 1: Rear access panel missing 1 thread insert. 2) E-SH-6, Cubicle 2: Craft found the STAB SPANNER MOUNTING NUT on phase B on the load side loose. 3) E-SH-6, Cubicle 4: One cable guard mounting screw on the unistrut was found loose. 4) E-SH-6, Cubicle 6: The fuse clip on each phase was found discolored. <I> **** Actions Taken **** Contacted Engineering, wrote CR <N> **** Equipment Description **** E-SH-6
393371 | CR | 20190514 | CAQ | D | Manhole ES07 Not functioning as intended | N | N |  | N | YES | <D> **** Detailed Description **** CAS received constant tamper and intrusion alarms without it being opened and without anyone in the area. <I> **** Actions Taken **** Posted compensatory measures. Notified Electrical Maintenance and Security Management. Generated CR/WR. <N> **** Equipment Description **** Manhole ES07 West of BRE 35
393372 | CR | 20190514 |  | 4 | Potential bumped valve | N | N |  | N | NO | <D> **** Detailed Description **** Potential bumped valve on RRC-PI-5. While pulling temporary power cables an individual had a loop in the cable. While pulling the cable to run it, the individual thought that the loop of the cable came in contact with the valve. The individual and the Supervisor immediately stopped and notified Operations of the potential bumped valve. <I> **** Actions Taken **** Contacted Operations and Management. Benched responsible craft invloved in the event. Craft completed event statements. Discussed event with the supervisor and craft and reinforced the positive behavior for reporting the event to Operations and also reinforced that when bump hazards are identified during the TAKE-2 the hazard needs to be elevated to the operating staff so they have the opportunity to provide guidance and action to protect the equipment from potential mispositions. Craft accepted the coaching. RX/MM Manager approved the craft to return to work. Also, this CR was not initiated by the end of shift on 5/13/19 as required. Immediate coaching was provided to the responsible supervisor and craft. WPS Management is providing coaching to all supervisory personnel on the EN requirement during the 5/14/19, 1230 schedule review meeting and the day - night shift turnover meeting. <N> Williams Plant Services.
393373 | CR | 20190514 |  | 4 | Unexpected Plateau downtime |  |  |  | N | NO | <D> **** Detailed Description **** Plateau unexpectedly went offline during the morning of May 14th. <I> **** Actions Taken **** The IS Solutions Center was notified and began making the approapriate technical contacts. Plateau was restarted, monitored and brought back online. No further actions required for resolution.
393374 | CR | 20190514 |  | 4 | PTZ 29 | N | N |  | N | YES | <D> **** Detailed Description **** Tamper Supervision PTZ works and has a good picture | 02-00-SEC-PTZM-1
393375 | CR | 20190514 | CAQ | D | Out of Spce water released to the CST |  |  |  | N | NO | <D> **** Detailed Description **** FDR-TK-9 sampled on 5/13/19 @1836 was released to the CST with TOC above the limit. The TOC was 2.47 ppb and the limit is 200 ppb per SWP-CHE-02. All other chemistry parameters were within limits. The water transfer was directed by the shift manager in response to a low CST level following reactor cavity floodup. Documentation with a CR is required for this activity per CI-9.2 step 5.4. Recommend Category D-Trend.
393378 | CR | 20190514 | CAQ | D | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0068449 Shopmade ARM Power Supply found OOT & adjusted within specs. EFIN EVAL: Measurement taken with OOT deviation added are still within requirements. No Plant Impact. No Action Required. DEF #7012A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
393379 | CR | 20190514 |  | 4 | BS-MO-22A high running loads identified during PM Stroke | N | N |  | N | NO | <D> **** Detailed Description **** WOT 02123280-07 PMT identified the running loads were above design (130% of running current). <I> **** Actions Taken **** Performed evaluation (see EDMS for eval). The conclusion is the high running loads are acceptable for BS-MO-22A. The maximum nuber of strokes in an hour should be limited to 6. However the valve is not stroked this many times in an hour. Recommend closing CR to trending.
393380 | CR | 20190514 | CAQ | D | M&TE Rejected |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0063323 Biddle Dig. Low Resistance Ohmmeter- model 247000 found OOT. EFIN EVAL: Test performed was a balance test. OOT would not affect. Rejected- Broken beyond repair. No Plant Impact. DEF #7013A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
393382 | CR | 20190514 | CAQ | D | M&TE Rejected |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0065892 Check-Line Dig. Tensiometer- model DTMBL-50KB found OOT. EFIN EVAL: Out of the 182 checks, only 3 required re-tensioning from this it can be concluded that the instrument was still in Calibration. Rejected- Broken beyond repair. No Plant Impact. DEF #7014A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
393383 | CR | 20190514 | CAQ | D | M&TE Rejected |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0060916 Fluke Dig. Multimeter- model 8842A found OOT. EFIN EVAL: Range out of tolerence not used. Rejected- Unable to adjust. No Plant Impact. DEF #7021A written. No Action Required. <I> **** Actions Taken **** None Trenidng purposes only.
393384 | CR | 20190514 |  | 3 | CI-9.2 procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** CI-9.2, Radwaste Tank Processing Plan should be revised with the following changes. Delete step 5.4 as it is no longer the accurate with the current Chemistry Department strategy for recording of data. Consider revising step 5.6 to not require a log entry for tank transfers and reprocesses.
393385 | CR | 20190514 | CAQ | D | Approved Deviation per SWP-CAP-01 |  |  |  | N | NO | <D> **** Detailed Description **** Per SWP-CAP-01 CARB review is required 20 calendar days folowing evaluation/investigation assignment closure. Due to R24 CARB review will be performed after R24 has been completed. This deviation has been approved by PGM and CAP Supervisionfollowing evaluation/investigation assignment closure. Due to R24 CARB review will be performed after R24 has been completed. <I> **** Actions Taken **** Notified evaluation/investigation template manager/evaluators of deviation and adjusted PARB calendar. Recommend CAQ D/Trend
393386 | CR | 20190514 |  | 4 | SMA-TCV-1 has failed shut | N | N |  | N | YES | <D> **** Detailed Description **** Could not get flow through SMA-CC-1 without throttling SMA-TCV-1 bypass valve SCH-V-35 open. <I> **** Actions Taken **** Contacted PSRO, Wrote this CR/WR, and requested caution tag to document throttling SCH-V-35 to control Machine Shop temperature. | 02-00-SMA-TCV-1
393387 | CR | 20190514 |  | 3 | R24 LL |  |  |  | N | NO | <D> **** Detailed Description **** New revision of PPM 10.25.141A/B/C has several operations signatures to verify proper ground device installation. These should be removed. These steps are unnecessarily using operations manpower during outage times when operations is busy and resources are limited. Previously we hung danger clearances to allow for ground installation prior to install and are present for a portion of the install which was adequate, we do not need to have this new level of involvement. If further discussion of what is required is needed contact myself or operations management. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
393388 | CR | 20190514 |  | 3 | PPM 1.3.9 Section 4.4 update is needed. |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.3.9 Section 4.4 (Temporary Modifications Made Permanent) provides the location of SharePoint guidelines for making temporary modifications permanent. "Refer to the guideline in SharePoint > theCurrent > Team Sites > PROJECT SITES > Engineering Change > Standard Design Process (SDP) > EC Module Guidelines > Converting Temporary Modifications to a Permanent Change." This SharePoint location no longer exists. The current SharePoint location for this guidance appears to be: "SharePoint > theCurrent > Team Sites > PROJECT SITES > Engineering Change > Standard Design Process (SDP) > ENG-DES-50 Interface > EC Module Guidelines > Temporary Modifications > 6 - Converting Temporary Modifications to a Permanent Change." Please update/correct PPM 1.3.9 Section 4.4.
393389 | CR | 20190514 |  | 3 | Unable to provide remote HP coverage undervesel |  |  |  | N | NO | <D> **** Detailed Description **** The equipment necessary to provide undervessel remote monitoring, (cameras, headsets, stand alone Wireless Remote Monitoring - WRM) as required by RWP as a dose control measure, is not available. Specifically, undervessel cameras are not available or connected and there is no stand-alone WRM monitoring computer available on the RX 501 SW side that can be used if line-of-sight coverage is to be used in lieu of an undervessel camera. This means that to support undervessel work, HP technicians must stand in a dose field of 5 to 20 mrem/hr to provide continuous coverage for those working undervessel. These items should have been available prior to start of undervessel work starting last night. <I> **** Actions Taken **** Contacted Turbine building HPs and Laborers to extract cameras from the turbine building 471 so one can be placed undervessel. Attempted to set up WRM-specific computer on the SW side of the RX building. <N> Cameras are up and running. Issues with ALARA Cast are still being resolved and appropriate personnel are working through the issues. ALARA Cast is functional. No further action required.
393390 | CR | 20190514 |  | 4 | X-Rays 3&4 |  |  |  | N | YES | <D> **** Detailed Description **** X-Rays 3 & 4 powered off on thier own. | 02-00-SEC-XR-2,02-00-SEC-XR-3
393391 | CR | 20190514 |  | 4 | XD's 3 & 5 |  |  |  | N | YES | <D> **** Detailed Description **** XD's 3 & 5 are in a constant state of " stabilizing temperature". | 02-00-SEC-XD-3,02-00-SEC-XD-5
393392 | CR | 20190514 | CAQ | D | LPCS-V-51 Manual Operator Difficult to Operate | Y | N |  | N | YES | <D> During LLRT preparations for test of LPCS-V-5 and 6, the manual operator for isolation valve LPCS-V-51 was very stiff to close by its had wheel. This extended LLRT Prep time. Maintenance is required to avoid internal failure of the manual operator. preparation to close <I> Notified LLRT SRO, informed EOC/OCC Review of parts indicates several items in stock. Ref. Velan P/N P2-3311-N-16 <N> C -554- CR at INPROG, moved to SRO for OPS review. | 02-00-LPCS-V-51
393394 | CR | 20190514 |  | 4 | 1st Quarter 2019 Security Training roll up |  |  |  | N | NO | <D> **** Detailed Description **** There were 3 recorded 1st attempt failures during 1st quarter 2019 security weapons qualifications. Failures were documented and remediation was performed. This CR is for trending purposes only. <I> **** Actions Taken **** Security and Operations Support Management informed. Documentation has been verified as reflecting the issues correctly.
393395 | CR | 20190514 |  | 3 | R24 LL- Schedule of Alt SDC Thermocouple Installation |  |  |  | N | NO | <D> **** Detailed Description **** The scheduling of the Alt SDC temporary thermocouple installtion was scheduled after all other work for the diassembly of the RPV was copmpleted. The work could have been performed anytime the refueing bridge was available. The current logic tie delays operations unecessarily from beginning preps to align Alt SDC for operation. <I> **** Actions Taken **** Wrote this AR <N> **** Equipment Description **** The purpose of the temporary installation is to assist oper ations ion dertmining the Delta T for indication of the dri ving head for natural circulation.
393396 | CR | 20190514 |  | 3 | ODPS bldgs. 43 and 44 new alarms. |  |  |  | N | YES | <D> **** Detailed Description **** OPDS bldg 43 (S/U 230 KV line) and OPDS bldg. 44 ( B/U 115 KV line) have new alarms. Both Bldgs have the following additional alarms: Sel-451 Set 2 trouble, Sel-735 Set 2 trouble and Set 2 F/O cut out. TRS also has and additional alarm " Set 2 Control Power Loss" protection trouble alarm. Suspect alarms are due to Plant S/D and bus SH-6 outage? <I> **** Actions Taken **** Notified supervisor/MCR. <N> **** Equipment Description **** OPDS buildings in the Transformer Yard.
393397 | CR | 20190514 |  | 4 | Current CW temp blowdown may not meet scheduled activities |  |  |  | N | NO | <D> **** Detailed Description **** Currently using a diesel driven pump (Godwin pump) to support CW basin blowdown, blowdown is at 2000 gpm which equates to 1 ft per 17 hrs. Need to install electric pumps to facilitate blowdown. <I> **** Actions Taken **** OCC notified <N> **** Equipment Description **** CW pump house
393398 | CR | 20190514 |  | 4 | HD-LS-6BL found wired incorrectly | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO#02095223, "HD-LS-6BL level alarm in with normal level indicated".found annunciator wired to switch terminals 1 & 3, should have been wired to terminals 2 & 3. Stopped notified supervison. Contacted engineering. Reviewed system prints. <I> **** Actions Taken **** Per direction of system engineering and plant prints relanded wires to correct switch terminals 2 & 3.
393399 | CR | 20190514 |  | 4 | Poor Lighting in the 471 Heater Bay | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The 471 Heater Bay, is a Radiation Area and Contaminated Area. The Lighting is Poor in nmany areas and does not meet the OSHA Regulations. Many permanent bulbs are burnt out. We need to replace the permanent bulbs that are burnt out and add Temporary Lighting for the Outage. <I> **** Actions Taken **** Notified HP Supervision. Notified Safety. Initiate CR/WR Non-essential lighting <N> **** Equipment Description **** 471 Heater Bay
393400 | CR | 20190514 |  | 4 | E-CP-TSCHV/1 loss of annunciator power | N | Y |  | N | YES | <D> **** Detailed Description **** E-CP-TSCHV/1 has suffered a loss of power to its annunciators. This was evidence by the Annunciator tiles being unresponsive to the Test button and the Annunciator Power Failure Bell in constant alarm. This issue was discovered while investigating a ground on MC-7AB. No abnormalities were found on MC-7AB (TSC HVAC room). The ground on MC-7AB was able to be reset but annunciator power did not return to the TSC HVAC control panel. Please investigate/repair. <I> **** Actions Taken **** Notified MCR | 02-00-E-CP-TSCHV/1
393401 | CR | 20190514 |  | 3 | R24LL: ECCS Check IST Surveillance Scheduling |  |  |  | N | NO | <D> **** Detailed Description **** There are five full flow injection surveillances required to be performed during each refuel outage (see list below). . OSP-LPCS/IST-R701, OSP-HPCS/IST-R701, OSP-RHR/IST-R701, OSP-RHR/IST-R702 and OSP-RHR/IST-R703. . These surveillances are usually scheduled just after we enter Mode 4 so we can flush the associated RPV nozzle to reduce dose rates. However, the surveillance can not closed out because there is a step to record the completion of the LLRT test on the check valve which can not be completed until the associated divisional window starts. . The model work orders for these IST check valve tests should have an XX task created to perform the partial surveillance for the check valve injection test at the front of the outage and then schedule the rest of the surveillance at the divisional window. . This change will improve predictability in that we won't have five surveillances remaining open for over a week riding the schedule. <N> Action complet
393403 | CR | 20190514 |  | 4 | Turbine Building - Higher Indoor Temperature | N | N |  | N | NO | <D> **** Detailed Description **** Due to work on E-DP-S1/1C, the HVAC for the turbine building is not operating resulting in higher indoor temperatures, particularly on the scaffolds in the T471 heater bay. This condition is likely to remain for a few days until tasks in WO 0211511708 to re-energize are completed. <I> **** Actions Taken **** Notified supervisors to maintain compliance with ISPM-13, High Temperature Work Areas by monitoring temperatures. Notified OCC that coolers for cool down areas are needed for the T471 heater bay.
393404 | CR | 20190514 | CAQ | D | DETECTOR CIRCUIT TROUBLE on FP-CP-CO2 | N | Y |  | N | YES | <D> **** Detailed Description **** The DECTOR CIRCUIT TOUBLE light was lit on FP-CP-CO2. The alarm was silenced. MCR was notified. The reset button was pushed per the ARP, and the alarm did not clear. The generator exciter housing is currently removed from the exciter. <I> **** Actions Taken **** Notified MCR | 02-00-FP-CP-CO2
393405 | CR | 20190514 |  | 3 | R24LL exciter shipping brace needs jacking bolt | N | N |  | N | NO | <D> **** Detailed Description **** The shipping brace for the exciter is used to support the exciter shaft when the exciter is disconnected from the generator. The shipping brace has 3 bolt holes on each side, the center hole needs to be tapped to allow using it as a jacking bolt to adjust the height of the brace to provide proper support of the shaft. <N> **** Equipment Description **** E-EXC-1 shipping brace Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
393406 | CR | 20190514 |  | 4 | Minor First-Aid |  |  |  | N | NO | <D> **** Detailed Description **** The employee opened a file cabinet drawer and the whole drawer came out and fell onto the floor causing a minor scratch onto her left index finger. The scratch was cleaned and a band-aid was applied. Employee has since returned back to work with no issues. This is a minor first-aid. <I> **** Actions Taken **** WPS Safety followed ISPM-1 procedure requirements while notifying Occupational Health, ENW Industrial Safety and Site Support Contractor Manager regarding the details of this Minor First-Aid. No further action is required. <N> Williams Plant Services.
393407 | CR | 20190514 |  | 4 | TDAS point X327 is currently indicating ~ 2 inches less |  |  |  | N | YES | <D> **** Detailed Description **** TDAS point X327 is currently indicating ~ 2 inches less than RFW-LR-608 (FLOOD UP RANGE) red pin. They were tracking the same until ~ 1420 on 5/14/2019. <I> **** Actions Taken **** Informed CRS/SM | 02-00-RFW-LR-608
393409 | CR | 20190514 |  | 4 | HD-LS-6BL Lessons Learned | N | N |  | N | YES | <D> **** Detailed Description **** HD-LS-6BL is a low level switch that monitors the HP heater 6B and will open on Low Level. Work order 02095223 was initiated to replace HD-LS-6BL, during repair efforts craft found wires terminated on terminals 1 and 3, instead of terminals 2 and 3 as documented on the determ/reterm sheet. Terminal 2 is the common terminal on a Form C contact. When the wires were terminated on terminal 1 and 3 the circuit would never be completed as one of the two contacts would always register open as the switch changes state. This implies that when WR 29127681 corrective actions was completed on 3/31/16 with an incomplete understanding of the circuit design as well as improper verification upon work completion. I & C Maintenance and Engineering worked to resolve the issues via WO 02095223 <I> **** Actions Taken **** Notified EOC and Shift Manager Worked with I&C Maintenance to resolve <N> **** Equipment Description **** Turbine Generator Building 471' Elevation F6/7.8 | 02-00-HD-LS-6BL
393411 | CR | 20190514 |  | 3 | Procedure change to PPi.PPM,10.17.3 |  |  |  | N | NO | <D> **** Detailed Description **** Procedure 10.17.3 "Main Steam Isolation Valve Overhaul" need steps 7.2.6 through 7.2.12 and steps 7.11.1 through 7.11.3. These steps are not used since the cam bracket assembly is not removed with this procedure. This change can be made during the next procedure review cycle. <I> **** Actions Taken **** Initiated this CR after being informed of the issue by the performing Electrician. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
393412 | CR | 20190514 | CAQ | D | O-CRD-HCU-4259 -001 isolations leaking by | Y | N |  | N | NO | <D> **** Detailed Description **** WO 02110058 is for replacing the water accumulator on this HCU. Water continues to issue through CRD-V-4259/107 at slow rate ~ pencil stream. Hose remains connected to 107 valve to capture drainage. Craft should evaluate ability to perform their work with this leakby rate. Consider scheduling this in the CRD system window to minimize D/P across isolation valves (crd pumps will be off).
393413 | CR | 20190514 | CAQ | D | DG4 abnormal noise | N | Y |  | N | YES | <D> **** Detailed Description **** While running DG4 for WR 29148278 pmt, a sporadic rattling/grinding noise was heard from the fan/alternator area. See video attached in EDMS. | 02-00-E-GEN-DG4
393414 | CR | 20190514 |  | 4 | (R24LL) Job delayed because correct resources not identified |  |  |  | N | NO | <D> **** Detailed Description **** It was not recognized until the vendor arrived on site, that the static ground straps had to be hung by qualified station electricians. The electric shop had to divert resources to make this happen on an emergent basis. Details: Oil leak on transformer E-TR-6/61 was added to R24 in 1Q19 due to environmental concerns and a commitment to the state. In order to align PMs with the SH-6 outage window in the long range plan, the inspect-and-clean PM were added into R24, with the understanding that shop electrical resources would not be used to perform the PM work. The procedure to perform the PM, normally performed by the station electricians, has a step to install static grounds. No task was initially created to install static grounds for the vendor - they are not qualified to install these grounds. New tasks were added emergently. <I> **** Actions Taken **** 1. Emergent issue created by OCC 2. Eletcric shop diverted resources to hang static grounds.
393415 | CR | 20190514 |  | 3 | OSPPPCV is not working. | N | N |  | N | YES | <D> **** Detailed Description **** OSPPPCV is not working. System Status shows multiple red ice cubes for PPCRS MUXS. Needs to investigate and repair. This is the repeat issue. No abnormal alarm on PPC-COMP -8715. <I> **** Actions Taken **** CRS/System Engineer informed. | 02-00-PPC-COMP-8715
393416 | CR | 20190514 | CAQ | D | FDR-TK-9 sent to CST's with Hi UV Sulfates | N | N |  | N | NO | <D> **** Detailed Description **** FDR-TK-9 sent to CST's with Hi UV Sulfates Results are 6.1 ppb UV Sulfates, limit is 5 ppb <I> **** Actions Taken **** Informed PSRO, MCR
393417 | CR | 20190514 | CAQ | D | RRA-CC-8 and 9 could not be drained | N | Y |  | N | YES | <D> **** Detailed Description **** Clearance O-RRA-CC-8/9TSW-001 to drain Cooling Coils RRA -CC-8 and RRA-CC-9 in the Steam Tunnel was hung, but no water drained from the TSW piping. This was probably due to the vent and drain valves being plugged. TSW-V-205 and 207 are ball valves TSW-V-208 and 209 are globe valves Maintenance needs to be aware that no water was drained from the system. The clearance has been signed as hung as all the valves are in the required position with drain hoses attached. <I> **** Actions Taken **** Informed Production and OCC <N> **** Equipment Description **** Main Steam Tunnel | 02-00-RRA-CC-8,02-00-RRA-CC-9
393418 | CR | 20190514 | CAQ | D | Annunciator P603-A8 Drop 5-6 SLC TANK LEVEL HI/LOW locked in | Y | Y |  | N | YES | <D> **** Detailed Description **** Annunciator P603-A8 Drop 5-6 SLC TANK LEVEL HI/LOW locked in. SLC-LIC-601 currently reads ~5000 gal, TDAS point X077 reads 4889 gal. <I> **** Actions Taken **** Informed CRS/SM | 02-00-SLC-LI-601
393420 | CR | 20190514 |  | 4 | DEH-PI-1 found OSL after DEH was shut down |  |  |  | N | YES | <D> **** Detailed Description **** DEH-PI-1 is the pressure indicator for DEH filter transfer system pressure. After DEH was shut down, this gauge was found reading Off Scale Low. The gauge needs calibration or replacement. The pressure indicator is in the kidney loop filtration and does not impact system operation. This is not a startup issue. <I> **** Actions Taken **** documented condition <N> **** Equipment Description **** DEH skid, right side panel, TG471E | 02-00-DEH-PI-1
393421 | CR | 20190514 |  | 4 | TOA-42-3A6B contactor chattering. |  |  |  | N | YES | <D> **** Detailed Description **** TOA-42-3A6B contactor was chattering loudly after starting TOA-FN-1A. <I> **** Actions Taken **** Informed FIN electrical supervisor who inspected the noise at the breaker. No immediate concern, but should be investigated for possible contactor replacement. . Update: The following day the fan indicating lights were dimly pulsating, so the fan was stopped. See video in EDMS. <N> **** Equipment Description **** TG 501 east | 02-00-TOA-42-3A6B
393422 | CR | 20190514 |  | 3 | RRC-L-1B Assembly completed before Coating Applied | N | N |  | N | YES | <D> Work Instructions in WO 02136481-04 directed SSC pipefitters to assemble RRC-L-1B lower oil reservoir before coating was applied on base metal. Primer of class 1 coating requires bare metal to be sandblasted and this cannot occur with the RRC-L-1B assembled and will cause re-work to occur by the SSC Pipefitters to dis-assemble RRC -L-1B and re-assemble after coating. The scheduled installation of 05-26-19 work is not expected to be impacted. <I> Iniated planning to revise work instructions on WO 02136481-04 Notified Supervision Notified EN Painters of action taken <N> CR at INPROG. Moved to Approved and SRO for OPS review. Work instructions have been revised. No further actions required. | 02-00-RRC-L-1B
393423 | CR | 20190514 |  | 3 | nonroad engine information not submitted to E&RP | N | Y |  | N | NO | <D> **** Detailed Description **** During a site walk down by Environmental and Regulatory Programs (E&RP) staff on 5/14/2019, various nonroad engines were found in the CGS main transformer yard (1 generator, 4 light towers, 1 welder, 1 air compressor, 2 pressure washers) and lot outside the ISFSI (2 light towers). Equipment/engine information was not provided to E&RP prior to bringing the equipment on site (as required in GBP-ENV-07). <I> **** Actions Taken **** Notified E&RP Manager. Discussed requirement with Transformer Yard Coordinator. Obtained equipment/engine information by inspecting equipment and by calling Sunbelt Rental company. An updated Notice of Intent to Operate Nonroad Engines was submitted to the Energy Facility Site Evaluation Council (EFSEC) and WA Department of Ecology on 5/14/2019. No additional actions needed at this time. <N> The cumulative engine size for nonroad engines currently at CGS is ~1,330 horsepower. If additional nonroad engines are utilized and the cumulative engine size exceeds 2,000 hp, EFSEC/Ecology approval is required prior to operation. R24LL
393424 | CR | 20190514 |  | 4 | BRE 34 Door needs maintenance |  |  |  | N | YES | <D> **** Detailed Description **** The door to BRE 34 needs maintenance. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Security notification made,CR/WR generated <N> **** Equipment Description **** BRE 34 is located south of building 62 and east of the GSB
393426 | CR | 20190514 |  | 3 | Spare Condensate Booster Motor needs inspections & tested |  |  |  | N | NO | <D> **** Detailed Description **** Spare Condensate Booster Motor (CATID 8632/UTC 0000541368/GE Serial No. HHH285001698) was evaluated on CR 391391-03 and determined to need inspection and testing like the Condensate Booster Motor COND-M-P/2A being installed in R-24 due to the same reason that it has been in long term storage since 2015. PM 23590 under WO 02127099 was performed on 10-25-18 and was the first document to PM these motors. WOT instructions were N/A'd for both motors. COND-M-P/2A motor was inspected and tested at a vendor verifying all crtical motor parameters are acceptable for installation for operation in R-24. The spare new GE motor has no path for funding to inspecti and test it to verify readiness for installation into the plant and PM 23590 needs to be revised to revise it reflecting just the PM on UTC 0000541368 <I> **** Actions Taken **** Estimated cost of inspection and testing the spare motor and put on Risk Register requesting funding Notified Asset Management, Mainteance Services, Electrical Maintenanc, Supply Chain, Motor Component Engineering.
393427 | CR | 20190514 |  | 3 | Dropped electronic dosimeter in the drywell. |  |  |  | N | NO | <D> **** Detailed Description **** A worker dropped his electronic dosimeter in the drywell and it came to rest on a pipe resulting in an invalid dose alarm. <I> **** Actions Taken **** Histogram read to obtain dosimeter history Worker restricted from access to the RCA pending investigation. <N> On 05/14/19 @ 1720 a worker's DRD fell onto a RWCU pipe line inside the drywell 541 elevation (RWP 30004340 / ALARA Task 02128605-01-08). Worker immediate notified nearby HP Technician. DRD was retrieved. Worker and HPT exited the area. Note: DRD history shows worker in a dose rate field of approximately 50 mrem/hr. When dropped, the DRD came to rest in a dose rate field of 2,400 mrem/hr on contact and 1,100 mrem/hr at 30 cm. Form 19086 has been completed and sent to records. No further action required.
393428 | CR | 20190514 |  | 4 | R24 LL CW Temp Dewatering rate and method inadequate |  |  |  | N | NO | <D> **** Detailed Description **** CW temporary blowdown rate at the start of R24 was inadequate. This resulted in overflow to the electrical vault and ultimately in flooding in the Radwaste Building which required unplanned laborer resources to clean up water and caused a concern with Total Organic Carbons potentially making their way to the CSTs. Additionally, the high basin level has the potential to impact scheduled work. The current pumping method is one Godwin pump. A second Godwin pump was staged but the parts to connect it were not staged. A similar issue occurred in R23. An R23 LL CR was written that recommended use of fire pumps due to issues with submersible pumps (CR 00365700). The associated WO was cancelled due to concerns with NEIL requirements. <I> **** Actions Taken **** Emergent Issue during R24.
393429 | CR | 20190514 |  | 4 | W-1 sump pump is in PTL due to CW level issues. |  |  |  | N | YES | <D> **** Detailed Description **** W-1 sump pump ( FDR-P-8) is in PTL due to CW level issues. The pump currently does not have power due to the SH-6 outage. Recommend evaluating the water in the sump prior to restoring the pump to normal opartion. <N> Per Chemistry, the water will need to be pumped out of the sump prior to returning the pump to service. | 02-00-FDR-P-8
393435 | CR | 20190514 |  | 4 | Minor cut on finger - no first aid needed |  |  |  | N | NO | <D> **** Detailed Description **** While carrying a pair of work order package folders, an employee rotated one of the folder in their hands and caught their right middle finger on the edge of the metal fastener attached at the top of the folder - contact which resulted in a small cut on the end of the finger. The employee did not immediately realize the small cut had occurred, but noticed a small amount of blood that had accumulated and dried on the cut. This minor incident did not require first aid. <I> **** Actions Taken **** Called and left message with occupational health, called industrial safety (line out of service, email sent), notified department manager and the shift manager as required by ISPM-1. Also completed incident reporting requirements in PTL as required, reference Incident Report 19-0005.
393436 | CR | 20190514 |  | 3 | (QA) POC Meeting Administrative issues |  |  |  | Y | NO | <D> **** Detailed Description **** 2019 Pre-NIEP Focused SA 376427 identified multiple administrative issues with POC Meeting Minutes and Records. See EDMS for details. <I> **** Actions Taken **** Discussed with Quality and Regulatory Affairs Management. Recommend assignment to Regulatory Affairs. <N> The response to the deficiencies loaded up into EDMS was revised to add more clarifying language.
393438 | CR | 20190514 | CAQ | B | M3 CT terminal Block wires not terminated / arcing evidence |  |  |  | N | YES | <C> As per the MRT this is being changed from a CAQ C to a CAQ B Risk: MEDIUM - due to possible regulatory concerns Cause: uncertain Investigation Template required <D> **** Detailed Description **** During the execution of work order task 02115679-18 â€œE-TR -M3: TIGHTEN ELECTRICAL CONNECTIONS/CONDUIT HARDWAREâ€, inspection of a CT terminal block (303.3 X1 Winding Temperature), revealed wires were not terminated along with evidence of arcing (black deposits). . Note: This location had oil leaking out of it online. See EDMS for pictures. Reference CVI OMM 1205-00,28 <I> **** Actions Taken **** Took Pictures, contacted OCC and contacted Factory Rep. <N> All other inspections are complete for M1, M2 and M3. This is the extent of condition. . Per Regulatory Affairs the issue documented in this CR has a potential for an NRC more than minor NCV. Therefore this CRs priority is being changed to a condition adverse to quality and will be rescreened by the management team. . Refer to 393438-01 In-Prog. notes for additional information <R> This event resulted in a Green Finding for failure to follow plant procedure 10.25.19, "Termination and Splicing Instruction." There is no associated CCA. This finding is documented in IR 2019-003. | 02-00-E-TR-M3
393439 | CR | 20190514 |  | 4 | TMU leakby |  |  |  | N | YES | <D> There is leakby from TMU to the CW system. Engineering calculated ~1300 gpm. This impacts our ability to blowdown the CW basin. Suspect the closed stops for TMU-V-9, 6, 5 arenâ€™t adjusted properly. Investigate and repair. <I> Initiated CR. Informed emergent work manager, mechanical maintenance manager, and SM. CR 366206 (5/26/17) documents TMU-V-23 has 1300 GPM of leakby, that is the leakby that was communicated. The work to perform is coded RP00 but must be scoped into R25 during CW draindown activities. | 02-00-TMU-V-5,02-00-TMU-V-6,02-00-TMU-V-9
393440 | CR | 20190514 |  | 3 | Worker Reports Foot Injury |  |  |  | N | NO | <D> **** Detailed Description **** A worker (org code 52214) arrived at work on 5/14/19 and reported they had a blister to their foot in which they sought offsite medical care. Investigation is underway to assess the origin of the injury. <I> **** Actions Taken **** Notified RPM and Industrial Safety. ISPM-1, Safety Program, guidance followed. <N> Worker communicated that the reported injury is not work related. Per Legal, no additional documentation is required at this time.
393441 | CR | 20190514 |  | 4 | RWCU Purge Filter 7B Hi DP needs to be changed |  |  |  | N | YES | <D> **** Detailed Description **** Swapped to RWCU Purge Filter 7A due to a high differential pressure on CRD-DPI-7 of 33 psid. Filter needs to be changed. <I> **** Actions Taken **** Swapped RWCU Filters | 02-00-CRD-FU-7B
393442 | CR | 20190515 |  | 3 | R24LL Schedule change impact to FPC Assist Alt |  |  |  | N | NO | <D> **** Detailed Description **** When a laptop battery impacted a discharge test, E-B2-1 maintenance was moved up rendering RHR-V-8 inoperable. This impacted placing RHR-SYS-B in FPC Assist mode per the established procedure, since RHR-V-9 is declared inoperable to lift leads to make it a throttle valve. SOP-RHR-SDC -BYPASS states, DO NOT allow RHR-V-8 and RHR-V-9 to become inoperable at the same time without formal documentation that there are no other alternatives possible. The documentation should be prepared by Operations and Regulatory Affairs, and approved by POC. CAPR-2.1. Since the implementation of TS 3.3.5.2, this CAPR may need to be readdressed. However, Operators looking ahead in the procedure to implement SOP-FPC-ASSIST-ALT identified the problem, contacted licensing and ops managemnet in the OCC and changed SOP-FPC-ASSIST-ALT to allow throttling RHR-V-8 manually to maintain RHR-V-9 operable. It is anticipated since operators looked ahead, expanded the team, created a solution and operators will be standing by ready to implement, the schedule will not be impacted. Recommend a schedule tie between FPC Assist Alt and B2-1 or S2-1 maintenance be established to prevent this unless planned to do so.
393443 | CR | 20190515 |  | 4 | HD-LCV-12A has Internal valve degradation |  |  |  | N | YES | <D> **** Detailed Description **** (WO 02129938) AOV Diagnostics has shown HD-LCV-12A has internal valve degradation. Stem and plug may have become loose or possibly separated. Valve needs rebuilt to ensure proper operation. <I> **** Actions Taken **** CR written to allow for preplanned contingency to be OSCRâ€™d into outage. <N> **** Equipment Description **** TB 480' E9/9.3 | 02-00-HD-LCV-12A
393444 | CR | 20190515 | CAQ | D | SLC Level Indication Erratic - Needs to be rodded out | Y | Y |  | N | YES | <C> Trend to CR 393418 Same WR 29148658 <D> **** Detailed Description **** The level indication for SLC-TK-1 has been erratic and the bubbler need to be rodded out. <I> **** Actions Taken **** Generated WR | 02-00-SLC-LI-1
393446 | CR | 20190515 | CAQ | D | Refuel Bridge slack cable light flashing | Y | Y |  | N | YES | <D> **** Detailed Description **** While using the Refuel Bridge the operator started the bridge and the slack cable started blinking and the bridge controls operated the bridge backwards with the mast in the normal up position. The load cell display isnâ€™t constant. <I> **** Actions Taken **** Vendor replaced a module (MODULE, RELAY OUTPUT 16-POINT) per vendor recommendation. This did not correct the problem. Initiated a CR and Work request. | 02-00-NSSE-EQ-8
393447 | CR | 20190515 |  | 3 | R24LL: SOP-ENTRY-WW enhancement |  |  |  | N | NO | <D> **** Detailed Description **** The initial wetwell entry was delayed while verifying lighting circuits were energized (see WOT 0211167501). This verification was specified in the WOT instructions and not the SOP. It should be added to the prerequisites for SOP-ENTRY-WW. Additionally, these circuits are energized as part of SOP-ENTRY-DW. A note should be added to SOP-ENTRY-WW that these circuits are energized as part of SOP-ENTRY-DW. <I> **** Actions Taken **** Initiated CR
393448 | CR | 20190515 |  | 3 | Dropped ED |  |  |  | N | NO | <D> **** Detailed Description **** During the internal bolt removal for MS-DT-1C a Siemens craft tore his PC and after exiting the area discovered his ED came off his lanyard The ED was retrieved off the scaffolding decking by a fellow worker. Event was reported to Siemens supervision. <I> **** Actions Taken **** Reported to FME coordinator.
393449 | CR | 20190515 | CAQ | C | R24LL: SOP-RHR-SDC-BYPASS, SOP-RPS-OPS |  |  |  | N | NO | <D> **** Detailed Description **** Remove the CAPR for ensuring either RHR-V-8 or RHR-V-9 are operable at all times. This CAPR is superseded by the new TS requirements in Amendment 251 (adoption of TSTF-542). The CAPR supported maintaining the PCIV safety function in Mode 4 and 5. The new TS deleted all Mode 4 and 5 PCIV requirements from TS 3.6.1.3. The Mode 4 and 5 requirements are relocated to TS 3.3.5.2 and TS 3.5.2. The new TS requirements provide additional allowances for maintaining water inventory control (such as using a dedicated operator) in the event both RHR-V-8 and RHR-V-9 are inoperable. <I> **** Actions Taken **** Wrote CR
393450 | CR | 20190515 |  | 3 | Loss of smear disk |  |  |  | N | NO | <D> **** Detailed Description **** The HP tech requested the Siemens craft to perform a contamination smear of the area at the opening of MS-DT-1C hood. The craft was handed 5 smears and when the smears were returned to the HP tech one of the smear disks had fallen off the paper backing. The disk was not found. The dropped smear disk was reported to HP supervision. <I> **** Actions Taken **** Reported to FME coordinator.
393451 | CR | 20190515 |  | 4 | A pair of channel locks was found in the NONSEG BUS N2/X. |  |  |  | N | NO | <D> **** Detailed Description **** WORK ORDER 02112118-01 - A pair of channel locks was found in the NONSEG BUS N2/X on the 471â€™ elev. at Section D - 38 <I> **** Actions Taken **** Notified Williams Management.
393452 | CR | 20190515 |  | 4 | Failed freedom of movement check on BS-V-10A |  |  |  | N | YES | <D> **** Detailed Description **** During performance of WO# 0211099201 BS-V-10A failed the freedom of movement check after the valve was unpacked requiring further disassembly of the valve. Steps were already provided in the WO to continue and was approved by engineering. This CR is for tracking only and no further actions are required. <I> **** Actions Taken **** CR generated for tracking. <N> **** Equipment Description **** TB 488 | 02-00-BS-V-10A
393453 | CR | 20190515 |  | 4 | Failed freedom of movement check on BS-V-13A |  |  |  | N | YES | <D> **** Detailed Description **** During performance of WO# 0211282301 BS-V-13A failed the freedom of movement check after the valve was unpacked requiring further disassembly of the valve. Steps were already provided in the WO to continue and was approved by engineering. This CR is for tracking only and no further actions are required. <I> **** Actions Taken **** CR generated for tracking <N> **** Equipment Description **** TB 488 | 02-00-BS-V-13A
393454 | CR | 20190515 |  | 3 | R24LL: SOP-MSIV-OPS minor revision needed |  |  |  | N | NO | <D> **** Detailed Description **** SOP-MSIV-OPS step 5.7.4 references The Potential of Draining the Reactor Vessel or Cavity, this is now controlled per the Water Inventory Control LCS and should be evaluated if this step is needed. Recommend removing step 5.7.4 of SOP-MSIV-OPS major rev 018 minor rev 03 as it no longer appears to be relevant to current tech Spec Water Inventory Control. <I> **** Actions Taken **** Discussed with SROs.
393455 | CR | 20190515 |  | 3 | Unanticipated Dose Rate Alarm |  |  |  | N | NO | <C> Re-opened at request of department <D> Individual accessed the pltform around HPCS-V-4 in the overhead of 522' RX and received a dose rate alarm of 150 mrem/ hr. <I> Notified RP Supervision/ Management Performed Follow-up Survey VSDS_Prod-M-20190515-15 Ran Histogram on Electronic Dosimeter <N> A previous survey that was used for the briefing and a follow-up survey identified dose rates on the platform of 2-3 mrem/hr. The individual was interviewed and stated that he did not recall bumping his alarming dosimeter against anything. His alarming dosimeter setpoint was 80 mrem/hr. A histogram report showed a sharp spike when the alarm occurred. Individual left the area and reported to HP following the alarm. Surveys and histogram attached. This was an invalid dose rate alarm.
393460 | CR | 20190515 |  | 4 | TG HP access point safety issue |  |  |  | N | NO | <D> **** Detailed Description **** Entry door to TG (West) HP access point has a head knocker for anyone ~6'4" or taller. See attached EDMS photo. This hazard is not obvious when entering from the exterior and could result in an injury. Recommend safety review for potential improvement or elimination. <N> This is a safeguards issue and cannot be removed.
393461 | CR | 20190515 |  | 3 | WO 02115124-01 E-DP-S1/1C3 |  |  |  | N | NO | <D> **** ANONYMOUS CR - Detailed Description **** Work order 02115124-01 has a drawing EWD-50E-019 pre -modification for Panel E-DP-S1/1C3 the breaker nomenclature does not match what is in the field. Planning was called and they took notes and pictures. The work order will need to be revised to proceed. Work is at a stop at this time. nomenclature does not match whatâ€™s in the field. Planning <I> **** Actions Taken **** Contacted Planning and Management. <N> ANON CR generated. Reviewed for Safety Conscious Work Environment (SCWE), forwarded to OPS for review. Work is completed. Per Engineering, this issue was a misunderstanding and has been resolved.
393462 | CR | 20190515 |  | 4 | RW 437 drain is clogged and wont pass sufficient flow. | N | N |  | N | YES | <D> **** Detailed Description **** RW 437 drain is clogged and wont pass sufficient flow. The drain is located in front of E-CP-G11/P019. <I> **** Actions Taken **** stopped the draining before the drain overflowed. Wrote CR. <N> **** Equipment Description **** RW 437 drain in front of E-CP-G11/P019.
393463 | CR | 20190515 |  | 4 | X-ray 3 |  |  |  | N | YES | <D> **** Detailed Description **** Coffee spilled on X-ray belt. | 02-00-SEC-XR-3
393467 | CR | 20190515 |  | 3 | HD-V-5A handwheel is off | N | N |  | N | YES | <D> **** Detailed Description **** The Hand wheel on HD-V-5A is off and should be repaired if need be and replaced <I> **** Actions Taken **** Reported the Hand wheel to my supervisor Rob Rhodes <N> **** Equipment Description **** Main condensor on south side | 02-00-HD-V-5A
393468 | CR | 20190515 |  | 3 | Licensing and Engineering evaluation of TSAS 3.9.8 |  |  |  | N | NO | <D> **** Detailed Description **** Please provide an enginnering and licensing evaluation of when TSAS 3.9.8 condition C needs to be entered and what alternate coolant circulation methods can be credited for completion of this required action. Specifically while performing SOP-FPC-ASSIST-ALT.
393470 | CR | 20190515 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0066149 Fluke AC/DC Current Clamp- model i1010 found OOT & adjusted within specs. Not used during Calibration cycle. DEF #7030A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
393472 | CR | 20190515 | CAQ | D | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #45190 Fluke Current DC/AC Current Clamp- model 80I-1010 Passed Calibration but needed to be replaced. New one purchased. DEF #7031A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
393473 | CR | 20190515 |  | 4 | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0064311 Ashcroft Sensor- model HQS-2 50 in hg abs found OOT & Rejected- Unable to adjust. Not used during Calibraiton cycle. DEF #7032A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
393474 | CR | 20190515 |  | 3 | PPM 15.1.30 lacks residual pressure testing | N | N |  | N | NO | <D> **** Detailed Description **** NEIL insurance called Fire Protection on 5/14/19 and asked questions about our compliance with the expectation for flushing and flow testing of standpipes that are below the level of the fire main ring header. NEIL was told we revised PPM 15.1.30 to add this new NEIL expectation. NEIL asked about whether we are also recording residual pressure during flow as stated in the Interpretive Guidance section of the NEIL Loss Control Manual. This question was researched and the answer is no, PPM 15.1.30 sections 7.3 & 7.4 do not record residual pressure during the flushing. FP System Engineer trending of the residual pressure helps to ensure there is no internal pipe blockage. PPM 15.1.30 should be revised to meet the Interpretative Guidance section 4.2.8.5.9.2. See EDMS. This is not an LCS 1.10 operability issue and is not a restart constraint. Assign to Maintenance Procedures. It would be beneficial if this procedure revision were issued prior to the fall 2019 NEIL Property Loss Control inspection (exact date not set yet but assume early November). <I> **** Actions Taken **** Discussed with Fire Marshal (FP Supervisor & FP System Engineer on nights) and wrote this CR. Will notify NEIL of this CR condition.
393475 | CR | 20190515 |  | 3 | Investigation of TAR/TUR Reporting for Fluke 7250xi Pressure |  |  |  | N | NO | <D> Investigation of TAR/TUR Reporting for Fluke 7250xi Pressure Standard <I> Issued CR <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
393476 | CR | 20190515 |  | 4 | (R24LL) Ops outage Lesson learned to date |  |  |  | N | NO | <D> **** Detailed Description **** Attached to the EDMS is a list of Ops lesson learned from day 1 to 5.14.19. Operations is tracking all lessons learned in One note and will continue through out the outage. Ops CIC will issue CRs going forward to track the information when on shift. <I> **** Actions Taken **** Copied all LL to date and created CR for trending only.
393478 | CR | 20190515 |  | 4 | E-DISC-TR6/62 cover is broken | N | N |  | N | YES | <D> **** Detailed Description **** The cover to E-DISC-TR6/62 is broken at the lower hinge. The upper hinge is also in very poor repair and should be replaced/repaired as well. The cover is currently being held in place by two cover screws. The cover's state of disrepair does not impair the ability to operate E-DISC -TR6/62. The two cover screws and upper hinge are allowing the cover to perform its intended function, for the time being. E-DISC-TR6/62 is located outside of the #1 CW Electrical Bldg. <I> **** Actions Taken **** Informed SSS <N> **** Equipment Description **** Outside CW Elect. Bldg. #1 | 02-00-E-DISC-TR6/62
393479 | CR | 20190515 |  | 4 | E-DISC-2C2AR failed to close in. | N | N |  | N | YES | <D> **** Detailed Description **** Attempted to close in E-DISC-2C2AR and it would not close. The disconnect would operate to the ON position but would not close in. | 02-00-E-DISC-2C2AR
393480 | CR | 20190515 |  | 4 | RB 606 PCM/Frisker Room Light Malfunctioning | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The light in the Refuel Floor PCM/Frisker room is intermittently working. The high majority of the time the light is out. This makes the surveying of personnel who alarm the IPM and the counting of smears for contamination very difficult. The bulbs were changed out prior to R24. <I> **** Actions Taken **** Contacted RP Supervision and initiated a WR <N> **** Equipment Description **** Refuel Floor Lower Kelly Building PCM/Frisker room
393481 | CR | 20190515 |  | 4 | INADEQUATE LIGHTING RX 572 RHR-HX-1A |  |  |  | N | YES | <D> **** Detailed Description **** INSIDE RHR-HX-1A RM ON RX BLDG EL 572 THERE IS ONLY 1 WORKING LIGHT. IT IS DIRECTLY ABOVE THE ACCESS DOOR BEHIND THE SHEILD WALL AND PROVIDES NO LIGHT FOR WORK INSIDE THE ROOM. PLEASE REPLACE BULBS <I> **** Actions Taken **** NOTIFIED SUPERVISION, GENERATED CR, PROVIDED HEAD LAMPS TO CRAFT FOR WORK WITHOUT ADEQUATE LIGHTING. <N> **** Equipment Description **** RHR-HX-A RM RX BLDG 572
393482 | CR | 20190515 |  | 3 | Performance of OSP-RCS-C105 |  |  |  | N | NO | <D> **** Detailed Description **** PPM 3.4.1 step 8.2.2.g requires that OSP-RCS-C105 be performed when opening a new WIC permit, this is contrary to OSP-RCS-C105 which specifies it performance is only required when opening a WIC permit that has a drain time < 36hrs.
393483 | CR | 20190515 |  | 3 | Oil Puddles found on RRC 1B Pump Insulation and Motor | N | N |  | N | YES | <D> **** Detailed Description **** During inspection of the RRC B motor and pump, two puddles of oil were observed on top of the pumpâ€™s insulation (See the picture in the EDMS folders. The RRC-M-P/1B lower bearing reservoir oil level had been decreasing all last cycle, and seems the most likely source of the puddles. In addition, a small amount of oil was observed below the upper oil reservoir level float (RRC-LS-1B â€“ picture also attached). Both the upper and lower level floats (RRC-LS -1B and RRC-LS-2B) fittings should be examined for potential leaks and snugged as necessary. R24 Work Package 02124487 already has instructions to accomplish this. <I> **** Actions Taken **** Informed EOC. | 02-00-RRC-LS-1A,02-00-RRC-LS-1B,02-00-RRC-M-P/1B
393484 | CR | 20190515 |  | 3 | Procedure enhancement: OSP-NSSE-W401 |  |  |  | N | NO | <D> **** Detailed Description **** OSP-NSSE-W401 cannot be performed with the RPS jumpers installed IAW SOP-RPS-BYPASS. This should be identified in the pre-requresites for the surveillance.
393485 | CR | 20190515 |  | 3 | (R24LL) Not following SOP-CW-OPS | N | N |  | N | NO | <D> **** Detailed Description **** CUrrently we are running two godwin pumps for temporary blowdown. Per SOP-CW-ops section 5.9. this is written to use a godwin pump with an electrical pump as a backup. the Godwin pump is the primary and if needed the second pump (electric) can be run. This is not the current configuration. We got here because of poor planning. WO 02111561-01 was written to onlly hookup the godwin pump. AN electric pump was not staged. When the godwin pump was not keeping up with lowereing CW basin level WO 02111561-14 was added to install a second godwin pump. AT the same time the SOP-SW-OPS should have had a change writtin to allow the second godwinpump insteads of an electric pump. So now we are operationg outside of the way the SOP is written. This is a case of allowing schedule pressure to push us, instead of doing the right thing whis is to change the procedure this chould have been done in parrallel with writing the new work order task. . SOP-CW-OPS section 5.9 needs to be revised to allow the use of two godwin pumps or electric pumps. <I> **** Actions Taken **** Wrote CR
393486 | CR | 20190515 |  | 4 | GSB Chiller Nitrite Level Low | N | N |  | N | NO | <D> **** Detailed Description **** Monthly sampling of the GSB chiller indicated the nitrite level was approximately 25 ppm. The desired system concentration is 1000 ppm per PPM 12.14.10. <I> **** Actions Taken **** Chemistry supervision and responsible specialist notified. A chemical addition will be scheduled. Chemical addition was performed on 05/15/19. Low nitrates are expected upon chiller start-up from being laid up during the winter. No further action required. <N> **** Equipment Description **** GSB Basement - Service Building Chiller
393487 | CR | 20190515 |  | 3 | DHP breaker test box may have some deficiencies. | N | N |  | N | YES | <D> **** Detailed Description **** Replacement breakers for E-CB-N2/6 and E-CB-S/6 both failed their reduced voltage tests. The vendor came out and could not get them to function correctly. The breakers were sent to STI for a potential overhaul. They tested the breakers at reduced voltage without making changes and the breakers functioned fine. It was narrowed down to potentially being our test box for the breakers. | 02-00-E-CB-N2/6,02-00-E-CB-S/6
393489 | CR | 20190515 |  | 4 | Fire extinguisher discharged in Transformer Yard |  |  |  | N | NO | <D> **** Detailed Description **** This occurred in the Transformer Yard during WO 02136425-01 to install new 500kV CCVTs. BPA was using a boom truck to support a line drop from the 500kV bus to the new CCVT. During the MIG welding activity on the aluminum bus, a spark entered the boom assembly of the crane and caused the material inside the boom assembly to smolder and to smoke. Upon noticing the smoke, the operator lowered the boom to allow the BPA electrician to discharge the extinguisher to prevent any burning. The most likely source of the cheat grass inside the boom assembly was nesting birds. <I> **** Actions Taken **** The BPA electrician has now cleaned additional material from inside the boom assembly.
393490 | CR | 20190515 |  | 3 | Determine if equalize charge is required after all tests |  |  |  | N | NO | <D> **** Detailed Description **** Battery discharge procedures, ESP-BXX-B101 and ESP-BXX -F101, have two steps that direct the user to perform an equalize test on the tested battery. The first is conditionally based on specific gravity readings take after the discharge, the second is a blanket requirement to place the battery on equalize. This second step needs to be investigated as to the driving source and to determine if it can be made conditional or removed. <I> **** Actions Taken **** Wrote CR. <N> **** Equipment Description **** Station batteries
393491 | CR | 20190515 |  | 3 | Evap pond 1B sediment level high | N | N |  | N | NO | <D> **** Detailed Description **** The sediment level in evaporation pond 1B (flocculator backwash sludge) is impeding flow and movement of water. Sediment interferes with the normal function of the system and challenges the ability to respond to changing conditions. <I> **** Actions Taken **** Sediment levels discussed and documented during quarterly inspection of ponds. Remediation must occur during dry months when water movement can accommodate sludge removal. (non-outage) See also CR 388501. Recommend to Facilities.
393492 | CR | 20190515 |  | 4 | HD-LCV-12A Foriegn material preventing valve from closing | N | N |  | N | YES | <D> HD-LCV-12A was diagnostic tested on 5-14-19 per OSCR 384207 for not controlling tank level. Test showed the valve was not reaching full travel yet displayed solid travel stops at both ends of stroke. Suspected a potential issue with the plug/stem. Submitted OSCR 393445 and was approved. Opened valve and found a small chunk of metal wedged in the cage with indication of the plug making contact with the foriegn material. This would prevent the valve form controlling level as documented in CR 380574 <I> Performed visual inspection of piping for any additional FM did not see any. Informed EOC <N> T -480- - -E9/9.4 - CR at INPROG. Approved CR, moved to SRO for OPS Review. | 02-00-HD-LCV-12A
393493 | CR | 20190515 |  | 3 | R24LL- No overall shop 9 dose graph created |  |  |  | N | NO | <D> **** Detailed Description **** In R23 there was an overall valve work graph tracking estimated vs. current dose. For the daily dose report for R24, the valve graph was replaced with the seperate high dose valve work which has made it difficult to see current vs. estimated dose for all valve work. The valve team needs this data to help drive dose control with a 35 Rem estimate. <I> **** Actions Taken **** requested support from ALARA on report creation.
393494 | CR | 20190515 | CAQ | C | RHR-V-8 Leakage Indicated Test Pressure Non-Conservative | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of TSP-RCS-R802 per WO 02110827, RHR-V-8 As-Found LLRT (Local Leak Rate Test) exceeded its admin limit with a leak rate of 1.557 gpm but less than the surveillance acceptance criteria of 4.75 gpm. During test data review by engineering a concern was identified pertaining to whether the test conditions meet the required test pressure range specified on the RHR-V-8 data sheet. (Reference page 57). Review of the RHR-V-8 leakage surveillance test conditions and comparing them to Calculation ME-02-08-14, the indicated pressure recorded at the test cart pressure gauge (1000 psig) may be below the low band of the required test pressure range of 966 â€“ 1010 psig. <I> **** Actions Taken **** Notified LLRT SRO / EOC/OCC <N> **** Equipment Description **** RB504 SW Valve Room <R> The LLRT will be completed and evaluated as an aggregate through the outage, once it is completed the total leakage will be evaluated for exceeding TS limits and then any potential reportability can be assessed. At this time there is not enough information to assess as this CR only documents that the admin limit has been exceeded. | 02-00-RHR-V-8
393495 | CR | 20190515 | CAQ | C | RHR-V-8 As-Found LLRT Leakage Exceeds Admin Limit | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of TSP-RCS-R802 per WO 02110827, RHR-V-8 As-Found LLRT (Local Leak Rate Test) exceeded its admin limit with a leak rate of 1.557 gpm. The admin limit is 0.15 gpm. The leak rate is below the RHR-V-8 surveillance limit of 4.75 gpm. Due to exceeding the admin limit a review of the penetration minimum pathway is required to determine if the minimum pathway leakage is acceptable or maintenance should be performed. <I> **** Actions Taken **** Notified SM / EOC / OCC <N> **** Equipment Description **** RB504' SW Valve Room <R> The LLRT will be completed and evaluated as an aggregate through the outage, once it is completed the total leakage will be evaluated for exceeding TS limits and then any potential reportability can be assessed. At this time there is not enough information to assess as this CR only documents that the admin limit has been exceeded. | 02-00-RHR-V-8
393496 | CR | 20190515 |  | 3 | RMC Laborer â€“ Struck Scaffold |  |  |  | N | NO | <D> **** Detailed Description **** RMC Laborer struck a scaffold pole in the TG 471 heater bay. The individual was wearing the correct PPE and PCs. Supervision/Management/Safety/Occupational Health informed. The individual was evaluated by Occ Health and released to continue working without restriction. Contact RMC Laborer office for additional details, x2142 or x2338. <I> **** Actions Taken **** Occ Health requested the individual to follow-up the next day. <N> This AR-CR is being addressed under AR-CR 393558. Appropriate cross references have been added.
393497 | CR | 20190515 |  | 4 | R24 LL: Water clarity delayed fuel moves in R24 |  |  |  | N | NO | <D> **** Detailed Description **** Water clarity delayed the commencement of refueling activities after RHR was shifted to FPC assist. Clarity in the RPV degraded to the point that moves could not be performed. This impacted critical path. <I> **** Actions Taken **** Initiated CR for future lessons learned.
393498 | CR | 20190515 |  | 4 | SH-6 C phase low voltage on restoring the bus | N | N |  | N | YES | <D> **** Detailed Description **** After closing in S6 breaker for restoring SH-6 from electrical maintenance the C phase indication in the main control room indicates 4200V with the A and B phase indicating 7500V. All other breakers are currently open per the restoration procedure. No amps are indicated in the main control room or locally. It appears to be an indication issue. SH-5 indicates normal voltage on all phases. <I> **** Actions Taken **** Wrote CR | 02-00-E-CB-SH6
393499 | CR | 20190515 |  | 4 | Missed sign off step in Work Package for shielding install. |  |  |  | N | NO | <D> **** Detailed Description **** RP had Laborer install shielding on 1â€PI(1)-4S (RHR-DPIS )-12A) inside the Drywell. Step 4.2 of Work Instructions for WOT 02109594 14 has the shielding coordinator 'Obtain Operations Shift Manager or designee approval to install shielding on Plant System.' The shielding coordinator on duty did not complete that step prior to the installation of the shielding. <I> **** Actions Taken **** Notified RP, Operations Managment, and Shift Manager of missed step. Documented CR.
393500 | CR | 20190515 |  | 4 | R24 lessons learned - E shop |  |  |  | N | NO | <D> **** Detailed Description **** Documentation for R24 lessons learned. N2/6 and S/6 preoutage breaker configuration work was not completed prior to R24 start due to breaker deficiencies. The breakers were not properly scheduled in the outage prior to R24 start and will now affect outage metrics (base line starts and finishes) until they can be actually worked. Another lesson learned is whitespace utilization of the SSC electrical resource curves. In house electrical resource curves were red (greater than 80 percent loaded) on several days during the outage. On day 4 some work was transferred to SSC electrical to reduce peak loading of in house electrical. Pre-emptive levelizing would have benefitted schedule adherence. <I> **** Actions Taken **** Initiated CR based on lessons learned
393501 | CR | 20190515 |  | 4 | Leak on air operator HD-LCV-6A2 | N | N |  | N | YES | <D> **** Detailed Description **** SA leak of HD-LCV-6A2. Noticable air leak from regulator on AIR operator <I> **** Actions Taken **** Wrote CR <N> **** Equipment Description **** Located in the South B bay of TB 441 adjacent condenser. | 02-00-HD-LCV-6A2
393502 | CR | 20190515 |  | 4 | Steam cut found on MS-HX-1B LP east manway cover | N | N |  | N | YES | <D> **** Detailed Description **** During the as-found inspection of MS-HX-1B under WO 02111979, it was found that the east end low pressure manway has a steam cut (see EDMS for pictures). Recommend machining then weld build-up repair. <I> **** Actions Taken **** Reported this issue to EOC and initiated this CR and WR for the repair <N> **** Equipment Description **** MS-HX-1B East | 02-00-MS-HX-1B
393503 | CR | 20190515 |  | 4 | LLRT on RHR-V-23 error, 80 mrem wasted |  |  |  | N | I DONT KNOW | <D> **** ANONYMOUS CR - Detailed Description **** LLRT on RHR-V-23 was attempted while RHR-P-2B was running, which cannot be done and should not be attempted. The result from this was 80 mrem wasted (76 mrem inside the RX 548' South Pipe Space, 4 mrem outside the room). <I> **** Actions Taken **** Op's discontinued the LLRT and all individuals exited the Contaminated, High Radiation Area. <N> ANON CR generated. Reviewed for Safety Conscious Work Environment (SCWE), forwarded to OPS for review.
393504 | CR | 20190515 | CAQ | C | ANII Identified "UNSAT" Monitoring in Document Control |  |  |  | Y | NO | <D> **** Detailed Description **** The Authorized Nuclear Inservice Inspector (ANII) issued an UNSAT Monitoring report to CGS dated 5/10/19 for the area of document control based on a recurrence of lost ASME Plans and Weld Records that had been planned but not yet implemented. The inspector documented that there have been at least six examples of this in the past three months. The inspector documented that he was calling this monitoring area unsatisfactory until a solution is set in motion to ensure better document control at CGS. The Monitoring Report is attached to this CR in EDMS. CRs for lost documents are cross-referrenced. Based discussions with Quality and IS, determination was made that QC will change the process in how these documents are routed after review. Recommend AR assignment to Maintenance Support. Recommend action to QC to change routing process until long term action in place. Also recommend action to Maintenance and/or IS to provide the necessary training and tools to allow ASME and Weld Records to be fully planned in electronic format to avoid need for paper routing. <I> **** Actions Taken **** See Description. <N> Extending the initial due date for this CR to allow the proper owner to be selected. RAP. Interim Actions taken: 1. QC to stop routing ASME Plans / Work Orders to Work Order Package Prep and instead route them directly to the respective shops. (COMPLETE) 2. WOPP to distribute all work orders to the respective shops for storing until implementation (Complete with exception of some discipline Z shops) Owed-to group changed from AR-Quality to AR-MNTPROG as agreed in meeting on 7/8/19.
393505 | CR | 20190515 |  | 4 | Insufficient water pressure on RB 606â€™ may delay outage | N | N |  | N | YES | <D> **** Detailed Description **** There is insufficient water pressure on Rx 606â€™ to operate the IVVI inspection tool to the maximum distance required for examination. This low water pressure condition appears to be a repeat of an R22 event documented under CR 328518 and worked under W/R 29120967. Multiple condensate water service boxes on 606â€™ were checked with the same results (NE and NW panels). Pressures are fluctuating between 20psi and 40psi (60psi minimum is required to fully operate the tool). Pressure was sufficent for nozzle flushing and will support examinations in higher regions of the RPV but will need to be resolved to complete the inspection scope. COND-P-3 discharge should be 0-200psig. <I> **** Actions Taken **** Tried multiple water service outlets, vendor checked equipment to verify it was operating satisfactorily, discussed with RFF coordinator. Checked for prior events CR 328518, W/R 29120967. | 02-00-COND-P-3
393506 | CR | 20190515 | CAQ | D | Water discovered in manholes E-MH-E1A/-E1B, E-MH-E4A/-E4B |  |  |  | N | YES | <C> Trend to CR 393517 <D> **** Detailed Description **** During investigation of water leaking into the RW building through electrical conduits on the W437â€™ elevation (AR CR 393428) water was discovered in manholes E-MH-E1A, E-MH-E 1B, E-MH-E4A, & E-MH-E4B. Water was found to be running into E-MH-E4A, & E-MH-E4B from the direction of the CWPH electrical vault B105. Per Appendix A of the FSAR submergence in standing water for less than a few days does not significantly impact the integrity of the cables. Water needs to be pumped from the manholes. Per Environmental the water discovered in the manholes cannot be pumped into storm drains, it must be pumped back into the CW basin. Use existing WR 29148660. <I> **** Actions Taken **** Informed EOC, discussed with environmental & maintenance. <N> **** Equipment Description **** South side Radwaste building/North side of CWPH. | 02-00-E-MH-E1A,02-00-E-MH-E1B,02-00-E-MH-E4A,02-00-E-MH-E4B
393510 | CR | 20190515 |  | 4 | IPM-8 HP-EQ-32777 out of service at HP PAP | N | N |  | N | NO | <D> **** Detailed Description **** Body sensor indication on IPM-8 at HP PAP. Instrument tagged out of service. <I> **** Actions Taken **** Informed supervision, work request written. <N> **** Equipment Description **** HP-EQ-32777
393511 | CR | 20190515 |  | 4 | SL-63 OTS Alarm for 6a, 6B, and 6C | N | N |  | N | YES | <D> **** Detailed Description **** With SL-63 Energized and Breakers 6A, 6B, and 6C closed the Control room is getting the associated Overload alarm for the three aforementioned MCC supply breakers <I> **** Actions Taken **** OPS and Maintenance leadership informed Initiating WR with this CR for Troubleshooting | 02-00-E-SL-63
393512 | CR | 20190515 | CAQ | C | E-B2-1 capacity has decreased | Y | Y |  | N | YES | <D> **** Detailed Description **** E-B2-1 surveillance ESP-B21-F101 was completed under WO 02124385-01. Calculated capacity is currently at 97.65 percent. The pervious performance of this surveillance was done under WO 02072658-01 in May of 2015, where the calculated capacity was at 108.2 percent. Per TS the capacity must be GE 83.4% in ESP-B21-F101 section 4.5 for indications of degradation. See precautions and limitations in ESP-B21-F101 section 4.5. By this definition the battery is degraded, but still meets all tech spec requirements. The reason for the degradation in this case is the fact that there was GE 10 percent drop in capacity between the previous test and this one. E-B2-1 is scheduled to be replaced online see WO 02115649 with a scheduled start date of 3/20/20. Follow on action to this CR per TS SR 3.8.6.6 is to increase the frequency of ESP-B21-F101 to annual. Performance of this surveillance requires reactor to be in mode 4 or 5, replacement should be done as scheduled. Battery remains able to perform its design function. <N> **** Equipment Description **** . | 02-00-E-B2-1
393513 | CR | 20190515 |  | 4 | BS-V-10B packing does not meet preferred packing stress | N | N |  | N | YES | <D> **** Detailed Description **** BS-V-10B was packed on 5/15/19 using Chesterton 5300 graphoil packing. The packing was torqued to 22ft/lbs. producing a packing stress of 1500 psi. Increasing the torque beyond 22ft/lbs. causes the valve to bind. Chesterton 5300 packing is manufactured in dies pressed to 2000 psi. and must be torqued to a value that creates greater than 2000 psi stress in order to achieve consolidation. At 1500 psi. (75% of the manufacturing pressure) no consolidation will take place (the process whereby the packing is compressed and spreads to fill the void between stem and stuffing box). Without achieving adequate consolidation leak free operation is not guaranteed. If the packing is torqued to a value that ensures consolidation takes place â€“ the valve will bind up. This has been a recurring issue with these non-return valves. AP Services has improved packing material that seals at lower gland stress, with less packing friction, using less rings. This packing was approved for use during R23 under RIE 365987-01 Cat IDâ€™s have been created based on the measurements obtained during disassembly and inspection work order 02112822, and suitable replacement packing is due onsite 5/16/19. It is Engineeringâ€™s recommendation that the valve be repacked with the new AP Services style 5000 packing set to prevent potential leakage or binding. <I> **** Actions Taken **** Packing was ordered and is due on site 5/16/19 Work order 02112822 is still open to facilitate the repack <N> **** Equipment Description **** T 488 D3/9.1 | 02-00-BS-V-10B
393515 | CR | 20190515 |  | 3 | R24LL: COND-V-998 is in a dangerous position to operate |  |  |  | N | YES | <D> **** Detailed Description **** COND-V-998 is just under the 471 elevation floor, it also is about 5 foot out from the 456 elevation ledge. This valve is supposed to be uncapped and opened per SOP -COND-SHUTDOWN. recommend finding a better and safer way to vent this. changing the location of the valve or adding a scaffolding task to the outage work. safety first. <I> **** Actions Taken **** discussed with supervision and walked down. Valve was N/a'd | 02-00-COND-V-998
393516 | CR | 20190516 |  | 3 | Clearance Order not assigned to Wet Well entry tasks |  |  |  | N | NO | <D> **** Detailed Description **** The scope of Work Order tasks 02118301-04 and 05 is to install and remove a system test plug to support an LLRT. A Clearance Order was not assigned to these tasks for entry into the Wet Well. <I> **** Actions Taken **** Notified OCC Operations Manager who assigned operations personnel to review the tasks for a Clearance Order.
393517 | CR | 20190516 | CAQ | D | Equip implication for water found leaking on RW 437 on 5/14 | N | Y |  | N | YES | <D> **** Detailed Description **** This CR is being generated to discuss the equipment implications of the issue discussed in CR 393428 that was coded as R24 LL. On 5/14, Water was leaking from electrical conduit that resulted in flooding in the Radwaste Building 437â€™ elevation (see video/photos in EDMS). The water was coming out of the shorter conduits with the taller conduits having standing water in them about 12â€ to 18â€ above the floor. The water source that was evaluated was from the electrical vault in the Circ Water Pump house MC room. The CW basin level is currently high due to a known leaking TMU valve (CR 366206), however, the CW vault has been known to flood in the past with no water leaking through electrical conduit. There are 2 double manholes between the RW building and the CWPH, E-MH-E1 and E-MH-E4. These were inspected for water and results documented in CR 393506. FSAR appendix A.2.1.32 states that "Significant moisture is defined as periodic exposures that last more than a few days (e.g., cable in standing water). Periodic exposures that last less than a few days are not significant. The manholes will need to be drained however to prevent significant moisture for the cables being in standing water (see email in EDMS) <I> **** Actions Taken **** Notified EOC and SM | 02-00-P-BLDG-MISC,02-00-W-BLDG-MISC
393518 | CR | 20190516 |  | 4 | TSW Leakage Past TO-HX-1A Isolations | N | N |  | N | YES | <D> **** Detailed Description **** While hanging O-TO-HX-1A/R24-001, WO 02111477, equipment operators reported excessive flow through TO-HX-1A vent valves TSW-V-22A and 19A. This was noted after time was given to allow residual TSW pressure to be released. Double valve isolation is being provided on the TSW side of the HX via TSW-V-17A, 18A, 20B, 21, and 304. Recommend evaluating for additional isolations that would provide adequate conditions for the TO-HX-1A inspections. <I> **** Actions Taken **** TSW-V-19A and 22A closed to stop water. Notification of ops production center and documented in CR. | 02-00-TSW-V-17A,02-00-TSW-V-18A,02-00-TSW-V-20B,02-00-TSW-V-21,02-00-TSW-V-304