393519 | CR | 20190516 |  | 3 | CO-60 found in Turbine Buillding Demin Water |  |  |  | N | NO | <D> **** Detailed Description **** Chemistry took weekly Demineralize water sample from TG 441' sample point. Results of isotopic showed 3.86e-7 uCi of CO-60, CO-58, & MN-54. <I> **** Actions Taken **** Resampled TG Demin water and analyzed it on a differrent detector and it still showed contamination of 1.74 uCi. Contacted Production Center to flush TG Demin water. Who informed me to write Cr & WR since OPs does not have procedure to flush TG Demin Water. Informed them not to use Demin water until it ican be Free Released. Contacted Chemistry Supervisor who in turn contacted OCC and informed them to tag out Demin Outlets that are being used. Chemistry is now going out to sample Demin Water sample points in the Reactor Building and Radwaste Building and sampling TG from a different sample point... <N> **** Equipment Description **** DW-V-132 Tg 441' Chemistry has completed sampling demin water sample points in the Reactor Building and Radwaste Building. Results from sampling show that these sample points are clean. HP was contacted to decontaminate the TG 441 sample point. Chemistry will resample after decontamination. HP went to decontaminate the sink and couldn't find any contamination. Chemistry resampled and analysis no longer found the presence of contamination. No further action required.
393520 | CR | 20190516 |  | 4 | TSW-RV-117E is Stuck Open. | N | N |  | N | YES | <D> **** Detailed Description **** TSW-RV-117E, (located on Cond-P-2C), has failed and is stuck open. This needs to be fixed before we can get to 100% Power. | 02-00-TSW-RV-117E
393521 | CR | 20190516 |  | 3 | CVI ISO 317-00,4708,1 (CIA-4116-1) | Y | N |  | N | NO | <D> **** Detailed Description **** Drawing CVI ISO 317-00,4708,1 calls out a 600# class globe valve for CIA-V-762, however Asset Suite shows that the valve is a 1500# class globe valve (CID 0054314092). Drawing 317-00,4708,1 was updated by BDC 88-0261-0A pages A23 and A24 which calls out a 600# class globe valve for CIA-V-762. However FCR 88-0261-0-01 authorizes the use of 1500# class globe valves in lieu of the 600# class valves. Recommend revising CVI ISO 317-00,4708,1 to show that CIA -V-762 is a Â½â€ 1500# globe valve per FCR 88-0261-0-01. Also an extent of condition should be performed to determine if other valves associated with BDC 88-0261-0A are impacted. This is a documentation issue only and does not impact any SSCs at Columbia Generating Station. <I> **** Actions Taken **** Notified my Supervisor and wrote this CR
393522 | CR | 20190516 |  | 3 | R24LL: Procedure enhancement for TSP-CIA/X56-C801 |  |  |  | N | NO | <D> **** Detailed Description **** TSP-CIA/X56-C801 steps 7.1.5 and 7.1.6 cannot work as written if the CIA system pressure has not been bled off. please add steps to remove spv fuses for CIA-V-39A and 39B. <I> **** Actions Taken **** Wrote CR
393523 | CR | 20190516 |  | 4 | WOA-FL-1A cannot be advanced | N | N |  | N | YES | <D> **** Detailed Description **** WOA-FL-1A has new filters, but they cannot be advanced to clean sections due to the end of roll alarm remaining in (see CR 392111, 4-12-19). Please repair. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 487 | 02-00-WOA-FL-1A
393524 | CR | 20190516 |  | 4 | BRE 21A door needs maintenance |  |  |  | N | YES | <D> **** Detailed Description **** The upper locking latch and trim plate on the door for BRE 21A needs maintenance. It appears the upper locking latch needs to be profiled. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Security notification made, CR/WR generated <N> **** Equipment Description **** BRE 21A at the security checkpoint
393525 | CR | 20190516 |  | 4 | R24LL - MSIV Scaffolding Requirements |  |  |  | N | NO | <D> **** Detailed Description **** During the installation of rigging for MS-V-28B, it was identified that the scaffolding requirements for the MSIVs has changed to include fall protection. This was not anticipated as this has not been part of past outage requirements. <I> **** Actions Taken **** Modified scaffolding to include a handrail rather than requiring fall protection. Generated CR. Need to include this into our LL going forward to ensure the scaffolding plan is accurate for future MSIVs.
393526 | CR | 20190516 |  | 3 | PPE Non-compliance Issue With ISPM-16 & Potential FME Conern |  |  |  | N | NO | <D> It was identified that some of the Fastenal PPE vending machines are intermittently dispensing the Moldex rocket -style ear plugs (purple plastic containers) without the required attached lanyards. It is unknown whether this is a manufacturer, supplier or vendor issue; however, this is non-conformance issue and not in accordance with ISPM-16 Personal Protective Equipment 3.5.9 a, which states, â€œThe ear plug type hearing protection provided at Columbia Generating Station (CGS) MUST HAVE ATTACHED lanyards to prevent the ear plugs from becoming foreign material and risking damage to equipment. <I> Initiated CR for tracking and trending to document a procedural non-compliance issue with potential negative impact. Advise the organizational department responsible for the Fastenal contract to communicate the issue to the vendor. Recommend an inspection of all Fastenal vending machines on-site to identify and remove similar non -compliant items. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
393527 | CR | 20190516 |  | 4 | R24LL - MSRV Coordination w Fuel Moves |  |  |  | N | NO | <D> **** Detailed Description **** Some MSRV scope has been impacted by the radiological controls in place during fuel moves. Need to determine whether this schedule logic was known during schedule development. Some MSRVs are able to be worked due to their locations while some are not. <I> **** Actions Taken **** Generated LL CR. Need incorporate LLs into future schedules to prevent this conflict.
393528 | CR | 20190516 |  | 4 | RFW-P-1B Oil Saturated Insulation | N | N |  | N | YES | <D> **** Detailed Description **** While performing a shiftly Fire Marshal walk-down for combustible material, RFW-P-2B was found to have several sections of insulation that are totally saturated with combustible oil. Numerous OE exists where oil saturated equipment and/or rags have caught fire. Recommend replacing sections of the insulation that are oil-soaked before returning RFW-P-2B to service. . This was also identified in R23 and the RFW-P-2A insulation was replaced as a precaution in R23. The RFW-P-2A insulation did not display signs of oil soaked insulation from my observations. . Station should be cautious around the oil soaked insulation while performing any hot work in the RFW-P-2B room or remove oil soaked insulation from the RFW-P-2B room. . Review of OPEN Plant Ignition Source (Hot Work) Permits did not identify any permits actively being used for hot work. The insulation is not an immediate fire concern. Recommend removing the oil soaked insulation from the plant. <I> **** Actions Taken **** Verified no hot work activities in immediate vicinity during walkdown, verified no open hot work permits as of the initiation of this CR. Verified insualtion is in a relatively safe location for the time being. <N> **** Equipment Description **** T -447- - -F4/10.5- | 02-00-RFW-P-1B
393531 | CR | 20190516 | CAQ | D | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0064688 Sierra Flowmeter- mdoel 830H-4-OVI-D-V1-HT found OOT & adjusted within specs. EFIN EVAL: A device parameter was accidently changed. With this configuration, the values read would have been significantly off. The user would have identified the issue. When corrected, the device was within Calibration limits. No Plant Impact. DEF #7023A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
393532 | CR | 20190516 |  | 3 | R24LL: Procedure enhancement for TSP-RCS-R802 |  |  |  | N | NO | <D> **** Detailed Description **** TSP-RCS-R802 section 7.9.3.w1) should be valve 15 and w3) should be valve 17. . Step 7.9.2.q.1) should be valve 17 and q.3) should be valve 15 <I> **** Actions Taken **** Wrote CR
393533 | CR | 20190516 |  | 4 | HD-V-5A33 stuck or clogged | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WO#02027022-06, HD-V-5A33 (lower drain valve for HD-LS-22A) was not allowing water to pass through it. The valve appears to be full open, but was not letting water flow into the instrument tree. Unsure at this time whether there is crud at the bottom of the drain leg or the valve itself is broken and stuck. <I> **** Actions Taken **** Informed supervisor and wrote this CR. | 02-00-HD-LS-22A,02-00-HD-V-5A33
393534 | CR | 20190516 |  | 3 | broken door latch on MUD trailer | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** On 5/16@0040, chemistry technician opened door to MUD trailer to take routine log. Upon disengaging the latch to the entry door, the entire latching mechanism, including the vertical arm, fell away from the door, strking the plastic housing of the lamp adjacent to the door. The lamp housing shattered, and the latching arm fell to the ground. The door is not currently able to be secured. <I> **** Actions Taken **** The technician collected the visible pieces of the lamp housing and placed them next to the door, and stowed the latching arm next to the door as well, to be dealt with in daylight. The technician pushed the door closed but was unable to secure it due to lack of a functioning door latch. The technician informed chemistry supervision and MCR. <N> **** Equipment Description **** MUD TRAILER DOOR
393535 | CR | 20190516 |  | 4 | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0064982 Fluke True RMS Multimeter- model 287 was returned damaged to Tool Crib and was Not used during Calibration cycle. Rejected- Rotary Switch knob broken. DEF #7033A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
393537 | CR | 20190516 |  | 4 | HV-V-31G - walkdown identified degradation | N | N |  | N | YES | <D> **** Detailed Description **** Walkdown of HV-V-31G identified the steam leak coming from the pressure seal instead of the packing. R24 scope is to replace the packing and perform an external PM (Lubricate stem and inspect actuator grease). Based on the steam leak the actuator needs refurbed/replaced and the pressure seal replaced. See attached pictures in EDMS. <N> The valve was unsuccessfully electrically backseated on-line | 02-00-HV-MO-31G,02-00-HV-V-31G
393538 | CR | 20190516 |  | 4 | HV-V-30H - walkdown identified degradation due to steam leak | N | N |  | N | YES | <D> **** Detailed Description **** Walkdown of HV-V-30H identified the steam leak coming from the pressure seal instead of the packing. R24 scope is to replace the packing and perform an external PM (Lubricate stem and inspect actuator grease). Based on the steam leak the actuator needs refurbed/replaced and the pressure seal replaced. See attached pictures in EDMS. <I> **** Actions Taken **** Valve was electrically backseated. | 02-00-HV-MO-30H,02-00-HV-V-30H
393539 | CR | 20190516 |  | 4 | R24 lessons learned - E shop outage staffing | N | N |  | N | NO | <D> **** Detailed Description **** Documentation of R24 lessons learned. Supervisor staffing of 4 with a lead on each shift does not adequately manage 4 full time crews due to fatigue rule required time off. On 5 of the seven days one of the supervisors has a day off resulting in one of the other supervisors managing two crews. This reduces productivity and oversight in the field. Recommend one additional supervisor on each shift. A discipline specific outage coordinator could fill one of those 2 gaps. <I> **** Actions Taken **** Documented lessons learned
393540 | CR | 20190516 |  | 4 | WO 02129294 HV-MO-30D did not contain a PMT task | N | N |  | N | NO | <D> **** Detailed Description **** WO 02129294 HV-MO-30D did not contain a PMT task as required by PPM 10.25.74 Attachment 9.4. **Recommend trendning CR. <I> **** Actions Taken **** Contacted planning supervision.
393541 | CR | 20190516 | CAQ | C | Personnel did not accurately provide historical dose | N | N |  | N | NO | <D> **** Detailed Description **** Personnel in-processing with the Rx Maint. group did not provide accurate dose assessment for the current year while in-processing. Individuals updated, reviewed, and signed current year dose on form 848 and did not include non -domestic dose. This dose was a significant amount of their annual radiological dose and by not properly updating challenged the sites administrative dose goals. The condition was identified when dose extensions were requested. <I> **** Actions Taken **** . Dose extensions for Rx Maint. Individuals have been placed on administrative hold/restrictions until the dose has been confirmed. In-processing briefing for 848 form is including an emphasis on Non-domestic dose as well. 2 individuals RCA access has been restricted until the annual dose has been confirmed. RP management has been notified. <N> Issue is related to individual's failure to report historical dose. Neither vendor nor ENW has access to this information. See EDMS for full response. No further actions to be taken by RxMaint.
393542 | CR | 20190516 |  | 4 | R24 lessons learned - E shop support tasks for main turbine | N | N |  | N | NO | <D> **** Detailed Description **** Document lessons learned. Electrical support for main turbine disassembly/reassembly was not factored into the outage schedule. Support tasks and resource allocation was not identified and incorporated into the schedule and wound up being emergent support causing delays to already scheduled Electric shop work to prevent delays to Siemens work. <I> **** Actions Taken **** Documented lessons learned
393543 | CR | 20190516 |  | 4 | TDAS X067 does not match with RWCU-TI-607 PT 5 | N | N |  | N | YES | <D> **** Detailed Description **** TDAS X067 does not match with RWCU-TI-607 PT 5. It indicates 8 F lower than RWCU-TI-607 PT 5. Need to investigate and resolve the issue. OPS use those indications to control RPV temperature during alternate FPC assist. <I> **** Actions Taken **** CRS/SM informed | 02-00-RWCU-TI-607
393546 | CR | 20190516 |  | 3 | Damaged Grating | N | N |  | N | NO | <D> **** Detailed Description **** Damaged Grating @ East Side Alpha Water Box NE Corner 441â€™ TG Grating has become degraded and in need of repair due to years of Cart traffic from Scaffold Storage Area. Grating is cracked and/or broken and presents with a 1â€-2â€ depression at connection to adjacent Concrete flooring creating an abrupt stopping point during Material Handling evolutions. Grating appears to be damaged beyond repair. Recommended replacement to provide level transition from Grating to Concrete <I> **** Actions Taken **** WPS Superintendent notified <N> Closed to WR in cross reference. No futher actions required.
393547 | CR | 20190516 |  | 4 | HD-LCV-3B1 As Found packing friction too low | N | N |  | N | YES | <D> **** Detailed Description **** During as found diagnostic testing under WO 02112230 packing friction was found at 32 lbf with no adjustment remaining. This will leak next run cycle if left unattended. Valve needs to be repacked. <I> **** Actions Taken **** Wrote OSCR. Informed Valve team | 02-00-HD-LCV-3B1
393548 | CR | 20190516 |  | 4 | Minor First-Aid | N | N |  | N | NO | <D> **** Detailed Description **** An employee while cutting a pipe inside the 471'TG Heater Bay received a minor burn to his left forearm. Employee had all the required PPE (FR clothing included), while performing this activity. Employee notified Safety and first-aid was self-administered. Employee has since returned back to work with no issues. This is a minor first-aid. <I> **** Actions Taken **** WPS Safety followed ISPM-1 procedure requirements while notifying Occupational Health, ENW Industrial Safety and Site Support Contractor Manager regarding the details of this Minor First-Aid. Not further action is required.
393550 | CR | 20190516 |  | 4 | HV-V-27H will not cycle after repack | N | N |  | N | YES | <D> **** Detailed Description **** After replacing valve 27H, WO# 02085907-01, the valve would not cycle. The packing was removed and the valve still would not cycle. <I> **** Actions Taken **** Contacted valve engineer. He looked at it and suggested to either, take it apart and investigate, or to cut out old valve and replace with a new one. <N> **** Equipment Description **** Turbine Bld. 506 , D3/12.5
393551 | CR | 20190516 | CAQ | D | Bad lock/handle on E-CP-DG/REP1 | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of SOP-DG1-STBY the back panel door of E-CP-DG/REP1 was very difficult to unlock and the handle was difficult to operate once unlocked. Once switches inside were verified the door was reshut, but was unable to be relocked. Recomend replacing handle and/or lock. <I> **** Actions Taken **** Initiated this CR, left door unlocked. | 02-00-E-CP-DG/REP1
393552 | CR | 20190516 |  | 3 | Broken studs and stuck nuts during LPC T-piece disassembly | N | N |  | N | YES | <D> **** Detailed Description **** During unbolting of the T-piece above Low Pressure Turbine â€œCâ€ (MS-DT-1C) there were several studs and nuts that broke, the nut stuck to the stud, or the studs were stuck and had to be cut off in order to allow separation of the components. Seven studs were broke or cut on the right side were MS-V -163C connects with the crossover piping. Thirteen studs broke and another thirteen had a nut stuck to the stud (twenty-six studs total) on the LPC crossover adapter flange where the T-piece connects to the top of LPC. The remaining stud remnants need to be drilled out while preserving the hole threads to the extent possible. Once removed, the internal threads of the hole are to be inspected and re-tapped. If the thread condition is unsatisfactory, install helicoil in accordance with PPI PPM 10.2.252. [See EDMS for documentation of the OEM repair plan.] <I> **** Actions Taken **** Received recommended repair plan from the OEM <N> **** Equipment Description **** T-piece/crossover piping above LPC work instructions have been updated. | 02-00-MS-DT-1C,02-00-MS-V-163C
393553 | CR | 20190516 |  | 4 | Security Checkpoint Vehicle Accident |  |  |  | N | NO | <D> **** Detailed Description **** A delivery driver with a semi-truck struck part of the vehicle serpentine barrier. <I> **** Actions Taken **** Facilities contacted and barrier blocks were put back in place. Driver sent to FFD. Security Managment, OCC, Resident NRC and Shift Manager notified.
393556 | CR | 20190516 | CAQ | B | Loss of power to RHR-V-53A during open stroke. | Y | N |  | N | YES | <C> CR Bring back for additional information - LIC, MNT, & ENG. RISK: Medium. CAUSE: Uncertain. Severity B, Investigation Template Required <D> **** Detailed Description **** Loss of power to RHR-V-53A during open stroke for SOP-RHR -FILL section 5.4.41.c. Light indication immediately cleared when taking switch to the open position. Verified Light buld good. Reset the thermal overloads. Sent operator to look at RHR-V-53A locally. Operator reports that valve is full closed locally. Request that fuses be inspected and replaced <I> **** Actions Taken **** See description. Informed supervision <N> This is the 5th time in the last 5 years that wires have been rolled (motor/valve goes the wrong direction) without bumping for rotation. This can and has damaged equipment at ENW and should be considered a personal safety concern. If the valve goes the wrong direction, the only controls are fuses / TOL's. The weak links can easily be compromised. Ref CR's 300941 (DEH-42-2C2C), 366026 (RCIC-V-22), 366029 (RHR-V-8) , 391986 (RHR-V-73A), 317158 (bump for rotation) . RHR-V-53 is the RHR loop A Shutdown Cooling return valve. It cannot be opened with RPV pressure > 153 psi. The valve was in its' required position at all times and Pressure Integrity was maintained at all times for ATWS. * The pressure integrity can be compromised and can cause significant valve/actuator degradation. In this case, we were lucky. <R> REP/REGE assignments cancelled with Licensing Supervisor concurrence. | 02-00-RHR-42-7BA5B,02-00-RHR-MO-53A,02-00-RHR-V-53A
393557 | CR | 20190516 |  | 4 | Man Down |  |  |  | N | NO | <D> **** Detailed Description **** control room received notification of a man down at 11:10am
393558 | CR | 20190516 |  | 2 | RMC Laborer â€“ Personal Injury |  |  |  | N | NO | <D> **** Detailed Description **** At approximately 1200 on 5/15, a RMC Laborer struck a scaffold pole, documented in CR 00393496. The individual was evaluated by Occ Health and released same day. At 0521 on 5/16 the individual reported difficulty while driving to work. The individual was escorted to Occ Health where it was determined that outside care was needed. Supervisor escorted the individual to a local hospital for further evaluation. Contact RMC Laborer office for additional details, x2142 or x2338. <I> **** Actions Taken **** Individual was evaluated by hospital staff and released. OI-34 completed for event related to restricted duty or lost time accidents. <N> Completed Form 26890, HU Performance Review Worksheet has been uploaded into EDMS. No further action required.
393559 | CR | 20190516 |  | 3 | (Non EN/CGS) Calibration Reports and stickers incorrect |  |  |  | N | NO | <D> **** Detailed Description **** (Non EN/CGS) Calibration Reports and stickers had incorrect re-call date Asset# BNI-PB-003 & BNI-PB-004 (non-CGS Customer). Recommend assign to AR-CALSERV group for completion. <I> **** Actions Taken **** Requested technician to review in Metcal database to see if we can determine why the re-call date is not correctly populating as this is a automatic process once the calibration is performed. Corrected copies and new stickers will be issued to the customer.
393560 | CR | 20190516 |  | 4 | Personal Medical Condition â€“ Transport Off-Site |  |  |  | N | NO | <D> **** Detailed Description **** n Thursday, May 16, 2019 an Energy Northwest contractor employee experienced a personal medical condition at the Turbine Building 501 office area. A 2222 call was placed at 11:10 a.m. A medical responder tone out was initiated by the control room per PPM 1.9.14. The patient was evaluated by the medical responders. A Registered Nurse arrived and further evaluated the patient. Hanford Fire Department (HFD) Medic 1923 and Ladder 1923 arrived at 11:20 A.M. The patient was further evaluated by HFD and transported to Kadlec Medical Center at 11:55 A.M. <I> **** Actions Taken **** The employee is from organization 52238. An acting supervisor left site to meet the patient at Kadlec Medical Center. Radiation Protection provided an EN employee rider for Medic 1923 in order to assist HFD.
393561 | CR | 20190516 |  | 4 | TG 471 Heater Bay Poor Lighting | N | N |  | N | NO | <D> **** Detailed Description **** Due the walk down of TG 471 following the personal injury, documented in CRs 00393496 and 00393558, it was observed that between several LP heaters the lighting is inadequate. The areas with poor lighting are between heaters 2A-5A, 5A-2B, and 2B-5B. <I> Non-essential lighting. <N> Needs WR?
393562 | CR | 20190516 | CAQ | D | MSP-MS/IST-R701 failed to close | Y | N |  | N | YES | <D> **** Detailed Description **** Working 02111582-01 MSP-MS/IST-R701 did not close properly MS-V-37D, and MS-V-38G failed to close properly <I> **** Actions Taken **** Lubricated , and cycled per step 7.2.2.a still not seat properly . contacted supervisor | 02-00-MS-V-37D,02-00-MS-V-38G
393564 | CR | 20190516 |  | 4 | CIA-TK-1A light lit on CIA-CP-1 | Y | N |  | N | YES | <D> **** Detailed Description **** On OPS-2 rounds, CIA-TK-1A light was found lit on CIA-CP-1. The solenoid pilot valve for CIA-TK-1A, CIA-SPV-1A was found to be cool to the touch, indicating it was de -energized. CIA-TK-1A bottle pressure was 2450 psig and steady. The MCR was notified. CIA timers were removed from service per SOP-CIA-OPS section 5.5. <I> **** Actions Taken **** Notified MCR | 02-00-CIA-CP-1
393565 | CR | 20190516 |  | 3 | DAMAGED INSULATION MS-HX-1A, 1B | N | N |  | N | YES | <D> **** Detailed Description **** DURING MAINTENACE ACTIVIES IT WAS IDENTIFIED THAT INSULATION BLANKETS AROUND THE MOISTURE SEPERATOR MANWAYS ARE HEAVILY DAMAGED FROM STEAM LEAKS AND ROUTINE OUTAGE ACCESS. RECOMMEND ADDING WORK TASK TO R-25 SCOPE TO REPLACE INSULATION AROUND MANWAYS. SEE PICTURES IN EDMS <I> **** Actions Taken **** NOTIFIED SUPERVISION, TOOK PICTURES, INITIATED CR Need WRs initiated. <N> **** Equipment Description **** MOISTURE SEPARATOR 1A MOISTURE SEPARATOR 1B MS-HX-1A and MS-HX-1B - EPNs xRef'd Work request generated. CR closed to work management process.
393566 | CR | 20190516 | CAQ | C | RHR-HX-1A coating requires removal for ASME XI examination |  |  |  | N | YES | <D> **** Detailed Description **** During MT surface examination of the RHR-HX-1A supports (AS-1) under work order 02116546, the examiners found evidence of coating on the area to be examined. Per SPS -4-3, Step 3.6.4 â€œAll coatings in the area of the examination are required to be removed prior to examination.â€ . This location was last inspected in 2009 with a task to clean the weld. The task was closed at that time with the comment â€œNot requiredâ€. It is believed that the coating was not detectable at that time but through time and aging has become more apparent and contrasting to the metal. Examiners noted that the coating was not readily apparent on two of the four supports but when detected on the third support they stopped due to unexpected conditions. <I> **** Actions Taken **** Reviewed SPS-4-3 and verified that the requirement to remove coatings existed in both the procedure and the revision in place in 2009. Initiated an OSCR to remove the coating from AS-1 see Cross References. Recommend assignment to AR-CPROG to evaluate extent of condition. | 02-00-RHR-HX-1A
393567 | CR | 20190516 |  | 4 | R24 Outage Safety blitz walkdown discrepencies | N | N |  | N | NO | <D> **** Detailed Description **** There were 2 instances of appliances plugged into power strips identified during a walkdown of all temporary outage trailers inside the protected area. One was a microwave and the other was a coffee maker. <I> **** Actions Taken **** Coaching was provided to all personnel present regarding the requirements for plugging in these items. The issues were corrected on the spot.
393569 | CR | 20190516 |  | 4 | DOE Emergency Response fax not answering | N | Y |  | N | YES | <D> **** Detailed Description **** The DOE ONC Emergency response fax was found inoperable while doing monthly maintenance. <I> **** Actions Taken **** Contacted DOE ONC and learned they recently replaced their fax machines and they would resolve the issue on their end. Follow-up testing verified the problem has been resolved and the fax now works. Notified EP. NCAQ-D Close for trending <N> **** Equipment Description **** DOE EOC off site
393571 | CR | 20190516 |  | 3 | (QA) Inconsistent Use of Nomenclature in 5 PM WOT Instr's |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) A quality review of five Preventive Maintenance (PM) Work Order Task (WOT) instructions revealed the inconsistent use of nomenclature by the maintenance planners for steps requiring more than one worker's initials. Three of four PM WOT instructions for replacing identical solenoid pilot valves used "Peer Check"; however, the inconsistent fourth WOT used "Second Check", which is a nomenclature not defined within MI-1.22 "Maintenance Planning Program". The fifth PM WOT for replacing O-Rings on a trip manifold used "Second Verification", which is inconsistent with the MI-1.22 definition that it is used for important steps on critical equipment. This fifth WOT does not contain "critical equipment" based on MI-1.22A "Maintenance Planners Guide" pointing to Asset Suite D031 panel for Critical Equipment listed as Criticality "C". Inconsistent use of nomenclature in WOT instructions can lead to confusion, which could result in a loss of productivity while figuring out how to interpret the nomenclature. Requirements: (See Details in EDMS) â€¢ MI-1.22 rev 020 does not use, nor define, the nomenclature "Second Check". â€¢ The following three WOTs contain "Peer Check" for selected steps for cleanliness, parts installation, torque, and alignment: o WOT 02112562-01 "DEH-SV-TRIP/A, Quadvoter Solenoid Vlv Replacement" o WOT 02112564-01 "DEH-SV-TRIP/B, Quadvoter Solenoid Vlv Replacement" o WOT 02112565-01 "DEH-SV-TRIP/C, Quadvoter Solenoid Vlv Replacement" â€¢ The following one WOT contains "Second Check" for the same steps for cleanliness, parts installation, torque, and alignment: o WOT 02112563-01 "DEH-SV-TRIP/D, Quadvoter Solenoid Vlv Replacement" â€¢ D031 panel shows each Equipment Piece Number (EPN) listed in the four WOTs above as Criticality "N". Each of the four EPNs is a component of composite DEH-IR-TRIP, for which its D031 panel also shows Criticality "N". â€¢ The following one WOT contains "Second Verification" for selected steps for clean/inspect, verify parts, and installation: o WOT 02112390-01 "DEH OPC Trip Manifold O-Rings Replacement (Shell)" â€¢ This WOT just above does not contain an EPN with a Critical Equipment box on a D031 panel. This WOT uses Work Item DEHOPCTRIPMANIFOLD instead of any EPNs. â€¢ The acting Maintenance Services Manager agrees that the nomenclature for steps requiring more than one worker's initials should be consistent with MI-1.22 and should be consistently used by the maintenance planners in WOT instructions. <I> **** Actions Taken **** Contacted acting Maintenance Support Supervisor and acting Maintenance Services Manager. . Quality recommends this CR be routed to Maintenance Planning. . This is a Deficiency found during the Quality R-24 Outage Surveillance SR-19-01.
393573 | CR | 20190516 |  | 3 | 15.1.4 FP-110 operability procedure enhancement. |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** 15.1.4 step 7.26.6 gives conditions for depressing the stop push button, and one of the conditions is if any of the alarm resets are depressed. Since the battery reset is always depressed in step 7.26.3, ( ie not a conditional step), then the stop pushbutton must always be depressed. This implies that step 7.26.6 should read " Depress the stop pushbutton" or step 7.26.3 should be evaluated as to whether it is necessary. <I> **** Actions Taken **** Notified supervisor and initiated this AR.
393574 | CR | 20190516 |  | 3 | SO-RV-258- WO planned without addressing Limitation on use |  |  |  | N | NO | <D> **** Detailed Description **** While replacing the relief valve it was noted that there was a Limitation on Use requiring an EC or RIE to be APPROVED prior to installing CID 31128. The Work Order task did not mention the LOU nor did it reference any EC or RIE. After posing this question to Engineering it was determined that an EC/RIE would not be required and that the LOU should be removed from the CID. LOU was removed from the CID allowing for valve installation with out an EC or RIE. Planning did not address this issue during the planning process pre-outage. <I> **** Actions Taken **** Notified EOC / OCC.
393575 | CR | 20190516 |  | 4 | Unable to calibrate HD-LT-7A | N | N |  | N | YES | <D> **** Detailed Description **** While performing calibration on HD-LT-7A WO# 02118050-01 found it to be out of tolerance. We were unable to get the needed span out of the transmitter. Span is short by 1 pound <I> **** Actions Taken **** Replaced pilot relay and flapper/nozzle. Were able to get closer to the tolerance for the calibration but still out of spec. Notified supervision and wrote this CR. Recommendation is to replace the leveltrol anddisplacer. | 02-00-HD-LT-7A
393577 | CR | 20190516 |  | 3 | Take 2 Card improvement recommendation |  |  |  | N | NO | <D> **** Detailed Description **** The Take 2 card should add the question- Do I need to be on a Clerance Order for this work? Especially during outage many non-craft type personal are in the plant and in areas which may need protection from a clearance. This is a good reminder for everyone to check that they are on the clearance for the work. <N> See assignment 01. This recommendation was determined to not add value as the question recommended is already included on the card and within a task preview. Changing the card would incur additional unnessary expense.
393578 | CR | 20190516 | CAQ | D | Temporary blowdown recorder not indicating. | N | Y |  | N | YES | <D> **** Detailed Description **** Temporary B/D recorder at the CWPH is not indicating flow. The screen is blank and does not respond to button manipulation to take it out of sleep mode. The attached power supply is on. Please T/S and repair as necessary. <I> **** Actions Taken **** Notified CRS/MCR. <N> **** Equipment Description **** CWPH
393579 | CR | 20190516 |  | 4 | Safety - Oily residue spill in HVAC room |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** 2nd floor Yakima, Door S233 to HVAC room, inside door is good size spill of oily residue. Frequent traffic in this room shiftly makes this a latent hazard. <I> **** Actions Taken **** Contacted Facilities Informed co-workers Wrote CR
393580 | CR | 20190516 | CAQ | D | NSSE-eq-8 intermittent slack cable indication | Y | Y |  | N | YES | <D> **** Detailed Description **** An intermittent "Slack Cable" signal is occuring on the refuel bridge. <I> **** Actions Taken **** Stopped refuel bridge operation. Informed OCC. Initiated work order task 01157435 13. <N> **** Equipment Description **** Reactor Building 606 | 02-00-NSSE-EQ-8
393581 | CR | 20190516 |  | 4 | Broken stud on MS-HX-1A WEST END LP CHANNEL HEAD | N | N |  | N | NO | <D> **** Detailed Description **** Working on WO 02111978-02 MS-HX-1A one of the studs broke off. <I> **** Actions Taken **** Contacted engineer, PM and the OCC. *Contact engineer for further details*
393582 | CR | 20190516 | CAQ | C | (QA) Deficiencies in approved WOs affecting QC/PV inspection |  |  |  | Y | NO | <D> **** Detailed Description **** D-10: Deficiencies in approved work orders affecting QC/PV inspections. Related Objective: Objective 7 Problem Statement: Several deficiencies affecting Quality Control (QC) and Peer Verification (PV) Inspections have been identified in approved and/or ready to perform work orders for the R24 outage and on-line work over the last year. Incomplete quality planning results in additional time for walkdowns & job preparation to revise the plans and can lead to errors in implementation that could lead to missing required inspections. As a part of the 2019 Pre -NIEP focused self-assessment, a review of condition reports and QA observations identified that there have been several deficiencies related to work order (WO) planning of tasks requiring QC or PV inspections over the last year. <I> **** Actions Taken **** Notified Quality and Maintenance Management, this issue was identified during 2019 Pre-NIEP SA 376427. Recommend assignment to Maintenance. <N> Assignment 01 was extended multiple times by the Maintenance Services Manager due to not having an permanent planning supervisor. There was no risk to these extentions.
393584 | CR | 20190516 | CAQ | D | Flooding in MH-ES-7 | N | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02144397 and mark completion required box, then taken back to complete <D> **** Detailed Description **** Recent water intrusion from the CW system has left several feet of water in MH-ES-7. The water in the MH is warm/hot which is unexpected. <I> **** Actions Taken **** Security/OCC notified. <N> **** Equipment Description **** MH-ES-7 manhole . The cause of the manhole flooding is due to leakage from TMU. Flooding of manholes is an expected condition and is analyzed. Flooded manholes should be dewatered in a timely manner.
393585 | CR | 20190516 |  | 4 | First Aid |  |  |  | N | NO | <D> **** Detailed Description **** While working in the TG 441â€™ East Condenser Bay at approx .1710 a worker was struck by another worker in the Left Thumb with a Wrench. When the Wrench was removed from a cabinet after completing a task the gravity of the movement brought the Wrench into contact with a worker standing adjacent to the activity <I> **** Actions Taken **** Worker notified their Foreman, Supervisor and WPS Safety. Worker was evaluated and received Ice and Ibuprofen and will report to Safety tomorrow prior to beginning work tomorrow. All WPS and EN notifications were made
393587 | CR | 20190516 |  | 3 | R24LL: Verify breaker OTS are reset | N | N |  | N | NO | <D> **** Detailed Description **** While restoring E-SH-6 related switchgear, E-MC-6C had to be taken out of service a second time so that E-CB-63/6C could be racked out to investigate why the overcurrent trip switch would not reset. This rework could have been avoided by verifying the state of the OTS devices after racking in the breaker but prior to closing it in. For example, revising step 5.21.8 of SOP-ELEC-480V-OPS to rack in the breakers, verify the applicable OTS points are reset, then close the desired breakers would have identified that the 63/6C OTS had not reset and electrical maintenance could have investigated the problem prior to MC-6C being energized.
393589 | CR | 20190516 |  | 3 | R-24 lessons learned TG471 heater bay |  |  |  | N | NO | <D> **** Detailed Description **** On 5/16/19 at approximately 19:00 to 22:00 the west side of turbine 471 was closed for a breaker racking evolution. This was not on the schedule and impacted many groups trying to enter the heater bay for scheduled work. HP had to change the entry point to the south hallway which is not built for that amount of people, it only has one entry in and out. This entry point is not known to all of the visiting craft and impacted multiple jobs. This is a repeat issue. <I> **** Actions Taken **** Notified the OCC and my manager intiated this CR. Recommend making the entry point from the south hallway large enough to accommodate the mass of people entering and exiting the heater bay and have laundry and trash big enough to accommodate the work. Also with the breaker racking announcement, notify people to enter through the south hallway and have RP available to switch entry points. . <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
393590 | CR | 20190516 |  | 3 | (QA) WOT Missing LOU in P&L |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Work Order Task (WOT) 02111975-24 did not contain Limitation on Use (LOU) to perform a VT-1 examination per SPS-7-1 in the Precaution and Limitations as required by MI-1.22, Maintenance Planners Guide. The 02111975-24 Work Package did contain completed VT-1 inspection sheets, meeting the requirements of G-101, Quality Control Inspection Plan, therefore this is not a failed inspection but an administrative planning issue. See EDMS for full details. <I> **** Actions Taken **** This issue was identified during QC parts verification. Issue was discussed with Reactor Maintenance Supervision, recommend assignment to Reactor Maintenance/Planning.
393591 | CR | 20190516 | CAQ | D | EOF & APEL water and sediment above accepted criteria | N | Y |  | N | NO | <D> **** Detailed Description **** Lab analyses on fuel from EOF & APEL non-emergency diesel tanks showed both tanks had fuel that contained water & sediment that is slightly above the accept criteria. <I> **** Actions Taken **** Informed chemistry supervision and wrote a CR. <N> **** Equipment Description **** EOF and APEL non-safety related fuel oil tanks.
393592 | CR | 20190517 |  | 3 | As Found Time COND-RLY-TK1/AOP1C |  |  |  | N | YES | <D> **** Detailed Description **** As Found Time COND-RLY-TK1/AOP1C was out of tolerance range. As-Found time was 199.5 seconds Tolerance range is 171 - 189 seconds. <I> **** Actions Taken **** Adjusted relay per PPM. As Left time is 178.46 seconds Notified supervisor & OP's Engineer should evaluate the tolerance range for this model relay. Manufacture time for non class one ( 1E ) relays is 10% & ot the 5% SUGGEST HAVEING DATA SHEET TOLERANCE RANGE CHANGED IF POSSIBLE <N> **** Equipment Description **** E-MC-3C COMP 2B | 02-00-COND-RLY-TK1/AOP1C
393593 | CR | 20190517 |  | 4 | Imformational: CST SiO2 Greater Than Limit For Mode 1 |  |  |  | N | NO | <D> **** Detailed Description **** CST SiO2 is 36 ppb on both initial and resample. Per SWP -CHE-02, Table 6.5.8 the SiO2 limit for the CSTs is <10 ppb for mode 1 operation. Per notes: recycle of water containing greater than 100 ppb is normal and may result in temporarily exceeding the Normal Mode 1 Range for short periods after plant outages. <I> **** Actions Taken **** Inromational CR written. MCR/CRS/SM and chemistry supervision informed.
393594 | CR | 20190517 |  | 4 | E-CB-31/3D would not rack out to the remove position |  |  |  | N | YES | <D> **** Detailed Description **** While racking out circuit breaker, E-CB-31/3D, per WO 02111298-07 it would not go to the remove position to allow the breaker to be pulled out of the cubicle for bus cleaning. <I> **** Actions Taken **** Wrote CR and informed CRS | 02-00-E-CB-31/3D
393595 | CR | 20190517 |  | 4 | HD-LCV-3C1 Valve Packing |  |  |  | N | YES | <D> **** Detailed Description **** During performance of as found diagnostic testing on HD -LCV-3C1 via work order 02112232 it was discovered that the valve packing friction is extremely low and there is indication of an active packing leak. There is no adjustment left on the packing follwer to increase friction. This valve should be repacked in R-24 to eliminate the risk of packing failure. <I> **** Actions Taken **** Contacted valve testing supervisor, AOV program Owner. <N> **** Equipment Description **** Turb. HTR. Bay 488 F8/12.4 | 02-00-HD-LCV-3C1
393597 | CR | 20190517 |  | 4 | (R24 LL) CW Basin Level Went LT 438 FT | N | Y |  | N | YES | <D> **** Detailed Description **** TMU system was shutdown to lower CW basin level faster due to gross leakage past TMU-V-23. Set a key parameter of CW basin level of 440 ft to restart TMU to maintain CW basin level at 439 ft for water box inspections. TMU pumps could not be restarted due to TMU-FIS-5A/B/C not working (all pumps tried). CW basin level quickly lowered to 438 ft, dispatched an additional operator to shutdown the temporary blowdown pumps. Restarted TMU-P-1C by jumpering the flow switch to raise CW basin level. CW basin level was LT 438 ft from 2129 on 5/16/19 to 0009 on 5/17/19. <I> **** Actions Taken **** restarted TMU-P-1C after jumpering the flow switch. | 02-00-TMU-FIS-5A,02-00-TMU-FIS-5B,02-00-TMU-FIS-5C,02-00-TMU-V-23
393598 | CR | 20190517 |  | 4 | Cut to finger |  |  |  | N | NO | <D> **** Detailed Description **** While preparing to grease the HP slide supports, employee was changing out a grease tube when grease spilled from the end of the tube onto his glove. Employee removed glove and reached to remove tube to prevent grease from continuing to spill. Finger was cut on the inside of the damaged grease tube. <I> **** Actions Taken **** Work was stopped, radiation protection was contacted, and employee was escorted out of the RCA. Worker's employer called their work care and employee was advised to clean finger and apply a band aid. Importance of stopping when faced with adverse conditions and PPE usage was discussed with the crew. Notified Supervision, Turbine Project Supervision, Safety, and OCC. Employee consulted employers EN Safety and OCC <N> **** Equipment Description **** Turbine Deck 501
393599 | CR | 20190517 |  | 4 | R24 temporary IPM-8 |  |  |  | N | NO | <D> **** Detailed Description **** Temporary HP-EQ-32776 set up to support R24 outage is out of service due to low beta counts. <I> **** Actions Taken **** Placed out of service and notified the HP supervisor. <N> **** Equipment Description **** HP-EQ-32776 on the east side of the TB 441 condenser bay
393600 | CR | 20190517 | CAQ | C | Security Sensitive Information in AR-EVAL and AR-CR |  |  |  | N | NO | <C> Sensitive information has been removed from the EDMS of both the AR-Eval and the AR-CR. <D> **** Detailed Description **** Information marked as Security Sensitive Information, withhold from public disclosure in accordance with 10 CFR 2.390, was identified as attached to the EMDS on an AR-EVAL and AR-CR. This information has now been locked down by IT on the AR-EVAL and AR-CRâ€™s EDMS. This AR-CR written to identify the issue for failing to ensure compliance with SWP-SEC-11 paragraph 4.8.4 which would require at least password protection for the record included in EDMS. <I> **** Actions Taken **** alidated with design engineer supporting the assignment via another EC that this information is not required and to identify if it existed elsewhere (found in the AR-CR as well). Worked with IT Duty Manager and IT specialist to lock-down the documents on the EDMS on the AR-EVAL and AR -CR. Information on the details have been sent to Security Safeguards & Compliance Specialist.
393601 | CR | 20190517 |  | 3 | R24 LL: SL31 bus outage removed power from snubber testing |  |  |  | N | NO | <D> **** Detailed Description **** SL31 bus outage removed power from snubber testing. SL31 estinated recovery in 24 hours. No effect on critical path, this is a lessons learned CR. <I> **** Actions Taken **** OCC was notified, posssible temp power to be evaluated. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
393602 | CR | 20190517 |  | 4 | IPM at PAP in GSB is out of service due to Fault |  |  |  | N | YES | <D> **** Detailed Description **** IPM HP-EQ-32777 is in fault stating: Count aborted, Please leave, when no one is in the machine <I> **** Actions Taken **** Contacted HP Lead tech of the Reactor Building, told the HP supervisor and crated this CR <N> **** Equipment Description **** GSB, Yakima building Primary access from the RCA | 02-00-HP-EQ-32777
393603 | CR | 20190517 |  | 4 | ARGOS at Primary access is in fault |  |  |  | N | YES | <D> **** Detailed Description **** ARGOS HP-EQ-42784 is in fault stating: low background beta counts. <I> **** Actions Taken **** Took maching out of service, told reactor building HP lead tech and the HP supervisor. Created a CR <N> **** Equipment Description **** Primary RCA Access point. | 02-00-HP-EQ-42784
393604 | CR | 20190517 |  | 4 | TMU-C-1B not running in AUTO |  |  |  | N | YES | <D> **** Detailed Description **** TMU-C-1B is not running to maintain pressure in TMU control air system. Standby compressor is required to start to restore pressure. Breaker and control switch lights out. Bulbs in breaker are very difficult to remove so bulb check was not performed. Attempted breaker reset but no change in status. Could potentially be a fuse issue. <I> **** Actions Taken **** Attempted reset with CRS direction but no change. | 02-00-TMU-42-8R3E
393605 | CR | 20190517 |  | 3 | Loss of Weld Record data in through EWP |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Work order 02125690-01, for EPN MS-V-172B, was at status â€œworkingâ€ and through the process of being checked in and out of multiple tablets experienced a complete loss of data on Weld Record 2-13642. This EPN is a critical, NSR, Seismic Class 2, Code Group D (ANSI B31.1) component. The electronic work order was checked in on the tablet in the Mechanical Maintenance shop after the completion of the shift. During the process of validating the work order in Dataglance, the original weld record was replaced after a revision was made to the package. This appears to be the cause of the data loss of the signatures on the weld record. The weld record was filled out over multiple shifts by Mechanical Maintenance welders and QC personnel, upon successful final visual inspections, in the respective weld numbers pertaining to the work that had been completed. The Weld Record was still in use at the time when the complete loss of data in the weld record had occurred. The signoffs for Welder Identification, Fit Up, Preheat/Interpass, and Welder Final Visual, as well as the QC Final Visual (MWP-11) have been lost in the associated WR. Documentation for the acceptance of the welds which were inspected by QC was maintained per the QC Callout. After discussion with Quality Control, traceability can validate the prior acceptance for the purpose of re-performing the respective welder and inspector sign offs for the new WR. A new copy of the weld record will need to be issued in order to complete field work on the remaining welds and re-document the previous welds. Remaining sign-offs can be re-documented by the welder who performed the welding activities. This error in EWP will create rework and significant lost time for the completion of the job. <I> **** Actions Taken **** Notified Craft Supervisor, Notified QC, Notified EWP and generated CR <N> **** Equipment Description **** T 448' F10/10.3
393606 | CR | 20190517 |  | 4 | Security XD-3 | N | N |  | N | YES | <D> **** Detailed Description **** Security XD-3 is showing a detector flow warning. <I> **** Actions Taken **** Generated CR/WR and contacted I&C for support. | 02-00-SEC-XD-3
393607 | CR | 20190517 |  | 4 | IPM-8 Low Beta Counts | N | N |  | N | YES | <D> **** Detailed Description **** HP-EQ-32776 displays low beta counts <I> **** Actions Taken **** Placed it out of service and notified HP Supervisor <N> **** Equipment Description **** TB 441 condenser bay, temporary set up to support R24
393612 | CR | 20190517 |  | 4 | HP-EQ-42712 | N | N |  | N | YES | <D> **** Detailed Description **** Upper detector has fault <I> **** Actions Taken **** Placed it out of service and initiated a CR/WR <N> **** Equipment Description **** HP-EQ-42712
393613 | CR | 20190517 |  | 4 | Incorrect wiring identification found | N | N |  | N | YES | <D> **** Detailed Description **** During the PMT for the E-DP-S1/1C3 QMB disconnects replaced under WO 02115124, it was identified that the wires for disconnects 2 and 6 had phase tape indicating the positive and negative wires were rolled and do not meet the standard configuration. After investigating, it was determined that the same issue was identified previously in CR 286704 which attempted to correct the drawing but did not properly identify the actual issue. The red phase tape is on the negative lead which is incorrect and leads to confusion. The PMT tested satisfactory and is physically correct, only the labeling is oncorrect. Recommend removing the red tape from the negative lead, and properly applying red tape to the positive leads for disconnects 2 and 6. <I> **** Actions Taken **** Craft relanded wires the same as they were removed. Discussed with PM and initiated CR. | 02-00-E-DISC-DPS11C3/2,02-00-E-DISC-DPS11C3/6,02-00-E-DP-S1/1C3
393614 | CR | 20190517 | CAQ | C | Isolation of CRD Pump Suction During Maintenance | Y | N |  | N | YES | <C> RISK: Medium. CAUSE: Clear. Severity B, Investigation Template Required MRT Change from B to Severity C/Low Risk. NO Investigation Template Required. <D> **** Detailed Description **** CRD-FU-10B was replaced per WR 29148091 and SOP-CRD -FILTERS; section 5.8. Approval from Operations had been obtained for Maintenance personnel to operate valves per SOP-CRD-FILTERS provided an experienced Maintenance person was involved. Mechanical Component Manager accompanied the Mechanics. During the filter integrity check, leakage was identified from the filter o-ring flange connection. Performance of section 5.8 placed CRD-FU-10B in service and removed CRD-FU-10A from service. To repair CRD-FU-10B leak, Maintenance personnel began to re-perform section 5.8 without first shifting to CRD-FU-10A. This action isolated suction to the CRD pump. <I> **** Actions Taken **** Coordinated with Operations to restore CRD. <N> Cause: Craft personnel reperformed SOP-CRD-FILTERS steps 5.8.1 - 5.8.6 after O-ring leak detected. Flow was isolated as a result. Personnel had been given permission for perform valve line up under oversight of the component manager on shift, but did not specifically discuss performing the entire section. Corrective Action: Night Order issued stated that Operations will not allow craft to manipulate in service equiment. | 02-00-CRD-FU-10B
393615 | CR | 20190517 |  | 3 | (QA) FME Cover Deficiencies |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) FME Cover deficiencies discovered during walkdown. During a Quality Auditor walkdown of the turbine building the following FME cover deficiencies were identified. TSW -V-201 downstream piping is removed and there is no FME cover installed on the flange. Several new pipes ready for installation in the TSW system have tape as an FME cover. The mesh FME cover over the lower east end manway of MSR -HX-1B was not secured properly and half of it has fallen down. Refer to pictures in EDMS. These conditions can allow the introduction of foreign materials in the piping systems and cause damage to equipment. <I> **** Actions Taken **** Discussed this issue with the WPS supervisors and sent them the pictures. They stated that they will correct these conditions promptly. Initiated this CR. <N> Williams Plant Services. Both area FME conditions have been corrected. WPS Supervisor has verified as-left conditions are SAT. Coaching was provided to supervisor responsible for this work. No further actions required.
393616 | CR | 20190517 |  | 3 | Electrical backfeed not labeled |  |  |  | N | NO | <D> **** Detailed Description **** Due to the SL-21/SL-31 cross-tie capability, there is a backfeed from E-SL-21 into the E-CB-31/21 cubicle that is not labeled. Anytime E-SL-21 is energized, the lower stabs in the E-CB-31/21 cubicle (unit 4A) will also be energized. The power cables connected in the rear section of the switchgear will also be energized. Recommend permanent Danger labels warning personnel of this backfeed be placed on the E-CB-31/21 cubicle door and the rear cover.
393617 | CR | 20190517 |  | 4 | Initial COND-HX-9 entry on 471â€™ | N | N |  | N | YES | <D> **** Detailed Description **** WOT 02108276-05 for COND-HX-9 initial entry includes entry to each bay at the 471â€™ elevation only. General steam erosion observed in each bay. Charlie bay a Â½â€ dump line on the south side did not have a dump shield (none in the area, either at bottom of condenser or previously removed). Bravo bay a steam dump shield was found on top of the tubes (item removed) this was on the southeast portion, small portion of COND-HX-1B steam shield was missing on east side, small debris found and removed. <I> **** Actions Taken **** This CR is to document the conditions found and no action is needed at this time. Bravo bay will have scaffold built to extraction line expansion joints where more inspections will take place (fine location of steam dump shield, etc.) Task -01 will include the entire steam side inspection for further review. | 02-00-COND-HX-9
393618 | CR | 20190517 |  | 3 | Contaminated Individual Unable to be Fully Decontaminated |  |  |  | N | NO | <D> **** Detailed Description **** A Carpenter working in the Turbine Building Heater Bay was found with approximately 80 ccpm of contamination on the left upper bicep. Multipe decontamination methods (showering, sloughing, sweating, tape press, etc.) were not successful at removing the contamination. A whole body count showed approximately 10 nCi of Co-58 and 14 nCi of Co-60. Contamination appears to be embedded in the individual's skin. <I> **** Actions Taken **** Decontamination efforts were exhausted. A whole body count was performed to identify the isotopic mixture. The RPM and the OCC were notified. RPM approval was obtained to release the individual in accordance with PPM 11.2.15.13. <N> WIlliams Plant Services.
393619 | CR | 20190517 |  | 4 | Loose nut found on stud on RFT-DT-1B governor rack | N | N |  | N | YES | <D> **** Detailed Description **** A loose nut was found on a 3/4-1" stud on the RFT-DT-1B governor rack. <I> **** Actions Taken **** Craft notified Operations supervisor. <N> Loose nut identified by craft during RFT overhaul. This will be corrected during reassembly under WO 02047040. CR to trend/ or System Engineer evaluation. | 02-00-RFT-GOV-1B
393620 | CR | 20190517 |  |  | Pursuit of Excellence at Cost of SCWE and Teamwork |  |  |  |  | NO | <D> **** ANONYMOUS CR - Detailed Description **** ***SENT TO ECP***** See ECP for contents of CR <N> CR initiated anonymously, reviewed for SCWE content. Moved and forwarded to AR-ECP.
393621 | CR | 20190517 | CAQ | D | Wellhouse #2/Flocculator Fire Alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received Wellhouse #2/Flocculator Building Fire alarm. Ops 4 reports no fire, but that Ionization Detector 49-2 is activated/tripped, causing the alarm. <I> non-essential fire protection. | 02-00-FP-ID-49/2
393622 | CR | 20190517 |  | 4 | TG501' West SAM9 Not Operational |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** TG501' West SAM9 Not Operational. Display shows Fault. We need this to help Free Release items from the RCA. HP-EQ-42998 <I> **** Actions Taken **** Notified HP TG Supervisor. Initiate CR/WR. <N> **** Equipment Description **** TG501' West
393623 | CR | 20190517 | CAQ | C | Unacceptable Preconditioning RHR-V-8 prior to as-found LLRT | Y | N |  | N | YES | <D> **** Detailed Description **** RHR-V-8 was tested for LLRT on 5/15/19 to obtain the as -found leak rate results. Due to problems with the test method, higher than expected leak rate and equipment limitations, the as-found test results were not at valid test conditions. Later that day, the PM task to stroke and lubricate the valve stem was performed (WO 02139431). This task is known to affect MOV performance (see PPM 10.25.132 section 4.1.4, Testing) and is required to be performed after as-found MOV testing to prevent preconditioning the test. This can also affect LLRT performance. Per IST-4, IST Program Plan, this is unacceptable preconditioning. IST- 4 requires the following for this case: â€œIf unacceptable preconditioning has occurred and conditions no longer support conduct of an as-found test until the maintenance activity is completed, the event should be captured in the corrective action program to evaluate the impact and take any additional remedial actions that may be necessary; such as additional tests, results of the inspection, condition of replaced parts, etc..â€ <N> The unacceptable preconditioning documented does not impact operability of RHR-V-8 as this issue pertains to how the LLRTs after the as-found were performed. When unacceptable preconditioning is identified one action is to document in CAP and another is to perform additional tests. Additional test has been performed on 5/18/19 with a leak rate of 1.94gpm which is above admin limits but well below the Tech Spec limit of 4.75gpm. | 02-00-RHR-V-8
393624 | CR | 20190517 | CAQ | C | Failure to Meet ASME XI, Category C-C examination requiremen |  |  |  | N | YES | <D> **** Detailed Description **** CR 393566 documents the fact that the coating needs to be removed from the RHR-HX-1A supports to allow for ASME SCXI required examination scheduled this outage. A review of the work and examination history could not show that the coatings were removed for previous examination either thus the prior examinations are not valid, therefore, CGS is not compliant with ASME table IWC-2500-1, Category C-C requirements for RHR-HX-1A & 1B. RHR-HX-1A & 1B are the only two vessel components in this ASME category. <I> **** Actions Taken **** Discussed with Licensing. Reviewed two other Class 2 surface examinations and verified that the coatings were removed, this issue appears to be limited to the RHR heat exchangers. CR 393566 and OSCR 393568 addresses coating removal and performance of the examination in R24. This CR is to document the historical non-conformance issue and impact to the ISI Program, assign to AR-CPROG. | 02-00-RHR-HX-1A,02-00-RHR-HX-1B
393627 | CR | 20190517 |  | 4 | mt-cra-1 | N | N |  | N | YES | <D> **** Detailed Description **** The Main Contactor for MT-CRA-1 will not latch and allow crane operation. WR 29148760 has been initiated <I> **** Actions Taken **** Notified the Turbine/Generator Project Manager, the OCC, the FIN Electricians and generated this Condition Report. | 02-00-MT-CRA-1
393628 | CR | 20190517 |  | 3 | BHI RP - Unable to get timely breaks and Lunch |  |  |  | N | NO | <D> **** Detailed Description **** Due to staffing cuts from R23 and current workload, many BHI RP technicians are not getting breaks or lunch's in a timely manner. In addition, they are not getting time out of the field to document surveys and air samples <I> **** Actions Taken **** Initiate Condition Report. Spoken to RadOps Supervisor and Area EN Lead technicians With Blaine HIghlands approval shut down work in TB Heater Bay on 5/16 for approximately 1 hour to allow technicans a lunch break at 1500 ( they started their shift at 0500-0600)
393630 | CR | 20190517 |  | 4 | RFW-DT-1B Overhaul Clearance Order Delay |  |  |  | N | NO | <D> **** Detailed Description **** The subject work under WO 02047040 has not started as scheduled due to a delay in the hang of O-RFW-DT-1B/R24 -002. It appears O-RFW-DT-1B/R24-001 was hung instead. <I> **** Actions Taken **** Notified the PSRO and the RxM OCC rep. The PSRO reports the tags are in the field to be hung at this time (5/17/19 @ 11:40).
393631 | CR | 20190517 |  | 4 | R24LL Incorrect logic on inital condenser entry task |  |  |  | N | NO | <D> **** Detailed Description **** In the R24 schedule, lighting, ventilation and scaffolding tasks for the intial entry to the condenser were logic tied with a FS to the removal of the hotwell hatches task. These tasks should have been tied as a FS with the inital entry to the condenser task. <I> **** Actions Taken **** Outage managment, scheduling and applicable work groups were notified of the late starts to the task. No further action required
393632 | CR | 20190517 |  | 4 | TMU-V-1C had to be manually closed | N | N |  | N | YES | <D> **** Detailed Description **** TMU-V-1C had to be manually closed when securing TMU-P-1C. The valve stroke most of the way closed in the field but still indicated mid position in the control room when the valve quit moving. TMU-P-1C was observed to be rotating backwards in the field. With CRS permission TMU-V-1C was manually closed in order to stop TMU-P-1C from rotating backwards. When the valve was manually closed the CR position indication went to full closed. <I> **** Actions Taken **** Wrote CR Informed CRS | 02-00-TMU-V-1C
393633 | CR | 20190517 | CAQ | D | Control rod did not withdrawl | Y | N |  | N | YES | <D> **** Detailed Description **** When attempting to withdrawl a control rod for uncoupleing activities IAW PPM 6.5.9 the control rod was not able to be withdrawl. There was no rod block and no issue noted with the RDCS stystem <I> **** Actions Taken **** attempted vent the control rod by inserting the contol rod when fully inserted. Actions per ABN-ROD to vent and double clutch the control rod allowed the rod to move. There is no degraded condition. | 02-00-CRD-HCU-1455
393634 | CR | 20190517 |  | 4 | Badge lost during work in Transformer Yard |  |  |  | N | NO | <C> MRT Change from CAQ to NON-CAQ. <D> **** Detailed Description **** During work in the Transformer Yard, a BPA electrician lost his badge. He was wearing fall protection while working in a lift vehicle, and was not aware that the lanyard had broken until he removed his harness. <I> **** Actions Taken **** He notified the Transformer Yard Coordinator who notified the Security lieutenant who escorted the worker off site. As they were leaving site, the individualâ€™s coworkers notified him that they had found his badge. A Security officer retrieved the badge from the coworkers and the Lieutenant returned it to the individual.
393636 | CR | 20190517 |  | 3 | R24 LL: Overal slowness observed in software applications |  |  |  | N | NO | <D> **** Detailed Description **** There has been consistent intermittent slow downs in a variety of software applications performance during R24. This is CR is to document the decline in overall system performance during refueling outages. Specific application performance issues will be documented in actions on this CR. <I> **** Actions Taken **** IS team working on current actions for R24. Long term actions will be documented on this CR. Recommend NCAQ3 - ITMGMT
393637 | CR | 20190517 |  | 4 | CW-FN-26 and CW-FN-27 need oil addition. | N | N |  | N | YES | <D> **** Detailed Description **** CW-FN-26 oil level is at the S/D add mark and CW-FN-27 is about 1/32" below the S/D add mark. Please add oil as required. <I> **** Actions Taken **** Notified supevisor. <N> **** Equipment Description **** CW-CT-2B | 02-00-CW-FN-26,02-00-CW-FN-27
393639 | CR | 20190517 | CAQ | C | CIA-V-31A exceeds its admin limit | Y | N |  | N | YES | <C> CR reopened to add completion required check mark to referenced WO 02079232 per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** During performance of TSP-CIA/X89B-C801 per WO 02112310, CIA-V-31A As-Found LLRT (Local Leak Rate Test) exceeded its admin limit with a leak rate of 190 sccm. The As-found leak rate could not be quantified due to inability to achieve test pressure. The X89B penetration minimum pathway was 67.67 sccm per test of CIA-V-30A. OSCR for intrusive maintenance is required. <I> **** Actions Taken **** Notified LLRT SRO/OCC <N> **** Equipment Description **** C539 | 02-00-CIA-V-31A
393640 | CR | 20190517 |  | 3 | R24LL: TSP-FPC/X100-B801 revision required |  |  |  | N | NO | <D> **** Detailed Description **** TSP-FPC/X100-B801 procedure needs to be changed. On page 3 of 10 the note below step 3.3 needs to reference PPM 10.24.242 vice 10.24.241. <I> **** Actions Taken **** initiated CR and notified procedures
393641 | CR | 20190517 |  | 4 | RFW-DT-1A Turbine Lube Oil Coolers, TSW will not drain. | N | N |  | N | YES | <D> **** Detailed Description **** Hanging of clearance O-TSW-RFW/AR-001, final four valves drain the TSW side of Lube Oil Coolers. No water flowed from drains TSW-V-8A and TSW-V-8B, and minimal dripping of water comes out of vents TSW-V-7A and TSW-V-7B. TSW verified for free release, hoses for drain valves going into a 55 gal drum, hoses for vent valves going to a second 55 gal drum. A third 55 gal drum is staged. <I> **** Actions Taken **** Unable to poke and break up rust, similar to TSW draining of H2 Coolers, because one cooler has a globe valve. Although the other cooler has a ball valve, both cooler drains turn at a sharp 90 degrees and attach to the cooler, so trying to poke the rust out is not feasable.. Production Supervisor and Manager informed. CR & WR written, and notes will be added to clearance. | 02-00-TSW-V-7A,02-00-TSW-V-7B,02-00-TSW-V-8A,02-00-TSW-V-8B
393642 | CR | 20190517 |  | 4 | BHI Employee First Aid Injury |  |  |  | N | NO | <D> **** Detailed Description **** A BHI HP technician was injured whiel working in drywell at 548' elevation. Employee impacted Hardhat on strut jarring neck and back <I> **** Actions Taken **** Employee was escorted to Site Medical where he was examined. released to work with no restrictions
393643 | CR | 20190517 |  | 3 | Danger and Caution tape usage.. Lessons Learned R24 |  |  |  | N | NO | <D> **** Detailed Description **** Most plants in the industry donâ€™t want you â€œduckingâ€ under Caution or Danger tape. The reasoning is, it can catch on your hard hat, shoulders, safety harness, etc. and possible create awkward body positioning. If it catches on hard had or safety harness, there is a potential for injury, and/ or knocking down stantions and flagging. <I> **** Actions Taken **** To eliminate the hazard, create an entry point (gate/s) made of the appropriate flagging that can be opened up (lifted) and then connected again to secure entry point. This eliminates the hazard, and controls access to the area. It also creates a point where everyone entering can pause and read the signage before entering. If it is a Danger area, it creates an area where the point of contact can stand and control who, and when he lets anyone in the area. If used correctly, this will also be the safest point to enter the area for walking paths, overhead work, etc.
393644 | CR | 20190517 |  | 3 | MCC-3B Door latches not working | N | N |  | N | YES | <D> **** Detailed Description **** 2C Bucket, Safety latch does not stop door from opening when is in the on position. 5A Bucket, Safety latch does not release at all when in the open position, had to open with screwdriver from front of hand switch. <I> **** Actions Taken **** Need ENG eval to replace or repair. <N> **** Equipment Description **** E-MC-3B T-471, E1/14.5 WO 02112899 will address issues. Closing CR to work management process. | 02-00-E-MC-3B
393648 | CR | 20190517 |  | 3 | Late Identification of Lead Based Paint |  |  |  | N | NO | <C> MRT Change from CAQ to NON-CAQ. <D> **** Detailed Description **** Project 34411701 Drywell Material Storage was notified late that lead sampling and possibly lead abatement will be needed to install storage boxes in containment. This was not identified in the planning phase. WO 02120897 will be impacted. . This does not affect plant equipment. <I> **** Actions Taken **** Informed supervision. <N> **** Equipment Description **** C-TK-1.
393649 | CR | 20190517 |  | 3 | R24LL SOP-CW-SHUTDOWN |  |  |  | N | NO | <D> **** Detailed Description **** To clarify and verify no vacuum exist when opening manway covers. Also adds a caution to notify operators that this may cause circ water basin level rise. see attached file <I> **** Actions Taken **** see attached file
393650 | CR | 20190517 | CAQ | C | MS-V-28B Unanticipated resistance during poppet removal. | Y | N |  | N | YES | <D> **** Detailed Description **** During MS-V-28B poppet removal, unanticipated resistance was experienced with the poppet approximately 5 inches out of the bore. Since this is not an expected condition, the work was stopped to expand the team to determine the best path forward. <N> **** Equipment Description **** ST 505 H4/5.5 | 02-00-MS-V-28B
393651 | CR | 20190517 |  | 3 | (QA) Noncompliances with PPM 1.3.63 for Vacuum |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Vacuum cleaner staged on TG 441' did not meet control requirements in PPM 1.3.63 "Vacuum Cleaner, Fan, and Blower Control" twice. Very early in the morning on 5/17/19, a Quality Auditor found a vacuum cleaner a contamination sticker on it that was staged on TG 441 elevation in the condenser bay south side. The vacuum had no bag/tape on the suction port and no tamper proof seals, contrary to PPM 1.3.63. The Quality Auditor talked to a Health Physics (HP) Technician who contacted the person on the "Staged For" sign. Later the same morning, another Quality Auditor found the suction hose covering the previously open suction port on the vacuum; however, the other end of the suction hose was uncovered. The metal catches holding the vacuum containment sections together had twisted wires instead of tamper proof seals, contrary to PPM 1.3.63 (see photos in EDMS). Not covering a vacuum suction port and suction hose could result in contamination escaping, and tamper proof seals inhibit unqualified individuals from opening a contaminated vacuum. Requirements: (See details in EDMS) Factual Basis: (See details in EDMS) Insights: â€¢ HPI-15.8 is not aligned with PPM 1.3.63 on installing tamper proof seals on vacuums. It appears the twisted wires had resulted from HPI-15.8 "Controlled Vacuum Cleaner Minor Maintenance" steps 5.2.4b and 5.2.4c. These two steps say "wire seal", but the "Wire on Vacuum" photo shows a wire is not "sealed" because (unlike the tamper proof seals) the wire can be untwisted, removed, and re-twisted without showing evidence of tampering. â€¢ The second Quality Auditor contacted an HP Supervisor who sent an HP technician to seal the other end of the suction hose with tape. Quality confirmed that this was accomplished. â€¢ In November 2015, Quality identified a similar issue during an audit as noted in Condition Report 339273 "(QA) Vacuum / Attachments not Taped". <I> **** Actions Taken **** Contacted the Chemistry/Rad Services Manager. . Quality recommends this CR be routed to Radiation Protection. . This Deficiency was identified during the R-24 Quality Surveillance SR-19-01.
393652 | CR | 20190517 |  | 3 | superfluous pipe hanger that provides no support |  |  |  | N | NO | <D> **** Detailed Description **** Description: During R23 there was a pipe support attached to location 334-13 that provided an obstruction to perform a FAC exam. The low measurement is adjacent to the pipe support. WO # 02113389-10 was used to cut out hanger RFW-944 in R24. However, it was discovered that hanger RFW-944 held an adjacent tee section of pipe. A review of construction documentation show that the obstruction hanger was not represented on ISO 215-00,1168. This represents a possible configuration management issue. The obstruction appears to be a piece of tube steel welded to the pipe that provides no support. <I> **** Actions Taken **** Notified Planning to correct the welding package so the WO can continue Wrote the CR and notified EOC . Work Order 02113389-10/11 have been returned to address the drawing vs field discrepancy. <N> Looked at the vault package for CVI ISO 215-00,1168 (RFW-416-6.9) and a Burns and Roe Memorandum dated 8/06/82 states that pipe support hanger RFW-78 is required to be deleted. Also CVI DWG 215-08,11185 (RFW-78) is statused as historcal and a Fitter Welder redline drawing in the vault package dated 11/31/81 shows hanger RFW-78 . Hanger RFW-78 also does not appear in pipe stress calculation AED CAL 8.42.800. If the remnants of hanger RFW-78 are removed the exposed elbow needs to be insulted. . From the 'tube steel welded to the pipe' description, this item is a trunnion. .
393653 | CR | 20190517 | CAQ | D | CVB-V-1JK no open indication light | Y | N |  | N | YES | <C> CR reopened to cross reference additional WR 02111599, marked completion required box, then taken back to complete <D> **** Detailed Description **** Workiing MSP-CVB/ST -B101 WO # 0211159903, When vacuum breaker is cycled open , linkage arm hits and bounces of indicator , open light it control room flashes on the off, when closing actuator was jerky. | 02-00-CVB-V-1JK
393654 | CR | 20190517 |  | 4 | Striped screw on TB641, TGB471 Main Gen CT's set 05 |  |  |  | N | NO | <D> **** Detailed Description **** The terminal screw at wire AY-4 field side is striped. Can't determ to do megger test of wire.per WO#02115725-05 step 4.4 <I> **** Actions Taken **** Notified E.O.C. for resolution. Asked engineer to iniate step in WO to fix per thier resolution.
393655 | CR | 20190517 | CAQ | D | CVB-V-1QR actuator jerky when closing | Y | N |  | N | YES | <C> CR reopened to add completion required check mark to referenced WO 02111599 per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** Working MSP-CVB/IST-B101 WO # 02111599-03 CVB-V-1QR actuator jerky when closing | 02-00-CVB-V-1QR
393656 | CR | 20190517 |  | 4 | while performing WO 0212200302 found IBD-TS-F3 OOT | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** IBD-TS-F3 Trip was found out, tripped at 204Â°F SP is 200 Â°F Â±3Â°F <I> **** Actions Taken **** adjusted to within tolerance
393657 | CR | 20190517 | CAQ | C | Linear indication reported on the Steam Dryer near tie bar | N | N |  | N | YES | <D> **** Detailed Description **** During R24 IVVI inspections, a linear indication has been reported on the steam dryer bank below TB-AB-3 (reference DRAFT Indication Notification Report INR-CGS-19-001 in EDMS). The indication is approximately 1.25 inches long. When compared to R22 data from the same location, the indication was visible but not reported. A comparison to the previous data shows no apparent change in the termination points from R22. The indication is not in a critical weld or location. <I> **** Actions Taken **** Reviewed R22 and R18 video footage. Performed preliminary review of industry guidance. Preliminary assessment is that the indication stable, not structurally significant and will not require repair. Assign to AR-CPROG to complete evaluation in accordance with BWRVIP-139 Rev 1-A. <N> Based on the evaluation in AR 393657-01 the condition is acceptable and no repairs are required. The indication will be examined next outage to ensure it is stable and there is no propensity for growth or debris generation. This subsequent examination, along with the R22 examination results will provide a high degree of confidence that there is no active degradation mechanism. Once the indication is determined to be stable, the inspection frequency will be at least every 5 cycles in accordance with industry guidelines. WR 29149082 was actioned to WO 02144958 to remove the retainer and/or replacing the beam in R25. . Re-opened the CR to update the RXSU coding. | 02-00-MS-RPV-3
393658 | CR | 20190517 |  | 3 | MT-ELEV-4 is out of service | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-4 failed multiple times on 5/17 which required support to assist individuals to exit. The elevator has been placed out of service pending repairs. <I> **** Actions Taken **** CR written and OCC notified. <N> RW elevator has been reliable. No further action from Ops at this time. | 02-00-MT-ELEV-4
393659 | CR | 20190517 |  | 4 | MT-ELEV-2 erratic behavior | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of the SL-31 outage, MT-ELEV-2 experienced erratic behavior. Temp power was lost to E -RECT-LP3DAA/6/5 during the bus outage and the elevator would not respond to button controls and traveled from the RB 606 to RB 422 and back to the RB 606 continuously without stopping on any floors. The outer doors on the RX 441 and RB 422 were manually opened to allow the people trapped in the elevator to exit. Power from the temporary power source from E-DISC-PPF10/2/9/1 was removed to during the retrieval of the personnel. When power was returned to E-DISC-PPF10/2/9/1, the elevator was no longer moving on its own and stopped on the RB 422 elevation. <I> **** Actions Taken **** CR written, OCC and SM informed of issue. <N> **** Equipment Description **** RB SW 422
393660 | CR | 20190517 | CAQ | D | wma-dpis-53 in alarm with normal d/9 | Y | N |  | N | YES | <D> **** Detailed Description **** The SWITCHGEAR FILTER 53A DIFFERENTIAL PRESSURE HIGH / LOW alarm H13-P826.P1 (1-2) is locked-in. WMA-DPIS-53A indicates 0.55" H2O locally with WMA-FN-53A running. This is between the alarm low setpoint of 0.1"H2O and alarm hi setpoint of 0.8 "H2O. <I> **** Actions Taken **** Submitted CR and WR. Notified the CRS and SM. | 02-00-WMA-DPIS-53A
393662 | CR | 20190517 |  | 4 | E-MC-3B malfunctioning breaker switches |  |  |  | N | YES | <D> **** Detailed Description **** While preforming WO 020762801, it was noticed that MCC 3B breakers 8B, 7A, 7D, and 4D are not cycling and resetting properly. Additional maintenance beyond the scope of procedure PPM 10.25.105 section 7.1 is required. <I> **** Actions Taken **** Called PSRO, wrote CR <N> **** Equipment Description **** T-471, E1/14.5 Motor control center E-MC-3B . In addition, Breakers E-MC-3B8B and E-MC-3B7A could NOT be placed in the closed position.
393664 | CR | 20190518 | CAQ | D | CIA-PS-29 did not reset at IMDS reset pressure | Y | N |  | N | YES | <D> **** Detailed Description **** When re-pressurizing CIA following LLRT's, CIA-PS-29 did not reset. This drives alarm H13-P840.A5.5-3, CIA HEADER PRESSURE LOW. After re-pressurization, CIA-PI-29 indicates at least 105 psig. The IMDS for CIA-PS-29 indicates that CIA-PS-29 should reset and the alarm should clear at less than 105 psig. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CIA-PS-29
393666 | CR | 20190518 |  | 4 | E-DISC-TR5/51 does not have open sticker indication. |  |  |  | N | YES | <D> **** Detailed Description **** While hanging clearance order O-E-CB-CTA/R24-001 WO 02113930 and opening disconnect E-DISC-TR5/51 it was noted that E-DISC-TR5/51 does not have open sticker indication as compared to E-DISC-TR5/52. A new sticker is needed. | 02-00-E-DISC-TR5/51
393667 | CR | 20190518 |  | 4 | Stuck studs on RFW-HX-6B |  |  |  | N | YES | <D> **** Detailed Description **** Working work order 02111387-01, RFW-HX-6B, two studs with nuts seized up on the shell side of the heat exchanger. They cannot be removed, so they will need to be cut off. They will need to be drilled out and possibly require Heli-coil installation if the threads are damaged on the shell side.This is a Lessons learned from 2013, when the same issue occurred. Work order 01177977.ENW Mechanics will need to drill out the cut-off studs and possibly install Heli-coils. <I> **** Actions Taken **** Contacted OCC and Management for direction. <N> **** Equipment Description **** RFW-HX-6B, Heater Bay
393668 | CR | 20190518 |  | 4 | No power to WEA-FN-2A |  |  |  | N | YES | <D> **** Detailed Description **** WEA-FN-2A in the chemistry lab does not have power. <I> **** Actions Taken **** Informed chemistry superverision and wrote a CR. <N> **** Equipment Description **** 487' RW chemistry lab | 02-00-WEA-FN-2A
393669 | CR | 20190518 |  | 4 | Bad fuse on 3BB-2 | N | N |  | N | YES | <D> **** Detailed Description **** While preforming procedure 10.25.53 on panel 3BB a bad fuse (FRN-20) was found in 3BB-2, for Local control panel B35 -P001A <I> **** Actions Taken **** Contacted OCC and wrote CR <N> **** Equipment Description **** 3BB-2, T-471 B4/16.0
393670 | CR | 20190518 | CAQ | C | RHR-V-8 as found LLRT above admin limit | Y | N |  | N | YES | <D> **** Detailed Description **** RHR-V-8 as found LLRT per WO02110827-11 performed on 5/18/19 is 1.94 gpm. The Admin limit is .15gpm. The Tech Spec limit is 4.75 gpm <I> **** Actions Taken **** Informed OCC/SM | 02-00-RHR-V-8
393674 | CR | 20190518 |  | 3 | R24LL: TSP-RCS-R802 documentation for high flow test cart | Y | N |  | N | NO | <D> **** Detailed Description **** No formal documentation of high flow test cart use was documented in TSP-RCS-R802. Specificaly test cart setup is in section 5.0 and attachemtn 9.1. This does not reflect the test setup used. Step 7.9.1.gg is a pounded step for acceptable leak rate and is supported by attachement 9.7. This attachemnt has a specific calculation to support the leak rate in step 7.9.1.gg and does not reflect using the high flow test cart. <N> This was not a change in test methodology. The test was performed in accordance with PPM 10.24.242 which contains direction to operate the cart. An enhancement to TSP-RCS -R802 should be considered.
393675 | CR | 20190518 |  | 4 | COND-DPT-5 found out of tolerance |  |  |  | N | YES | <D> **** Detailed Description **** During performance of COND-DPT-5 loop cal per WO#02138587 -01, COND-DPT-5 was found out of tolerance high. <I> **** Actions Taken **** Performed zero shift and returned to service. Wrote this CR to document. | 02-00-COND-DPT-5
393676 | CR | 20190518 | CAQ | D | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0052389 White Box Hygrothermograph- model CT485-AL found OOT & adjusted within specs. EFIN Eval: A review of the charts showed no sustained RH above 30%. No Plant Impact. DEF #7027A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
393677 | CR | 20190518 |  | 3 | 10.25.19 Recommend enhancement |  |  |  | N | NO | <D> **** Detailed Description **** PPM 10.25.19 Termination and Splicing Instruction, step 3.1.1 directs to verify phase tape colors and if appropriate phase tape color is not correct, to replace the tape before leads are connected. If this is performed as written, it would then place the plant out of configuration as many of the EWD drawings identify what phase colored lead is terminated to which termination point. During performance of WO 02117247-01 to replace the coil for E -MC-7BA, it was identified that the existing phase labeling was not in a standard configuration. However, this configuration is reflected properly on drawing EWD-63E-018 as the T1 and T2 leads are shown as swapped. This condition is normal in conditions where the rotation of a component is found incorrect and leads are rolled to correct the condition. In these conditions, the leads should not be relabeled. Recommend PPM 10.25.19 be revised or clarified. <I> **** Actions Taken **** Discussed discrepancy with craft and QC. Initiated CR. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
393678 | CR | 20190518 |  | 3 | Condenser Hotwell FME | N | N |  | N | YES | <D> **** Detailed Description **** During the initial main condenser hotwell inspection, COND-HX-9, some foreign material was found. See EDMS photos. The two small metal plates were removed by HP per request. Some small pieces of material on the suction screen were noted, but not a significant concern do to small size and minimal blockage. Also, there were some corrosion products (sludge) that had settled out in low flow areas and also not a significant concern due to small size of particles and being upstream of condensate demineralizers. Recommend accept as-is evaluation for remaining foreign material. No work request generated. <N> **** Equipment Description **** TG 441 condenser hotwell. | 02-00-COND-HX-9
393679 | CR | 20190518 | CAQ | D | MS-RMS-RV/2D as found testing | Y | N |  | N | YES | <D> **** Detailed Description **** Performed as found testing of MS-RMS-RV/2D. One contact block has loose mounting screws. Switch has an intermediate position while going from Auto to Off in which some contacts fail to change state. Some closed contact resistances are greater than the 1 ohm acceptance criteria. See WO 02136022-05. <I> **** Actions Taken **** Contacted supervision, engineering, CRS | 02-00-MS-RMS-RV/2D
393680 | CR | 20190518 | CAQ | D | MS-RMS-RV/2B as found testing | Y | N |  | N | YES | <D> **** Detailed Description **** Performed as found testing of MS-RMS-RV/2B. Switch has an intermediate position while going from Auto to Off in which some contacts fail to change state. Some closed contact resistances are greater than the 1 ohm acceptance criteria. See WO 02136019-06. <I> **** Actions Taken **** Contacted supervision, engineering, CRS | 02-00-MS-RMS-RV/2B
393681 | CR | 20190518 | CAQ | D | MS-RMS-RV/3A as found testing | Y | N |  | N | YES | <D> **** Detailed Description **** Performed as found testing of MS-RMS-RV/3A. Switch has an intermediate position while going from Auto to Off in which some contacts fail to change state. Some closed contact resistances are greater than the 1 ohm acceptance criteria. See WO 02136021-06. <I> **** Actions Taken **** Contacted supervision, engineering, CRS | 02-00-MS-RMS-RV/3A
393682 | CR | 20190518 |  | 4 | RFW-FCV-10A positioner air leak | N | N |  | N | YES | <D> **** Detailed Description **** RFW-FCV-10A has a significant air leak at the positioner. This leak can be heard from ~30ft away. This valve is scheduled to be worked in R24 under WO 02117516. WR not initiated. <I> **** Actions Taken **** Discussed with AOV SME. | 02-00-RFW-FCV-10A
393684 | CR | 20190518 |  | 4 | Unauthorized Materials in Stay Clear Areas | N | N |  | N | NO | <D> **** Detailed Description **** During a walk down of the Reactor Building at 0700 on 5/18/19, the following conditions were observed. Stay Clear area for E-IR-H22/PO05 at R522 south: Hose ran across the Stay Clear area. (The panel was also protected.) Stay Clear area for RWCU-FT-15 at R501 west: Hose coiled and stored across Stay Clear Area. Two metal chairs were also in the Stay Clear area. <I> **** Actions Taken **** The materials were safely moved out of the Stay Clear areas without entry into the area. OCC Shift Outage Manager & OCC Operations Manager were both advised.
393685 | CR | 20190518 |  | 4 | CRD-F-7a at 42 psid | N | N |  | N | YES | <C> MRT Change from CAQ to NON-CAQ. <D> **** Detailed Description **** CRD-F-7a at 42 psid, needs to be changed out <I> **** Actions Taken **** Informed MCR | 02-00-CRD-F-7A
393686 | CR | 20190518 |  | 4 | woa-aw-1, leaks water onto 487 floor. | N | N |  | N | YES | <D> **** Detailed Description **** Found water extending from Air Wash pumps nearly to HVAC panels. Clear there have been prior issues since there was a dam and mop head on floor to keep mess from spreading into rest of area. Could not find active leak, Air wash pumps were running at the time but had just started up recently. Possibly dump valves dumped more water than floor drain could handle. <I> **** Actions Taken **** Initiated AR & WR, informed MCR and HP to coordinate cleanup. | 02-00-WOA-AW-1
393688 | CR | 20190518 | CAQ | D | High current on battery E-B0-1B | Y | Y |  | N | YES | <C> Trend to CR 393699 <D> **** Detailed Description **** Per ESP-BAT-W101, steps 7.1.2a current is not less than or equal to limit range. According to att. 9.1 the current must be less than or equal to 0.1A. Actual current recorded is 7.68A DC. This battery had been off the charger for approximately 18 hours due to work on E-PP -7 and had been on float charge since 0300 on 5/18/19. <I> **** Actions Taken **** Notified CRS per att. 9.2 Disposition of Float Current <N> **** Equipment Description **** E-B0-1B Radwaste 467' Battery room 1 E-B0-1B is Inoperable due to discharge during E-PP-7A outage. Reference CR 393699. T19-FOB-E-PP-7A-001 is tracking the Inoperable condition. | 02-00-E-B0-1B
393689 | CR | 20190518 |  | 4 | RFT-PS-63Q1/1A/1 Needs to be replaced | N | N |  | N | YES | <D> **** Detailed Description **** While performing 0211241801 RFT-PS-63Q1/1A/1, 63Q1/1A/2 & 63Q1/1A/3 CALIBRATION we were unable to calibrate RFT-PS -63Q1/1A/1. Tried to adjust PS back into spec, when we tasted the switch it continued to drift, we are unable ta achieve repeatability <I> **** Actions Taken **** Write CR, Contacted supervisor, need WO to replace with new bech tested switch. | 02-00-RFT-PS-63Q1/1A/1
393690 | CR | 20190518 |  | 4 | Suppression Pool Foreign Material (FME) | Y | N |  | N | YES | <D> **** Detailed Description **** This CR is generated per step 7.3.4 of PPM 8.3.384 SUPPRESSION POOL CLEANLINESS DETERMINATION to document foreign material discovered in the suppression pool. The foreign material has been removed and retained for engineering evaluation. No further foreign material has been discovered. A final containment closeout inspection dive in the suppression pool will be performed prior to the end of R24 outage. Picture of foreign material posted to EDMS. <I> **** Actions Taken **** 1) Initiated AR-CR 2) Provided this information to system engineering for further evaluation per PPM 8.3.384. 3) FME program ccoordinator notified. <N> **** Equipment Description **** C-TK-1
393691 | CR | 20190518 |  | 4 | TSW leak Aux Boiler Room | N | N |  | N | YES | <D> **** Detailed Description **** Pipefitters identified small pinhole leak from TSW piping in the NE corner of the Aux Boiler room. Further investigation determine this leak is in the supply piping to SCH-CR-51 (Service BLDG Chiller). Leak is currently dripping at a rate of about 1 drop every 5-10 sec. <N> **** Equipment Description **** TB 441', Aux boiler room NE corner.
393693 | CR | 20190518 | CAQ | C | RHR-V-8 LLRT Test exceeded admin limit | Y | N |  | N | YES | <D> **** Detailed Description **** Performed local leak rate testing (LLRT) utilizing a Graftel high flow test cart per WO 0211082711 and measured 1.94 gpm. This value exceeds the admin limit of 0.15 gpm but within the tech spec number of 4.75 gpm. The test performed in R23 was measured at 0.94 gpm. The change between R23 and R24 is 1.00 gpm. The degradation between R23 and R24 is within a normal range of expected change given that we experienced 2 unplanned shutdowns. Current trend shows that the values will remain within limits through cycle 25. Based on this trend, it is recommended that RHR-V-8 be repaired during R25 which aligns with the divisional outage schedule. Lube and inspect per WO 02139431 was performed prior to LLRT testing. This is acceptable preconditioning because 1) it was not performed with the intent of biasing the test results and 2) it was a normal maintenance activity. Preconditioning is normally not performed prior to LLRT. <I> **** Actions Taken **** Notifed shift manager Discussed with Engineering EOC/OCC. | 02-00-RHR-V-8
393694 | CR | 20190518 |  | 3 | R24LL Need full coverage for Maintenance Procedures |  |  |  | N | NO | <D> **** Detailed Description **** The off shift and only Maintenance procedure writer was contacted at 2130 on May 17 to revise a procedure for Critical Path RHR-V-8 LLRT. An on-shift Operations Procedure writer was able to respond to the emergent procedure revision that was needed. This is a shortfall on the part of Maintenance that when the OCC is staffed, a person should be designated and available to handle any emergent procedure changes. The OCC should have a schedule of Maintenance personnel, with their pagers / cell phone numbers assigned to handle any emergent procedure revision needed. <I> **** Actions Taken **** Notified Supervision. Also Kudos to Operations for responding and assisting with the emergent procedure revision. <N> Close to trending R24LL for Maintenance. No actions required at this time.
393695 | CR | 20190518 |  | 4 | Clemco CMS-2 CO Meter Over High Flow Limit | N | N |  | N | NO | <D> **** Detailed Description **** The CO monitoring instrument used to test breathing air, currently on the T501' east end, is receiving a higher than allowed flow rate. Actions to reduce the flow rate to the instrument are urgently needed to support the continuation of dust blasting on LP turbine and other components. Info on the instrument can be found in HPI-15.5. This is not a permanent Plant Equipment issue but is an impact to the outage work schedule. <I> **** Actions Taken **** generate this CR and WR to support replacement of instrument tubing or installation of a properly sized flow regulator. Suggest I&C support to HP to resolve this condition. Notified OCC much earlier. <N> **** Equipment Description **** T501 east end near dust blasting equipment
393696 | CR | 20190518 |  | 4 | E-TR-6/63 Nitrogen Pressure Low | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-6/63 Nitrogen pressure is low out of spec. Normal pressure is 0-4" psig and current pressure is 0 psig. Please add N2. <I> **** Actions Taken **** Talked to the CR and EOC | 02-00-E-TR-6/63
393697 | CR | 20190518 |  | 4 | Air flow to Carbon Monoxide monitor too high | N | N |  | N | YES | <D> **** Detailed Description **** A carbon monoxide (CO) monitor was installed in conjunction with the Bullard air line filter at the sand blasting area on TG 501â€™ East. This is per HPI-15.5, but the flow rate to the CO monitor was not within the procedure specified range. Consider using a different sized tubing that is rated for at least 125 PSI, or a device to regulate flow rate to the CO monitor to be within procedure direction. <I> **** Actions Taken **** Discussed with supervision and OCC. <N> **** Equipment Description **** TG 501' sand blasting area Bullard air line filter.
393698 | CR | 20190518 |  | 4 | E-TR-M3 Neutral (H0) bushing was discovered to be chipped | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of the diagnostic testing for E-TR -M3 a chip was discovered in the H0 bushing. The diagnostic for the bushing tested satisfactory but it is recommended by BPA to put some glyptol paint on the bushing. BPA has the glyptol to repair patch the bushing surface. This has no impact on the operation of E-TR-M3 based on the diagnostic testing performed under WO 02109236-01. The purpose of this CR is to document the condition and monitor the bushing until it is replaced. Glyptol will be put on the bushing under the M3 Diagnostic testing WO. See EDMS for pictures. | 02-00-E-TR-M3
393699 | CR | 20190518 | CAQ | D | E-B0-1B float current not restored to less than 0.2 amps | Y | Y |  | N | YES | <D> **** Detailed Description **** 1.8.6.1.O requires a condition report see LCS basis. WO 02119476 to investigate arching in E-PP-7A. Temporary power was not provided to the chargers during the maintenance. The 24V charger and battery were inoperable to perform the maintenance. The battery remains inoperable pending restoring the battery float voltage to within specification. Partial ESP-BAT-W101 will be performed again <I> **** Actions Taken **** Informed electrical supervisor, engineering, and Shift Manager, and the OCC. <N> E-B0-1B previously declared inoperable for E-PP-7A work. T19-FOB-E-PP-7A-001. CR satisfies LCS 1.8.6.1.O. | 02-00-E-B0-1B
393700 | CR | 20190518 |  | 3 | R24LL: TSP-CONT/ISOL-B501 section 7.2 procedure enhancement | N | N |  | N | NO | <D> **** Detailed Description **** R24 TSP-CONT/ISOL-B501 section 7.2 procedure enhancement Section 7.2 â€“ Step 7.2.12 key 56 not 58, Step 7.2.25 key 36 â€“ this also needs to be updated in section 5.2 Add a note â€“ If SOP-RPS-BYPASS has been completed no half scrams will occur. Change all the cautions to half scram may occur <I> **** Actions Taken **** write this cr
393701 | CR | 20190518 |  | 4 | Foreign materials found on TO-HX-1A tubesheet | N | N |  | N | YES | <D> **** Detailed Description **** During TO-HX-1A as found inspection under WO 02111477, some corrosion products were found on the inlet/outlet tubesheet of the heat exchanger. The foreign materials were retrieved and the heat exchanger will be cleaned as planned. This is for trend only. <I> **** Actions Taken **** Initiated this CR. <N> **** Equipment Description **** T501 | 02-00-TO-HX-1A
393703 | CR | 20190518 |  | 4 | Yellow Caution tag on ground inside PA | N | N |  | N | NO | <D> **** Detailed Description **** While walking near vehicle access gate, noticed a yellow Caution tag on the ground. One side said "Handrail only". Notified supervisor and nerby security officer, who picked up and looked at other side of tag - blank. <I> **** Actions Taken **** notified supervisor and security officer.
393704 | CR | 20190518 |  | 4 | (QA) Not all Phase 2 protection scheme found hanging | N | N |  | Y | NO | <D> **** Detailed Description **** As part of walkdown in the Main Control Room a Quality Auditor identified the H13-P618 panel (RHR B and RHR C logic panel) was not protected per Phase 2 of the Shutdown Safety Plan. In addition, protection scheme was found not hanging for MC-8B and MC-8BA room. Operations immediately rehung protection scheme and no work is known to have occurred on the equipment. The potential, however, was there to work on the â€œprotectedâ€ equipment and impact the reliability of Shutdown Cooling. Shutdown Safety Plan manager verified protection scheme was hanging, including both of these locations, the day before. No known direction to lift this protection scheme or cause of the protection scheme to be lifted is known. <I> **** Actions Taken **** Discussed with Shift Manager and Shutdown Safety Plan Manager. Verified protection scheme re-hung.
393705 | CR | 20190518 |  | 3 | Foreign materials found on TO-HX-1A tubes bundle | N | N |  | N | YES | <D> **** Detailed Description **** During TO-HX-1A bundle inspection under WO 02111477, some foreign materials were found on couple of baffle plates (see EDMS for pictures). The foreign materials look like oil cruds probably because this heat exchanger has been out of service for 2 cycles. Other than that, the bundle is in good condition, the OD side of the tubes are clean and no further cleaning is needed. Recommend action to the system engineer to evaluate the need to remove the cruds. <I> **** Actions Taken **** Discussed with system engineer and EOC then initiated this CR. <N> **** Equipment Description **** t501 | 02-00-TO-HX-1A
393706 | CR | 20190518 |  | 3 | RFW-HX-6B davit arm needs repair | N | N |  | N | NO | <D> **** Detailed Description **** The Davit arm for the manway on RFW-HX-6B needs repair. The arm does not support the weight of the manway for removal, It sags and binds the manway bolts. This was discovered during removal of the manway W.O. 02111387-01 RF24 <I> **** Actions Taken **** initiated cr <N> Ownership of this AR moved back to AR-MNTPLAN as assigned by CRG. Change was a result of a mis-communication. . CR will be corrected under WO 02144867. No other action required.
393707 | CR | 20190518 | CAQ | C | Replacement parts for RRC-FT-14B, 24B reduced qualified life |  |  |  | N | NO | <D> **** Detailed Description **** I&C craft identified that the replacement transmitters intended for installation at RRC-FT-14B and RRC-FT-24B (WOs 02087668, 02087672) appeared to be used and not new. This is of concern because these transmitters have a qualified life of 25 years (per QID 156009-01) and these replacement transmitters (UTCs 553297, 553296) may not have their entire qualified life remaining. A records search identified that they indeed were removed from the plant in 1993 due to a Part 21 notification (ref. NRC Bulletin No. 90-01). It is probable that the parts were sent to the OEM for refurbishment at that time but this has not yet been confirmed. This was a good catch by the I&C craft. Please assign to system engineering for resolution. <I> **** Actions Taken **** Discussed with I&C shop, informed EOC <N> Discussion with EQ engineer indicates that the parts under discussion are acceptable for installation. After they are installed, the EQ engineer can process the AR-SMS to change the PM late dates. | 02-00-RRC-FT-14B,02-00-RRC-FT-24B
393708 | CR | 20190518 |  | 4 | Craft alerted op's to report a touched valve. |  |  |  | N | NO | <D> **** Detailed Description **** Craft electricians supporting AC bucket work on the 471" leval of the reactor building where de-mobing the work area with a push cart. While maneuvering through a tight corner, one worker inadvertantly brushed up against a peice of plant equipment. Relizing the componant was a valve.(PSR-V-area with a push cart. While manuvering through a tight and contacted op's. <I> **** Actions Taken **** Stopped, contacted Op's to come to the area and asses the valve for possable mis- positioning. Operations validated that The valve had not been manipulated. The crew was coached to reinforce the expectation for identifying hazzads prior to traversing throuogh the plant. Craft supervisor reinforced the workers positve behavior.
393709 | CR | 20190518 |  | 4 | FM found in A circulating water train inlet to Condenser |  |  |  | N | YES | <D> **** Detailed Description **** A Health physics technician noticed an aerosol can floating in A circulating water train inlet to Condenser below CW-V-2A during inital entry survey <I> **** Actions Taken **** Reported to Project Manager <N> **** Equipment Description **** T443 B7/7.7 | 02-00-CW-V-2A
393710 | CR | 20190518 |  | 4 | Report Only |  |  |  | N | NO | <D> **** Detailed Description **** Employee working in the Condenser, 471' Heater Bay, was relocating Partition Plates and pinched their Right Ring Finger between two Plates. Employee notified their Foreman and continued working for the next hour in the CA. When they took their Gloves off while Doffing they noticed slight discoloration to the affected Ring Finger. <I> **** Actions Taken **** Employee and Foreman reported to WPS Safety for evaluation. Employee had full range of motion in Finger, minor discoloration and no pain without squeezing affected area. All WPS and EN notifications made and CR generated. No treatment required. This is a Cautionary Report Only.
393711 | CR | 20190518 |  | 4 | R24LL RFW feed pump clearance change requested |  |  |  | N | NO | <D> **** Detailed Description **** An R21 LL identified moving the work associated with PM 00023951 and 23950 for RFT governor actuators to local tags per I&C request. This was performed in this method for R22 and R23 as well. For R24, I&C has requested moving the scope of work back to a danger tag . This was identified during task preparation walkdown during R24 resulting in CORC rework (no clearances have been hung yet for this work). Not a tagging issue. CR written to document this is the preferred method for I&C for this PM for future outages to prevent future rework. <I> **** Actions Taken **** Tags moved from local back to danger. Same clearance boundaries will be copied and used for future outages.
393712 | CR | 20190518 |  | 4 | MT-CRA-1 trip. | N | N |  | N | YES | <D> **** Detailed Description **** MT-CRA-1 stopped functioning while preparing for lift. <I> **** Actions Taken **** Crane placed in safe condition. OCC notified. Whiting notified and in route to site. <N> **** Equipment Description **** MT-CRA-1
393713 | CR | 20190518 |  | 4 | BS-MANWAY-4/3 deteriorated | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02139394 BS-MANWAY-4/3 S5 LEAK the manway was opened, the gasket removed, and mating surfaces cleaned. Inspection from the craft discovered of the manway cover and manway sealing surfaces are deteriorated in several areas. . See EDMS for pictures <I> **** Actions Taken **** Notified Mechanical management, Engineering, OCC, and initiated CR and WR <N> **** Equipment Description **** 471 TG Heater Bay | 02-00-BS-MANWAY-4/3
393714 | CR | 20190518 |  | 4 | MT-ELEV-4 | N | N |  | N | YES | <D> **** Detailed Description **** elevator received a fire alarm? as reported to the SSS by the attendant. upon inventigation, the PLC had no fault codes present and showed the 441 front door open. attempted fault reset, and computer reset per sop, with no result. tried to use the FB key to take manual control and shut door on 441 and move elev manually with no success <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-MT-ELEV-4
393715 | CR | 20190518 |  | 4 | HD-V-31B failed the as/found freedom of movement check. | N | N |  | N | YES | <D> During performance of PPM 10.2.99 under WO# 02111314-01 HD-V-31B failed the as/found freedom of movement check. Steps are provided in this WO to remove packing and repack as required to determine the cause of failure. After packing was removed the valve stroked freely with no indication of binding. Repack instructions and final PPM -10.2.99 inspections are covered in this WO# 02111314-01 and no further actions are required. This CR is generated for tracking only. <I> CR generated for tracking. <N> TG 503" CR at INPROG. Approved CR & moved to SRO for OPS Review. | 02-00-HD-V-31B
393716 | CR | 20190518 | CAQ | D | RHR-V-104 ALARA | N | N |  | N | YES | <D> **** Detailed Description **** RHR-V-104 is a manually operated valve overhead in the RB 548 valve room. It is very difficult to operate due to tight packing. Operation requires multiple operators to complete the RHR/FPC cross-time in a timely manner due to fatigue/heat stress. The valve is operated via a ladder, which induces additional risk due to fatiguing an operator in an elevated position. Additionally, the dose rates near this valve were about 10 mrem/hour during R24. It would reduce dose and improve safety for multiple operators if the valve packing was adjusted to allow for smoother operation in the future. <I> **** Actions Taken **** Documented condition in CR and WR for adjustment. | 02-00-RHR-V-104
393717 | CR | 20190519 |  | 4 | Fender Bender in a Parking Lot |  |  |  | N | NO | <D> **** Detailed Description **** During the afternoon of 5/18, a fender bender occured in a parking lot (within the OCA, but the parking lot where the incident occured is unknown at this time). Vehicles involved were personal vehicles and no EN property (structures or vehicles) were involved. All personnel are uninjured and minor damage occured (paint scratches / exchanges on bumpers). Event occured when both vehicles were backing out of their parking spots. <I> **** Actions Taken **** Generated CR. Informed Control Room via Operations Outage Manager. Coached individuals involved.
393718 | CR | 20190519 |  | 3 | Incorrect procedure revision utilized during work |  |  |  | N | NO | <D> **** Detailed Description **** During Work Package review of CRDM exchange work order tasks WO 02111975-24 thru 43, it was noted that PPM 10.5.7 attachment 8.1 revision 18 was planned for each CRD replacement and the â€œReview of Hold Points Being Completedâ€ were signed by QC and ANII. PPM 10.5.7 revisions 19 and 20 have been processed since originally planned without any updating for replacement to the current revision 20 Attachments 8.2 requiring new QC and ANII signatures. SWP -PRO-01, step 4.3 notes, â€œWhere procedures have been printed for work packages in support of a specific work activity, subsequent new revisions with changes that do not impact the work scope of the activity may be reconciled, and the procedure that is in the package may then be initialed with an accompanying comment that it does not need to be reprinted because the work being performed is not affected by the revision.â€ <I> **** Actions Taken **** Having verified with the CRDM exchange Project Manager that indeed the work performed is not affected by the change, the work orders will be reconciled once work is complete. This action is to document the process is per SWP-PRO-01 procedural guidance and one action required for adding the annotated comment and referencing the CR#. No other impact other than reconciliation after work is needed at this time.
393719 | CR | 20190519 |  | 3 | Portal J Component location errors |  |  |  | N | NO | <D> **** Detailed Description **** Portal J listed two components on the 522 when they were actually in the B RPS room on the RW 467. RHR-42-8A6A and RHR-RLY-80/V64B both were lited as being at the R 522 but also in the RPS 2 room. <I> **** Actions Taken **** please correct the location on these in portal J.
393720 | CR | 20190519 |  | 3 | R24LL: Create new section in SOP-LO-OPS |  |  |  | N | NO | <D> **** Detailed Description **** Create a procedure in SOP-LO-OPS to use the opposite side (A or B) pump to pump down the sump of the RFT. In the event of a bus outage or failed pump. Also add these fun facts. The discharge pressure drops from approx 8 pounds to 5 pounds when it starts cavitating. Pumping down the sump takes approx 1 hour. Pumping down the sump of 700 gallons adds approx .2 feet to the dirty oil tank. <I> **** Actions Taken **** document actual data for questions that were asked otr calculated
393722 | CR | 20190519 |  | 4 | MT-CRA-1 will not bridge | N | N |  | N | YES | <D> **** Detailed Description **** MT-CRA-1 Will not bridge in either direction, it appears that the brakes have locked and will not disengage. . WR 29148072 minor work instructions could be utilized for investaging <I> **** Actions Taken **** Initiated CR and WR per Emergent issues manager | 02-00-MT-CRA-1
393723 | CR | 20190519 | CAQ | D | SGT-FN-1A2 operating with SGT-FN-1A1 low flow alarm in | Y | N |  | N | YES | <D> **** Detailed Description **** After transferring RPS-B to the alternate power supply SGT -FN-1A2 was found running with a SGT-FN-1A1 low flow alarm locked in. This is not a normal response to swapping RPS-B to alternate. The low flow alarm cleared when the SGT -EHC-1A1 was placed in PTL to reset the logic. The system was put in a standby lineup per SOP-SGT-SHUTDOWN. <I> **** Actions Taken **** Contacted the EOC, wrote this CR. | 02-00-SGT-FN-1A2
393724 | CR | 20190519 |  | 3 | R24LL: SOP-ELEC-SM3-MAINT procedure change required. |  |  |  | N | NO | <D> **** Detailed Description **** SOP-ELEC-SM3-MAINT references E-CB-PP-3C/6 which is incorrect. The correct EPN is E-CB-PP-3CC/6. This was verifed through SOP-ELEC-AC-LU and EWD-46E-311. <I> **** Actions Taken **** Initiated this CR and notified the Ops procedure group supervisor.
393725 | CR | 20190519 |  | 4 | Clearance required revision due to siphon path potential |  |  |  | N | NO | <D> **** Detailed Description **** During task preview/print reviews prior to briefing and authorizing field hang L-RHR-V-4C-001, EO identified potential siphon pathway with â€œNO TAGâ€ valve RHR-V-167C through the valve bonnet which could occur during valve stroking. This clearance incorporates both as-found, as -left, and valve repairs. RHR-V-167C was on the clearance as it was identified as an interference valve that would need to be removed during valve disassembly. However, the suction strainer isolation is scheduled after the AF MOV valve stroke which was different than the original schedule when the clearance was originally constructed. EO brought the question to production supervision. The potential leakage path was validated by the production center and valve team. <I> **** Actions Taken **** Clearance was revised to remove the â€œno- tagâ€ valve from the As-Found MOV testing. This is a level 4 tagging event perOI-12. Notified SM.
393728 | CR | 20190519 |  | 3 | EC TMOD removed without correct approvals per PPM 1.3.9 |  |  |  | N | NO | <D> **** Detailed Description **** EC TMOD 17086 restoration work order task (02123616-01)was taken to completed prior to the R TMOD OPS milestone being signed as required by PPM 1.3.9 and PPM 10.1.27. During R24 13 temporary modifications are being restored and all require this approval prior to restoration. <I> **** Actions Taken **** Contacted Operations for EC TMOD 17086 for the correct approval.
393729 | CR | 20190519 |  | 4 | sam9 |  |  |  | N | NO | <D> **** Detailed Description **** top detector fault <I> **** Actions Taken **** out of service, cr /wr writen norityed supervison <N> **** Equipment Description **** HP-EQ- 42998 TB 501 WEST
393730 | CR | 20190519 | CAQ | D | TEA-SR-26 Heat Trace not working correctly |  |  |  | N | YES | <D> **** Detailed Description **** The TEA-SR-26 heat trace lost power in the SL/31 outage. When the power was restored the heat trace would not rise above 80 degrees Fahrenheit. The temp is normally 100-114 degrees. We can not achieve a valid sample if the heat trace doesn't return to above 100 degrees. I&C will need to investigate why the heat trace is stuck at 80 degrees. Chemistry can not close work order 02079551-24 from the SL/31 outage until we can return TEA-SR-26. Chemistry is currently sampling from a plenum on the TG roof which is not the safest way to take compensatory measures. Did the loss of power to the heat trace cause it to set itself to a default setting and it needs to be reset? <I> **** Actions Taken **** Notified Shift manager, Chemistry supervision, chemistry specialist The breaker was open for the heat trace. This was part of the SH6 / PP-7A restoration and had not yet been performed. The breaker was reclosed and the power to the heat trace has been restored along wiht the sample rack. There is no DNC. <N> **** Equipment Description **** TEA-SR-26 TG 525' | 02-00-TEA-SR-26
393731 | CR | 20190519 |  | 4 | TOA-TIS-22A will not change state to allow pump operation | N | N |  | N | YES | <D> **** Detailed Description **** TOA-TIS-22A will not change state to allow TOA-P-2A1 to run in AUTO. The red light is continually lit even when the setpoint is adjusted past the current temperature. <I> **** Actions Taken **** Shifted to TOA-P-2A2 running to provide airwash <N> **** Equipment Description **** TG 501 west | 02-00-TOA-TIS-22A
393733 | CR | 20190519 |  | 3 | EDR-RMS-P/19 EPN at STATUS REMOVED |  |  |  | N | NO | <D> **** Detailed Description **** The EPN "EDR-RMS-P/19" is at STATUS REMOVED in portal J. EDR-RMS-P/19 is S35 on 02G11-05,14,3 and is still installed in the plant. This EPN has been categorized incorrectly and needs to be taken to the correct status. This makes the status of this EPN INACTIVE in ESOMs.
393734 | CR | 20190519 |  | 3 | Tubing installed under different work instructions |  |  |  | N | NO | <D> **** Detailed Description **** After completing work order 02116778-01, it was discovered that all of the tubing was installed on RFW-CP-RFT/1B. The majority of the tubing installation was to be installed in task 17 of this work order. The work instructions did not delineate where the tubing would to start or stop specifically. The material was all listed under the 01 task. Work order 02116076-01 needs a revision to specify the amount of tubing that will be installed specifically in this work order. The instructions need to refer the individuals to the task that the tubing will be installed in completely. This is not considered rework. <I> **** Actions Taken **** Task 17 will be performed and worked to review and verify the tubing has been installed correctly per EC 114838.
393735 | CR | 20190519 | CAQ | C | RFW-V-10B As-Found leak rate exceeds admin limit | Y | N |  | N | YES | <D> **** Detailed Description **** RFW-V-10B had an as-found leak rate of 3,740 sccm which exceeds the admin limit of 2125 sccm. RFW-V-10B serves as a barrier for both Primary Containment integrity and Secondary Containment Bypass leak limits. <I> **** Actions Taken **** Notified LLRT SRO, EOC Contingency WO 02085916, RFW-V-10A HARD SEAT INSTALLATION Pllanned. RFW-V-10B is operable. Final testing results pending. See INOP sheet. <N> **** Equipment Description **** drywell 512'' Az 345 | 02-00-RFW-V-10B
393736 | CR | 20190519 | CAQ | C | RFW-V-32B As-Found Leak Rate exceeds admin limit | Y | N |  | N | YES | <C> Re-opened at the request of T. Dion to add WO 02155363 and check mark to completion required box, then taken back to complete <D> **** Detailed Description **** The As-found LLRT test of RFW-V-32B has exceeded its admin limit because test pressure could not be obtained. REF WO <I> **** Actions Taken **** Notified LLRT SRO, EOC Contingency WO 02085917 for R24 RFW-V-32B hard seat Installation planned. <N> **** Equipment Description **** Stm Tunnel 504 | 02-00-RFW-V-32B
393737 | CR | 20190519 |  | 4 | P840.A4.8-6 will not reset | N | N |  | N | YES | <D> **** Detailed Description **** Alarm is clear but will not reset. Likely needs a new card. Card ID 304341 Rev 1. <N> **** Equipment Description **** MCR p840
393740 | CR | 20190519 |  | 3 | R24 LL Dosimetry telemetry issues |  |  |  | N | NO | <D> **** Detailed Description **** The telemetry system used by RP to monitor worker dose and dose rate remotely experienced issues during the outage that delayed work. Each issue was resolved to allow work or contingencies were implemented to provide job coverage. Issues were experienced during job setup and not during job coverage activities. RP to evaluate telemetry system equipment, software, process and procedures for improvements. <I> **** Actions Taken **** SOM and RPM notified.
393741 | CR | 20190519 | CAQ | D | FP-HS-TGB40 gated wye leakage | N | N |  | N | YES | <D> **** Detailed Description **** FP-HS-TGB40 gated wye leakage due to one of the ball valves not functioning/ seating properly Need to replace gated wye to FB cart in TG 441 turnout station <I> **** Actions Taken **** Informed FP engineer Replaced gated wye with one from TG 441 turnout Non-essential fire protection. | 02-00-FP-HS-TGB40
393742 | CR | 20190519 | CAQ | D | SW-V-153T would not operate | Y | N |  | N | YES | <D> **** Detailed Description **** SW-V-153T would not operate more than 1/2 to 1 full turn. Cycled the valve several times and would not operate to the full open position. Could not completely hang O-RRA-CC-14 -001. | 02-00-SW-V-153T
393743 | CR | 20190519 |  | 4 | Request removal of R-DOOR-R413 for WO 02111406 |  |  |  | N | YES | <C> MRT Change from CAQ to NON-CAQ. <D> **** Detailed Description **** Request removal of R-DOOR-R413 to allow access to RRA-CC-10 for clearance hang and for the subsequent maintenance. Scaffolding is in place but the doors will not open fullly preventing access. This is due to a pipe which runs close to the door. | 02-00-R-DOOR-R413
393744 | CR | 20190519 |  | 4 | RB 501 Scupper Overflow due to RRC-RV-15B Lifting | N | N |  | N | YES | <C> MRT Change from CAQ to NON-CAQ. <D> **** Detailed Description **** While hanging clearance O-RRC-P-1B/R24-001, operators on the RB 501 noticed water backing up and out of a scupper shortly after the main control room remotely closed RRC-V -16B. Investigation showed this was due to RRC-RV-15B lifting due to CRD system pressure buildup in the piping between RRC â€“V-16B and RRC-V-8B, a valve known to leak-by. In the future, this clearance should be hung in conjunction with the CRD system shutdown in order to prevent pressure buildup in the system due to leakby. Shutting down the CRD system is called out in the clearance order hang instructions for O-RRC-P-1B/R24-001, but not until after this clearance is hanging, which is too late to prevent relief valve lifting. <I> **** Actions Taken **** Informed the CRS and Shift Manager. Dispatched laborers to contain the water on the floor of RB 501. Opened MWR-V -120 to drain downstream piping from scupper. Attached a hose to drain piping to EDR via RRC-V-92 and RRC-V-86B. Initiated C-RRC-V-8BDRAIN-001 clearance to caution tag open RRC-V-92 and RRC-V-86B in order to prevent RRC-V-15B from lifting. Re-closed MWR-V-120. Added clearance notes to O-RRC-P-1B/R24-001 to warn of the potential for lifting RRC-RV-15B (relief valve). | 02-00-RRC-V-8B
393745 | CR | 20190519 | CAQ | C | RFW-V-10A has exceeded its LLRT admin limit | Y | N |  | N | YES | <D> **** Detailed Description **** The As-Found LLRT test of RFW-V-10A was performed in accordance with TSP-RFW/X17A-B801. The results of the LLRT indicate that RFW-V-10A has exceeded its admin limit because test pressure could not be achieved. The admin limit for this valve is 2125 sccm. <I> **** Actions Taken **** Notified LLRT SRO / EOC Contingency WO 02085916 R24 Hard seat replacement planned for repairs. RFW-V-10A is operable pending final testing results. See inop sheet. <N> **** Equipment Description **** C512 AZ5 | 02-00-RFW-V-10A
393746 | CR | 20190519 |  | 3 | R24 Lessons Learned |  |  |  | N | NO | <D> **** Detailed Description **** Problem Statement: While performing WO 02122003-01 (Isophase link inspections), it was discovered that there was no data sheet in plannerâ€™s attachment 5 to document Main to Aux bus links. Also, this task should be broken out so that the each link has its own task. This will help with the task implementation and scheduling. <I> **** Actions Taken **** Contacted planning to generate a data form to document the recordable data for the main to aux bus links. . <N> Data sheet has been created. No further actions required.
393747 | CR | 20190519 | CAQ | D | RRC-CB-RPT4B pantograph assembly requires replacement | Y | N |  | N | YES | <D> **** Detailed Description **** During MOC Switch Assembly Refurbishment under work order# 02111439 the pantograph was found to be in rough shape and would not operate as designed. After cleaning the inside of the holes ov the movable blocks they were found rough and the pins on which the blocks slide on were rough and possibly bent. The movable blocks were unable to be on the pins fully without binding. A new pantograph assembly was ordered and installed in E-SH-12 (Unit 5) <I> **** Actions Taken **** Replaced pantograph assembly | 02-00-RRC-CB-RPT4B
393748 | CR | 20190519 |  |  | Planning impact |  |  |  | N | NO | <D> **** Detailed Description **** OSCR 392836 was approved by Outage Scope Panel on 5/7 to add additional scope to the TR-M window. The OSCR was missing an assignment to planning to ensure the WO was updated to plan the additional work scope. Planning resources were impacted today by an unnecessary emergent request because this outage window will be closing soon and the work needed planned to ensure it was worked prior to closing the window . No further actions required, this CR is to document the impact. 4/Trend R24LL <N> Cancelling at request of originator
393749 | CR | 20190519 |  | 4 | Potable Water line break | N | N |  | N | YES | <D> **** Detailed Description **** In an attempt to supply potable water the the TB 441' for condenser tube cleaning, a large water line leak was noticed outside near the transfer yard after opening PWC-V -417 <I> **** Actions Taken **** PWC-V-417 was closed to stop the leak <N> **** Equipment Description **** Outside near the transformer yead | 02-00-PWC-V-417
393751 | CR | 20190519 |  | 4 | TMU-V-1A Cycled Open then Shut Unexpectedly | N | N |  | N | YES | <D> **** Detailed Description **** While lining up to start TMU-P-1A per SOP-TMU-START, when TMU-RMS-V/18A was taken to OPEN per step 5.8.1.d, TMU-V-1A (pump discharge valve) was observed to cycle full open then shut. Confirmatory effects of this were observed on TMU flow going to zero, running TMU pump amps rising to 95 and TMU header pressure dropping to 60 psig. After confirming that the discharge valve had shut and the pump shaft was stationary, the pump was then started with no other issues. | 02-00-TMU-V-1A
393752 | CR | 20190519 |  | 4 | TMU-V-1C Failed to Fully Shut Following Pump Shutdown | N | N |  | N | YES | <D> **** Detailed Description **** While shutting down TMU-P-1C per SOP-TMU-SHUTDOWN, TMU-V-1C never indicated fully shut per step 5.7.3.c and the pump was observed to rotate backwards. Manual control was taken of TMU-V-1C and the valve was fully shut, allowing TMU-P -1C to stop rotating. Recommend TMU-MO-1C be adjusted to fully shut the valve. | 02-00-TMU-MO-1C
393753 | CR | 20190519 |  | 3 | MT-CRA-1 Operations Documentation | N | N |  | N | NO | <D> **** Detailed Description **** Documentation on operation of MT-CRA-1 after upgrade of the main hoist variable speed drive motor needs to be included in training or orientation of crane operators qualifying to operate the crane. <I> **** Actions Taken **** Conducted orientation with R24 crane operators on changes to crane operation since main hoist upgrade.
393755 | CR | 20190519 | CAQ | D | TSW-RIS-5 alarming frequently | N | Y |  | N | YES | <D> **** Detailed Description **** TSW-RIS-5 is frequently alarming on low flow. Had chemistry flush the SR which didn't help. This seems to have been caused when we swapped running TSW pumps . <I> **** Actions Taken **** Wrote CR, attempted to cleara alarm by flushing SR. Entered ODCM for TSW-RIS-5 OOS. . O19-TSW-RIS-5 -001 Sample rack flused - declared operable at 11:45. There is no longer a DNC. Reference above sheets for more information. | 02-00-TSW-RIS-5
393756 | CR | 20190519 |  | 3 | TB 471 Heater Bay Cleanliness |  |  |  | N | NO | <D> During a walkdown of the 471 heater bay it was noted that work groups do not appear to be cleaning up during their work or upon completion of work. See attached photos in EDMS, Discussed HP items with technicians. No workers observed actively workinging at locations pictured <I> Initiated CR. <N> CR at INPROG. Approved CR & moved to SRO for OPS Review. Williams Plant Services. Work was in-progress with crew a break when pictures were taken. Pipefitters were in the process of grinding out 28" pipe and elbow when they took a work break (scheduled and heat management driven). Later in the shift when all of the grinding was completed the work area was cleaned and managed properly. Craft were coached on the requirements for in-process house- keeping and accepted coaching. No additional actions are required at this time. This CR can be closed.
393757 | CR | 20190519 |  | 4 | LLR24 |  |  |  | N | YES | <D> **** Detailed Description **** When isolating RRC loop B for clearance O-RRC-P -1B/R24-001, Operations lifted RRC-RV-15B. This was because of an identified issue with RRC-V-8B not fully isolating. This was not known to CR staff when isolating the loop. The result was CRD water flowing onto the ground on the RB 501. <I> **** Actions Taken **** A Caution C/O was placed on RRC-V-16B to inform the operator that closing this valve may lift a relief valve. <N> **** Equipment Description **** RB 501 | 02-00-RRC-V-8B
393758 | CR | 20190519 |  | 3 | Sealing Surface Erosion on TO-HX-2A | N | N |  | N | YES | <D> **** Detailed Description **** During the inspection of the turbine oil heat exchangers TO-HX-2A and 2B under work order 02078413, an eroded section of the 2A reversion chamber flange sealing surface was found to be eroded. See the pictures in the EDMS folder. The eroded section is about two inches long and greater than two thirds of the sealing surface in this area is eroded away. The reversing changer will either have to be replaced or the eroded area will have to be built up and machined before the heat exchange can be reassembled. <I> **** Actions Taken **** Discussed the replacement/repair with the maintenance supervisor. Additional planning will be required. <N> Work instructions have been changed as required. No further actions. | 02-00-TO-HX-2A
393759 | CR | 20190519 |  | 4 | Need additional scaffolding for RRA-CC-10 work WO 02111406 |  |  |  | N | YES | <D> **** Detailed Description **** RRA-CC-10 is not completely accessible from the access doors. A tall extension ladder needs to be installed inside the MCC room (MCC-8BA) to facilitate access. This will allow cleaning of the cooling coil per WO 02111406 <I> **** Actions Taken **** Informed Operations Production Manager and Mechanical Maintenance | 02-00-RRA-CC-10
393760 | CR | 20190519 |  | 4 | Electrical Problem SL-11, SL-21 | N | N |  | N | YES | <D> **** Detailed Description **** Ground alarms SL-11 and SL-21, E-RLY-50N/T1/11 arching additionally a problem was noted with the A phase in the TLC-1, note SL-11 and SL-21 are cross tied. Investigate check in spare cubicle on all phases. <I> **** Actions Taken **** Informed SM, electrical supervisor, and supervision. | 02-00-E-TR-1/11
393761 | CR | 20190519 |  | 4 | E-CB-2/21 finger clusters | N | N |  | N | YES | <D> **** Detailed Description **** while racking out E-CB-2/21 breaker, 2 fingers on finger cluster of B-phase dislodged from cluster. <I> **** Actions Taken **** removed old finger cluster and installed new finger clusters per supervisions direction. <N> **** Equipment Description **** E-CB-2/21 in E-SM-2 TW 471' | 02-00-E-CB-2/21
393762 | CR | 20190519 |  | 3 | Evaluate The Use Of Ultrasonic Transducers On CISP |  |  |  | N | NO | <D> **** Detailed Description **** Please evaluate the use of multiple immersible ultrasonic transducers on the CISP during outages to reduce general area dose rates due to contamination accumulation on sections that sit below cavity water level. These transducers could hang from the side of the CISP and continually supply decontamination efforts while IVVI inspections are ongoing. This could potentially be a huge savings in personnel exposure for multiple reason including, IVVI inspections, less decon required and lower dose rates on the CISP during removal from the cavity. This would additionally lower exposures during CISP removal from the DSP prior to outages and will decrease general area dose rates while the CISP is staged on the refuel floor prior to installation into the cavity and once again following its removal from the cavity. <I> **** Actions Taken **** Informed RP Supervision of this ALARA suggestion.
393764 | CR | 20190519 |  | 3 | Late entries in eSOMS 4 temps, 2 in house, E shop |  |  |  | N | NO | <D> **** Detailed Description **** Late entries for temps were due to the watchbill did not match the schedule worked. The 2 in house were for 5/13/19. <I> **** Actions Taken **** eSOMs have been correct by shop tech support. Temp schedule were changed just prior to the start of the outage and eSOMs was not updated.
393765 | CR | 20190519 |  | 4 | R24 LL CR â€“Dedicated HP/DSR support for Condenser Inspection |  |  |  | N | NO | <D> **** Detailed Description **** Main Condenser inspections continues to be delayed due to requirement for multiple organizations be aligned to support engineering inspections. Similar issues arose in R23 but the coordination issue has increased in R24. Recommend for R25 dedicated resources are planned for COND-HX-9 steam side inspections. This will shorten the window for discovery work and allow more margin for outage resources. <I> **** Actions Taken **** Nightshift PM is working dutifully to align resources so engineering can finish false floor inspections and complete COND-HX-9 steam side initial inspections for R24. <N> **** Equipment Description **** COND-HX-9 STEAM INSPECTIONS
393766 | CR | 20190519 | CAQ | D | CRDM leaking through o-ring. | Y | N |  | N | NO | <D> **** Detailed Description **** During CRDM exchange, CRDM 14-55 was observed to have excessive leaking through the o-ring, 40 DPM. This will require pulling the mechanism out to replace the o-ring. <I> **** Actions Taken **** Wrote the CR, discussed with Undervessel team and RP for support. This does not affect the operation of the CRDM as this is part of the outage scope. This CR is to document the o-ring issue and will be replaced as part of maintenance. No further action required.
393767 | CR | 20190519 |  | 3 | SOP-CRD-HCU procedure change needed. |  |  |  | N | NO | <D> **** Detailed Description **** SOP-CRD-HCU procedure change needed. Step 5.7.33 needs removed. CRD-V-107/XXX is isolated from the Reactor by CRD-V-101/XXXX and CRD-V-102XXXX as such it does not require a dedicated operator per PPM 3.4.1. This action is accomplished by step 5.7.9 to establish dedicated operator untill tags are hung on CRD-V-101/XXX and CRD-V-102XXXX.
393768 | CR | 20190519 |  | 4 | Heat damage found on E-RLY-81T1 | N | N |  | N | YES | <D> **** Detailed Description **** While performing the calibation on E-RLY-81T1 in WO#02111904-01 there was excessive heating found on several points of the circuit board. The relays as found and as left readings were all found to be in tolerance. Had engineering evaluate the condition of E-RLY-81T1 for acceptability and it was determined that this relay needs to be replaced. Also recomended by engineering to have relay sent to the vendor for further evaluation based on it only being in service for 4 years. <I> **** Actions Taken **** Consulted engineering, contacted supervisor and operations, and wrote CR. <N> **** Equipment Description **** E-CP-H13/P842 | 02-00-E-RLY-81T1
393769 | CR | 20190519 |  | 4 | E-CB-CTA floor tripper cam is too high. | N | N |  | N | YES | <D> **** Detailed Description **** While racking in E-CB-CTA per SOP-ELEC-BKR-OPS per step 5.13.19 it was noticed that the open floor tripper cam was much higher than the closed tripper cam. Request electrical maintenance investigate and adjust as necessary. This needs to be resolved before closing breaker. | 02-00-E-CB-CTA
393770 | CR | 20190519 |  | 4 | RFW-FCV-2A packing has degraded | N | N |  | N | YES | <D> **** Detailed Description **** Diagnostic testing per WOT 02079876-01 has determined that the packing has degraded on RFW-FCV-2A. Required gland stress cannot be achieved without affecting normal valve operation. Recommend repacking. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** T 484' F2/7.0 | 02-00-RFW-FCV-2A
393771 | CR | 20190519 |  | 3 | Tasks not properly statused in syntempo |  |  |  | N | NO | <D> **** Detailed Description **** SO tasks are not being timely statused in syntempo and it is masking predecessors for work, costing time for people to individually ensure that tasks are completed. <I> **** Actions Taken **** Wrote CR
393772 | CR | 20190519 |  | 4 | FO-42-1B3D failed to reclose. | N | N |  | N | YES | <D> **** Detailed Description **** During Ground isolation investigation for SL-11 ground, opened FO-42-1B3D, FO-P-2A, attempted to reset ground. didi not reset, then attempted to reclose and would not reclose. <I> **** Actions Taken **** continued with ground isolation of SL-11. did not find source. wrote CR for FO-42-1B3D not closing. informed OCC and emergent issues of unsucessful ground search. | 02-00-FO-42-1B3D
393773 | CR | 20190519 |  | 4 | R24LL - SDSP Containment Function Shot on Goal |  |  |  | N | NO | <D> **** Detailed Description **** R24LL â€“ The Shutdown Safety Plan (SDSP) credits the Reactor Building (RB) HVAC as one of two secondary containment trains of ventilation during the Control Rod Drive Mechanism (CRDM) Water Inventory Control (WIC) work window. During the nightshift activities review by the Shutdown Safety Program Manager, a potential conflict with the SDSP was identified due to the CRDM WIC window extending into nightshift. RB HVAC was scheduled to be unavailable for temporary power installation this evening (5/19/19). As RB HVAC is credited in the Shutdown Safety Plan for the Containment Safety Function during the CRDM WIC window, this results in a conflict. <I> **** Actions Taken **** Notified electrical bus coordinator and OCC. No impact to the station because RB HVAC was not tagged out at the time of the identification of the conflict. Recommend incorporating lessons learned into future revisions of the SDSP. <N> SDSP Rev 0 Minor 2 issued 5/20/19 to alleviate this conflict.
393774 | CR | 20190520 |  | 3 | Update PPM 1.3.57 floor plugs eval mode 4/5 for TS 3.5.2 |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.3.57 Current floor plug evaluation attachment 9.4 describes flood barrier not required for modes 4 and 5. TSTF 542 (Water Inventory Control) now requires ECCS operable in all modes. Pulling more than one floor plug on an operable ECCS system could lead to common mode failure in modes 4 and 5. Recommend re-evaluating attachment 9.4 related to flooding common mode failure for modes 4 and 5 for required operable ECCS pumps. Recommend update to NOTE 2 and NOTE 11 (page 55)to limit the number of floor plug assemblies allowed to be removed to no more than 1 in modes 4 and 5 for operable ECCS pumps.
393775 | CR | 20190520 |  | 3 | Broken EPN label |  |  |  | N | YES | <D> **** Detailed Description **** The EPN label for SW-V-780B is broken and needs to be replaced. See pic in EDMS. RCIC pump room 422' in the overhead next to RRA-FN-6. | 02-00-SW-V-780B
393776 | CR | 20190520 |  | 4 | HD-LS-6BL will not reset | N | N |  | N | YES | <D> **** Detailed Description **** Under WO#02095223-01, the switch plate for HD-LS-6BL was replaced to correct an issue where the switch would not reset with normal level in COND-HX-6B (See CR#332262). While performing as-left calibration of instrument, it demonstrated the same behavior. Suspect that the float mechanism is dirty/sticking. Recommend replacing entire HD-LS-6BL. <I> **** Actions Taken **** Notified supervisor and wrote this CR. | 02-00-HD-LS-6BL
393777 | CR | 20190520 |  | 4 | First Aid |  |  |  | N | NO | <D> **** Detailed Description **** Employee was walking down the corridor to the Dress Out area on 441â€™ TG and brushed their hand against the wall. When the employee reached the Dress Out area they realized they had a superficial scratch on the top of their Left Hand <I> **** Actions Taken **** Employee left the RCA and washed their hands then reported to WPS Safety where a Band Aid was applied. CR generated. All WPS and ENW notifications made
393778 | CR | 20190520 |  | 4 | SS-PCV-4E Valve Packing Friction | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of as found diagnostic testing via Work Order 02052511-01. It was identified that the valve packing friction is low and the valve is sticking. There is currently only an 1/8" of adjustment left on the packing follower which eliminates the possibility of acheiving prefered friction. SS-PCV-4E should be repacked this outage to avoid packing failure and controlling issues. <I> **** Actions Taken **** Discussed with valve team. Notified AOV program owner and wrote this AR. <N> **** Equipment Description **** Turb. 501 B8/11.5 | 02-00-SS-PCV-4E
393779 | CR | 20190520 |  | 3 | R24 LL - PPM 6.5.9 enhancement recommended |  |  |  | N | NO | <D> **** Detailed Description **** PPM 6.5.9 step 4.7.1 is written to verify that a control rod blade (CRB) remains uncoupled from the control rod drive mechanism (CRDM) prior to attempting movement of the CRB to prevent damage to the components should leak by allow the CRB to recouple to CRDM. The procedure has a note after step 4.7.1.b that says that this step assumes the Position Indicating Probes (PIPs) have been re -installed, and that if no indication is noted, that consultation with the undervessel personnel for PIP installation status shoudl be undertaken. This step and procedure assumptions are that a PIP that has been removed to support CRDM work has been re-installed. This set of assumptions pre-cludes moving CRBs if PIPs are not installed/functional. Other methods of verifying the CRB remains uncoupled is not discussed or authorized in the procedure. <I> **** Actions Taken **** Recommend revising procedure to allow alternate means of verifying blade uncoupling in case PIP is not installed/functional. This would allow blade movement to begin as soon as CRDMs torqued, or even in parallel as is done at other sites.
393781 | CR | 20190520 |  | 4 | E-TR-PDP5/B mounts have rusted through | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-PDP5/B, a transformer located under the window in the Wellhouse #2 building (40) has the bolts which attach it to the floor that have completely rusted through and separated. The transformer is currently prevented from falling over by the cables that attach to it. The transformer easily moves on the mount. Please repair. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** Wellhouse #2 building (40) | 02-00-E-TR-PDP5/B
393782 | CR | 20190520 |  | 4 | HD-V-31A has dual indication | N | N |  | N | YES | <D> **** Detailed Description **** HD-V-31A has dual indication. Identified during performance of WO 02070687-01. <I> **** Actions Taken **** Identified in CR/WR | 02-00-HD-V-31A
393783 | CR | 20190520 |  | 4 | HD-V-32D has no indication either in CR or IR-16 | N | N |  | N | YES | <D> **** Detailed Description **** HD-V-32D does not have indication in the Main Control Room or IR-16. Verified bulbs not blown. <I> **** Actions Taken **** Notified CRS. | 02-00-HD-V-32D
393784 | CR | 20190520 |  | 3 | Inspect Main Bus - Insulators, Dampers, Links | N | N |  | N | YES | <D> **** Detailed Description **** While performing WO #02122003-01 (Inspect Main Bus - Insulators, Dampers, links) craft notice a 3/8' chip on a insulator located on inspection point A16 on the A phase on the Isophase bus duct located in the transformer yard. <I> **** Actions Taken **** Craft stop work, notified supervision, OCC and EOC. CR was written <N> **** Equipment Description **** Isophase transformer yard A phase inspection point A16
393785 | CR | 20190520 |  | 3 | Not Meeting ADA Handicap Parking Regulations |  |  |  | N | NO | <D> **** ANONYMOUS CR - Detailed Description **** There is not sufficient handicap parking made available at the nearesst entrance to protected area for all the additional outage personnel. This is actually an ADA Federal Regulation. Please add additional handicap spaces required by federal regulations, duing the outage. <I> **** Actions Taken **** Made Energy Northwest aware of lack of compliance with this CR. <N> ANON CR generated. Reviewed for Safety Conscious Work Environment (SCWE), forwarded to OPS for review. Closing CR to cross referenced CR 393356, as it is same subject
393786 | CR | 20190520 |  | 4 | COND-HX-9 Water Box Coating Degradation | N | N |  | N | YES | <D> **** Detailed Description **** During Engineering as-found inspections of the main condenser water boxes (COND-HX-9) on 05/19/19 large sections of coating have peeled off the interior and smaller section of coatings are missing near the tube sheet to water box interface in the A outlet water box. Additionally, a large section of coating has peeled off of the B outlet water box. There is no significant loss of material in any of these locations, however, continued operation in this condition will begin to erode the water box. Photos are attached to the EDMS. <I> **** Actions Taken **** Notified the EOC System Engineering Manager of the condition. | 02-00-COND-HX-9
393787 | CR | 20190520 | CAQ | D | CRDM leaking through O-ring | Y | N |  | N | NO | <D> **** Detailed Description **** During CRDM exchange, CRDM 38-19 was observed to have excessive leaking through the o-ring after torque, 120 DPM. This will require pulling the mechanism out to replace the o-ring. <I> **** Actions Taken **** Wrote the CR, discussed with Undervessel team and RP for support. This does not affect the operation of the CRDM as this is part of the outage scope. This CR is to document the o-ring issue and will be replaced as part of maintenance. No further action required
393788 | CR | 20190520 |  | 3 | Inspect Aux Bus Insulators & Rigid Links | N | N |  | N | YES | <D> **** Detailed Description **** While performing WO #02122003-06 (Inspect Aux Bus Insulators and Rigid Links) Craft notice several chips missing from the bushing locate on inpection point NC-6 on the C Phase on the Aux bus going to N1 transformer. <I> **** Actions Taken **** Craft stop work notified supervision, OCC and EOC. CR was written. <N> **** Equipment Description **** Aux Bus in Transformer Yard "C" phase at inspection point NC-6
393790 | CR | 20190520 | CAQ | D | RHR-V-4C as-found unseating loads higher than design | Y | N |  | N | YES | <D> **** Detailed Description **** Diagnostic testing on RHR-V-4C identified the as-found unseating loads higher than design. The attached engineering evaluation shows the valve would have performed its design function as required. Acceptance Criteria = 35,464 lbs (actuator ratings) Field Measured unseating loads = 39,108 lbs <I> **** Actions Taken **** R24 WO 02107551 already had actions to address the high unseating loads. | 02-00-RHR-V-4C
393791 | CR | 20190520 |  | 4 | Poor Lighting in Heater Bay |  |  |  | N | NO | <C> Trend to CR 393811 <D> **** Detailed Description **** Industrial Safety: Craft reported inadeqaute lighting in the heater bay making for unsafe working conditions. this issue. Work Requests exist that will support correcting this issue. <I> **** Actions Taken **** Craft reported this issue to the Site Support Contractor Manager, Initiated this CR.
393792 | CR | 20190520 |  | 4 | COND-HX-9 False Floor Initial Entry |  |  |  | N | YES | <D> **** Detailed Description **** Initial inspection of the alpha bay false floor showed cracking stemming from a vertical support. The tips of the cracks were drilled out, but the crack has propogated past the hole. The cracks are near the charlie tubes near the 5th row of risers from the east wall. Additionally, FME was discovered in both the alpha and east bravo bays, including an LED light, a zip tie, and a small pipe fitting. See EDMS for photos. The west bravo and charlie bays still need initial entry and inspection. <I> **** Actions Taken **** Removed large pieces of FME. Notified EOC. Small pipe fitting appears to be a nozzle from a desuperheat spray head. <N> **** Equipment Description **** T -441- - -B9/10.5- | 02-00-COND-HX-9
393793 | CR | 20190520 |  | 4 | Multiple Fall Protect. Harnesses found with wrong color ring | N | N |  | N | NO | <D> **** Detailed Description **** While performing inspections in the main condensor water boxes, there were multiple harnesses found with either purple or white inspection rings. Harnesses were taken away from work site and returned to tool crib on RW467 for re -inspection . Proper harnesses with the appropriate red inspection ring per ppm 10.4.12 (RED) were obtained and left at the site for use. This is CR is being written to provide awareness and ensure we are using properly evaluated PPE. <I> **** Actions Taken **** Discussed with EOC Systems Engineering Manager.
393794 | CR | 20190520 |  | 3 | Review switchyard transformer diagnostic testing PMIDs | N | N |  | N | YES | <D> **** Detailed Description **** After discussion with BPA they have provided recommendations on what changes can be made to the transformer and bushing testing in each diagnostic PM. This CR is being written to document this condition and to ensure the appropriate changes are made to the transformer PMs. Recommend assignment to system engineering. | 02-00-E-TR-M1,02-00-E-TR-M2,02-00-E-TR-M3
393795 | CR | 20190520 |  | 3 | Main transformer conduits and fasteners should be checked | N | N |  | N | YES | <D> **** Detailed Description **** An inspection of the all conduits for tightness should be added to the PMs for the new main transformers should be performed based on past experience. Over the last two outages many conduit fittings and hardware have been found loose and needed tightening. Loose fittings during an operating cycle could allow water to get into the boxes on the transformers and cause issues with equipment on the transformer and could result in transformer trips. | 02-00-E-TR-M1,02-00-E-TR-M2,02-00-E-TR-M3
393796 | CR | 20190520 |  | 3 | R24 - Lessons Learned - R24 HCU PM clearances | N | N |  | N | NO | <D> **** Detailed Description **** The majority of the initial O-CRD-HCU-XXXX clearances for R24 for the PM WOs per 10.5.9 as well as 4 of the WOs that have accumulator replacements have the CRD-V-107/XXXX drain valve off the associated water accumulator danger tagged open. These valves are removed as part with the water accumulator as part of the maintenance activity. Reference previous clearances used in R22 when last campaign was performed 4 years ago, specifically O-CRD -HCU-2619-002) for WO 02050164 4 years ago in Danger-22 folder compared to WO 02082568 with O-CRD-HCU-1015-001 in R24 which requires a revision to make the CRD-V-107/1015 a no tag. <I> **** Actions Taken **** Generated CR for future Outage Clearance preparations. Currently all 11 PM WOs that were stand alone PM WOs require the clearance revision as well as the associated 01A clearances that are associated with the Solenoid Pilot Testing. Of the 7 type PM Work Orders that are actually performing accumulator replacements as part of the WO as opposed to just removal 4 of these require the clearance modified as well.
393797 | CR | 20190520 |  | 3 | HD-LCV-5B21 and HD-E/P-5B21 IMDSs | N | N |  | N | YES | <D> **** Detailed Description **** While performing WO# 02139749-01 checked the most recent flow scan which stated that the max air supply to the valve is 21 psig. The IMDS is indicating that the valve is a 6 to 30 psi valve. <I> **** Actions Taken **** Talked to supervision and called the engineer Edward Schumacher who asked me to write a CR and he would try and get the answers needed | 02-00-HD-LCV-5B21
393799 | CR | 20190520 |  | 4 | Badge Demagnetized |  |  |  | N | NO | <D> **** Detailed Description **** ENW Laborer badge became demagnetized while worker was attempting to exit the Reactor building. The worker noticed the badge was not working and contacted Security. <I> **** Actions Taken **** Security processed the worker out of the Reactor building and presented the worker to supervision. When questioned, the worker had not come into contact with a magnet. Access created a new badge.
393800 | CR | 20190520 |  | 3 | R24 lessons learned - Isophase inspections |  |  |  | N | NO | <D> **** Detailed Description **** R24 lessons learned documentation. WO 02122003 Inspect main bus - insulators, dampers, links originally scheduled for 5 12hr shifts is taking much longer than scheduled. Resource hours of 180 is significantly less than actual. The main task needs to be broken down into much smaller tasks to make it easier to track progress. Several emergent requests for scaffold were made as the initial construction was insufficient. Recommend scaffold group record all scaffold that was built to support the isophase bus inspections. <I> **** Actions Taken **** Recommend planning make necessary enhancements to model work order. Update resource hours to 360
393806 | CR | 20190520 | CAQ | D | FP-HS-TGB21 Leak | N | N |  | N | YES | <D> **** Detailed Description **** FP-HS-TGB21 valve appears to have a packing leak. This hose station is currently being utilized for condenser tube cleaning. Valve has been throttled to minimize leakage from the hose station. <I> **** Actions Taken **** Valve was throttled to minimize leakage. Laborers dispatched to clean up water and prevent further intrusion into clean area. | 02-00-FP-HS-TGB21
393808 | CR | 20190520 |  | 4 | R24 lessons learned - emergent work |  |  |  | N | NO | <D> **** Detailed Description **** Emergent work is constantly pulling electrical resources from scheduled work on night shift. Flooded manholes, cranes, grounds, security equipment, unscheduled and unplanned support tasks, and last minute temp power requests are all pulling electrical resources from the schedule. Evaluate a larger FIN team and staffing around the clock to include supervision.
393809 | CR | 20190520 | CAQ | C | MT&E Found Out of Tolerance |  |  |  | N | NO | <C> What pieces of Equipment was this MT&E used on in the plant? <D> **** Detailed Description **** Calcode #0062574 Piezotronics Accelerometer Model 357M38 found OOT and rejected <I> SEE ATTACHED EDMS FOR DEF #7038A EVAL FROM BOLET.
393810 | CR | 20190520 |  | 4 | MT&E Found Out of Tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0068210 Ind Scientific Model MX4 found OOT and adjusted, Replaced O2 sensor <I> Not used during Calibration cycle. No Plant Impcact. DEF #7034A written. No Action Required.
393811 | CR | 20190520 |  | 4 | TG 501' Lighting is Poor in Many Areas. Safety Concern. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** TG501' Lighting is Poor in Many Areas. Need to re lamp the permanent lighting, that has burnt out, during our 2 year run cycle. This is a Safety Concern. <I> **** Actions Taken **** HP Suoervisor Notified. EN Safety and Williams Safety Notified. CR/WR Initiated. <N> **** Equipment Description **** TG501' Poor Lighting
393812 | CR | 20190520 | CAQ | C | MT&E found out of tolerance |  |  |  | N | NO | <C> What pieces of Equipment was this MT&E used on in the plant? <D> Calcode #0066443 Proto Torque wrench Model 6064C found out of tolerance and repaired and adjusted to customer specified requirements. <I> Per PPM 1.5.4 section 4.4.3 (a-c) Torque Wrench had acceptable post use verification @ +/- .06%. DEF #7037A written. No Action Required. <N> CR at INPROG. Approved CR & moved to SRO for OPS Review.
393813 | CR | 20190520 |  | 3 | Operation of Main Transformer cooler groups | N | N |  | Y | YES | <D> **** Detailed Description **** The new main transformers cooler groups are currently operated with two coolers always running and the other two come at different temperature setpoints when the transformer is in service. After various discussions with the new main transformer vendor they have provided direction on cooler operation for the main transformers. After discussions with vendor in the past Energy Northwest has asked what the impacts would be for operating 3 coolers all year round and only cycling the last cooler when it is needed. The operation of three coolers will reduce the amount of alarms associated with the coolers since they will not be started and stopped as frequently. The intent of this CR is to update the operation and determine if they should be on at times or if they should be turned on during cold and warm weather operations. | 02-00-E-TR-M1,02-00-E-TR-M2,02-00-E-TR-M3
393816 | CR | 20190520 |  | 3 | MS-LS-24J Location coordinates incorrect |  |  |  | N | YES | <D> **** Detailed Description **** The coordinates for MS-LS-24J in D31 need to be â€œT473 B3/6.5â€ <I> **** Actions Taken **** CR <N> No new equipment issue identified. The issue identified is that the location description in asset suite is incorrect. | 02-00-MS-LS-24J
393817 | CR | 20190520 |  | 3 | ALARA Suggestion - Improved Lighting TG 501' ,TG 471' |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** My suggestion is to invest in much more LED Lighting, as we have already, in certain areas. Every outage, we start these two areas and many other areas, with poor to no lighting. By upgrading these areas to LED, it will save a lot of Time, Dose and Money. And also result in a more efficient Run Cycle and Outage. <I> **** Actions Taken **** Notified HP Supervision. Notified Safety. Initiate CR. <N> **** Equipment Description **** TG501' TG471'
393818 | CR | 20190520 |  | 3 | AR-SPV-2A/2B solenoids stuck open. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing WO# 0207675001 MS-FT-25A loop cal AR-SPV -2A and AR-SPV-2B appeared to be stuck in the open position not allowing AR-V-2A and AR-V-2B to cycle per logic conditions. <I> **** Actions Taken **** All loop conditions were verified SAT per MS-FT-25A loop calibration. All as found values were SAT, with no adjustments made to loop components. Verified voltage readings at CR-FS-25A on E-IR-2 to be consistant with logic expectations. Mechanically agited AR-SPV-2A and AR-SPV-2B. Following agitation solenoids vented air through vent port. Valves stroked closed as expected. Cycled logic conditions several times to verify solenoids were no longer stuck in the open position and would respond as expected to logic changes. Valves stroked open and closed as expected via MS-FS-25A. Recommend evaluating replacing AR-SPV-2A and AR-SPV-2B.
393819 | CR | 20190520 |  | 3 | Revise ESP-B11--B101 AND ESP-B12-B101 |  |  |  | N | NO | <D> **** Detailed Description **** Revise ESP-B11--B101 PAGE 14 Battery Connection Drawing. The same changes need to be done on the B12 procedure. Markup attached to the EDMS <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor.
393820 | CR | 20190520 |  | 3 | MT-CRA-1 Will Not Lift LP-C Rotor | N | N |  | N | YES | <D> **** Detailed Description **** During an attempt to lift LP-C rotor, after disassembly, MT-CRA-1 would not lift the rotor from its bearings. There was no fault observed on the main hoist drive or other obvious indicator as to why it failed to lift. <I> **** Actions Taken **** Mechanical shop and on-site Whiting technician are conducting suggested inspection from Whiting corporate. Additional actions to follow. <N> **** Equipment Description **** T501 overhead . Added Whiting limit switch repair document and engineering concurrence email to the EDMS folder of this CR. . Suggest an action to determine if the OEM that performed the main hoist upgrade provided incorrect recommendations related to load testing post upgrade and whether future... ... efforts to load test and correctly set over weight limits should be considered warranty work. . Re-opened at the request of the AR-RXMAINT group. | 02-00-MT-CRA-1
393821 | CR | 20190520 |  | 4 | MT&E Found Out of Tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0063705 Clemco Carbon Monoxide Alarm Model CMS-2 fount OOT and rejected <I> Not used during Calibration cycle. No Plant Impact. Rejected- No parts available. DEF #7035A written. No Action Required.
393822 | CR | 20190520 |  | 4 | MT&E Found Out of Tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065114 IND Scientific Monitor Model ITX found OOT and rejected <I> Not used during Calibration cycle. No Plant Impact. Rejected- No parts available. DEF #7036A written. No Action Required.
393824 | CR | 20190520 |  | 3 | R24 Lesson Learned - Work delays due to laptops taken by IS |  |  |  | N | NO | <D> **** Detailed Description **** Work on RRC was delayed while attempting to locate Laptop CGS45 with the appropriate logicmaster software. Laptop was not checked out in Mettrack by any individual and was ultimately located in the IS storage cabinet in the Kootenai bldg. Earlier in the outage a separate laptop was unable to be located by the shop, and was not checked out in Mettrack. This laptop was found in Building 88 cyber storage cabinet being used for testing by IS. Everyone including IS, should be checking out PMMD so that it can be tracked down when needed for use in the plant. <I> **** Actions Taken **** Discussed issue with Asst. IS Manager. Initiated CR. Recommend action to IS to correct the issue. Recommend IS postpone any further laptop or storage cabinet testing until after R24 so the laptops remain available for use in the plant. <N> The Laptop was checked out per SWP-CSW-15 however METTRACK does not provide the location of laptop when bing checked in. In addition, SWP-CSW-15 allows for a paper check-out mthod when METTRACK is not available that would not be viewable unless a review of the logs was complete.
393825 | CR | 20190520 |  | 4 | E-RLY-81GS As found pickup out of tolerance. | N | N |  | N | YES | <D> **** Detailed Description **** During calibration of E-RLY-81GS per PPM 10.25.34 and WO#02111904-01 the As found pickup frequency was 55.90 HZ with a data sheet range of 55.95 to 56.05 HZ. <I> **** Actions Taken **** Relay was adjusted per PPM 10.25.34. As left pickup is 55.95 HZ. Relay tested Sat with all As left data in tolerance. Notified CRS and supervisor. | 02-00-E-RLY-81GS
393826 | CR | 20190520 | CAQ | C | Set screw gap on Jet Pump #9 exceeds allowable limit | Y | N |  | N | YES | <D> **** Detailed Description **** During R24 IVVI monitoring of the jet pump set screws and auxiliary wedges the set screw gap on Jet Pump #9 were found to exceed the allowable limit. The examination results are documented in indication notification report INR-CGS-19-002 (see EDMS). Each jet pump has two set screws, one vessel side (VS) and one shroud side (SS). The VS gap is 0.023 inches and the SS is 0.015 inches with an allowable of 0.020 inches per GENE-0000-0040-5440 and TM -2144. Contingency W/O 02010014 is in place to address this condition by installation of auxilary wedges. Parts are available in the wharehouse but measurements and machining will be required along with a Design Change. <I> **** Actions Taken **** Recommend assignment to AR-CPROG to update TM-2144. This impacts the Cummulative Usage Factor for the jet pump riser tracked under the Fatigue Management Program. Last auxiliary wedge installation performed by CGS was under W/O 02005851 and EC 10060. | 02-00-MS-JP-9
393827 | CR | 20190520 |  | 3 | Materials not ordered prior to working task |  |  |  | N | NO | <D> **** Detailed Description **** The work orders identified in the cross-reference required sparing a large amount of unused conductors for the MSIV limit switches. PPM 10.25.19 requires that all spared conductors inside containment or the steam tunnel be covered with Raychem nuclear end sealing kits (NESK). This material was not identified prior to working the job and due to the large number of conductors being spared, there was insufficient quantity of the NESK on hand to perform the work. An alternate end seal criteria was requested and approved by EC 17769. Additional NESK stock is also being procured. The work orders were also reviewed and they do not identify that the NESK is required for sparing these conductors. The model work orders need to be updated to identify the NESK for future work. <I> **** Actions Taken **** Initiated EC Eval 17769 to approve alternate end seal criteria. Verified supply chain was taking action to order new NESK stock.
393828 | CR | 20190520 |  | 4 | E-RLY-67G As found data out of tolerance | N | N |  | N | YES | <D> **** Detailed Description **** During calibration of E-RLY-67G per PPM 10.25.38 and WO# 02111904-01 the As found upper unit volts pickup was 60.3 VAC with a data sheet tolerance of 57.0 to 58.0 VAC. Also the lower unit amps minimum pickup As found was 0.034 Amps with a data sheet tolerance of 0.024 to 0.026 Amps. <I> **** Actions Taken **** Notified CRS and supervisor. Adjusted relay per PPM 10.25.38. As left volts pickup is 57.7 VAC. As left amps minimum pickup is 0.025 amps. Relay tested Sat with all As left data in tolerance. | 02-00-E-RLY-67G
393829 | CR | 20190520 |  | 3 | (R24LL) LLRT delayed by improper sequencing of clearance |  |  |  | N | NO | <D> **** Detailed Description **** The LLRT for RWCU-V-40 was delayed because a required hang -clearnce activity was scheduled after the LLRT. As a result, proper drainage could not be obtained. The hang -clearance was needed for another LLRT (RWCO-V-5A/5B) which is scheduled to occur after the RWCU-V-40 LLRT. <I> **** Actions Taken **** Actions taken to pull up the hang-clearance action.
393830 | CR | 20190520 |  | 4 | (R24LL) Entries into different Hi-Rad zones delays LLRT |  |  |  | N | NO | <D> **** Detailed Description **** The LLRT on RCC-V-21, 40, 219 (02117192-01) required entries into hi-rad zones in both the dry-well and the RB. These areas require checking into different RWPs and going into different locations for briefs and entry/exit controls. As a result the time to set up hoses and manipulate equipment to set up for the LLRT took longer than expected. These activities could have been better planned, coordinated and required durations better estimated in the outage schedule and execution.
393831 | CR | 20190520 |  | 3 | R-24 LL: Performance Improvement (HU Trend) Outage plan |  |  |  | N | NO | <D> **** Detailed Description **** This Condition report is being initiated to capture Lessons Learned for Outage preparations and enhance program plans to support Outage activities in the future. <I> **** Actions Taken **** Discussed with Performance Improvement Manager and Performance Improvement Program Manager (HU), initiated CR Assign to AR-PERFIMP <N> Actions completed, additional AR initiated to track planning actions for HU and Trend programs for R-25, first actions to start in August 2020. No additional actions required, received PI Manager approval for closure
393834 | CR | 20190520 | CAQ | D | unstable float voltage on E-B0-2A | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing ESP-BAT-W101 per WO#02112549-08, electricians found float voltage on E-B0-2A to be 0.7 volts higher than the acceptable range. 26.5-27.5VDC. As found was 28.2 VDC. Per attachment 9.3 of ESP-BAT-W101, OPS were notified and permission was given to adjust the voltage into the acceptable range. With a DMM connected to the analog meter on the charger, a very small CCW turn was given to the FLOAT potentiometer. The Voltage spiked to approx. 29.0VDC and the Analog meter was bouncing from 3 -9amps for several minutes. It seems that the FLOAT potentiometer needs to be Wiped as it is very touchy. <I> **** Actions Taken **** Notified PSRO, Supervisor and Write CR/WR . <N> **** Equipment Description **** Charger Room #2 467 Vital island E-C0-2A
393835 | CR | 20190520 |  | 3 | CID#28204 not as expected. |  |  |  | N | NO | <D> **** Detailed Description **** During the rebuild of the spare MSIV air operator on WO#02109526-01, it was identified by the mechanical craft that the new hydraulic manifold CID#28204 (P/N 975-35637) was not completely threaded in the end that houses the check ball retainer. This configuration would not allow the check ball to be effective in preventing flow and places the seat on the wrong side of the flow path. This manifold was not used. <I> **** Actions Taken **** Contacted engineering and R.A Hiller Company. It was advised by Hiller that the manifold be returned for inspection. See attached pictures in EDMS. <N> **** Equipment Description **** Spare MSIV AO hydraulic Manifold.
393838 | CR | 20190520 |  | 3 | Procedure 12.5.8 enhancements |  |  |  | N | NO | <D> **** Detailed Description **** On page 16 of 12.5.8 the second note refers you to section 0, it should refer you to section 11. Additionally each section for noble gas sampling has the user close the sample isolation valve, then note the time and flow. If this is performed it could result in the user not noting the flowrate before the valve is isolated and flow is 0. <I> **** Actions Taken **** Supervisor and specialist informed
393839 | CR | 20190520 |  | 4 | SA-MON-1 zero drift after electrical outage | N | N |  | N | YES | <D> **** Detailed Description **** SA-MON-1 has been reading between -3 ppm and -5 ppm since it was placed in service along with SA-C-1 after an electrical outage . The IMDS sates that for a 0 ppm source, output should be between +5 to -0 ppm. Instrument was CALIBRATED SAT PER WO 02110230. ON 4/24/19. Appears recalibration is needed. <I> **** Actions Taken **** Notified MCR | 02-00-SA-MON-1
393841 | CR | 20190520 | CAQ | C | Inspection issues for E-TR-8AF/1 (WO 02078873) | Y | N |  | N | YES | <D> **** Detailed Description **** Found screw to be stripped on lower right hand corner of dead front. Breaker #2 "C" phase has 1/4" of copper showing from previous termination. <I> **** Actions Taken **** CR generated for ENG eval. . The issue described in the CR appears to be referencing the wrong EPN and Work order. correct EPN is: E-PP-8AG WO: 02111297 . Confirmed with DA Bostwick via phone the inspection issues were with E-PP-8AG. (WO 02111297). RW Green 5/21/19 <N> **** Equipment Description **** B 441' C7/3.1 (SWPH-B) | 02-00-E-TR-8AF/1
393842 | CR | 20190520 |  | 3 | CID 74211060 does not reflect QL3 requirements |  |  |  | N | NO | <D> **** Detailed Description **** QL3 CID 74211060 for a 4" Blank Electrical Box Cover is not configured for augmented quality (Quality Level 3) procurement. Eight Purchase Orders (PO) were issued since 4/24/2018 (see AR CR references) for the procurement of non-safety non-augmented quality stock under CID 74211060. The Asset Suite indicator that would have flagged the items as requiring a quality receipt inspection and acceptance tagging was not set correctly for QL3. . CID 74211060 was issued to multiple work orders (See AR CR references) having either non-safety related Fire Protection (FIRE PROT2) or non-safety related Essential Fire Protection (FIRE PROT1) quality classifications. The Essential Fire Protection (FIRE PROT1) applications require the quality receipt inspection. . CID 74211060 has since been reconfigured by Procurement Engineering (5/20/2019) to invoke the necessary quality inspections, utilizing the appropriate plant process (receipt inspection), required for augmented quality procurement. Recommend assigning this CR to Supply Chain Services (SCS) to address existing inventory of non-safety non-augmented quality CID 74211060 stock. SCS to generate additional actions as necessary to address CID 74211060 non-safety non-augmented quality stock issued to the plant for use in non-safety related augmented quality (QL3) applications. <I> **** Actions Taken **** generated CR, configured 74211060 to invoke augmented quality inspection, notified SCS (buyer)
393843 | CR | 20190520 |  | 4 | Computer point L164 required calibration | N | N |  | N | NO | <D> **** Detailed Description **** While performing WOT 0205159601 computer point L164 required calibration. <I> **** Actions Taken **** Calibrated SAT. Generated AR for tracking. No further actions required
393844 | CR | 20190520 |  | 3 | Isophase bus degraded insulator | N | N |  | N | YES | <D> **** Detailed Description **** During isophase bus inspection in accordance with WO 02122003, insulator A9 was identified as having several cracks, there is also large amounts of glyptal on the insulator from previous attempts to repair the damage to the insulator. The OEM recommends replacing cracked insulators rather than attempting any repairs. This insulator should be replaced. CR 393784 documents a chip on the A16 insulator and OSCR 393823 was initiated to consider replacing both insulators as part of the R24 inspection. See EDMS for pictures of the A9 insulator. <N> **** Equipment Description **** Insulators located in the transformer yard | 02-00-E-BUS-ISOPHASE/A
393845 | CR | 20190520 |  | 3 | MS-PS-25A non repeatable during calibration. |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing WO 02112078 01 for MS-PC-11A loop cal. MS-PS-25A was found out of Spec with and expected value of 600 psig +/- 9.5 psig. Trip value was 672 psig and reset 519 psig. During calibration switch repeatability was not consistent during several cycles of trip and reset attempts. Recommend evaluating switch for replacement. <I> **** Actions Taken **** Informed I/C Supervision and wrote CR
393846 | CR | 20190520 | CAQ | D | Emergency DC Lighting Fixtures in Stair No. 7 not Lit | N | Y |  | N | YES | <D> **** Detailed Description **** Both Division 1 and Division 2 emergency DC lighting fixtures in Stair No. 7 are not lit. These unlit emergency DC lighting fixtures are located on the wall at landings EL. 471, EL. 482, and EL. 501 for Division 1 and landings EL. 467, EL. 487, and EL. 496 for Division 2. Per Paragraph 9.5.3.2.3 of the FSAR, the emergency DC lighting in the Remote Shutdown Room and the access route from the Main Control Room to the Remote Shutdown Room are to be continuously lit. Suspect that the bulbs are burned out and will need to be replaced. The emergency DC lighting for both divisions in the Remote Shutdown Room and just outside the Remote Shutdown Room are lit and they are fed from the same disconnects (E -DISC-S11D1 and E-DISC-S12D1) as the unlit fixtures in Stair No. 7. <I> **** Actions Taken **** Informed the SM and created WRs to have the bulbs replaced. | 02-00-E-DISC-S11D1,02-00-E-DISC-S12D1
393847 | CR | 20190520 |  | 4 | Isophase bus broken damper handle |  |  |  | N | YES | <D> **** Detailed Description **** During inspection of the isophase bus in accordance with WO 02122003 the deionizer / Damper assemblies are inspected for condition of welds and freedom of movement. During inspection of the damper D3 in the transformer yard the handle for the damper was broken. Recommend taking a handle from a spare damper assembly in the warehouse (reference CATID 25201) and replacing the handle on the in service damper. This task sould be worked as a minor maintenance activity <I> **** Actions Taken **** Discussed with EOC and craft. <N> **** Equipment Description **** Crossover dampers located on the top of the isophase bus in the transformer yard. | 02-00-E-BUS-ISOPHASE/A
393848 | CR | 20190520 |  | 3 | eSOMS PQ&S Database Overloaded |  |  |  | N | NO | <D> **** Detailed Description **** eSOMS PQ&S software performance is slow. The issue was reported to IS and FFD in March 2019. In December 2018, a single fatigue rule (NFR) calculation by the software was clocked at 24 seconds. In March 2019, a single NFR calculation was clocked at 69 seconds. Today, 5/20/2019, a single NFR calculation can be clocked at 150 seconds. At this rate, the software may not be functional soon. The current impact is inefficiency of simple scheduling tasks and fatigue checks for prospective workers. Impacts of software failure could result with inability to calculate and track over 500 workers covered by fatigue rules. Therefore it could potentially impact outage related production schedules and resources if not immediately addressed. Recommend immediate database truncation/ compaction. <I> **** Actions Taken **** Initiated CR.
393849 | CR | 20190520 | CAQ | C | In-body wash out (Degraded) on MD-V-72 | N | Y |  | N | YES | <C> The scope change needs to be included in a WR/WO/WP, then the CR can be closed to the WR/WO/WP that will address the CAQ. . This CR was closed by outage management with no assignments. However, engineering requested it to be reopened and assigned to AR-EOC. (see EDMS) <D> **** Detailed Description **** During disassembly and inspection under WO# 011884430, wash-out of the plug, seat, seat landing and valve body was found that is beyond repair. Valve replacement is needed. <N> **** Equipment Description **** TG 496 Work will be done under WO 01188443. OSCR approved by OSP (see cross references). Closing to work management process | 02-00-MD-V-72
393851 | CR | 20190520 | CAQ | D | IDS 7&8 Malfunction |  |  |  | N | YES | <D> **** Detailed Description **** IDS Malfunction 7&8. A pin is out of place on IDS 7. <I> **** Actions Taken **** Comp Measure put in place. | 02-00-SEC-IDS-E/S/7/8
393853 | CR | 20190520 |  | 4 | FM discovered during the disassembly LPC turbine |  |  |  | N | NO | <D> **** Detailed Description **** On night shift 5/19 a Â½â€ thick semi-circular, black piece of metal on the horizontal joint of the LPC turbine, near the generator end L-3 blades. No other metal was found in the area or on other areas of the horizontal joint. No other Foreign material was found. Siemens is investigating the source of the metal; it appears to be a retention screw from the upper half of inner cylinder #2, which would have been mated with the horizontal joint during operation, therefore this piece of metal would have been captured in the clearance pocket between the lower and upper halves. Siemens inspected the blade path (both rotating and stationary) of the LPC turbine and found no indications of foreign material intrusion. Siemens will conduct further inspections on inner cylinder #2 upper half following the LPC rotor lift <I> **** Actions Taken **** Metal was removed and the system engineer was notified
393854 | CR | 20190520 |  | 4 | IR-V-IR3/V18 is broken and will not reposition. |  |  |  | N | YES | <D> **** Detailed Description **** IR-V-IR3/V18 will not operate. It will move approximately 1.5 turns. This is not Full Stroke on this valve. (IR-V -IR3/V18 was compared it to adjecent valves). IR-V-IR3/V18 grinds and makes noise when attempts to operate it are made. This valve must be repaired prior to the end of the Outage. This valve is a small Instrument Rack Valve. It is attached to the system via small Tubing Fittings. This will be a quick fix with a new valve. <I> Notified OCC that this valve must be repaired prior to start up. | 02-00-IR-V-IR3/V18
393856 | CR | 20190520 |  | 4 | First Aid |  |  |  | N | NO | <D> **** Detailed Description **** Employee was Traversing down stairs from the Electrical Tree House muster area when they felt a pain in their Left Knee. Employee was not carrying any materials and was holding the Handrail at time of incident. <I> **** Actions Taken **** Emnployee notified Supervisor and WPS Safety for evaluation. Employee was prescribed Ice and Ibuprofen resulting in First Aid. All WPS and ENW notifications made.
393858 | CR | 20190520 |  | 4 | MS-AO-121 Actuator Leaking |  |  |  | N | YES | <D> **** Detailed Description **** While Performing work in the heater bay. A Crane Valve crew noticed a loud air leak. Upon further investigation it was determined that the actuator vent for MS-AO-121 was blowing air. This is an indication that the piston seal in the actuator has failed. Reccomend initiating a work order to investigate, Repair and as left diagnostic. MS-AO-121 is Steam Trap station #6 Bypass isolation valve. It is not accessible while online. It is a quailty class 2 Category 2B component in the AOV program. <I> **** Actions Taken **** Talked with the Crane Valve supervisor and generated this AR. <N> **** Equipment Description **** Turb. 493 Htr. Bay D1/9.2 | 02-00-MS-AO-121,02-00-MS-V-121
393859 | CR | 20190520 | CAQ | D | MS-DPT-32 found OOT. CR for tracking | N | Y |  | N | NO | <D> **** Detailed Description **** During the performance of work order 02112077 task 01, MS-DPT-32 was found out of tolerance low. Found 0.12mA low at 0% and 0.19mA low at 100% with a tolerance of plus or minus 0.08mA. <I> **** Actions Taken **** CR generated for tracking and transmitter calibrated to within tolerance. loop cal left SAT <N> **** Equipment Description **** MS-DPT-32. 471 R, P009
393860 | CR | 20190521 |  | 3 | R24LL: Additional alarms while performing TSP-RPS-B502 |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** during performance of TSP-RPS-B502, the RO informed us that during testing, H13.P603.A8.3-5 (RBM upsclae/INOP) and H13.P603.A8.6-6 RBM downscale came into alarm along with our other alarms that are specified in the procedure. <I> **** Actions Taken **** Informed the Supervisor, and created this Cr to get the procedure revised to reflect the 2 alarms that came in during testing <N> **** Equipment Description **** Main Control room
393861 | CR | 20190521 |  | 4 | Received Bus 21 Ground alarm |  |  |  | N | YES | <D> **** Detailed Description **** On 5/21/19 00:22 the MCR received H13.P800-C2 8-2 Bus 21 Ground alarm. Local indications revealed the ground to be loacted on MC-2B. This ground has been intermittent, and so far isolations have been unsuccessful. Previous ground was isolated to E-LP-2RA ckt 5 <I> **** Actions Taken **** Informed CRS | 02-00-E-MC-2B
393863 | CR | 20190521 |  | 4 | MSIV-V-28C work stopped due to poor radworker practices |  |  |  | N | NO | <D> **** Detailed Description **** On 5/20/19 nightshift work crew on MSIV-V-28C was stopped due to performing unauthorized scrubbing on valve internals. Workers stated they would be taking internal valve measurments, but were discovered by HP tech scrubbing inside the valve body. This work was NOT approved for the HP controls at the time. <I> **** Actions Taken **** Workers were coached and asked to leave the RCA. HP supervision and OCC RP manager was informed. <N> Work was stopped due to a miscommunication between shifts. HP had deconned MS-V-28C prior to the worker peforming work and knew that the worker would be using a honing stone to remove galling and minor imperfections prior to taking their readings. The individual was dressed appropriately for the work and there was no spread of contamination. This is not an RWP violation. Correct EPN is MS-V-28C.
393864 | CR | 20190521 | CAQ | C | Print M530-1 needs to be changed for DPT-32. |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of WO# 02112077-01, on 5/20/19, we noticed that P&ID M530-1 showed DPT-32 at G-12 with only 1 sensing line. It should have 2 sensing lines attached because it is a differential pressure transmitter. It appears that maybe the electrical signal line going to the right from the transmitter should actually be the other sensing line and connect over at G-4. This transmitter reads differential pressure across the RPV plate and the current drawing only shows one sensing line connected to the transmitter that comes from above the plate. Recommend the drawing get changed display the other sensing line and where it is connected. <I> **** Actions Taken **** Notified Leadership and initiated CR
393865 | CR | 20190521 |  | 3 | R24LL: TSP-RFW/X17A-R802, EPN error |  |  |  | N | NO | <D> **** Detailed Description **** TSP-RFW/X17A-R802 Step 7.3.10 EPN should be RFW-V-141 instead of RWCU-V-141. <I> **** Actions Taken **** Initiated CR
393866 | CR | 20190521 |  | 4 | RWCU-V-40 LLRT Not Coordinated with Test Lineup |  |  |  | N | NO | <D> **** Detailed Description **** RWCU-V-40 LLRT was being performed under TSP-RFW/X17A-R802 (WO 02112015). It appears the test was performed on the volume prior to establishing the lineup. Test was performed the next shift under the correct lineup. <I> **** Actions Taken **** Supervisor notified the control room, Production Manager and OCC.
393867 | CR | 20190521 |  | 4 | HD-V-31A failed as/found freedom of movement check. |  |  |  | N | YES | <D> **** Detailed Description **** During performance of PPM 10.2.99 under WO# 0211284401 HD -V-31A failed the as/found freedom of movement check. Steps are provided in this WO to remove packing and repack as required to determine the cause of failure. After packing was removed the valve stroked freely but had some resistance between the shaft and bushings requiring further disassembly. The bushings were polished but not replaced due to availability and a new rock shaft was installed removing the resistance per existing work instructions in WO# 02111314-01. No further actions are required. This CR is generated for tracking only. <I> **** Actions Taken **** CR generated for tracking. <N> **** Equipment Description **** TB483 | 02-00-HD-V-31B
393868 | CR | 20190521 |  | 4 | Isophase bushing glaze damaged |  |  |  | N | YES | <D> **** Detailed Description **** The B phase vertical bushing going to the N1 and N2 transformer primary bus appears to have been damaged by hot material, possibly from when the access holes were cut. The bushing glaze is pitted and some slag material appears to be embedded in the surface. Photos uploaded to EDMS Docs. | 02-00-E-BUS-ISOPHASE/B
393869 | CR | 20190521 |  | 3 | R24LL CW blowdown preps for R25 |  |  |  | N | NO | <D> **** Detailed Description **** SOP-CW-OPS Attachemnt 6.4 temporary blowdown calibration curve only goes to 2800 GPM. With 2 or more pumps aligned, flow can be higher. Additionally CBD-RO-1 limits flow. Should be evaluated for temporary removal. This will improve blowdown rate for R25 basin drain and future outages. <I> **** Actions Taken **** Recommend assign actions to evaluate temporary removal of CBD-RO-1, actions to revise work order tasks to remove restricting orifice in support of basin CW drain. Additional action to update SOP-CW-OPS to put in a higher temporary flow range instrument and associated calibration curve. <N> CW blowdown preps tracked per AR 396117 task 06. Close this R24LL to that activity.
393870 | CR | 20190521 |  | 3 | SRD fell into the reactor cavity during CRB shuffle |  |  |  | N | NO | <D> **** Detailed Description **** While covering the removal of cables from the reactor cavity , an individual leaned against the upper handrail which dislodged the self-reading dosimeter (SRD) from the pocket of the protective clothing. The SRD fell into the reactor cavity and came to rest on the top of a fuel assembly. The pocket of the protective clothing was closed with velcro as required by GEN-RPP-04. <I> **** Actions Taken **** Work was stopped, and the individual exited the RCA. A restriction from the RCA was placed on the individual pending completion of an investigation. The SRD was retrieved intact with no missing pieces.
393871 | CR | 20190521 |  | 3 | R24LL; RCC-V-219, body galled, needs replacement | Y | N |  | N | YES | <D> **** Detailed Description **** while working WO 02112271 to inspect RCC-V-219, it was discovered in the field that the seal weld was 3/8 inch +, It was expected to be 1/8". This is stainless on stainless fine thread and by oversizing the weld in the past, it caused the valve body to be bound/Galled to the point of not being able to remove the bonnet. This will require a new work plan to cut out and replace the valve. This is a lesson learned because energy northwest worked on this valve in 2009 and performed the seal weld in question <I> **** Actions Taken **** Notified supervision, OCC and Planning Pictures uploaded. | 02-00-RCC-V-219
393873 | CR | 20190521 | CAQ | D | RRA-CC-10 anodes not included in the LOU |  |  |  | N | YES | <D> **** Detailed Description **** RRA-CC-10 anodes (Cat ID# 58902333) is not included in the Limits on use (LOU) for this coiling coil. LOU needs to be revised to include RRA-CC-10. <I> **** Actions Taken **** Notified planning, EOC, Maintenance OCC representative and initiated CR <N> Bill of Materials (BOM) 6W18-50-5608T version 000 was added to RRA-CC-10. AR-RIE 328207 was added to CID 58902333 D202 panel. The initial planning for work associated with RRA-CC-10 had a different anode selected. | 02-00-RRA-CC-10
393874 | CR | 20190521 | CAQ | D | SW-FE-39 discovery requires ASME Plan nuts and bolts | Y | N |  | N | YES | <D> **** Detailed Description **** During WO 02112410 disassembly of flow element, Craft used good maintenance fundamentals and technical skills. They discovered severely degraded fasteners/hardware. Immediately notified supervision. Contacted planning for new hardware and work plan updates. <I> **** Actions Taken **** discussed with supervision, notified planning, returned WO for updates. | 02-00-SW-FE-39
393875 | CR | 20190521 |  | 3 | MT-CRA-1 main hook upper limits out of adjustment | N | N |  | N | NO | <D> **** Detailed Description **** During the removal of the LPC turbine rotor it was determined that there was not adequate clearance to travel over the main steam lines on the TBG 501 to reach the turbine power rollers. <N> Suggest adding an action to determine whether the OEM that performed the main hoist upgrade is responsible for the incorrect high limit setting and needs to correct the condition as warranty work.
393876 | CR | 20190521 |  | 4 | damaged flex on hd-ls-3bht | N | N |  | N | YES | <D> **** Detailed Description **** during step 4.3 of wo # 02113941-03 found flex damaged it is split almost the whole length. <I> **** Actions Taken **** stopped contacted my supervisor and the crs and wrote this cr <N> **** Equipment Description **** 501 t G/10.7 | 02-00-HD-LS-3BHT
393878 | CR | 20190521 |  | 3 | Parking Lot Safety Concern |  |  |  | N | NO | <D> **** ANONYMOUS CR - Detailed Description **** The parking lots are currently unsafe with the large amount of oversized trucks in parking lots. Many of these trucks are too long for the designated parking spaces and either overhang into the roadway or the crosswalks. It is currently impossible to walk through the crosswalks without dodging truck bumpers, trailer hitches, etc. This also is causing a difficult time seeing cars travelling down the paths documented by numerous near misses as well as one accident. Recommend designating a separate parking lot (gravel lot) for large trucks to protect personnel safety. With safety as our #1 priority this should be addressed right away and can be solved with no cost. <I> **** Actions Taken **** Submitted CR for Safety action. <N> ANON CR generated. Reviewed for Safety Conscious Work Environment (SCWE), forwarded to OPS for review.
393879 | CR | 20190521 |  | 4 | MT-HOI-28 Upper limit stuck | N | N |  | N | YES | <D> **** Detailed Description **** During the use of subject hoist in the Hot Machine Shop, the hook was move to the full upper position then back down. The hook will now no longer go up. All other functions are working. <I> **** Actions Taken **** Generated condition report. Notified Site rigging coordinator. <N> **** Equipment Description **** MT-HOI-28
393880 | CR | 20190521 |  | 4 | Degraded conduit identified near BS-V-11A -See pictures | N | N |  | N | NO | <D> **** Detailed Description **** During walkdown of BS-V-11A, degraded conduit was observed. See attached pictures (Specifically pictures: P5180034, P5180035, IMG 0413) <N> **** Equipment Description **** Near BS-V-11A
393882 | CR | 20190521 |  | 3 | EDR Drawing Discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** Upon review of EWD-35E-022, the reference drawing for G11 -P001-1 shows CVI-DWG-02G11-05,14,22. That reference is incorrect. Per CVI-DWG-02G11-05,14,01 shows that the EDR -P-19 (G11-C041) correct reference is CVI-DWG-02G11 -05,14,26 in section C(5) of the drawing. In addition, drawing AED-MEC-M620-540-6 logic does not follow the IMDS for both EDR-LS-19A and 19C, EWD-35E-022 and CVI-DWG-02G11-05,14,26 where the logic flowpath does not match how the equipment operates. Also drawing AED -MEC-M620-540-6 setpoints indicated seemed to be reversed from the instruments IMDS. <I> **** Actions Taken **** Notified EOC, Drafting, and Design Engineering <N> See EDMS for a visible print of EWD-35E-022
393883 | CR | 20190521 |  | 4 | Temp modification 17554 |  |  |  | N | YES | <D> **** Detailed Description **** WO# 02138132-01 When performing the PMT portion of the work order 4.6 was to verify that "LP heater 1C level HI trip" Clears. The alarm did not clear after reterming wire BM2D-0063 (red) on to TB7B-12. <I> **** Actions Taken **** Supervision, CRS, OCC and engineering have been notified and WR initiated <N> **** Equipment Description **** Cond-hx-1c | 02-00-HD-LS-1CHT
393886 | CR | 20190521 | CAQ | C | RIE 365987-01 did not identify AED SPC 15F.1 as an impacted |  |  |  | N | NO | <D> **** Detailed Description **** RIE 365987-01 did not identify AED SPC 15F.1 as an impacted document in 2017. AED SPC 15F.1 was not updated to include AP 5000/5718 packing as an acceptable replacement for the Chesterton packing. AED SPC 15F.1 is a Certified Design Specification for Valves that requires a PE stamp approval. This condition may be updated as a part of EC DEC 17767. This is a documentation issue only and does not impact any SSCs at Columbia Generating Station. <I> **** Actions Taken **** Actions: Notified EOC Design Supervisor Recommend CATQ C/AR-DMC
393887 | CR | 20190521 | CAQ | C | R24LL - Leakage observed through RHR-V-4C Strainer Covers |  |  |  | N | NO | <C> No WR, Back to Orig. of CR. Provide Coaching cross reference EPN's and write WRâ€™s. <D> **** Detailed Description **** During verification of the RHR C suction strainer boundaries, Operations observed ~12 gpm leakage past the strainer covers. The covers must be removed and replaced with the liners to maintain a seal. There was a contingency work order, but it did not cover the actions necessary to restore a water tight seal (just actions necessary to maintain WW level). <I> **** Actions Taken **** CR generated. <N> Per SOD 6/3/19 this work was completed on the original WO and a WR is not needed. No additional action needed on this AR. WP is cross referenced.
393888 | CR | 20190521 |  | 3 | Lessons Learned - CRDM Exchange in RB 441 Train Bay |  |  |  | N | NO | <D> **** Detailed Description **** This CR documents lessons learned during the movement of CRDMs from 501 RB to the 441 RB train Bay and placement into transport boxes for rebuiild. Specific Items are documented in EDMS Docs associated with this CR. <I> **** Actions Taken **** Recommendations associated with lessons learned are included in EDMS documentation.
393889 | CR | 20190521 |  | 4 | MS-PS-25A Needs to be replace See CR 393845 | N | N |  | N | YES | <D> **** Detailed Description **** MS-PS-25A Needs to be replace See CR 393845 <I> **** Actions Taken **** Replace using WR, continue WO 0211207801 MS-PC-11A LOOP CALIBRATION when complete | 02-00-MS-PS-25A
393890 | CR | 20190521 |  | 4 | E-P-M3/P2 is making whining noise | N | N |  | N | YES | <D> **** Detailed Description **** While testing the new flow meters for E-TR-M3 cooler group 2 with no fans running it appears the pump is making a squeeling noise. This noise appears to be an issue with the bearings for the pump. This CR is being written to document the condition. Note: The station currently has 2 pumps onsite that could be used for replacements but the pump needs to be replaced with the transformer out of service. Recommend replacing this pump during the outage. This pump could have been squeeling for some time but it would not be heardunless the fans are off and only the pump running. This was discovered during the Transformer accessory check. | 02-00-E-P-M3/P2
393892 | CR | 20190521 |  | 3 | EWD-72E-049 has an incorrect power supply. |  |  |  | N | NO | <D> **** Detailed Description **** While preparing clearance O-RFW-PS-63QA1A-001 it was discovered that EWD-72E-049 says the power coming from wire AD11C-6 is coming from E-DISC-DPS11C/6 when it should say the power is coming from E-DISC-DPS11C/14. This needs to be corrected. This could lead to a future clearance order error. EWD-50E-003 lists the correct power supply for wire AD11C-6.
393893 | CR | 20190521 |  | 4 | 3 timer relays have failed during E-TR-M3 accessory checks | N | N |  | N | YES | <D> **** Detailed Description **** The 2A-1, 27E and 27N relays are continuously hanging up during the accessory check and have not reset. The purpose of this CR is to identify the issue and to order replacement relays under MR 274178 (CAT ID 38973). WO 02110183-01 will be revised to replace these relays. replacement relays under MR 274178 (CAT ID 38973). WO 02110183-01 will be revised to replace these relays. | 02-00-E-TR-M3
393894 | CR | 20190521 |  | 4 | Foreign materials in TSW-HX-8 | N | N |  | N | YES | <D> **** Detailed Description **** During the as-found inspection on TSW-HX-8 (Seal Oil Cooler-Air Side) under WO 02113088, some clams, corrosion products and plastic pieces were found on the tubesheets of this heat exchanger. Some tubes were blocked by those materials as well. There was no performance issues reported this cycle. The heat exchanger will be cleaned and eddy current tested as planned this outage to make sure of its tubes integrity. No further actions are needed. This is for trending. <I> **** Actions Taken **** Discussed with system engineer and initiated this CR | 02-00-TSW-HX-8
393895 | CR | 20190521 |  | 3 | New Alarm in 115 kV OPDS building (44) | N | N |  | N | YES | <D> **** Detailed Description **** Building 44, the Backup Transformer OPDS building, has a new alarm, Set 2 CONTROL POWER LOST which was not included in AR 393396. <I> **** Actions Taken **** notified MCR <N> **** Equipment Description **** Building 44 (115 kV OPDS building).
393898 | CR | 20190521 |  | 4 | Weld needed to be re-performed | N | N |  | N | NO | <D> **** Detailed Description **** While attempting to install HD-LS-1CHT under WO 02138024-01 it was identified that the fabricated LS spool piping was too long to allow for installation. The weld that was previously accepted by QC will have to be cut, the piping shortened and re-welded then accepted for final visual again. Notified PLE and QC then corrected the weld record to reflect the re-performance of weld. <I> **** Actions Taken **** CR generated
393899 | CR | 20190521 |  | 4 | Drinking water in the drywell --safety concern-- | N | N |  | N | NO | <D> **** ANONYMOUS CR - Detailed Description **** Drinking water hasn't been replenished at a good enough frequency in the drywell. Several instances it has been out and that is a safety concern for workers. <N> ANON CR generated. Reviewed for Safety Conscious Work Environment (SCWE), forwarded to OPS for review. RMC Laborers have increased the frequency to verify the water supply at the Rx501 location is adequate. No further action required.
393900 | CR | 20190521 |  | 3 | R24 lessons learned - E-shop MSIV work |  |  |  | N | NO | <D> **** Detailed Description **** R24 lessons learned documentation: MSIV work model work orders do not have enough resources hours allocated causing work delays to subsequent follow on work in the schedule and higher dose accumulation than planned. MS-V-22A, B, C, and D Replace cable and connector are taking approximately 3 times the currently scheduled duration. This is consistent with previous R23 durations. Recommend change duration tasks from 8 hrs to 24 hrs.
393903 | CR | 20190521 |  | 4 | MT-CRA-1 NORTH BRIDGE BRAKE | N | N |  | N | YES | <D> **** Detailed Description **** North Bridge Brake is making a chattering noise and causing it to heat up, and dragging on the bridge. <I> **** Actions Taken **** Contacted Whiting Vendor, Turbine Project Manager and wrote this CR. <N> **** Equipment Description **** MT-CRA-1 TG 501' | 02-00-MT-CRA-1
393904 | CR | 20190521 |  | 4 | Heater Bay fall protection equipment without red rings |  |  |  | N | NO | <D> **** Detailed Description **** On back shift EN Safety entered the TG 471 to do a walkdown and discovered multiple fall protection harnesses staged for use with an out of date inspection ring in place. <I> **** Actions Taken **** In total, 16 harnesses were inspected and proper colored ring (red for 2019) installed. Per ISPM-9: A competent person SHALL perform the inspection. Competent Person - The Competent Person is an Authorized Person who has been approved by the Department Manager to perform fall protection equipment inspections. The individual is knowledgeable of fall protection equipment, including the manufacturerâ€™s recommendations and instructions for the proper use, inspection, and maintenance; and who is capable of identifying existing and potential fall hazards; and who has the authority to take prompt corrective action to eliminate those hazards; and who is knowledgeable of the rules contained in this ISPM regarding the erection, use, inspection, and maintenance of fall protection equipment and systems. ID-15 Safety First message loaded for 5/22 to further communicate the standard here at EN. Industrial safety program managaer is aware of this issue.
393905 | CR | 20190521 |  | 3 | (QA) Attachment does not match body of procedure |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Attachment 9.3 of PPM 10.25.53, Inspection of Lighting Panels and Power Panels, lists resistance readings in the micro ohm range while the body of the procedure requires reading in the one ohm range. Additionally, Quality identified step 7.1.15e has two action steps which is contrary to the requiements of SWP-PRO-03, Writer's Manual, step 2.1.2a.7) that requires steps or substeps have one action per step. Difference in requirements can lead to confusion and potentially incorrect data collection. . Recommend reviewing the procedure and making adjustments to bring the body of the procedure and the attachments in alignment, and to align the procedure with the requiremts of the Writer's Manual. . This issue was identified during a Continuous Monitoring observation of Work Order 02111297, E-PP-8AG - Clean & Inspect Power Panel. <I> **** Actions Taken **** This issue was discussed with Electrical Craft/Maintenance Supervisor.
393906 | CR | 20190521 |  | 3 | (QA) SSC supervisors of welding not assigned to MSAH |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Contrary to MWP-1, Maintenance Welding Operating Procedure SSC supervisors of welding activities were not assigned to MSAH Qual. Group prior to refueling outage in -processing at CGS. This could result in a failure to meet welding procedural requirements for CGS. No unsupervised welding was performed at CGS this is an administrative CR. . Factual Basis: â€¢ MWP-1, Maintenance Welding Operating Procedure step 10.2 states, â€œThe required PQD Qual. Group for supervisors of welding activities at CGS is MSAH.â€ â€¢ On May 6th only one SSC employee at EN was listed in PQD viewer â€¢ Upon notification the SSC superintendent add additional SSC supervisors of welding activities. o The General Superintendent knew the qualification assignment was needed but had not completed this prior to QA notification of the issue. â€¢ The SSC Manager indicated that the potential cause was Form 26471 R15, Personnel Requirements Form, does not contain Qualification Group MSAH (ME000694) as an option in the Training Requirements section on page 4. . Insights : The SSC WPS Superintendent stated that he had not selected who would be the supervisors of welding activities. . This is a deficiency identified during audit activities for Special Processes Audit AU-SP-19. Recommend assigning to AR-SSCCRC <I> **** Actions Taken **** Discussed and vetted with Site Support Contractors Mgr. <N> Williams Plant Services. The corrective actions will be a process change. No procedure was violated by this condition. The WPS General Superintendent knew the qualification assignment was needed but had not completed this prior to QA notification of the issue. The SSC Manager indicated that the potential cause was Form 26471 R15, Personnel Requirements Form, does not contain Qualification Group MSAH (ME000694) as an option in the Training Requirements section on page 4. Insight: The SSC WPS Superintendent stated that he had not selected who would be the supervisors of welding activities at the time QA identified this issue. Those selected were assigned and satisfactorily completed the CBT.
393908 | CR | 20190521 |  | 3 | NDE indications on LPC Inner Cylinder #2 | N | N |  | N | YES | <D> **** Detailed Description **** During NDE of the LPC (MS-DT-1C) Inner Cylinder #2 upper half, 22 (twenty-two) indications/cracks were identified on the stationary blades preceding the rotating L-0 blade row. There are 10 cracks on the GOV end, all of which are on the convex side and range from 1 to 5 inches in length (most are around 4 inches). There are 12 cracks on the GEN end, mostly on the convex side but many on the concave side as well. Length of these cracks are in the range of 1 to 4 inches (most 3-4 inches). The cracks reside in the welded area at the inner shroud with the exception of two that were noted to be in the airfoil itself. [GEN end blade 4 and GEN end blade 36.] The last time this LP turbine was dismantled for inspection was during R20/2011. Siemens report 0NET11003606 documents field maintenance and repair of both stationary and rotating blades. This report identifies 29 total indications [23 in the upper half and 6 in the lower half] and notes that 28 (twenty-eight) indications were repaired on LPC. The indications were ground out and/or welded as necessary and received a re-inspection. <I> **** Actions Taken **** Discussed with Turbine PM Informed EOC Requested from OEM and engineering eval and recommendation Briefed Siemens PM on need to ensure the right resources are onsite if repairs are recommended and approved Reviewed data sheet from the R20 report and compared to the NDE report for R24. Of the 22 indications identified in R24 on the upper half of the cylinder, only three match the same location as the ones identified and repaired in R20. | 02-00-MS-DT-1C
393909 | CR | 20190521 |  | 4 | E-RLY-50N/T1/11 arching issue | N | N |  | N | YES | <D> **** Detailed Description **** Documented in CR# 393760 E-RLY-50N/T1/11 was arching during a ground fault event. When Operations transfered E-SL-21 to E-SM-2 to attempt to isolate the ground E-RLY-50N/T2/21 started arching. With both relays arching inside the relay they should each be looked at by the Relay Shop to ensure they are still reliable. <I> **** Actions Taken **** Informed Relay Supervisor, Informed OCC | 02-00-E-RLY-50N/T1/11,02-00-E-RLY-50N/T2/21
393911 | CR | 20190521 |  | 4 | RB SW elevator bump noise. | N | N |  | N | YES | <D> **** Detailed Description **** As the elevator passes upward past the 471 to the 487 a loud bump can be heard from the lower door area facing the Reactor side. This only occurs on the way up, and only at this elevation area. <I> **** Actions Taken **** Informed MCR, intiated AR | 02-00-MT-ELEV-2
393912 | CR | 20190521 |  | 3 | REMP air sample pump short hours | N | Y |  | N | NO | <D> **** Detailed Description **** REMP air sample station 1 located just south of CGS was found short approximately 33 hours. It was off due to a planned power outage per SOP-ELEC-SH6-MAINT, WO# 02079546. Sampling from this station is not an OCDM Table 6.3.1-1(2) requirement but is an EFSEC 332 required location. Recommend AR to Environmental Services to include deviation in annual report. <I> **** Actions Taken **** Noted pump running after power interruption. Wrote CR. <N> Re-assigned at the request of ENLAB supervisor.
393913 | CR | 20190521 |  |  | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #00123456, Manufacturer Model Description was found OOT.
393915 | CR | 20190521 | CAQ | D | SW-V-2B and Spacer Plate Erosion damage | Y | N |  | N | YES | <D> **** Detailed Description **** SW-V-2B inspection per WO 02111475-01 found erosion on the seat ring retainer and downstream spacer plate. The erosion is encroaching on the gasket sealing area. See EDMS for pictures. Recommend replacement of the seat ring retainer and spacer plate. <I> **** Actions Taken **** Notifed craft supervisor to have WO package replanned for replacement of parts. <N> Added to T19-R24-SWB-OUTAGE-001. | 02-00-SW-V-2B
393917 | CR | 20190521 |  | 4 | HD-LS-6BHT out of tolerance | N | N |  | N | YES | <D> **** Detailed Description **** While perfoming 02113941-06 found HD-LS-6BHT out of tolerance. Found at 2 1/8 in below centerline. IMDS requires 31/8 in +/- 1/4 in below centerline. <I> **** Actions Taken **** Contacted supervision and calibrated HD-LS-6BHT to IMDS and wrote this CR | 02-00-HD-LS-6BHT
393918 | CR | 20190521 |  | 3 | LPC Bearing 7 upper half loss of babbit material | N | N |  | N | YES | <C> MRT request this be re-assigned as a 3/SEBOP <D> **** Detailed Description **** During NDE activities on LPC (MS-DT-1C) bearings, Bearing 7 [east end of LPC] was noted to be missing the babbit material from a large area on the upper half of the bearing exposing bare metal. Search the warehouse, if no parts can be found, the bearing requires rebabbiting. The last time the bearing was inspected and NDEâ€™d was in R20/2011. The report shows no reportable indications for both the upper and lower halves. [Reference: Siemens outage services report NDS-0NET11003A41]. NDE initial findings report for R24 is in the EDMS. <I> **** Actions Taken **** Informed EOC and OCC Eng Mgr Discussed with OEM <N> **** Equipment Description **** Bearing 7, GOV end (East) of LPC | 02-00-MS-DT-1C
393919 | CR | 20190521 | CAQ | C | (IST) OSP-RHR/IST-R704 valve testing preconditioned | Y | N |  | N | YES | <D> **** Detailed Description **** The 2 year IST surveillance OSP-RHR/IST-R704 (PMID 16931) was credited to WO 02139431 (RHR-V-8 LUBE/INSPECT) where the surveillance was used as a PMT. At the same time the surveillance was credited as the PMT for RHR-V-9 work and RHR-V-123A and RHR-V-123B bucket starter coil replacements as noted in the above work order. OSP-RHR/IST-R704 should have been performed prior to any maintenance on RHR-V -123A/B or RHR-V-8/9 and thus constitutes unacceptable preconditioning. <I> **** Actions Taken **** Discussed with EOC. <N> The unacceptable preconditioning documented does not impact operability of RHR-V-8 as this issue pertains to how the stroking after the as-found were performed. When unacceptable preconditioning is identified one action is to document in CAP and another is to perform additional tests. Additional test has been performed on 5/17/19 with an opening stroke speed of 18.21 seconds and a closing stroke speed of 19.35 which are both within limits measured in WO 0213943104. | 02-00-RHR-V-123A,02-00-RHR-V-123B,02-00-RHR-V-8,02-00-RHR-V-9
393920 | CR | 20190521 | CAQ | C | SLC-V-4B- Multiple issues with work order and ppm | N | N |  | N | NO | <D> **** Detailed Description **** See attached EDMS file for list of issues. <I> **** Actions Taken **** Notifed manager. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity C to evaluate for any lesson learned action. Reference CR 396817. Originally CRG had dispositioned this CR as a D/Trend. . Assignment 01 is acceptable. MHUBER 08/19/2019 (acting Maint. Support Supervisor)
393921 | CR | 20190521 |  | 4 | R24 LL LLRT rad planning issues | N | N |  | N | NO | <D> **** Detailed Description **** The rad planning for LLRT activities did not include valve line up activities required for an LLRT activity. The planning did estimate worker dose for the lineups. When LLRT testers needed to enter high dose areas to line up for an LLRT, delays were encountered to prepare high risk plans, hold high risk briefs and change RWPs to address the radiological conditions encountered for the valve line ups. These delays could have been minimized during the planning process by being identified and planned with the LLRT test. <I> **** Actions Taken **** RPM and SOD informed. Planning was revised and entries made in accordance with site procedures.
393922 | CR | 20190521 |  | 4 | E-M-M1/F6 for E-TR-M1 is rubbing on shroud | N | N |  | N | YES | <D> **** Detailed Description **** Cooler group 2 on E-TR-M1 was replaced during R24 by ABB under warranty. After starting cooler group 2 it was discovered that the fan for E-M-M1/F6 was rubbing against the fan enclosure. The fan is part of cooler group #2 operation for E-TR-M1. It is recommended this gets repaired prior to power operations. <N> OCC informed by engineering. | 02-00-E-M-M1/F6
393923 | CR | 20190521 |  | 3 | R24LL; E-TR-M3 Accessory PM did not Notify Ops Prior to Trip | N | N |  | N | NO | <D> **** Detailed Description **** Main transformer M3 Accessory PM did not Notify Ops Prior to 86TM Trip. During the M3 accessory PM (02110183-01) it directs installing a jumper to trip E-RLY-86TM. Then it directs contacting the Control Room to verify the trip and then request Operations to reset E-RLY-86TM. The work order should have a step to contact the Control prior to initiating a trip. Also of note, the work order does not request the reset of E-RLY-86XU and E-RLY-86X1U. This also affects the accessory testing for the M1 and M2 Transformers. Work was stopped. Worked with the Control Room to reset the E-RLY-86TM relay. All three Main transformer PMs will be reviewed and holds placed to contact the Control prior to initiating any trips. Recommend updating the PMs and the PMTs listed below with the above information. 02110267-01 E-TR-M1: ACCESSORY TESTING 02110182-01 E-TR-M2: ACCESSORY TESTING 02110183-01 E-TR-M3: ACCESSORY TESTING And PMTs: 02134315-02 E-RLY-M1/63G - PMT OF NEW BUCHHOLZ RELAY 02134314-02 E-RLY-M3/63G - PMT OF NEW BUCHHOLZ RELAY 02134312-02 E-RLY-M2/63G - PMT OF NEW BUCHHOLZ RELAY <I> **** Actions Taken **** Contacted the Shift Manager, stopped work and worked with the Lead RO .
393924 | CR | 20190521 |  | 4 | MS-42-1A11B tripped while attempting to reset. | N | N |  | N | YES | <D> **** Detailed Description **** MS-42-1A11B tripped after closing in the breaker to support PMT for MS-V-68. MS-42-1A11B tripped immediatelly following reset after CRS permission to reset. <I> **** Actions Taken **** Informed CRS/SM | 02-00-MS-42-1A11B
393926 | CR | 20190521 |  | 4 | RRC-CB-PP2/ASD/SL63 tripped free during Inspection | N | N |  | N | YES | <D> **** Detailed Description **** RRC-CB-PP2/ASD/SL63 was inspected under WO 02111489. While the electricians were performing section 7.1.20 of PPM 10.25.2 (Trip Latch overlap Adjustment) the breaker tripped free. The trip latch is degraded and requires replacement. This DS416 breaker UTC#540214 was overhauled by STI on 4/12/2015 and has an 8 year overhaul frequency. <I> **** Actions Taken **** Informed EOC and initiated this CR <N> Engineering contacted STI because the breaker had just been overhauled in 2015 and its overhaul frequency is A8. STI recommended taking this breaker out of service and send it back to them to replace the degraded trip latch. Electricians will get one of the overhauled DS416 breakers from the warehouse to replace the failed breaker. | 02-00-RRC-CB-PP2/ASD/SL63
393927 | CR | 20190521 |  | 4 | while performoing WO 0212024306 found COND-CTS-1A2 OOT | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** COND-CTS-1A2 was OOT at the top end of range reading was 20.08ma desired is 20.0ma Â±0.06ma <I> **** Actions Taken **** adjusted to within tolerance
393928 | CR | 20190521 |  | 4 | TSW-FI-P/1A stuck due to debris | N | N |  | N | YES | <D> **** Detailed Description **** TSW-FI-P/1A was placed into service per SOP-CW-START section 5.1.3. As flow was being established through the instrument, three pieces of debris lodged between the float and the metering tube. Maintenance was just completed on this meter. Piping needs to be flushed prior to installation of the meter. It is recommended the condition of the pipe be investigated as there may be significant flow obstruction. <I> **** Actions Taken **** Notified Supervision | 02-00-TSW-FI-P/1A
393929 | CR | 20190521 | CAQ | C | Bucket Replacement PMTs for MOVs vs. PPM 10.25.74 compliance | Y | Y |  | N | NO | <D> **** Detailed Description **** When the motor starter / bucket for a MOV is repaired or replaced, the requirements of PPM 10.25.74 apply (specifically, the MOV Test Matrix, Att. 9.4). This procedure directs testing that needs to be performed for this activity. After review of R24 WOâ€™s for bucket replacement of MOVs, the following items are not being performed as prescribed in PPM 10.25.74: 1. No Phase rotation check prior to replacement and after replacement of bucket. 2. No current readings taken at the MCC while stroking the valve. <I> **** Actions Taken **** Identified 24 R24 WO's for bucket work on MOVs. Listed in references. Notified EOC and Maint. Planning.
393930 | CR | 20190521 |  | 4 | R24LL; CRD HCU Clearance preparations. |  |  |  | N | NO | <C> Trend CR to 393796 <D> **** Detailed Description **** R24 LL CRD HCU Clearance preparations. Most of the O-CRD -HCU-XXXX-001 Clearances were prepared with Danger tags added to CRD-V-107/XXXX. On WO Tasks for CRD-HCU-XXXX Refurbishments, the CRD-V-107/XXXX actually required a No Tag as CRD-V-107/XXXX will be removed during accumulator removal and installation. This required about 24 hours of rework to create new and amend existing clearances. <I> **** Actions Taken **** Submitted R24 LL <N> cancel to 393796
393933 | CR | 20190521 |  | 4 | Report Only |  |  |  | N | NO | <D> **** Detailed Description **** Employee working in the TG 456 was trying to bring two Insulating Pads together on a Pipe when they felt discomfort in their Right Wrist. The employee did not strike any objects during this evolution and was wearing all required PPE. <I> **** Actions Taken **** Employee notified his GF and Supervisor and reported to WPS Safety for evaulation. No treatment required or given. Report Only.
393934 | CR | 20190521 |  | 3 | Repair on WO 02115656 (BS pipes in the condenser) |  |  |  | N | YES | <D> **** Detailed Description **** All the gussets on 306-7: 22â€ Extraction Steam to BS-EJ-2D and 306-8: 22â€ Extraction Steam to BS-EJ-2C showed external erosion wear. Pipe thickness indicate no emergent replacement. However, locations under the gussets that are approximately 3â€x3â€ areas had deep pits that could not be measured. Given that the pipe appears to be in good shape, only external repairs are needed. <I> **** Actions Taken **** Initiated CR <N> **** Equipment Description **** Inside the Condenser | 02-00-BS-EJ-2C,02-00-BS-EJ-2D
393935 | CR | 20190521 | CAQ | C | RFW-V-10B As-Found leak rate exceeds admin limit | Y | N |  | N | YES | <D> **** Detailed Description **** RFW-V-10B had an-found leak rate retest result of 8420 sccm which exceeds the admin limit of 2125 sccm. Test performed per TSP-RFW/X17B-R801 Major Revision 10 Minor 2. RFW-V-10B serves as a barrier for both Primary Containment integrity and Secondary Containment Bypass leak limits. See CR 00393735. <I> **** Actions Taken **** LLRT SRO notified. OCC OPS and Emergent Work Notified. EOC Tech Services Notified. <N> Engineering is requesting cancellation of the REP/REGE assignments on the CRs indicated below because only the admin limit was exceeded. This does not indicate that the valve(s) (or containment) are inoperable. LLRT testing is performed to determine total containment leakage which is quantified after evaluating all LLRT results to determine operability of primary containment. <R> REP/REGE assingments cancelled with Licensing Supervisor concurrence. | 02-00-RFW-V-10B
393936 | CR | 20190521 |  | 4 | HD-42-2C8B disconnect would not reclose in when cycled |  |  |  | N | YES | <D> **** Detailed Description **** HD-42-2C8B disconnect would not reclose in when cycled. While hanging a local clearance the breaker would not reclose in when cycled for testing. please luubricate/repair as needed. <I> **** Actions Taken **** wr/cr discussed with production | 02-00-HD-42-2C8B
393937 | CR | 20190521 | CAQ | D | MD-V-72 License Renewal Exam Showed Erosion Damage | N | Y |  | N | YES | <D> **** Detailed Description **** While performing WO 01188443-09 license renewal inspection of MD-V-72 and the associated piping, the as-found VT-1 exam identified that there was erosion damage and localized corrosion that could have impacted the intended function of the valve. The valve is being replaced under WOT 01188443-01 to restore full qualification of the valve, therefore, no functionality determination or other action is required. This inspection is required under Commitment No. 12, Chemistry Program Effectiveness Aging Management Program. No further action is required under this CR. It is recommended to trend the CR for Chemistry Effectiveness AMP trending. <I> **** Actions Taken **** Talked to Immediate Supervisor to discuss results of visual inspection and initiated CR. <N> **** Equipment Description **** T 496 G1/6.0 | 02-00-MD-V-72
393938 | CR | 20190521 |  | 4 | Relief valve failed on LLRT baily test cart | N | N |  | N | NO | <D> **** Detailed Description **** Relief valve on baily leak rate cart failed. Pressure relief valve should lift at 1150 psi while performing a test it was noted that relief valve is lifting at 600 psi. Relief valve needs to be reset and retested. <I> **** Actions Taken **** Notified supervisor <N> **** Equipment Description **** RX 548
393939 | CR | 20190521 | CAQ | C | RCC-V-71A de-clutch pin broken | Y | Y |  | N | YES | <D> **** Detailed Description **** While backseating RCC-V-71A per a WO the declutch lever locking pin broke while pulling the lever down. The handle went loose and the handle spun loose from the shaft. Supervisor was informed. <N> WORK PERFORMED: FOUND THE DECLUTCH LEVER KEY TO BE SHEARED. REPLACED KEY AND PLACED RCC-V-71A ON THE BACKSEAT. Issue resolved on 5/26/19 | 02-00-RCC-V-71A
393940 | CR | 20190521 |  | 4 | TG-DET-SPD has damaged cable. |  |  |  | N | YES | <D> **** Detailed Description **** Found TG-DET-SPD cable to be damaged. <I> **** Actions Taken **** Informed Supervisor. | 02-00-TG-DET-SPD
393942 | CR | 20190522 |  | 4 | Employee injured elbow on structural steel. |  |  |  | N | NO | <D> **** Detailed Description **** An actuator technician hit his elbow on structural steel while pulling on a chainfall. The chain was hung up and when it freed his arm moved too far back and hit the steel. <I> **** Actions Taken **** He was taken to the site nurse who advised him to have an x-ray performed. He was taken to an urgent care facility. X-ray showed no broken bones. No presriptions were ordered. <N> **** Equipment Description **** C 555'
393944 | CR | 20190522 | CAQ | C | RHR-V-27B exceeded its LLRT admin limit, then failed | Y | N |  | N | YES | <D> **** Detailed Description **** The As Found LLRT test performed on RHR-V-27B per WOT 02112329-01 exceeded its admin limit. Initially, the leak rate monitor showed approximately 1300 sccm of leakage. After hearing a noise and hearing â€œgurglingâ€ the leak rate on the monitor increased to approximately 40,000 sccm. The admin limit for this valve is 885 sccm. As required by the LLRT test performance the packing was inspected and verified to have zero leakage around the packing. RHR -V-27B provides isolation for the suppression pool spray. The RHR system is considered a closed loop water-filled extension of primary containment. <I> **** Actions Taken **** Notified LLRT SRO, OPS OCC, Engineering OCC, EOC Tech Services, and MOV Engineer <N> Engineering is requesting cancellation of the REP/REGE assignments on the CRs indicated below because only the admin limit was exceeded. This does not indicate that the valve(s) (or containment) are inoperable. LLRT testing is performed to determine total containment leakage which is quantified after evaluating all LLRT results to determine operability of primary containment. | 02-00-RHR-V-27B
393945 | CR | 20190522 |  | 4 | R24LL, Failed Tool Lanyard Grip Tape caused dropped item |  |  |  | N | NO | <D> **** Detailed Description **** While building scaffold inside the MS-DT-1C hood at the 492â€™ level, an individual was traversing under some lateral restraints when his side cutters slipped out of his tool lanyard. The side cutters were attached to his tool lanyard with FME tape. When the FME tape failed, the tool was easily identified on the 471â€™ FME tarp. A member of the crew notified the FME monitor right away and it was agreed by the FME monitor that it was easily retrievable. The side cutter were successfully retrieved. <I> **** Actions Taken **** Contacted FME monitor right away and contacted Supervision and OCC. Initiated Condition Report.
393946 | CR | 20190522 | CAQ | D | CAS-C-1A oil level low | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1A has no oil visible in the sightglass. Please add oil. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 441 E | 02-00-CAS-C-1A
393947 | CR | 20190522 |  | 4 | Seal oil room sump is >1/2 full. | N | N |  | N | NO | <D> **** Detailed Description **** Seal oil room sump is >1/2 full. Please pump this sump. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 441 W seal oil room.
393948 | CR | 20190522 | CAQ | D | CRD 26-43 Double Notches Following Coupling | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of PPM 6.5.9 rod 26-43 was coupled and following the venting of the rod it double notched multiple times. CR/WR to track rod operation and speed adjustments. | 02-00-CRD-DRVE-2643
393949 | CR | 20190522 |  | 4 | BS-42-1A13B failed to close while being tagged out | N | N |  | N | YES | <D> **** Detailed Description **** BS-42-1A13B failed to close while being tagged out. While testing the disconnect the disconnect failed to close. Please lubricate or repair as necessary <I> **** Actions Taken **** cr wr informed production | 02-00-BS-42-1A13B
393950 | CR | 20190522 | CAQ | C | RFW-V-32B leak rate exceeds admin limit | Y | N |  | N | YES | <D> **** Detailed Description **** RFW-V-32B had an as-found leak rate of 5100 sccm which exceeds the admin limit of 2125 sccm. Reference CR 393736. <I> **** Actions Taken **** Notified LLRT SRO, OCC Operations, OCC Engineering, OCC Emergent Work, EOC Technical Services, Check Valve Engineer <N> Engineering is requesting cancellation of the REP/REGE assignments on the CRs indicated below because only the admin limit was exceeded. This does not indicate that the valve(s) (or containment) are inoperable. LLRT testing is performed to determine total containment leakage which is quantified after evaluating all LLRT results to determine operability of primary containment. <R> REP/REGE cancelled with Licensing Supervisor concurrence. | 02-00-RFW-V-32B
393951 | CR | 20190522 |  | 4 | HD-V-32B failed as/found freedom of movement check |  |  |  | N | YES | <D> **** Detailed Description **** During performance of PPM 10.2.99 under WO# 02111315-01 HD-V-32B failed the as/found freedom of movement check. Steps are provided in this WO to remove packing and repack as required to determine the cause of failure. After packing was loosened the valve stroked freely with no indication of binding. Repack instructions and final PPM -10.2.99 inspections are covered in this WO# 02111315-01 and no further actions are required. This CR is generated for tracking only. <I> **** Actions Taken **** CR generated for tracking <N> **** Equipment Description **** TB 483 | 02-00-HD-V-32B
393953 | CR | 20190522 |  | 4 | Baily LLRT Water Cart Exceeds Design Pressure |  |  |  | N | NO | <D> **** Detailed Description **** During capacity test for baily LLRT water cart, replacement high pressure relief valve was lifting due to excess pressure. Relief valve was replaced earlier due to suspected failure. Swapped high pressure gauges and verified pressure did not exceed 600 psi through snubbed valve and relief valve continued to lift. <I> **** Actions Taken **** Contacted supervisor <N> **** Equipment Description **** RX 548
393955 | CR | 20190522 | CAQ | C | Could not achieve LLRT test pressure on RFW-V-10A | Y | N |  | N | YES | <D> **** Detailed Description **** Test pressure could not be achieved on RFW-V-10A during LLRT testing. RFW-V-10B serves as a barrier for both Primary Containment integrity and Secondary Containment Bypass leak limits. <I> **** Actions Taken **** Notified OCC, EOC, and Check Valve Engineer <N> Engineering is requesting cancellation of the REP/REGE assignments on this CR because only the admin limit was exceeded. This does not indicate that the valve(s) (or containment) are inoperable. LLRT testing is performed to determine total containment leakage which is quantified after evaluating all LLRT results to determine operability of primary containment. . Reopened to update RXSU coding based on outcome of assignment 03. <R> REP/REGE cancelled with Supervisor concurrence. | 02-00-RFW-V-10A
393956 | CR | 20190522 |  | 4 | SW-MO-12B | Y | N |  | N | NO | <D> Minor insulation damage being repaired with piece of heat shrink. <I> notified supervision, initiated cr. purchaced parts <N> SW-MO-12B CR at INPROG. Approved CR, moved to SRO for OPS Review. Repaired under WO 02112405.
393957 | CR | 20190522 | CAQ | D | SW-MO-2B Limit switch assembly bolting was loose | Y | N |  | N | YES | <D> **** Detailed Description **** During as-found testing on SW-MO-2B, the limit switch assembly was found loose. The diagnostic testing WO corrected the issue. CR is initiated for trending. <I> **** Actions Taken **** SW-MO-2B diagnostic testing WO corrected the condition. No anamolies were identified in the diagnostic traces. The as-found test showed SW-MO-2B was able to perform its design function as required. **Condition is corrected**No further action is required. | 02-00-SW-MO-2B
393961 | CR | 20190522 |  | 4 | M&TE Reject | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0050995 Tennelec Scaler/Timer - Model 535P found OOT. Not used During Calibration cycle - No Plant Impact. Rejected - Count Rate Check - 85 MHz. Found white, gooey substance had leaked length of one circuit board. <I> **** Actions Taken **** None Trending Purposes only DEF# 7039A written
393962 | CR | 20190522 | CAQ | D | M&TE Rejected | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #45507 Biddle Test Set - model 220015 Found OOT - Used for Info Only - No Plant Impact. Rejected - Current is sketchy, Unreliable. DEF# 7040A written No Action <I> **** Actions Taken **** None Trending purposes only
393965 | CR | 20190522 |  | 4 | R24 LL: OCC LLRT resource allocation | N | N |  | N | NO | <D> FIN Craft resources were allocated to the LLRT Team afternoon of 5/21/18. The individual taped a high pressure hose down at SE 522. This was the highlight of the afternoon while getting a 1 mRem. There was no plan in place and throwing more bodies was a waste of FIN resources. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
393966 | CR | 20190522 |  | 4 | R24 LL: OCC LLRT resource allocation |  |  |  | N | NO | <D> **** Detailed Description **** FIN Craft resources were allocated to the LLRT Team afternoon of 5/21/18. The individual taped a high pressure hose down at SE 522. This was the highlight of the afternoon while getting a 1 mRem. There was no plan in place and throwing more bodies was an inefficient use of FIN resources resulting in unnecessary dose. <I> **** Actions Taken **** Discussed issue in the morning D15
393967 | CR | 20190522 |  | 4 | B43 Fire Alarm System TROUBLE issues reported | N | N |  | N | YES | <D> **** Detailed Description **** Security Communications Center received a TROUBLE signal from Building 43 fire alarm system on Saturday, May 18 at approx. 2130 hrs. This automatic TROUBLE alarm was recorded 5 times within 30 minutes. See EDMS for a history log of over 25 TROUBLE alarms from this fire alarm panel in one month, since April 18, 2019 to May 18, 2019. See EDMS for a copy of the log. This fire alarm panel needs to be investigated. <I> **** Actions Taken **** SCC Officer used checklist 22 to make notifications. SCC dispatched an officer to assess the alarm. No other response recorded. <N> **** Equipment Description **** Building 43, Transformer Yard Facilities fire alarm issue. Does not affect the power block. | 02-00-FP-CP-S43
393968 | CR | 20190522 |  | 4 | (QA) MS-LS-24B Gouges on Pipe | N | N |  | Y | YES | <D> **** Detailed Description **** (QA) Two gouges/scribe marks, which appear to be existing, were identified on 1 inch sched. 160 pipe at the edge of the heat affected zone of welds 4 and 9 as shown on weld record 2-13800. The scribe marks have the appearance of being made by a thin saw blade, appear to greater than 1/32â€ depth and are ~80% of the pipe circumference. Issue was identified during weld inspection activities for the replacement of MS-LS-24B per WOT 02135924-01. Field welds for this work has not been accepted due to the proximaty of the gouge to the heat affected zone, and will require engineering determination or repair. . . <I> **** Actions Taken **** Notified Craft Supervisor, Weld Engineering, QC Level III and Qualtiy Services Supervisor. <N> Code Programs recomends blending out the scribed line from a "notch" which is unacceptable to rounded smooth transition with a 3/8" round file. . QC verified scribed line has been removed to a rounded smooth transition. No sharp edges remain. When measured, filed area appeared to be < 1/32â€ depth. Remaining field welds on weld record 2-1300 have been inspected by QC, found satisfactory and signed off within the weld record. | 02-00-MS-LS-24B
393970 | CR | 20190522 |  | 3 | R24 LL: Main generator HIPOT testing | N | N |  | N | NO | <D> **** Detailed Description **** Main generator HIPOT testing is a task within the 01 main inspection task. HIPOT testing should be a seperate task to allow proper coordination and scheduling of the activity. <I> **** Actions Taken **** Discussed with EOC and OCC
393971 | CR | 20190522 |  | 4 | HD-MO-20A actuator grease degradation due to steam leak | N | N |  | N | YES | <D> **** Detailed Description **** HD-MO-20A actautor was removed to support repack, The actuator is severly degraded and requires refurbishment. <I> **** Actions Taken **** 2 spare actuators are available on elevation 507 to refurb and perform a drop swap for the degraded actuator. | 02-00-HD-MO-20A
393973 | CR | 20190522 |  | 4 | M&TE Reject | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0065619 IND SCIENTIFIC MONITOR, GAS - Model ITX found oot. Not used During Calbration Cycle - No Plant Impact. Unit alarming because of bad O2 sensor. No replacement O2 sensors are being manufactured anymore. As found data not be obtained. This unit is to be rejected. DEF# 7041A
393976 | CR | 20190522 |  | 4 | COND-CB-C1C had silicone in the A and C phase puffer tubes | N | N |  | N | YES | <D> **** Detailed Description **** Curing a detailed inspection of COND-CB-C1C per 10.25.13 the steps to test the puffer tubes failed. Upon inspection the tubes were found blocked with silicone. The tubes were removed and cleaned and tubes re siliconed on. The breaker then passed the puffer tube test. <I> **** Actions Taken **** Notified Engineering. | 02-00-COND-CB-C1C
393977 | CR | 20190522 | CAQ | D | R-DOOR-R304 not functioning as designed | Y | Y |  | N | YES | <C> CR reopened to cross reference additional WR 29145363, marked completion required box, then taken back to complete <D> **** Detailed Description **** DOOR-R304 not functioning as designed. The door is having issues with the dog latch. Contact Security for more information x2185 <I> **** Actions Taken **** CR/WR Generated | 02-00-R-DOOR-R304
393978 | CR | 20190522 |  | 4 | CM-11 At GSB PAP RCA Exit Point Out Of Service | N | N |  | N | YES | <D> **** Detailed Description **** The standby lever on CM-11 HP-EQ-53253 located at the GSB PAP RCA exit point is broken and will not trigger the CM-11 to stop counting while the detector is in its holder. <I> **** Actions Taken **** A second CM-11 is currently in working condition at the PAP, so 53253 was unplugged from its power source to prevent it from continuously counting. Notified RP Supervision and initiated WR. <N> **** Equipment Description **** GSB PAP RCA Exit Point | 02-00-HP-EQ-53253
393979 | CR | 20190522 |  | 4 | Close RHR-V-18C in support of WO 02107551 | Y | N |  | N | YES | <D> **** Detailed Description **** RHR-V-18C will be closed in support of RHR-V-4C leak-by investigation. | 02-00-RHR-V-18C
393983 | CR | 20190522 |  | 4 | Dehalogenation skid affects CBD-FR-10 | N | N |  | N | YES | <D> **** Detailed Description **** On 4/27/19 ot approx 0500 CL-SKID-2 (dehalogenation skid) was shudown by the project. this caused the current loop for CBD-FT-10 to no longer have a cuurent path for CBD -FT-10 and caused CBD-FR-10 indication to go to zero. Per Discussion with the project manager the dehalagenation skid will not be ready until after the new fiscal year (mid July). To restore CBD-FR-10 to service the wiring for CBD-FT-10 needs to be restored to the current revision of EWD-56I-002 (Rev 17). Prior to turning the dehalagenation skid over to operations the wiring will need to be retored to EC16616 design. the return of the wiring will be tracked by the EC closeout punch list per the project manager. <I> **** Actions Taken **** Wrote CR and WR. need to add two tasks to WO 02119558: One to move wire from CBD-FT-10 from TB3-13 to TB3-11 in E -IR-17. the other task will need to move the wire back to TB3-13 when the project is ready to perform post modification testing in task 05 | 02-00-CBD-FT-10
393984 | CR | 20190522 |  | 4 | CW BLD 29 | N | N |  | N | YES | <D> **** Detailed Description **** Was investigating CBD-FT-10 and discovered CW BLD 29 was installed without any maintenance technical involvement. Maintenance needs knowledge about this skid for future troubleshooting and repair. <I> **** Actions Taken **** Notified Supervisor <N> **** Equipment Description **** CW BLD 29 CW Building 29 will be maintained and repaired by an outside vendor. No further action required.
393985 | CR | 20190522 |  | 4 | CW BLD 14 | N | N |  | N | YES | <D> **** Detailed Description **** Was investigating CBD-FT-10 and discovered CW BLD 14 was installed without any maintenance technical involvement. This insulation caused CBD-FT-10 to fail when power was removed. Maintenance needs knowledge about this skid for future troubleshooting and repair. <I> **** Actions Taken **** Notified Supervisor <N> **** Equipment Description **** CW BLD 14 CW Building 14 will be maintained and repaired by an outside vendor. No further action required.
393986 | CR | 20190522 | CAQ | D | Revise limitations on use for MDR relays, CATID 68604340 | N | N |  | N | NO | <D> **** Detailed Description **** CR 371655 documented DG2 failure develop voltage during a hot restart following a 24 hour run. The apparent cause evaluation identified binding following extended operation or extended energization of the relay. One of the corrective actions (reference CR 371655-08) was to implement a limitations on use to require burn in of the relay and a hot restart to verify replacement relays would function properly after being energized for several hours. (See EDMS for additional details) . This means all replacement relays must pass an 8 hour burn-in, simulated hot restart following the burn in AND must have as PMT a 24 hour run followed by an actual hot restart. . Engineering Evaluation: The intent of the action was to either perform an 8 hour burn-in with simulated hot restart, OR (not AND) 24 hour run followed by an actual hot restart as PMT. Based on the event described in CR 371655 an 8 hour burn in followed by functional testing (simulated hot restart) is adequate to ensure proper operation of a relay that has been energized for an extended time. Both limitations are not required as they are duplicate tests and performing one of two tests poses no risk to the performance of the relays. Recommend revising the limitations on use (LOU) to allow either of the two tests rather than both tests. <I> **** Actions Taken **** DIscussed with EOC and OCC, initiated CR to document condition and track resolution. <N> The LOU has been revised to allow either of the two tests rather than both tests.
393987 | CR | 20190522 | CAQ | C | Procedure noncompliance during irradiated component movement | N | N |  | N | NO | <D> **** Detailed Description **** On 5/22/19, the Radiological Controls of the Upper Containment required by HPI-12.74 were invoked for removing LPRMs from the core, manipulated within the flooded reactor cavity from the Refuel Floor. Because these items are irradiated components, the upper Drywell exclusion area and area radiation monitors required by HPI-12.74 on the DW 572 were verified to be in place prior to commencing the activity at 0130. However, work was permitted to continue on RCIC Valve 63, located on DW 541. This is contrary to the instructions listed in HPI-12.74 Step 5.2.2.3 which specifically precludes working on this valve due to its proximity to the N6 Nozzle. Upon discovery of the work, access to the area was restricted by RP supervision in accordance with HPI -12.74. <I> **** Actions Taken **** A review of access records found. No elevated dose rates were present in the area and the highest dose rate measured on an individualâ€™s ED was 127 mR/hr. which is in-line with the expected dose rates in the area. RP Supervisor, OCC RP and RPM were notified.
393988 | CR | 20190522 |  | 4 | Access Badging Computer did not operate as expected. | N | N |  | N | YES | <D> **** Detailed Description **** Access badging computer assigned to Bldg. 184 did not operate as expected. Video capture did not work as designed, causing access personnel to utilize the main access station at Bldg. 64. Cause was determined to be hardware related to the associated accessories. <I> **** Actions Taken **** Program Manager Access Authorization advised. Senior Engineer for Access Badging contacted and worked on system until cause was determined. Security Services Manager was advised. | 02-00-SEC-CPU-IEBS/2
393990 | CR | 20190522 |  | 3 | Workers contaminated during shielding installation | N | N |  | N | NO | <D> **** Detailed Description **** Four workers were contaminated while shielding piping near RFW-FCV-10A/B on TG 471 elevation. Workers shielded the pipe without removing the highly contaminated insulation that was present. Workers were wearing face shields during the evolution. Workers were decontaminated and monitored in accordance with PPM 11.2.15.13. <I> **** Actions Taken **** RP Supervisor, OCC RP and RPM were notified.
393991 | CR | 20190522 | CAQ | C | EWD-46E-283 drawn incorrectly and needs revision (TOP-TIER) | N | N |  | N | NO | <D> **** Detailed Description **** At grid locations D8-D7 the "NORMAL SUPPLY" and "ALTERNATE SUPPLY" for E-CP-M3 should have their EPN's read as follows: NOMRAL SUPPLY E-PP-2DB CKT 3 DIV B VIA E-CB -PP2DB/3. ALTERNATE SUPPLY E-PP-3CB CKT 3 DIV A VIA E-CB -PP-3CB/3. See revision 13 of this same drawing for correct EPN labeling.
393992 | CR | 20190522 |  | 4 | As found RRC-MV/I-640B termenation doesn't match print |  |  |  | N | YES | <D> **** Detailed Description **** RRC-MV/I-640B appears to be missing the chassis ground (the print show one to term 5 and RRC-MV/I-640A is wired to reflect the print were as 640A isnâ€™t ). This may be the reason the TE didnâ€™t work as designed. We need WO to rewire or install and bench cal a new RRC-MV/I-640B. Ref WO 0212970601 REPLACE RRC-TE-23B and EWD-1E-001 <I> **** Actions Taken **** Wrote CR, contacted supervisor, need WO to fix | 02-00-RRC-MV/I-640B
393993 | CR | 20190522 | CAQ | D | SRM-MM-1B cable issue | Y | Y |  | N | YES | <C> CR reopened to cross reference additional WR 29150728, marked completion required box, then taken back to complete <D> **** Detailed Description **** 0204332601 SRM-MM-1B MOTOR MODULE REPLACEMENT-When Removing old Motor module the Speedo cable coupling that attached to motor has separated from the cable (looks like it should be crimped See photoâ€™s this needs to be evaluate by engineering. <I> **** Actions Taken **** wrote CR, contacted supervisor | 02-00-SRM-MM-1B
393994 | CR | 20190522 |  | 4 | Small scratches found on the TSW-HX-8 east tubesheet | N | N |  | N | YES | <D> **** Detailed Description **** During the as-found inspection on TSW-HX-8 under WO 02113088, small scratches/grooves were found on the surface of the east tubesheet. It seems like the scratches could provide a water leak path to the oil. Itâ€™s also believed that the scratches were caused by pulling the bundle out for cleaning in R22 (2015) and there was no reports or indications of water intrusion to the oil since. Based on that, the rough/sharp edges of these grooves will be cleaned during R24. Recommend action to system engineer to continue trending and monitoring water content in the seal oil cooler (air side). <I> **** Actions Taken **** Discussed with system engineer and initiated this CR <N> **** Equipment Description **** T441 | 02-00-TSW-HX-8
393995 | CR | 20190522 |  | 3 | R24LL Changes for planning tagging Generator |  |  |  | N | NO | <D> **** Detailed Description **** During the grounding of the Main Generator and Iso-Phase Bus, there was some confusion on where to hang grounds on the Iso-Phase Bus. The developed plan had the grounds being installed on the Generator side of TG-DISC-LINK/A, B, & C with static grounds being placed on the Generator side of the Clam Shell links. See Word Doc in EDMS for details. <I> **** Actions Taken **** Made sure Supervisor understood the plan for grounding Generator and IsoPhase Bus. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
393996 | CR | 20190522 |  | 3 | (NRC 2019 RP) Observation: Insulation Storage in Drywell |  |  |  | N | NO | <D> **** Detailed Description **** During the 2019 Rad Safety Inspection an observation was made by the NRC that the current configuration for storage of insulation in the Drywell could potentially present an opportunity for personnel to retrieve insulation without HP approval. The insulation is currently staged inside of a posted LHRA boundary. <I> **** Actions Taken **** Recommend assignment to AR-RADPR to evaluate observation. <N> Per Chemistry/Radiological Services Manager, this CR is being trended to AR 00362637 R-24 Lessons Learned SA (cross referenced) . No further action is required at this time.
393997 | CR | 20190522 |  | 3 | Use of Manual RCA Access Process for DW Entry |  |  |  | N | NO | <D> **** Detailed Description **** On 5/20/19, an individual was accessed into the Undervessel area of the Drywell on RWP 3000-4318 via manual means by RP personnel. This was done because the individual did not have sufficient margin to access RWP as its ED setpoint was 600 mRem for dose. This elevated dose setpoint was because it had been the RWP used to exchange the CRDMs on the previous shift with dose rates up to 77 R/hr. This ED setpoint was no longer required as all of the highly activated CRDMs had been removed. But, the RWP was chosen for this activity as it best outlined the contamination control requirements for extracting and servicing the newly installed CRDMs. <I> **** Actions Taken **** The use of the manual access method is permitted for specialized use as determined by RP Supervision by GEN -RPP-11. All RWP entry and coverage requirements for the activity were met. But was a non-conservative approach as it bypasses the TES computer systemâ€™s mechanisms to ensuring personnel have sufficient margin available for the entry as well as automatically tracking the individualâ€™s dose. In addition, not all of the requirements outlined in GEN-RPP-11 when using an alternate means of RCA access were followed regarding the use of a Radiation Exposure Card to document this transaction and ensure the individualâ€™s dose margin was updated promptly. Dose has been updated, Radiological Services Manager notified and reviewed issue.
393998 | CR | 20190522 |  | 3 | Positive Exit Whole Body Count result |  |  |  | N | NO | <D> **** Detailed Description **** A contractor (employee ID xxxxx) received exit whole body count (WBC) on 5/18/19 and left the site. When the Whole Body Count was reviewed a couple days later, it was noted that the WBC identified less than 6 nCi of Co-60 with an uncertainty of 37%. The contractor had cleared the personnel contamination monitors upon exiting from the RCA and protected area. Recommend Rad Support evaluate to confirm that activity less than screening levels, and adequate operation of personnel contamination monitors. <I> **** Actions Taken **** Discussed with co-worker and supervision. <N> CR edited to remove Employee ID Number.
393999 | CR | 20190522 |  | 4 | E-TR-6/63 is leaking nitrogen |  |  |  | N | YES | <D> **** Detailed Description **** E-TR-6/63 was indentified to have a bad level indicator and while performing WO 02111307 to fix the problem, it was discovered that the level indicator gauge was not bad, the XFMR was just over filled with the silicon fluid. The N2 as-left level was 2 Psi and after the XFMR was in service for 2 days, the N2 level dropped to 0 Psig. AR CR 393696 was initiated and under WR 29148806 FIN team filled E-TR-6/63 with 3 Psi of N2 on 5/21/2019. On 05/22/2019, the nitrogen level was observed to have drooped agin to 0 psi. No oil leak observed. E-TR-6/63 needs to be inspected for N2 leaking. <I> **** Actions Taken **** Talked to EOC <N> We need to inspect for the N2 leak because the N2 leak may cause moisture contamination to the XFMR | 02-00-E-TR-6/63
394000 | CR | 20190522 |  | 4 | TO-42-S21B1A bucket rebuild - incorrect power wire installed | N | N |  | N | NO | <D> **** Detailed Description **** WO# 02072954 (TO-42-S21B1A for TO-P-EOP) directs replacement of obsolete components (disconnect switch, contactors, etc.). The power wiring is also being replaced. The original replacement wire (#2 AWG) was installed; however the correct wire should be #4/0 AWG. The bucket is still under clearance order and in progress - this will require rework of the installed wire. Specific direction for wire size was not included in the installing task; wiring was pre-fabricated during bench test. <I> **** Actions Taken **** The installing work order is still in progress; the wire will be replaced.
394004 | CR | 20190522 | CAQ | D | RCIC-V-601 Extremely hard to operate. | Y | N |  | N | YES | <D> **** Detailed Description **** RCIC-V-601 Extremely hard to operate. Opened to perform leak rate on RCIC-V-40 and RCIC-V-68. When restoring from test, RCIC-V-601 was taken closed and was found to be leaking by. Valve was taken closed more by hand and was still leaking by. <I> **** Actions Taken **** CR/WR Supervision and OCC notified. | 02-00-RCIC-V-601
394007 | CR | 20190522 |  | 3 | (QA) 4 of 6 WOT Cover Sheets Missing Initials/Printed Name |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Four of six Work Order Task (WOT) front cover sheets reviewed by Quality were missing the initials and printed name of everyone that had performed work, contrary to SWP -PRO-01 "Procedure and Work Instruction Use and Adherence". Two WOTs were already at "Finished" status, and two WOTs were at "Working" status. This is a procedure use and adherence issue with no actual consequence because the WOTs had not yet become a Quality Assurance Record (QAR). Potential consequences include rework to find the missing persons and get them to sign the WOT cover sheets, and possibly more rework to amend the QARs, if the errors are not caught in the Supervisor reviews prior to the creation of the QARs. Requirements: â€¢ MI-1.8 "Conduct of Maintenance" rev 072-002 section 7.0 requires strict compliance with SWP-PRO-01 for work documents. â€¢ SWP-PRO-01 rev 032-002 requires signing off a step by initialing the step, then entering the initials and a printed name on the front cover sheet." [italics added] Factual Basis: On 5/22/19, these two WOTs at "Finished" status had six performers (four Mechanics and two Electricians) initial/date in the body of the WOT instructions, but each front cover sheet was missing the initials and printed name of the same two Electricians: â€¢ WOT 02112564-01 "DEH-SV-TRIP/B, QUADVOTER SOLENOID VLV REPLACEMENT" â€¢ WOT 02112565-01 "DEH-SV-TRIP/C, QUADVOTER SOLENOID VLV REPLACEMENT" On 5/22/19, this WOT at "Working" status had two performers (I & C Technicians) initial/date in the WOT instructions, but the front cover sheet was missing the initials and printed name of both I & C Technicians: â€¢ WOT 02118048-09 "TO-PS-ZA1 REPLACEMENT" On 5/22/19, this WOT at "Working" status had one performer (Mechanic) initial/date in the WOT instructions, but the front cover sheet was missing the initials and printed name of this Mechanic: â€¢ WOT 02078413-11 "TO-HX-2A â€“ CLOSE, TORQUE BOLTS" Insights: â€¢ Upon notification by Quality, the Component Group Manager for the Electrical Shop took both WOT 02112564-01 and WOT 02112565-01 from "Finished" to "Working" and obtained the missing signatures from the two Electricians. â€¢ Each of the four WOTs above were being worked as an electronic Work Package (eWP), which keeps the cover sheets and the instructions in two separate files, which hinders performers in entering initials and printed names on the cover sheets. (Three paper WOTs reviewed had initials and printed names on the cover sheets.) <I> **** Actions Taken **** Contacted the three Component Group Managers in Maintenance. . Recommend routing this CR to Maintenance. . This is a Deficiency identified during Quality Surveillance SR-19-01.
394008 | CR | 20190522 |  | 4 | N1 Hi-side Bushing Terminal Pads found loose |  |  |  | N | YES | <D> **** Detailed Description **** During the ground drops in support of hi-pot, the terminal pads on the N1 transformer high-side bushings were found loose after noticing one askew (see picture in the EDMS). These terminal pads need to be re-tightened before the N1 highside links are re-installed (WO 02122003-05 (E) INSTALL LINKS- RECONNECT XFMRS & GEN AFTER HI-POT). <I> **** Actions Taken **** Notified Supervision, System Engineer and contacted OCC. | 02-00-E-TR-N1
394009 | CR | 20190522 |  |  | CEP-V-2A exceeds leak rate admin limit |  |  |  | N | YES | <D> **** Detailed Description **** The as-found leak rate for CEP-V-2A containment side flange was 316 sccm which exceeds the admin limit of 50 sccm. <I> **** Actions Taken **** Notified LLRT SRO, OCC, and EOC. | 02-00-CEP-V-2A
394010 | CR | 20190522 | CAQ | C | Communicator failed testing | N | Y |  | N | YES | <D> **** Detailed Description **** Security performs a test of the Communicator system at shift change. At 6pm 5/22/2019 the officer was unable to log into the Primary Communicator system. After multiple attempts, the Officer proceeded to activate the test scenario on the Backup system. The Backup system failed to send any pages to the pager. <I> **** Actions Taken **** Spoke with the Security Officer to determine what issues were experienced. Performed a test and recieved the same response the Officer had reported. Called the Vendor to report the issue, and was connected to a tech rep. The tech was able to resolve the issue with the Backup system, which was confirmed with test completed by the IS Analyst and Security. Security was instructed to use the Backup Notification system until further notice. They were also asked to verify the information is passed on during shift change. IS leadership and EP were notified of the issue, and the resolution at this time. The Backup system is serving as our Primary means of Emergency Notification. <N> **** Equipment Description **** Cloud service | FW-00-SOFT-COTS-COMM NXT
394013 | CR | 20190522 | CAQ | C | AL LLRT RCC-V-21, RCC-V-40 and RCC-V-219 exceeded admin limi | Y | N |  | N | YES | <D> **** Detailed Description **** Combined As-Left LLRT of RCC-V-21, RCC-V-40 and RCC-V-219 exceeded its admin limit of 1475 sccm with a recorded leak rate of 1960 sccm. <I> **** Actions Taken **** Notified LLRT SRO and OCC | 02-00-RCC-V-21,02-00-RCC-V-219,02-00-RCC-V-40
394014 | CR | 20190522 |  | 4 | REA-DPIT-3B plastic indication cover broken |  |  |  | N | YES | <D> **** Detailed Description **** REA-DPIT-3B was reported as broken. Discovered plastic cover for digital indication on ground in three pieces. Indication appears to be functioning. <I> **** Actions Taken **** Put cover back on and held in place with red tape. | 02-00-REA-DPIT-3B
394015 | CR | 20190522 | CAQ | D | (QA) Tech Spec Surveillance not reviewed by Operations |  |  |  | Y | NO | <D> **** Detailed Description **** Technical Specification Surveillance ESP-B11-B101, 24 Month Battery Testing of 125 VDC E-B1-1, was completed on 5/17/19 but not reviewed for Operability by CRS/Shift Manager (see WO 02111921-01). Review of EWP workflow process shows that an Ops Review was not completed after WO was taken back to working. Subsequently, an Electrical Craft Supervisor reviewed and approved the surveillance for closure. Quality informed the CRS and the CRS has reviewed the surveillance and signed as SAT. <I> **** Actions Taken **** Notified CRS and SM.
394016 | CR | 20190522 | CAQ | D | CCTV 46 | N | N |  | N | YES | <D> **** Detailed Description **** CCTV 46 lost video feed. <I> **** Actions Taken **** Compensatory measure put in place. | 02-00-SEC-CCTV-ISFSI/46
394017 | CR | 20190522 | CAQ | C | CEP-V-2A exceeds as found leak rate admin limit | Y | N |  | N | YES | <D> **** Detailed Description **** The as-found leak rate for CEP-V-2A containment side flange was 316 sccm which exceeds the admin limit of 50 sccm. <I> **** Actions Taken **** Notified LLRT SRO and OCC <N> Engineering is requesting cancellation of the REP/REGE assignments on this CR because only the admin limit was exceeded. This does not indicate that the valve(s) (or containment) are inoperable. LLRT testing is performed to determine total containment leakage which is quantified after evaluating all LLRT results to determine operability of primary containment. <R> REP/REGE assignments cancelled with Supervisor concurrence. | 02-00-CEP-V-2A
394018 | CR | 20190522 |  | 4 | BOP TURN STILE |  |  |  | N | YES | <D> **** Detailed Description **** WHILE NOT ALLOW ACCESS | 02-00-HP-EQ-42854
394019 | CR | 20190523 |  | 4 | IBM-8 TB 5O1 WEST |  |  |  | N | YES | <D> **** Detailed Description **** DETECTOR FAILURE <N> **** Equipment Description **** TB 501 | 02-00-HP-EQ-C018698
394020 | CR | 20190523 | CAQ | C | RWCU-FT-16 FOUND OOT DURING CALIBRATION | Y | N |  | N | YES | <D> **** Detailed Description **** While performing WO02094539 Task 1 RWCU-FT-16 was found OOT during work step 4.5. <I> **** Actions Taken **** CR Generated to adress OOT findings. Transmitter FT-16 being replaced under same work order. As-Lefts will be performed after transmitter replacement <N> **** Equipment Description **** Reactor 501' <R> REP/REGE assignments not needed. Engineering provided information and attached it to the in-progress notes of the REGE assignment. They are being reproduced here. The REGE was completed, the REP will be cancelled. No further actions necessary. . The transmitter is for the high blowdown flow isolation of RWCU-V-1. The transmitter was OOT for a stand alone transmitter cal using +/- 0.04 mA as the calibration Acceptance criteria prior to EQ replacement. We donâ€™t normally calibrate just the stand alone transmitter since we test the loop and the loop would have been in cal. The loop has the transmitter and the Flow Switch. They input at the transmitter and verify the flow switch trips within the desired band. Since we are replacing the transmitter (due to EQ life), they did an as found on just the transmitter only (transmitter dp input to transmitter mA output). The loop would have still been in cal. The ISP would have checked the loop and they would have N/Aed the transmitter calibration since the loop would have passed. This is what we did the last two performances of this 2 yr ISP. There was no failure and the equipment would have met the Technical Specifications. It just didnâ€™t meet the stand alone transmitter calibration which has acceptance criteria not based on any technical specifications, it is +/- .04 mA across the entire output of the transmitter. -- | 02-00-RWCU-FT-16
394021 | CR | 20190523 | CAQ | C | foreign material floating in wetwell ~AZ 230 | Y | N |  | N | YES | <D> **** Detailed Description **** Mechanics were cleaning up and prepping for RHR spray/drain and noticed 3 items floating in the wetwell. A max air hood, an orange PC glove, and another unidentified red object. Approximate location is AZ 230 on the outside edge of the pool. <I> **** Actions Taken **** Notified supervisor and FME Vital island. | 02-00-C-TK-1
394022 | CR | 20190523 | CAQ | D | Rod 38-19 bad indications during PPM 6.5.9 | Y | N |  | N | YES | <D> **** Detailed Description **** On 5/23/19 during the performance of PPM 6.5.9, rod 38-19 had no indication (showed blanks) for positions 46, 36, 26, 16, or 06. The Rod Worth Minimizer on those positions showed "??" and the N2 screen on TDAS/PPC showed "BA" for bad indication. <I> **** Actions Taken **** Informed CRS, verified four rod display was operating properly | 02-00-CRD-DRVE-3819
394023 | CR | 20190523 |  | 3 | Potential miss-positioned valve |  |  |  | N | NO | <D> **** Detailed Description **** An individual was reaching down to pick up a tool bag and felt that he had moved a hand wheel on RCC-V-83D. The individual came out of the Drywell and notified the Drywell Coordinator and their Supervisor. Operations was contacted and the valve was walked down with the individual and an Operator to identify the valve. <I> **** Actions Taken **** Contacted Management and Operations. <N> The operations walkdown concluded that the valve identified was not manipulated. The valve was still in its normal procedurally controlled position. Williams Plant Services.. This is a good example of following station procedues. I recommend this CR be closed. Event discussed in Williams D15s.
394024 | CR | 20190523 |  | 3 | Replacement TO-HX-1A inlet/outlet head misalignment | N | N |  | N | YES | <D> **** Detailed Description **** The new replacement stainless steel inlet/outlet head for TO-HX-1A, turbine oil heat exchanger, does not align properly with the inlet/outlet TSW piping. See EDMS photos. Evaluation is needed to determine if the old head can be reused or if the new head can be reworked by the manufacturer. <I> **** Actions Taken **** Notified EOC. <N> **** Equipment Description **** T501 east end WO 02111477-25 is at working status to modify the TO-HX-1A head piping for fitup per EC 17185. It is not necessary to evaluate the old head for reuse or to modify the inlet head. . This CR is being closed based on WO 02111477 per recommendations from Engineering see EDMS | 02-00-TO-HX-1A
394025 | CR | 20190523 |  | 4 | R24 - LL scafolding |  |  |  | N | NO | <D> **** Detailed Description **** On the fire protection project (00820801), the logic ties for tasks to remove scaffolding are tied to the completion of the installation task not the PMT task. This existed in 19 of 21 cases resulting in one case where a scaffold was taken down pre-maturely. The logic ties were reviewed multiple times during the planning of R24 so opportunities were missed to catch this error in logic. <I> **** Actions Taken **** Reported the issue to the OCC and provided input to the outage scheduler to correct this logic. Also, informed Williamsâ€™s management not to remove scaffolding for fire protection without project concurrence.
394026 | CR | 20190523 |  | 3 | R24 Lessons Learned CW Basin Dewatering |  |  |  | N | NO | <D> **** Detailed Description **** Consider having two low head Godwin pumps installed for dewatering the circulating water basin. In addition to installing a second pump consider removing the restricting orifice in the circulating water blow down line to improve dewatering times. A second flange was fabricating in R24 to support two pump operations. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817. Per email from Eric Franke (see EDMS) two actions are needed 1) install 2 Godwin pumps to facilitate a faster drain rate. Eric created an action per the ops R25 AR 396117-06 to track 2) The other action is to consider removing restricting orifice CBD-RO-1 to allow faster blowdown flowrates with the temporary blowdown rate. AR Eval was created and cross ref'd to this AR.
394027 | CR | 20190523 |  | 4 | R24 Lessons Learned - Use of Inductive Heating |  |  |  | N | NO | <D> **** Detailed Description **** During future outages the site should consider having inductive heating tools/procedures/qualified personnel on site or a vendor service available to apply inductive heating on components to support maintenance. During R24 MS-V-24B had a poppet that could not be removed. It took approximately 15 hours to get TEAM on site to support using inductive heating.
394028 | CR | 20190523 | CAQ | C | CSP-V-93 exceeds AF leak rate admin value | Y | N |  | N | YES | <D> **** Detailed Description **** The leak rate admin limit of 148 sccm was exceeded for CSP-V-93 (TSP-CSP/X66-R801 per WO 02112651). Measured as -found leakage is 474 sccm. <I> **** Actions Taken **** Notified LLRT SRO and OCC <R> The REP/REGE assignments for this CR are not required and are being cancelled. This condition is not reportable to the NRC and does not challenge past operability of plant equipment. Concurrence for cancellation has been obtained from Regulatory Affairs Management. | 02-00-CSP-V-93
394033 | CR | 20190523 |  | 4 | (R24 LL) Oversight during High Risk Work Plan development |  |  |  | N | NO | <D> **** Detailed Description **** During execution of High Risk Work Plan briefing for RHR -V-4C the question was raised about the fact that the fabricated plate for system closure had only 8 bolt holes as designed and fabricated, while the valve had 24 bolts in the bonnet. The issue raised pertained to the possibility of having more than one stuck bolt that did not match the current pattern drilled in the fabricated plate. The plan was not written to accommodate for studs that may have been stuck outside of the 8-bolt pattern of the plate fabricated for the contingency. <I> **** Actions Taken **** The issue was discussed during the briefing and later brought to the OCC. The path forward was decided to remove nuts and bolts leaving 8 that matched the plate pattern before removing the last 8, therefore meeting the intent of the closure device. After this was accomplished, disassembly was allowed to proceed. Wrote this CR. No further action required.
394034 | CR | 20190523 |  | 4 | XD-03 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** XD-03 requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** XD-03 taken out of service. Contacted OCC and I&C Component Group Manager. Initiate CR/WR | 02-00-SEC-XD-3
394035 | CR | 20190523 |  | 3 | R24LL: Direction for alt power for under vehicle lights |  |  |  | N | NO | <D> **** Detailed Description **** Deenergization of either E-MC-2D or E-MC-3C removes power from Transformer Yard receptacles that provide power to lighting under vehicles staged there. The applicable procedures should include instructions to provide temporary lights under vehicles in the Transformer Yard for the duration of the respective outage. The specific sections are SOP-ELEC-SM2-MAINT, section 5.5, Removal of MC2D from service and SOP-ELEC-SM3-MAINT, section 5.5, Removal of MC3C from service. <I> **** Actions Taken **** Found alternate source of power for lighting under vehicles during SL31 outage while LP2DB was tagged out. During the recent SL31 outage, most vehicles in Transformer Yard had lights fed from E-LP-2DB or E-LP-3CB. Since E -LP-2DB was deenergized for maintenance, the loss of E-LP -3CB resulted in no available receptacles to provide power for vehicles staged there. The procedure should have directed the placement of lights under any vehicles needing them.
394036 | CR | 20190523 |  | 3 | Temp Lift process cumbersome when work goes beyond 1 shift |  |  |  | N | NO | <D> **** Detailed Description **** While trying to perform the Hi Pot testing of the Isophase Bus, the work went over several shifts. The Temp Lift process doesnt allow for the next shift to sign on the clearance or temp lift unless the temp lift is rehung and a new temp lift is processed. This stops work and adds several hours to completing the task at hand. There needs to be a feature added to esoms to allow the next shift to sign on the clearance and temp lift even if it is already in place.
394037 | CR | 20190523 |  | 4 | R24 lesson learned - Temp lift process causing work delays |  |  |  | N | NO | <D> **** Detailed Description **** R24 lessons learned documentation. Refer to CR 394036. The current temp lift process is causing significant work delays to generator Hi-Pot testing when the work crosses shifts. On 5/22/19, a 3.5 hour delay occurred when the oncoming shift was required to rehang the temp lift 2018 -0074 and restore multiple grounds only to execute a new temp and remove grounds with the new shift of workers. Recommend evaluate and streamline current process to eleminate unnecessary work and schedule delays. This is a repeat issue from R23. <N> Duplicate of CR394036.
394038 | CR | 20190523 | CAQ | D | CRA-FN-1A2 tripped when restarting after RCC restoration | Y | Y |  | N | YES | <D> **** Detailed Description **** Started CRA-FN-1A2 and CRA-FN-1A1 IAW with SOP-CRA-OPS. Initially CRA-FN-1A2 inticated on. The light indication went dim initially and was visible with the lens cover removed. Then the light went out and recieved 4.813.H1 drop 1-3 "LOWER COOLER FAN1A TRIP". Recomend investigaing CRA -FN-1A2 breaker, fuses, and/or overloads per the ARP. <I> **** Actions Taken **** Wrote this CR and generated WR. | 02-00-CRA-42-7B2D,02-00-CRA-FN-1A2
394039 | CR | 20190523 |  | 3 | EC 17185 was not incorporated in WO 02111477 | N | N |  | N | YES | <D> **** Detailed Description **** The recommendations and installation requirements of EC 17185 â€œMaterial Change for TSW I/O Head on TO-HX-1Aâ€ were not incorporated into WO 02111477 work instructions. Recommend action to planning to review EC 17185, revise the work order accordingly and order the required materials. <I> **** Actions Taken **** Talked to planning and initiated this CR <N> **** Equipment Description **** t501 | 02-00-TO-HX-2A
394040 | CR | 20190523 |  | 3 | Process issue for temporary lifts |  |  |  | N | NO | <D> **** Detailed Description **** We have had multiple problems processing temporary lifts. Two options are available to perform a temp lift. First option is anyone signed on to accept the temporary lift, the second option is everyone signed on the clearance sign off and then perform the temporary lift. The problem is people are signing off vice accepting the temp lift when their task requires them to be signed on the clearance to perform the work that the temp lift is designed to perform. After the temporary lift is processed tags and the tags lifted the people are locked out of signing on the clearance(s) they need to be signed on to perform their work. The low proficiency of the temporary lift process is causing rework and delays to the schedule. <I> **** Actions Taken **** Informed supervision and the OCC.
394041 | CR | 20190523 |  | 3 | Add threaded holes for swivel hoist rings in valve bonnets. | N | N |  | N | YES | <D> **** Detailed Description **** Condensate check valves (COND-V-119A, B & C) were replaced in 2011 and were equipped with a tapped hole in the center of the bonnet to allow bonnet removal in a horizontal line application. Our valves were installed in a vertical line which eliminates the use of the tapped centered hole for disassembly. Maintenance requests installation of two swivel hoist rings at two locations (10:00 & 12:00) and between bonnet bolt holes to allow for safe removal of bonnets. The bonnet estimated weight is 757 lbs based on a bonnet thickness of 3.125â€ thick and diameter of 33â€. The distance between bolt holes is 3.875â€. Inventory of tool room has 1/2" x 13 TPI Crosby Hoist Rings. These rings are rated at 2500 Lbs. Recommend drilling holes 1.375â€ deep to allow use of the short and long swivel bolts. <I> **** Actions Taken **** Intiated CR for addition of lifting eye threads. . The proposed permanent configuration change requires an AR type EVAL with associated Engineering authorization unless generic approval for this type of change already exists. For the subject nonsafety-related non-ASME EPNs, preliminary assessment would be that a Commercial Change modification package (CCP) would be needed. <N> **** Equipment Description **** Turbine 441 Makes for an easier, safer and more efficient lift of valve bonnets, but not require for startup. | 02-00-COND-V-119A,02-00-COND-V-119B,02-00-COND-V-119C
394043 | CR | 20190523 | CAQ | D | Lost Full-In indication for CRD-HCU-3819 | Y | N |  | N | YES | <D> **** Detailed Description **** Lost Full-In indication for CRD-HCU-3819 while performing Restoration of CRDM per 6.5.9 for CRD-HCU-1455. This also resulted in a select block for the current selected rod for 02-23. <I> **** Actions Taken **** Infromed CRS/SNE/SM | 02-00-CRD-HCU-3819
394044 | CR | 20190523 |  | 4 | Unlabeled Chemical Found in Storage Cabinet | N | N |  | N | NO | <D> **** Detailed Description **** During monthly chemical storage area inspection, an unlabeled can of corrosion inhibitor (unknown manufacturer) was found in Kootenai Building Room 104D, Cabinet 17-0001. <I> **** Actions Taken **** Provided chemical to Environmental & Regulatory Programs for proper disposal. Coaching on chemical labeling standard was provided to and accepted by personnel who use corrosion inhibitor.
394045 | CR | 20190523 |  | 3 | Additional Kiosks needed in Bldg. 88 | N | N |  | N | NO | <D> **** Detailed Description **** R24LL: Operating experiance has proven that we need at least two more Kiosks in Builging #88 for refuelings. This outage we started with ony one station; the second was out of service for repairs for at least a week. The location of our two are at the same location as a coke machine and mens restroom causing severe foot traffic conjestion. For refueling outages, adding two more centrally located in the WPS office area would be a great help. <I> **** Actions Taken **** Initiated this AR
394046 | CR | 20190523 |  | 3 | Asset Suite Compliance Credit Dates for PM & SV | N | N |  | N | NO | <D> **** Detailed Description **** Currently in Asset Suite (P604) there is a check box flag â€œComplianceâ€ on the Model Work Order M101 panel. For tech spec Surveillances that flag should be checked so that the correct compliance completion date is captured and recorded in Asset Suite. This is important as it impacts the DADs crystal report for PPM 1.3.40. It was noticed recently that some completion dates on the DADs report are not the actual SV completed date as signed off by the CRS (eg Finished status 50). The Compliance Credit Date was added to the DADs report, but even then some of those compliance dates were â€œblankâ€. A review of model work orders (MWO) found that 471 out of 1203 SVâ€™s have that compliance flag NOT checked which means the compliance date is not recorded in Asset Suite. Further investigation with PM Coordinator and Asset Suite IS personnel could not determine why some MWOâ€™s have that flag checked and some do not. A procedure or instruction could not be found that gave direction or criteria for when that flag should be checked. More details for evaluation: When that flag is checked (Yes) on the MWO that carries forward to the generated PM/SV work orders. That results in the system capturing the â€œCompliance Credit Dateâ€ for that PM or SV when it is completed, and records that date on D083 (PMHST). That compliance date is then captured by the DADs report. If that box is not checked then the system only captures the date that the PM or SV work order goes to COMPLETE status 85. The complete status date can be days or even weeks after the PM or SV was finished (eg the date the SV is signed off by the CRS). . <I> **** Actions Taken **** Discussed with IS Asset Suite Support and PM Coordinator. Updated the DADs report for PPM 1.3.40. . Recommendation: Perform a data mod to check the compliance box for all MWOâ€™s associated with Surveillances where the PMID is in ACTIVE status. Also, data mod all the PMGEN WOâ€™s that were generated from those MWOâ€™s (eg the Futures) to check the box. This will ensure that going forward we will be capturing the actual Compliance Credit Date for those SVâ€™s. Establish a written procedure or instruction to provide guidance and criteria for which PMs and SVs should have the compliance box checked, who is responsible, etc. Validate that the DADs report for PPM 1.3.40 is capturing the correct compliance dates from Asset Suite. <N> The IS Evaluation and any actions associated with this request are documented and cross referenced to AR 00395222 - SV Model WOs be Flagged as Compliance WOs. . No further action of this CR is required.
394047 | CR | 20190523 |  | 4 | R24LL Move Vending Machine in Building 88 | N | N |  | N | NO | <D> **** Detailed Description **** R24LL: The need to move the vending machine in building 88 will help with hallway conjestions. The Machine is currently located next to two KIOSKS and the mens restroom. There is plently of room on the West wall next to the window for the machine. <I> **** Actions Taken **** Initiated this AR <N> Coca Cola has been contacted for resolution. No further action required.
394049 | CR | 20190523 |  | 3 | Observation Program Ehancement | N | N |  | N | NO | <D> **** Detailed Description **** In order to do more effective observations each of the premade observation forms in the "Create Observations" need to have a block to enter comments that fall outside the premade forms comments. The current premade observation forms force supervisors to fit all comments from an observation into specific premade comments that do not always apply. One of two things would help. First would be the creation of an "other" box at the end to capture comments that do not fit in the premade form. Second would be to bring back an observation form similiar to the old "Easy Observation" giving the supervisor the freedom to capture comments from observations over all categories caputred in the dozen or so observation forms we have.
394050 | CR | 20190523 |  | 3 | LPC Inner Cylinder 1 horizontal joint erosion | N | N |  | N | YES | <D> **** Detailed Description **** Steam erosion has removed material at the horizontal joint of Inner Cylinder 1 within LPC (MS-DT-1C). The leakage allows steam to leave the steam path and bypass the remaining stages of blades resulting in a small loss of efficiency/power generation. Additionally, there is evidence that the condition is causing degradation of the horizontal joint studs that hold the upper and lower halves together. <I> **** Actions Taken **** Discussed with EOC and OCC Working with OEM on risk and duration to repair and to prepapre for needed resources for repair work <N> **** Equipment Description **** LPC inner cylinder 1 | 02-00-MS-DT-1C
394051 | CR | 20190523 | CAQ | C | EWD-46E-281 has incorrect EPNs | N | N |  | N | NO | <D> **** Detailed Description **** Revision 16 of EWD-46E-281 has the incorrect EPNs. The EPNs were correct on revision 15. The Normal Supply breaker liste on EWD-46E-281 is E-CB-PP2DB/10. It should be E-CB -PP2DB/1. The Alternate supply breaker is listed as E-CB -PP3CB/1. It should be listed as E-CB-PP3BC/1. It also has that the normal supply goes to E-PP-2BB. The normal supply is powered from E-PP-2DB.
394052 | CR | 20190523 | CAQ | D | E-RLY-CR1AX suspected to have malfunctioned | Y | N |  | N | YES | <D> **** Detailed Description **** SGT-A inadvertently auto-initiated on 5/18/2019 after RPS-B was transferred to the alternate power source (ref. CR 393723). The suspected cause of the inadvertent SGT-A initiation is a malfunction of E-RLY-CR1AX contacts 115 -116. These contacts close to energize the coil of E-RLY -3TR/7 and start SGT-A on a FAZ signal (ref. EWD-108E-001 and EWD-46E-106A). When RPS-B is transferred to the alternate power source, power is lost to the RPS-B bus for a short duration of time which results in a loss of power to the coil of MS -RLY-K106 (ref. EWD-1E-096) and an RC-1 half trip. This RC-1 half trip in combination with a malfunction of E -CR1AX would have resulted in the observed inadvertent start of SGT-A. E-RLY-CR1AX is suspected to have malfunctioned based on the timing of the event and the various other symptoms observed. <I> **** Actions Taken **** Discussed with EOC, SM | 02-00-E-RLY-CR1AX
394053 | CR | 20190523 |  | 3 | SUPPORT RFW-49 CUT TO FACILITATE RFW-DT-1B OVERHAUL | N | N |  | N | NO | <D> **** Detailed Description **** DURING THE PERFORMANCE OF W/O 02047040-13, REMOVE INTERFERENCES, FOR THE OVERHAUL OF RFW-DT-1B IT WAS NECESSARY FOR SIEMENS TO CUT THE LOWER W4x13 STEEL MEMBER OF SUPPORT RFW-49 DUE TO INTERFERENCES. <I> **** Actions Taken **** GENERATED THIS CONDITIONAL REPORT & SIEMENS FIELD ENGINEER NOTIFIED THE OCC. IT IS RECOMMENDED THAT A ENGINEERED APPROVED BOLTED SPLICE PLATE BE ADDED AT THE CUT LINE TO FACILITATE FUTURE OVERHAUL WORK. . The proposed permanent configuration change requires an AR type EVAL with associated authorization from Engineering - preliminary assessment indicating a Commercial Change. modification package (CCP) would be needed. <N> **** Equipment Description **** RFW-DT-1B ROOM, WEST WALL, ELEV. 459'-9",
394054 | CR | 20190523 |  | 4 | E-IR-17 panel missing one of the latches | N | N |  | N | YES | <D> **** Detailed Description **** E-IR-17 panel missing one of the latches. Latch needs to be replaced. Panel door is secured with remaining latches <I> **** Actions Taken **** wrote CR and WR to replace latch | 02-00-E-IR-17
394055 | CR | 20190523 |  | 3 | E-BUS-ISOPHASE, HIPOT testing issues |  |  |  | N | NO | <D> **** Detailed Description **** During HIPOT testing of the isophase bus the HIPOT test equipment was not capable of maintaining the voltage levels as described in the work instructions. The work instructions specified 63 KV for 15 minutes, the test set shut down after 3 minutes. Review of the operating instructions for the test set indicates the test set was designed to shut down after 3 minutes for voltages above 60 KV. <I> **** Actions Taken **** Reviewed the work instructions and test results for all electrical tests on the isophase bus. Megger values and DLRO readings indicated excellent insulation condition. Review of the 3 minute HIPOT data showed steady voltage and leakage current of 0.9 microamps for the endire duration of the test. Test results are satisfactory and do not need to be repeated. Recommend assigning as 3 to System engineer to review HIPOT procedures and make recommendations for future testing. <N> **** Equipment Description **** Turbine building
394057 | CR | 20190523 |  | 3 | WO 02111993 step 4.19 needs removed |  |  |  | N | YES | <D> **** Detailed Description **** During the 500KV trip checks under WO 02111993 step 4.19 requires the ASHE to CUT out the contact extenders. By doing this it cuts out the 230 KV UV alarm from ASHE which during an outage is important. The rest of the outputs from these contact extender are for the 500KV system and not cutting out these extenders have no impact on the system since it is currently out of service. The purpose of this CR is to document that the contact extenders were cut out and then were recut in under WO 02111993 so the 230KV UV alarm could be returned to service. It was out of service from 0935-100. It is also recommended that PMID 21507 be updated to remove step 4.19 since it has not impact on the 500KV system and these contact extenders should remain in-service. | 02-00-E-TR-S
394058 | CR | 20190523 |  | 3 | B64 Fire Sprinkler Leak Discovered | N | N |  | N | YES | <D> **** Detailed Description **** A leak in the fire sprinkler piping has been discovered in Building 64 (Willamette Building). This is a pinhole that is leaking a cloud of water mist onto the ceiling tiles. The hole is on a section of 4 inch sch 40 carbon steel pipe. The B64 fire sprinkler system has been isolated. Office 141 is directly below the leak. The occupant has been vacated and ceiling tiles removed to allow water cleanup. Assign this AR to AR-TEFP to evaluate the pipe condition and have a bacteria sample taken and analyzed by Chem Lab. <I> **** Actions Taken **** Sprinkler system isolated. Impairment written with compensatory measures. Work Request written. Non-essential fire protection. <N> **** Equipment Description **** B64 Fire Sprinkler System
394061 | CR | 20190523 | CAQ | D | RPS-POS-33T/2B | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** 02111944-01 REPLACED FAILED LIMIT SWITCH. DUE TO FAILURE THE ARM POSITION IS UNKNOWN. HOWEVER THIS WILL BE ADDRESSED IN THE PMT 02111944-02 ARM SPUN FREELY AND APPEARED LOOSE. <I> **** Actions Taken **** CR ENGINEERING ANALYSIS <N> **** Equipment Description **** RPS-POS-33T/2B CR references limit switch replaced under 02111944-01. This WO task is at ready. Limit switch replaced under 02118077 -01.
394062 | CR | 20190523 |  | 4 | (NRC 2019 RP) PSF Radiological Source Label Discrepancies | N | N |  | N | NO | <D> **** Detailed Description **** During an NRC radioactive source inspection it was discovered that three source labels SID numbers 08-132, 08-133, and 2-79-033 did not have the activity units ( ie: uCi) on the label. Also SID 2-84-058 was found faded and in need of replacement. <I> **** Actions Taken **** Assured NRC individual the labels would be repaired and replaced in a timely manner, and a picture of the fix would be forwarded to her. Notified HP Supervision. Documented occerence via Condition report. replacement. <N> Labels have been replaced; see pictures in EDMS. No further action required.
394063 | CR | 20190523 |  | 4 | Revise PPM 10.25.139 main generator hipot | N | N |  | N | NO | <D> **** Detailed Description **** Revise PPM 10.25.139 to allow the option of performing the main generator HIPOT test without breaking the neutral connection. . See EDMS for marked up procedure <I> **** Actions Taken **** Discussed with EOC, OCC and Siemens <N> Procedure change completed.
394064 | CR | 20190523 |  | 3 | Individual left site prior to RWP sign-out | N | N |  | N | NO | <D> **** Detailed Description **** Individual with DLR # 00028655 terminated employment without first signing out of RWP at HP access. <I> **** Actions Taken **** Request a lost SRD dose estimate be performed and notified RP supervision. Recommend CR to RP-ops to lost SRD dose estimate and update RCA entry.
394066 | CR | 20190523 | CAQ | D | Blown fuse in RWCR restricting ability to process | N | N |  | N | YES | <D> **** Detailed Description **** Blown fuse in RWCR restricting ability to process water. Fuse blew and indication/ Control was lost to various RW valves. Valves effected- FDR-V- 148 and 173, as well as EDR-V-39. <I> **** Actions Taken **** Blown fuse appears to be on board G11-P001-1, Fuse block JJ, Fuse "JJ-F28". Fuse is 5 amp type "MIN". Recommend replacing fuse | 02-00-E-FUSE-G11P11/JJF28
394069 | CR | 20190523 |  | 4 | RCC-HX-1C Drain Line Leak | N | N |  | N | YES | <D> **** Detailed Description **** RCC-HX-1C (TSW side) has a leak coming from the drain line on the underside of the HX. This leak is upstream TSW-V -68C TSW Drain Valve RCC-HX-1C. Leak is approx 1 drop every 5 seconds. | 02-00-RCC-HX-1C
394070 | CR | 20190523 | CAQ | D | ISP-MS-B901 VPI OOS | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing WO 021156601 VPI action pak calibration checks. MS-VPI-POS/5B was found out of spec, expected trip of 6.0 vdc +/- .5vdc and reset value of 3.0vdc +/-. Trip occured at 6.9 vdc and reset at 3.6 vdc. Adjusted values into spec, as left trip of 5.9 vdc and reset 3.0 vdc. MS -VPI-POS/3C would not trip and appeared to be failed. Unit was replaced under WO 0211156602 and tested SAT after replacement. All as left values for MS-VPI-POS/xx SAT after applicable sections of ISP-MS-B901 performed. <I> **** Actions Taken **** Informed Supervision, wrote CR, and calibrated MS-VPI-POS -3C and MS-VPI-POS/5B with spec. All as left values SAT.
394071 | CR | 20190523 |  | 4 | BOOTY RIPPED WHILE IN C-ZONE | N | N |  | N | NO | <D> **** Detailed Description **** While working in the LP-C Turbine, Stationary Blade area, a booty ripped open while on the foot of the person performing the duties of Fire Watch. The booty did not fall into the condenser. Another booty was obtained and put on, then work continued. The ripped booty was successfully removed from the CA Zone and put into RAD Trash. <I> **** Actions Taken **** The individual notified his supervisor, the Turbine Coordinator and the HP Representative on the 501 elevation.
394072 | CR | 20190523 | CAQ | C | LLRT for CEP-V-2A Flange Less than required pressure band |  |  |  | N | YES | <D> **** Detailed Description **** Reference WOT 0213082601. TSP-FLG/X3-C801, LLRT of CEP-V -2A inboard test flange, directs use of pressure decay test method per PPM 10.24.241, Flow Makeup and Pressure Decay Leak Rate Testing. The leakage exhibited was at a value that reduced the final test pressure to 36 psig which is below the acceptable test limit of 38.0 psig. Therefore, re-performance is required using the Flow Makeup LLRT test method specified in PPM 10.24.241. The LLRT re-test flow makeup data sheet will be attached to TSP-FLG/X3-C801 to satisfy the TS/SR. <I> **** Actions Taken **** Notified LLRT SRO, EOC Test to be reperformed. | 02-00-CEP-V-2A
394075 | CR | 20190523 |  | 4 | Missed opportunity to document IPR on 02111924 14 01 | N | N |  | N | NO | <D> **** Detailed Description **** ALARA Task 02111924 14 01 actual dose total exceeded 500 mrem on 05/20/19. The ALARA Task has exceed the estimated dose at about the same time and there was no In Progress Review documented. <I> **** Actions Taken **** The Wetwell coatings inspection work is not completed. A formal In Progress Review is being documented and will determine a revised dose estimate. <S> An In-Progress Review and revised dose estimate completed, uploaded to EDMS of RWP 30004258.
394078 | CR | 20190523 |  | 4 | HD-LT-2C2 out of tolerance | N | N |  | N | YES | <D> **** Detailed Description **** While perfomring the calibration of HD-LT-2C2 for the transmitter to be out of tolerance. All the readings were off by approx. 1 pound high <I> **** Actions Taken **** Notified supervision and perfomred calibration. As Left Values are in spec and the loop to the controller was in spec as well | 02-00-HD-LT-2C2
394080 | CR | 20190523 |  | 3 | (NRC 2019 RP) Observation: CA Exit Non-Compliance |  |  |  | N | NO | <D> **** Detailed Description **** During the 2019 Rad Safety Inspection an observation was made by the NRC that personnel are not monitoring through the IPMs after leaving the Turbine Building 471 heater bay contaminated area as required per GEN-RPP-04 Section 4.4.4. <I> **** Actions Taken **** HP has installed signs in the area instructing personnel of the requirement to monitor after exiting contaminated area. Recommend assignment to AR-MMGR to evaluate observation.
394081 | CR | 20190523 |  | 3 | MS-V-TV/2 linkage | N | N |  | N | YES | <D> **** Detailed Description **** While working MS-V-TV/2 for Inspect/repair switch linkage package under WOT 02111943-04, craft observed one primary linkage rod bent and loose. Craft tightened. linkage that <I> **** Actions Taken **** Video taken as part of EWP on tablet. Can be seen on media of file 02111943-04. Engineering can contact Mechanics for futher details as needed. Craft stated if new primary linkage is onsite and needs replaced it would not be a difficult task, estimate less than 30 minutes of actual field time. | 02-00-MS-V-TV/2
394083 | CR | 20190523 |  | 4 | Sec Comp/IEBS Host datapump export transfer not working |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The datapump exports are no longer transferring through the diodes and out to the corp network. <I> **** Actions Taken **** Comp Eng & IS staff were notified, the diodes were reconfigured as needed, IEBS host stack restarted, file transfer success verified, system returned to service
394085 | CR | 20190523 |  | 3 | COND-CB-C1A Found red liquid under charging motor | N | N |  | N | YES | <D> **** Detailed Description **** During detailed inspection for COND-CB-C1A a red liquid was found under the charging motor. Most likely came from the charging motor windings. <I> **** Actions Taken **** Notified EOC. No one available to assist on days. <N> Condition expected. Fluid was bearing oil. No further actions required. | 02-00-COND-CB-C1A
394086 | CR | 20190523 |  | 4 | HD-LT-2C OUT OF TOLERANCE | N | N |  | N | YES | <D> **** Detailed Description **** While performing calibration of HD-LT-2C WO# 02111586-01 found it to be out of tolerance 1 pound low <I> **** Actions Taken **** Notifiied supervision and calibrated transmitter into the required tolerance | 02-00-HD-LT-2C
394087 | CR | 20190523 |  | 3 | R24LL - Purchase Additional borescopes prior to R25 |  |  |  | N | NO | <D> **** Detailed Description **** This CR is being generated to request the purchase of additional borescopes prior to R25. Due to the potential scope in R25 (i.e. general plant work and predicted license renewal inspections) additional borescopes are being requested to allow for more simultaneous inspections in potentially contaminated & non-contaminated areas of the plant. Currently we have only two â€œcleanâ€ borescopes, which is requiring coordination between engineering, NDE, and the License renewal team during this outage. If purchased this will enhance efficiency during R25. <I> **** Actions Taken **** Supervisor notified and discussed with License Renewal engineer. Action to either License Renewal or NDE to purchase additional borescopes prior to R25. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
394088 | CR | 20190523 |  | 3 | R24 FAC Location 629-1 (MD-629-1-P) was found below Tmin | N | N |  | N | NO | <D> **** Detailed Description **** Component MD-629-1-P, location 629-1, was examined during R24. This component is a moisture drain header that drains into the main condenser. This component is an 8â€ pipe with three inlet nozzles mounted on the horizontal plane of the header. The damaged area is located 180Â° from the nozzle. This component was replaced in R18 due to similar damage opposite the nozzle. Examination of the component revealed an area of about 1 square inch that was below the minimum allowable thickness. Based on the system and the fact that it is located near the condenser the corrosion mechanism is very likely to be moisture impingement, not FAC. <I> **** Actions Taken **** Recommended action: 1.) Design Engineering review the Tmin value to determine if margin is available. This component had a minimum encountered thickness of 0.163â€, the minimum allowable thickness is 0.17â€. The calculated wear rate is 24 mill per year. 2.) If margin is not available, recommend a repair method from the list: A.) If code allows, install a welded target plate on the pipe OD until R25 and replace the header. B.) Since the area of degradation is small, cut out and install a small window containing the area of degradation C.) Replace the header 3.) Implement repair <N> **** Equipment Description **** TG 483' C6/10.3 Heater Bay Drain Header Upstream the Main Condenser
394090 | CR | 20190523 |  | 3 | (QA) Mode 4 to Mode 5 PPM 1.3.40 has multiple errors |  |  |  | Y | NO | <D> **** Detailed Description **** A Quality Auditor identified multiple errors in the official copy of PPM 1.3.40, Outage Mode Change, Refueling Activity Readiness, and ISFSI Activity Readiness Evaluation, for Mode 4 to Mode 5 change. Errors include typos/editorial and several incorrect â€œLast Date Completedâ€ entries. Procedure directs utilizing a Crystal Report with last completion and late dates included. Crystal Report was recently determined to be inadequate (see CR 394046). ). In addition, Portal J establishes a completion date in the Crystal Report if the work order is canceled and thus an incorrect last completed date. This is the case with multiple surveillances that had frequencies extended in the last couple of months. Without the Crystal Report, surveillance verification is a significant manual effort and impacts oversight activities for the STA. Review did not identify any surveillances past their due date and/or not current (all mode change requirements met). The potential exists, however, for a surveillance to be late and not meet Technical Specification requirements and impact future mode changes. <I> **** Actions Taken **** Notified Quality Management, day/night Shift Managers and day/night STAs. Verified all mode change requirements were met. <N> CR given to Opsst due to multiple issues requiring multiple assignments. Errors in the procedure may need correction by OPSPROC, Asset Suite due dates not correct should go to ITMG (see AR 394046, Crystal report may also need revision (ITMG).
394091 | CR | 20190523 |  | 4 | IBD-42-2R13C failed to close in. | N | N |  | N | YES | <D> **** Detailed Description **** Lifting tags per O-E-ISOPHASE-001, DT 6469 has IBD-42-2R13C lift position as ON. It failed to close in, would just return to open (never actually closing). <I> **** Actions Taken **** After it failed to close pressure was place on various portions of cover near disconnect, it still failed to close. Informed supervison. | 02-00-IBD-42-2R13C
394092 | CR | 20190523 |  | 3 | Near Miss: Battery Powered Caulking Gun |  |  |  | N | NO | <D> **** Detailed Description **** A Painter was cleaning a battery powered caulking gun inside bldg 85. He was using paint thinner and a rag. While cleaning, the rag ignited. The painter threw the rag in the dirt outside bldg 85 and stamped out the fire. The fire was small and the Painter felt that stamping it out was an appropriate method to extinguish the fire. <I> **** Actions Taken **** The Painter verified that the fire was fully extinguished and contacted his supervision to report the incident. <S> Fire Event Report 19-0002 initiated to capture information. ICES report initiated Discussion with Mechanical Component Group Manager. This event was discussed at the shift change D15. Building 85 is a storage building only. The building is a Hazardous Location classified as Class I Division 2 per Article 500 of the National Electrical Code (NFPA 70) 2017 Edition. There are no electrical outlets in the building.
394093 | CR | 20190524 |  | 3 | CGS Site Map in MCR needs updating |  |  |  | N | NO | <D> **** Detailed Description **** The large posterboard of the CGS site map in the MCR is outdated and needs to be updated for all current buildings. This supports prompt direction to the fire brigade during a fire or medical emergencies. <I> **** Actions Taken **** CR written
394095 | CR | 20190524 |  | 4 | PSR-V-640 Difficult to Operate | N | N |  | N | YES | <D> **** Detailed Description **** PSR-V-640 is very difficult to operate. This valve is in the RWCU HX room, which is both a locked high radiation and contamination area. This valve has multiple CRs for leakage and difficulty operating. Recommend evaluating adjusting the valve packing or valve replacement. This would reduce dose. In its current condition it takes operations over 30 mrem of dose to operate. <I> **** Actions Taken **** Notified production center and documented in CR. | 02-00-PSR-V-640
394096 | CR | 20190524 |  | 3 | Pipe Broken in 1C Condenser | N | N |  | N | YES | <D> **** Detailed Description **** While walking down work order task 02008963-01, MS-DT-1C repair support weld on Condenser Press tap. It was discovered that the pipe is broken. This is accessed from the 501â€™ TG. <I> **** Actions Taken **** Recommend Engineering review to verify that pipe needs to be repaired. <N> **** Equipment Description **** MS-DT-1C
394097 | CR | 20190524 | CAQ | C | Misaligned mounting holes for power transformer | Y | N |  | N | YES | <D> **** Detailed Description **** WO 0211 7671 01 The purpose of this task is to replace the existing starter contactor coils and control power transformer (CPT) for RHR-42-8A6A. AR 360819 (and AR 369412) identified a potential Part 21 issue with starter coils installed in NLI MCC buckets. AR-OBS 375956 approves this change. The new transformer mounting base will not line up with the existing mounting holes in the back plate. <I> **** Actions Taken **** Contacted Planning & Enginering <N> **** Equipment Description **** RHR-42-8A6A . This CR was written to document that the transformer did not align with the mounting holes in the adapter plate provided for RHR-42-8A6A (motor starter for RHR-V-42B) as expected. Work Request (WR) 29148965 was generated to correct the problem. . The issue was corrected by issuing material request (MR) 00275326 under Work Order 02117671.01 to provide the correct size transformer for the application as work was still in progress. The pre-staged materials had pulled a size 4 transformer when a size 1 transformer was required. The craft withdrew the size 1 transformer (MR 00275326) and installed it under the original task. Thus the WR was not used and was cancelled.
394098 | CR | 20190524 | CAQ | D | FCP-1 RW 487 General area trouble alarm locked-in | N | N |  | N | YES | <D> **** Detailed Description **** FCP-1 alarm drop 5-4 trouble alarm is locked-in (RW BLDG 487' GENERAL AREA). A tour of the RW 487' revealed no abnormal conditions (other than a slight smell of circuit breaker lubricant in the breaker maintenance area). Breaker maintenance was in progress when RW 487 tour was made. FCP-2 alarm drop 1-1 MAIN PLANT MANUAL PULL STATION ACTUATED is NOT in alarm - therefore, per the ARP, a manual pull station is not the cause of this alarm. FP Zone 24. <I> **** Actions Taken **** Notified the CRS and Shift Manager. Submitted CR and WR. | 02-00-FP-CP-FCP1
394099 | CR | 20190524 | CAQ | D | Dowel pins unable to be removed on RCIC-DT-1 | Y | N |  | N | YES | <D> **** Detailed Description **** While working 02116077-01 step 4.7.2 to remove the dowel pins, the pin ends mushroomed and were not able to be removed. Attempt was made to cut them flush and drive them out with no success. A machining task will need to be created to drill out and machine new dowel pins, (Note: taper pins were made out of a soft material and had no means to remove them mechanically.) <I> **** Actions Taken **** Initiated this condition report notified my supervisor and the system engineer. Notified planning to create a task for this repair. | 02-00-RCIC-DT-1
394100 | CR | 20190524 | CAQ | C | Received 602.A5 drop 1-1 Refueling floor area rad High | N | Y |  | N | YES | <D> **** Detailed Description **** Received 602.A5 drop 1-1 Refueling floor area rad High. Indications on board 672 for ARM-RIS-1 were approximately 300-400 mrem per hour, this remained there for approximately 2-3 minutes then returned to normal rate of approximately 180 mrem per hour. HP reported there was no work activities on the Rx 606 at the time of the alarm. Hp did a survey of the area and found nothing abnormally high that would correspond with the northwest area of the 606. This may be a spurious alarm as HP found no indications of high radiation locally. <I> **** Actions Taken **** Informed CRS | 02-00-ARM-RE-1
394101 | CR | 20190524 |  | 4 | Technical Data unavailable for work on RCIC-DT-1 |  |  |  | N | NO | <D> **** Detailed Description **** While implementing WO 02116077-01 planning was asked where the terminology used in the work order came from. Planning gave us some snip-its from an animated video on the disassembly and assembly of the drive turbine that had this terminology and showed specific oil lines and mounting brackets with this same terminology and locations that was not in the work order. Other than a few pictures in the work order for measurements this video is not available to the craft performing this work, this is less than excellent. This video should be made available, if we have tools that will help be more efficient and understand how the machinery works we should train accordingly and have this information in the work package. <I> **** Actions Taken **** Notified my supervisor and the EOC, initiated the condition report, this is a LASER opportunity missed. Wrote TREQ
394103 | CR | 20190524 |  | 4 | SAS workstation needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security computer workstation 2 video wall in the secondary alarm station needs maintenance. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Security notification made, CR/WR generated <N> **** Equipment Description **** SAS WS 2 in the control room
394108 | CR | 20190524 |  | 4 | PWC-P-4A blew fuses or tripped overloads. | N | N |  | N | YES | <D> **** Detailed Description **** While attempting to swap from PWC-P-4B to PWC-P-4A the PWC-P-4A tripped. Green light on PWC-42-7CB1B is out. Attempted to reset overloads with no change in light. <I> **** Actions Taken **** Turned disconnect PWC-42-7CB1B off. | 02-00-PWC-42-7CB1B
394109 | CR | 20190524 |  | 4 | R24LL HCU scope for HCU overhauls not provided early enough |  |  |  | N | NO | <D> **** Detailed Description **** CRD HCU maintenance matrix added to work order as an attachment Master 7 file on May 8th (example WO 02082591). It identified the scram test switches required replacements. However, the clearance had been created over 6 months prior (Sep 2018) and this scope of work was not in the planning scope as identified by the planner or work order instructions. All of the clearances for HCU normally have the test switches tagged unless it is known they need to be replaced. The volume 10 step is conditional and none was identified as required to be replaced. As a result, all 17 clearances require re-write. Additionally, maintenance was delayed for these HCUs while waiting for clearances to be re-written, tags hung, holders rolled, and tags lifted on the switches that have already been hung (6 clearances), This scope needs to be identified by engineering during the planning process prior to tagging milestones. <I> **** Actions Taken **** Re-wrote HCU tags to support maintenance
394110 | CR | 20190524 |  | 3 | Potential near miss â€“ work coordination |  |  |  | N | NO | <D> **** Detailed Description **** While coordinating WO 02135924-14, Remove TMOD EC# 17409 at E-IR-8, with operations, MS-RMS-120B was found to have a â€œNo Tagâ€ under clearance L-MS-AO-120B-001 for WO 02136024 -01, Open, inspect, and repair internal leak by of MS-V -120B, and is currently at working status. Current position of MS-RMS-120B is in Auto and MS-V-120B is closed. WO 02135924-14 instructs to remove fuse E-FUSE-IR8/TB3F1 which will remove power to MS-SPV-120B and cause MS-V-120B to fail open. If the Crane Valve Techs were working or testing this valve an injury could have resulted. There is no logic tie between these two work orders in the schedule. This task should be performed after the work on MS-V-120B is finished. <I> **** Actions Taken **** Notified operations, supervisor, component manager, OCC, wrote CR <N> Logic tie is made in P6. TMod to follow completion of work on MS-V-120B. ner 5-24-19
394111 | CR | 20190524 |  | 3 | Work performed without bringing work order to working |  |  |  | N | I DONT KNOW | <C> Changed from CAQ to non-CAQ as per the MRT. <D> **** Detailed Description **** The second layer of shielding was installed on piping near RWCU-V-4 prior to bringing the associated work order task to working and without the tag out in place for hanging shielding on a drained line. Operations had verified that the line was drained prior to the shielding installation as required by EC 17433. The Work order task was 02120341-45. A Radiation Protection supervisor was signed onto a clearance for this line, but not the clearance associated with this work order. <I> **** Actions Taken **** Notified Operations and the RPM. Revised the work order package. Based on turnover an assumption was made that the package was ready to go; however, none of the involved parties correctly verified the assumption. Later when the paperwork was being processed the issue documented in this CR was found. RWCU-MO-4 was verified to be drained prior to installing the temporary shielding. There was another clearance which accomplished the same thing and the RMC Supervisor was signed onto it. The work order instructions were changed to match up with the tag out that was actually hanging. It should be noted that 3 of the 4 Shielding WOTs were on O-RWCU-SYS/R24-001. One AT 02120341 45 was on O-RWCU-V-4/STEM-001. AT 02120341 was revised to assign clearance order O-RWCU-V-4/STEM-001.
394114 | CR | 20190524 |  | 3 | Incorrect sign at West RCA access |  |  |  | N | NO | <D> **** Detailed Description **** A sign at the west entrance to the RCA incorrectly states that cell phones are not allowed in the RCA. As of May 01, 2019 cell phones are allowed in the RCA as controlled by PPM 1.3.72. Due to the volume of signs on walls throughout the plant, it is likely others can be found with wrong information as well.
394115 | CR | 20190524 |  | 4 | Pinhole leak on 6'' TSW Piping in Aux Boiler Room | N | N |  | N | YES | <D> **** Detailed Description **** There is a pinhole leak on SCH-CR-51 TSW inlet piping. The leak is located on the NE side of the Aux Boiler Room, about 4 feet downstream of TSW-V-649. The leak is approximately 3 drops/min. Please evaluate. <N> **** Equipment Description **** 6'' TSW piping NE side Aux. Boiler Room.
394116 | CR | 20190524 |  | 4 | Packing leak from instrument rack valve | N | N |  | N | YES | <D> **** Detailed Description **** Observed audible leakage from IR7/V15 valve packing. Most likely needs adjustment to correct leakage. <I> **** Actions Taken **** wrote CR <N> **** Equipment Description **** T -501- - -E0/6.8 - | 02-00-E-IR-7
394117 | CR | 20190524 |  | 4 | Level control loop for HD-LIC-2C found out of specification | N | N |  | N | YES | <D> **** Detailed Description **** While performng a calibration of HD-P/I-2C on work order 02111586-01, the pressure to current converter was found out of specification high by approximately 5 ma at the 50%,75%, and 100% values . The specification is plus or minus .08 ma. This would cause a higher level of indication on HD-LIC-2C than actual level. <I> **** Actions Taken **** Calibrated HD-P/I-2C to within specification per IMDS and work order 02111686-01 . Informed supervision. Returned system to service. <N> **** Equipment Description **** 501 Turbine Building IR-8 | 02-00-HD-P/I-2C
394118 | CR | 20190524 | CAQ | D | RHR-V-112B has no position indication while closed | Y | N |  | N | YES | <D> **** Detailed Description **** RHR-V-112B has no position indication when closed. Plate is making contact with position switch. Switch was manipulated several times. indication did not change at all. | 02-00-RHR-V-112B
394119 | CR | 20190524 |  | 3 | R24LL: Lessons learned draining RHR systems |  |  |  | N | NO | <C> Changed from CAQ to non CAQ as per the MRT. <D> **** Detailed Description **** It is very common to have a siphon from the wetwell when draining RHR systems for outage work. Before R25 SOP-RHR -DRAIN should be enhanced to include instruction for breaking the siphon on the test return/min flow line with air.
394121 | CR | 20190524 |  | 3 | R24LL: Procedure enhancment for OSP-NSSE-W402 |  |  |  | N | NO | <D> **** Detailed Description **** OSP-NSSE-W402 references TSP-SRM-W401 which has been replaced by TSP-SRM-M401. Please update the procedure.
394122 | CR | 20190524 |  | 3 | 02107729-02 instructions changed after SRO review |  |  |  | N | NO | <D> **** Detailed Description **** 02107729-02 original task was to continue SPTM-TE-1A investigation and the SRO hold was removed on 7-2-18 and evaluated as a no clearance order required. The Current 02 document was created on 2-14-19 which included Wetwell entry for divers to install the underwater portion of the new thermocouple and Swagelok fitting. This is a clearance order requirement for Wetwell entry and didnâ€™t contain new SRO/RO hold so it could be evaluated. <I> **** Actions Taken **** Work order tasks were evaluated and placed on the R24 WW clearance. This Task was at READY when the WW C/O was assigned to the tasks
394126 | CR | 20190524 |  | 4 | Contractor for 52211 struck bollard inside protected area | N | N |  | N | NO | <D> **** Detailed Description **** A contractor for org code 52211 struck a ballard with his vehicle while inside the protected area. No damage was done to the vehicle or the integrity of the ballard. Rubber and paint transfer occured between wheel and barrier. <I> **** Actions Taken **** Security supervision notified. CR generated.
394127 | CR | 20190524 |  | 4 | R24 lesson learned - OSP-ELEC-W102 surveillance duration |  |  |  | N | NO | <D> **** Detailed Description **** R24 lesson learned documentation. The weekly surveillance - OSP-ELEC-W102 is normally scheduled for a 2 hr duration during online periods. Due to the electrical lineup and equipment out of service the surveillance is taking 5 hrs to complete. Recommend planning or scheduling increase the duration to 5 hrs during the outage period.
394128 | CR | 20190524 |  | 3 | 500 kV Expansion Couplers Broken Aluminum Sheets | N | N |  | N | YES | <C> Changed to 3/SEEIC at the request of engineering supervision. <D> **** Detailed Description **** During inspections of the 500 kV bus it was noted that one broken aluminum leaf each for the A (feeds M3 Transformer) and B phase (feeds M2 Transformer) 500 kV expansion couplers. This has happened in the past. Reference AR CR 181730 <I> **** Actions Taken **** Notified Supervision, EOC and Emergent Work Manager <N> Also identified on the A phase. Correction: A is M1, B is M2 and C is M3 . EC 8152 describes the total number of aluminum link laminations required for full power operation (see cross references) | 02-00-E-TR-M2,02-00-E-TR-M3
394130 | CR | 20190524 |  | 4 | R24 lesson learned - E shop peer verifier duration |  |  |  | N | NO | <D> **** Detailed Description **** R24 lesson learned documentation. The E-shop peer verifier scope duration for each job is one hour. Most work is requiring the peer verifier to be tied to the task for the full duration of the work. This is not accounted for in the resource curves and schedule durations. This lost resource is reducing shop productivity.
394131 | CR | 20190524 | CAQ | D | Foreign Material discovered on Cavity Floor |  |  |  | N | NO | <D> **** Detailed Description **** During cavity vacuuming activities, lock wire was discovered on the southeast portion of the cavity floor area. <I> **** Actions Taken **** Contacted FME Coordinator/RB606, OCC, RP/RB606, Reactor Maintenance. Filled out Form 26337, Loss of FME Integrity â€“ Notification and Recovery. Reactor Maintenance retrieved the lock wire. See EDMS for additional information. <N> **** Equipment Description **** NA Lockwire documented as removed - there is no DNC.
394132 | CR | 20190524 |  | 4 | ARP holders on H13P603 need replaced. | N | N |  | N | NO | <D> **** Detailed Description **** ARP holders on H13P603 need replaced. Its an acrylic or plexiglass that is used to store the ARP's for the individual panels. Its currently being held together w/tape. Please replace <I> **** Actions Taken **** Informed CRS <N> **** Equipment Description **** H13-P603 ARP Holders.
394135 | CR | 20190524 |  | 3 | R24 LL: enhancements to Isophase bus inspections |  |  |  | N | NO | <D> **** Detailed Description **** The following enhancements should be considered for the Isophase bus inspection work order. . 1. Add detail on inspection of the neutral enclosure 2. Provide guidance for the nylon fasteners at the baffle 3. Deionizers are not removed for inspection 4. Need clear criterial for insulator inspections 5. need a planned WO task to replace insulators as necessary 6. Add steps to the isophase procedure to direct HIPOT testing of all three phases in both directions at the same time, only test individual phases if the HIPOT of the entire bus fails. 7. Rearrange steps to ensure the insulator inspections are started first, this moves discovery of damaged insulators to the beginning of the maintenance window allowing time to replace any degraded insulators without impacting the maintenance window 8. Add steps to direct HIPOT testing of all three phases in both directions at the same time, only test individual phases if the HIPOT of the entire bus fails. <I> **** Actions Taken **** Initiated CR to revise work instructions. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
394137 | CR | 20190524 |  | 3 | (QA) Copy of Work Instructions Not at Work Site |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) No copy or applicable pages/sections of Work Order Task (WOT) 02113088-01 instructions at the work site on 5/23/19, contrary to SWP-PRO-01 "Procedure and Work Instruction Use and Adherence". This is a procedure use and adherence issue with no known consequences at this time. Factual Basis: â€¢ SWP-PRO-01 rev 032-002 step 4.2.2 states, "Reference Use Procedures, Work Instructions, and Orders â€“ Allowed for activitiesfor which the consequences of an improper action are not immediate and are not irreversible. The performer is to PERFORM the following: . . . b. HAVE a copy or applicable pages/sections open at the work site." â€¢ A Quality Assurance (QA) auditor observed two boilermakers cleaning TSW-HX-8 with no WOT instructions copy or applicable pages/sections at the work site at approximately 0915 hours on 5/23/19. Insights: â€¢ One boilermaker interviewed said he did not know there was a requirement to have a copy of the WOT instructions at the work site. â€¢ He also said his foreman had the WOT instructions. <I> **** Actions Taken **** Contacted the SSC Superintendent and SSC Supervisor over the foreman for the boilermakers. . Recommend routing to SSC. . This Deficiency was identified during the Quality Outage Surveillance SR-19-01. <N> Williams Plant Services. Another Craft Supervisor reported the responsible Foreman was in close vicinity to the work area when this issue was observed. The Foreman was responsible for documenting the work progress and had stepped away for a minute to monitor another work location. Coaching has been provided and the need to follow SWP-PRO-01 as it is written.
394138 | CR | 20190524 | CAQ | D | DG-RLY-DG2/K16 lug needs repaced | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of 02112991 01, it was noted that a lug on the subject relay on terminal K was bent and twisted beyond the allowance of PPM 10.25.19. It appears functional but should be replaced. <I> **** Actions Taken **** Notified supervsor. | 02-00-DG-RLY-DG2/K16
394139 | CR | 20190524 | CAQ | D | Metal fatique E-PP-8AF | Y | Y |  | N | YES | <D> Metal fatigue on E-PP-8AF found during clean and inspect. Screws on top left and bottom right of dead front do not hold good, stripping. <I> Write CR to report condition of degraded metal. <N> W467 K/14.7 CR at INPROG. Approved and moved to SRO for OPS review. | 02-00-E-PP-8AF
394140 | CR | 20190524 |  | 4 | R24 LL Outage admin computer access |  |  |  | N | NO | <D> **** Detailed Description **** OCC admins assigned to update the outage status page and plant risk page did not have the required permissions to update the outage risk page <I> **** Actions Taken **** Updated the access permissions for the current outage admins
394142 | CR | 20190524 | CAQ | C | As-Left LLRT of X-1E Containment Hatch Failed | Y | N |  | N | YES | <D> **** Detailed Description **** PMT WOT 02115128-38, for As-left LLRT of containment inspection hatch X-1E failed its leak rate. The leakage was excessive that test pressure of 38.0 psig could not be obtained. Indicated leakage was 1600 sccm which is siginificantly greater than the Admin limit of 50 sccm Verified LLRT hose connection and Inspected outer O-ring with Snoop leak indicator and no leakage was observed from outer O-ring. Therefore highly suspect inner O-ring leakage. <I> **** Actions Taken **** Notified LLRT SRO, EOC, Rx Maintenance <N> **** Equipment Description **** C -569- | 02-00-C-X-1E
394144 | CR | 20190524 | CAQ | C | RPIS or DMM Inop Following Extender Card Removal | Y | N |  | N | YES | <D> **** Detailed Description **** Following RPIS extender card removal the RPIS or DMM INOP alarm locked in (P603-A7 1-7) with multiple control rods indicating full in and full out with rod drift alarms. RPIS and DMM were reset per the ARP with no change. The RWM temp power was plugged into an outlet powered via SM-8 which is secured at this time for the SM-8 outage. Recommend updating instructions in SOP-ELEC-TEMPPOWER for RWM temp power to make it inverter backed. <I> **** Actions Taken **** CR to move temp power for RWM to SM-7 or inverter backed outlet in the future. <N> Re-opened and reassigned to OPSPROC per Author and concurrence from OPSPROC supervisor. | 02-00-PPC-CRT-RWM
394146 | CR | 20190524 |  | 3 | R24LL: Procedure enhancement to TSP-RFW/X17A-R802 |  |  |  | N | NO | <D> **** Detailed Description **** TSP-RFW/X17A-R7802 step 7.1.8 should refer to attachment 9.6 Step 7.2.36 should say specify step 9.4.56 and 9.4.57 of attachment 9.4 <I> **** Actions Taken **** Wrote CR
394149 | CR | 20190524 | CAQ | D | (QA) FP Piping Temporary Hanger Installed | N | Y |  | Y | YES | <D> **** Detailed Description **** (QA) During a Quality Auditor walkdown of the turbine building a temporary hanger is installed on a fire protection sprinkler pipe in the aux boiler room overhead next to the column at G/5. Refer to picture in EDMS. It appears that this temporary hanger has been installed for a long time. There are permanent hangers installed upstream and downstream of this hanger. This should be corrected before the scaffold is removed per work order task 02106152-13 , SC- REMOVE SCAFFOLD TSW PIPING (T.465') AUX BLR RM, which is scheduled on 6/9/19. <I> **** Actions Taken **** Initiated CR. Informed FP Engineer and Fire Marshall via email. <N> **** Equipment Description **** T466 G/5 | 02-00-FP-ZONE-1
394150 | CR | 20190524 |  | 3 | E-TR-M1 links installed incorrectly. |  |  |  | N | YES | <D> **** Detailed Description **** During the performance of work order 02122003-05, (INSTALL LINKS- RECONNECT XFMRS & GEN AFTER HI-POT), the flexible links to transformer E-TR-M1 were installed/configured. incorrectly. Once identified, the links were removed, configured correctly, and re-installed in accordance with PPM 10.25.197. <I> **** Actions Taken **** Generated CR to document the incorrectly installed transformer links, Notified OCC, and Ermergent Team Lead. <N> **** Equipment Description **** Trabnsfomer yard | 02-00-E-TR-M1
394151 | CR | 20190524 |  | 4 | MCR kitchen sink is backed up |  |  |  | N | YES | <D> **** Detailed Description **** MCR kitchen sink has a clog in the drain piping, affected components include the kitchen sink, the bathroom sink, the dishwasher drain path, and the ice maker drain path. Water is currently stagnant or draining very slowly in both the bathroom sink and the kitchen sink, when the ice maker pumps the water it has collected into the drain it causes water to issue from under the sink and onto the floor. <I> **** Actions Taken **** Minimized use of the MCR sink, cleaned up water with mop, placed wet floor sign into the kitchen area, and generated WR. <N> **** Equipment Description **** Main Control room kitchen
394153 | CR | 20190524 | CAQ | D | C0-2A Voltage High out of Spec | Y | Y |  | N | YES | <D> **** Detailed Description **** On 5/25 Night shift C0-2A volatge was found to be high out of specification at 27.8V. Per PPM 3.1.10 C0-2A voltage is required to be 26.5 - 27. 5V when not in equalize. Over the last 14 days voltage has ranged from 27.5V to 28.3V. <I> **** Actions Taken **** Informed MCR supervision, initiated CR for tracking | 02-00-E-C0-2A
394155 | CR | 20190525 |  | 3 | Tig welding wire dropped while welding in the LP-C. (FME) |  |  |  | N | NO | <D> **** Detailed Description **** During the repair of LPC L0 stationary blades, a 6â€ piece of 3/32" Tig welding wire was dropped into the Charles condenser bay. The final location of the piece of wire is unknown. <I> **** Actions Taken **** Notifies Siemens supervision, Turbine project manager, FME coordinator, and OCC. Recovery plan will be developed to retrieve the wire.
394156 | CR | 20190525 | CAQ | C | Individual recieved a dose alarm |  |  |  | N | NO | <C> CR reopened, changed to CAQ from nonCAQ as per the MRT. <D> **** Detailed Description **** ENW employee recieved a dose alarm while working in the DW while performing LLRT. Individual recieved 81.5 mrem on a set point of 80 mrem. Worker was in the drywell for 4.5 at time of alarm. <I> **** Actions Taken **** Restricted access from the RCA per HPI-12.96 <N> **** Equipment Description **** PIV-X73E1 Forms 26441, 26443, histogram and pre/post alarm surveys have been uploaded into EDMS. No further action required.
394157 | CR | 20190525 | CAQ | D | As Found Misidentified MC panels | Y | N |  | N | NO | <C> Changed from "C" to "D" as per the MRT. <D> **** Detailed Description **** While working work order 02111292-01 in the RPS Room 2 on the 467â€™ elevation of the RW building, the craft noticed a conflict in the identification. Although the MCâ€™s have the proper identification (black letters on orange background) there are other covers with smaller metal identification tags that have been misplaced. MC-S1-2D 125VDC and MC-8A 480VAC smaller metal identification tags have been reversed. <I> **** Actions Taken **** Notified Operations and was instructed to replace the covers as found and initiate a CR. <N> Need for engineers to ensure proper labels are identified and planning to plan fabrication and installation of labels. MNTSSC should not be the OWED TO group. WPS personnel found the issue and reported it.
394158 | CR | 20190525 | CAQ | D | As found time out on E-RLY-62/B/8/1 | Y | N |  | N | NO | <D> **** Detailed Description **** While performing ESP-RLY62B81-B301 under WO#02111914-01 the as found time for E-RLY-62/B/8/1 was out of tolerance at 3.58 seconds. This time was only outside the setting range of 3.43-3.57 seconds, It was not outside the tech spec range of 3.06 - 3.94 seconds. Adjusted the relay back into setting range per the steps in ESP-RLY62B81-B301 and the as left time was 3.54 seconds. <I> **** Actions Taken **** Notified operations, notified supervisor, adjusted relay back into tolerance and wrote this CR
394159 | CR | 20190525 | CAQ | C | RHR-V-4C guide rail inappropriately welded | Y | N |  | N | YES | <C> This CR is a bringback for Engineering to gather more information. <D> **** Detailed Description **** The WO to weld RHR-V-4C guide rails required a stitch weld of the lower area of the wedge guide rails. A contract welder welded al 3 location on the upper portion of the guide rail not the lower portion as required by the WO. <I> **** Actions Taken **** Informed Engineering and OCC. Engineering inspected the welds and determened that the welds should be blended to match the stitch welds installed during manufacturing. . Photos in EDMS <N> **** Equipment Description **** R -452-R014- -J0/4.2 -RHR C UPPER LEVEL | 02-00-RHR-V-4C
394161 | CR | 20190525 |  | 4 | TSW-SR-34 valve leak | N | Y |  | N | YES | <D> **** Detailed Description **** Minor leak on TSW-SR-34/V-19 when the valve is in the open position. <I> **** Actions Taken **** Informed chemistry supervision and CR/WR. | 02-00-TSW-SR-34
394162 | CR | 20190525 | CAQ | D | TR-M3 Deluge System (D59) issue |  |  |  | N | YES | <D> **** Detailed Description **** During the performance of PPM 15.3.14 â€œDeluge Systems Trip Test and Strainer Flushâ€ for TR-M3 following step 7.3.51 it appears that FP-V-D59/491 (Solenoid valve) was not closing which inhibits restoration of the system. <I> **** Actions Taken **** Stopped the job initiated CR and WR. Notified supervision, MCR, OCC. | 02-00-FP-V-D59/491
394163 | CR | 20190525 |  | 3 | Drawing did not match field terminations in E-SL-81 unit 2 |  |  |  | N | NO | <D> **** Detailed Description **** while working Work Order 02043299 Task 01 Replace Cell Switch in cubicles, Craft identified two wires were landed on the Normally open contacts, not the Normally closed contacts shown on drawing E534-16A. Need to update all associated drawings to reflect field configuration <I> **** Actions Taken **** Craft Stopped work, Notified supervisor Supervisor contacted EOC EOC sent Engineering to validate connections compare to drawing. Updated PWTI to reflect as found wiring. Initiated CR to document drawing error. <N> Drawing markup for E534-16A uploaded to EDMS added photos of TOC switch. 52H.3 shows C11 & D11 as found
394167 | CR | 20190525 |  | 3 | OSP-RCS-C105 Revision Recommendation |  |  |  | N | NO | <D> **** Detailed Description **** Step 7.8 of OSP-RCS-C105 is a pounded step to verify drain time is GE 36 hours but step 7.9 is not for entering the appropriate TS 3.5.2 action. Recommend revising step 7.8 to say â€œIF drain time is GE 36 hours complete this step and exit the surveillanceâ€ and 7.9 to be a pounded step. <I> **** Actions Taken **** CR
394168 | CR | 20190525 |  | 4 | During Loop Cal SS-PI-39 is Out of Tolerance |  |  |  | N | YES | <D> **** Detailed Description **** During the performance of SS-PCV-39, 02111603, loop calibration SS-PI-39 was found out of tolerance. Per the IMDS addenda 1 if the as found values are outside of tolerance to initiate a CR. <I> **** Actions Taken **** Initiated CR, notified supervisor. <N> **** Equipment Description **** SS-PI-39 | 02-00-SS-PI-39
394169 | CR | 20190525 | CAQ | D | Breaker E-MC-8C7A not functioning |  |  |  | N | YES | <D> **** Detailed Description **** While performing a clean and inspect on E-MCC-8C we attempted to restore the breaker 7A to the as found position. The breaker would slowly return back to the open postion after it was closed. The breaker was left in the open position. As found was closed. <I> **** Actions Taken **** left breaker in open position and informed supervisor. | 02-00-E-MC-8C
394171 | CR | 20190525 |  | 3 | CID 60110701 unable to be calibrated from warehouse | N | N |  | N | YES | <D> **** Detailed Description **** MS-PS-25A requires replacement and CID 60110701 was ordered under MR 274170. The switch was installed in the plant and ultimately unable to be calibrated. There are no more of this CID in stock and unavailable on RAPIDS. Lead time from vendor is 79 days which does not support replacement in R24. <I> **** Actions Taken **** Initiatded CR. Need Procurement engineering to identify a replacement part or if this PS can be taken from another location. | 02-00-MS-PS-25A
394173 | CR | 20190525 |  | 4 | Drawing shows lighting circuits reversed | N | N |  | N | YES | <D> **** Detailed Description **** During work order 02136055, tasks 51 and 60, the Work Order Holder for the local clearance closed circuit breakers E -CB-LP2DB/11 and 13 to restore following light replacement. The respective breakers energized the lights shown for the opposite breaker. Drawing E820-1 shows the lights as they should be. <I> **** Actions Taken **** Submitted WR to correct this. | 02-00-E-LP-2DB
394174 | CR | 20190525 |  |  | W-DOOR-C302 not closing properly |  |  |  | N | YES | <D> **** Detailed Description **** W-DOOR-C302 will not fully shut without assistance. | 02-00-W-DOOR-C302
394175 | CR | 20190525 | CAQ | D | W-DOOR-C203 not closing without assistance. | N | Y |  | N | YES | <D> **** Detailed Description **** W-DOOR-C203 will not fully shut without assistance. <I> Issued BIP 19-0248. Placed on flood tour. | 02-00-W-DOOR-C203
394176 | CR | 20190525 |  | 3 | Blade magnetization check step N/Aâ€™d in WO 02110816 | N | N |  | N | NO | <D> **** Detailed Description **** The use of N/A was used at Step 4.4 of WO 02110816. Although this is a PM WO, the source document for the PM (MOT TURB-1-1) is intended to perform visual inspection of turbine components with primary focus being last stage blades. The MOT does not prescribe the scope of the step that is was N/Aâ€™d. The method to obtain the requested data for the step is not defined, does not fit well with the remaining steps, and the step should be removed from the Work Order instructions. The intent of the stop is adequacy of the blade magnetization is validated using BVM data, not through visual inspection or field measurement. Request assignment to planning to edit Model Work Order No MOT revision required <I> **** Actions Taken **** N/Aâ€™d the step Informed EOC
394177 | CR | 20190525 |  | 3 | Rx 522 east EOP box missing CRD Hose. | N | N |  | N | YES | <D> **** Detailed Description **** The Reactor 522 ft. level, East EOP box is missing its CRD vent hose. Most likely used during S/D. Seal was missing. <I> **** Actions Taken **** Notified CRS. Performed inventory IAW ppm 5.0.6 and relocked the EOP box. No other items identified as missing and seal was not installed. <N> **** Equipment Description **** Rx 522 E
394178 | CR | 20190525 |  | 3 | R24 LL CVB maintenance delayed by no wetwell entry | N | N |  | N | NO | <D> **** Detailed Description **** Scheduled periods of no wetwell entry due to RHR maintenance delayed containment vacuum breaker work by over 36 hrs. In previous outages, a dedicated drywell/wetwell scheduler was able to identify and reduce such schedule conflicts. If the overlaps remain, durations of CVB work should be modified to reflect the anticipated lost time due to periods of no wetwell entry. <I> **** Actions Taken **** Initiated LL CR at request of Mech shop manager.
394179 | CR | 20190525 |  | 4 | R24 LL Competing priorities in RX 501 Valve Room B | N | N |  | N | NO | <D> **** Detailed Description **** The RX 501 Valve Room B is small enough that further consideration should be given to the amount of work scheduled for the space at one time. Crane valve crews working on RHR-V-16B needed enough of the available space that work scheduled for adjacent components (RHR-RO-10B) needed to be rescheduled. This issue was not identified until after workers were fully briefed and in the field. <I> **** Actions Taken **** Initiated CR at request of Mech shop manager
394181 | CR | 20190525 |  | 3 | Damaged steam sensing line in Bravo bay of Condenser | N | N |  | N | YES | <D> **** Detailed Description **** Piping leading to a pressure sensing basket in the Bravo Condenser bay is broken. This piping is located in the upper northeast corner of the Bravo Condenser Bay. Per system engineer, this sensor piping is no longer used and can be removed and capped if necessary. There is no immediate concern of piping breaking off completely. See attached picture in the EDMS folder. | 02-00-COND-HX-9
394183 | CR | 20190525 |  | 3 | Damaged support hanger for extraction steam sensing line | N | N |  | N | YES | <D> **** Detailed Description **** A pipe support hanger for extraction steam pressure sensing piping is damaged. This hanger is located in the upper northeast corner of the Bravo Condenser Bay. Per system engineer, this sensor piping is no longer used and can be removed and capped if necessary. There is no immediate concern of this issue causing damage to the piping. See attached pictures in the EDMS folder. | 02-00-COND-HX-9
394184 | CR | 20190525 | CAQ | C | RCIC-V-111 missing one seat ring retaining screw | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of W/O 02111379, check valve inspection of RCIC-V-111 found one seat ring retaining screw missing and another screw with the head missing with the shaft still threaded in, screw size is #5-40X1/4" <I> **** Actions Taken **** informed OCC, maintenance management and returned work order to repair/replace disc assembly <N> **** Equipment Description **** R475 J6/7.4 | 02-00-RCIC-V-111
394185 | CR | 20190525 | CAQ | C | RCIC-V-112 has one seat ring retaining screw missing | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of W/O 02111380, RCIC-V-112 internal check valve inspection, found one seat ring retaining screw missing, screw size is #5-40X1/4" <I> **** Actions Taken **** informed OCC, maintenace management and returned work order to planning for asme plan to repair/replace disc assembly <N> **** Equipment Description **** R475 J6/7.4 | 02-00-RCIC-V-112
394186 | CR | 20190525 |  | 3 | Calculation 2.06.20 - GT 20 CMRs | N | N |  | N | NO | <D> **** Detailed Description **** In accordance with Design Procedure DES-4-1, the intent of this CR is to document that the working copy of calculation 2.06.20 has greater than 20 Calculation Modification Records (CMRs) at â€˜Modifiedâ€™ status. There is no impact to the day-to-day operation of CGS. This assignment should be given to Electrical Design (AR-DEI) to revise the calculation and incorporate the â€˜Modifiedâ€™ status CMRs into the next revision.
394187 | CR | 20190525 |  | 3 | Calculation E/I-02-95-01 - GT 5 CMRs | N | N |  | N | NO | <D> **** Detailed Description **** In accordance with Design Procedure DES-4-1, the intent of this CR is to document that calculation E/I-02-95-01 has greater than 5 Calculation Modification Records (CMRs) at â€˜Modifiedâ€™ status. There is no impact to the day-to-day operation of CGS. This assignment should be given to Electrical Design (AR-DEI) to revise the calculation and incorporate the â€˜Modifiedâ€™ status CMRs into the next revision.
394189 | CR | 20190525 |  | 3 | Calculation E/I-02-87-07 - GT 5 CMRs | N | N |  | N | NO | <D> **** Detailed Description **** In accordance with Design Procedure DES-4-1, the intent of this CR is to document that calculation E/I-02-87-07 has greater than 5 Calculation Modification Records (CMRs) at â€˜Modifiedâ€™ status. There is no impact to the day-to-day operation of CGS. This assignment should be given to Electrical Design (AR-DEI) to revise the calculation and incorporate the â€˜Modifiedâ€™ status CMRs into the next revision.
394190 | CR | 20190525 |  | 3 | Changes detected in FW sparger weld indications | N | N |  | N | YES | <D> **** Detailed Description **** During R24 monitoring of the feedwater (FW) sparger weld indications reported in R22 & R23, some changes in length were noted (see Indication Notification Report INR-CGS-19 -003 in EDMS). The changes are attributed to improved inspection capability and not actual growth of the indication. The feedwater spargers are not safety related and the indications will not inhibit the feedwater system from performing its function. <I> **** Actions Taken **** Assign to AR-CPROG to verify the reported changes are still bounded by the evaluation in AR-EVAL 00330490. | 02-00-MS-RPV-3
394191 | CR | 20190525 |  | 3 | Calculation 2.05.06 - GT 5 CMRs | N | N |  | N | NO | <D> **** Detailed Description **** In accordance with Design Procedure DES-4-1, the intent of this CR is to document that calculation 2.05.06 has greater than 5 Calculation Modification Records (CMRs) at â€˜Modifiedâ€™ status. There is no impact to the day-to-day operation of CGS. This assignment should be given to Electrical Design (AR-DEI) to revise the calculation and incorporate the â€˜Modifiedâ€™ status CMRs into the next revision.
394192 | CR | 20190525 |  | 3 | Calculation E/I-02-92-09 - GT 5 CMRs | N | N |  | N | NO | <D> **** Detailed Description **** In accordance with Design Procedure DES-4-1, the intent of this CR is to document that calculation E/I-02-92-09 has greater than 5 Calculation Modification Records (CMRs) at â€˜Modifiedâ€™ status. There is no impact to the day-to-day operation of CGS. This assignment should be given to Electrical Design (AR-DEI) to revise the calculation and incorporate the â€˜Modifiedâ€™ status CMRs into the next revision.
394193 | CR | 20190525 |  | 3 | LED Light Replacement Package Missed Update after EC Rev | N | N |  | N | YES | <D> **** Detailed Description **** Work Order 02136055 YARD LIGHTING REPLACEMENT - CIRCUIT E -CB-LP2DB/1 replaced Transformer Yard lighting as instructed. After installation of lights attached to E -CB-LP2DB/1 it was identified that the package was missed in being revised. This work order will be taken to FINISHED instead of performing rework and challenging the TRM/TRN window. If it is decided to change the LED lights in the future, they may be performed online without a terminal clearance. This is due to their location above the Trenwa and not below the 500 kV lines. <I> **** Actions Taken **** Initiated CR. Is revision of EC DEC 17345 needed to address this? | 02-00-E-LP-2DB
394195 | CR | 20190525 | CAQ | D | Re-examination of steam dryer lifting lugs shows no change | N | N |  | N | YES | <D> **** Detailed Description **** 24 monitoring of the indications on the steam dryer lifting rod brackets at 135 and 315 degree azimuths showed no discernable change (ref INR-CGS-19-004 in EDMS). The indications were originally identified and evaluated in R22 under CR 329067 and found to be acceptable as-is. The indications were re-examined in R23 with no change reported (CR 365404). This is the second consecutive examination with no disernable change despite operation at MUR levels. This CR is writtin for trending purposes only the indications do not impact plant operation or plant start -up concern. <I> **** Actions Taken **** Recommend this CR be a trend. Per BWRVIP guidance these locations can return to their normal inspection frequency. This will be addressed as part of the normal program update. | 02-00-MS-RPV-3
394197 | CR | 20190525 | CAQ | D | Re-examination of steam dryer Lower Guide shows no change | N | N |  | N | YES | <D> **** Detailed Description **** R24 monitoring of the indications on the steam dryer 180 degree lower guide showed no discernable change (ref INR -CGS-19-005 in EDMS). The indications were originally reported in R22 under CR 329792 and appear to be the result of mechanical damage. They were evaluateed as acceptable as-is and are monitored to ensure the mechanical damage does not lead to fatigue or stress related degradation. The indications were re-examined in R23 (CR 365431) with only minor additional mechancial degradation noted. This is the second consecutive examination with no disernable change overall. This CR is writtin for trending purposes only, the indications do not impact plant operation and they are not a plant start-up concern. <I> **** Actions Taken **** Verified that the degradation is still bounded by the evaluation under CR 365431. Recommend this CR be a trend. | 02-00-MS-RPV-3
394201 | CR | 20190525 |  | 2 | Workers entered the wetwell without signing onto a C/O |  |  |  | N | NO | <C> AR/CR Reopened at request of S. Stewart / Maintenance to add information. Will be taken back to complete by maintenance <D> **** Detailed Description **** On May 20 an emergent scaffold was requested and a new WO task was created to install and remove scaffolding in the wet well WO (02088276-09 and 10). The scaffolding crew entered the wet well and installed the scaffolding per 02088276-09 without being signed onto a C/O. during interviews the scaffolding crew stated that they were unaware that a C/O was required for Wet well entry as it was not referenced in the requirements panel of their SC task <I> **** Actions Taken **** Intitiated an event investigaton, contacted maint management <N> EN Scaffold Builders.
394202 | CR | 20190525 | CAQ | C | E-CB-B/8 delta force not in tolerance | Y | N |  | N | YES | <D> **** Detailed Description **** After performing a MOC switch inpsection, the delta force acceptance criteria was not in the 20-35 pound range. Contacted Engineering to get resolution. Engineering recommeded adjusting the sure close spring to increase the delta force. <I> **** Actions Taken **** Notified Engineering. | 02-00-E-CB-B/8
394203 | CR | 20190525 | CAQ | D | OCA Camera 88 |  |  |  | N | YES | <D> **** Detailed Description **** OCA Camera 88 is not functioning as intended. Please contact Security Supervision at 2185 for details. <I> **** Actions Taken **** Posted compensatory measures. Notified Security Management and generated CR/WR. <N> **** Equipment Description **** OCA Camera 88
394205 | CR | 20190525 | CAQ | C | CMS-RE-27F J2 Connector broken | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing work order 02092411-01 step 4.5.2 it was discovered that inside TB-C568 the center pin of J2, cable 2PRM-144 is broken off. J2 connector is a 75 Ohm conductor seal assembly. <I> **** Actions Taken **** Contacted Supervisor and Engineering for further evaluation and or replacement plan. <N> **** Equipment Description **** CMS-RE-27F
394206 | CR | 20190525 |  | 3 | sheared pin on 48" pipe wrench |  |  |  | N | NO | <D> **** Detailed Description **** While removing studs on the inner cylinder on LP-C, a pin on the jaw of the 48" pipe wrench sheared and a 3/8" piece fell into the condenser. Retrieval attempt is underway. <I> **** Actions Taken **** Stopped work and notified the Supervisor, Turbine Coordinator and had this CR Initiated.
394208 | CR | 20190525 |  | 3 | Ceramic Tig Cup broke while welding on the Horizontal Joint |  |  |  | N | NO | <D> **** Detailed Description **** A Tig Cup broke while welding on the Horizontal Joint for LP-C, and fell into the Condenser. 1/2 of the broken piece was easily retrieved, and the remainder of the cup went into the condenser. A search for the piece is underway. <I> **** Actions Taken **** Stopped work, notified the Supervisor and the Turbine Coordinator. Initiated this CR and began retrieval actions. <N> CR reopened at the request of Maintenance CIC.
394209 | CR | 20190525 |  | 4 | EDR-LS-19A and associated pump needs to be replaced |  |  |  | N | YES | <D> **** Detailed Description **** 0208590901 I&C /MECH. REPAIR/REPLACE EDR-LS-19A (W-6 SUMP, during the discovery process to figure out if we can replace or repair the Level switches for W-6 sump pump the craft discovered the switches are bad and need to be replaced ( there are 3 float switches on this pump 2 SquareD 9036 float switches and a Furnas 69L2163H float switch). The pump, conduit and the wiring to the pump are in poor shape as well. Maintenance recommends that we replace the pump, conduit, wiring and switches. <I> **** Actions Taken **** wrote cr, contacted Supervisor | 02-00-EDR-LS-19A
394210 | CR | 20190525 | CAQ | C | RWCU-MO-1 THRUST BELOW ACCEPTANCE VALUE | Y | N |  | N | YES | <D> **** Detailed Description **** RWCU-MO-1 was diagnostically tested per WOT 02120340-05 on 5/23/19. The measured thrust was below the acceptance value. The valve and actuator are being modified during R24. The valve and actuator will be setup and tested to verify that it is capable of performing its design function on demand. The attached evaluation provides basis that RWCU-V-1 was fully capable of performing its intended functions since last tested in 2013. (See EDMS) <I> **** Actions Taken **** Evaluated limiting condition (see EDMS). | 02-00-RWCU-MO-1
394211 | CR | 20190525 |  | 3 | R24 lessons learned OPS HCU tagging cable,string or rope. |  |  |  | N | NO | <D> **** Detailed Description **** Last three outages have cause a scramble for cable twine or rope to tag out banks of HCU. we typically will tag out all the 101 valves on a bank with a single string,cable or rope. We dont necessarily have the cable string or rope on hand when it comes time to hang the tags. this results in a scramble and taking resources from the tool crib or where we locate it. Recommend when we generate the tagout for r-24 we include a note to contact the OPS 456 Operations Coordinator and place on a list of items to purchase prior to the outage. <I> **** Actions Taken **** CR to request a change in the process to better prepare for the next outage. <N> Action complete
394213 | CR | 20190525 |  | 3 | PPM 1.3.23 Controlled key missing from MCR locker |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.3.23 "Administrative Control of Plant Operating Keys" Main Control Room Key # 195 is missing both the Issuable white tagged and Non-issueable (master) Red tagged keys. These keys are for MT-MTS-6B/3D the Radwaste elevator manual power transfer switch. MT-MTS-6B3D is verified to be locked to it's normal 6B source. The bypass, interlock, and cyber key log has no entries showing that this key has been issued. CR initiated for tracking. <I> **** Actions Taken **** Informed CRS and SM. Verified keys were not located in RWCR or PSRO key lockers. Verified locked switch is in the proper position.
394214 | CR | 20190525 |  | 4 | Declared Alcohol at Security Checkpoint |  |  |  | N | NO | <D> **** Detailed Description **** A visitor for Turbine Emergent work brought alcohol to the Security Checkpoint. <I> **** Actions Taken **** Security Supervision Notified, OCC Notified. PGM Notified
394215 | CR | 20190525 | CAQ | D | control rod 38-23 does not indicate full in | Y | N |  | N | YES | <D> **** Detailed Description **** control rod 38-23 does not indicate full in - this gives rod select block to RDCS and rod insert and W/D block to RMCS. Short form - refuel bridge cant be loaded over core - no refueling operations until corrected. N2 screen indicates BA or bad indication. This was not a blade that was changed out and that cell has 4 bundles in it. | 02-00-CRD-RPIS-1
394216 | CR | 20190525 |  | 4 | ARGOS HP-EQ-42782 is not always detecting person, GSB PAP |  |  |  | N | YES | <D> **** Detailed Description **** The ARGOS HP-EQ-42782 is not always detecting a person when the are inside. <I> **** Actions Taken **** created CR, told Lead HP tech and supervisor. <N> **** Equipment Description **** GSB, PAP RCA exit point | 02-00-HP-EQ-42782
394217 | CR | 20190525 |  | 4 | Inoperable circuit breaker E-PP-8AZ #10 | N | Y |  | N | YES | <D> **** Detailed Description **** WO-02042674-01, Entails to clean and inspect panel E-PP -8AZ. Electrical craft reinstalled breakers and found that the #10 breaker would not cycle from off to on. The breaker was removed and examined. The craft cycled the breaker from off to on without any hesitation, the breaker was reinstalled with the same results of not being able to cycle occurred. <I> **** Actions Taken **** Called engineering for resolution <N> **** Equipment Description **** E-PP-8AZ
394218 | CR | 20190525 |  | 4 | WOâ€™s 02111630-01 and 02111631-01 returned to planning |  |  |  | N | NO | <D> **** Detailed Description **** During implementation of WOâ€™s 02111630-01 and 02111631-01 it was noted that the work orders had multiple discrepancies with the gaskets being used (material) and plant component status control for valve manipulation. Please update model work orders for future use. <I> **** Actions Taken **** Notified my supervisor and planning and initiated this CR and took packages to return status
394219 | CR | 20190526 |  | 4 | RRC-FIS-39A & B documents list enhancement |  |  |  | N | NO | <D> **** Detailed Description **** The documents page on the D030 screen for RRC-FIS-39A(B) does not have CVI OMM 02B35-06,4 listed. Please add this document to both RRC-FIS-39A and RRC-FIS-39B document lists, as this was the only document found that shows the flowpaths internal to the mechinism. <I> **** Actions Taken **** Initiated CR . The requested D030 updates for RRC-FIS-39A(B) have been made. <N> CR reopened to edit severity.
394220 | CR | 20190526 |  | 4 | R24: E-PP-8AZ disc 9 will not close | N | Y |  | N | YES | <C> Duplicate of CR 394217 <D> **** Detailed Description **** Following E-PP-8AZ clean and inspect per 02042674 disconnect 10 will not close. This is a QMB disconnect. MSSC stated that this disconnect will close when disconnects 9 & 10 are not installed but 10 will not close when installed. This was performed on day shift and apparently tried twice per their turn over. Disconnects 9 & 10 are a single unit and can only be removed as a pair. Recommend trouble shoot and repair/replace. Note: disc 10 feeds MCR supervisory, disc 9 feeds DEH valve test pnl <I> **** Actions Taken **** Verified with RO that E-PP-8AZ-10 would not close, verification included opening outer cover and checking linkage internal to disconnect. <N> **** Equipment Description **** disconnect 10 | 02-00-E-PP-8AZ
394221 | CR | 20190526 |  | 3 | R24LL; CVB replacement air hoses inadequate connections | Y | N |  | N | YES | <C> Owed to group changed from SCS to PROCENG as per the MRT. <D> **** Detailed Description **** In 2010, AR 225385 performed an RIE for replacment SS braided hoses. The new hoses were not specified correctly to minimize fitting connections. Since these hoses were specified with "tube fittings" it has caused maintenance to double the amount of tubing connections (4) instead of the normal (2) which these valves had originally. The hoses need to be specified with "tube adapters" swagelok Part No's SS-FM4TA4TA4-24 and SS-FM4TA4TA4-18. Recommend an action to change the part numbers and remove the existing stock from the warehouse. This may help with maintenance's AFI in mechanical joints The air hose Cat I'ds also need installed on the BOM's for the CVB Air Operators. <I> **** Actions Taken **** Took the CVB engineer into the wetwell and showed him the issues. Keeping our fingers crossed that he can make the changes that has been needed for a long time. I couldn't show my supervisor because he is not PAPR qualified. | 02-00-CVB-AO-1A1
394222 | CR | 20190526 |  | 4 | (NRC) "A" SW Pumphouse Exterior Lighting All Out |  |  |  | N | YES | <D> **** Detailed Description **** All the external lighting on the A SW pumphouse is extinguished. Verified the non-spare breakers on E-LP-3DC were all closed. Astronomical time clock E-TM -SWPH1A/LTG/EXT appears to be set correctly. The yard lighting in the area appears to provide sufficient illumination for safety. <I> **** Actions Taken **** Checked for obvious issues lik tripped breakers or damaged timer, found nothing visually. | 02-00-A-BLDG-MISC,02-00-E-LP-3DC,02-00-E-TM-SWPH1A/LTG/EXT
394223 | CR | 20190526 |  | 4 | (NRC) "A" SW Pumphouse Personnel Doorknob Stiff |  |  |  | N | YES | <D> **** Detailed Description **** The doorknkob on the A" SW Pumphouse personnel door A -DOOR-G101 is pretty stiff and hard to turn. Needs maintenance or replacement. <I> **** Actions Taken **** Door does function for safe egress. | 02-00-A-BLDG-MISC,02-00-A-DOOR-G101
394224 | CR | 20190526 | CAQ | C | RRC-V-13B Failed as found LLRT | Y | N |  | N | YES | <D> **** Detailed Description **** RRC-V-13B would not build up pressure for LLRT testing. the flow was at the max of the equipment. WO 02119749-01 TSP-RRC/X43B-C801 <I> **** Actions Taken **** Document failure in surveillance. Informed CRS, OCC and LLRT coordinator. | 02-00-RRC-V-13B
394225 | CR | 20190526 | CAQ | D | RPIS Probe MUX card module 2 fille 1 slot 14 is degraded/ | Y | N |  | N | YES | <D> **** Detailed Description **** During troubleshooting of RPIS system faults (WR 29148996) we reseated Probe Mux card module 2 file 1 slot 14, while inspecting the card for damage we saw the edge connector on the card has healily worn and is most likely the cause of the intermittent indication we were seeing. This Card need to be replaced ASAP. The replacement can be done online or during R-24 as long as these is no fuel movements going on. <I> **** Actions Taken **** Informed CRS/Supervisor/Engineering about the failing card and created CR/WR to replace the Probe Mux Card when we get more than one spare card in stores. | 02-00-CRD-RPIS-1
394226 | CR | 20190526 |  | 3 | PPM 3.1.1 update |  |  |  | N | NO | <D> **** Detailed Description **** AR 374932 changed the surveillance frequency of the ISP -RPS-Q901/902/903/904 surveillances from every 92 days to every 184 days and replaced them with an S coded surveillance number. PPM 3.1.1 was not updated to reflect the new surveillances. See page 40 of PPM 3.1.1. <I> **** Actions Taken **** Notified CRS>
394227 | CR | 20190526 |  | 3 | non quailified techs working on RPIS system |  |  |  | N | YES | <D> **** Detailed Description **** WOT 02110193-11 (removal of RPIS jumper cards) was worked by 2 temp I&C techs. This job came up towards the end of the day shift on 5/24. There was applied schedule pressure to get this task done due to OPS wanting to move fuel at the start of the oncoming night shift. After the task was completed to remove the jumper cards, RPIS system locked up. while troubleshooting the RPIS failure, it was found that 3 of the Probe Mux Cards in module 2 file 2 were not seated correctly or at all. These card are very difficult/tricky to remove and seat correctly. The cards that were incorrectly seated may not of been the cause of the RPIS lockup, but were a contributing factor to the issue. The station lost about 2.5 shifts of fuel movement. <I> **** Actions Taken **** Notified Supervision/Management that any and all work on RPIS and RDCS needs to be done by I&C techs that are qualified (ICAU in pqd). RPIS/RDCS is a very complicated system and is very difficult to troubleshoot and it takes alot of time to pinpoint the problem. Time that is precious during refuel outages. <N> CR reopened at trainings request. It is now 3/TRNMGT | 02-00-CRD-RPIS-1
394228 | CR | 20190526 |  | 4 | Hygrothermograph in whse 3 had batteries removed |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO#02132991-01, the hygrothermograph in warehouse 3 (building 78) was found without batteries. This piece of equipment had previously been inspected on 4/24/19 and the chart paper shows that it only recorded three days of data (until 4/27/19) before having the batteries removed. <I> **** Actions Taken **** Notified supervisor and wrote this CR. <N> **** Equipment Description **** Warehouse 3 (building 78)
394229 | CR | 20190526 |  | 4 | Hygrothermograph in bldg 113 missing |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO#02111591-01, the hygrothermograph in building 113 (paint locker) was discovered to be missing. The last known asset number located in this building is 0052387. It is unknown where it is at this time, but it was inspected on 4/24/19. <I> **** Actions Taken **** Informed supervisor and wrote this CR. <N> **** Equipment Description **** Building 113 (paint locker)
394230 | CR | 20190526 |  | 4 | FP-MDS-D68/2 degraded Label |  |  |  | N | YES | <D> **** Detailed Description **** While performing 15.3.14 it was noticed that the labels for FP-MDS-D68/2 and FP-MDS-D69/2 are barely legible. Due to the location on the outside of the building the direct sun light has degraded sticker type lable to the point they are peeling off. the labels on the side degraded also. New labels need to be made and installed. <N> **** Equipment Description **** FP-MDS-D68/2
394231 | CR | 20190526 |  | 3 | RRA-CC-9 Configuration different |  |  |  | N | NO | <D> **** Detailed Description **** While working work order 02106151-01, to re-install RRA-CC-9 sheetmetal panels. It was discovered that the original panels did not fit. The new coil and the old coil are not like for like. The new coil inlet and outlet flanges are off by 4 1/8â€. A new front panel will need to be fabricated and installed. The piping in work order 02106152-01 will require a revision to the weld record and work instructions to rework some of the piping. This revision will allow proper flange connections. <I> **** Actions Taken **** Contacted the EOC and Management Additional information from R24 EOC: 1) 5/25 EOC nights determined that TSW supply/return piping changes for installation of the nonlike-for-like replacement coil are within PPM 10.2.28 construction tolerance. 2) 5/26 EOC days determined that the replacement coil is a right-hand coil, not the left-hand coil that was desired for like-for-like replacement. Craft looked at the replacement coil for RRA-CC-8 in the warehouse (CID 61113605) - it is also a right-hand coil. A Design Equivalent Change modification package (DECP) will be required for installation of the right-hand replacement cooling coil at RRA-CC-9. AR EVAL 394251 has been initiated per DES-2-9. Once the nonlike-for-like replacement coil is installed, CVI 873-00,1 will no longer be correct for RRA-CC-9 - RRA-CC-9 will look like CVI 873-00,2 (i.e., RRA-CC-8) except the flow direction arrow for the AIR FLOW will be reverse. <N> The CC ordered was "left handad" but the one recieved was right handed. EC 17792 modified the right handed to be installed in R24 as temp modification but some Efficiency was lost due to this modification.
394233 | CR | 20190526 |  | 3 | EWP needs Material Issue tickets and Acceptance Tags |  |  |  | N | NO | <D> **** Detailed Description **** EWP/ Dataglance automatically adds the Material request to the WO but does not add the Issue Tickets or acceptance tags. Currently craft has to add them manually to each work order. This is a very time consuming/error likely evolution. Suggest making this an automated function when parts/ material are issued. This CR is for tracking purposes. <I> **** Actions Taken **** Notified supervision and EWP <N> This CR is being closed with the suggested issue ticket or acceptance tags automated enhancement request captured in the eWP Issues List, which addresses eWP issue and request for enhancements.
394234 | CR | 20190526 |  | 3 | (R24LL) Evaluate new main transformer spare parts inventory |  |  |  | N | YES | <D> **** Detailed Description **** During the 25/500KV window during R24 during the accessory check PM for E-TR-M3 some of the relays failed. While reviewing the parts new CAT IDs were created to order parts and the recommended parts are already obsolete. The importance of spare parts for the main transformers is to ensure a lack of parts do not extend 25/500KV window during an outage. Recommend assignment to system engineer to evaluate which additional spare parts should be stocked for future outages. | 02-00-E-TR-M1,02-00-E-TR-M2,02-00-E-TR-M3
394237 | CR | 20190526 | CAQ | C | as found and as left delta readings on E-CB-B/8 | Y | Y |  | N | YES | <D> **** Detailed Description **** as-found and as left delta force readings did not meet applicable range when first tested. <I> **** Actions Taken **** adjusted sure-close and performed test again and passed. wrote CR and documented in comments of work order. <N> **** Equipment Description **** W467 K7/14.2 (E-SM-8 room) Adjustments made per work instructions. CR is for documentation. | 02-00-E-CB-B/8
394238 | CR | 20190526 | CAQ | C | E-CB-8/3 As found MOC pin force test <65 lbs | Y | Y |  | N | YES | <D> **** Detailed Description **** As found MOC pin force test <65 lbs. <I> **** Actions Taken **** Adjusted MOC pin force, generated CR. <N> **** Equipment Description **** E-CB-8/3 Condition corrected under wo 02111274 | 02-00-E-CB-8/3
394239 | CR | 20190526 | CAQ | D | As-Found Condition of IRM-DRVE-DET/2C | Y | Y |  | N | YES | <D> **** Detailed Description **** This CR is to document the as-found condition of IRM-DRVE -DET/2C during performance of WOT 02043328-11. Refer to documents posted to EDMS. Work package completed satisfactorily. <I> **** Actions Taken **** 1) Informed system engineering of findings. 2) Submitted CR. 3) Informed operations. | 02-00-IRM-DRVE-DET/2C
394240 | CR | 20190526 | CAQ | C | M&TE Rejection |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0068591 Proto Torque Wrench- model 6064C 40-200in/lb found OOT & Rejected. OCC & EOC notified of OOT/ Rejection- wrote CR #394240 to capture the OOT/Rejection in compliance with PPM 1.5.4 & SWP-CAP-01. Given to EFIN to evaluate on 5/26/19. DEF #7042A written. When EFIN has completed their Eval- will attach EDMS. <I> **** Actions Taken **** OCC &EOC were notified of OOT/ Rejection- wrote CR #394240 to capture the OOT/Rejection in compliance with PPM 1.5.4 & SWP-CAP-01 Given to EFIN to evaluate. EFIN Eval: WO #02109790-15 was reviewed against criteria in PPM 1.5.4 and deemed to NOT be acceptable. Step 7.7.17 needs to be re -performed. OCC notified 5/27/19. DEF #7042A written.
394241 | CR | 20190526 | CAQ | D | SW-FE-37B does not match the drawing | Y | Y |  | N | NO | <D> **** Detailed Description **** During performance of WO 02112412-01 Insp/clean SW-FE-37B it was discovered that the flow element does not conform to the drawing D-FE-039. There are steps in the package to drill the holes to make it match. This CR is for documentation of the as found condition. <I> **** Actions Taken **** CR generated, flow element made to conform to the dwg
394242 | CR | 20190526 |  | 4 | R-24 Lessons learned |  |  |  | N | NO | <D> **** Detailed Description **** Temporary LED lighting is needed for the elevators when bus outages are going on. Light being inadequalte is a safety hazard for personel entering and exiting the elevator. <I> **** Actions Taken **** Notified supervision
394243 | CR | 20190526 |  | 4 | WO 02078876 prerequisites incorrect |  |  |  | N | NO | <D> **** Detailed Description **** WO 02078876 task 2 prerequisite 3.2 states the generator rotor must be removed for the work. Repair and testing of the fiber optic vibration monitoring system requires partial disassembly of the generator but does not require removal of the rotor. <I> **** Actions Taken **** Discussed with turbine deck coordinators, worked with planning to remove the prerequisite
394244 | CR | 20190526 | CAQ | D | FDR-V-171 shows signs of leakby, indicates dual | N | N |  | N | YES | <D> **** Detailed Description **** FDR-V-171 shows signs of leakby, causing FDR-DM-111 to drain water back to FDR-TK-6. Valve also shows dual indication on mimic noard G11-P001-1. Recommend possibly increasing air signal to shut valve more tightly, or rework internals. Also properly align limit switches <I> **** Actions Taken **** Informed MCR | 02-00-FDR-V-171
394246 | CR | 20190526 |  | 4 | Generator Water Detector Level High Alarm received in MCR. | N | N |  | N | YES | <D> **** Detailed Description **** Generator Water Detector Level High Alarm received in MCR Panel 820.B3 drop 7-5. Water is accumulating in H2-LS-6C at a rate of 1-2 gallons every 4 hours. <I> **** Actions Taken **** Performed steps of ARP and drained about 1 gallon of water. Temp log established to drain detector H2-LS-6C once every 4 hours. <N> **** Equipment Description **** TG 471W | 02-00-H2-LS-6C
394247 | CR | 20190526 |  | 4 | TSW-PCV-20 packing leakage. | N | N |  | N | YES | <D> **** Detailed Description **** TSW-PCV-20 packing leakage appears to be getting worse each outage. Laborers report that a bucket under the valve needs to be emptied about every 40 minutes. This was last written up on 10-2-2017. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG-441 E | 02-00-TSW-PCV-20
394248 | CR | 20190526 |  | 4 | N1 Winding Temp 49T Alarm | N | N |  | N | YES | <D> **** Detailed Description **** During the walkdown in SOP-ELEC-BACKFEED with Operations, we found the N1 transformer winding temp 49T in alarm. Temperature indications looked normal. Recommend reset of the alarm. | 02-00-E-TR-N1
394249 | CR | 20190526 |  | 4 | Washout Side of Trenwa by M4 Transformer | N | N |  | N | YES | <D> **** Detailed Description **** During a walkdown of SOP-ELEC-BACKFEED with Operations, we found a washout of the side of the Trenwa near the M4 Transformer. This May have occured during dleuge testing. Recommend investigate and fill hole. <I> **** Actions Taken **** Placed two pylons in the hole. <N> **** Equipment Description **** Trenwa near the M4 transformer.
394250 | CR | 20190526 |  | 4 | E-CB-N1/2 will not rack in (affects backfeed) | N | N |  | N | YES | <D> **** Detailed Description **** E-CB-N1/2 will not rack into the E-SM-2. Multiple attempts to rack this breaker in have been unsuccsesfull. Electrical maintenance applied lubricant to the Primary Stabs to assist in breaker racking, but it appears the breaker is having issues racking in well before the main contacts are engaging. Suspect the shutter mechanism/roller is what is preventing the breaker from being racked in. The levering screw was only able to be rotated ~ 2 turns and excessive torque was required. Please investigate repair shutter assembly. This will impact backfeed, which is scheduled for 5/27 @ 1600 <I> **** Actions Taken **** Informed Electrical Production SRO <N> **** Equipment Description **** TG 471W | 02-00-E-CB-N1/2
394253 | CR | 20190526 |  | 3 | Dropped Item in the â€œAâ€ inlet waterbox FME level 1 area | N | N |  | N | NO | <D> **** Detailed Description **** While working on WO 02113928-01 and replacement of the anodes in A inlet waterbox a Â¾â€ nut fell out of the employees hand. This is an FME level 1 work area. <I> **** Actions Taken **** Notified the OCC and direct supervision. The team will follow guidlines provided in PPM 10.1.13 with added focus on the planned retrieval. Once a retrieval plan is established Form 26337 will be filled out and uploaded to the EDMS. <N> **** Equipment Description **** Alpha Inlet Waterbox T441 below the butterfly valve. Williams Plant Services.
394254 | CR | 20190526 | CAQ | C | HCV-RIS-RAD/1 IMDS needs updating |  |  |  | N | NO | <D> **** Detailed Description **** In order to perform a calibration loop check on HCV-RIS -RAD/1, the IMDS needs updating. Replace RM4 Analog Output tolerance with HCV-MV/I-1 Output tolerance in madc. The HCV-MV/I-1 Output is a better representative of the functioning of the components in the loop and also due to accessibility issues with RM4. <I> **** Actions Taken **** Request IMDS change in order to issue new calibration procedure 10.27.119.
394256 | CR | 20190526 |  | 4 | R24LL â€“ Turbine Generator project support not scheduled |  |  |  | N | NO | <D> **** Detailed Description **** The turbine generator project continues request support from the electric shop for scoped evolutions that do not have schedule tasks or resources allocated. These requests for embedded support are impactful and not planned or scheduled. This needs to be corrected for R25 on planned projects like this. Examples are requests for generator neutral link removal, generator hi-pot support (10.25.139 sections 7.1 & 7.11), and thermal head re-terms. <I> **** Actions Taken **** Talked to turbine project manager and floor coordinator.
394258 | CR | 20190526 |  | 3 | RCC-V-730A Hand wheel | N | N |  | N | YES | <D> **** Detailed Description **** RCC-V-730A Hand wheel is missing <I> **** Actions Taken **** Informed my supervisor Rob Rhodes <N> **** Equipment Description **** Its in the Dry well @ 64 degrees and knee level . Reopened CR to address Reactor Startup attribute. | 02-00-RCC-V-730A
394259 | CR | 20190526 |  | 3 | RRC-V-19 "COLD" adjustment of new Reed Switch | Y | N |  | N | I DONT KNOW | <C> Changed Owed to group to elecm, removed RXSU, and changed to non-CAQ as per the MRT. <D> **** Detailed Description **** WO#02126177-01 instructs electricians to replace Switch 1 and Switch 4 for RRC-V-19 OPEN and CLOSE indication, then to perform a "COLD" adjustment before Mode 3 "HOT" adjustment to reduce potential Dose. Adustments are to be made with a non-ferrous tool (9/64 allan wrench) to eliminate magnetic interference within the switch when adjusting up/down. A request/order was put in for the appropriate tool and has not arrived in time for COLD adjustment. Close indication switch has been set to a "best guess position" with repeatable performance based on guidance from 10.25.100. <I> **** Actions Taken **** Notified Supervision <N> **** Equipment Description **** RRC-V-19 MR was submitted for tool. Request could not be completed in time. Adjustments have been made and WO is finished.
394260 | CR | 20190526 |  | 2 | worker entered the wetwell without signing onto the clearanc |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of WO 02088276-01 a worker entered the wet well to perform peer verification steps and did not sign onto the clearance order. when he realized that there was a clearance order that needed to be signed on hei mmediately contacted his supervisor. <I> **** Actions Taken **** Contacted Maint manager, performed event investigation. <N> This clearance order level 3 event will be addressed by AR 394201. A HUIT has been assiigned to Maintenance to address the issue and Operations will own the parent CR. No additional action required for this CR
394261 | CR | 20190526 |  | 4 | Not enough O-ring seat surface on TO-HX-1A reversing head | N | N |  | N | YES | <D> **** Detailed Description **** While recoating the reversing chamber (bottom head) of TO -HX-1A, some of the o-ring seat surface was removed while sand blasting. Itâ€™s believed that ~1/8â€ in width was taken off. Recommend action to boilermakers to apply belzona on the removed section to restore the o-ring seat to no less than Â¼â€ in width then machine that surface. <I> **** Actions Taken **** Informed EOC and system engineer then inititated this CR | 02-00-TO-HX-1A
394262 | CR | 20190526 |  | 4 | E-CVT-500KV/A is exhibiting excessive crackling noises | N | N |  | N | YES | <C> Reopened CR to edit Owed to Group. <D> **** Detailed Description **** Once Backfeed from BPA ASHE Station was established a walkdown of the Transformer Yard was conducted. At the new CCVT installed on Alpha Phase of the 500KV line, it was observed by the System Engineer and Transformer yard Coordinators that E-CVT-500KV/A is exhibiting excessive crackling noises around the termination area at the corona ring at the top of the CCVT. <I> **** Actions Taken **** Notified supervision, OPS and generated this CR. <N> **** Equipment Description **** Transformer Yard under BPA Alpha Phase Tower. | 02-00-E-CVT-500KV/A
394263 | CR | 20190526 | CAQ | D | RFW-V-10B Disc hits valve body prior to designed hinge stop. | Y | N |  | N | YES | <D> **** Detailed Description **** During initial inspection under WO# 02085914-01, valve disc was stroked to verfiy full open position. The O.D. of the Resilient Seat Retainer hits the valve body prior to the designed hinge hard stop. Valve body has indications where the disc has been hitting. <I> **** Actions Taken **** Initiated CR for discrepancy. <N> **** Equipment Description **** Drywell 52 | 02-00-RFW-V-10B
394264 | CR | 20190526 |  | 4 | E-TR-M1 Alarm during 25/500KV energization (R24) | N | N |  | N | YES | <D> **** Detailed Description **** Alarm Point 1 â€œGas Operated Alarmâ€ came in during energization. Alarm was reset and did not come back in. | 02-00-E-TR-M1
394265 | CR | 20190526 |  | 4 | E-TR-M3 Alarms during energization (R24) | N | N |  | N | YES | <D> **** Detailed Description **** The following alarms were received during 25/500KV energization: 16 Cooler 3 Failure or Off Position 17 Cooler 4 Failure or Off Position 18 Loss of Oil Flow Pump 1 19 Loss of Oil Flow Pump 2 20 Loss of Oil Flow Pump 3 22 Very Low oil level or high flow rate Trip 1 23 Very Low oil level or high flow rate Trip 2 24 Loss of Normal Power Also the 86-1 and 86-2 were actuated. These relays are associated with the buchholz relay and points 22 and 23 of the local annunciator. All alarms and lockouts were reset per the ARP and cleared. <I> **** Actions Taken **** Notified Production and reset the alarms per the ARP. | 02-00-E-TR-M3
394266 | CR | 20190526 |  | 4 | Dropped scaffold tube in the â€œCâ€ inlet waterbox | N | N |  | N | NO | <D> **** Detailed Description **** While working on WO 02078764-03 and removal of the scaffold supporting replacement of the lower disc pin on CW-V-2C a 6â€™ scaffold tube was dropped into the water below. This is a FME level 1 area. <I> **** Actions Taken **** Notified the OCC and direct supervision. The team will follow guidelines provided in PPM 10.1.13 with added focus on the planned retrieval. Once a retrieval plan is established Form 26337 will be filled out and uploaded to the EDMS. Reference work request 29149026. <N> **** Equipment Description **** Charlie Inlet Waterbox T441 below the butterfly valve. Williams Plant Services. Item was recovered and documented in the EDMS
394269 | CR | 20190526 | CAQ | C | RWP Dressout Violation |  |  |  | N | NO | <D> **** Detailed Description **** Worker entered Contamination Area without any Protective clothing. RB 501' CA <I> **** Actions Taken **** Supervision informed, individual restricted from RCA. <N> **** Equipment Description **** RB 501 SOP CA A Crane individual went through open door at Drywell Controlled Area DCA. Postings were adequate, the individual just didnâ€™t read the signs. The door he entered was closed, but not locked. The individual traversed the DCA to SOP area and was stopped by RP. RP restricted the individual from RCA. The RPM met with him and his supervisor, and ultimately he was released back to work.
394270 | CR | 20190526 |  | 3 | Install Meltric devices in E-PP-F10/3 |  |  |  | N | YES | <D> **** Detailed Description **** To support the future refueling outages install three 60 amp Meltric devices on the side of E-PP-F10/3. See AR 373530 for this same type of work on E-PP-F10/4. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817. | 02-00-E-PP-F10/3
394271 | CR | 20190526 |  | 3 | FM on beam iside inner annulus at 0 az 519' el | Y | N |  | N | YES | <D> **** Detailed Description **** while working wo # 02114367 for rwcu-te-21 noticed sheet metal screws out of reach and minor insulation damage at the enterance/exit of the inner annulus at 519' el 0 az. <I> **** Actions Taken **** told suppervisor took pictures wrote this cr <N> **** Equipment Description **** 519' el 0 az | 02-00-RWCU-TE-21
394272 | CR | 20190526 |  | 3 | Dose alarm received while doff PCs at TG501 SOP |  |  |  | N | NO | <D> **** Detailed Description **** A worker received a dose alarm while removing PCs at TG501 SOP. Coworkers all received a dose of 0 mRem and no dose alarm. The worker with the dose alarm had 102 mRem. The accumulated dose indicating on his dosimeter. The workers work area and travel path were all <1 mRem/hr. <I> **** Actions Taken **** The worker notified his fellow workers, exited the area, and contacted HP. Electronic dosimeter used was removed from service and examined by Radiological Support personnel. <N> Form 26441 and Histogram have been uploaded into EDMS. Per RP Supervision, this was an invalid alarm. The ED was dropped which caused the alarm.
394273 | CR | 20190526 |  | 4 | PAP SAM 42814 handle is coming loose | N | N |  | N | YES | <D> **** Detailed Description **** RCA exit at PAP/ GSB HP-EQ-42814 SAM's handle keeps coming loose <I> **** Actions Taken **** Told HP Lead and Supervisor and created CR | 02-00-HP-EQ-42814
394274 | CR | 20190526 |  | 4 | TSC womens bathroom sink water not working | N | N |  | N | NO | <D> **** Detailed Description **** Sink in womens bathroom at the TSC is not working properly <I> **** Actions Taken **** Told HP lead tech and Supervisor and created CR <N> **** Equipment Description **** TSC womens bathroom
394275 | CR | 20190526 |  | 3 | Need procedural enhancement for ARC flash protection in CA's |  |  |  | N | NO | <D> **** Detailed Description **** Current RWP requirements for CA's do not address ARC flash protection when needed for ISPM-20 activities. <I> **** Actions Taken **** Wrote CR, discussed with another HP supervisor, recommend procedure change to 11.2.8.2. This may affect other HP procedures too and require more research.
394276 | CR | 20190526 |  | 3 | Items missing from Fire Brigade Station 1 on TG 441 |  |  |  | N | NO | <D> **** Detailed Description **** During completion of Work Order 02133231-02, it was noted that 2 required items are missing from TG 441 Fire Brigade Station 1. The missing items are one radio and the spare thermal imaging camera (TIC) <I> **** Actions Taken **** Informed RP supervision and shift manager. <N> reassigned from AR - opstaff to AR -TEFP per email Cooper to Poznanski dated 5/28/2019
394277 | CR | 20190526 |  | 3 | E-RLY-59/81T had an as found time that was out of tolerance | N | N |  | N | YES | <D> **** Detailed Description **** E-RLY-59/81T had an as found time of 6.43 seconds which is out of tolerance per the data sheet tolerance of 5.7-6.3 seconds. There are some discrepencies between the data sheet tolerance and E514-14 that may need to be looked at by engineering. The data sheet tolerance is 5.7-6.3 seconds which is 5% and E514-14 has a tolerance of 6 seconds plus or minus 1 second which would put our tolerance at 5-7 seconds. Relay was adjusted and as left time was in tolerance at 5.89 seconds. <I> **** Actions Taken **** Informed operations and supervisor. Adjusted relay back into tolerance. | 02-00-E-RLY-59/81T
394279 | CR | 20190527 |  | 4 | PWC-TBE-1 is leaking | N | N |  | N | YES | <D> **** Detailed Description **** PWC-TBE-1, the influent turbidity meter for the flocculator, is leaking from both its drain valve and spillover connection. This unit (Hach 1720C) is long obsolete. Recommend replacement or repair of this unit. Note that PWC-TBE-2 is also a Hach 1720C, but is not currently leaking. Both units should be replaced. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** Flocculator building | 02-00-PWC-TBE-1
394280 | CR | 20190527 |  | 3 | SPECIAL TOOLS, M&TE,removed from staging area TG501 |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Tools, M&TE, miscellaneous pant equipment from blade vibrations probes and LVDTs moved from the TG501 I&C staged area. Bags of tools that were arranged for specific jobs on the turbine deck have been taken and no one received a turnover on where they have been taken to. Tool crib was checked and expanded the team to different departmentsâ€™ laborers and Siemens. This was done on DAYSHIFT if anyone knows where they are at please put them back there are special tools (one & only kind of type) and will be needed this could delay jobs and impact schedule when those jobs come up. <I> **** Actions Taken **** Notified supervisor of different departments and initiated CR for action tracking <N> **** Equipment Description **** TG501 Items cannot be relocated. Replacements acquired.
394281 | CR | 20190527 | CAQ | D | E-CB-8A1CR has stripped â€œCâ€ phase mounting lug. | Y | N |  | N | YES | <D> **** Detailed Description **** During the removal of temporary power for E-C1-2B it was determined that the â€œCâ€ phase mounting lug for E-CB-8A1CR was stripped out. â€œCâ€ phase lead was landed but could not be torqued. Breaker will need to be replaced. | 02-00-E-CB-8A1CR
394282 | CR | 20190527 |  | 4 | MCR annunciator Bus 31 MCC OL Trip won't clear | N | N |  | N | YES | <D> **** Detailed Description **** 4.800.C3 drop 7-4 will not clear in the MCR. Supply breakers for MC-3A, 3B, 3C, 3D and 5C all had their OC trip switches reset locally at each breaker but alarm did not clear. All supply breakers are closed. <I> **** Actions Taken **** Depressed pushbutton labeled "Push to reset OC trip switch" for supply breakers to MC-3A, 3B, 3C, 3D and 5C. Alarm remained locked in. | 02-00-E-SL-31
394283 | CR | 20190527 | CAQ | D | PMT for WMA-FN-52B exceeded criteria in work package | Y | Y |  | N | YES | <D> **** Detailed Description **** The percent unbalance for WMA-FN-52B did not meet the criteria for PMT per WO 02117675-05. The percent unbalance for current at 22.6% was greater than the 10% specified in the work instructions. Current for phase A was 15.8 amps, phase B was 13.0 amps, and phase C was 16.4 amps. The voltage imbalance was within tolerance at 0.195%. Similar results were found in March 2015 under WO 02036774-04 on WMA-FN-52B where current unbalance was recorded at 18.4%. CR330505 was written and current readings were later recorded at less than 1% unbalance. Coil replacement in 2017 under WO 02107458-02 had satisfactory current readings. Recommend a re-measurement of line current for each phase at the earliest convenience as the current readings recorded could be indicative of a failing fan motor, a result of normal bus loading at the time the readings were taken, or a result of the test equipment. <I> **** Actions Taken **** Discussed results with craft and reviewed history on component. Discussed with SM. Initiated CR. | 02-00-WMA-42-8F1B,02-00-WMA-M-FN/52B
394284 | CR | 20190527 |  | 3 | GEN-RPP-14 needs update for evaluation of RWCU shielding |  |  |  | N | NO | <D> **** Detailed Description **** GEN-RPP-14 Temporary shielding does not take in to consideration seismic requirements of RWCU piping upstream of RWCU isolation valves RWCU-V-1 and 4 relative to Tech Spec 3.5.2. Crrently the procedure identifies RWCU as not essential in modes 4 and 5 nor downstream if the isolation instrumentation is inoperable or the isolation valves cannot otherwise be credited or isolated. With the adoption of TSTF 542, the procedure and supported engineering evaluaton needs to be revisited. <I> **** Actions Taken **** Additionally, consider including evaluation methodology captured in AR 394278 to supplement procedure taboles
394285 | CR | 20190527 | CAQ | D | RRC-FT-24B as-found OOT | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of ISP-APRM/RRC/B302, RRC-FT-24B was found OOT on step 7.4.24. RRC-FT-24B was replaced under 02087668-01 and ISP-APRM/RRC-B302 is initial PMT for replacement transmitter. Adjusted per procedure to within as-left specifications <I> **** Actions Taken **** Notified operations, supervisor, wrote CR. <N> Reopened CR due to accidentally cancelling it. Reopened second time to edit the completion required check box.
394286 | CR | 20190527 | CAQ | C | PSR-V-X77A/1 exceeds admin limit | Y | N |  | N | YES | <D> **** Detailed Description **** As-found LLRT on PSR-V-X77A/1 measured leak rate at 9060 sccm (at test pressure of 38.643 psig) which is above its admin limit of 750 sccm. Test performed under WO 02112019 -01 and TSP-PSR-R801. <I> **** Actions Taken **** Notified LLRT SRO and OCC | 02-00-PSR-V-X77A/1
394292 | CR | 20190527 | CAQ | D | PSR-V-X77a/2 fails valve position indication test | Y | N |  | N | YES | <D> **** Detailed Description **** PSR-V-X77A/2 valve position indication (VPI) did not show greater than 20,000 sccm after opening the valve. Pressure was maintained in the required pressure band. Leak rate monitor only showed 1400 sccm. Test performed under WO 02112019-01 and TSP-PSR-R801. <I> **** Actions Taken **** Notified LLRT SRO and OCC | 02-00-PSR-V-X77A/2
394293 | CR | 20190527 |  | 4 | RCC-P-1C auto started when conditions not met | N | N |  | N | YES | <D> **** Detailed Description **** During recovery of RCC-P-1B and RCC-P-1C during SOP-ELEC -SM8-MAINT; RCC-P-1B was taken out of "pull to lock" and started to restore normal 2 pump operation. RCC-P-1C was then taken out of "pull to lock" to the normal after stop position at which time it auto started. There appears to be an issue in the control power logic for RCC-P-1C that is making it believe there are not 2 RCC pumps running when there really are. <I> **** Actions Taken **** RCC-P-1C was taken back to "pull to lock" to prevent 3 pump operation and a caution tag will be generated for PCSC. | 02-00-RCC-P-1C
394294 | CR | 20190527 |  | 3 | Delay in completion of WO 02111490 |  |  |  | N | NO | <D> **** Detailed Description **** While performing 02111490 (E-MC-8BB) E-CB-8B2D: INSPECT MCCB (SR) delays to finishing the 01 task were encountered. Poor quality turnover along with PPM 10.25.48 instructions needing enhancement contributed to the delay in finishing the 01 task <I> **** Actions Taken **** Generated CR to document issues with completion of task. Informed Electrical Component Manager and OCC. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
394295 | CR | 20190527 |  | 3 | RFW-DT-1A set screws on the retaining nut need shortened | N | N |  | N | YES | <D> **** Detailed Description **** During installation of the oil guard assembly (CID 37642) on WO 02116715-01 it was discovered that the existing 2 allen set screws that are 90 deg. apart on the retaining nut that holds the turning gear, protrudes into the path of the oil guard assembly. This will need to be adjusted due to the thrust of the turbine and will need to be investigated and a repair path made. <I> **** Actions Taken **** Notified my supervisor the main control room and initiated this condition report | 02-00-RFW-DT-1A
394296 | CR | 20190527 | CAQ | D | PDIS MET tower data not available | N | N |  | N | YES | <D> **** Detailed Description **** After restoration of SM-8 power the MET data is not available on PDIS. The data is comming through on Board L indications. MET remains Non-functional. <I> **** Actions Taken **** Wrote CR | 02-00-MET-TE-1
394298 | CR | 20190527 |  | 4 | OPDS TRB annnunciator silence does not work. | N | N |  | N | YES | <D> **** Detailed Description **** 115KV OPDS TRB annunciator alarms will not silence when the silence button is depressed. There are currently 2 locked in alarms: Set 1 and Set 2 Alarm/Trip Cutout alarms. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** Transformer Yard.
394300 | CR | 20190527 |  | 3 | Importance of an ASD maintenance procedure |  |  |  | N | YES | <D> **** Detailed Description **** While attempting to completeWO 02116454-01 RRC-IMD-ASD1B/2 clean and inspect I had some questions on instruction4.15.4 which statesâ€œusing a 1000v megger read the resistance to ground.Expected value isGT 2 megaohms.â€ We stopped work and expanded the team.After finding several questions that could not be answered promptly I pulled some history packages. While reading through 2015(WO 02067310-01) I found the same step to measure resistance on the bus work in the drive and found an important NOTE that was NOT in WO 02116454-01.In WO 02067310-01(2015 package) above instruction 4.4 a boxed in NOTE readsâ€œthe jumper is required to maintain continuity for the bus work.Fluke 25 will be used to measure resistance; both grounds on the NATL boards will need to be removed.Any induced voltage ABOVE 45 VOLTS WILL DAMAGE THE NATL BOARDSâ€ <I> **** Actions Taken **** This is where stopping work stopped a possible event from happening, if craft would have moved forward and proceeded with a 1000v megger test, as directed in WO 02116454-01( the 2019 package), boards in the ASD drive would have been fried! This is one of many mistakes in this package that craft has found. We need a written procedure for work step clarity, consistency, and equipment reliability. Replacement parts for this system are obsolete as all damaged parts need to be sent off and refurbished which is costly in both time and money. Supervision, craft, and engineering informed of more detailed concerns via email. <N> **** Equipment Description **** RRC-IMD-ASD1B/2 in ASD building 8 | 02-00-RRC-IMD-ASD1B/2
394304 | CR | 20190527 |  | 3 | PPM 10.25.139 revision |  |  |  | N | NO | <D> **** Detailed Description **** PPM 10.25.139 provides guidance to perform HIPOT testing of the main generator. Section 7.1 of the procedure has a step to install shunt screws in the CT terminal box to short and ground the CTs. There is no step in the recovery section to remove the shunt screws. Please revise the procedure to provide guidance to remove the shunt screws if necessary, shunt screws may need to stay in place if they were installed or are being controlled by another procedure such as SOP-ELEC-BACKFEED. <I> **** Actions Taken **** Discussed with EOC and OCC. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
394305 | CR | 20190527 |  | 4 | Oil identified under E-TR-N1 tap changer control | N | N |  | N | YES | <D> **** Detailed Description **** Oil found below tap changer control on E-TR-N1. While performing the 25/500KV energization walkdown oil was seen below the E-TR-N1 tap changer control. This leak was previously identified under AR-CR 00359415 and WO 02106169. | 02-00-E-TR-N1
394306 | CR | 20190527 |  | 3 | R24LL Logic between two PM's that is needed. |  |  |  | N | NO | <D> **** Detailed Description **** The executable work order 02110832 for PMIOD-RQ 00017421-02 for funtional test of EGEN1RE068 task 02 was not performed before 02111988-07 which lifted a lead preventing 02110832-02 from being performed. 02111988 is the executable work order for PMID-RQ Inpliment Plant Backfeed. Need to make the 02 task for 00017421-02 a predecessor to task 07 of work order for 00023592-01 <I> **** Actions Taken **** Reschedule the affected tash to a later point in the outage that had the the right conditions to perform the work.
394307 | CR | 20190527 | CAQ | D | RHR-V-4C - Inspection / blue check | Y | N |  | N | YES | <D> **** Detailed Description **** RHR-V-4C wedge seating surface has several indications on the wedge seating surface on both sides. Additionally, the as-left blue check identified the seat width was too wide and did not achieve 360 deg bluing between the 5 - 7 o'clock position afte seat lapping. This requires a 8 degree angle change. The wedge is barely hittting the heal (lots of wedge material left) whih would require 0.010 removal. See attached pictures in EDMS. <N> As documented in WO 02107551, RHR-V-4C seating surfaces (disc and seats) were lapped, the in-body guides and guide rail on the disc were cleaned up (smoothed) and the valve was reassembled. The results of the As Left diagnostic testing on RHR-MO-4C show vast improvement over its As Found condition and is attributable to the work performed this outage. The force required to unseat the disc when going open, was exceeding actuator rating at the start of the outage. Now the unseating force (Open thrust at cracking) is reduced by ~25,000 lbs and is now only ~50% of the force applied when the valve is closed (Thrust at Total). | 02-00-RHR-V-4C
394308 | CR | 20190527 |  | 4 | R22 LL: LESS THAN ADEQUATE COMMUNICATION RESULTED IN IMPACT |  |  |  | N | NO | <D> **** Detailed Description **** Less than adequate communication for establishing radiological controls of upper containment areas per HPI -12.74 on 5/26/17 unnecessarily impacted work in the upper drywell during fuel movement. Schedule activities associated with main steam relief valves were prevented from being worked. <I> **** Actions Taken **** Informed OCC.
394309 | CR | 20190527 | CAQ | D | RHR-V-4C failed blue check | Y | N |  | N | YES | <C> Duplicate of 394307 <D> **** Detailed Description **** In support of work order 02107551-05, the wedge for RHR-V -4C failed its blue check <I> **** Actions Taken **** Engineering and the Outage Command Center are evaluating the path forward. <N> As documented in WO 02107551, RHR-V-4C seating surfaces (disc and seats) were lapped, the inbody guides and guide rail on the disc were cleaned up (smoothed) and the valve was reassembled. The results of the As Left diagnostic testing on RHR-MO-4C show vast improvement over its As Found condition and is attributable to the work performed this outage. The force required to unseat the disc when going open, was exceeding actuator rating at the start of the outage. Now the unseating force (Open thrust at cracking) is reduced by ~25,000 lbs and is now only ~50% of the force applied when the valve is closed (Thrust at Total). | 02-00-RHR-V-4C
394310 | CR | 20190527 |  | 4 | R22 LL: IMPACTS TO UPPER DRYWELL WORK DURING FUEL MOVEMENT |  |  |  | N | NO | <C> Duplicate of 394308 <D> **** Detailed Description **** R22 LL: IMPACTS TO UPPER DRYWELL WORK DURING FUEL MOVEMENT NOT IDENTIFIED DURING OUTAGE SCHEDULE DEVELOPMENT . Exclusion area impacts on drywell work when establishing radiological controls of upper containment areas per HPI -12.74 were not identified during outage schedule development. This lesson learned needs to be captured for future outage scheduling. <I> **** Actions Taken **** Informed OCC.
394311 | CR | 20190527 | CAQ | D | RHR-V-53B As-found inspection | Y | N |  | N | YES | <D> **** Detailed Description **** RHR-V-53B iinternal valve inspectoin identified the leak-by on the seat which may have been the result in previous RHR Overpressure events. The seat and idisc are covered wiith corrosion products on downstream side . See attached piictures. <I> **** Actions Taken **** Condition is corrected during maintenance. | 02-00-RHR-V-53B
394312 | CR | 20190527 |  | 3 | RPS-MG-2 tripped off | N | N |  | N | YES | <D> **** Detailed Description **** A few seconds after RPS-MG-2 came up to rated speed and the motor on pushbutton was released it tripped off and coasted back down. Initially while the pushbutton was held the green light went off and the red on light lit; upon tripping, conditions reverted as expected to green light on, red off. Voltage was stable about 120vac. <I> **** Actions Taken **** Informed CRS & SSS <N> REFERENCE SOP-RPS-START SECTION 5.2 START OR RESTART OF RPS-MG-2 , 5.2.2E. RELEASING RPS-RMS-MG2/START WHEN RPS-MG-2 HAS COME UP TO SPEED IS OPEN TO INTERPRETATION. WE FOUND THAT HOLDING IN THE START PUSHBUTTON FOR 30 SECONDS WORKED GREAT. RECOMMEND AN ENHANCEMENT MADE TO THIS PROCEDURE TO ADD A NOTE REFERNCING THE 30 SECOND PUSHBUTTON HOLD IN TIME. | 02-00-RPS-MG-2
394314 | CR | 20190527 | CAQ | C | Snubber disconnected from extension tube | N | N |  | N | YES | <D> **** Detailed Description **** Snubber RWCU-950N (WEST) on a 6â€ RWCU (2)-3 line was found disconnected from its extension pipe with broken bolts in RX 548â€™ RHR-HX-B room. The EAST snubber is still intact. Photos are attached to EDMS. Recommend replace snubber and bolts. Recommend CR go to AR-DMC. <I> **** Actions Taken **** Notified EOC/OCC. <N> **** Equipment Description **** Hanger ID RWCU-950N (W). Located @ 564' elev in the RX 548' RHR-HX-RM.
394315 | CR | 20190527 | CAQ | D | PRM-SR-1 found secured | N | Y |  | N | YES | <D> **** Detailed Description **** While performing CSP-INST-D201, Chemistry Daily Channel and Source Checks, it was discovered that PRM-SR-1 trouble light was locked in and that the sample rack had been secured. The instrument log indicated that the initiating condition was NGD-11 AC not valid. <I> **** Actions Taken **** Chemistry supervision and specialist informed. Supervisor informed IC. CRS and CRO informed. PRM-RIS-1 instrument log reviewed. Compensatory measures entered for the loss of PRM-SR-1 - T19-R24-SM8-MAINT-001. Flow verified through PRM-SR-2 501' corridor. | 02-00-PRM-SR-1
394317 | CR | 20190527 | CAQ | D | 9 fasteners as-found torque values below acceptable value. | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Per WO#02085089-01, 02085090-01 and 02085091-01, torque verification is performed on mounting hardware for solenoid cluster assemblies on MS-SPV-28B1, 28C1 and 28D1. work steps require verification of 25 ft/lbs on items 31, 55, 57, 67, and 77 (CVI 853-00,1). On MS-SPV-28B1, four fasteners were found 1/2-1 flat short of 25 ft/lbs. On MS-SPV-28C1, four fasteners were fount 1/2-1 flat short of 25 ft/lbs. And on MS-SPV-28D1, one fastener was approximately 1-flat short of 25 ft/lbs. <I> **** Actions Taken **** notified Supervisor and Generate CR. Fasteners were tightened to 25 ft/lbs per work instructions. All as left are satisfactory. <N> **** Equipment Description **** Steam Tunnel MS-V-28/A,B,C and D
394318 | CR | 20190527 |  | 4 | COND-LCV-1B packing leak | N | N |  | N | YES | <D> **** Detailed Description **** COND-LCV-1B packing leak found while inspecting valve. WO# 02109599-02 <I> **** Actions Taken **** write this CR. | 02-00-COND-LCV-1B
394319 | CR | 20190527 |  | 3 | Extension Cords Plugged Together |  |  |  | N | NO | <D> **** Detailed Description **** Two sets of extension cords were found daisy chained together at T471 C.8/14.5 under the main generator. This condition is not in accordance with ISPM-6, section 3.7. 1(d). One set is daisy chained using a blue cord plugged into a yellow cord that is fed from TG-PDU-471-8. This set of cords has a work-in-progress sign with an EN electrical supervisorâ€™s name on it. A second set is daisy chained using an orange cord plugged into an orange cord that is then plugged into a yellow cord that is fed from TG-PDU -471-8. This second set of cords appears to feed lighting and other equipment on the scaffold under the main generator. <I> **** Actions Taken **** Notified the OCC Maintenance Manager. Notified the EN Electrical Component Manager. Actions are underway by the latter to correct the issue. See EDMS for photos. <N> Condition has been restored and coaching provided to shop.
394320 | CR | 20190527 | CAQ | D | SLC-TK-1 Hi/Low Level alarm | Y | N |  | N | YES | <D> **** Detailed Description **** Received â€œSLC TANK HIGH/LOWâ€ alarm in the Main Control Room. SLC-TK-1 indicates 5000 gallons, which is unchanged. Request Maintenance correct the issue. | 02-00-SLC-TK-1
394321 | CR | 20190527 |  | 4 | 3 Pieces of M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** 3 Pieces of M&TE were NOT used during Calibration cycle and have been Suspended until R25. Calcode #0064672 Ashcroft Sensor- model HQS-2 60psig. DEF #7043A written. Calcode #0065572 Ashcroft Sensor- model HQS-2 60psig. DEF #7044A written. Calcode #0068166 Heise Sensor- model HQS-2 60spig. DEF #7045A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
394322 | CR | 20190527 |  | 4 | Temp loss of power to IN-5 | N | N |  | N | YES | <D> **** Detailed Description **** IN-5 was powered from MC-2D and operations trasfered SL-21 from SL-11 to SM-2, this caused a temp loss of power to IN-5. <I> **** Actions Taken **** Write CR | 02-00-E-IN-5
394323 | CR | 20190527 |  | 3 | Steam droplet impingement found on condenser tube | N | N |  | N | YES | <D> **** Detailed Description **** During light check on the shell side of the condenser, steam droplet impingement erosion (SDIE) indication was found on one tube (see EDMS). This tube is in section 3 of the lower module of the A inlet waterbox (Row 41, Column 1). Itâ€™s not known if this tube is the leaking tube, further investigation is on-going to verify. The tube will be permanently plugged this outage. It was decided not to ECT both B and C waterboxes this outage due to scope change to 100% on the A waterbox. However, as an extent of condition due to this finding, itâ€™s highly recommended that the peripheral tubes on these two boxes (as a minimum) to be eddy current tested and to plug any similar indications. This indication is a first SDIE indication found on the new condenser. Recommend action to condenser system engineer for trending and monitoring. <I> **** Actions Taken **** DIscussed with System engineer and initiated this CR | 02-00-COND-HX-9
394324 | CR | 20190527 |  | 4 | Inverter 5 alarms of low AC output voltage. | N | N |  | N | YES | <C> Duplicate of CR 394322 <D> **** Detailed Description **** Wither Inverter 5 on the Manual Bypass after a swap of power of 31 & 21 the following alarms were present. Manual Bypass, Bypass, and low AC output voltage. The lights: UPS trouble and Low AC output voltage were illuminated. <I> **** Actions Taken **** Alarms were checked, Mimic bus showed proper AC output voltage, Alarms reset leaving only Bypass alarms & UPS trouble in. Informed MCR & initiated AR. The alarms and inverter response was expected for this condition. System is being restored from SL-21/11 cross connect and SM-8 outage. No additional actions required. | 02-00-E-IN-5
394325 | CR | 20190527 |  | 3 | SM-2 incoming and running voltage off when attempting backfe | N | N |  | N | YES | <C> CR re-opened and assigned as 3/SEEIC at the request of Engineering. <D> **** Detailed Description **** When attempting to transfer SM-2 to the normal transformer from the startup transformer for backfeed. When the N1/2 sync selector switch was taken to manual the incoming bus voltage indicated 1600V when the running bus correctly indicated 4160V. See EDMS for pictures. <I> **** Actions Taken **** Notified CRS and SM In addition the main generator voltage jumped from 6kv to 9kv voltage when the sync selector switch was taken to the man position | 02-00-E-SM-2
394326 | CR | 20190527 |  | 4 | PAAP Vehicle Kiosk | N | N |  | N | NO | <D> **** Detailed Description **** Tried to perform vehicle check-in evolution and the kiosk locked up â€œcanâ€™t be displayedâ€ <I> **** Actions Taken **** Left messages on both numbers listed. My Supervisor has the keys
394327 | CR | 20190527 |  | 3 | Procedure 10.19.7 contains reference errors and requires rev | N | N |  | N | NO | <D> **** Detailed Description **** Maintenance procedure 10.19.7 contains a reference table 5.2.11a on page 7 which contains a list of drawings which are not available from Document Control. These drawing are no longer controlled and are controlled by the component engineer. Need procedure revision to correct ttttttttttttttttttttttttttttttttr <I> **** Actions Taken **** Obtained drawings from the component Engineer to allow tracking the relavent work and used controlled drawings from the equipment documents list in access suites to perform work. Notified project manager <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
394328 | CR | 20190527 |  | 4 | WO 02 13 6055 - 05 not completed during R24 | N | N |  | N | NO | <D> **** Detailed Description **** WO 02136055 Task 05 was intended to be worked to replace the Transformer Yard lights with new Crouse-Hinds LED style lamps. The effort to work these LED replacement packages was to be done as filler work during windows of opportunity with Transformer Yard tasks during R24. Only 2 of the 4 lamps to be installed per this work package were completed prior to going to backfeed. <I> **** Actions Taken **** Notified supervision and generated this CR. Task 62 to WO 02136055 was generated to install the two remaining lamps on the West 500KV Tower during a future outage.
394329 | CR | 20190527 |  | 3 | Peer Verifier step needed for terminations | N | N |  | N | YES | <D> **** Detailed Description **** While performing task preview for MS-RMS-RV/1A it was discovered that peer verification was required for terminations in E-CP-H13/P601 per QAP-ASU-07. Four switches have been replaced during R24 without the terminations being peer verified. <I> **** Actions Taken **** Notified supervision, OCC, and planning. Packages revised to add peer verification steps. Tasks being planned to peer verify terminations on the installed switches. <N> **** Equipment Description **** E-CP-H13/P601 . This issue was discussed with QC and Engineering and the determination was no Peer Verification was required. MS-RMS-RV/1A does not fall under the two categoryâ€™s that require the peer verification for quality 2+ EPNâ€™s. It only falls under the Seismic 1M category and PV is not required per QAP-ASU-07 .
394331 | CR | 20190527 |  | 4 | TDAS crash during SL 21 power transfer | N | N |  | N | YES | <D> **** Detailed Description **** TDAS crash during SL 21 power transfer. Need to reboot TDAS. <I> **** Actions Taken **** SM/CRS informed. | 02-00-TDAS-COMP-8715
394332 | CR | 20190527 |  | 4 | NSSE-EQ-8 mast camera failed | N | N |  | N | YES | <D> **** Detailed Description **** The mast camera stopped working during final fuel shuffle on move #595 <I> **** Actions Taken **** Notified OCC. PARR rep is troubleshooting and will recommend a repair as soon as it is known. Mast camera has been repaired. | 02-00-NSSE-EQ-8
394334 | CR | 20190527 |  | 4 | Extension Cords Plugged Together (Second Observation) | N | N |  | N | NO | <D> **** Detailed Description **** A set of three extension cords were found daisy chained together at T471 from D/â€™15 to E/13 and along the base of MC-2R and MC-3B. This is currently providing the power to the T471 West HP access point to the heater bay from TG -PDU-471-8. The extension cord setup is contrary to ISPM -6, section 3.7. 1(d) <I> **** Actions Taken **** Notified HP at the T471 desk and offered information on how to correct the situation. Notified the OCC Radiation Protection Manager, the OCC Shift Outage Manager, the Operations Support General Manager and EN Fire Protection. Condition has been corrected - no further action required.
394335 | CR | 20190527 |  | 3 | RFW-P-1A axial thrust (float) measured at 0.030â€ | N | N |  | N | YES | <D> **** Detailed Description **** On 5-24-19 mechanical maintenance notified engineering that they discovered the axial thrust (float) of RFW-P-1A to be 0.030â€. Upon review, the OMM manual calls for a nominal axial thrust (float) of 0.018â€ to 0.025â€. A total float of 0.030â€ should indicate ~ 15 mils on the dual thrust monitor, which is the bottom limit of the â€œalertâ€ range. . However, the on-line thrust monitoring equipment for RFW -P-1A (RFW-VBI-XE/P1A) has been trending at ~ +12.5 mils (0.0125â€). . There is currently also an ongoing investigation of the Bravo feedwater pump (RFW-P-1B) axial thrust issue which has a total axial float of 0.031â€, Ref. CR 386522/WO 02138813. The Bravo pump axial thrust had been trending up and has reached the â€œalertâ€ range as documented (continued) in AR CR 386522 and associated ODMI. In addition, the tow probes that measure the thrust on the Bravo pump differ by approximately 0.004â€ thrust. <I> **** Actions Taken **** Notified EOC <N> **** Equipment Description **** T441 East See below for probe A/B indications. 3/19/19 3/28/19 4/24/19 Probe A +12.5 +12.5 +12.4 Probe B +13 +12.75 +12.7 | 02-00-RFW-P-1A
394336 | CR | 20190527 | CAQ | D | (QA) Rejected Inspection RHR-V-4C, Cleanliness | Y | N |  | Y | YES | <D> **** Detailed Description **** (QA) Quality Control identified a piece of wire at the bottom of RHR-V-4C valve body while performing cleanliness inspection step 4.14 of task instructions per WOT 02107551-05, Valve Reassembly, resulting in a rejected inspection. The wire was approximately 1.5 inches in length and was located at the bottom of the valve body four to five inches downstream of the seat. The QC inspector prompted craft, provided coaching and craft removed the piece of wire. After the wire was removed, cleanliness inspection was re-performed by QC and found satisfactory. . <I> **** Actions Taken **** Notified Quality Services Supervisor and Valve Team Supervisor. | 02-00-RHR-V-4C
394338 | CR | 20190527 | CAQ | D | RHR-RV-30 failed as found set point testing | Y | N |  | N | YES | <D> **** Detailed Description **** RHR-RV-30 failed its as found set point test and leak test. rebuild of valve required. <I> **** Actions Taken **** Initiated this CR per TSP-RV/IST-R701 <N> **** Equipment Description **** R -422-R006- -L8/8.5 - | 02-00-RHR-RV-30
394339 | CR | 20190527 |  | 3 | Unanticipated ED dose rate alarm during Wetwell diving act. | N | N |  | N | NO | <D> **** Detailed Description **** Diver received an unanticipated electronic dosimeter (ED) dose rate alarm while performing diving activities in the Wetwell. The diver was using a mop during the activities and the mop head came in close proximity to the ED on the divers right leg. This caused a momentary dose rate alarm of 840 mrem/hr versus an alarm setpoint of 800 mrem. <I> **** Actions Taken **** Informed the diver of the dose rate alarm. Followed guidance as listed in the High Risk Plan and informed Mike Davis (RPM) and JC Smith (ROS) of the dose rate alarm. The diver was removed from the water and a discrete radioactive particle (DRP) survey was performed of the diver. No DRPs were detected and RPM gave permission for diving activities to recommence. <N> Form 26441 and Histrogram uploaded into EDMS. No further action required.
394340 | CR | 20190527 |  | 3 | R24 FAC LOCATION 626-10 (MD-626-10-N (C)) LOW WALL THICKNESS | N | N |  | N | NO | <D> **** Detailed Description **** This component is a 4â€ pipe that dumps directly to the main condenser and is believed to have a sparging header inside the condenser. This component is showing high wear and must be replaced in R25. This component was replaced in R22 due to similar damage and evidence is available that indicates it was repaired prior to R22. Based on the system and the fact that it is located near the condenser, the corrosion mechanism is very likely to be moisture impingement mixed with flashing flow cavitation, not FAC. Since these mechanisms are mechanical in nature (not FAC), carbon steel and chrome molly steel are not good choices for replacement. Stainless steel is strongly recommended. The upstream piping to these components is already stainless steel. A short section of the upstream stainless-steel piping is also showing signs of wear and should also be replaced. <I> **** Actions Taken **** Recommended action: 1.) Design Engineering initiate a plant modification to replace the carbon steel pup piece, the carbon steel nozzle, a short section of the stainless steel pipe, and the carbon steel sparging header inside the condenser with stainless steel. 2.) The plant modification should also include design changes to reduce the erosive nature of the fluid entrance into the condenser. One such changed could include a larger diameter entrance nozzle coupled with a higher schedule piping. 3.) Initiate work orders to implement the replacement and redesign.
394341 | CR | 20190527 |  | 4 | Failed EBU's | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WO# 02111928-01, EBU's SWS1/2 & SWS1/3 did not light up when the AC switch was put into the off position. <I> **** Actions Taken **** Fire impairment was intiiated and lanterns stage per step 7.21. Replaced bad 12 volt batteries and re-performed testing procedure. Non-essential lighting. <N> **** Equipment Description **** EBUSWS102 emergency lighting
394342 | CR | 20190527 | CAQ | D | RFW-MO-65B As Left Testing shows decrease in seating thrust | Y | N |  | N | YES | <D> **** Detailed Description **** RFW-MO-065B was diagnostically tested per WOT 02111389-01 on 05/25/2019. As Left test was performed following cleaning and lube of the stem. The measured seating force decreased by 46,883 lbs (~23.72%). The maintenance performed between the AF and AL tests do not explain the significant decrease in seating loads. It is likely that the strain gage bond to the stem is degrading and needs to be replaced. Numeric values for as found vs as left seating forces are shown in EDMS. <I> **** Actions Taken **** Discussed with EOC and valve contractor. | 02-00-RFW-MO-65B
394344 | CR | 20190527 |  | 4 | RFW-FCV-10B needs gasket surface repair | N | N |  | N | YES | <D> **** Detailed Description **** Internal body inspection showed heavy steam cutting in the upper portion of the body where the pressure seal type gasket makes contact. Engineering recommends utilizing continental machine services to repair prior to rebuild. Damaged area will have to be cut away, weld filled and machined back to original dimensions <I> **** Actions Taken **** wrote cr. gathering info for path forward <N> **** Equipment Description **** T471 | 02-00-RFW-FCV-10B
394345 | CR | 20190527 | CAQ | C | Replacement Probe Mux card for index rod 22-39 not PMT'd | Y | N |  | N | YES | <D> **** Detailed Description **** PRobe mux card in Miodule 2 FIle 2, slot 20 was replaced by WR 29148996. when the bad card was found a PMT is required to Verify proper function of new card. This PMT was not added to the WR once the bad card was found. PMT still needs to be performed . This pmt affects the position indication for four rods (22-39, 18-39, 22-35 and 18-35) during the PMT and will prevent fuel movement during the PMT. this PMT needs to be performed prior to rod movement. . this should be added to a WO to perform PMT. Also WR 29148996. found an additional probe card that needs to be replaced for rod 38-23. This will also need to be PMT'd Add tasks to WO 02144746 <I> **** Actions Taken **** Wrote CR <N> Re-opened as assignment 01 says the work will be completed under a WO that was not cross referrenced, this is not in compliance with SWP-CAP-01. The WO has been added and completion required box has been checked. However, as this is reactor startup constraint the CR should remain open until complete or determined to not be a constraint. | 02-00-CRD-RPIS-1
394346 | CR | 20190527 |  | 3 | E-PT-G2/C was not fully racked in | N | N |  | N | YES | <D> **** Detailed Description **** During the investigation for AR-CR 394325 it was discovered that the C-PHASE PT was not fully racked in with the secondary contacts made up. All 3 phases of PTs were racked out and racked in under WR 29149051 with all secondary contacts verified to be made up. Upon further investigation this condition or prior has made it difficult to close the door because it has <N> CR re-opened and assigned to AR-OPSST at the request of Operations. | 02-00-E-PT-G2/C
394347 | CR | 20190527 | CAQ | C | RFW-MO-65A GREASE DEGRADED | Y | N |  | N | YES | <D> **** Detailed Description **** A Full PM per PPM 10.25.4 was performed on RFW-MO-65A per WOT 02124705-01 on 5/26/19. The gearcase grease was evaluated at NLGI grade 3. PPM 10.25.4 directs that this grease is acceptable, but will need to be replaced before end of next outage. A grade of GT 3 is unacceptable and the valve may be inoperable. Per procedure, the grease was independently evaluated by 2 qualified evaluators and determined to be acceptable at grade 3. <I> **** Actions Taken **** Discussed condition of grease with qualified grease evaluators to confirm acceptable condition. Notfied EOC. | 02-00-RFW-MO-65A
394348 | CR | 20190527 | CAQ | D | RHR-V-16B, SURFACE DEFECTS FOUND ON VALVE INTERNALS | Y | N |  | N | YES | <D> **** Detailed Description **** As part of WO 02107553, RHR-V-16B WELD VALVE BODY GUIDES EC 16817, the valve was disassembled and the internals inspected on 5/26/19. Surface indications were noted on the valve seat and the valve disc that could contribute to increased leakage past the valve. Two indications lineup so that they mate with one another when the valve disc is seated. It should be noted that the AF LLRT results were well below their admin limits with relatively little leakage past the boundary valves (RHR-V-16B and 17B). Pictures included in EDMS. <I> **** Actions Taken **** Discussed with valve contractor. Notified EOC. <N> Clarification: The indications / surface defects are on each side of the disc seating surface and not on the valve seats. The indications are at the same point on each side of the disc (0300 / 0900). â€“ K. Trappett | 02-00-RHR-V-16B
394349 | CR | 20190527 | CAQ | C | Leakby past SW-V-108B and SW-V-110B | Y | Y |  | N | YES | <D> **** Detailed Description **** While flushing the lower coils for WMA-CC-53B under WO 02114583-01, water was noted to be coming out of the open upper coil anode ports, and onto the floor of the air handler unit. The air handler unit floor is connected to a nearby floor drain and leak rate was well within the capacity of the drain line, so flooding was not a concern. During flushing, water could be observed leaking past the upper coil isolation return valve, SW-V-108B. As both upper and lower coil isolation valves were tagged closed, leakby past the lower coil return isolation valve, SW-V -110B, must also be present. | 02-00-SW-V-108B,02-00-SW-V-110B
394350 | CR | 20190527 | CAQ | D | RCIC-MO-76 PMT failed to stroke full open | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of the PMT for WO 02110811 (Full PM per PPM 10.25.4, Lube & Inspect) on 5/27/19, the valve failed to stroke full open. When the control switch was taken to open the valve traveled open for approximately 7 seconds, whereas full open would take 11.4 seconds. As soon as the open torque switch bypass switch opened the motor received signal to de-energize. Upon investigation it was discovered that the open torque switch spring had no tension and needs to be replaced. This did not affect the valveâ€™s ability to close, but would have affected the valveâ€™s ability to go more than ~60% of full open. The valve performs no safety function in the open direction. Hence no impact to past valve operability. <I> **** Actions Taken **** Discussed with valve vendor. Notified EOC. | 02-00-RCIC-MO-76
394353 | CR | 20190527 |  | 3 | R24LL: TSP-RFW/X17A-R802 needs enhancement. |  |  |  | N | NO | <D> **** Detailed Description **** TSP-RFW/X17A-R802 needs enhancement. The following recommended changes are based upon step numbers in Major Rev 006, Minor Rev 002: Steps 9.4.56 and 9.4.57 should be removed from attachment 9.4 and made into a new attachment for draining the RWCU piping. Step 9.4.58 should be moved to step 7.3.13, being sure to not repeat valves. Steps 9.5.22, 9.5.23, and 9.5.24 should be deleted, because the previous 2 recommended changes will cover actions required in these steps. Step 9.5.25 should be moved to become new step 7.3.15. Step 7.2.36.a should refer to the new attachment for draining the RWCU piping, instead of Attachment 9.4. <I> **** Actions Taken **** Informed SM, wrote this CR.
394357 | CR | 20190527 |  | 3 | First Responder medical cabinet needs re-stocked |  |  |  | N | NO | <D> **** Detailed Description **** The first responder medical cabinet in the Equipment Operator center in the Yakima Bldg. needs to be inventoried / restocked following use during a medical response on 5/27/19. Additionally, one oxygen bottle was taken by the ambulance crew. <I> **** Actions Taken **** Notified CRS and Shift Manager. <N> Following a medical response on 5/27/19, on the following day the oxygen tank from the First Responder Medical cabinet in the Equipment Operator center was replaced. The AED unit was checked was verified to be rescue ready and unit pads for AED were replaced. On 5/30/19 a complete inventory of the First Responder Medical cabinet in the Equipment Operator center was performed.
394358 | CR | 20190527 |  | 4 | Personal Medical Condition - Tranport Off-Site |  |  |  | N | NO | <D> **** Detailed Description **** On Monday May 27, 2019 an Energy Northwest employee experienced a personal medical condition at the Yakima Building 441â€™ Security Break area. A 2222 call was placed at 20:05. A medical responder tone out was initiated by the control room per PPM 1.9.14. The patient was evaluated and treated by the medical responders. Hanford Fire Department (HFD) Medic 1923, Ladder 1913, and Medic 93 arrived at 20:18. The patient was further evaluated by HFD and transported to Kadlec Medical Center at 20:39 <I> **** Actions Taken **** The employee is from organization 52622. A supervisor left site to meet the patient at Kadlec Medical Center. OCC updated at 2100 Meeting by Industrial Safety.
394359 | CR | 20190527 | CAQ | C | RRA-FN-14 - Failed to start | Y | N |  | N | YES | <D> **** Detailed Description **** Durin performance of OSP-INST-B703 section 7.3, step 7.3.8, RRA-FN-14 failed to start. Rewiring for WO 02088849 was performed under WO 02117672-01 per Step 4.25. <I> **** Actions Taken **** Inoformed OCC. <N> E-FUSE-FRTP/BBF5 removed and verified good. Reinstalled, then fan started. Recommend REP/REGE for determing if there is a definite activity that could have caused the fuse to be loose. | 02-00-RRA-42-8BB1E
394361 | CR | 20190527 |  | 3 | R24LL: (NRC) SOP-ELEC-500KV-OPS recommendation |  |  |  | N | NO | <D> **** Detailed Description **** Concerning when the 25kv generator voltage did not indicate as expected in the MCR after closure of the 500kv breakers at ASHE substation, the NRC recommended we add checking or listing the voltage in the procedure steps to force verification of actions taken. The backfeed procedure directs the operator to SOP-ELEC-500KV-OPS for 500kv breaker closure.
394362 | CR | 20190528 | CAQ | C | SW-M-P/1B Cable Terminations were cut | Y | N |  | N | YES | <D> **** Detailed Description **** The cable terminations were cut during the removal of tape for WO 02111471. The cut did not affect the insulation of the cable so the termination kit does not need to be replaced. The cables passed the tan delta and withstand test (7 kV). Recommend adding a task to the work order to repair the cut with safety-related heat shrink prior to re-terming the cables in order to prevent further degradation. Pictures are located in DataGlance. <I> **** Actions Taken **** Notified Electrical Maintenance Supervisor and EOC. | 02-00-SW-M-P/1B
394363 | CR | 20190528 | CAQ | D | MS-V-160 Actuator Enclosures As-Found damage. | Y | N |  | N | YES | <D> **** Detailed Description **** The Actuator controller enclosures & covers for the Turbine Bypass Valves was found damaged. The mounting tabs are snapped off, most likely due to vibration durition during operation. See attached photos. <I> **** Actions Taken **** Notified EOC, System Eng, Located OE part and created CAT ID # 39018 (enclosure) & CAT ID # 39019 (cover). Recommend replacing all 4 with new. Fabrication possible if long lead time exist for OE. <N> **** Equipment Description **** MS-V-160
394364 | CR | 20190528 |  | 3 | MS-SPVD-SV/XX's not installed |  |  |  | N | I DONT KNOW | <C> CR changed from CAQ C to nonCAQ 3 as per the MRT. <D> **** Detailed Description **** MS-SPVD's had been installed prior to the electricians installing the soleniod valves for the following work orders 02143798-01(1A), 01175986-01(1B), 02143799-01(3B), 01175979-01(3A) and 01175971-01(5B). In previous history the work orders had a prerequisite that MS-SPVD-XX has been removed prior to starting work, this prerequisite was not included in the current work order. <I> **** Actions Taken **** Craft stop work and notified supervision, OCC and EOC. Pictures were taken and forwarded to supervision, OCC and EOC. CR was initiated. <N> **** Equipment Description **** C 547' AZ/RAD 45/21 DryWell
394365 | CR | 20190528 |  | 4 | XD-06 Failed Operability Test |  |  |  | N | YES | <D> **** Detailed Description **** XD-06 requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security supervision notified. Initiate CR/WR. Contacted I&C supervisor for support. XD taken out of service. | 02-00-SEC-XD-6
394366 | CR | 20190528 |  | 4 | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065646 Industrial Scientif Gas Monitor- model itx.Used for personal safety only. Rejected no longer supported for parts. DEF #7046A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
394373 | CR | 20190528 |  | 3 | 25KV Voltage indications remain degraded (AR 394346) | N | Y |  | N | YES | <D> **** Detailed Description **** PCB-4885 and 4888 were closed per SOP-ELEC-500KV-OPS in support of 500KV backfeed. The BPA Dittmer Operator called the MCR a few minutes after the breakers were closed and asked whether we had any abnormal indications. It was relayed to him that we still had an indicated imbalance on the 3 phases of the 25KV system (all 3 phases indicated significantly different values). See EDMS file for the voltage on the 3 phases. The Dittmer dispatcher stated that there had been a significant drop in 500KV system voltage (~ 20KV) after breaker closure and that he was re -opening the breakers due to a suspected issue with the 500 KV system. (A momentary voltage drop is expected when energizing the 3 Main & 2 Normal transformers). Reference previous CR's <I> **** Actions Taken **** Notified the CRS and Shift Manager. Submitted CR to document the condition. | 02-00-E-PT-G2/A
394374 | CR | 20190528 | CAQ | C | ms-v-28c | Y | Y |  | N | NO | <D> **** Detailed Description **** wo# 02079277 09. cotter pin called out in the work order is not like for like to the one that was as found. The cotter pin was replaced with the Cat id # 25300093 called out in the work order. <I> **** Actions Taken **** initiated CR for action tracking. notified supervision.
394376 | CR | 20190528 |  | 4 | HV-V-30H requires replacement in future outage | N | N |  | N | YES | <D> **** Detailed Description **** HV-V-30H was disassembled due to steam leak. The wedge and seats showed signs of degradation. The degradation requires replacement of the valve. See attached pictures. <I> **** Actions Taken **** The leak was repaired and the valve will close as required, Expect some leakage through the seats/wedge interface. | 02-00-HV-V-30H
394377 | CR | 20190528 |  | 4 | MT-ELEV-2 not functioning | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-2 not functioning correctly, elevator will go up and down, however doors will not open. Temporary power provided to MT-ELEV-2 for SL-31 outage. Normal power restored to MT-ELEV-2. MT-ELEV-2 still does not function correctly after removing temporary power. Investigate and repair MT-ELEV-2. <I> **** Actions Taken **** Informed supervision and OCC | 02-00-MT-ELEV-2
394378 | CR | 20190528 |  | 3 | Investigate Outlier Results for TEMP-IR-114. | N | N |  | N | NO | <D> **** Detailed Description **** Investigate Outlier Results for TEMP-IR-114. Please assign to AR-CALSERV
394379 | CR | 20190528 |  | 4 | RMC Laborer â€“ Back Discomfort | N | N |  | N | NO | <D> **** Detailed Description **** A Laborer reported back discomfort to supervision after 1800 on 5/27/19. Occupational Health and RP OCC representative were informed. The Laborer was directed to report to Occ Health after 0630 on 5/28/19. <I> **** Actions Taken **** Supervision escorted the individual to Occ Health. Occ Health evaluated the individual and was released to continue working without restriction.
394381 | CR | 20190528 |  | 4 | WEA-FN-2A does not start | N | N |  | N | YES | <D> **** Detailed Description **** WEA-FN-2A provides ventilation for a fume hood in the Chemistry lab on RW 487'. Green off light is illuminated on WEA-42-7E2B, but the fan does not turn on at the local switch inside the Chemistry lab. <I> **** Actions Taken **** Wrote CR/WR | 02-00-WEA-FN-2A
394382 | CR | 20190528 |  | 4 | Minor First-Aid | N | N |  | N | NO | <D> **** Detailed Description **** Employee while operating a forklift stated that she felt a possible sting on upper jaw in front of left ear. Employee notified supervision and safety. Ice was applied and employee has returned back to work. <I> **** Actions Taken **** WPS Safety followed ISPM-1 procedure requirements while notifying Occupational Health, ENW Industrial Safety and Site Support Contractor Manager regarding the details of this Minor First-Aid. No further action is required. <N> Williams Plant Services.
394383 | CR | 20190528 | CAQ | C | R24 LL: RFW-MO-65B Diagnostic Testing | N | N |  | N | YES | <D> **** Detailed Description **** During work order 02111389 RFW-MO-65B diagnostic testing it was identified that water must be present at the seats to perform the testing. A false reading is received when the disc is not lubricated due to drag. Recommend revision to work order for future maintenance. <I> **** Actions Taken **** Discussed with MOV system engineer and Valve PM. <N> After discussions with MOV Engineer this also applies to RFW-MO/V-65A diagnostic testing. | 02-00-RFW-MO-65B,02-00-RFW-V-65B
394384 | CR | 20190528 |  | 4 | TOA-P-2B1 excessive pump seal leakage | N | N |  | N | YES | <D> **** Detailed Description **** TOA-P-2B1 excessive pump seal leakage Difficult to quantify leakage but it is noticably flowing from the pump seal to the bedplate <I> **** Actions Taken **** Informed MCR Recommend shifting pumps | 02-00-TOA-P-2B1
394386 | CR | 20190528 |  | 3 | COND-M-P/2A I/C resources not identified and incomplete PCSC |  |  |  | N | YES | <D> **** Detailed Description **** 0207754104 does not have I/C resources identified. The steps to remove the two thermocouples do not comply with challenge question #2 on the PCSC check list. More documentation is required and steps added to the task. <I> **** Actions Taken **** Notified Supervisor Filled out PCSC Readiness Check card and dropped it in box | 02-00-COND-M-P/2A
394388 | CR | 20190528 | CAQ | C | Missed QC Hold Point / Rework on Snubber RWCU-950N (W) |  |  |  | N | YES | <D> **** Detailed Description **** During replacement of snubber RWCU-950N (W) in the 548' RHR-HX-B room on 5/27 as part of CR 394314, the QC hold point for torque verification was missed. The snubber will need to be loosened and re-torqued with QC verification. <I> **** Actions Taken **** Contacted QC about issue and to discuss path forward. Notified OCC Manager, OCC Engineering and OCC HP <N> **** Equipment Description **** Snubber RWCU-950N (W) is located in 548' RHR-HX-B room.
394389 | CR | 20190528 |  | 3 | torque wrench 0067432 cal date 1-11-2020 10-50 in.Lbs | N | N |  | N | YES | <D> **** Detailed Description **** Torque wrench was set to 36 inch pounds to tighten a Â¾ inch nut on the end of DEH-SV-160B. In the process of torqueing the threaded end of the hollow solenoid shaft that runs through the coil sheared off. 1 either the torque wrench is failing. Or 2 the product had a weak spot or was defective <I> **** Actions Taken **** Stopped work, notified supervisor, returned tool to dirty tool crib attendant and explained torque wrench 0067432 needs to be evaluated and that we think it could be out of cal. New sv is ready to be bench tested and installed <N> **** Equipment Description **** TB 481 B/6.4 | 02-00-DEH-SV-160B
394390 | CR | 20190528 |  | 4 | Contract Employee Suffered an Insect Sting/bite | N | N |  | N | NO | <D> **** Detailed Description **** At approximately 1025 this morning outside the door to Trailer #158, a Framatome employee was bitten/stung on the back of his upper right arm by either a bee or a wasp. His employer has been notified, and the event has been reported to Framatomeâ€™s Industrial Safety Program. Energy Northwestâ€™s Occupational Health organization has also been notified. . The Framatome employee has since returned to work. . The Energy Northwestâ€™s Industrial Safety Program Manager states that this wasp/bee sting does not constitute a â€œFirst Aidâ€ event. <I> **** Actions Taken **** 1) The contract employee reported the event to ENW's Occupational Health organization. 2) The contract employee reported the event to his parent company (Framatome.)
394391 | CR | 20190528 |  | 4 | Fire Brigade cabinet door left open |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During safety blitz observation the enclosed area containing the Fire Briigade equiment on TG 441 the flam cabinet was observed to be left with the door open. Posted sign indicated door must be closed when not in use. <I> **** Actions Taken **** Attemped to close door, but it was skewed and unable to close. Reviewed with Safety, initated CR and WR
394392 | CR | 20190528 | CAQ | D | DEA-FN-23 log dP Alarm on DGHV-2 |  |  |  | N | YES | <D> **** Detailed Description **** "EXH AIR FAN OIL RM DEA-FN-23 DIF LOW DEA-DPS-23" alarm was in on DGHV-2 while taking OPS-2 rounds. Fan was found OFF. Followed ARP- depressed the reset button on DEA-42-8AA6F and placed DEA-RMS-FN/23 to ON. DEA-FN-23 started and the alarm was cleared. May be related to SM-8 restoration. AR for trending. <I> **** Actions Taken **** Notified MCR, hit the reset button on disconnect and started fan. | 02-00-DEA-FN-23
394393 | CR | 20190528 |  | 4 | Missing wheel chocks on carts near 441 dress out area |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During saftey blitz observation wheel chocks were noted as missing from the large carts between the TG 441 dress out area and the Painters Sat. Accumulation Area. Six carts are located in this area. Four of the carts had appropriate chocks. One cart had no chocks. One cart had one chock attached and second chock had fallen off . <I> **** Actions Taken **** Reveiwed with Safety, iniated CR and WR
394394 | CR | 20190528 |  | 4 | Staged material for Closed WO and chemicals not stored |  |  |  | N | NO | <D> **** Detailed Description **** During saftey blitz observation two carts of general materials were observed with WIP signs (WO 020509860) from 12/31/2018 on the RW 507 Basketball Court area. The carts also contained 4-5 chemcial products/aresol cans which need to be returned to storage or properly disposed. <I> **** Actions Taken **** Reviewed WO and noted it was closed. Review with Safety, initated CR and WR
394395 | CR | 20190528 |  | 4 | MT&E Found Out of Tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0068431, Tektronix Model P6022 Probe found out of Tolerance and rejected it. Not used during Calibration cycle, No plant impact and No Action Required, DEF# 7047A
394397 | CR | 20190528 | CAQ | C | HN connectors on CMS-RE-27E and 27F not snug | Y | Y |  | N | YES | <D> **** Detailed Description **** When installing the new HN connectors on the Victoreen teflon cables for CMS-RE-27E, it was identified that the CVI drawing detail for the connector did not result in a tight connection (cable to connector). This results in poor stress relief for the connection point. Additional detail is required to provide a secure connector installation. Recommend assignment to plant programs to provide shim detail. <I> **** Actions Taken **** Discussed issue with I&C technician and EOC. | 02-00-CMS-RE-27E,02-00-CMS-RE-27F
394399 | CR | 20190528 |  | 4 | As found out of tolerance for COND-PS-4A/3 | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WO# 02077541-48, COND-M-P/2A, CALIBRATE COND-PS-4A/1, 2 & 3. Found COND-PS-4A3 out of tolerance low. <I> **** Actions Taken **** Adjusted switch. As left in tolerance <N> **** Equipment Description **** T441 F/16.0 | 02-00-COND-PS-4A/3
394400 | CR | 20190528 |  | 3 | R24LL: SOPs do not address OPDS equipment. |  |  |  | N | NO | <D> **** Detailed Description **** During a recent walkdown of the 115kV Open Phase Relay House, Building 44, there was a fire protection panel in trouble alarm. There was no evidence of fire and no way to identify the cause of the trouble alarm. Upon further consideration, it was recalled that there was a recent outage on E-SM-8. Upon examination, it was noted that the manual transfer switch for the feed to the building, OPDS -MTS-TR/B/8AA/7AA is in the MC8AA position. A review of procedure SOP-ELEC-SM8-MAINTshows there is no mention of any OPDS equipment. Similarly there is no mention in SOP -ELEC-SM2-MAINT, SOP-ELEC-SM3-MAINT or SOP-ELEC-SM7-MAINT. The manual transfer switch on the 230kV OPDS building is OPDS-MTS-TR/S/2D/3C. Please include direction for transfer of power away from the source being isolated. <I> **** Actions Taken **** Submitted this CR to document this issue.
394401 | CR | 20190528 |  | 4 | Hanger TSW-1100-13 on Return Line from Cooling Coil RRA-CC-9 | N | N |  | N | NO | <D> Piping installed in existing Hanger TSW-1100-13 dictates welding lugs to the pipe on both sides of the forementioned Hanger, the 90 degree elbow is touching the angle iron not allowing enough room to install but one lug <I> CR generated, engineering contacted and pictures sent . Engineering evaluated the single lug at TSW-1100-13 acceptable (the second lug was not required) because the installed configuration still provides 3-WAY restraint for the associated TSW supply piping to RRA-CC-8/9 as designed. See the e-mail attached to the EDMS of this AR CR 394401. The affected isometric drawing update will be captured as part of existing DOC AS 264973-19 for RIE 264973-08. No further action associated with this AR CR 394401 is needed. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review. | 02-00-RRA-CC-8,02-00-RRA-CC-9,02-00-TSW-PIPE-MISC
394402 | CR | 20190528 |  | 4 | Not enough O-ring seat surface TSW-HX-8 reversing end elbow | N | N |  | N | YES | <D> **** Detailed Description **** While recoating the reversing end elbow of TSW-HX-8 some of the o-ring seat surface was removed while sand blasting. Itâ€™s the second time this happens (referencing CR 394261). This elbow will be replaced with a new one. Recommend action to maintenance (coating team) to better protect sealing surfaces while sand blasting. <I> **** Actions Taken **** Informed EOC and initiated this CR <N> **** Equipment Description **** t441 | 02-00-TSW-HX-1A
394403 | CR | 20190528 |  | 3 | RMC Laborer â€“ Work Related Injury |  |  |  | N | NO | <D> **** Detailed Description **** Continuation of CR 00394379 where an individual reported back discomfort. During a follow-up discussion, Occ Health indicates the back discomfort is due to work related activities. <I> **** Actions Taken **** Informed RP management of the elevation of injury status. Occ Health indicated that backshift supervision will need to query the individualâ€™s status and have the individual report to Occ Health the following morning. <N> Injury classified as first aid. Individual had a follow-up appointment with Occupational Health and has no restrictions. No further action required.
394405 | CR | 20190528 |  | 3 | R24 LL â€“ Snubber group Contractors N45.2.6 |  |  |  | N | NO | <D> **** Detailed Description **** Several work packages for Snubbers require QC verification of torque. The snubber team consisting of contractors from Basic-PSA are ANSI N45.2.6/ASME NQA-1 certified personnel. Energy Northwest should recognize this qualification in the contract with Basis-PSA. This would remove the requirement for Energy Northwest QC inspectors and therefore save time and dose during outages.
394406 | CR | 20190528 |  | 4 | Bus 21/2 trip annunciator with no tripped breaker. | N | N |  | N | YES | <D> **** Detailed Description **** Bus 21/2 trip annunciator actuated and immediately cleared in the MCR but investigation found that the breaker did not trip and no indications that any of the events that cause the breaker to trip of the breaker were in. Electricians were working in SL-21 bus at the time. <I> **** Actions Taken **** Notified CRS | 02-00-E-RLY-74/21/2
394407 | CR | 20190528 |  | 3 | FM - BROKEN TIG TORCH DROPPED PIECE IN LP-C | N | N |  | N | NO | <D> **** Detailed Description **** During Welding Operations on the lower section of the Hood Spray Piping, inside the lower half of LP-C, a piece of the Tig Torch broke and fell within the FME Area. The craftsman was coming out of the area for break and was bringing out his torch and hoses. He set them on the edge of the area while he exited out of the area. He bumped the hoses and the end (opposite the torch) was knocked into the open area and it drug the remaining hoses and torch into the hole. The Back Cap (see EDMS for write-up with picture) broke, and a small (~1 Â½â€) piece of plastic fell into the â€œCâ€ condenser bay. A search was made of the area and the area in the condenser at 471, and the broken piece was not located. <I> **** Actions Taken **** Worker Notified his Supervisor, the Turbine Coordinator and the FME Monitor.
394408 | CR | 20190528 |  | 4 | RB 606 IPM Fault on High Background | N | N |  | N | YES | <D> **** Detailed Description **** IPM will not clear high background. <I> **** Actions Taken **** Surveyed instrument for contamination and searched area for any exterior sources to no avail. <N> **** Equipment Description **** RB 606 HP-EQ-42663
394409 | CR | 20190528 |  | 3 | Outage #24 FAC Location 383-1 configuration management issue | N | N |  | N | NO | <D> **** Detailed Description **** FAC ID HV-18814-E (Location 383-1), located on line 3â€H V(4)-2, should be comprised of either P11 alloy or 304 stainless steel according to B15.1 pipe specifications. However, chemical analysis shows that this component is carbon steel with no chrome content. Adjust component are P11. This represents a configuration management issue. This component is showing minimal wear. The next scheduled inspection is in R57. <I> **** Actions Taken **** Recommended actions: 1) Assign a task to Design Engineering to look for an evaluation that allows for non-chrome alloys. And either 2a) have Design Engineering perform an EC-EVAL to allow a non-chrome alloy to be used until R25 and replace this component with P11 or 304 in R25, or 2b) replace this component in R24 with P11 or 304.
394410 | CR | 20190528 | CAQ | C | Indications of contact and wear on JP-11 Beam Bolt | Y | N |  | N | YES | <D> **** Detailed Description **** During R24 examination of the Jet Pump #11 (JP-11) beam bolt retainer, wear was observed on the beam bolt and jet pump elbow (see INR-CGS-19-10 in EDMS). The wear appears to be the result of the retainer plate vibrating against the beam bolt and jet pump during operation. The indications are minor at this time but the concern is that excessive movement could lead to damage similar to that reported on JP-5 beam in R20 (CR 240434). <I> **** Actions Taken **** The IVVI team remotely manipulated the retainer and verified it was still bolted tightly to the jet pump therefore movement and further damage should be limited. The cause of the contact was likely due to maintenance activities performed in R23 when the new beam was installed. Tooling is not available to remove the retainer at this time so a W/R is initiated to consider removing the retainer in R25. Recommend assignment to AR-CPROG to evaluate the condition as acceptable as-is. | 02-00-MS-JP-11
394411 | CR | 20190528 |  | 4 | FIRST AID REPORT TG 501' |  |  |  | N | NO | <D> **** Detailed Description **** While working in LP-C, bolting the milling machine to the base. The bolt broke and he hit his left arm causing a laceration. The laceration to the left forearm is about 1Â½ inches long. It was not bleeding when he left the floor to go to Occupational Health. The company nurse applied a band aid and permitted the Siemens Employee to return to work. <I> **** Actions Taken **** Employee notifed his supervisor, who then notified the Turbine Deck Safety Monitor and the Turbine Deck Coordinators. Safety accompanied the individual to Occupational Health for treatment.
394412 | CR | 20190528 | CAQ | C | RFW-V-10A Disc hits valve body prior to designed hinge stop. | Y | N |  | N | YES | <D> **** Detailed Description **** During initial inspection under WO# 02085916-24, valve disc was stroked to verfiy full open position. The O.D. of the Resilient Seat Retainer hits the valve body prior to the designed hinge hard stop. Valve body has indications where the disc has been hitting. <I> **** Actions Taken **** Initiated IR and notified ENS Check Valve Engineer <N> **** Equipment Description **** Drywell 512 | 02-00-RFW-V-10A
394413 | CR | 20190528 | CAQ | D | RWCU-FE-35 - unexpected leakage following inst line cut | Y | N |  | N | YES | <D> **** Detailed Description **** Following instrument line cut on RWCU-FE-35 per WO 02140829, approximately 1 gpm of water was noted to come out of the instrument line. This condition will need to be corrected to perform boroscope inspection of RWCU-FE-35 and subsequent repair of the pipe. <I> **** Actions Taken **** Contacted OCC. Directed LLRT EO to provide maximum torque to isolation valves. | 02-00-RWCU-FE-35
394415 | CR | 20190528 | CAQ | D | R24 Examination of JP-17/18 RS-9 indication showed no change | Y | N |  | N | YES | <D> **** Detailed Description **** The R24 re-examination of jet pump 17/18 riser indication showed no apparent change from previous examinations (see INR-CGS-19-08 posted in EDMS). This CR is for monitoring and trending only and to document the examination results after operation at Thermal Power Optimization (TPO). Given no change in the indication, it is bounded by the evaluation documented under GEH Report 001N6043.4 which covers all operating conditions including TPO and ARTS/MELLLA. Therefore there is no start-up or equipment function concern. <I> **** Actions Taken **** Recommend Trend Only. Reference CR 365708 for R23 examination results. | 02-00-MS-JP-17,02-00-MS-JP-18
394416 | CR | 20190528 | CAQ | C | Missing config mgmt info for SRV setpoint tolerance change |  |  |  | N | NO | <D> **** Detailed Description **** License Amendment Request 240 was approved and implemented in 2017 to change the setpoint tolerances for Safety Relief Valves. In support of the proposed Technical Specification Changes, analysis was commissioned by GE Hitachi Nuclear Energy. The document â€œCGS SRV Safety Valve Setting Tolerance Change Supplement to GE-NE-187-24-0992, Rev 2â€, approved April 5, 2016 concluded that the proposed setpoint changes had no significant safety impact, and served as a primary basis for requesting the changes. While this document appears to have gone through a rigorous review by Energy Northwest, it does not appear to have been captured as a configuration management design record as required by SWP-CM-02 Step 3.4.2. As such, it is difficult to retrieve this record. Recommend CAQ C to Engineering/Projects to ensure that this GE report be documented and processed in accordance with SWP-CM-02 and applicable Design Engineering Instruction guidance. Suggest also extent of condition review (focused on design documents processed independently of EC 15492, which was commissioned after submittal of the LAR to support the project effort) for other design documents associated with this particular change that might have been missed. <N> Note: The record location information for the original GE report GE-NE-187-24-0992, Rev 2 has been identified. Doc Number â€“ GE-NE-187-24-0992; Doc Date 7-1-93; Doc Type â€“ QAR ; Sub Type â€“ FUL on QAR Roll 7922, Frames 1582-1639.
394418 | CR | 20190528 |  | 4 | Foreign Material removed from COND-HX-9 â€œBâ€ condenser bay | N | N |  | N | YES | <D> **** Detailed Description **** This CR is for documentation purposes only. During close -out inspection of the steam side Bravo condenser bay (WO 02108276-01), a significant amount of foreign material was noted (pieces of welding rods, tie wraps, weld slag, metal shavings, broken cutting tools, tape, and string). Pictures in EDMS. Despite being covered by tarps, small piles of metal shavings were found on top of and in between tubes. Large items were collected and removed and vacuuming is in progress to remove remaining material. Any new foreign material discoveries will be documented in a separate CR, as the close-out inspection continues. This condition is similar to what was experienced in the Charlie bay in 2017 (CR 00367120) | 02-00-COND-HX-9
394419 | CR | 20190528 | CAQ | D | PPC-COMP-8715 DP20 OVFL | Y | N |  | N | YES | <D> **** Detailed Description **** PPC-COMP-8715 was found to be in error state again. Checked UT8715 and found DP20 was in OVFL. DP20 should be reset. . TDAS is currently primary. This impacts operations if TDAS were to have issues, there would not be a backup system. <I> **** Actions Taken **** Notified SM, wrote CR/WR | 02-00-PPC-COMP-8715
394422 | CR | 20190528 |  | 3 | Equipment information not updated |  |  |  | N | NO | <D> **** Detailed Description **** The scope of WO 02111276 was changed by the electric shop from performing a breaker inspection to swapping the breaker to reduce their R24 man-hours. When the work was performed, the work instruction steps to update the EPN information by removing and installing the breaker UTCs were marked as N/A. In addition, the steps to fill out and attach a repair data sheet for the breaker removed from service were marked as N/A. These steps do need to be performed. Recommend action to electrical maintenance to follow through and perform the required steps.
394423 | CR | 20190528 |  | 4 | SAM handle continues to come lose HP-EQ-42814 | N | N |  | N | YES | <D> **** Detailed Description **** GSB, primary RCA access/exit point sam HP-EQ-42814, has a handle that is constantly coming lose. <I> **** Actions Taken **** Continue to tighten bolt, contacted HP Lead tech, spoke with HP supervision again and created this second CR <N> **** Equipment Description **** GSB - Yakima, primary access/exit from RCA | 02-00-HP-EQ-42814
394426 | CR | 20190528 |  | 4 | Upper TG Roof Membrane unattached from substrate | N | Y |  | N | YES | <D> **** Detailed Description **** During walk-down of upper TG building roof per WOT 02111870-01 it was identified that the Turbine Building roof North-West corner roof membrane has separated from the parapet wall. The roof substrate beneath the membrane is exposed along the north wall from the north-west corner almost all the way to the next roof drain along the north wall (estimated about 36 ft long). The roof membrane appears not to be adhered to the substrate for approximately 8 ft south of the north parapet wall. See photos in EDMS. . Columbia has internal operating experience with roof leaks for this roof and damage to equipment below from water intrusion. Therefore, the recommendation is to have this repaired during R24 outage to ensure a sound roof system devoid of any potential leaks. <I> **** Actions Taken **** Informed the EOC manager and initiated this CR. | 02-00-T-BLDG-MISC
394427 | CR | 20190528 |  | 4 | Lighting deficiencies noted during Safety Blitz. | N | N |  | N | NO | <D> **** Detailed Description **** During the safety blitz that occurred on 05/28/19 @2100 hours, lighting deficiencies were noted on the Turbine building 441 northeast area near the condenser, and also at the northwest area of the condenser. 2 HID type fixtures were out, and one fluorescent fixture in the northeast area, and one additional HID type fixture in the northwest area of the condenser. <I> **** Actions Taken **** Generated CR to document lighting issues, contacted Electrical component manager and Craft supervisor in charge of Turbine building lighting. <N> **** Equipment Description **** .
394428 | CR | 20190528 |  | 3 | Work instruction verification |  |  |  | N | NO | <D> **** Detailed Description **** It was discovered that the latest Rev 0 was not current in the work instructions on work order 02136481-01. Additional steps to have QC verify material were added into the latest revision. These steps were performed in the 04 pre -fabrication, task per DWG D-RRC1BLUBE-497 from EC 17469, where QC verified all of the material and the configuration. No QC hold points were by-passed. The CR has been generated so that QC can re-verify the configuration of the oiler is acceptable per DWG D-RRC1BLUBE-497 from EC 17469 and material verification sheets. <I> **** Actions Taken **** Pre-approved work order 02136481-01 Rev 0, was reconciled with QC and Supervisor. <N> During field Task 01 QC inspection activities, the Quality Control Lead Level III Inspector instructed the supplemental QC to re-verify the piping assembly to re-verify configuration per DWG D-RRC1BLUBE-497. It was verified acceptable by QC. No further action is required based on QC re-verification and previous QC inspections of material acceptance. No QC Hold Points were by-passed. This CR was generated for QC to re-verify the configuration of the oiler per DWG DWG D-RRC1LUBE-497 per EC 17469.
394429 | CR | 20190529 |  | 4 | Trash Found Above Flame-Retaining Ring of Trash Barrel |  |  |  | N | NO | <D> **** Detailed Description **** During Night shift Safety Blitz walkdown of TG 501, two (2) trash barrels for disposable PCs were found with trash above the flame-retaining ring. Only one of the barrels had a label identifying that the trash needed to be maintained below the top of the flame-retaining ring. . Recommend this CR be trended. <I> **** Actions Taken **** HP supervisor on walkdown donned appropriate protective clothing and remedied situation. Coaching could not be provided as no workers were in the affected areas.
394430 | CR | 20190529 |  | 4 | Doors Found Open on C-Van TG 501 |  |  |  | N | NO | <D> **** Detailed Description **** During Safety Blitz walkdown on Night shift, C-van on south side of turbine (el. 501) was found with doors open though signage on doors stated doors had to be closed to comply with fire code requirements. Doors were closed by walkdown personnel (after donning gloves). Siemen's craft superintendent queried walkdown personnel if doors were found open or opened to look inside and when informed the doors were found open he took the action to reinforce the requirment to close the doors with Siemen's personnel. <I> **** Actions Taken **** 1) Close C-van doors 2) Provided feedbeack to Siemen's craft lead 3) Initiated CR.
394431 | CR | 20190529 | CAQ | D | RRA-CC-9 License Renewal Exam Showed Corrosion Damage | Y | Y |  | N | YES | <D> **** Detailed Description **** While performing WO 02106152 License Renewal (LR) inspection of RRA-CC-9 TSW piping, the as-found VT-1 exam identified that there was corrosion damage including localized corrosion that could have impacted the intended function of the pipe. The pipe is being replaced with new stainless steel under WOT 01188443-01 to restore full qualification of the valve. Therefore, no functionality determination or other action is required. . NDE observed approximately 20-30% of the 1-1/2â€ piping inspected had evidence of reduced diameter. The corrosion was a uniform layer with moderate-to-major surface deposits. There was one deposit that obstructed approximately 35% of the internal diameter near 45-degree elbow downstream of RRA-CC-9. There was no slime observed or foul odor consistent with biological activity noted. The external of the pipe had minor surface corrosion but no evidence of a through wall leak. This pipe degradation is consistent with system performance observed during the previous operating cycle. This inspection is required under LR Commitments No. 14, Cooling Unit Inspection Program and No. 42, Open Cycle Cooling Water Program. . No further action is required under this CR. It is recommended to trend the CR for AMP trending. <I> **** Actions Taken **** Discussed issue with AMP Owner, Supervisor and EOC. <N> **** Equipment Description **** Steam Tunnel | 02-00-RRA-CC-9
394432 | CR | 20190529 | CAQ | C | Discrepancy in Weekly LHRA Check Form DIC Number |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing the Weekly LHRA (Locked High Radiation Area) and VHRA (Very High Radiation Area) Door Check forms (Form 27145) a discrepancy was noted with the DIC number. Revision 000 of this form was initiated 12/13/2016 when VSDS (Visual Survey Data System) was implemented in December 2016. Previously this door check was recorded on a survey map. Revision 000 of Form 27145 used DIC number 1541.12, and the DIC index in share point identifies Weekly LHRA and VHRA Door Checks form as DIC 1541.12. Both Revision 001, 01/04/2017, and Revision 002, 07/06/2017 of Form 27145 omitted the DIC number. There currently is no DIC number on the form. Prior to the form when the door checks were recorded on a survey map format - those documents were sent to records and stored under DIC 1517. A review of the procedure 11.2.24.1 (Revision 036) driving the use of Form 27145, in Section 4.0, Documentation, incorrectly lists the corresponding DIC number as 1552.3. According to the DIC Index in Sharepoint this number is the Key Repository Open/Close Log. However, this discrepancy appears to have existed in PPM 11.2.24.1 at least as far back as 1999, in Revision 20. In addition, the Form should also contain the driving document (i.e., PPM 11.2.24.1) somewhere on the form and currently it does not. When the correct DIC is determined it should be added to the header of form 27145. <I> **** Actions Taken **** Contacted Nightshift Rad Ops Supervisor and discussed this issue. Notified the RP Department Records Custodian. Initiated this CR to document condition and make any corrections and alignment with the DIC number discrepancies and DIC Index guidelines. <N> RP Operations Supervisor has approved closure of this CR.
394433 | CR | 20190529 |  | 4 | WO 02077541-60: COND-TE-514A Damaged Wires | N | N |  | N | YES | <D> **** Detailed Description **** While determing COND-TE-514A per referenced WO, wires were discovered damaged at a Chicago Fitting 2â€ below the transmitter. The Temperature element wires are at the transmitter head are undamaged and in good condition, the issue is with the â€œfieldâ€ wires that connect the Temperature element to the Junction Box. New thermocouple wire should be ran from the junction box to the Temperature element housing. <I> **** Actions Taken **** Supervision notified. CR generated, and WR written to fix the damaged wiring. <N> **** Equipment Description **** COND-TE-514A (441TB)
394434 | CR | 20190529 |  | 4 | BS-V-21A has cracked tack weld | N | N |  | N | YES | <D> **** Detailed Description **** Disc nut / stud tack weld is cracked and disc / seat alignment is to one side (right). <I> **** Actions Taken **** Repair tack weld and move hanger arm spacer from left side to right side to centralize disc on inbody seat during reassembly. <N> **** Equipment Description **** TB 471 HB | 02-00-BS-V-21B
394435 | CR | 20190529 |  | 3 | AED Recommendation |  |  |  | N | NO | <D> **** Detailed Description **** I think we need more AED's in the power block and near the breakrooms in the Yakima building. There is already an O2 bottle and first aid kit in the EO breakroom, but not an AED. A recent event showed how valuable the AED is and the time it takes to get to an AED and back to a man down is valuable time lost, especially in the power block. I recommend installing AED's in main hallways on most if not all elevations in the power block. The cost of the equipment is well worth the life it will save if needed. <I> **** Actions Taken **** Informed supervision and wrote CR. <N> Occupational Health and Industrial Safety have reviewed the locations of the AED and the concern raised in this AR. Both departments believe that both the number and locations of the AEDs are sufficient to respond to an emergency. In addition, the medical responders are trained in the AED locations and should be able to access the AED if needed in an appropriate amount of time. Action complete.
394437 | CR | 20190529 |  | 4 | Upper TG Building Roof Reinforcing Pads | N | N |  | N | YES | <D> **** Detailed Description **** During walk-down of upper TG building roof per WOT 02111870-01 it was identified that multiple membrane reinforcing pads installed on roof seams appear to be coming up at the edges. These pads varied in size from approximately 6â€x6â€ to 6â€x12â€ and were installed at seams as reinforcement and some were installed possibly for repairs to previous hole or tears in the membrane. These pads remain adhered to the roof but should be glued and/or caulked along edges to provide a full seal to underlying roof membrane. Recommend this work be performed during R24 outage to ensure a sound roof system devoid of any potential leaks. There are multiple locations (about 16) and repair locations are easily found per walk-down of the roof. Engineering support is available if required by contacting the EOC. See pictures in EDMS for more information. May be prudent to coordinate potential repair with work to repair NW corner of roof membrane under WR 29149088 (CR 00394426). <I> **** Actions Taken **** Wrote this CR. | 02-00-T-BLDG-MISC
394438 | CR | 20190529 |  | 4 | Upper TG Roof Membrane not Adhere to Substrate | N | N |  | N | YES | <D> **** Detailed Description **** During walk-down of upper TG building roof per WOT 02111870-01 it was identified that the roof membrane is not fully adhered to the substrate in two locations. One location is along the north parapet wall starting about 80 ft from the NW corner for approximately 25 ft. A second location along the north wall in the central part of the TG roof next to the expansion joint. See photos in EDMS. . May be prudent to coordinate potential repair with work to repair NW corner of roof membrane under WR 29149088 (CR 00394426) <I> **** Actions Taken **** Wrote this AR. | 02-00-T-BLDG-MISC
394440 | CR | 20190529 | CAQ | D | Pen seal for CMS-PT-8 self identified as a failure | Y | Y |  | N | NO | <D> **** Detailed Description **** Pen seal for CMS-PT-8 self identified by I/C technicians as a failure prior to having QC inspection performed. <I> **** Actions Taken **** QC notified that the seal will be re-poured and will need cleanliness inspection performed prior to the second shoot, supervisor notified, CR generated. Work order 02073390-01 has 74hrs of float as of 5/28/19 @ 1106 - OCC contacted and the issue identifies as NO impact to the schedule. <N> **** Equipment Description **** CMS-PT-8
394445 | CR | 20190529 |  | 3 | R24LL - Peer Check CPR qualifications |  |  |  | N | NO | <D> **** Detailed Description **** At the start of R24 there was a plan to use Operations Training personnel as peer checks for the first couple of days. Peer checking on certain tagging evolutions requires CPR qualifications. Most Operations Trainers do not have CPR qualifications and were unable to perform this function. Consider qualifying Operations Trainers who will be performing peer checks during an outage CPR prior to outage start to help facilitate in this role.
394446 | CR | 20190529 | CAQ | C | RCIC-DT-1 had gasket material in the oil pump gear | Y | N |  | N | YES | <D> **** Detailed Description **** While performing WO #02116077-01 to inspect the oil pump gear and housing for foreign material due to recent OE at River Bend, it was observed that there was some Permatex #2 that had been transferred to the driven gear and had no material on the drive gear itself. This material was very light and after removal showed no degradation to the driven gear. <I> **** Actions Taken **** Notified engineering and my supervisor, wrote this condition report. Pictures will be uploaded to the EDMS | 02-00-RCIC-DT-1
394448 | CR | 20190529 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: TR-S A-0 B-0C-0 TR-B A-119KV B-118kv C 118KV Sensors Startup and Backup voltages are as follows: E-TR-S A: 0 B: 0 C: 0 E-TR-B A: 119 B: 118 C: 118 Sensors were tripped and are reset: J7, J11,J14,J16 Cause was momentary open and reclose of Ashe-Slatt-1 this is on the 500KV system. No reports of any damage or outages needed at this time by BPA <I> **** Actions Taken **** Followed ARP
394449 | CR | 20190529 |  | 3 | PPM 12.9.9 needs updated. |  |  |  | N | NO | <D> PPM 12.9.9 (PASS LLRT Valve Lineups). Section 4.16.3 & 4.18.3 When lining up to Suppression pool the procedure has you lining PSR-RMS-HC/723 in position 1 (Drywell atm.) instead of position 2 (Suppression Pool Atm.) This does not allow line-up of PSR-V-710, 711, 718 and 719 to open for LLRT valve testing for suppression pool.. Section 4.16.5 has PSR-RMS-4 lined to Drywell Upper (SP-99) instead of wetwell (SP-100). This does not allow PSR-V -83/2 to open for LLRT testing. Section 4.18.5 has SP-101 mislabeled as Drywell Upper instead of Wetwell. <I> Had peer check by LLRT personnell. Had supervision pen and ink procedure and wrote CR. Contacted chemistry specialist to revise procedure. <N> Found at INPROG status, took to approved.
394451 | CR | 20190529 |  | 3 | TSW-HX-8 Inlet head alignement issues | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The flanges on the inlet head of TSW-HX-8 do not line up. They do not seem to be two holed. The inlet head flange and the pipe flange were able to be mated up. Suggest this be reviewed by Engineering. This work is performed under work order 02113088-20. <I> **** Actions Taken **** Contacted Management
394452 | CR | 20190529 |  | 3 | Foreign Material removed from COND-HX-9 "B" condenser bay | N | N |  | N | YES | <D> **** Detailed Description **** Inadequate foreign material control practices in the main condenser resulted in significant amounts of foreign material being found in the COND-HX-9 "B" condenser bay during TG 471 closeout inspections . Tarps installed to protect condenser tubes were not sufficient to prevent foreign material entering the tube bundles. Pandecking was not sufficiently cleaned prior to removal. Foreign material found included 5 sheet metal screws, 1 large neon ziptie, one weld rod, and numerous small pieces of metal from cutting/welding activities. Photos were not able to be taken as a HEPA vacuum was used to remove the items with a 6ft long 3/4" tube extension to fit down into tube channels. This foreign material was found after a shift of cleaning performed by laborers. This foreign material has the potential to cause tube leaks which could require a significant extended downpower to repair/plug. This is very similar to what was found during R23 in COND -HX-9 "C" condenser bay (AR 367120), <I> **** Actions Taken **** Removed all foreign material that was seen. Notified EOC. <N> **** Equipment Description **** TG 471 All FM was removed. No futher actions required. | 02-00-COND-HX-9
394453 | CR | 20190529 |  | 3 | Timer relays not functioning correctly for E-TR-M3 | N | N |  | N | YES | <C> Why are the parts not functioning properly? <D> **** Detailed Description **** After initial energization of the 25/500KV system it was discovered that the 27N relay had given alarm point 24 of E-TR-M3. This relay was replaced under WO 0211018301 along with the 2A-1 and 27E relay. While installing these replacement relays it was identified that some of the previously used relays that were purchased had to be thrown out due them not functioning correctly. It is recommended that all of the relays replaced under WO 0211018301 be replaced during R24 so they do not continue to provide alarms to the control room during the operating cycle. Reference AR-CR 00393893 and 00394265. | 02-00-E-TR-M3
394455 | CR | 20190529 |  | 4 | (QA) Rejected Inspection- Support RWCU-139 Weld | N | N |  | Y | YES | <D> **** Detailed Description **** (QA) Upper tube-to-tube weld of support RWCU-139, performed per WOT 02120340-04 and WR 2-13674, was rejected by Quality Control due to spatter / slag on the surface of the weld and the weld being undersized. Requirements of W-103 (Visual Inspection of Welds Made to the AWS D1.1 Code) and MWP-7 (AWS General Structural Welding Standard) were not met. . Quality Control provided coaching to the craft, weld was reworked, QC inspection was re-performed and the weld was found satisfactory. . . <I> **** Actions Taken **** Notified Quality Services Supervisor, Craft Supervisor and Quality Control Level III Inspector. <N> **** Equipment Description **** RWCU-139 SUPPORT - C 540' AZ 150-20 Issue resolved by weld rework and acceptance by QC as documented in the CR. Williams Plant Services.
394456 | CR | 20190529 |  | 3 | R24LL lessons learned LLRT's delayed due to Chem Tech Quals | N | N |  | N | NO | <D> **** Detailed Description **** TSP-PSR-R801 was delayed by 24 hours due to an insufficient number of Chemistry Technicians being qualified and fatigue rule. <I> **** Actions Taken **** OCC was informed. <N> WO was scheduled to start on 05/29/19 and was moved up to 05/27/19. No Chemistry resources or support tasks were added for this WO when it was planned.
394457 | CR | 20190529 |  | 3 | Tube support erosion indications on COND-HXs | N | N |  | N | YES | <D> **** Detailed Description **** During eddy current testing on COND-HX-2B and 4C under WO 02111007 and 02117683 respectively, some support wear signals were detected at multiple locations. The eddy current testing shows some general erosion on some support plates that might be due to steam erosion. Thereâ€™s no need to plug the tubes this outage until further investigation is done. Recommend action to heat exchanger engineer to evaluate possible ways to inspect the support plates on COND-HX-2s and COND-HX-4s and add the inspection to R25 scope. <N> **** Equipment Description **** T471 and T501 | 02-00-COND-HX-2B,02-00-COND-HX-4C
394458 | CR | 20190529 | CAQ | D | SGT-FN-1A2 operating with SGT-FN-1A1 low flow alarm in | Y | N |  | N | YES | <D> **** Detailed Description **** After transferring RPS-B to the normal power supply, SGT -FN-1A2 was found running with a SGT-FN-1A1 low flow alarm locked in. This is not a normal response to swapping RPS-B back to the normal source. The low flow alarm cleared when the SGT-EHC-1A1 was placed in PTL to reset the logic. The system was put in a standby lineup per SOP-SGT -SHUTDOWN. | 02-00-SGT-FN-1A2
394459 | CR | 20190529 | CAQ | C | CATID 56235235 non-usable when inspected in field. | Y | N |  | N | YES | <D> **** Detailed Description **** CATID 56235235 was ordered for use on CRD-AO-11, WO 02119375-01. Upon removal from the package, the craft identified the small gasket was broken. This small gasket fits under a nut on the inside of the Air Operator. Generated MR 00277149 and contaced OCC for expediting and obtaining a replacement as none are on hand. <I> **** Actions Taken **** Will contact EOC for an alternate path as well as there is an o-ring that provides the shaft seal and this gasket only sits under a nut at the bottom of the air operator in which a gasket from another similar material or some thread sealant may be able to be used. <N> **** Equipment Description **** CRD-AO-11 Equipment currently out of service for maintenance. WO 02119375 | 02-00-CRD-AO-11
394460 | CR | 20190529 |  | 3 | fuel bundle 29 34 lighter than typical on insertion into cel | Y | N |  | N | YES | <D> **** Detailed Description **** While inserting fuel bundle YLW129 into location 29-34 it was noted that the loaded weight of the bundle was about 50-80 lbm less than typical. Around 560 vice 640. This could be indicitive of excess friction with the control rod blade <I> **** Actions Taken **** Informed SNE and control room On 5/27/2019, this bundle had difficulty being inserted and was placed in the temporary storage location in the spent fuel pool JJ-02. <N> **** Equipment Description **** rx core
394461 | CR | 20190529 |  | 4 | Radiological Waste Blocking Electrical Equipment | N | N |  | N | NO | <D> **** Detailed Description **** Radiological waste located at the RW437, Q1-13.2 is blocking access to an electrical disconnect. The waste appears to be combustible. ISPM-6, 3.7.6(a) requires 3 feet of clearance in front of electrical equipment. ISPM -6, 3.7.6(b) requires a 3 foot combustible free zone in front of disconnect switches. <I> **** Actions Taken **** Notified RMC Laborer Supervisor to have the waste moved. There is currently a very large volume of radiological waste in that area. <N> Per the RMC Supervisor, radiological trash has been loaded into c-vans. No further action required.
394463 | CR | 20190529 |  | 3 | Shipping Survey using other-than-specified inst model | N | N |  | N | NO | <C> Re-opened at the request of the department. <D> **** Detailed Description **** On 5/28/2019, three radioactive shipment surveys were completed using a Telepole survey meter instead of the Model 14C surey meter specified in 11..2.13.1 R41 MR1 Step 5.10.2. In Rev 39 of 11.2.13.1 this step (4.13.7 is this rev) stated to "Use GM type meters" witht he Model 14C as an example. In revision 40 this step was erroneously changed to replace the generic instrument type with a specific model. <I> **** Actions Taken **** Initiated CR. Discussed with shipping supervisor the intent of this step. Initiated minor revision 2 to 11.2.13.1 to return the step to referencing a generic instrument type rather than specific model. <N> Contrary to those statements in this CR regarding previous revisions to this PPM; this instrument has been specified in procedure by name (specifically the 14C) in all revisions dating back to 2002 as it was a corrective action in response PERA 201-2696-03 and is in LETTER GO2-02-009, DATED 1/17/2002 (reference RTS C-11562) which specified the 14C, but that information could have been intended for just burial site or commitment could be outdated - Need to ensure if this is removed that it is IAW SWP-LIC-01 and LBDM-01. Also, for reference as ie or eg are often confused for one another: An i .e., stands for id est (as was used in revision 039) and means.... that is, or, in other words. An e.g., exempli gratia in Latin and if used, means for example, or, such as.
394464 | CR | 20190529 |  | 4 | TMU-42-8R3E (TMU-C-1B) suspected blown fuse | N | N |  | N | YES | <D> **** Detailed Description **** TMU-42-8R3E (TMU-C-1B) is suspected of having a blown fuse(s). There are no control power lights lit at TMU-42 -8R3E or at the TMU-C-1B control panel. TMU-C-1B would not respond to its control switch being taken to ON. Additionally, there is a broken bulb stuck in one of the light sockets of TMU-42-8R3E. Please investigate lack of power to TMU-C-1B, and repair light socket. <I> **** Actions Taken **** Informed MCR | 02-00-TMU-42-8R3E
394465 | CR | 20190529 |  | 4 | Kelman service light on for E-TR-M2 | N | N |  | N | YES | <D> **** Detailed Description **** While performing a walkdown of the transformer yard it was notice that Kelman service light was on for E-TR-M2. The Kelman DGAs for each transformer will be serviced and calibrated under WO 02134478. | 02-00-E-AY-TR/M2
394466 | CR | 20190529 |  | 3 | Upper Drywell controls during fuel movement | N | N |  | N | NO | <D> **** Detailed Description **** Benchmark upper Drywell controls industry practices as well as procedural guidance to aid in HPI-12.74 revision prior to R-25. <N> Actions to address this CR are being taken under CR 393987.
394467 | CR | 20190529 |  | 4 | PWC-SEW-11 has inadequate flow. | N | N |  | N | YES | <D> **** Detailed Description **** PWC-SEW-11 has inadequate water flow. Please T/S and repair as necessary. This is a reoccuring problem for this station. <I> **** Actions Taken **** Notified CRE. <N> **** Equipment Description **** CWPH | 02-00-PWC-SEW-11
394468 | CR | 20190529 |  | 3 | R24LL: Recommend enhancement to SOP-CAS-OPS |  |  |  | N | NO | <D> **** Detailed Description **** Recommend removing step 5.12.4 from SOP-CAS-OPS since incredibly this step requires industrial safety sampling of temporary air compressor discharge prior to starting the compressor. Also later in the procedure if using Atlas Copco compressors step 5.12.8.b. has us verify CO monit oring is in place. The section for using the Rand 1600 compressor does not have this requirement. Recommend making both compressor steps, 5.12.7 and 5.12.8, CONDITIONALLY address the breathing air question.
394469 | CR | 20190529 |  | 3 | R24 LL SW-V-2A/2B Spacers | N | N |  | N | NO | <D> **** Detailed Description **** Spacers for SW-V-2A and 2B should be pre-fabricated prior to the outage. The rings are well known to need replacement due to corrosion. There was no pre-outage task to do so. Having them prefabricated and at the ready would have reduced time and machinist/welding resources necessary to complete SW divisional maintenance. <I> **** Actions Taken **** Initiated LL CR at request of Mechanical Component Group Manager. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
394470 | CR | 20190529 |  | 3 | R24LL Snubber Contractor Attendance in Boot Camp | N | N |  | N | NO | <D> **** Detailed Description **** R24LL; The Snubber Contractor - Basic-PSA should attend the Supplemental Worker Orientation "Boot Camp" requird for all manual workers that perform work on plant equipment (PPM 1.4.7). This contractor is managed by Engineerng (54121). CR 394388 suggests that we missed the opportunity to assist engineering with their contract/work. . The responsible engineer could use this assignment to aid him in setting up his contract/work for future Refueling Outages. <I> **** Actions Taken **** Discussed this recommendation with Chris Smith.
394471 | CR | 20190529 | CAQ | D | (QA) QC rejection of ASME item for RRC-V-13B | N | N |  | Y | NO | <D> (QA) QC identified an unsatisfactory condition while performing ASME parts acceptance for work order 02033547 task 01. ASME material WOT instructions calls for an ASME III Class 2 1974 edition and winter 1975 addenda item Cat ID 12494. Acceptance Tag for Cat ID 12494 (valve) that was presented to QC shows it to be ASME III Class 2 1974 edition and summer 1975 addenda. ASME information between the Acceptance Tag conflicts with the ASME material WOT instruction. The ASME PIC signature acceptance for the item had been performed for Cat ID 12494.No work has been performed and no material has not been installed in the plant. <I> Notified the ASME PLE, WPS Supervisor, QC Level III and QC Supervisor. . Planner corrected the WOT instruction and QC accepted ASME parts. No further action requried. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review. Williams Plant Services.
394472 | CR | 20190529 | CAQ | C | ME-02-02-25 and ME-02-02-27 calcs used non-conservative Temp | N | N |  | N | NO | <D> **** Detailed Description **** ME-02-02-25 and ME-02-02-27 calcs used non-conservative Temp. This was identified during review of industry OE (Ref AR 389648). Preliminary calcs were performed with the correct temperatures and identified insiginficant decrease in margin. The evaluations are attached in EDMS. This change in margin did not impact any plant component (MOVs) from performing its design function. <I> **** Actions Taken **** Shift manager was briefed.
394473 | CR | 20190529 |  | 4 | Siemens Millwright First Aid Incident | N | N |  | N | NO | <D> **** Detailed Description **** While working in the #5 Thrust Bearing cavity, a Siemens Millwright was positioning himself at the thrust bearing and scrapped his right elbow. He did not notice the abrasion until he was walking out to break. The Occupational Health Nurse reported the condition as â€œan abrasion with a minor laceration approximately Â¼â€ longâ€. A band aid was applied, and the Siemens Employee to return to work. <I> **** Actions Taken **** The employee notified his supervisor, who then notified the Turbine Coordinator. The supervisor escorted the employee to Ocupational Health for evaluation and treatment of the wound. The turbine coordinator initiated this CR.
394474 | CR | 20190529 |  | 4 | Lost indication on TDAS computer | N | N |  | N | YES | <D> **** Detailed Description **** Lost of indication on TDAS computer. Expect power supply issue. Need to investigate and repair. <I> **** Actions Taken **** Engineer informed | 02-00-TDAS-COMP-8715
394476 | CR | 20190529 |  | 3 | Current scheduling of PM prevents adequate history/tracking | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** WR#29149065 asks for two AMS-4s to be calibrated as soon as possible. As two of the AMS-4s in the field will be out of calibration today. PMs for AMS-4s and 3s continue to be scheduled in bunches and are not tracked against the EPN. This removes traceability and effects reliability (last minute calibration pulling manpower from other jobs during the outage). To prove this, the AMS-4 that I calibrated today had a calibration sticker on it, meaning it had been calibrated in the past, but there is nothing speaking to this in its history. This makes checking past performance against current performance difficult. This is does not align with our business model and has proven to be reactive instead of proactive. If there is a PM for each unit traceability will increase and we can schedule the work and remove the need for reactive maintenance. <I> **** Actions Taken **** Completed Calibration, informed HP, supervisor and Manager, wrote this CR.Past CR written #355064
394477 | CR | 20190529 |  | 3 | Several HP Instruments are missing in May inventory | N | N |  | N | NO | <D> **** Detailed Description **** Work package 0213321201 driven CR. Unable to locate several HP Instruments during Monthly Portable HP Instrument inventory. Mirion AMP-100s: RM-41 and RM-56. DCA-3096: AD015. These are used as Area Radiation Monitors and are likely installed somewhere in the RCA. Previously missing (since 2017) AMP-100: RM-39 was not located. It was reported (2018) to be in RW 467' Decon but I couldn't locate it. HP does not have a reliable method of tracking instruments temporarily installed in the plant. An HP log entry would likely suffice . <I> **** Actions Taken **** Notified HP Supervision Verified that FSAR and PPM 11.2.24.1 instrument minimum requirements are satisfied. Posted list of missing instruments in HP Office. Wrote CR per Model Work Order #00DKV9 step 4.4 <N> **** Equipment Description **** Not applicable.
394479 | CR | 20190529 |  | 4 | Unable to access bldg 186 vault for hydrothermograph | N | N |  | N | NO | <D> **** Detailed Description **** while performing 02132991-01 TEMP/HUMIDITY RECORDER MONTHLY CHECKS, the tech obtained the key for vault in bldg 186 from warehouse and when trying to open the door to the vault, the key just spun in the lock. <I> **** Actions Taken **** Initiated CR and contacted facilities. <N> **** Equipment Description **** Building 186 vault
394480 | CR | 20190529 |  | 4 | REA-FN-3 has no lights and will not start. All controls off | N | N |  | N | YES | <D> **** Detailed Description **** REA-FN-3 has no lights and will not start. All controls off of the circuit are de-energized as well. E-PP-3DAC/3 was verified closed. Fuses need to be checked. HP would like to start this fan soon. This is for CRD rebuild room. | 02-00-REA-FN-3
394481 | CR | 20190529 |  | 3 | R24 lesson learned - local clearances cause work delays | N | N |  | N | NO | <D> **** Detailed Description **** R24 lesson learned documentation. Local clearances on two components are causing work delays because only one discipline can work on the component at one time. RWCU-V-1 has valve work and electrical work on the same local clearance L-RWCU-V-1/R24-001. The electrical and mechanical work can not occur at the same time due to clearance procedure requirements. RHR-V-53B magnesium rotor replacement has similar issue with it's local clearance L-RHR-V-53B/R24-001. Major work should be performed on a Danger tag clearance and then moved to a local clearance or temp lifted for testing. <N> No furhter action required.
394484 | CR | 20190529 |  | 4 | 2019 LNI elevator inspection report - Reactor Bldg SW 2948 | N | N |  | N | NO | <D> **** Detailed Description **** Inspection report from Labor and Industries notes required actions. Response due 8/18/219. A copy of the inspection report is uploaded in EDMS docs <I> **** Actions Taken **** Logged Inspection Report, Created CR. Please provide updates to E&RP <N> **** Equipment Description **** Reactor Bldg SW 2948
394485 | CR | 20190529 | CAQ | C | Standard Out of Tolerance | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0066292 Vitrek Model 4700 found OOT No plant impact. NOD# 19-026 assigned.
394486 | CR | 20190529 |  | 3 | Rigging qualifications not identified as needed in work orde | N | N |  | N | NO | <D> **** Detailed Description **** Historically, arc chute removal has not been considered to be a rigging task, and WO 02112085-01 does not require rigging qualifications. The newly adopted method by which the items are lifted, however, is well within the realm of rigging and should be evaluated for qualification requirements and potential procedure/work order instruction changes. Workers were observed on the TG 471 removing arc chutes from a circuit breaker using a portable gantry (A-frame,) chain fall and wire rope sling per ESP-CBS5-F101 (step 7.1.2.f). After the observation, the observer checked, and found that none of the workers had any rigging qualifications. <I> **** Actions Taken **** Notified Electrical Component group manager, Mechanical Component group manager, Training leadership, and Site Rigging Coordinator. Initiated CR.
394487 | CR | 20190529 |  | 4 | (QA) Vacuum Suction Hose Inlet Opening Not Bagged/Taped | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) Vacuum cleaner staged in Room T-112 on TG 441' did not meet control requirements in PPM 1.3.63 "Vacuum Cleaner, Fan, and Blower Control". Mid-morning on 5/29/19, a Quality Auditor noticed two vacuum cleaners with contamination stickers on them that were staged in Room T -112 on TG 441 elevation. One vacuum had no bag/tape on the open end of its attached suction hose, contrary to PPM 1.3.63. The other vacuum had no suction hose and its suction port was taped over. The Quality Auditor notified a Health Physics (HP) Technician who went to take care of it. Not bagging or taping a contaminated vacuum suction hose could allow the undesired result of contamination escaping from the vacuum. Requirements: â€¢ PPM 1.3.63 rev 006 steps 4.1.8a, 4.1.8c, 4.2.2c, 4.2.3e, Attachment 7.1 step E on page 10, and Attachment 7.1 - 3rd bullet up from bottom of page 11 require covering the suction port on the vacuum and the vacuum attachments with bags/tape. Factual Basis: â€¢ At approximately 0955 hours on 5/29/19, a contaminated vacuum with an attached suction hose was found with the open end of the hose uncovered (not bagged/taped), contrary to PPM 1.3.63. (see photo in EDMS) Insights: â€¢ The Quality auditor returned to Room T-112 later in the morning and verified the vacuum suction hose inlet end opening had been covered with tape. (see photo in EDMS) â€¢ On 5/17/19, Quality identified an uncovered suction hose inlet end opening on a different contaminated vacuum near the condenser, and initiated AR-CR 393651 "(QA) Noncompliances with PPM 1.3.63 for Vacuum". <I> **** Actions Taken **** Contacted the Chemistry/Rad Services Manager. . Quality recommends routing to Radiation Protection. <N> Per RMC Supervisor the vacuum suction hose inlet opening has been taped. No further action required.
394488 | CR | 20190529 |  | 4 | (QA) Safety Blitz Walkdown - Unlabeled Substance | N | N |  | Y | NO | <D> **** Detailed Description **** A Quality Auditor identified an unlabeled bottle with an unknown substance inside on the RW 452 elevation. The substance appeared to be residual oil from work already performed. Owner of the job cart contacted and the substance was identified and taken care of. <I> **** Actions Taken **** Contacted owner and verified bottle no longer on the job site.
394489 | CR | 20190529 |  | 3 | (QA) Storage Level C item not in proper storage location | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) Identified a box of Refractory Ceramic Fiber stored outside of Building 75 rather than inside the building as required by SWP-MMP-02, "Warehousing", Attachment 7.3 section D. . Factual Basis: Portal J identifies Catalog ID 18451, "REFRACTORY CERAMIC FIBER", as Q Level 1 and Storage Level C. SWP-MMP-02, "Warehousing", defines Level C items as "â€¦ those that require protection from exposure to the environment, airborne contaminants, gravitational forces, and physical damage.", and requires Level C items to be stored within a fire resistant, tear resistant, weather-tight, and well ventilated building or equivalent enclosure. Contrary to this, Quality identified the box containing refractory insulation (Catalog ID 18451) stored outside of Building 75, "Painters and Materials Warehousing" (See EDMS for pictures). . Other Insights: Discussing the above with the Warehousing/Traffic Supervisor, and the Site Support Contractors Manager, all agreed that the current method of storage was inappropriate for the item's Storage Level Requirements. . The Site Support Contractors Manager took immediate action to move the items to an appropriate storage location and to obtain appropriate equivalent enclosures to allow storage in the current location.. This problem is considered a Deficiency identified during performance of Work Order 0210615205, " In ~ Rework Penetration SEAL R310-4025 (STM TNL DOOR)" in R24 . Quality recommends that this CR be routed to Site Support Contractor. <I> **** Actions Taken **** Contacted the Site Support Contractors Manager. <N> Williams Plant Services. The insulation in question has been relocated into a C-Van near the CST Tanks. Added one week to closure date of this AR (9-5-19) to allow time to review actions performed/completed.
394490 | CR | 20190529 |  | 4 | Trouble alarm for E-TR-S always in during when 230KV is out | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02114646-01 it was discovered while testing the alarms on E-TR-S locally to actuate the C4 drop 2-7 alarm it would not work. Without jumpering out the alarm contact on E-RLY-47/27/TRS a trouble alarm will not be received for E-TR-S. In order to check this alarm the 230KV has to be in-service or the contact for this relay has to be jumpered in the control room to test the alarm. During the accessory check all alarms for E-TR-S are functioning correctly and providing input to the alarm relay for E-TR-S. Note: This condition also impacts E-TR-B accessory checks under PMID 5853-04. <I> This is a testing / WO impacting condition and does not identify any degraded condition. <N> initiated AR-SMS to update MWOs with changes. T. Mclaen 5/29/18 | 02-00-E-RLY-47/27/TRB,02-00-E-RLY-47/27/TRS,02-00-E-TR-B,02-00-E-TR-S
394491 | CR | 20190529 | CAQ | C | CVB-V-1EF Failed its LLRT per TSP-CVB-R801 | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of containment vacuum breaker surveillance TSP-CVB-R801 CVB-V-1EF failed its LLRT due to not being able to establish test conditions. A pressure of negative 1.250 psig was obtained with a negative 1.6 to 1.8 requirement. Flow was recorded at 25,800 SLPM with an acceptance criteria of 291,686 for each CVB dual disc set. Suspect test equipment vacuum pump degradation. <I> **** Actions Taken **** Notified LLRT SRO/ EOC/OCC <N> **** Equipment Description **** Wetwell The LLRT will be reperformed when appropriate test conditions can be established. There is no indication of inoperability therefore the REP/REGE assignments can be cancelled <R> REP/REGE cancelled with Licensing Supervisor concurrence. | 02-00-CVB-V-1EF
394493 | CR | 20190529 |  | 4 | Top limit switch not working |  |  |  | N | YES | <D> **** Detailed Description **** Limit switch on BS-V-8A (Top) no indication in the control room once the switch is made. <I> **** Actions Taken **** Notified Aov engineer. | 02-00-BS-V-8A
394494 | CR | 20190529 |  | 3 | RRA-M-FN/8 bearings changed to double shielded | Y | N |  | N | NO | <D> **** Detailed Description **** Need to update PPM 10.2.13 to reflect that RRA-M-FN/8 now has double shielded bearings and does not require lubrication. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
394495 | CR | 20190529 |  | 4 | R24 Lesson Learned - communication of closed emergent issues |  |  |  | N | NO | <D> **** Detailed Description **** As a station, we communicate every new emergent issue that comes up through email. When we close the emergent issues, no communication is provided unless you happen to be listening to the OCC update meeting when the issue is closed. Key stakeholders in emergent issues should be notified when emergent issues are closed and in some cases, part of the decision to close the emergent issue. <I> **** Actions Taken **** Initiated CR. Informed Emergent issue team and OCC rep.
394496 | CR | 20190529 | CAQ | D | SLC-TK-1 aluminum flashing loose and peeling | Y | N |  | N | YES | <D> **** Detailed Description **** On the top of SLC-TK-1 the aluminum flashing is loose and peeling. It has the potential to cause poor footing which could result in severe personal injury. <I> **** Actions Taken **** Supervisor and CRS informed. Take 2 performed to identify and mitigate the hazard through avoiding the affected area. | 02-00-SLC-TK-1
394498 | CR | 20190529 | CAQ | C | Position Switches installed incorrectly on MSIV | Y | N |  | N | YES | <D> Position Limit switch 1 on MS-V-28A, MS-V-28B, and MS-V-28C was installed incorrectly on the limit switch cam assembly, (see pictures in EDMS) it was to be on the opposite side of the cam. But was not installed that way. <I> Generated WR 29149115, 29149116, 29149114 to move the position switches to the correct position (see pictures in EDMS) <N> MS-V-28A, MS-V-28B, and MS-V-28C CR at INPROG. Approved CR, moved to SRO for OPS Review. | 02-00-MS-V-28A,02-00-MS-V-28B,02-00-MS-V-28C
394499 | CR | 20190529 | CAQ | C | Found RCC-CB-P1B aux. contacts misconfigured | N | Y |  | N | YES | <D> **** Detailed Description **** Found the 29-30 aux.2 contact out of configuration per the E534-19A. Contacts were made up as open, closed, open, closed. The E534 shows the configuration as open, closed, closed, closed respectively. Checked contacts at both the aux. 2 contact and at rear secondary contacts to confirm. <I> **** Actions Taken **** Left breaker out of cubicle. Contacted supervisor and FIN team manager to configure breaker for operations PCSC. Staged breaker in hallway with W.I.P. sign WR 29149039. Initiated CR | 02-00-RCC-CB-P1B
394500 | CR | 20190529 |  | 3 | PPM 10.17.3 requires revision | Y | N |  | N | NO | <D> **** Detailed Description **** MS-V-28B Limit switch adjustment guide plate dimension changed from 14.875 in to 14.75 in during recent performance of 10.17.3 in WO-2079278-11. Revise step 5.2.13f to match new dimensions. <I> **** Actions Taken **** Wrote CR; won't need till R25. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
394501 | CR | 20190529 |  | 3 | R24 LL Enhance ESP-MSIV-B301 & 10.17.3 |  |  |  | N | NO | <D> **** Detailed Description **** Dimensions that are used in more than one procedure may change when valves undergo an overhaul such as MSIV Limit switch guide plates. Work is then delayed until the affected procedures are updated. Recommend dimensions be removed from procedure for dimensions that routinely change and add a Prerequisite to record current data from an approved source. <I> **** Actions Taken **** Discussed with supervision. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
394502 | CR | 20190529 |  | 4 | RWCU V 34 Cobalt Levels > LLD |  |  |  | N | NO | <D> **** Detailed Description **** As part of cobalt reduction efforts, RWCU V 34 was cleaned in accordance with HPI 12.91,Elemental Cobalt Sampling, protocol. Results identifed up to 27 micrograms of Co-60, which is above the LLD. The Cobalt Reduction Program Management Sponsor evaluated the results and concluded with approving the valve for reasembly without further cleaning. <I> **** Actions Taken **** Notified Cobalt Reduction Program Manager, Valve Project Coordinator and initiated CR in accordance with HPI-12.91
394503 | CR | 20190529 |  | 3 | Calculation 8.14.108 - GT 5 CMRs at â€œModifiedâ€ |  |  |  | N | NO | <D> **** Detailed Description **** In accordance with Design Procedure DES-4-1, the intent of this CR is to document that calculation 8.14.108 has greater than 5 Calculation Modification Records (CMRs) at â€˜Modifiedâ€™ status. There is no impact to the day-to-day operation of CGS. This assignment should be given to Mechanical Design (AR-DMC) to revise the calculation and incorporate the â€˜Modifiedâ€™ status CMRs into the next revision. <I> **** Actions Taken **** Discussed this issue with the Mechanical Design Supervisor Initiated this CR in accordance with DES-4-1
394504 | CR | 20190529 |  | 4 | CAS-T-3A not popping |  |  |  | N | YES | <D> **** Detailed Description **** CAS-T-3A did not pop in the time it took the other two to go through two cycles. Trap needs to be cleaned out. <I> **** Actions Taken **** N/A | 02-00-CAS-T-3A
394506 | CR | 20190530 | CAQ | C | HPCS-V-4 as-found leak above admin limit | Y | N |  | N | YES | <D> **** Detailed Description **** HPCS-V-4 as-found leakage was measured at 0.25 gpm which is above its admin limit of 0.15 gpm but below the tech spec limit of 4.75 gpm. Leak test performed per TSP-RCS-R803 under WOT 02113444-03. <I> **** Actions Taken **** LLRT SRO, EOC, and OCC notified <N> Equipment Operators discovered leak-by through HPCS-V-76. HPCS-V-76 is a boundary test volume valve. The leak-by through HPCS-V-76 artificially inflates the leak rate of HPCS-V-4. With approval of LLRT SRO, HPCS-V-6 was tighten and the leak reate test on HPCS-V-4 was re-done. The test results from the re-test was less than the admin limit and less than the tech spec limit. | 02-00-HPCS-V-4
394507 | CR | 20190530 |  | 3 | Evaluate leaving the Torit scaffolding in place, TG 501. |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate leaving the Torit ventilation units scaffolding in place on the TG 501 during operations. Considerable time and cost is required to install and remove scaffolding to support the two Torit ventilation units on the TG 501 floor every outage. The duct work scaffolding has been approved to stay up with the plant on line. This recommendation was made by the Williams carpenter General Foremen. <I> **** Actions Taken **** None <N> An AR type EVAL should be initiated for this request.
394508 | CR | 20190530 |  | 3 | Evaluate voltage tolerance for 24VDC system logs | Y | Y |  | N | YES | <D> **** Detailed Description **** Form 27152 of PPM 3.1.10 specifies the 24VDC bus voltage as indicated on E-VM-DP/S0/B at H13-P800 should be 26.5 to 27.5 VDC while the associated battery is in float. While in equalize the range is 28.6 to 29.0 VDC. This reading is routinely above the prescribed 27.5 limit while the battery is in float. The calibration of this meter is current per WO 02109040 (ESP-AMVMB02-X301). This discrepancy has been identified several times. <I> **** Actions Taken **** I recommend changing the required voltage range. The SR 3.8.7.1 and 3.8.8.1 required voltage is 26 to 29 VDC per OSP-ELEC-W102. Please evaluate what is required by 3.1.10. <N> **** Equipment Description **** MCR H13-P800 | 02-00-E-VM-DP/S0/B
394509 | CR | 20190530 |  | 4 | Personal Medical Condition - Transport Off-Site |  |  |  | N | NO | <D> **** Detailed Description **** On Wednesday May 29, 2019 an Energy Northwest employee experienced a personal medical condition at the Yakima Building 441â€™ Health Physics Access Control. A 2222 call was placed at 23:08. A medical responder tone out was initiated by the control room per PPM 1.9.14. The patient was evaluated and treated by the medical responders. Hanford Fire Department (HFD) Medic 1923 & Ladder 1923 arrived at 23:24. Ladder 1913 was stationed outside the Protected Area per HFD on standby. The patient was further evaluated by HFD and transported to Kadlec Medical Center at 23:50 <I> **** Actions Taken **** Reviewed the event with Operations and Health Physics personnel. OCC reviewed the event at the 0100 meeting.
394510 | CR | 20190530 |  | 4 | SA-V-100/6 |  |  |  | N | YES | <D> **** Detailed Description **** SA-V-100/6 is on RX 522. Used to supply air for disassembly and testing of air operators for HCU rebuilds. After multiple times being opened and closed, started to operate hard. Left valve in open position to allow continued use. <I> **** Actions Taken **** Initiated this CR and reported to Supervisor. <N> **** Equipment Description **** SA-V-100/6 RX 522 West side | 02-00-SA-V-100/6
394511 | CR | 20190530 |  | 3 | Westinghouse DHP breaker as found testing failed. |  |  |  | N | NO | <C> Is there one on order? <D> **** Detailed Description **** During the initial testing of a replacement 6.9 KV Westinghouse DHP type breaker (UTC #0000368917) the breaker did not pass the â€œAs Found Reduced Voltage TRIP Test per PPM 10.25.13. 10.25.13. This circuit breaker was sent out, and received back, from a Vendor that Energy Northwest utilizes for breaker refurbishments. <I> **** Actions Taken **** Generated CR to document issue discovered with circuit breaker. Contacted engineering regarding the as found testing. With engineering present validated the test configuration, and other circuit breaker internals.
394512 | CR | 20190530 |  | 3 | EC17554 (Remove TMOD) Implemented without OPSPROC assignment |  |  |  | N | NO | <D> **** Detailed Description **** Notification was received on 05/30/19 that the TMOD associated with EC 17554 had been removed from the plant and that procedures affected by this EC needed to be revised back to their pre-EC condition. This was the first communication between Engineering and Operations Procedure Group on the removal of this TMOD. An assignment had not been created for OPSPROC to revise the affected procedures. Other ECs with similar issues have occurred lately: EC 16355, EC 17061, EC 17111, EC 17761, EC 16703, EC 17221, EC 15817 <I> **** Actions Taken **** Submitted this AR for trending. Initiated discussion with Engineering supervior.
394513 | CR | 20190530 |  | 3 | No Occupational Health personel on nightshift during R24 |  |  |  | N | NO | <D> **** Detailed Description **** There are no occuaptional health personnel on nightshift during the outage. The are about 1000 people here on each shift with many doing strenuous work while working long hours in sometimes physically challenging conditions . In the last three nightshifts there have been two significant medical incidents. While the first responders were awesome in each case, it would seem that there should be 24/7 medical coverage for such a large workforce in these conditions. This would lend better support to the stations focus areas of safety first and risk management is core business. <I> **** Actions Taken **** Wrote this Condition Report <N> Staffing OH 24/7 during an outage has never occurred at Columbia. Columbia has highly trained emergency responders on-site 24/7 that are the first on the scene for any serious event. With any significant medical situation, the OH clinic is not equipped to diagnose or treat the condition, resulting in transport off-site to a hospital emergency room by the Hanford ambulance for the care needed. Hospital transport is available and occurs with or without OH presence. For medical situations of a less significant nature, first aid response is available using first aid kits located throughout the plant. If assistance is needed locating the kits, supervision and/or safety personnel can help. The OH clinic is open 7 days per week from 6 a.m. to 4 p.m. for consultation, follow-up and/or care. Input is also available from the OH Supervisor on an emergency basis during off-hours via pager or cell phone. . The absence of OH staff on-site during nightshift is normal and does not nightshift is normal and does not present an increased safety risk to personnel. No further action is required.
394514 | CR | 20190530 |  | 4 | E-BUS-NONSEG/S/X insulator chips |  |  |  | N | YES | <D> **** Detailed Description **** Two insulators in E-BUS-NONSEG/S/X were found to have small chips. These insulators are located at SX-D53-54 C phase and D-53-53-3 B phase. <I> **** Actions Taken **** Notified managment, notified Williams craft that they should be replaced. <N> **** Equipment Description **** TG 441' | 02-00-E-BUS-NONSEG/S/X
394519 | CR | 20190530 |  | 3 | (QA) Scaffold outside of room R410 is unnecessary |  |  |  | Y | YES | <D> **** Detailed Description **** (QA) Scaffold outside of room R410 to support work on RRA -CC-10 is unnecessary. During a continuous monitoring field work activity a Quality auditor observed work performed for Work Order 02111406, RRA-CC-10 Water side Inspect/Clean/Anode Replace. This work order contains tasks to install and remove a scaffold to door R-DOOR-R413 to support work on RRA-CC-10. With both of these doors removed, (they can't be opened very far due to piping interference, refer to AR 393743) a person cannot access the cooling coil or the fan in the air handler. There is not enough room for a person to squeeze between the doorframe and the air handler to get to the other side of the unit where the cooling coil piping is located (Refer to pictures in EDMS). An extension ladder is located inside this MCC room to reach the cable trays above MC-8B & MC-8BA and reach the cooling coil. The ladder and scaffold platform above the safety related motor control centers was installed on a different scaffold task in the cooling coil work order. . Recommend removing the outside scaffold tasks from model work orders 01178552, (RRA-CC-10 - INSPECT UNIT / CLEAN COILS) and 02047333 (RRA-CC-10, WATER SIDE INSPECT/CLEAN/ANODE REPLACE). Also, to specify in model work orders 01170031 (RRA-FN-10 REPLACE NEOPRENE COUPLING SLEEVE) and 01110243 (RRA-FN-10 LUBE INTERNAL FAN SHAFT BEARINGS) that the scaffold is to be installed inside of room R410 and not outside. <I> **** Actions Taken **** Initiated CR to revise model work orders associated with RRA-CC-10 & RRA-FN-10 that require access to the unit. | 02-00-R-DOOR-R413,02-00-RRA-CC-10,02-00-RRA-FN-10
394520 | CR | 20190530 | CAQ | D | Packing leak on FP-V-47 | N | N |  | N | YES | <D> **** Detailed Description **** While performing 15.3.15 internal inspection FP-V-47 began leaking when it was cycled. With the valve locked in the open position against the back seat it is still dipping approx 10 drops per minute. The packing follower is bottomed out. The valve needs to be re-packed. <N> **** Equipment Description **** Wet 4 Isolation | 02-00-FP-V-47
394521 | CR | 20190530 |  | 4 | CW-V-3A, seat contacted while removing pins | N | N |  | N | YES | <D> **** Detailed Description **** While removing the pins for the valve under WO 02103610, contact was made to the rubber seat with the hammer. Contact was made at the 2:30 and 9:30 positions using due north as the 12 o-clock position. <I> **** Actions Taken **** Notified supervision, and engineering Pictures were taken, inspection of rubber seat was performed from engineering and Maintenance supervisor <N> Engineering has examined the damage. The damage may cause some leakage past the valve. However, this valve is neede only to isolate CW to the 'A' water box if access is required while the plant is online. Leakage can usually be controlled via sump pumps. Repairs are not warranted at this time and this should be tracked against the valve in case leakage is seen in the future if the waterbox must be accessed on line. In other words, this CR will document the cause of the damage on the seats and when it occurred. | 02-00-CW-V-3A
394525 | CR | 20190530 | CAQ | D | Rod 38-23 Full in indication faulty | Y | N |  | N | YES | <D> **** Detailed Description **** During fuel movement, Rod 38-23 full in indication intermittently is coming in and out along with the 4 rod display showing XX. <I> **** Actions Taken **** Fuel movement has been suspended. OCC contacted. TS 3.9.4 actions being taken. <N> **** Equipment Description **** Rx core. | 02-00-CRD-ROD-3823
394527 | CR | 20190530 |  | 3 | R24LL: Enhance SOP-ELEC-DIV2-TEMPPOWER section 5.27/5.28 |  |  |  | N | NO | <D> **** Detailed Description **** When placing/removing CAS (security) on/from temp power per SOP-ELEC-DIV2-TEMPPOWER section 5.27/5.28, security needs to be informed at least a day in advance to verify they have manpower to support. They have checks that need to be completed after each power transfer. Future work orders should have support tasks for security to give them a heads up and schedule extra manpower.
394528 | CR | 20190530 |  | 3 | ISPM-20 needs clarification. |  |  |  | N | NO | <D> **** Detailed Description **** The attachments in ISPM-20 have this note at the beginning of each one except for att. 6.4: â€œNOTE: This table is to be used ONLY for energized work not covered by specific Columbia Arc Flash Study values (Attachment 6.4)â€ This note precludes use of any of the matrices for work in load centers that are listed in attachment 6.4. The current identified problem is that control power fuse removal for breaker racking operation, even with the remote racking tool, cannot be performed per the ISPM because entering the aux cabinet on the end of SLâ€™s is prohibited due to the calorie rating of these SLâ€™s as listed in the ISPM-20 Att. 6.4. The highest rated arc flash suit that is available at Columbia is 140 calories. A significant number of our SLâ€™s are listed far above that 140 calorie rating. The only 480 VAC component inside the aux cabinet is a 480/120 VAC transformer that is mounted above the head and the closest fuse block to be pulled for breaker racking operation is greater than two (2) feet below the transformer. There are some interpretations that section 3.4 of ISPM-20 gives the exception for being able to pull control power fuses in the aux cabinet and still be in compliance. There are other interpretations that donâ€™t see that exception. Please provide clarification as soon as possible to the operations and the electrical departments and correct the ISPM so that conflicting interpretations are removed by making it very clear one way or the other of the expected standard. <I> **** Actions Taken **** Discussed with multiple supervisors and wrote this AR/CR.
394534 | CR | 20190530 | CAQ | C | HPCS-V-76 is leaking by | Y | N |  | N | YES | <D> **** Detailed Description **** CR 394506 was written to document HPCS-V-4 leaking GT the admin limit, and this test utilized HPCS-V-76 as a boundary valve. On night shift, another LLRT utilizing HPCS-V-76 as a boundary valve experienced water leakage as well, leading the team to question the integrity of HPCS-V-76. <I> **** Actions Taken **** Notified supervision, LLRT lead, and LLRT engineer. Initiated this CR. <N> **** Equipment Description **** HPCS-V-76: SLC connection isolation valve | 02-00-HPCS-V-76
394535 | CR | 20190530 | CAQ | C | Incorrect ring lugs installed | Y | N |  | N | NO | <D> **** Detailed Description **** Problem Statement: Incorrect ring lugs were installed on SPV wiring for CRD -HCU 2655 (WO 02050162-16) CRD-HCU 0635 (WO 02082567-17 and CRD-HCU 1835 in WO 02082575-18. The PWTI identified the wire size to be #16 AWG but the wire size is identified on the wire is #18AWG <I> **** Actions Taken **** Notified Supervisor and Generated CR <N> **** Equipment Description **** CRD-HCU-2655 Location R522 K2/8.4 CRD HCU 1835 Location R 522 K2/8.4 CRD-HCU-0635 Location R522 K2/8.4
394537 | CR | 20190530 |  | 4 | SW-TI-2A/2A(position 1) reads high | Y | N |  | N | YES | <D> **** Detailed Description **** SW-TI-2A/2A (position 1) reads 78 degF while the remaining channels read 66, 66, 65. Suspect that the temperature element is very near the surface of the pond or even out of the water as spray pond A water level is 431' 8" at -16" from 433'. Room temperature is also at 78 degF. <I> **** Actions Taken **** Informed MCR | 02-00-SW-TI-2A
394539 | CR | 20190530 | CAQ | D | Wire run support in E-CB-8/83 is unsecured. | Y | N |  | N | YES | <D> **** Detailed Description **** Wire run support in E-CB-8/83 is unsecured. This is a metal support that should be bolted to cublice face similar to the upper support. Please see pictures in EDMS. It does not appear that this will contact the FRTS in the cublicle. However this should be corrected sooner that later as that it cannot be guaranteed that this will no shift in the future and cause issues. <I> **** Actions Taken **** Informed supervision and wrote this AR | 02-00-E-CB-8/83
394542 | CR | 20190530 | CAQ | D | High post UV sulfate analysis in CST | N | N |  | N | NO | <D> **** Detailed Description **** The weekly CST sample collected 5/30/19 indicates UV sulfate at 9.55 ppb. SWP-CHE-02 has a Normal Mode 1 Range of LT 5 ppb. The plant is currently in Mode-5. BWRVIP-190 Water Chemistry Guidelines list this as a diagnostic parameter that is considered Good Practice under NEI 03-08 classifications. It is not unusual to measure UV sulfate above the Mode-1 value in the current plant configuration. See previous CRs from R21 and R22. This condition is expected to correct itself upon completion of the outage. Recommend Cat. D/Trend <I> **** Actions Taken **** Notified Chemistry supervision.
394545 | CR | 20190530 |  | 4 | HD-LCV-5B21 needs repack | N | N |  | N | YES | <D> **** Detailed Description **** During diagnostic testing under WO 02139749 packing friction was abnormally low and did not respaond well to adjustment. Performance of this LCV will be affected. Valve needs to be repacked. <I> **** Actions Taken **** wrote OSCR <N> **** Equipment Description **** T471 | 02-00-HD-LCV-5B21
394548 | CR | 20190530 |  | 4 | Position indicator for RCC-V-4B is faulty | N | N |  | N | YES | <D> **** Detailed Description **** After swapping to RCC-P-1B from RCC-P-1C, it was noticed that the position indicator for RCC-P-1B was reading 66%. This should be reading 100%. The valve has been verified to be full open. <I> **** Actions Taken **** WR written. CRS informed. <N> **** Equipment Description **** MCR | 02-00-RCC-POI-4B
394549 | CR | 20190530 | CAQ | C | Non-traceable material used in CMS-RE-27E and 27F | Y | N |  | N | YES | <D> **** Detailed Description **** During installation of the connectors for CMS-RE-27E and 27F, the Techncians identified a fit up issue on the HN connectors (identified under AR CR 394397). A recommendation was provided by engineering based on guidance from PPM 10.25.19 to shim the connector using WCSF-070. This material was used in the installation as recommended but was not procured from the warehouse and did not have traceable documentation. The EPNs in which this material was used are safety related but the shim material does not support any safety function and was used as fill only. Recommend action to engineering to document downgrading the material (PCER) to accept its use in this application. <I> **** Actions Taken **** Discussed with procurement engineering, the I&C technicians, and planning. <N> PCER P19-0003 Revision 00 was approved on 5/31/19. Due to the nature of the installation and the role of the shim pieces, it is determined that there is no failure mode in this application that would impact the safety function of the connector and by extension the detector. The PCER included environmental laboratory analysis on the shim material that was used to support the justification that the shim material will not affect the safety function of the connectors. The shop needs to provide traceability for all piece parts that are used in all applications. Piece parts that are not to be used for safety related applications need to be segregated. Piece parts that can be used for safety-related use should be maintained such that traceability can be maintained. | 02-00-CMS-RE-27E,02-00-CMS-RE-27F
394550 | CR | 20190530 |  | 4 | PRA-FN-91B has no indication at MC-8R or MWHV2. |  |  |  | N | YES | <D> **** Detailed Description **** PRA-FN-91B has no energized indicating lights at MC-8R or MWHV2 its control panel. Replaced bulbs at both locations. Suspect a possible blown line fuse. This was discovered after TMU LSFT when SM-82 and MC- 8R were re-energized. Currently, Div-1 TMU pump and ventillation are in operation. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TMU pump house. | 02-00-PRA-FN-91B
394551 | CR | 20190530 |  | 3 | Recommended change to OSP-RCS-C103- Bottom Head drain Temp |  |  |  | N | NO | <D> **** Detailed Description **** Currently, OSP-RCS-C103 RPV Hydrostatic Inservice Inspection Temperature Surveillance uses bottom head drain temperature from MS-TR-6 point 356 fed from RWCU-TE-21. RWCU-TE-21 has two internal sensing elements. One feeds RWCU-TI-607 pt 5 and X067 and the other feeds MS-TR-6 point 356. I t would be better if operations ahd the option to use either point, that way if one fails or is out of service, the other point can be used without a procedure change during a critical path evolution. This is already done in OSP-RCS-C101, RPV HEATUP SURVEILLANCE where we allow the use of either, see below: . +6. Monitoring the RWCU or the Reactor Recirculation Coolant temperature allows the MINIMUM RPV METAL TEMPERATURE to be determined. Monitoring of the RWCU bottom head drain temperature element RWCU-TE-21, as read on RWCU-TI-607 pt 5 (H13-P602) OR MS-TR-6 pt 356 (RB 522) is acceptable ONLY if a RRC pump is operating for forced flow, AND RWCU flow of GT 50 gpm exists. Monitoring of the Reactor Recirculation Coolant temperature on RRC-TR-650 pt 1(2) is ONLY acceptable if the associated Reactor Recirculation pump is operating. {R-11469} . Recommend changing OSP-RCS-C103 to be similar to OSP-RCS -C101 and allow either indication point to be used for bottom head drain temperature.
394552 | CR | 20190530 |  | 3 | R24 lesson learned (LL) - MSIV and MSR solenoid work |  |  |  | N | NO | <D> **** Detailed Description **** R24 LL documentation. The MSIV and MS-RV work took approximately 3 times the scheduled duration and therefore 3 times the allotted dose. There are only a couple craft proficient at working these components. Recommend training department obtain mockups of the MS-RVs and MSIVs so that proficiency can be improved with all maintenance shops. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
394553 | CR | 20190530 |  | 4 | Industrial Safety-Noise Hazard Created By C102 Door Slamming |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Door closure for C102 door to Rad Waste Building stairwell is undersized or not properly adjusted to accommodate the weight of the door. The door slams shut and creates a loud bang the reverberates throughout the stairwell. The slamming present a significant noise hazard to personnel traversing the stairwell. Recommend an adjustment to the closure be made if possible or the closure be replaced with one that will better accommodate the weight of the door. <I> **** Actions Taken **** HP Supervision notified <N> **** Equipment Description **** C102 Door to Rad Waste Building Stairwell
394554 | CR | 20190530 |  | 3 | R24 lesson learned (LL) - E shop outage coordinator |  |  |  | N | NO | <D> **** Detailed Description **** R24 LL documentation. A dedicated outage coordinator is needed for each of the three maintenance shops. A single person can not keep up with all the requests and coordination needed for all three shops. A single person could eliminate the artificial bow wave created when data date riders don't get rescheduled and updating task durations on in-progress work. A discipline specific outage coordinator would also eliminate that role that a mainenance supervisor normally fills as a collateral duty. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
394557 | CR | 20190530 |  | 3 | Enhance SOP-ELEC-ISFSI-OPS (SHUTDOWN & START) Normal Source |  |  |  | N | NO | <D> **** Detailed Description **** Enhance SOP-ELEC-ISFSI-OPS (SHUTDOWN & START) with a note stating what is the Normal Source. SOP-ELEC-SM3-MAINT, step 5.2.7, says if necessary transfer ISFSI to the Normal power supply. The ISFSI SOP's do not say what the Normal supply is. SOP-ELEC-4160V-OPS implies that E-CB-1/500S is the Normal and 3/500s is the Emergency Supply. <I> **** Actions Taken **** Notified Ops Electrical Production.
394558 | CR | 20190530 |  | 4 | Lighting circuit breaker E-CB-LP2DB/8 tripping |  |  |  | N | YES | <D> **** Detailed Description **** WO 02136055-42 to upgrade transformer yard lighting was performed and quantity (4) old A37 style lamps were replaced with Crouse-Hinds L4 style lamps. Once completed, Lighting circuit breaker E-CB-LP2DB/8 trip was reset and tripped immediately. Circuit breaker was reset and tripped a second time. Troubleshooting is required on the circuit. Lamps are located on Insulator Towers M4-2 and M4-3. <I> **** Actions Taken **** Notified System Engineer, Supervision and generated this CR. <N> **** Equipment Description **** Located on 13 Line between Main 4 and Normal 2 transformers | 02-00-E-CB-LP2DB/8
394559 | CR | 20190530 |  | 4 | Parking Brake Pedal Not Functioning Properly |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Hyster Forklift (Vehichle # 38-235) parking brake in bldg. 75 is not functioning properly. The parking brake deos not engage when you press it down. At times, it will pop up intermittenly on its own. Also, sometimes it doesn't come up after releasing the brake. Plant Technician came in today and ordered the part and will install once it arrives. <I> **** Actions Taken **** Notified supervisor and facilities of the issue via email. Facilities mechanic ordered parts for the Hyster. He deemed it safe to drive and will install part once it arrives. <N> **** Equipment Description **** Fork Lift is located in Bldg. 75 Name removed from CR.
394560 | CR | 20190530 |  | 4 | R24 LL 230 KV END TO END TRIP TEST Logic Tie Error |  |  |  | N | YES | <D> **** Detailed Description **** Work Order 02111992-01 â€œBPA230KVTRIPTEST: 230 KV END TO END TRIP TESTâ€ was logic tied to after clearances were lifted in the TRS window and appears to have been setup to perform while the line was energized. This work must be performed with the 230 kV line de-energized. Logic was corrected to be performed before system window clearance lift. <I> **** Actions Taken **** Initiated Lessons Learned CR, corrected Logic, notified Supervision and OCC Maintenance Manager. | 02-00-E-TR-S
394561 | CR | 20190530 |  | 3 | (QA) Repeat Vacuum Suction Hose Open Inlet Not Covered | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) Vacuum staged in Room T111 today did not meet control requirements in PPM 1.3.63 "Vacuum Cleaner, Fan, and Blower Control". Same vacuum was in same condition in Room T112 yesterday (see AR-CR 394487). Early morning on 5/30/19, a Quality Auditor found a vacuum cleaner with a contamination sticker on it that was unattended and uncontrolled in Room T111. The vacuum had no bag/tape on the open end of its attached suction hose, contrary to PPM 1.3.63. The Quality Auditor soon notified a Health Physics (HP) Craft Supervisor who said he would resolve it. Not bagging or taping a contaminated vacuum suction hose could allow the undesired result of contamination escaping from the vacuum. Requirements: â€¢ PPM 1.3.63 rev 006 Attachment 7.1 contain "Worker Instructions for Vacuum Operation" on page 11, which states in 3rd bullet from the bottom, "COVER the openings on the suction lines after use, or between uses, to prevent release of contamination." â€¢ PPM 1.3.63 steps 4.1.8a, 4.1.8c, 4.2.2c, 4.2.3e, and Attachment 7.1 step E on page 10 also require covering the suction port on the vacuum and vacuum attachments with bags/tape. Factual Basis: â€¢ On 5/30/19, no one was in Room T111 at either approximately 0845 and 0915 hours, when a contaminated vacuum with an attached suction hose was found in the room with the open hose end uncovered (not bagged/taped), contrary to PPM 1.3.63. (see photo in EDMS) â€¢ This is the vacuum found in Room T112 the previous morning (see AR-CR 394487) in the same condition with the open suction hose end uncovered, and then had the end covered with red duct tape by an HP Technician after notification by Quality. Insights: â€¢ It appears the vacuum had been used because an HP Technician covered the suction hose inlet opening with red duct tape yesterday morning, but the open hose end was uncovered today. <I> **** Actions Taken **** Contacted an HP Craft Supervisor, the Chemistry/Rad Services Manager, and the Turbine Project Manager. . Recommend routing to Reactor Major Maintenance. . This Deficiency was identified during the R-24 Outage Surveillance SR-19-01.
394562 | CR | 20190530 |  | 3 | (QA)OI-20 Qualification/Procedural Discrepancy for Refuelers |  |  |  | Y | NO | <D> **** Detailed Description **** Step 2.7.2 of OI-20, Fuel Handling Expectations, specifies that three individuals will be on the refuel bridge during refueling activities. One individual must have RFAE, Core Alt. Supervisor, qualification and the other two must have RFAA or RFAD, Refueling Floor Operator or Fuel Handling Operator, respectively. The step also specifies that one of the RFAA or RFAD individuals will be a phone talker. Currently, Columbia utilizes the RFAE (Core Alt. Supervisor) as the phone talker and that individual is not RFAA or RFAD qualified. The intent of the step, however is met as there are three qualified individuals on the bridge and one of them is in direct contact with the Main Control Room as the phone talker. Recommend action to Operations for a procedure revision to clarify the step. <I> **** Actions Taken **** Discussed with Reactor Maintenance and Operations Manager.
394563 | CR | 20190530 |  | 3 | E-BUS-NONSEG/S/Y bus housing damage | N | N |  | N | YES | <D> **** Detailed Description **** During inspection of the non segregated bus E-BUS -NONSEG/S/Y a section of the bus housing at location D64-65 was found deformed at the top of the bus. The bus is bent in toward the conductors resulting in the housing being closer to the bus conductors than allowed. The bus housing needs to be repaired to restore the air gap between the conductors and the housing. <I> **** Actions Taken **** Discussed with Williams electricians and EOC <N> **** Equipment Description **** D64-65 . See EDMS for pictures of the condition | 02-00-E-BUS-NONSEG/S/Y
394564 | CR | 20190530 | CAQ | D | NSSE-EQ-8, Damaged Grapple Power Cable | Y | Y |  | N | YES | <D> **** Detailed Description **** The Grapple Engage light extinguished when lowering a fuel assembly into the core stopping mast movement. Troubleshooting identified a damaged Grapple Power Cable. <I> **** Actions Taken **** Informed OCC, Refuel Floor Supervisor, Reactor Engineering, Westinghouse/PaR, NSSE System Engineer. Manually raised grapple with fuel assembly to a sufficient height to traverse to the Spent Fuel. Placed fuel assembly in original location. <N> **** Equipment Description **** RB606 | 02-00-NSSE-EQ-8
394565 | CR | 20190530 |  | 3 | Cannot perform TMOD SharePoint INSTALLATION guidance |  |  |  | N | NO | <D> **** Detailed Description **** For Temporary Modifications (TMOD), INSTALLATION of TEMPORARY MODIFICATIONS guidance is provided in SharePoint and referenced by ENG-DES-50 that Portal J will not allow the TMOD preparer to perform (perhaps because not all TMOD preparers have the same Portal J mojo). See the guidance mark-up attached to the EDMS of this AR CR. Could not perform the bullets directing checking the M111 'Review Required' box or setting the M111 'Control Room Communications' field. Please correct the TMOD SharePoint INSTALLATION guidance. <N> This guidance deficiency was noted while attempting to perform the direction for TMOD EC 17792.
394566 | CR | 20190530 |  | 4 | R-24 Lessons Learned (LL) East Smoking Area during Outage |  |  |  | N | NO | <D> **** Detailed Description **** Siemens workers were working on the east end of the Turbine Building last night on the TGB 441'& 501'. The east TGB 441' Crane Bay Doors are open, and cigarette and cigar smoke were entering the building causing discomfort and allergic reactions per Siemens personnel. Recommend moving the Designated Smoke area to a different location during scheduled outages. <I> **** Actions Taken **** I will provide the CR information to Siemens workers as they had expressed their concern to EN Safety.
394567 | CR | 20190530 |  | 4 | RCC-V-6 failed to Auto-close when expected | N | Y |  | N | YES | <C> Changed from CAQ to nonCAQ as per the MRT. <D> **** Detailed Description **** On 5/30/19, during the performance of OSP-INST-B703 Section 7.4, RCC-V-6 failed to auto-close as expected when less than 2 RCC pump breakers were closed. During the test setup, 3 RCC pumps were running in anticipation of the trip of pumps powered by SL-81. When the Fire remote transfer switch was taken to the emerg position, RCC-P-1B & C tripped as expected. RCC-V-6 should have close based on less than 2 RCC pump breakers closed, but was found open on inspection. Closed RCC-V-6 with CRS concurrence, and re -opened on restoration of RCC pumps. With the recent issues with RCC-CB-P/1B and 1C, suspect the problem may be with the breaker position switches. <I> **** Actions Taken **** Took action to close RCC-V-6, informed CRS/SM | 02-00-RCC-V-6
394568 | CR | 20190530 | CAQ | C | RHR-CB-P/2C green open socket broken | Y | Y |  | N | YES | <D> **** Detailed Description **** broken 24E bulb socket for RHR-CB-P/2C. . suggest an EVAL also be made up to replace all these sockets due to the high number of failures of this model. E-CB-41F 24e sockets were replaced with 1835 lamp sockets by an Engineer (54113) in the past - perhaps that would be a good place to start looking for design change data. This is the same issue for both air removal pumps indications and can (and does) result in a ground to the control power circuit. In this case it would impact safety related equipment and with multiple sockets involved could prevent breaker operation. The 24e bulbs are stamped material and the sharp edge of the metalic contacts on the bulb hang up in the socket and pressure breaks the insulator ejecting the resistor which has the wires connected. This issue can not be resolved since it is a manufacturing process NOT OURS <N> Name Removed from CR. Created AR EVAL 396052 for potential design change. | 02-00-RHR-CB-P2C
394569 | CR | 20190530 | CAQ | D | DEH-TK-1C low pressure | Y | Y |  | N | YES | <D> **** Detailed Description **** DEH-TK-1C indicates approximately 700 psig and must be greater than 1150 psig to support DEH system startup. This is a repeat issue; this accumulator had maintenance performed in May 2018 for the same issue. <I> **** Actions Taken **** Wrote this CR and informed system engineer and OCC. <N> cancelled by mistake. reopened and taken to complete | 02-00-DEH-TK-1C
394570 | CR | 20190530 |  | 3 | Editorial change to TSP-CRD-C101 |  |  |  | N | NO | <D> **** Detailed Description **** In the latest revision of TSP-CRD-C101 dated 4/19/19, a number of step sign-off blocks were inadvertently removed from the procedure sections 7.2, 7.3, and 7.5. Request sign-off blocks be added back into the procedure to allow operators to step track the procedure. In the meantime, circle/slash step tracking will have to be utilized. <I> **** Actions Taken **** Notified SM.
394571 | CR | 20190530 | CAQ | C | RRC-V-13B exceeds as left leak rate admin limit | Y | N |  | N | YES | <D> **** Detailed Description **** RRC-V-13B as left leak rate measured at 4970 sccm at 38.6 psig test pressure. The measure leak rate exceeded the admin limit of 150 sccm. Test performed per TSP-RRC/X43B -C801 via WOT 02033547-07. <I> Verified test setup correct. Snooped all test connections no indication of leaks. Verified boundary valves close tight. Notified LLRT SRO, OCC and EOC. | 02-00-RRC-V-13B
394572 | CR | 20190530 |  | 3 | ALARA Task for DW permanent shield boxes exceeded estimate |  |  |  | N | NO | <D> **** Detailed Description **** Alara Task 02120897 01 01 has exceeded its revised estimate by .361 Rem and its original dose estimate by 1.634 Rem. As a contributing factor, during the planning phase there were additional workgroups that were not accounted for in the dose estimate. In addition, the amount of supervision required was not adequately addressed. <I> **** Actions Taken **** Notified RP supervision and OCC Revised the estimate to account for remaining work scope Initiated this CR
394573 | CR | 20190531 | CAQ | D | SGT-FN-1A1 start on RPS B transfer again. | Y | N |  | N | YES | <D> **** Detailed Description **** RPS B transferred to alt. After ~10 sec noted SGT-FN-1A1 and SGT-EHC-1A1 (all 3 stages) started. SGT-V-5A1 did not reposition. After NSSSS reset. SGT-EHC-1A1 taken to ptl and back to auto. After ~10 sec SGT-FN-1A1 and SGT-EHC-1A1 restarted. After RC-1 reset SGT-EHC-1A1 taken to PTL and back to auto. SGT-FN-1A1 AND EHC-1A1 remained off. | 02-00-SGT-FN-1A1
394574 | CR | 20190531 |  | 4 | E-BUS-NONSEG/S/Y insulator chips | N | N |  | N | YES | <D> **** Detailed Description **** Four insulators were identified as having chips in them and should be replaced. The locations are SY-9 C phase, SY-12 B phase and SY-14 B and C phase. <I> **** Actions Taken **** Recommended replacement of insulators. <N> **** Equipment Description **** TG 441' | 02-00-E-BUS-NONSEG/S/Y
394575 | CR | 20190531 |  | 3 | R24LL: SOP-CN-SHUTDOWN enhancements |  |  |  | N | NO | <D> **** Detailed Description **** Revise the drain section for add additional vent paths for venting residual N2 See EDMS for recommended added steps/instructions highlighted in yellow.
394576 | CR | 20190531 |  | 4 | Smoke in CRD Pump Room due to COND-P-4 | N | N |  | N | YES | <D> **** Detailed Description **** COND-P-4â€™s front bearing has failed, resulting in grey smoke throughout the CRD pump room in the RB 422. The MCR received E-FCP-1 3-3 RX BLDG 422/441 FAN/PUMP ROOMS annunciator at 0244, this was followed by a CRD pump room manual pull station activation and simultaneous watch stander reports of smoke in the CRD pump room at 0249. The fire brigade responded and at 0258 the fire brigade leader reported that COND-P-4â€™s bearing had failed resulting in the smoke and damage to the paint on the pump. At no time did anyone witness a visible flame. <I> **** Actions Taken **** Notified MCR and Fire Marshall. Entered ABN-FIRE. Evacuated the Reactor Building. | 02-00-COND-P-4
394577 | CR | 20190531 | CAQ | D | MS-RV-3D Broken connector | Y | Y |  | N | YES | <D> **** Detailed Description **** While electricians were performing WO #02112566-04 step 4.9, they found a broken connector on the SRV actuator solenoid valve "C" <I> **** Actions Taken **** Craft stop work on SRV actuator solenoid valve "C" on MS -RV-3D notified supervision, OCC and EOC. Initiated CR. Notified Planning need to add steps in the task for ordering and replacing the broken connector. <N> Work instructions have been updated with steps to order and replace broken connector. | 02-00-MS-RV-3A
394578 | CR | 20190531 | CAQ | D | Insulation Inspection In Drywell WO 02108865-01 | Y | Y |  | N | YES | <D> **** Detailed Description **** Engineering inspection of the drywell identified the following areas of deteriorated or displaced insulation. *Azimuth 270 deg. elev. 509 insulation falling off bottom of pipe at RHR-V-50B. *RFW pipe at 90 deg. azimuth , elevation 563' blanket insulation has slid down piping, exposing the internals of the reflective insulation above .*RFW pipe at 270 deg azimuth, elevation 546' reflective insulation damaged from standing on the insulation. ** None of these deficiencies will impact the design function of any equipment and will not prevent proper drywell cooling ** <I> **** Actions Taken **** Notified the EOC System Engineering Manager WO exists from R23 but no actions have been taken in R24 to make repairs WO 02113357 . RHR location is immediately downstream of RHR-V-50B - the pipe clamp is for support RHR-SB-33. Reference CVI 215 -00,14247, CVI 215-00,14242, and CVI 215-08,13638. Insulation drawing for this piping is CVI 250-00,363 - added applicable EPN cross-references (RHR-V-50B & RHR-V-112B). Per CVI 250-00,363 the uninsulated area of the pipe clamp (RHR-SB-32/33) should have pad insulation installed. RFW location at 90 deg Az is likely CVI 250-00,77 but there isn't pad insulation up high - pad insulation is lower. RFW location at 270 deg Az is likely CVI 250-00,80. CVI 1131 -00,12 page 5 has a picture from 2009 of a radworker standing on this reflective insulation. <N> **** Equipment Description **** Drywell Insulation
394579 | CR | 20190531 | CAQ | B | Dose Rate Alarm due to Unposted High Radiation Area |  |  |  | N | NO | <C> RISK: Medium. CAUSE: Complex. Severity: B, Investigation Template Required. Potential NCV <D> **** Detailed Description **** A dose rate alarm occurred on Reactor 606â€™ during decontamination of the Hawkeye IVVI track. Worker stopped and notified RP. Investigation ongoing. <I> **** Actions Taken **** A dose rate alarm occurred on Reactor 606â€™ during decontamination of the Hawkeye IVVI track. Worker stopped and notified RP. Investigation ongoing. <N> On 5/31/19 an individual received an electronic dosimeter (ED) dose rate alarm while working on the reactor building 606' refuel floor. The individual was deconning a highly contaminated component and disposing of the decon rags in a nearby radioactive material (RAM) bag. The accumulation of decon rags raised the dose rates in the bag to a point that exceeded the worker's ED dose rate alarm setpoint. This activity had been approved and was overseen by radiological services personnel who should have recognized the error-likely situation.
394596 | CR | 20190531 |  | 4 | R24LL - Operator Just In time training |  |  |  | N | NO | <D> **** Detailed Description **** The JITT is not integrated with the outage schedule. The training can occur any time and should be well planned out. During this outage, it has been planned during Ops critical path work causing job owners to be reassigned a few days before executation. This is not consistent with risk management is core business as it adds risk to divisional LSFT testing. I recommend next outage that JITT be scheduled as part of an integrated plan so we can better plan and minimize risk. <I> **** Actions Taken **** Lessons Learned CR for R25.
394597 | CR | 20190531 |  | 3 | Cancellation process for SDP EC Product Types |  |  |  | N | NO | <D> **** Detailed Description **** TMOD EC 15945 is APPROVED status (since 09/08/16) but was a contingency associated with AR CR 353783 that was never implemented and needs to be cancelled. For EC cancellation, ENG-DES-50 sends you to SharePoint guidance which sends you to DES-2-14. Because EC 15945 is APPROVED status, DES-2-14 directs that the EC should be revised per DES-2-15 and then cancelled per DES-2-14. However, DES-2-15 states that it is not applicable to Standard Design Process (SDP) EC Product Types (such as TMOD EC 15945) and sends you back to ENG-DES-50 to perform the revision. ENG-DES-50 sends you to IP-ENG-001 and SharePoint guidance to perform the revision. The SharePoint guidance for EC REVISIONS requires you to process an FCR and then initiate the EC Revision in the EC module. This currently directed process is ridiculously cumbersome for what should be a simple action (particularly for TMOD EC 15945. <N> Upon further examination, TMOD EC 15945 was not an SDP product and can be cancelled via the pre-SDP EC cancellation process. Regardless, the cumbersome nature of the SDP EC product cancellation process remains and should be addressed.
394598 | CR | 20190531 |  | 3 | HD-LCV-6A2 REGULATOR leaking | N | N |  | N | YES | <D> **** Detailed Description **** WR# 29148680 verified the regulator is leaking on HD-LCV-6A2. <I> **** Actions Taken **** Supervisor has talked to Mike Rhodes who wants to remove the regulator at HD-LCV-6A2 due to there being a regulator on IR-9 which also supplies the valve so the one on the valve is a second one which is not needed | 02-00-HD-LCV-6A2
394599 | CR | 20190531 |  | 4 | TSW piping needs to be replaced | N | N |  | N | YES | <D> **** Detailed Description **** During the new TO-HX-1A inlet/outlet head fit-up job under WO 02111477-25, pipefitters found that the two TSW inlet/outlet pipe spools are degraded and it is not advisable to do any weld job on them due to their deteriorated walls. Therefore, these spools (~3 ft. each) have to be replaced with new ones. <I> **** Actions Taken **** Discussed with the EOC and mechanical planner who is revising the WO tasks to include steps required to replace the spools with new ones. | 02-00-TO-HX-1A
394600 | CR | 20190531 |  | 3 | RW 542' ROOF DRAIN COVERS DEGRADES | N | N |  | N | YES | <D> **** Detailed Description **** Covers to four of the roof drains on the 542' EL RW roof were discovered to be degraded during roof replacement work. Pictures are posted to EDMS. <I> **** Actions Taken **** Notified OCC & EOC. | 02-00-W-BLDG-MISC
394601 | CR | 20190531 |  | 3 | R24 LL TSP-SLC/ISI-R801 and MCP-SLC-B101 not Coordinated |  |  |  | N | NO | <D> **** Detailed Description **** TSP-SLC/ISI-R801, the SLC System Pump Discharge Piping Leakage Test, requires the SLC piping to be pressurized from SLC-V-4A to HPCS-V-76. To accomplish this, the work package (02112266) requires this test be coordinated with the performance of MSP-SLC-B101 (Work Package 02111504) which pressurizes the piping for a leak inspection of the newly installed squib valve. Unfortunately, Work Package (WP) 02111504 didnâ€™t contain any instructions to coordinate with WP 02112266, and the work was completed, and the piping depressurized before TSP-SLC-R801 could be performed. A search of the TSP-SLC/ISI-R801 surveillance history showed that this same mistake had been made last outage as well (WP 02043545) requiring the addition of task 03 to the package to re-establish the required test conditions. The same task will now have to be added to WP 02112266 as well. In the future, instructions should be added to the MSP-SLC-B101 work package to ensure that notification is made to engineering to perform TSP-SLC/ISI-R801 when the SLC piping is pressurized under Attachment 9.3 of the MSP. In addition, the work package shouldnâ€™t be closed out until after the TSP inspections are complete.
394602 | CR | 20190531 |  | 4 | R24 LL - 75 kip Snubber Test bench clevis needs machined |  |  |  | N | YES | <D> **** Detailed Description **** The clevis on the piston end of the 75 kip snubber test bench needs machined to match the rear clevis so that PSA-10 size snubbers no longer need to be tested with a special adapter. This will reduce the number of QC callouts for torque verification during reassembly of the transition tubes to the snubber. snubber <I> **** Actions Taken **** Wrote LL CR and generate WR. <N> **** Equipment Description **** TG 471 West end Snubber Cage
394603 | CR | 20190531 |  | 3 | Revise calc E/I-02-93-04 |  |  |  | N | NO | <D> **** Detailed Description **** CMR policy per DES-4-1 (rev 24) states that a maximum of 5 CMRs with "modified" status may be outstanding against any calculation. When a 6th CMR goes to "modified" status, initiate an AR assignment to complete the calculation revision within 180 days. Calculation E/I-02-93-04 has 6 CMRs in â€œmodifiedâ€ status. This CR is for trending only and does not impact any plant SSCs. <I> **** Actions Taken **** initiated this CR
394604 | CR | 20190531 |  | 4 | TSW-PCV-20; non functional, broken actuator to valve link | N | N |  | N | YES | <D> **** Detailed Description **** During a reinvestigation of a known packing leak it was identified that the actuator to valve link was broken/seperated . This renders the valve inoperable. It appears that the manual overide link could have contributed to the break. See attached pictures in EDMS. Recommend complete valve & actuator removal and overhaul. <I> **** Actions Taken **** Notified OCC, AOV program manager and planning Recommend using exiting WO#02120309 and associated OSCR 394417. <N> **** Equipment Description **** Aux Boiler room | 02-00-TSW-PCV-20
394605 | CR | 20190531 |  | 4 | TSW-PCV-20 broken actuator arm â€“ impacts Start-up | N | N |  | N | YES | <D> **** Detailed Description **** The actuator arm for TSW-PCV-20 has broken off, likely due to cyclic fatigue. TSW-PCV-20 is currently being controlled using the manual handwheel mechanism. TSW-PC-20 is in Manual to prevent the valve actuator from cycling. TSW-PCV-20 is currently being throttled via the Manual handwheel mechanism to maintain Turbine Building TSW pressure at 104PSIG. Scaffolding will be required to obtain access to TSW-V-44 (TSW-PCV-20 Bypass) to allow isolation of TSW-PCV-20 for maintenance. This repair should have a high priority, as Manual control of TSW header pressure will become more difficult as TSW systems are restored. Note: standby TSW pump has auto start function on low TSW header pressure. See EDMS for pics <I> **** Actions Taken **** Informed MCR took manual control of TSW-PC-20 <N> **** Equipment Description **** TG 441 aux blr room | 02-00-TSW-PCV-20
394606 | CR | 20190531 |  | 3 | No EPN label for DW-FT-1 visible from floor. | N | N |  | N | YES | <D> **** Detailed Description **** A new flow transmitter and indicator were installed by EC 12510 - W/O 02095007. A label request was made, but only the CW-FI-1 label is visible. <I> **** Actions Taken **** wrote CR. NO IMPACT ON EQUIPMENT FUNCTION. | 02-00-DW-FT-1
394607 | CR | 20190531 |  | 4 | Leakby impacting CRD work | N | N |  | N | YES | <D> **** Detailed Description **** While preparing to work CRD-V-47A and CRD-FCV-2A leakage was noticed downstream CRD-V-54. Leakage is in excess of 1gpm. <I> **** Actions Taken **** Isolation valves were checked fully shut, this reduced leakage by approx 30%. Further isolation is recomended, Isolating the CRD-V-103/XXXX valves for the HCUs is recomended to fully isolate the leakby. | 02-00-CRD-V-47A
394608 | CR | 20190531 |  | 4 | E-MC-1A, switch won't close | N | N |  | N | YES | <D> **** Detailed Description **** While performing PMT on HD-MO-20A per WOT 02114720-06, the switch on the motor starter at E-MC-1A will not move to its closed position. <I> **** Actions Taken **** Notified valve team and initiated this CR. Contacted FIN team. | 02-00-E-MC-1A
394609 | CR | 20190531 |  | 4 | Scaffold required for TSW-V-44 | N | N |  | N | YES | <D> **** Detailed Description **** Scaffolding is required to access TSW-V-44, in support of TSW-PCV-20 repair (ref. AR# 394605). This valve is located in the Aux Boiler room, ~ 20ft above TSW-PCV-20. TSW-V-44 will be required to be throttled, as needed to maintain TSW header pressure. <I> **** Actions Taken **** informed MCR <N> **** Equipment Description **** TG 441 Aux Boiler room | 02-00-TSW-V-44
394610 | CR | 20190531 | CAQ | D | Minor wear found during shroud head bolt examinations | N | N |  | N | YES | <D> **** Detailed Description **** During the R24 examination of the steam seperator, indications of contact and wear were noted on 7 of the 36 shroud head bolts (see Indication Notification Report INR CGS-19-06 in EDMS). The wear is located at the interface between the bolts and the upper ring. This is a typical contact area where rubbing and fretting is not unusual. The bolts are non-safety related and serve to lock the steam seperator onto the core shroud. The fretting does not adversely affect the bolts which are fully qualified to perform their intended function. This CR is initiated for monitoring and trending only. Similar indications were reported in R22 (ref CR 330125). <I> **** Actions Taken **** All thirty-six shroud head bolts were examined. Recommend trend only. The bolts are fully qualified to perform its intended function. There is no risk of lost parts or debris. This is not a sart up restraint. | 02-00-MS-RPV-3
394611 | CR | 20190531 | CAQ | C | SW B pump step change in pump performance OSP-SW/IST-Q702 | Y | N |  | N | YES | <D> **** Detailed Description **** SW B pump step change in pump performance was noticed during OSP-SW/IST-Q702. After completing the OSP-SW/IST -Q702 for WO#02111475 following system maintenance the SW B system it was noted that the SW-P-1B went from above the reference curve to below the reference curve. System flow dropped from 9658.8 gpm to 9565.3 gpm with system pressure going from 215 psig to 210 psig. These values are still above both the action and alert range and this CR is only for trending purposes. <I> **** Actions Taken **** Wrote CR | 02-00-SW-P-1B
394612 | CR | 20190531 | CAQ | D | R24 Jet Pump Wedge and Set Screw Monitoring |  |  |  | N | YES | <D> **** Detailed Description **** During R24, IVVI examinations of the jet pump main wedge, set screws, and auxiliary wedges were performed including measurement of the set screw gaps. The results from this outage are documented in indication notification report INR-CGS-19-02, -07, -09, -11 see EDMS. The wedges and auxiliary wedges are in satisfactory condition showing only minor wear and movement and are fully qualified to perform their design functions. Additionally, the set screw gaps are within the allowable limits of TM-2144 with the exception of JP-9 which is addressed under CR 393826. This CR is initiated for monitoring and trending. <I> **** Actions Taken **** Recommend trend only. The components are fully qualified to perform their intended function. This is not a sart up restraint. | 02-00-MS-JP-1,02-00-MS-JP-10,02-00-MS-JP-11,02-00-MS-JP-12,02-00-MS-JP-13,02-00-MS-JP-14,02-00-MS-JP-15,02-00-MS-JP-16,02-00-MS-JP-17,02-00-MS-JP-18,02-00-MS-JP-19,02-00-MS-JP-2,02-00-MS-JP-20,02-00-MS-JP-3,02-00-MS-JP-4,02-00-MS-JP-5,02-00-MS-JP-6,02-00-MS-JP-7,02-00-MS-JP-8,02-00-MS-JP-9
394614 | CR | 20190531 | CAQ | D | CMS-RE-27F and CMS-RE-27E as-found installation discrepancy | Y | Y |  | N | YES | <D> **** Detailed Description **** Per conversation with FIN Team personnel, the connections between the CMS-RE-27F Electric Conductor Seal Assembly (ECSA) SEAL BODY (CVI 349-00,1,1 R0 Item 1) and MIDLOCK CAP (CVI 349-00,1,1 R0 Item 2) were found only finger tight when disassembled during R24. Per the IPS-780 Rev B Conax installation manual, these connections (which compress the MIDLOCK FERRULE - CVI 349-00,1,1 R0 Item 3), should have been installed torqued to 220-250 ft-lbs for our 1.00 DIA. FEEDTHROUGH (reference CVI 349-00,1,1 R0). Per CVI 349-00,1,1 R0 NOTE 6 this connection is shipped finger tight and is to be installed per Conax procedure IPS-780 per CVI 349-00,1,1 R0 NOTE 4. FIN Team personnel also indicated that a similar condition was also found during R24 disassembly of these connections for the CMS-RE-27E ECSAs except that these connections for 27E were found snug-tight (~30 ft-lbs torque) rather than only finger tight. <I> **** Actions Taken **** Initiated this AR CR 394614 to document these as-found conditions and notified the EOC. | 02-00-CMS-CONN-27E/HV,02-00-CMS-CONN-27E/SG,02-00-CMS-CONN-27F/HV,02-00-CMS-CONN-27F/SG,02-00-CMS-RE-27E,02-00-CMS-RE-27F
394615 | CR | 20190531 | CAQ | C | CVI SPC 01-00,163 series does not apply to CGS |  |  |  | N | NO | <D> **** Detailed Description **** CVI SPC 01-00,163 sheets 1A through 1N (Westinghouse drawing 830A561) do not apply to the CGS main turbine and should be removed from CVI. A Siemens representative confirmed that the CVI applies to the WNP-1 main turbine and not to CGS. The relevant spec for CGS is CVI SPC 01 -00,140. <N> This is a documentation issue only.
394616 | CR | 20190531 |  | 3 | PPM 10.25.202 references CATID 25879 incorrect insulators | N | N |  | N | NO | <D> CATID 25879 is for 3 1/2 inch tall insulators for E-BUS -NONSEG\S\Y. These insulators are the correct height but do not have the correct bolt pattern for the bus, the bottom 3/8 inch bolts are 3 inches apart and should be 2 inches apart (reference PPI 10.25.202 pg 49). These insulators will work for 4 inch square conductor and 6 inch square conductor since both use the center connection but not for the 8 inch Y bus which uses the 2 inch on center perimeter connections. CATID 68800046 is the correct CATID for E-BUS-NONSEG\S\Y. The procedure should be updated to reference the correct insulator CATID. <I> Discussed with craft and EOC, went to the warehouse and found the correct insulator, cleared a user hold on CATID 68800046and delivered the correct insulator to the craft for installation. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review. Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
394619 | CR | 20190531 | CAQ | D | Minor witness marks found jet pump sensing lines | Y | N |  | N | YES | <D> **** Detailed Description **** During the R24 examination of Jet Pump Loop B sensing Line Exit Bundle, indication of contact and movement were noted on the sensing lines (see Indication Notification Report INR CGS-19-12 in EDMS). The indications are located on the top of each sensing line where the lines pass through the bundle bracket and are approximately 1/8â€ long. They appear to be single contact marks that likely occur during RRC start-up or shutdown. The sensing lines are non-safety related and serve to provide jet pump flow information. The contact marks do not adversely affect the sensing lines which are fully qualified to perform their function. There is no indication that the marks could lead to a potential failure of the sensing line This CR is initiated for monitoring and trending only. <I> **** Actions Taken **** Recommend trend only. The sensing lines are fully qualified to perform their intended function. There is no risk of failure or lost parts. This is not a sart up restraint. Similar indications can be seen on the A loop in the R19 video. | 02-00-MS-JP-1,02-00-MS-JP-10,02-00-MS-JP-11,02-00-MS-JP-12,02-00-MS-JP-13,02-00-MS-JP-14,02-00-MS-JP-15,02-00-MS-JP-16,02-00-MS-JP-17,02-00-MS-JP-18,02-00-MS-JP-19,02-00-MS-JP-2,02-00-MS-JP-20,02-00-MS-JP-3,02-00-MS-JP-4,02-00-MS-JP-5,02-00-MS-JP-6,02-00-MS-JP-7,02-00-MS-JP-8,02-00-MS-JP-9
394620 | CR | 20190531 |  | 3 | R24 LL: UNABLE TO COMPLETE COATING TASKS |  |  |  | N | YES | <D> **** Detailed Description **** R24 LL: UNABLE TO COMPLETE SERVICE LEVEL 1 COATING TASKS . Three R24 WO tasks are unable to be completed due to lack of adequate procedural guidance for use of required application equipment. PPM 10.2.14 does not contain an Application Process to apply the currently available service level 1 coating. . <I> **** Actions Taken **** Notified OCC. Notified Coating Program Engineer. <N> Minor Rev 001 to Major Rev 030 for PPM 10.2.14 was issued on 5-30-19 in order for the coatings tasks to be completed.No further action required. | 02-00-C-TK-1
394622 | CR | 20190531 |  | 4 | Hand Injury in DW |  |  |  | N | NO | <D> **** Detailed Description **** An individual received a hand injury in the DW. <I> **** Actions Taken **** Individual was frisked and sent to Occupational Health. Notified the applicable supervisor, left message for industrial safety, and notified occupational health.
394623 | CR | 20190531 |  | 4 | RB SW Elevator 441 Button not working | N | N |  | N | YES | <D> **** Detailed Description **** The reactor building elevator 441 button is not always working when pressed. The elevator operator reports they have been selecting 422' from the 606' elevation to get the elevator to go down. <I> **** Actions Taken **** notified maintenance. <N> **** Equipment Description **** RB SW Elevator
394624 | CR | 20190531 |  | 3 | Contract individual injured hand during rigging activities |  |  |  | N | NO | <D> **** Detailed Description **** An individual working for Crane Nuclear (org code 52238) injured hand during rigging activities. The individual was assisting the maneuvering of the hard seat for RFW-V-10A when the webbing of his left hand between his thumb and index finger caught between the 200 pound disc and a piece of angle iron in the drywell. <I> **** Actions Taken **** Individual exited the drywell and reported with supervision to OCC health for evaluation. Rx and Major Maintenance Manager and control room have been notified. OI-34 complete. <N> All required PPE was worn during the evolution. After discussions with Crane the hard seat that was being moved was for RFW-V-10B
394626 | CR | 20190531 | CAQ | C | FME issue on MS-V-22A | Y | N |  | N | YES | <D> **** Detailed Description **** While performing ESP-MSIV-B301 on MS-V-22A, electricians dropped a lock washer and it fell below. There were no open systems below so the lock washer did not enter an open system. <I> **** Actions Taken **** Generated a limitations on use task in 02111886-01 to replace the lock washer with a peer verified quality class 1 lock washer. <N> **** Equipment Description **** MS-V-22A linkage arm | 02-00-MS-V-22A
394627 | CR | 20190531 | CAQ | C | PSR-V-X73/1 SPV spacer dropped in drywill, not recovered | Y | N |  | N | NO | <D> **** Detailed Description **** PSR-V-X73/1 SPV spacer dropped in drywill, not recovered. Spacer is item 6 in the part dwg. Spacer is like a ring collar. ~ 1/4" thick, 5/8 dia with a 1/4 hoke in the center. <I> **** Actions Taken **** Created task 02093901-12 to make a new one. Extras should be made and put in stores and add to the BOM. attempt to retrieve was made by the Dry well cordinators, but was unsuccessful. Engineering needs to evaluate this condition.
394629 | CR | 20190531 |  | 3 | Narrative logs from Dataglance failing to transfer to eSOMS |  |  |  | N | NO | <D> **** Detailed Description **** The interface logic that transfers FWC logs from Dataglance to eSOMS is encountering duplicate data causing the entire data transfer to abort at each occurrance. <I> **** Actions Taken **** IS Analyst contacted. Work around put in place to correct the immediate impact to WO.
394630 | CR | 20190531 |  | 3 | Debris and Silt Found on CW Inlet Tunnel Floor | N | N |  | N | YES | <D> **** Detailed Description **** During a remote underwater camera search for foreign material dropped in the main condenser (COND-HX-9) inlet water box 'A' on 05/30/19, various debris was found at the bottom of the CW intake tunnel. The debris appeared to be beneath silt that had accumulated on the floor of the tunnel and when areas of silt were remove as part of the foreign material retrieval efforts, this debris was exposed. The intake screens in the CW pumphouse have been known to allow debris past the screens as is evidenced by the foreign material found in the COND-HX-9 water boxes during refueling outage as-found inspections. The most common materials found are plastic parts from the cooling towers (fill clips, pieces of fill, drift eliminators). The next most common foreign material found is rusted metal that has sloughed off of steel surfaces in the circulating water pumphouse structures and piping. Most of this rusted metal material is from surfaces downstream of the CW pump intake screens. This plastic and metal material is the material that was also seen at the bottom of the CW inlet tunnel. The material either fell to bottom of the tunnel flow when flow was stopped or was caught in an eddy at the bottom of the tunnel and remained there during operation. This material found at the bottom of the CW inlet tunnel will not prevent the main condenser from performing its design functions. The material might enter the main condenser water box where it would pass through the condenser; become lodged in a tube; or settle to the bottom of the waterbox where it might be caught in another eddy. The worst case here would be that the material is caught in a tube where it would restrict flow or cause a tube leak. A flow restriction would cause a miniscule reduction in heat transfer function due to the large overall surface area of tubes that remain unobstructed. Tube leaks as a result of plastic or rusty metal debris is not likely due to the hardness of the titanium tubes and a history of finding these materials lodged in tubes without tube damage occurring. <I> **** Actions Taken **** Notified the System Engineering EOC Manager | 02-00-COND-HX-9
394631 | CR | 20190531 | CAQ | D | RHR Loop C Void detected during performance of WO 02112554 | Y | N |  | N | YES | <D> **** Detailed Description **** An Air/Gas Void was detected with ultrasonics at Location # 4. This location is on the RHR Loop C Crosstie and Condensate Fill (CVI 215-00,3125). The Void width is a 6" arc across the top of the pipe outer surface, with a length of 72.7 feet. This information was delivered to EOC for evaluation. <I> **** Actions Taken **** Notified Ops (OPS Support Spec V) Notified EOC (Engineering Supervisor) Initiated CR Names removed from CR <N> **** Equipment Description **** Loop C Crosstie and Cond Fill line, RHR C and RCIC rooms
394632 | CR | 20190531 |  | 3 | (R24 LL) No FIN Resources Available on Night Shift |  |  |  | N | NO | <D> **** Detailed Description **** There are no FIN resources on nightshift during R24. This has impacted the ability for nightshift to troubleshoot and repair equipment issues that arise on our shift. Recommend for future outages at least one FIN supervisor (or backshift craft supervisor) who is used to working with all craft disciplines and the work request process. Examples of were FIN resources would have been useful are RCC-CB-P/1B and SGT-FN-1A1 issues. <I> **** Actions Taken **** Discussed with OPS outage coordinator, CR to track. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
394633 | CR | 20190531 |  | 4 | DP-S1/4 voltage low OOS |  |  |  | N | YES | <D> **** Detailed Description **** E-DP-S1/4, at TMU, is indicating 120V while its charger is indicating approximately 134 V. There appears to be no load on the bus. Please investigate. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TMU | 02-00-E-DP-S1/4
394634 | CR | 20190531 | CAQ | D | CVB-AO-1K2 needs replacement | Y | N |  | N | YES | <D> **** Detailed Description **** During 02111599-19 mechanics were stroking the rear disc to make adjustments on the CVB-AO-1K1 actuator and found the 1K2 actuator to have leaking pistion seals. The actuator needs replaced and rebuilt for a spare. <I> **** Actions Taken **** notified supervisor | 02-00-CVB-AO-1K1,02-00-CVB-AO-1K2,02-00-CVB-V-1JK
394635 | CR | 20190601 |  | 3 | LLRT air cart broken during testing. |  |  |  | N | YES | <D> **** Detailed Description **** Two different LLRT tests were being performed simultaneously. TSP-RCS-R803 and TSP-SLC/X13-R801. The first is a water test run at ~1000 psig. The 2nd is an air test run at ~38.5 psig. There was only one block valve separating the two test volumes (HPCS-V-76). During testing HPCS-V-76 leaked by causing the water test to overpressurize the air test cart. Instrumentation on the air cart was isolated from the water before it was damaged but the drip leg volumes on the air cart were blown out. Several gallons of water were leaked on to the floor at the R 471 air cart test station. <I> **** Actions Taken **** The tests were suspended and the air cart instrumentation isolated. Test director was informed. HP was called to asess the water on the floor. | 02-00-HPCS-V-76
394637 | CR | 20190601 |  | 2 | PP-7B-C Danger Tagged Breaker Found On |  |  |  | N | NO | <D> **** Detailed Description **** E-CB-PP7BC/15 was found to be in the ON position. This was discovered while performing a temporary clearance lift per 18-19-0051. Clearance order investigation is underway. See EDMS for photos. <I> **** Actions Taken **** Notified MCR and SM.
394639 | CR | 20190601 | CAQ | D | RFW-MO-65A Grease inspection | Y | N |  | N | YES | <C> CR reopened to cross reference additional WR 29149255 and marked completion required box, then taken back to complete <D> **** Detailed Description **** Grease inspection was identified the motor pinion grease as Grade 3. PPM 10.25.4 Section 7.16.2 requires a CR to be generated if the grease is greater than 3. <I> **** Actions Taken **** Grease was inspected for consistency, color, contamination (dirt, wear debris, sludg rust, other particles were observed) , thickness and determined to be acceptable until the next refueling outage (R25). Minor moisture was observed in the motor pinion housing. **WR to refurb actuator** | 02-00-RFW-MO-65A
394640 | CR | 20190601 |  | 4 | Internals found degraded on COND-V-119C | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WO 02042797-01 on COND-V-119C, the initial inspection found valve internals degraded. Disc arm to disc post found with excessive wear to the point of disc rub on the body. <I> **** Actions Taken **** CR generated and contacted EOC <N> **** Equipment Description **** TBG 449 | 02-00-COND-V-119C
394641 | CR | 20190601 |  | 4 | S2-1A Room Lighting Dark - Needs new bulbs |  |  |  | N | YES | <D> **** Detailed Description **** S2-1A Room lighting needs replacement bulbs. Lights are flickering and room is very dimly lit. <I> **** Actions Taken **** N/A | 02-00-E-MC-S2/1A
394642 | CR | 20190601 | CAQ | C | Problems with execution of TSP-SLC/ISI-R801 |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of TSP-SLC/ISI-R801 (PMID 22332-01, WO 02112266) it was identified that the established test conditions were not sufficient to fully perform the required SLC piping inspections. . Task 02112266-03 was generated to replicate the attachments from MSP-SLC-B101 to pressurize the SLC system to perform the VT-2 leakage inspections, however, when reviewing the lineup it was became clear that the instruction were not adequate to fully pressurize all of the ASME class 2 piping that was specified to be inspected. The only portions of ASME class 2 piping that were appropriately pressurized and inspected were the volume between SLC-V-3A/B and SLC-V -4A/B. . All of the ASME class 1 piping, from the squib valves (SLC-V-4A/B) through the drywell portions of the piping up to HPCS-V-76, was appropriately pressurized and inspected SAT using the instructions from task 02112266-03. . Recommended Actions: ISI Program manager to review the TSP-SLC/ISI-R801 and determine the next steps. The remaining piping that needs to be inspected is all class 2 piping, and on the pump side of the squib valves. Separately a review of previous work orders / tests from 2015 (WO 02043545) and 2011 (WO 01181916) should be performed because it appears that the same test conditions were established at that time as well. <I> **** Actions Taken **** CR written, EOC/OCC notified. Requesting determination from ISI Program Manager on next steps. <N> **** Equipment Description **** SLC system
394643 | CR | 20190601 | CAQ | C | R24 LL - No PMT task for MS-POS-V/28A, B, C or D/1 switches | Y | N |  | N | YES | <D> **** Detailed Description **** No PMT task for MS-POS-V/28A, B, C or D/1 switches after they were replaced. There is a PMT task that checks the RPS logic from the MS-V-22's through the 28's which checks the 2 switches and 3 switches and there are checks for the 22A, B, C, and D/1 switches. The switches not PMT's are the open indication for the outboard MSIVs B, C, and D. Outboard MSIVs indicating both OPEN and CLOSED in the Closed Position. <I> **** Actions Taken **** OCC, Engineering, Electrical Supervision informed. Persuing troubleshooting activities. <N> **** Equipment Description **** MS-POS-V/28A, B, C, and D/1's in the Steam Tunnel
394644 | CR | 20190601 | CAQ | D | DG2 DC Fuel pump failure alarm on start/run | Y | N |  | N | YES | <D> **** Detailed Description **** During start of DG2 for OSP-ELEC-M702, recieived DC Fuel Pump Failure alarm 4.DG2.10-2. Verified both DC fuel pumps running with pressures indicated 52 and 51 psi. Alarm setpoint is 26 psi. Unable to determine if DO-PS-5B1 or 5B2 is the source of the alarm. Request maintenance investigate and repair faulty pressure switch. <I> **** Actions Taken **** Discussed with CRS and received direction to proceed with surveillance. Completed actions of ARP. <N> **** Equipment Description **** DG2 room | 02-00-DO-PS-5B1,02-00-DO-PS-5B2
394645 | CR | 20190601 |  | 4 | MS-V-115B - stuffing box steam cut |  |  |  | N | YES | <D> **** Detailed Description **** Packing was removed on MS-MO-115B due to an S4 packing leak. During inspection, the stuffing box was found with a steam leak on the upper end of the stuffing box. Recommend replacing valve in R25. <I> **** Actions Taken **** Revised packing data sheet to install the bushing on the upper end of the stuffing box. | 02-00-MS-MO-115B,02-00-MS-V-115B
394646 | CR | 20190601 |  | 3 | BS-V-8B Shaft bearing is stem cut. |  |  |  | N | YES | <D> **** Detailed Description **** While performing WOT 02110999-01 the shaft bearing on BS -V-8B was found steam cut and in need of replacement. <I> **** Actions Taken **** Initiated CR for tracking. <N> **** Equipment Description **** T488 D3/8.8 | 02-00-BS-V-8B
394647 | CR | 20190601 | CAQ | D | Need to perform a flush on RRC-V-13B |  |  |  | N | YES | <D> **** Detailed Description **** Based on the work perform on the RRC-V-13B check valve a water flush of the valve and associated RRC seal purge line should be performed prior to restart (ref. WR 29149165) . The reason for this flush is two-fold. . 1) Plenty of industry OE exists that following cutting/welding on the RRC seal purge piping a substantial flush of that piping should be performed to prevent a potential foreign material induced RRC seal failure (ref. ICES 301093 at Brunswick U1, ICES 246510 at Oyster Creek, ICES 225490 at Nine Mile Pt 2, and ICES 193485 at Columbia). Both the causes of the Brunswick and Nine Mile Point 2 OE was cutting / welding of one or more components in the RRC seal purge line that resulted in a foreign material induced failure of the Recirc pump seal. 2) Based on the current leak rate failure it is thought that there might be some foreign material on the valve seals preventing a tight closure. A flush of the valve would correct this issue. . Recommended Actions: Perform a thorough flush of the RRC-V-13B valve and surrounding seal purge line as detailed in WR 29149165. <I> **** Actions Taken **** CR written, EOC & OCC notified. Perform a thorough flush of the RRC-V-13B valve and surrounding seal purge line as detailed in WR 29149165. <N> **** Equipment Description **** Drywell | 02-00-RRC-V-13B
394649 | CR | 20190601 | CAQ | D | CRD-V-126/5447 packing leak 20 DPM | Y | N |  | N | YES | <D> **** Detailed Description **** I&C supervisor providing oversight for ISP-RPS-B501 on protected instrument rack H22-P026 observed water leaking from CRD-V-126/5447. He informed me when I discussed the work he was providing oversight for with him and I contacted the lead HCU Mechanic to investigate. This scram inlet valve is leaking at 20 DPM. <I> **** Actions Taken **** Informed HP and initiated the CR/WR to tighten the packing. Informed FIN team manager & supervisor via email. | 02-00-CRD-V-126/5447
394650 | CR | 20190601 |  | 4 | HV-V-31E stem degradation observed |  |  |  | N | YES | <D> **** Detailed Description **** During the re-packing on HV-V-31E, the stem was identified as degraded. | 02-00-HV-V-31E
394682 | CR | 20190601 | CAQ | D | refuel bridge mast support hoist stopped | Y | Y |  | N | YES | <D> **** Detailed Description **** While attempting to unstow the mast on the refuel bridge the hoist that supports the raising and lowering of the mast stopped while lowering after 1 foot of travel. <I> **** Actions Taken **** The vendor performed minor troubleshooting starting with cycling the power and verifying that the plug the hoist is plugged into has power. The plug has power and the motor on the hoist does not have a reset button that was visible. The vendor is going back to review the drawing to move to the next phase in troubleshooting. The bridge was parked back in a safe position. | 02-00-NSSE-EQ-8
394683 | CR | 20190601 | CAQ | D | RHR-MO-53B Diagnostic Testing | Y | N |  | N | YES | <D> **** Detailed Description **** During diagnostict testing, the torque switch was being raised to meet the minimum thrust requirement. Each setting was as expected. When the torque switch was set to the as-found position, degradation was heard and the torque switch did not stop the valve. The data was captured and no weak link was exceeded. It appears the thermals opened. The degradation sound came from the actuator. <I> **** Actions Taken **** Contacted EOC/OCC - Torque switch and spring pack need to be pulled and replaced and additional inspection/trouble shooting required. R24 scope - valve was disassembled and magnesium rotor replaced with an aluminum per design. <N> Actuator was repaired via WO 02112506. A new spring pack and torque switch was installed. The bearing locknut was not tight and the bearing cartridge cap was not properly staked / setscrewed. The bearing cartridge unthreaded which allowed the torqe switch to not engage. See attached pictures in EDMS. The condition was captured with the diagnostic test equipment. The valve and actuator weak links were not exceeded. Actuator Rating = 70,234 lbs Valve weak Link (w/instrument inacc) = 75,570 lbs Test data = Total thrust = 69,940 lbs . WO 02116081 task 06 replaced spring pack and torque switch. Following replacement, A/L Diagnostic test completed SAT. Info obtained from Keith Trappett and WO task 06 closure notes. | 02-00-RHR-MO-53B,02-00-RHR-V-53B
394684 | CR | 20190601 |  | 4 | High SDIV Level Prevents Performance of Bridge Surveillances | Y | N |  | N | YES | <D> **** Detailed Description **** In order to perform bridge surveillances OSP-NSSE-W401 and OSP-NSSE-W402, there can be no other rod blocks in effect. SDIV level is high and there is no air available to operate vent and drain valves due to maintenance in progress. <I> **** Actions Taken **** Walked down issue, reviewed prints and P&ID. Wrote WR 29149200. | 02-00-E-CP-H13/P611
394686 | CR | 20190601 |  | 3 | R24 LL: Ashe Impacts from SM-1 & SM3 outages not understood |  |  |  | N | NO | <D> **** Detailed Description **** Ashe Impacts from SM-1 & SM3 outages not understood and affect multiple organizations. Affected procedures such as, but not limited to, SOP-ELEC-SM3-MAINT & SOP-ELEC-SM3 -MAINT and outage planning must include advance notification and coordination through Unit Coordinators. The following description of the impacts was provided by the Ashe Chief Operator: â€œPer BPA Outage planning and coordination policy for communication equipment: A Three week notice is required. Actual wording is: 14 days prior to the outage week in which the outage is scheduled to start. Ashe station service switching affects communication equipment at Ashe. Communications equipment is on batteries only during station service switching at Ashe. Ashe is the node for two different fiber rings for the BPA communication network. In addition there are two fiber rings between Ashe and CGS which has 500 and 230 Fiber Optic Trip Transfer (FOTT). Therefore station service switching at Ashe must be coordinate in advance with any other communication work on the BPA fiber systems. BPA does not allow communication work on more than one node at a time on a fiber ring. If there are two simultaneous outages on two nodes of a fiber ring then all communications traffic can be dropped. This can impact the entire BPA grid. Communication can be SCADA control, AGC quantities, transfer trip, security circuits, etcâ€¦â€¦. Communication work requests must be evaluate by BPA PSC ORT for impact or possible impact to BPA communication network. (Possible impact is still considered an outage) Additionally Ashe SS impacts: Building fire alarm to Hanford Fire, their techs are available to reset only Mon â€“Thu and off on holidays. Also impacted is NOANET Northwest open access networkâ€ <I> **** Actions Taken **** Discussed with Ashe Cheif Operator and initiated this CR
394689 | CR | 20190601 |  | 3 | R24LL FAC | N | N |  | N | NO | <D> **** Detailed Description **** See EDMS for R24 FAC LL <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
394691 | CR | 20190601 | CAQ | D | grounding wire for IRM-F broken. | Y | Y |  | N | YES | <D> **** Detailed Description **** A grounding wire in IRM-F is broken. See picture for detail. It looks to be grounding the cable swinging arm to the chassis. The main chassis grounding wire is intact. <I> **** Actions Taken **** Engaged supervision. <N> **** Equipment Description **** MCR | 02-00-IRM-DET-2F
394692 | CR | 20190601 |  | 4 | Tubes plugging on COND-HX-5s | N | N |  | N | YES | <D> **** Detailed Description **** After analyzing the data from Eddy Current Testing (ECT) performed on COND-HX-5A and 5B (under WO 02111976 and 02111977 respectively), 4 tubes were identified for plugging on 5A and 8 tubes on 5B due to OD and tubes wear indications. This results in a total of ~8.7% (~271 tubes) tubes plugged on 5A and ~10% (~314 tubes) of the tubes plugged on 5B. Both heat exchangers are still within the plugging limit of 18.3% (302 more tubes could be plugged) calculated by True North study in 2016 (See EDMS). A rough calculation also shows that both heat exchangers are responsible for about 0.5 MWe loss due to current plugging. Actions resulted from the TN study to maintain the HXs integrity and performance are tracked under AR 359281. This CR is for trending purposes and no actions are required. <N> Per discussion with M. Nassaneh, the tubes discussed in this CR have already been plugged in R24; no further field work is needed as a result of this CR. | 02-00-COND-HX-5A,02-00-COND-HX-5B
394693 | CR | 20190601 |  | 3 | Inconsistent EPNs on several CIM transmitters |  |  |  | N | NO | <D> **** Detailed Description **** Several EPNs in Asset Suite for Cycle Isolation Monitoring (CIM) temperature transmitters are inconsistent, duplicated, or erroneous. See EDMS for list of actions needed. <I> **** Actions Taken **** Wrote CR. Spoke with Design Engineering.
394694 | CR | 20190601 |  | 3 | PPCV is no longer reliable. |  |  |  | N | YES | <D> **** Detailed Description **** PPCV is no longer reliable. Several attempt to resolve issue with PPCV did not fix the problem. If any issue with TDAS then we don't have a back up available for us to use then all the surveillance that required Histogram will have to stop. This is not the right time (recovery systems for the outage) for us just to have a single system without a back up. Need to put in the effort to correct the issue. <I> **** Actions Taken **** SM informed. | 02-00-PPC-COMP-8715
394695 | CR | 20190601 | CAQ | D | Small oil leak on top of X1 bushing of E-TR-S | Y | N |  | N | YES | <D> **** Detailed Description **** During removal of tags for O-TRS-LINKS-001, the Reactor Operator identified a small oil leak on the top of the X1 bushing. There is a small accumulation of oil on the top of the bushing and a few drips that have flowed over the sheds to the base of the bushing. The total volume of oil appears to be approximately two teaspoon or less. There was no evidence of long term leaks. <I> **** Actions Taken **** BPA electricians tightened slightly the two fill/vent plugs on the top of the bushings. They cleaned up the oil from the top, sheds and base of the bushing. <N> **** Equipment Description **** On E-TR-S, Startup Transformer | 02-00-E-BUSH-S/X1
394696 | CR | 20190601 |  | 3 | PPM 10.25.179 incorrectly directs use of Penetrox grease |  |  |  | N | YES | <D> **** Detailed Description **** During WOT 02112117-21, E-TR-S: INSTALL LINKS, the BPA electricians questioned the use of Penetrox oxidation inhibitor. The specific application was for installation of flexible links to rigid links, both of which have silvered surfaces. The Transformer Yard Coordinator looked at WOT 02076239-03 which was the last time the links were installed in 2017. At that time the System Engineer noted on the Link Torque Record that section 7.3 of the procedure states that grease is neither needed nor desired. The Link Torque Record on Attachment 9.11 needs to be corrected. <I> **** Actions Taken **** Annotated the Link Torque Record for WOT 02112117-21 to indicate that no grease was required. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications | 02-00-E-DISC-LINK/S/X1,02-00-E-DISC-LINK/S/X2,02-00-E-DISC-LINK/S/X3
394698 | CR | 20190601 | CAQ | D | R-Door-R204 Inside lock handle is off | Y | Y |  | N | YES | <D> **** Detailed Description **** R-Door-R204 inside lock handle is off. Lock handle is held on by a 1/4" roll pin that has brokenHandle is in the airlock by the door. Need to reinstall door lock handle with 1/4 roll pin. <I> **** Actions Taken **** wrot CR and WR | 02-00-R-DOOR-R204
394699 | CR | 20190601 | CAQ | D | HPCS-B1-DG3 monthly battery testing | Y | Y |  | N | YES | <D> **** Detailed Description **** post seal cracks not previously identified on cells 1,4,10,48,and 56. No electrolite leakage, recorded for trending only per ESP-B1DG3-M101. <I> **** Actions Taken **** notified supervisor and initiated CR | 02-00-HPCS-B1-DG3
394700 | CR | 20190601 | CAQ | C | Small chip in limit switch contact assembly block | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing task to extend control and power cables to support diagostic testing of SGT-MO-5B2 on the bench, electricians discovered a minor chip adjacent to the LS 6 contact. The chip does not appear to be a structural deficiency in the overall integrity of the contact assembly. The chip is in the sidewall of the termination point and the actual termination appears robust and unaffected by the chipped sidewall. The deficiency was discovered during WO#02103789-22 <I> **** Actions Taken **** notified Supervisor and generated CR <N> **** Equipment Description **** SGT-MO-5B2 RX-572 *MOV Engineer* The small chip on the limit switch contact assembly block does not impact the operation of the valve/actuator. It is on the outside edge. The chip does not impact the integrity of the limit switch contact assembly block. Recommend action to accept as-is. See attached picture.
394701 | CR | 20190601 |  | 4 | Internals found degraded on COND-V-119B |  |  |  | N | YES | <D> **** Detailed Description **** During performance of WO# 02072876 on COND-V-119B, the initial inspection found valve internals degraded. Disc arm to disc post found with excessive wear to the point of disc rubs on valve body. <I> **** Actions Taken **** Initiated CR on valve condition. <N> **** Equipment Description **** TBG 449 | 02-00-COND-V-119B
394702 | CR | 20190601 |  | 3 | R24LL: SOP-CAS-SHUTDOWN procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** We shutdown the CAS comperessors and str using a temp compressor the shutdown procedure needs to be revised to include secureing the CJW pumps if no CAS compressors are running. The TCV automaticcally close and stop all flow if the dryers are offline. EO found the CJW pumps running with no flow after 3 days, pump casing was 147 degrees. <I> **** Actions Taken **** secured the CJW pumps per the SOP.
394704 | CR | 20190601 | CAQ | D | RHR-MO-53B electrical bucket control power xformer bad | Y | N |  | N | YES | <D> **** Detailed Description **** When trying to perform diagnostic testing of RHR-MO-53B there was no power on the control power xformer output. The bucket is RHR-42-7BA8C. <I> **** Actions Taken **** Contacted the OCC Contacted the E-shop to assist in troubleshooting Coil/CPT replacement performed per 02118742 <N> **** Equipment Description **** MOTOR STARTER FOR RHR-V-53B R -522- - -H7/8.3 - | 02-00-RHR-MO-53B
394705 | CR | 20190601 | CAQ | D | RRC-42-8C4B Difficult to operate | N | Y |  | N | YES | <D> **** Detailed Description **** RRC-42-8C4B difficult to close in even while pressing on cabinet door while operating. | 02-00-RRC-42-8C4B
394706 | CR | 20190602 | CAQ | C | RRC-V-13B failed third leak rate as left test | Y | N |  | N | YES | <D> **** Detailed Description **** OPS flushed approximately 600 gallons of water through RRC -V-13B per WR 29149165. The retested per 02033547-07 TSP -RRC/X43B-C801. The test was unsat with a leakrate of 3100 SCCM. The admin leakage limit is 150 SCCM. <I> **** Actions Taken **** Wrote CR. Informed OCC and EOC. | 02-00-RRC-V-13B
394707 | CR | 20190602 |  | 4 | Internals found degraded on COND-V-119A |  |  |  | N | YES | <D> **** Detailed Description **** During performance of WO 02072876-01 on COND-V-119A, the initial inspection found valve internals degraded. Disc arm to disc post found with excessive wear to the point of disc rub on the body. <I> **** Actions Taken **** CR generated. EOC contacted <N> **** Equipment Description **** TBG 449 | 02-00-COND-V-119A
394708 | CR | 20190602 |  | 4 | Internals found degraded on COND-V-119B |  |  |  | N | YES | <C> Duplicate of CR 394701 <D> **** Detailed Description **** During performance of WO 02072875-01 on COND-V-119B, the initial inspection found valve internals degraded. Disc arm to disc post found with excessive wear to the point of disc rub on the body. The disc nut was not tack welded to the post as expected. The anti-rotation lugs on the disc were 180 degree out and positioned on the smaller portion of the disc arm rather than on the larger area of the arm. The disc nut pin was found missing. <I> **** Actions Taken **** CR generated and EOC contacted <N> **** Equipment Description **** TBG 449 | 02-00-COND-V-119B
394709 | CR | 20190602 | CAQ | D | RRC-V-13B failed second leak rate as left test | Y | N |  | N | YES | <C> Duplicate of CR 394706 <D> **** Detailed Description **** OPS flushed approximately 300 gallons of water through RRC-V-13B per WR 29149165. Then retested per 02033547-07 TSP-RRC/X43B-C801. The test was unsat with a leakrate of 3670 SCCM. The admin leakage limit is 150 SCCM. <I> **** Actions Taken **** Wrote CR. Informed OCC and EOC. | 02-00-RRC-V-13B
394711 | CR | 20190602 | CAQ | D | Dual indication for MS-V-28C when closed | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of diagnostic testing for MS-V-28C per WO 02079277-34; MS-V-28C was fast closed and never achieved full closed indication in the MCR. Visual indication in the steam tunnel was that the valve closed properly. Diagnostic testing can continue as good data is being obtained; however this will prevent timing adjustments and needs to be addressed. The valve also indicated dual upon slow closure per the same WO task 43. <I> **** Actions Taken **** MCR and OCC notified. | 02-00-MS-V-28C
394712 | CR | 20190602 |  | 3 | SOP-CN-START Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** SOP-CN-START needs a section added to restore the CIA regulator (CN-PCV-10). The procedure currently only has one section, which allows restoration of the containment make-up header (CN-PCV-5). CN-PCV-10 is restored by performing steps in both SOP-CN-START and SOP-CIA-START. These procedures are a challenge to work together with the outage drywell clearance order in place, when CN-PCV-5 is removed from service. A section for restoring CN-PCV-10 independent of CN-PCV-5 needs to be added to allow CIA restoration prior to lifting the drywell clearance. <I> **** Actions Taken **** Submitted CR
394713 | CR | 20190602 | CAQ | C | EMS 30071R1 Installation Instructions for SGT Butterfly vlvs |  |  |  | N | NO | <D> **** Detailed Description **** WO 02103789 replaces the SGT-V-5B2 seal on the SGT Butterfly valve. The seal is replaced via EMS 30071 R1. The instructions require mechanics, electricians and QC to set the seal up using diagonstic equipment and tightening the seat (360 deg seal) without overthrusting the valve. After this step is accomplished then the EMS directs a final adjustement (Step 4.2.4). This step results in 2 issues (1. loss of 360 deg seal & 2. Potential of exceeding valve/actuator weak-link). Step 4.2.4 Final Adjustment requires modification (i.e. (IF Required)) <I> **** Actions Taken **** Notes were added to the WO to address work order step and EMS: Step 4.2.4 "Final Adjustment" EOC was contacted and agreed with the path forward to make EMS Step 4.2.4 final adjustment optional (If required)
394714 | CR | 20190602 |  | 4 | RFW-FCV-2B indicates 6.4% when tripped. |  |  |  | N | YES | <D> **** Detailed Description **** Lifted a local tag on RFW-FCV-2B. the as left position should be 0% open but the valve indicates 6.4% open and would not close in manual. The B feed pump is tripped which should have also closed the FCV when the air was restored to the controls. Please investigate. | 02-00-RFW-FCV-2B
394727 | CR | 20190602 |  | 3 | Safety Stand Down Inadequency |  |  |  | N | I DONT KNOW | <C> Consulted with ECP. <D> **** ANONYMOUS CR - Detailed Description **** The last several Safety Stand Downs, are anything but that. I've been to several Nuclear Stations around the country and all of them take these Safety Stand Downs, very seriously, as they should be. They shut all work down at the station, for a period of time, longer than the two minutes, back to work at Columbia. The Safety Culture here at Columbia, is not very good. We need major improvements. <I> **** Actions Taken **** Initiate CR
394728 | CR | 20190602 |  | 3 | Stand down effectiveness |  |  |  | N | NO | <C> Consulted with ECP. <D> **** ANONYMOUS CR - Detailed Description **** A 2 minute discussion is not a station stand down. So far there have been 4 mandatory stand downs, 3 of them are safety related and one is schedule related. The clearance order stand down was life and death and was given the same amount of weight as a rework stand down. Why is our schedule equal to or more important than conveying the gravity of these situations? A station truly focused on safety would halt work on the outage when something as serious as a danger tagged breaker being found in the wrong position is discovered. Time is money, but death is forever. Itâ€™s time for Columbia to stand by our principles or change them to what we actually value.
394730 | CR | 20190602 |  | 3 | ENDRS Machine |  |  |  | N | NO | <D> **** Detailed Description **** During demobilization of Under-Vessel Equipment, the U/V ENDRS Machine was not sprayed down Under-Vessel prior to being removed. This resulted in more dose for attempted Decon. The ENDRS Machines inside the box (Located in the CRD Rebuild Room) is *600/180 mRem/hr which is located within a posted High Radiation Area. Both ENDRS Machines are currently inside the box. Recommend putting a Hold Point on future RWPâ€™s to ensure that the ENDRS Machine is sprayed down Under-Vessel prior to being removed. <I> **** Actions Taken **** -Notified Supervision -Initiated CR for R24 Lessons Learned <N> **** Equipment Description **** Drywell / Under-Vessel / CRD Rebuild Room
394731 | CR | 20190602 |  | 4 | TSW-HX-7, inlet chamber and water box degraded | N | N |  | N | YES | <D> **** Detailed Description **** Inspection of the generator hydrogen cooler inlet chamber and water box following removal in R24 identified degradation of the divider plates in the both the inlet chamber and water box. There is also a through wall hole approximately 1/4 inch in one of the inlet chamber pipes. Weld repairs will be required for both components See EDMS for pictures <I> **** Actions Taken **** Discussed with Painters, inspected the components and notified EOC and OCC of condition | 02-00-TSW-HX-7A,02-00-TSW-HX-7B,02-00-TSW-HX-7C,02-00-TSW-HX-7D
394733 | CR | 20190602 |  | 3 | FAILED HYTORC HEAD | N | N |  | N | NO | <D> **** Detailed Description **** While torquing the left side blade ring in MS-DT-LPC, two retaining screws sheared.and the retaining clamp was dislodged. Due to proper planning and preparation, all pieces were recovered and retrieved from the FME Level 1 Area. No further action required for this issue. <I> **** Actions Taken **** Immediatly stopped all work and retrieved the failed components. Notified the FME Monitor, their supervisor and the Turbine Deck Coordinator.
394734 | CR | 20190602 |  | 4 | E-CB-3/31 lockout available light is not illuminated in MCR. | N | N |  | N | YES | <D> **** Detailed Description **** E-CB-3/31 lockout available light is not illuminated in MCR. This indication issue is holding up SM-3 restoration | 02-00-E-CB-3/31
394735 | CR | 20190602 |  | 3 | Material discrepancy on replacement Disc Nut on BS-V-8B | N | N |  | N | YES | <C> CR reopened at engineerings request (see EDMS) to add actions. <D> **** Detailed Description **** Need Procurement Engineering to evaluate the use of A194 Grade 7 in lieu of required material A194 Grade 4 for Cat ID# 36605. IN R23 during refurbishment of BS-V-8E, replacement disc nut was issued as Grade 7. Procurement Engineering would not allow use of A194 Grade 7 and a Grade 4 was located in New York. Now in R24, BS-V-8B requires a new Disc Nut and the same problem exists with Cat ID 36605 stating 2â€-8UN ASTM A194 Grade 4. The material received is Grade 7. Reference OMM 70-00,24 Drawing 88G-0073V page 31 for material specification on 24â€ valve. <I> **** Actions Taken **** Notified EOC, Joanna Dobson <N> **** Equipment Description **** T471 . Discussed using A194 Gr. 7 material instead of A194 Gr. 4 material with technical services. After reviewing the ASME Code Section II 1971 ed. the mechnical properties of A194 Gr. 4 and Gr. 7 are identical. Also A194 Gr. 4 in no longer in regular production and would need to be special ordered if used. It is acceptable to use A194 Gr. 7 material in lieu of A194 Gr. 4 material because their mechanical properties are identical. | 02-00-BS-V-8B
394736 | CR | 20190602 |  | 4 | E-GEN-1, damaged end winding brace | N | N |  | N | YES | <D> **** Detailed Description **** During closeout inspection of the main generator an engineer noted damage to an end winding brace. The brace appears to have been cut to allow access to a stator building or through bolt nut. This condition has no impact on the overall end winding support structure and does not require immediate repair. See EDMS for pictures. <I> **** Actions Taken **** Discussed with Siemens, EOC and OCC. Recommend repair of the brace during the next major inspection | 02-00-E-GEN-1
394737 | CR | 20190602 | CAQ | D | CIA-PRV-1A is venting | Y | N |  | N | YES | <D> **** Detailed Description **** 10min after venting CIA-PRV-1A; and setting pressure in band 200-300#; the regulator began venting from holes in the stem area of the regulator body. I secured the vent by isolating the up and downstream valves. <I> **** Actions Taken **** Isolated the regulator by closing valves CIA-V-71A and CIA-V-TK/1A. Informed SSS | 02-00-CIA-PRV-1A
394738 | CR | 20190602 | CAQ | D | CIA regulators bottomed out before reaching pressure band. | Y | N |  | N | YES | <D> **** Detailed Description **** CIA regulator CIA-PRV-9A bottomed out before setting pressure above zero on CIA-PI-40A. CIA-PRV-12A bottomed out at 120# on CIA-PI-43A. Both regulators are below required pressure band of 200-300#. <I> **** Actions Taken **** Informed SSS | 02-00-CIA-PRV-12A,02-00-CIA-PRV-9A
394739 | CR | 20190602 | CAQ | C | RCIC-V112 disc assembly not like for like | Y | N |  | N | YES | <D> **** Detailed Description **** While performing W/O 02111380-01, check valve inspection, found one seat ring retaining screw missing and it was determined to change out the disc assembly with an asme, plan, old disc assmbly not like the new disc assembly, the locking pin hole on the threaded shaft of the disc assembly not in same location, the machined shoulders of the disc assemblies not the same height. ,pictures in data glance of work order 02111380-01, CATID 20516 <I> **** Actions Taken **** informed maintenance management, procurement and OCC of the issue, pictures in data glance of work order 02111380-01, CATID 20516 <N> **** Equipment Description **** RX 475 J6/7.4 Engineering needs to evaluate and accept replacement disk which is not a like-for-like replacement. T19-R24-RCIC -SYS-001. Engineering has reviewed the OMM and drawing CVI DWG 882 -00,1. Use of a thicker washer can be used to take up the space as the drawing provides no dimensions or washer thickness provided the nut has full thread engagement. An email with the above statement is attached to the EDMS on the parent AR. | 02-00-RCIC-V-112
394740 | CR | 20190602 |  | 3 | (R24LL) LP-C turbine erosion was noted in 2011 without follo | N | N |  | N | YES | <D> **** Detailed Description **** Cat-1 Emergent Issue (AR 394050) on steam erosion on the horizontal joint of Inner Cylinder 1 was noted in the Siemens report in 2011 (following R20) with no action taken to repair at the time or initiate followup action. Lesson learned would be to review other reports to see if there any other damage noted with no follow-up action initiated that may affect future outages. | 02-00-MS-DT-1C
394741 | CR | 20190602 |  | 4 | Incorrect replacement Relay for HSSF-RLY-4CR | N | N |  | N | NO | <D> **** Detailed Description **** WO 02104439-01 was a replacement of four Ice cube style relays and two hardwired relays. HSSF-RLY-4CR was expected to be an Ice cube style relay but was found to be a hardwired relay in the field. See EDMS for pictures. <I> **** Actions Taken **** Notified supervision, EOC and Control Room <N> **** Equipment Description **** .
394742 | CR | 20190602 |  | 4 | Poor Lighting in Stairway "A3" | N | N |  | N | YES | <D> **** Detailed Description **** The lighting in Stairway "A3" is poor. More than half of the 4' fluorescent fixtures are burned out. These should be replaced prior to starting up as this Stairway is inaccessible during Operation. <I> **** Actions Taken **** Created WR | 02-00-E-CB-LP2CA/1
394743 | CR | 20190602 | CAQ | D | S1-1 severe ground in multiple times. | Y | N |  | N | YES | <D> **** Detailed Description **** Main control room received the S1-1 severe ground down to 1k ohm in the negative and then in the positive direction. Each time the ground was only in for a few seconds at a time then would clear. The only known work that was near the S1-1 system was the control power for RWCU-V-4 comes off this system. It is not known if this was the cause. <I> **** Actions Taken **** Wrote CR Inform CRS <N> **** Equipment Description **** S1/1 125V DC system.
394744 | CR | 20190602 |  | 4 | BKR 31/3 Trip alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received the BKR 31/3 Trip Alarm when attempting to transfer E-SL-31 from E-SL-21 to E-SM-3 (SOP-ELEC-480V-OPS section 5.12 make before break transfer), the breaker did not close and the bus remained energized on E-SL-21. <I> **** Actions Taken **** Flagged the RMS back to trip to clear the alarm per the ARP for 800 C3 drop 5-4. Contacted maintenance and the OCC | 02-00-E-CB-31/3
394745 | CR | 20190602 |  | 3 | Incorrect location (coordinates) MS-HO-160B |  |  |  | N | NO | <D> **** Detailed Description **** portal J and the work package have incorrect location. 0211198016 The correct location is 481 B0/6.4 <I> **** Actions Taken **** cr initiated <N> **** Equipment Description **** MS-HO-160B
394746 | CR | 20190602 |  | 3 | Dropped Decon Spray nozzle tip in alpha outlet waterbox | N | N |  | N | YES | <D> While painters were prepping to coat the alpha outlet water box per 02111869-57, they dropped a Decon spray can nozzle tip in the alpha outlet water box, <I> informed maintenance, occ of dropped item, <N> T471 D3/13.0 | 02-00-COND-HX-9
394747 | CR | 20190602 |  | 3 | R24LL â€“ Save LP Rotor L-0 blades in R25 for emergency spares |  |  |  | N | YES | <D> **** Detailed Description **** During R20 (2011) several last stage blades, designated L-0 blades, were identified as having blade root cracks on LPC (MS-DT-1C). The inspection was expanded to the other two LP turbines. Spare blades were found in the warehouse and used to replace the damaged blades. A total of 14 blades were removed and replaced with the new blades. RCE AR 214084. Funding was later approved to purchase additional blades to compliment the remaining spares such that an entire row of blades for both the GOV and GEN ends of the turbine were available. Reference EVAL AR 262329. When the new Seed Rotor was manufactured, all the spare L-0 blades that were purchased following EVAL AR 262329 were utilized on the new rotor as a cost savings measure. This action resulted in having no emergency spares remaining. In R24, the decision was made [see email in EDMS] to scrap the LPC L-0 blades when they are removed from the rotor prior to be sent off for refurbishment (where it will received new L-1 and L-0 blades). This LL CR is to plan and schedule retention of blades from all or part of both L-0 blade rows for both the GOV and GEN ends of the rotor when the LPB rotor is removed from service in R25. The intent is to re-establish emergency spares. <I> **** Actions Taken **** raised question with major maintenance received decision from EOC <N> **** Equipment Description **** L-0 blade rows, GOV and GEN ends Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817. | 02-00-MS-DT-1B
394748 | CR | 20190602 |  | 4 | E-CB-3/31MOC switch PMT | N | N |  | N | YES | <D> **** Detailed Description **** during performance of 02111268-02 at step 4.2 MOC assembly found touching stop pin. <I> **** Actions Taken **** Informed supervisor initiated CR | 02-00-E-CB-3/31
394749 | CR | 20190602 |  | 4 | CF-FLX-42B/1, Ruptured | N | N |  | N | YES | <D> **** Detailed Description **** Recieved notification from OPS EO that Nalco was sprayed all over the Chemical feed pump skid in the CW pump house. Investigated and found that the suction hose CF-FLX-42B/1 had two small slits in the line. The inlet to the chemical supply tank was walked down and found to be isolated to the line in question. Suspect the rupture was due to age of the flex line in combination with heat expansion from outside temperature. The amount of chemical spilled was the contents of the supply piping from the tank isolation to the suction of CF-P-42B. <I> **** Actions Taken **** Ops Notified the control room. Attempted to contact enviromental. Started cleanup. | 02-00-CF-FLX-42B/1
394750 | CR | 20190602 |  | 4 | R24LL - TV actuator needed 90 deg DEH elbows transferred |  |  |  | N | YES | <D> **** Detailed Description **** The manifold mounted to the side of the actuator block for MS-V-TV/4 required three 90 deg elbows in order to mate up with plant DEH piping. The elbows from the old manifold block were transferred to the new one. This is a first time occurrence since the actuator block was new for R24. This lessons learned CR is to ensure parts are procured and ready for the next time a new actuator block is installed, or have them installed when supplied new. This condition will only apply to Throttle Valves that receive new actuator blocks. <I> **** Actions Taken **** Discussed with project manager Discussed with OEM Informed EOC <N> **** Equipment Description **** manifold block on side of TV/4 actuator block | 02-00-DEH-EHO-TV/4
394751 | CR | 20190602 | CAQ | D | MS-V-28C slow "fast closure" stroke time per OSP-MS/IST-Q701 | Y | N |  | N | YES | <D> **** Detailed Description **** This CR is to document MS-V-28C closing stroke time greater than the OSP-MS/IST-Q701 limit of 4.0 seconds. The TDAS measured stroke time was 4.14 seconds. The closing speed will be adjusted and retested per OSP-MS/IST-Q701 and WO 02079277. <I> **** Actions Taken **** Notified OCC. <N> **** Equipment Description **** RB 501' Steam Tunnel. | 02-00-MS-V-28C
394752 | CR | 20190602 |  | 3 | WOH failed to Sign Off CO |  |  |  | Y | NO | <D> **** Detailed Description **** A Work Order Holder (WOH) failed to sign off Clearance Order (CO) O-RHR-SYS-B-003 prior to end of shift as required by PPM 1.3.64, section 3.4.8. The WOH signed onto the clearance on 5/31/19 06:15 but did not sign off at end of shift. Individual was performing visual inspections only and is no longer badged to access equipment, therefor there is no issues with equipment configuration or need for continued personnel protection. Supervisor approval was given IAW PPM 1.3.64, section 3.2.4. Information was provided to Operations in order to allow work order holder sign-off IAW OI-12, section 7.4. .a. <I> **** Actions Taken **** Notified Operations for WOH signoff, provide information to Quality Management for review.
394753 | CR | 20190602 | CAQ | D | MS-V-28C slow closure time per 8.3.182 (slow close test) | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of PPM 8.3.182 per WO 02079277-19. MS -V-28C was slow closed per section 8.7 and the closure distances were SAT per 8.7.21, hover the slow close time was 68.00 seconds per step 8.7.23. The procedure directs an adjustment per section 8.10 if the time is outside the band of 20-60 seconds. The procedure allows an adjustment and 1 additional test. <I> **** Actions Taken **** MCR and system engineer informed. | 02-00-MS-V-28C
394754 | CR | 20190602 | CAQ | D | DG3 DC Soakback Pump Cable Degraded | Y | N |  | N | YES | <D> **** Detailed Description **** DLO-P-10 input power cable is worn. This cable is at ground level and made of rubber so it is very susceptible to inadvertent steps when passing through door D113. Recommend replacing this rubber cable with a flexible metal conduit similar to the AC soakback pump DLO-P-12. <I> **** Actions Taken **** Notified MCR and wrote CR. | 02-00-DLO-P-10
394755 | CR | 20190602 |  | 3 | DG3 Room Equipment Storage |  |  |  | N | NO | <D> **** Detailed Description **** Several authorized storage locations are exceeding their capacity. Permit #214 along the south wall has vacuums and other tarp covered equipment over its boundary tape. Permit #267 along the west wall has metal ramps being a storage tool box that are over the boundary tape. Recommend re-evaluating the boundaries to accommodate this extra equipment or removal of the equipment. <I> **** Actions Taken **** Notified MCR, Maintenance, and wrote a CR.
394756 | CR | 20190602 |  | 4 | R24 lessons learned assigned manpower |  |  |  | N | NO | <D> **** Detailed Description **** Not sure we accounted for the Manpower to send EO's to escort other craft into and out of protected areas while operating disconnects or removing equipment such as cable. Please ensure we account the for this task for manpower scheduling in r25 <I> **** Actions Taken **** cr/wr
394757 | CR | 20190603 |  | 4 | Cannot access Door T133 due to immobilized manlift | N | N |  | N | YES | <D> **** Detailed Description **** Door T133 was requested to be opened for material transfer. This door has already been written up for faulty operation and therefore cannot be opened electrically (CR 373813). Due to a manlift parked directly in front of the door, access is restricted to the manual clutch operator and chain drive. Moving the manlift was attempted, but a red FAULT light would not reset, even when following instructions for reset. This is precluding the material transfer to a C-van. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 441 W | 02-00-T-DOOR-T133
394758 | CR | 20190603 |  | 3 | Near Miss on Turbine Deck |  |  |  | N | NO | <D> **** Detailed Description **** Near Miss on Turbine Deck. Signaler went out of role and operated a chain fall which was on the aux crane hook. Unaware their radio was on, the signaler made a comment (including the word "up") while operating the chainfall and the crane operator took this as direction to bring the hook up. A support piece tipped slightly (~5Â°). The Crane operator observed this and stopped immediately. No equipment damage and no personnel were injured. Signaler was benched and a stand down will be performed prior to restarting work. <I> **** Actions Taken **** Stand down performed on the Turbine near miss. OCC provided concurrence to proceed with returning to work based on the results and content of the stand down
394759 | CR | 20190603 | CAQ | D | channel test lamp will not illuminate | Y | Y |  | N | YES | <D> **** Detailed Description **** while performing wo # 02111597-01 and isp-cms/prm-b304 on step 7.1.11 the channel test lamp did not illuminatefor cms-ris-27f. changed lamps twice and it would not illuminate.also step 7.1.15 confirm channel test lamp extinguished could not be verified because it never illuminated. <I> **** Actions Taken **** talked with supervisor and crs wrote this cr <N> **** Equipment Description **** bd-rad-23 main control room | 02-00-CMS-RIS-27F
394761 | CR | 20190603 | CAQ | D | M&TE Report Review could not be completed per PPM 1.5.4 |  |  |  | N | NO | <D> **** Detailed Description **** Accelerometer with SN: 7669 (Piezotronics Model 357M38) failed itâ€™s tolerance check at 6000 Hz (highest range) in the M&TE calibration lab on 5/17/19. The calibration report was turned over to EFIN to be evaluated per PPM 1.5.4 in order to see if there was any impact to plant equipment based on degraded component. The report contains 6 work orders which show the accelerometer was used to gather valve diagnostic data. However, neither the work orders, the data or the software (UltraCheck) show at which frequency the accelerometer is used. Upon talking to the site SME (Components Engineering), he does not believe the accelerometer is used at its highest range but we have not been able to verify. The vendor, Areva is the OEM for UltraCheck software that is used along with these accelerometers in order to gather data in valve diagnostics. Several emails have been sent with no respons e. The conflict in schedules and site assistance with this inquiry has been a challenge due to Outage scheduling conflict. We have not met the timeline per PPM 1.5.4, section 4.11.4 which states that if M&TE Deficiency report cannot be reviwed/dispositioned within 20 calendar days, then responsible organization will initiate CR per SWP -CAP-01. This CR meets the intent. Impacted WOs are cross-referenced. Right now, there is no evidence to believe there is a problem with the work orders performed, until we can validate accelerometer frequency usage with Areva point of Contact (Vedat.Ataman@areva.com). <I> **** Actions Taken **** Notified EFIN Supervisor and Components Engineering Group Supervisor. <N> Vendor sent out email on 6/3 days. M&TE Calibration report updated. No impact on referenced WOs. The accelerometer is not used in the 6kHz frequency range for valve diagnostics. Email attached to EDMS. No further actions required.
394762 | CR | 20190603 | CAQ | D | RHR-42-8BA5D does not close RHR B/C LSFT hold up | Y | Y |  | N | YES | <D> **** Detailed Description **** RHR-V-27B disconnect at MC 8BA did not close in when handle turned fully to the stop in the close direction. Spring tension could be felt but the contacts did not close in. | 02-00-RHR-42-8BA5D
394763 | CR | 20190603 | CAQ | D | R109 Door knob | N | N |  | N | YES | <D> **** Detailed Description **** R109's door knob is not functioning as intended. <I> **** Actions Taken **** Comp measure put in place. Shift manager, Maintenance and OCC notified. This is a non-essenail fire door. <N> **** Equipment Description **** R109- reactor building northeast door.
394771 | CR | 20190603 | CAQ | D | MS-V-28C closing stroke time outside 10.17.3 limit | Y | N |  | N | YES | <D> **** Detailed Description **** MS-V-28C closing stroke time is 3.023 seconds to meet operability requirements of OSP-MS/IST-Q701. The stroke time could not be adjusted to meet the 3.4 to 3.8 second requirement of PPM 10.17.3 under WO 02079277. <I> **** Actions Taken **** None <N> **** Equipment Description **** RB 501 steam tunnel. | 02-00-MS-V-28C
394772 | CR | 20190603 |  | 4 | M&TE Suspended/ Lost |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0067143 Industrial Scientific Gas Monitor- model Ventis MX4 missing from the Clean Tool Crib and NOT checked out. Suspended/Lost. DEF #7048A written. No Action Required . <I> **** Actions Taken **** None Trending purposes only.
394773 | CR | 20190603 |  | 4 | Biohazard Waste Found in Trash Receptacle |  |  |  | N | NO | <D> **** Detailed Description **** A syringe and needle were found in an on-site trash receptacle by a janitor. Nothing that can poke, cut or harm a janitor should be placed in trash receptacles. GBP-HR-53 "Blood Borne Pathogens", section 3.4 requires biohazard sharps to be placed in approved sharps disposal containers. <I> **** Actions Taken **** The janitor observed the material and was not injured. The janitor disposed of the material in a sharps container in accordance with the requirements. Occupational Health and Environmental & Regularity Services were notified.
394774 | CR | 20190603 |  | 3 | Large amounts of TOC's allowed to enter plant drains | N | N |  | N | NO | <D> **** Detailed Description **** Large amounts of TOC's allowed to enter plant drains with extremely limited ability to process/ remove them TOC excursion noticed after letting down under vessel area, but could be other source(s) <I> **** Actions Taken **** Informed MCR, Chemistry management Processing multiple times shows slight/ gradual progress but getting from 4500 ppb to less than the spec of 200 ppb may take days
394776 | CR | 20190603 |  | 3 | R24LL: Designated Motorcycle Parking |  |  |  | N | NO | <D> **** Detailed Description **** During R-24, there was not enough designated motorcycle parking to meet the demand. Several motorcyclists parked their bikes in white crosshatched areas that are not officially designated for motorcycles. . Two recommendations: . 1. Facilities develop a plan to create more designated motorcycle parking for future outages by taking some normal parking spots for cars and repurposing them for motorcycles. . 2. Facilities to paint "No Parking" on the white crosshatched areas that currently do not have "No Parking" painted on them. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
394777 | CR | 20190603 |  | 4 | RCC Water Radiation Monitor indicates no flow | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of CI-15.2, Daiily Monitor Data, it was noted that RCC-FIS-10, flow indication for RCC-SR-44, indicated 0 gpm flow to the radiation monitor. This is contrary to the expected condition of ~2.5 gpm. <I> **** Actions Taken **** CRS, chemistry supervisor and specialist informed. Noted in CI-15.2. | 02-00-RCC-SR-44
394778 | CR | 20190603 |  | 3 | Leak by on CRD-V-47A | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WO 02059041-01 for replacement of CRD-V-47A and WO 02101714-01 replacement of CRD-FCV-2A leak by was noticed following cutting the piping to CRD-FCV-2A. The isolation clearance boundary was revised twice from the original to try and eliminate the excess leak by to allow for replacement of the two valves. The Air Operator and bonnet were removed from CRD-FCV-2A on day shift, it was noticed then that there was residual water in the line but it was not flowing from the open bonnet. When nightshift made the pipe cuts to replace the 2A valve water began to flow from the piping between the two valves, indicating leak by. The water was captured and monitored but never subsided to allow for welding. CRD-V-47A was then closed and the water stopped. This would allow for the continued replacement of the 2A valve. <I> **** Actions Taken **** CR generated for documentation and recommendation of OSCR generation <N> **** Equipment Description **** Leak by on CRD-V-47A Work has been removed from R24 and will be rescoped for R25. | 02-00-CRD-V-47A
394779 | CR | 20190603 |  | 4 | MT-CRA-1 LIGHTING CIRCUIT | N | N |  | N | YES | <D> **** Detailed Description **** One of the lighting circuits on MT-CRA-1 has tripped twice. It will rest, but has tripped a second time. Please check it out. <I> **** Actions Taken **** Notified the Turbine Coordinator and he initiated this CR and Work Request. . <N> **** Equipment Description **** MT-CRA-1 - 501' TG.
394780 | CR | 20190603 | CAQ | D | R24 LL, Train Supervisors on Data Glance WO closure |  |  |  | N | NO | <D> **** Detailed Description **** While trying to add additional notes and comments or looking that what work was performed on R24 work already in records, found multiple missed signatures or inconsistant WO completions. Some of the items found was unneed document sent to records, but multiple instances of signtures missing on documents. Do not know the scope of missing signature, but multiple ones I looked at had issues. <I> **** Actions Taken **** Printed the missing signture pages for the ones I found, had them signed and sent the hard copy to records.
394781 | CR | 20190603 |  | 4 | Leaking Regulator on HD-LCV-10A2 | N | N |  | N | YES | <D> **** Detailed Description **** regulator requires replacement due to leak <I> **** Actions Taken **** Intiated CR. Discussed issues with AOV program manager. | 02-00-HD-LCV-10A2
394783 | CR | 20190603 |  | 3 | Records Submitted W/O Transmittal Attached |  |  |  | N | NO | <D> **** Detailed Description **** A Pile of records was submitted to Records control without a transmittal attached. Please Refer to SWP-REC-02 Section 4.3.2 for the proper submittal process. <I> **** Actions Taken **** Notified my supervision. Sending records back to Rad Material Control Supervision for corrections and re -submittal. <N> Records have been correctly submitted. No further action required.
394784 | CR | 20190603 |  | 4 | Employee injury |  |  |  | N | NO | <D> **** Detailed Description **** On 6/2/2019 an employee experienced increased ringing in their esrs on the way home from work. The employee had been exposed to loud noise on the 501 turbine deck. The conditon was reported upon returning to work on 6/3/2019 wherein the Employee was taken to occupational health for evaluation. <I> **** Actions Taken **** Initiated CR. Notified safety of concerns. Escorted employee to occ health. Completed OI-34 notification.
394786 | CR | 20190603 |  | 4 | TSW-TIC-9 needs to be replaced | N | N |  | N | YES | <D> **** Detailed Description **** While performing CC per 0209546703 TSW-TIC-9 Loop cal. Craft was unable to calibrate TIC. Tic needs to replaced and Loop cal needs to be re-performed <I> **** Actions Taken **** wrote CR. write WR to replace and re perform loop cal per 0209546703 <N> Replacement not required - completed calibration SAT. | 02-00-TSW-TIC-9
394787 | CR | 20190603 | CAQ | D | MS-RV-3D ADS Test Signal light not illuminate | Y | N |  | N | YES | <D> **** Detailed Description **** MS-RV-3D ADS Test Signal light not illuminate. Did replace with new light bulbs. Need to investigate and repair if needed. <I> **** Actions Taken **** SM informed | 02-00-MS-RV-3D
394788 | CR | 20190603 |  | 3 | Procedure change. ESP-R5051IMRRA-B301 |  |  |  | N | NO | <D> **** Detailed Description **** Remove Simultaneous Verification from step 7.4.4 <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
394791 | CR | 20190603 |  | 3 | Steam Tunnel camera has been moved | N | N |  | N | YES | <D> **** Detailed Description **** During R24, WO 02124414 was performed to replace the non -functional 501TG steam tunnel camera located within the Steam Tunnel between the RX and TG with a new camera. Telecom performed the work and the camera was tested on 5/17/2019. On 5/28/2019 it was observed that the camera has been moved from its location and is against a wall /steel support structure. This is causing the camera to be unable to PTZ as designed, and can possibly damage the motors. Dose will be taken putting the camera back into the correct position. <I> **** Actions Taken **** Shut the power supply to the camera off to eliminate any movement of the camera. Contacted multiple groups to see if they may have moved the camera, no confirmation. <N> **** Equipment Description **** 501TG Steam Tunnel Camera
394792 | CR | 20190603 |  | 4 | while performing COND-DPT 205 COND-DPS-205/2 was OOT | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** COND-DPS-205/2 trip point should be 11.2 psi Â±.2 was found tripping at 11.6 psi. wo# 02077039 <I> **** Actions Taken **** Adjusted to within tolerance.
394793 | CR | 20190603 | CAQ | D | Snubber load pin missing HV-1005N (T) | N | N |  | N | YES | <D> **** Detailed Description **** During scaffold installation near TG 471 COND-HX-9 A entry, it was noticed that the load pin of snubber HV-1005N (Top) was missing and the snubber was laying against the pipe with the rear pin still in place. The bottom snubber was still fully attached. These snubbers are located on the 20" HV(19 )-1 MS-RV-116D discharge line to the condenser. The function of these snubbers is to protect condenser nozzle 38 from overstress, preventing inleakage to the condenser. This snubber is a PSA-3, non-safety, B31.1, QC-2 support. Pictures in EDMS. <I> **** Actions Taken **** Notified EOC. <N> **** Equipment Description **** Snubber Hanger ID HV-1005N (TOP) - TG 471 Heater Bay D3/13
394794 | CR | 20190603 | CAQ | C | ANII hold point observation RCIC-V-63 VT-1 inspection | Y | N |  | N | NO | <D> **** Detailed Description **** Missed ANII hold point for the observation of the VT-1 visual inspection of the existing bonnet studs and nuts (ASME work plan 2-3017 step 2.3). The VT-1 examination was satisfactory and ANII has reviewed the examination results. <I> **** Actions Taken **** Quality, NDE, and ANII notified
394795 | CR | 20190603 | CAQ | D | CRD-AO-11 Actuator installed 90 degrees out | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-AO-11 actuator was replaced, when diagnostic testing was attempted on teh new actuator it was determined the new actuator was installed 90 degrees out compared to the old actuator and tubing <I> **** Actions Taken **** Discussed with installers and actuator was corrected Informed Manager Wrote CR | 02-00-CRD-AO-11
394797 | CR | 20190603 |  | 4 | E-CB-CTA closed indicating light socket is broken. | N | N |  | N | YES | <D> **** Detailed Description **** E-CB-CTA closed indicating light socket is pushed back into the breaker cubicle and hanging by its power supply wires. Discovered on OPS 3 rounds. Please repair. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 471W | 02-00-E-CB-CTA
394799 | CR | 20190603 |  | 4 | E-CB-2/21 open indicating light socket is broken. | N | N |  | N | YES | <D> **** Detailed Description **** E-CB-2/21 open indicating light socket is pushed back into the breaker cubicle and hanging by its power supply wires. Discovered on OPS 3 tour. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG-471W | 02-00-E-CB-2/21
394800 | CR | 20190603 | CAQ | C | RWCU-FT-16 LIMITATION ON USE ACTIONS NOT COMPLETED | Y | N |  | N | YES | <D> **** Detailed Description **** THE FOLLOWING LIMITATIONS ON USE WERE LISTED ON WO# 02094539 WORK INSTRUCTIONS BUT NO EVIDENCE OF THEM BEING INCORPORATED INTO THE WORK ORDER OR COMPLETED WERE FOUND. - -LIMITATION ON USE- - AFTER FIRST TIME INSTALLATION IN ANY EPN, ADD/UPDATE THE APPLICABLE TASK ATTRIBUTES PANEL WITH THE DOC UPDATE (Y/N) ATTRIBUTE AND SET ATTRIBUTE AS â€œYâ€ VALUE. IDENTIFY 10.24.32 OR CREATE NEW PPM IN THE DOC UPDATE (Y/N) ATTRIBUTE NOTES AS REQUIRING REVISION A GENERIC CALIBRATION PROCEDURE WILL NEED TO BE CREATED FOR ROSEMOUNT 3153N SERIES DIFFERENTIAL PRESSURE TRANSMITTERS. AFTER INSTALLATION, CREATE AN AR/ENG TO AR-PROCENG REQUESTING REMOVAL OF LOU FROM CID 36816 & - -LIMITATION ON USE- - AFTER INSTALLATION IN RWCU-FT-16, ADD/UPDATE THE APPLICABLE TASK ATTRIBUTES PANEL WITH THE DOC UPDATE (Y/N) ATTRIBUTE AND SET ATTRIBUTE AS â€œYâ€ VALUE. IDENTIFY THE APPLICABLE IMDS, ISP-RWCU-Q902, AND ICP-PMR/RTT-C601 IN THE DOC UPDATE (Y/N) ATTRIBUTE NOTES AS REQUIRING REVISION TO UPDATE CALIBRATION REQUIREMENTS AS NEEDED FOR THE INSTALLED 3153N TRANSMITTER. AFTER INSTALLATION, CREATE AN AR/ENG TO AR -PROCENG REQUESTING REMOVAL OF LOU FROM CID 36816 . THESE ARE REQUIRED FOR MAINTAINING PLANT CONFIGURATION CONTROL. . RECOMMENDED ACTION: ASSIGN TO WORK MANAGEMENT TO HAVE LOU REQUIRED ACTION TAKEN FOR DOCUMENT UPDATES. <I> **** Actions Taken **** DISCUSSED WITH PROCUREMENT ENGINEERING WROTE CR <N> **** Equipment Description **** RWCU BLOWDN TO CONDENSER FLOW XMTR | 02-00-RWCU-FT-16
394801 | CR | 20190603 |  | 3 | DMC 2000 Electronic Dosimeter Malfunction |  |  |  | N | NO | <D> **** Detailed Description **** RX Maintenance Employee Logged into a HRA RWP to perform work in the Drywell. Verified Electronic Dosimeter was reading 0.0 mRem prior to leaving the Drywell Trailer (also verified transmitting via ALARA-CAST). Electronic Dosimeter turned off prior to getting to the Turnstile at the RCA entrance. Worker talked to the RX BLDG HP Lead and was directed back to the Drywell Trailer where the individual was manually logged out and his Electronic Dosimeter was removed from service. Worker was issued a new Electronic Dosimeter. ED#00866669. <I> **** Actions Taken **** Notified Supervision Removed ED from Service Initiated Condition Report
394803 | CR | 20190603 | CAQ | D | E-SL-81 GFIP light socket is broken. | Y | Y |  | N | YES | <D> **** Detailed Description **** E-SL-81 GFIP has a bad light socket for CCH-CR-1B ground indication. ( Left socket ). The socket contacts are pushed back into the panel. Discovered on OPS 2 rounds. Please repair. <I> **** Actions Taken **** RW 467 VI. <N> **** Equipment Description **** RW 467 VI | 02-00-E-SL-81
394804 | CR | 20190603 | CAQ | C | RWCU-FT-16 SETPOINT CALC NOT UPDATED PRIOR TO INSTALL | Y | N |  | N | YES | <D> **** Detailed Description **** FOR W/O# 02094539; REPLACEMENT OF EPN RWCU-FT-16, SETPOINT CALCULATION E/I-02-94-1333 WAS NOT REVISED AND WAS NOT DOCUMENTED ON THE INSTALLING WORK ORDER FOR THE INITIAL INSTALLATION OF THIS INSTRUMENT. PER LIMITATION ON USE EPN RWCU-FT-16 CANNOT BE DECLARED OPERABLE. . THERE IS NO EVIDENCE THAT THE CID 36816 D205 â€œMâ€ NOTE LIMITATION ON USE SPES-1.9.4.3 WAS INCORPORATED OR COMPLETED ON W/O# 02094539. THE LOU REQUIREMENT FOR CALC UPDATE WAS NOT FOUND TO BE ON ANY DOCUMENTATION OR WORK ORDER TASK. PER D200: - -LIMITATION ON USE- - SEE PANEL D205. LIMITS WILL BE IDENTIFIED WITH A PRT CODE OF "M". SELECT "MORE DETAIL" (F9) ON THE STD/PROCED FOR THESE ITEMS FOR DETAILED INFORMATION. . PER D205 â€œMâ€ NOTE SPES-1.9.4.3 - -LIMITATION ON USE, SUBSTITUTION FOR INSTRUMENT/RELAY WITH SETPOINT- - SETPOINT CALCULATION REVISION MUST BE COMPLETED FOR THE INITIAL INSTALLATION OF THIS INSTRUMENT PRIOR TO DECLARING OPERABLE. RECORD SETPOINT CALCULATION AND REVISION NUMBER OR CMR NUMBER ON THE INSTALLING WORK ORDER. . RECOMMENDED ACTION: ASSIGN TO MAINTENANCE MANAGEMENT TO REVISE THE W/O TO SHOW THE LOU AND GET THE REQUIRED CALCULATION REVISION COMPLETED. <I> **** Actions Taken **** DISCUSSED WITH PROCUREMENT ENGINEERING DISCUSSED WITH EOC DESIGN CHAIR DISCUSSED WITH DESIGN ENGINEERING WROTE CR <N> **** Equipment Description **** RWCU BLOWDN TO CONDENSER FLOW XMTR | 02-00-RWCU-FT-16
394805 | CR | 20190603 |  |  | Cooling tower area deficiencies |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Horizontal water pipes used to provide water for cleaning upper CT flumes have such large leaks that water pressure is insufficient. Vertical pipes are still intact. <I> **** Actions Taken **** Notified supervisor, system engineer, and maintenance initiated this CR
394807 | CR | 20190603 | CAQ | C | CRD-V-11 | Y | N |  | N | NO | <D> **** Detailed Description **** WO #02119375 has a Mechanical task to remove limit switches on CRD-V-11. There is also an electrical task to remove the same limit switches, and this task was taken to complete with no documentation. There is also a Mechanical Task to re -install limit switches with torque PEER VERIFICATION and this was N/A'd. There is also an electrical task to re -install limit switches that has no instructions. <I> **** Actions Taken **** CONTACT SUPERVISION ELEC AND MECH INITIATE CR <N> **** Equipment Description **** CRD-V-11
394808 | CR | 20190603 |  | 4 | Degraded conditions noted in the cooling tower area | N | N |  | N | YES | <D> **** Detailed Description **** All hoizontal water pipes used to provide fire system water to wash upper deck flumes have leaks that impact available water pressure. Door latch mechanism for the large, double doors for equipment are rusted, with some parts bent or missing preventing some doors from latching. Some wiring clamps are missing or broken. A light fixture cover is partially detached and ground wire clamp broken at CW-CT-2B A stair rail near building 39' is missing. The top of the stairs are marked with candlesticks and danger sign. Personel door for CW-CT-1A covered stairway is off hinges. It is in a location where it does not present a danger to personel. Conduit clamps missing or broken on upper deck of CW-CT-1B <I> **** Actions Taken **** Contacted supervisor, Contacted system engineer, Contacted Maintenance Component Group Manager Took pictures (See EDMS) and Wrote this CR <N> **** Equipment Description **** CW-CT-1A CW-CT-1B CW-CT-1C CW-CT-2A CW-CT-2B CW-CT-2C | 02-00-CW-CT-2B
394810 | CR | 20190603 |  | 4 | MS-MO-115B breaker failure during PMT | N | N |  | N | YES | <D> **** Detailed Description **** During MS-MO-115B PMT 02115970-10 the breaker failed to energize. Will need repairs to breaker before PMT can be completed. <I> **** Actions Taken **** Contacted Valve Project Manager and initiated work request. | 02-00-MS-MO-115B
394811 | CR | 20190603 |  | 4 | E-CB-S/6 red close light will not illuminate in MCR | N | N |  | N | YES | <D> **** Detailed Description **** E-CB-S/6 red close light will not illuminate in MCR or on local panel. Light bulbs were replaced several times. Transferred SH-6 to TR-S following breaker overhaul of E -CB-S/6, E-CB-S/6 green light went out and E-CB-N2/6 tripped, SH-6 remains energized. No attempts have been made to transfer back to N2/6 due to uncertainty of whether or not E-CB-S/6 will trip once ECB-N2/6 closes. Further investigation is required. RPS-B is currently powered from alternate source E-MC-6A. | 02-00-E-CB-S/6
394812 | CR | 20190603 |  | 3 | R24LL: SOP-HPCS-FILL Procedure Change |  |  |  | N | NO | <D> **** Detailed Description **** SOP-HPCS-FILL (Rev 013 / Minor N/A) step 5.1.52 requires operating HPCS-P-1 in the CST to CST mode. HPCS-V-10 and HPCS-V-11 have been deactivated, so the CST to CST mode is no longer available.
394813 | CR | 20190603 |  | 4 | Department Instruction missing signature pages |  |  |  | N | NO | <D> **** Detailed Description **** A department instruction was issued with the signature review and approval pages removed from the Procedure-PDF. <I> **** Actions Taken **** The image in Asset Suite/EN Docs was updated to attach the revision signature review and approval pages. The responsible individual and procedure sponsor were coached to ensure the Procedure-PDF includes all pages of the document and the signature pages.
394814 | CR | 20190603 | CAQ | D | RRC-RLY-80T/RPT3B as found out of tolerance | Y | Y |  | N | NO | <D> **** Detailed Description **** While performing WO 02076250-01 RRC-RLY-80T/RPT3B0 as found dropout was slightly out of tolerance. The acceptance criteria was greater than or equal to 6.25 VDC. It Dropped out at 5.17 VDC. Craft performed a cleaning and inspection which included burnishing the contacts per 10.25.217. As left Dropout was left at 7.00 VDC. Relay function as designed just did not meet acceptance criteria on data sheet. <I> **** Actions Taken **** Notified supervision and the control room
394815 | CR | 20190603 | CAQ | C | Improper Torqueing on ECSA modules needs evaluation | Y | Y |  | N | YES | <D> **** Detailed Description **** CR 394614 identified that the Electrical Conductor Seal Assembly (ECSA) seal body and midlock cap were found without proper torqueing when disassembled. This condition could have impaired the sealing ability of the ECSA which is credited for qualification of the components. The loose ECSA midlock cap needs to be evaluated for impact on the qualification of the component during the time in which the deficient condition existed. This deficiency was corrected by the work orders listed in the cross reference, so no current impact to qualification exists. Recommend assignment to plant programs. <I> **** Actions Taken **** Initiated CR. | 02-00-CMS-RE-27E,02-00-CMS-RE-27F
394816 | CR | 20190603 | CAQ | C | RRC-L-1B Center Lid fastener chain is not attached | Y | Y |  | N | YES | <D> **** Detailed Description **** The chain to the fastener holding the lid on the center lower bearing constant level lubricator (3 total) is no longer connected. has been severed. <I> **** Actions Taken **** 1. Physicallly verified with SSC Fitters that chain is disconnected. 2. Notified Supervision 3. Notified PM Coordinator. 4. Notified Design Engineering. Not an operation concern for the next cycle run. Recommend an assignment to Mechanical Planning to replace center lid on RRC-L-1B when the oil is changed in R-25 on WO 02144522. (PMID 10580-10). CATID of Oiler is 38702. | 02-00-RRC-L-1B
394817 | CR | 20190603 |  | 3 | (QA) Repeat Non-Compliances for WOT Initials/Printed Name |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Two Work Order Task (WOT) front cover sheets reviewed by Quality were missing the initials and printed name of everyone that had performed work, contrary to SWP-PRO-01 "Procedure and Work Instruction Use and Adherence". This is a repeat of AR-CR 394007 initiated by Quality on 5/22/19. The two WOTs are at "Working" status. These are two procedure use and adherence issues with no actual consequence because neither WOT had become a Quality Assurance Record (QAR) yet. Potential consequences include rework to find the missing persons and get them to sign the WOT cover sheets, and possibly more rework to amend the QARs, if the errors are not caught in Supervisor reviews prior to creation of the QARs. Requirements: â€¢ MI-1.8 "Conduct of Maintenance" rev 072-002 section 7.0 requires strict compliance with SWP-PRO-01 for work documents. â€¢ SWP-PRO-01 rev 032-002 requires signing off a step by initialing the step, then entering the initials and a printed name on the front cover sheet." [italics added] Factual Basis: â€¢ On 6/3/19, WOT 02143175-01 "COND-EJ-2C, Replace Expansion Joint" was at "Working" status, and a performer (Mechanic) on 6/2/19 already initialed/dated a step on page 3 and a step on page 4 in the WOT instructions, but the front cover sheet was missing the initials and printed name of the Mechanic. â€¢ On 6/3/19, WOT 02101714-01 "CRD-FCV-2A, Replace Per EC -Malt 15866" was at "Working" status, and two performers (Mechanics) on 6/2/19 each already initialed/dated multiple steps on page 4 in the WOT instructions, but the front cover sheet was missing the initials and printed names of each of these two Mechanics. Insights: â€¢ The immediate corrective actions taken by Maintenance in response to AR-CR 394007 to improve compliance with this requirement were not fully effective. <I> **** Actions Taken **** Contacted the Component Group Manager for Mechanical Maintenance. . Recommend routing to Maintenance. . This is a Deficiency identified during the R-24 Outage Quality Surveillance SR-19-01.
394818 | CR | 20190603 | CAQ | D | (NRC Identified) Door R107 rubbing on bottom of frame | N | N |  | N | YES | <D> **** Detailed Description **** The NRC identified R-DOOR-R107 is rubbing at the bottom of the frame preventing the door from fully closing. The door is held closed properly, but wont latch without assistance. This is not an essential fire door. <I> Non-essential fire door. | 02-00-R-DOOR-R107
394819 | CR | 20190603 | CAQ | D | (NRC Identified) SM8 spare cubicle lower door latch | Y | N |  | N | YES | <D> **** Detailed Description **** The NRC identified the SM8 spare cubicle lower latch locks may not be proplery closed / aligned. All other latches are properly engaged. <I> This is a spare cubicle on SM8 and has not impact on the safety related equipment supported by SM-8. SM-8 remains operable. This is a degraded condition on the spare cubicle. <N> **** Equipment Description **** SM-8 Spare cubicle
394820 | CR | 20190603 |  | 3 | RFW-P-1B Thrust Bearing Initial Investigation |  |  |  | N | YES | <D> **** Detailed Description **** During the disassembly of the inboard thrust bearing, areas of wear were identified on the convex surface of the steel pins or buttons on the back of the bearing shoes. The lower shoes exhibited more indication of wear than the upper shoes. The face of the shoes had experienced any loss of material but did show some indication of unique surface patterns, presumably due to pressure or heat. The outboard bearing showed little wear on the pins or bearing surface. The upper radial bearing half was removed and there was an area that appeared to be darker, perhaps from heat. Work is under way to remove the lower bearing half. In addition, the pump case to upper bearing housing O-ring is broken at the mating surface of the upper and lower bearing housings. Pictures are in the EDMS. The vendors have been contacted for assistance. <I> **** Actions Taken **** Discussed with supervisor/EOC. <N> **** Equipment Description **** T441 | 02-00-RFW-P-1B
394821 | CR | 20190603 | CAQ | D | (NRC Identified) HPCS Panel Cover Bolt Loose | Y | N |  | N | YES | <D> **** Detailed Description **** E-CP-DG/RP3 3rd panel bolt from the top is loose. There are 4 bolts holding the panel door closed. (NRC Identified). <N> **** Equipment Description **** HPCS panel bolt loose - E-CP-DG/RP3
394822 | CR | 20190603 | CAQ | D | FP-V-105 leaks by when closed. | N | N |  | N | YES | <D> **** Detailed Description **** Performing 15.3.15 FP-V-105 when closed leaked by , leak by has no effect on function of valve or system, make maintanence very difficult with the ammount of water flowing out when faceplate is removed. <I> **** Actions Taken **** Contacted PSRO | 02-00-FP-V-105,02-00-FP-V-W3A/042
394824 | CR | 20190603 |  | 4 | S-DOOR-S200 Latch is broken, doesn't close Fire Door | N | N |  | N | YES | <D> **** Detailed Description **** Service building door S-200 does not close all the way due to a faulty door latch. This is a Fire Door located in the Service Bldg. 456' level. <I> **** Actions Taken **** Wrote CR/WR <N> **** Equipment Description **** Service Building 456. | 02-00-S-DOOR-S200
394827 | CR | 20190603 | CAQ | D | MS-VPI-LVDT/3A AND 1B FFAILED CALIBRATION | N | Y |  | N | YES | <D> **** Detailed Description **** DURING PERFORMANCE OF ISP-MS-B901 AND 10.27.59, MS-VPI-LVDT/3A WOULD NOT CALIBRATE INTO VALUES NEEDED. MS-VPI-LVDT/1B DID NOT BRING IN ALARM (H13-P601.5.8 SRV OPEN) AND INDICATE GREEN LIGHT (SRV OPEN ON 601 PANEL). THIS WAS DUE TO THE TEMP MOD 17409. DURING LAST CYCLE THIS LVDT HAD ISSUES, SO THE TEMP MOD WAS PUT IN PLACE. <I> **** Actions Taken **** TALKED WITH SUPERVISION AND WE REPLACED BOTH VPI LVDT'S AND CALIBRATED SAT. WOT 0211164007 FOR MS-VPI-LVDT/1B AND WOT 0211164013 FOR MS-VPI-LVDT/3A. | 02-00-MS-VPI-LVDT/1B,02-00-MS-VPI-LVDT/3A
394828 | CR | 20190603 |  | 3 | PPM 8.3.49 is Not Scheduled for R24 | Y | N |  | N | NO | <C> Severity changed from CAQ C to 3 per MRT and RXSU added <D> **** Detailed Description **** PPM 8.3.49 is scheduled per PMID 14165. It is a 2-year PM that verifies leakage from the CIA "A" and "B" headers is within calculated values to verify the 30-day supply of backup nitrogen for ADS operation post-accident. The PM generated WO 02110175 is NOT scoped in to R24 and is still at status 22. This test renders the ADS nitrogen supply INOPERABLE and cannot be performed on-line within the 12 hour TSAS 3.5. .G for ADS valves inoperable. <I> **** Actions Taken **** Informed SM, OCC and EOC. Added this CR to T19-R24 -CIA/N2-SYS -001. <N> Per Emergent Issue Closure Notes: On 6/15/19 at 1000, we backed out of PPM 8.3.49 as its not required to be performed. Eng has evaluated and determined quantitatively that the system is acceptable as is, all leaks are minor and will not challenge Mode 2. Refer to R24 Emergent Issue #139.
394829 | CR | 20190603 |  | 4 | T2 sump has suspected oil in it. |  |  |  | N | YES | <D> **** Detailed Description **** T2 sump has suspected oil in it. FD-RMS-P/13 has been taken to off while the sump gets pumped to barrels and sampled by chemistry. This is potentially the cause of our recent high TOC issues in EDR/FDR. <I> **** Actions Taken **** RMS taken to OFF | 02-00-FD-P-13
394830 | CR | 20190603 |  | 4 | roll pin damaged on RFT-B speed probe bracket |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** A roll pin was damaged that is part of the bracket that holds the speed probes for B feed water turbine. It already has two allen-head bolts that hold it. I do not believe the pin is damaged enough to worry about it, but i would like engineering's input. <I> **** Actions Taken **** worte this cr and informed EOC Engineer Performed Walkdown and pin is very tight in place (even though extruded), cover does not rest on pin. Pin should remain as-is. This pin is not in the turbine OMM (below a level of detail) . <N> **** Equipment Description **** west side of speed probe mounting bracket on B feed water t urbine
394831 | CR | 20190603 |  | 4 | flex pulled from RFW-TE-55A |  |  |  | N | YES | <D> **** Detailed Description **** on reacotor feed water pump A, I found RFW-TE-55A had its flex pulled from it. needs repaired <I> **** Actions Taken **** wrote this cr | 02-00-RFW-TE-55A
394832 | CR | 20190603 |  | 4 | condulet cover gasket is wrong east of RFW-P-1A |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** condulet cover gasket is to big and will leak east of RFW-P -1A. Needs to be replaced <I> **** Actions Taken **** wrote this cr <N> **** Equipment Description **** east of RFW-P-1A and about 7 feet up
394833 | CR | 20190603 |  | 3 | Inadequate planning of restoration from TM EC 17264 |  |  |  | N | NO | <D> **** Detailed Description **** On 06/03/16 at 22:59, OPSPROC received notification via email that TM EC 17264 was removed from the field.. An assignment to prepare procedure revisions for this change was assigned to OPSPROC four minutes prior to sending the notification email. AR 392486-02 was assigned with a locked due date of 06/06/19 (less than 3 days). AR 394512 was submitted 05/30/19 for very similar inadequacies of the Engineering Change process. <I> **** Actions Taken **** Supervisor was informed of this repeat action. Submitted this AR for trending purposed.
394834 | CR | 20190604 | CAQ | C | WO 02101714-12 CRD-FCV-2A Returned | Y | N |  | N | YES | <D> **** Detailed Description **** The new proximity style position switches donâ€™t have a â€œNormally Closedâ€ contact with a termination and a â€œCommonâ€ termination. The CTI identifies lifting the â€œNCâ€ wire from the open switch, the â€œNCâ€ wire from the closed switch, one wire to the open switches â€œCommonâ€, and a jumper between the open and closed switch â€œCommonâ€s. The new switches have no termination points. They have four (4) leads coming out of them that need to be landed somewhere or spliced somewhere. The CTI in the EC doesnâ€™t reflect this or, at a minimum, identify what to do with â€œSpareâ€ wires. The Female connection on the new switches is Â½â€ and the old switches had all Â¾â€ hardware and flex. There are no lugs and or butt splices identified. All of the new parts need to be QCâ€™d. W.O.# 02101714-12 and/or EC 15866 needs more detail on new installation instructions. <I> **** Actions Taken **** Informed Electrical supervision. Informed OCC that Work order could not be worked as written. Craft walking over to talk with EOC. | 02-00-CRD-FCV-2A
394835 | CR | 20190604 |  | 4 | Daily Dose Report FAC Dose was Incorrect |  |  |  | N | NO | <D> **** Detailed Description **** After noticing FAC UT Top Ten Job actual dose was not increasing, investigation found one of the FAC UT Work Orders was incorrectly entered in the Spreadsheet. <I> **** Actions Taken **** Corrected WO entry in the Spreadsheet Corrected the FAC UT and Scheduled Actual dose on the Daily Dose Report. Informed Supervision.
394836 | CR | 20190604 |  | 4 | E-CB-S/6 NO CLOSED INDICATION LIGHTS LOCALLY OR IN MCR |  |  |  | N | YES | <D> **** Detailed Description **** Cycled E-CB-S/6 for WR 29149263. Both the MCR and local closed lights for E-CB-S/6 flickered momentarily and then wemt out after E-CB-S/6 was closed. Other than the lights the breaker operated normal. | 02-00-E-CB-S/6
394837 | CR | 20190604 |  | 4 | Fire door S-DOOR-S200 does not fully close on its own | N | N |  | N | YES | <C> Duplicate of AR 394824 <D> **** Detailed Description **** Fire door S-DOOR-S200 does not fully close on its own. It appears that the latching mechanism needs lubrication. <I> **** Actions Taken **** Informed CRS/SM, wrote this CR and WR. | 02-00-S-DOOR-S200
394838 | CR | 20190604 | CAQ | C | CRD-AO-11, part from BOM does not fit | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-AO-11 failed PMT and required rebuild, during disassembly it was discovered that the piston O-Ring does not fit correctly in the piston /cylinder. CAT ID-56406133 was called out in the BOM and installed, but even the spares in the ware house do not fit properly. the O-ring needs a larger cross section in order to work correctly. <I> **** Actions Taken **** Notified OCC and planning. Measured O-Ring - it is correct to the part number and description, but is NOT the right size. Reviewed history: it looks like this O-Ring has been installed in the last 4 outages and has had to be replaced due to leakage. this needs to have the correct size O-ring installed to prevent future needless rebuilds. <N> Re-opened this CR per request from Engineering CIC. Condition Adverse to Quality CRs cannot be closed to AR-EVALs. AR-EVAL 394934-01 conclusion: The new O-ring has the same form, fit and function as the original O-ring. It is the vendor recommended replacement component. A higher Durometer O-ring better resists the deformation under pressure that has been allowing air leakage to occur. Therefore, the new O-ring is considered acceptable for use in this application. | 02-00-CRD-AO-11
394839 | CR | 20190604 |  | 3 | Presence of radioactivity on new equipment |  |  |  | N | NO | <D> **** Detailed Description **** As part of our ongoing efforts for RFW FCV 10B, a new machining tool was received on site on 6/3/19. While the initial radiological receipt survey did not identify radioactivity, an additional survey assessment was performed an identified the presence of radioactivity. The secondary radiological assessment involved the use of a Tool and Equipment Monitor (TEM), for hoses and a filter on the equipment and all items alarmed the TEM. Following this TEM assessment, the equipment filter was taken to Chemistry for isotopic analysis and result identified the presence of radioactivity including Co-60 and Co-58. There was no loose contamination or smearable contamination identified as part of assessment. <I> **** Actions Taken **** This machining equipment was shipped to Columbia and identified as â€œcleanâ€ and did not have any identifiable markings indicating the presence of radioactive material. At this time that does not appear to be accurate based on preliminary radiological assessments to date. TEM data is captured on radiological survey document and a hard copy of isotopic resutls for fitler were provided to RP Mgmt. This equipment has been relocated into a posted RMA and labeled as radioactive material <N> Receipt of new welding machine for RFV-FCV-10B is documented on Survey VSDS_Prod-I-20190604-1. No further action required.
394841 | CR | 20190604 |  | 3 | 487 RW Decon Shower IPM-8M placed OOS - past due for cal |  |  |  | N | NO | <D> **** Detailed Description **** Due to lack of resources IPM-8M calibration was not completed by 6/3/2019 on 487 RW Decon Shower IPM-8M HP-EQ -C015124. Unit was tagged out of service at 00:00 6/4/2019. This is a resource availalbility and competing priority issue. <I> **** Actions Taken **** Notified OCC/RPM and Radiological Support HP Instrument SME. Requested support from dayshift HP instrument calibration qualified personnel. <N> IPM HP-EQ-C015124 has been calibrated, source checked and placed back into service. No further action required.
394845 | CR | 20190604 |  | 4 | Breaker E-CB-C1/4/CB2 was found tripped free |  |  |  | N | YES | <D> **** Detailed Description **** S1/4 voltage was trending down with the charger output at 132V (see CR 394633). Breaker E-CB-C1/4/CB2 (DC out) was found tripped. Breaker was reset and voltage was restored. This has happened before and recommendation was to replace breaker. <I> **** Actions Taken **** Breaker was reset | 02-00-E-CB-C1/4/CB2
394846 | CR | 20190604 |  | 4 | Water on RHR-B Pump room floor |  |  |  | N | YES | <D> **** Detailed Description **** Roughly 20 gallons of water was discovered covering approximately 50% of RHR-B pump room floor prior to performing step 5.2.43 of SOP-RHR-FILL. <I> **** Actions Taken **** Informed MCR Informed HP Investigated leak source, appears to be floor drains backing up. | 02-00-RHR-P-2B
394847 | CR | 20190604 |  | 4 | Bus 61/62 MCC OL Trip Locked In | N | N |  | N | YES | <D> **** Detailed Description **** Bus 61/62 MCC OL Trip has been locked in on P800-C2 drop 6-6 following SH-6 outage. Please investigate and repair before R24 is completed. <I> **** Actions Taken **** CR/WR | 02-00-E-SL-61,02-00-E-SL-62
394848 | CR | 20190604 |  | 4 | Bus 31 MCC OL Trip Alarm Locked In | N | N |  | N | YES | <D> **** Detailed Description **** Bus 31 MCC OL Trip Alarm is locked in on P800-C3 drop 7-4. MC-3B has the tripped indication on eDNA but the overload could not be reset locally. Investigate and repair. <I> **** Actions Taken **** CR/WR | 02-00-E-SL-31
394849 | CR | 20190604 | CAQ | D | Air/Gas Void detected, RHR Loop B | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** WO 02112560, RHR-B UT Fill Verification. VOID detected at Location #2, 6" Discharge Pipe at RHR-FE-12. Demension of void is 5 inch arc by 10 foot length. <I> **** Actions Taken **** Notified Operations and Engineering.
394851 | CR | 20190604 |  | 3 | CR Feedback Needed | N | N |  | N | NO | <D> **** Detailed Description **** Currently when a CR is generated there is no feedback given to who wrote the CR. We need a notification such as an Email to notify who wrote the CR on what actions were taken. There has been many times a CR was cancelled or taken care of but there is no way to know the status without looking that specific CR up in Portal J. <I> **** Actions Taken **** Notified supervision <N> **** Equipment Description **** .
394852 | CR | 20190604 |  | 3 | Lesson Learned for Drywell work | N | N |  | N | NO | <D> **** Detailed Description **** Performing work in the drywell requires planning and preparation to achieve dose ALARA. Electricians were performing work on PSR-V-X77A/1 (WO#02124415-07). This task is a funchtion check of the reed switches on a Target Rock valve. The work steps instruct to stroke the valve and verify proper indication in the control room and chemistry sample control panel. If indications were incorrect, then remove the cover of the valve and verify wiring matches the drawings and make switch adjustments to the appropriate switch (both instructions in the same signoff step). To me, since this valve was a newly installed replacement, the wiring and inspection should have been completed prior to being installed into the Drywell. Two electricians spent 30 minutes each to verify wiring in a tight space with difficult to read wiring labels in a HRA, a bench task would serve ALARA. <I> **** Actions Taken **** Discussed in morning D15 and write CR <N> **** Equipment Description **** PSR-V-X77A1 C506 AZ319
394853 | CR | 20190604 |  | 3 | improper storage of materials in the Plant | N | N |  | N | NO | <D> **** Detailed Description **** In the past two days I have found approx. 7 instances of improper storage of tooling/Misc items in the plant. Tooling was found without proper Staged For/Work IN Progress signage, as well as several items of PPE that appear to be abandoned in the main 441 Corridor. A discussion in each group D15 should be conducted to emphasize the expectation for station housekeeping standards. <I> **** Actions Taken **** Write CR and cleaned up as found messes. <N> **** Equipment Description **** various locations
394854 | CR | 20190604 |  | 4 | Work Stoppage and extra dose received. R24 LL | N | N |  | N | YES | <D> **** Detailed Description **** During performance of click testing in the Drywell on MSRV-1A, 1B, 3A, 3B, and 5B, communication with the control room was lost due to time pressure and lack of communication from the OCC. Communication with the control room for this work is established by a phone in the drywell and electricians were performing testing with the control room on the line when power to the phone was removed. Craft had no idea why this happened and tried to re-establish communication. While troubleshooting the issue, craft found another group in the drywell disconnecting all communication systems and temp power. When craft informed the group that they needed the phone for there testing, the group informed the craft that they were told by OCC that all work in the drywell was complete and all temp power and communication equipment needed to be removed. <I> **** Actions Taken **** Electricians and contractor group worked together to re-establish temp power for the communication equipment. After 1/2 hour of work stoppage and unnecessary dose taken, communication was finally re-stored and work was completed. | 02-00-MS-RV-1A,02-00-MS-RV-1B,02-00-MS-RV-3A,02-00-MS-RV-3B,02-00-MS-RV-5B
394855 | CR | 20190604 |  | 3 | Procedure change to SOP-RPS-START and SOP-RPS-START-QC | N | N |  | N | NO | <D> **** Detailed Description **** As verified by investigation under WR 29149220, holding the start button for RPS-MG-1(2) serves no purpose, as the start signal is sealed in immediately upon pushing the button. Correct procedures as follows: 1. Remove "AND HOLD" from SOP-RPS-START steps 5.1.2.c, 5.2.2.c., 5.6.3.c, and 5.7.3.c. 2. Remove "AND HOLD" from SOP-RPS-START-QC steps 2.1.2.b and 2.2.2.b. <I> **** Actions Taken **** As noted in WR 29149220, the procedure appears to have changed for no reason in Rev 7.
394858 | CR | 20190604 |  | 3 | System Description Manual SD000128 requires update | N | N |  | N | NO | <D> **** Detailed Description **** System Description Manual SD000128 requires update. EPN MS-V-72 listed on page 18 should be MD-V-72 as confirmed by AED MEC M657. <I> **** Actions Taken **** Initiated CR for document update.
394859 | CR | 20190604 |  | 3 | LL -Work Planned by wrong department planner. | N | N |  | N | NO | <D> **** Detailed Description **** Mechanical Planners continue to be assigned Electrical task. Packages often need to be edited due to lack of trade knowledge. <I> **** Actions Taken **** informed supervision
394862 | CR | 20190604 |  | 3 | R24LL: RHR-B testing logic ties |  |  |  | N | NO | <D> **** Detailed Description **** There were three sections of OSP-INST-B701 scheduled before lifting the RHR-B system clearance and they could not be performed until the system clearance was removed since the valves being tested per OSP-INST-B701 was being tagged closed via the system clearance order. . The Day 0 outage schedule was reviewed and it shows these OSP-INST-B701 scheduled after lifting the system clearance and logic tied indirectly to the lift clearance. However, during the window execution another LSFT was started before lifting the RHR-B system clearance (presumably to document closing a RHR-C valve to support the LSFT) and this appears to have pulled the three OSP-INST-B701 activities forward in the schedule before lifting the system clearance. Consequently, these OSP-INST-B701 activities rode the schedule for a few days until the RHR-B system clearance could be lifted. . Recommend all testing tasks have a direct predecessor to the lift clearance activity associated with the components being tested.
394863 | CR | 20190604 |  | 4 | R24LL: RB Door R106 opening affected by staged material |  |  |  | N | NO | <D> **** Detailed Description **** During R24, there were a few instances in which material was staged in the swing arc immediately outside of Reactor Building Door R106 (King Kong Doors) in the fenced area that hindered the ability to secure the south door. Recommend that an exclusion area be painted on the ground outside the doors showing the swing arc to preclude material storage within the arc. Rough sketch attached in EDMS. <I> **** Actions Taken **** Equipment was relocated outside of the swing arc prior to opening the doors. <N> **** Equipment Description **** R-DOOR-R106
394864 | CR | 20190604 |  | 3 | R24LL: Bill of Material Accuracy for Valve Parts |  |  |  | N | NO | <D> **** Detailed Description **** There have been a number of issues where the correct parts were ordered per the bill of materials for a valve but the parts don't fit. This is mostly related to gaskets and o -rings. . Recommend a review be completed post-outage of all the emergent material requests generated during R-24 to determine whether or not the Bill of Materials needs to be updated so that next time we work on these components we have the correct parts. . When applicable, actions should be initiated to update the bill of materials or other documents based on this review. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
394865 | CR | 20190604 |  | 3 | R24LL: Shipping Costs during R-24 |  |  |  | N | NO | <D> **** Detailed Description **** During R-24, we have had several material requests requiring air freight and other shipping costs. . Recommend we look at all emergent procurements from two angles: . 1. what parts did we buy during the outage for planned original scope, that did not involve discovery, where the initial planning did not order those parts? . 2. What parts were ordered due to discovery or expanded scope on work that was in scope prior to the outage starting? For these issues, what level of contingency evaluation was performed? . 3. Tally the amount of money spent expediting materials should have been ordered prior to the outage. . 4. Create an action for Outage Management to consider this information and update the contingency planning process as needed. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817. 11/4/19- moved from SCS to OTMG for tracking actions to completion.
394866 | CR | 20190604 |  | 4 | Contractor's unescorted access was inadvertently termed |  |  |  | N | NO | <D> **** Detailed Description **** Contractor has the same name of a temporary employee, but is in a differant org. The individual submitting the termination did not notice the org code differances while completing the termination. <I> **** Actions Taken **** Re-processed the contractor and his access was later restored after he re-applied for his unescorted access. Notifications were made to both organizations and I briefed the Security Services Manager. Please assign to org #52235
394867 | CR | 20190604 |  | 3 | R24LL: SOP-RHR-SDC revision needed for unavailability |  |  |  | N | NO | <D> **** Detailed Description **** Current revision of SOP-RHR-SDC indicates in step 5.1.16 that WHEN RHR SDC is initiated in Mode 3, . THEN ENTER RHR LPCI Loop A as inoperable and unavailable in the electronic logs. . This procedure should be reviewed to make it clear on when RHR unavailability should be recorded. RHR system is unavailable when it is in line-up for SDC mode and not at pump start. . And/or update procedure to use dedicated operator to maintain RHR-LPCI available. Reference AR 00393014 for guidance for required steps when using dedicated operator that needs to be included in the SOP-RHR-SDC procedure. . Recommend that the CR be assigned to Ops Procedures group. <I> **** Actions Taken **** Discussed this subject with Control Room Supervisor, System Engineer and my supervisor. . Recorded RHR-SYS-B as unavailable when placed in SDC line -up.
394868 | CR | 20190604 |  | 3 | CSP-DO-C101 needs minor revision |  |  |  | N | NO | <D> **** Detailed Description **** CSP-DO-C101 pag 8 for when they receive the results of the new fuel requires faxing of information. The fax numbers are not viable anymore. It is best if we scanned a pdf to a general email for the Warehouse and the QC Receiving dept. A copy of the marked up procedure will be in EDMS doc <I> **** Actions Taken **** Notified Chemistry supervision, Ware house Quality receiving.
394870 | CR | 20190604 |  | 4 | Relamp overhead lighting. (Bluedot) | N | N |  | N | YES | <D> **** Detailed Description **** Please relamp the following bluedot flourescent lights. Condensor bay SW corner and DG-2 west. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** 441 SW condensor bay. DG-2 W
394871 | CR | 20190604 |  | 3 | R24 Lessons Learned RB 606 Dose Savings | N | N |  | N | NO | <D> **** Detailed Description **** The slings to remove the moisture separator were rinsed down for approximately 20 minutes while they hung above the DSP. This is not usually done to such an extent, but should be done with future sling removals. The slings for the separator R23 highest reading on bags was *742/125 mrem/hr compared to highest reading this outage *180/40 mrem/hr, this is a significant decrease in dose rates. This will save dose and mitigate radiolocial risk associated with having to deal with bags of trash that create a High Radiation Area. See photo in EDMS <I> **** Actions Taken **** Informed RP Management. Presented ALARA Dose Savings cards to the HP Technicians and Laborers performing the work and recommending to rinse the slings aggressively.
394873 | CR | 20190604 |  | 3 | Truck driver access to RCAs while hooking up a shipment | N | N |  | N | NO | <D> **** Detailed Description **** A question was raised about monitoring truck drivers during access to a radiological controlled area (RCA) and/or radioactive material area (RMA) when picking up a trailer for off-site shipment. Site procedures do not cover the activity of placing a shipment into transport as it pertains to dose monitoring. DOT regulations do not require dosimetry or dose monitoring of truck drivers. Technical Basis 12-02 provided recommendations on how and when to monitor truck drivers during transportation activities in RCAs/RMA. The recommendations were not incorporated into site procedures. <I> **** Actions Taken **** RPM informed. Recommend reviewing TBD 12-02 for incorporation of recommendations into site procedures.
394874 | CR | 20190604 |  | 4 | HV-MO-31G water in actuator | N | N |  | N | YES | <D> **** Detailed Description **** HV-MO-31G actuator was removed to replace packing due to a steam leak. The actuator was found full of water and needs refurbished. | 02-00-HV-MO-31G
394876 | CR | 20190604 | CAQ | C | MT&E Found Out of Tolerance | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** CalCode #0063397 IET Labs Inc Model 1433-10 found OOT and required repair from manufacturer, Used during calibration cycle DEF #7049A <I> EFIN WILL EVALUATE USAGE AND WILL ATTACH EDMS Decade box failed tolerance @ 20ohm. All other settings passed on 4/16/19. Decade box was sent out for repair and all values are SAT (returned 5/28/19). Decade box was last used on WO #02105832-01 to simulate a load. Load setting under this WO was 108.25 ohms. No Impact to Plant SSC. No Action Required. DEF #7049A
394878 | CR | 20190604 |  | 3 | Emerson identified potential radio failure on CIM TTs |  |  |  | N | YES | <D> **** Detailed Description **** Cycle Isolation Monitoring (CIM) temperature transmitters (TTs) have been failing since installation in R23 (CR 383469). Diagnoses performed on 6/29 under WR 29148644,47,48,49 last week determined the potential of radio transmitter failures in addition to battery failures. Emerson engineers are recommending additional work to reset transmitters, reprogram transmitter network IDs, and attempt rejoin to network. Requesting follow-on work to above WRs with Emerson technician on 6/11 and 6/12 to diagnose transmitter issue. Battery replacement WR 29149170 can continue as planned through FIN I&C. The transmitter radio failure is an issue Emerson has not encountered and may be due to gamma radiation damage. Recommend Design Engineering assess potential radiation protection/qualification. <I> **** Actions Taken **** Initiated CR. Discussed radiation field assessment with Design Engineering. Discussed the diagnosis needed for the transmitters with EOC. Initiated plans for vendor to make second visit to site. Initiated AR EVAL 394927 for long-term assessment action indicated in this AR CR 394878. | 02-00-BS-TT-DV/5A,02-00-HV-TT-RV/17A,02-00-HV-TT-RV/20A,02-00-HV-TT-RV/20B,02-00-MS-TT-RV/116A,02-00-MS-TT-RV/116B,02-00-MS-TT-RV/116F,02-00-MS-TT-V/189,02-00-MS-TT-V/234
394879 | CR | 20190604 |  | 3 | Adjust float of the thrust bearing in RFP-B |  |  |  | N | YES | <D> **** Detailed Description **** Axial float of the B RFP to be adjusted to .005-.009â€ This is per the vendor reccomendation. Revise PPM 10.18.3 and all other applicable procedures as needed. <I> **** Actions Taken **** CR generated. OOC notified. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications | 02-00-RFW-P-1B
394880 | CR | 20190604 | CAQ | D | Issue draining RHR-FIS-10B per 0211561213 | Y | Y |  | N | YES | <D> **** Detailed Description **** Issue draining RHR-FIS-10B per 0211561213. <I> **** Actions Taken **** Instrument drain valve #V75 maybe plugged. | 02-00-RHR-FIS-10B
394882 | CR | 20190604 |  | 3 | Recommended Enhancements to Procedure CI-12.22 | N | N |  | N | NO | <D> **** Detailed Description **** Procedure CI-12.22 (Gas Chromatography) Section 7.1 could benefit from minor enhancements to reflect laboratory practice and improve ease of use during system start-up. <I> **** Actions Taken **** A field copy of the current procedure with the suggested changes has been provided to the instrument specialist who owns the system.
394883 | CR | 20190604 |  | 4 | HV-MO-31B breaker failure during PMT | N | N |  | N | YES | <D> **** Detailed Description **** During HV-MO-31B PMT 02120350-06 the breaker failed to energize. Will need repairs to breaker before PMT can be completed. <I> **** Actions Taken **** Contacted Valve Project Manager and initiated Work request | 02-00-MS-MO-115B
394884 | CR | 20190604 |  | 3 | R24LL: Revisions to TSP-RCS-R801 and TSP-RCS-R802 needed | N | N |  | N | NO | <D> **** Detailed Description **** TSP-RCS-R802 was revised on 6/3/19 to allow LLRT testing of RHR-V-53B while the system was aligned to the condensate storage & transfer system via RHR-V-63B. After reviewing other sections of the procedure, it was identified that other sections of the procedure need a similar revision. Additionally, TSP-RCS-R801 for division 1 systems could beneifit from similar revisions. Marked up copies of TSP -RCS-R801 and TSP-RCS-R802 included in EDMS. <I> **** Actions Taken **** Wrote this CR and provided proposed mark-ups.
394886 | CR | 20190604 |  | 3 | R24LL - evacuate area near MSIVs prior to stroke test |  |  |  | N | NO | <D> **** Detailed Description **** Operations announced to stay clear of inboard MSIVs during valve stroke testing. Individuals in or near the drywell did not heare the message. Please add step to procedure to contact drywell HP control point or DW coordinator to ensure no one is in the line of fire during the test and call again after test is complete. contact drywell personnel to evacuate drywell MSIV area <I> **** Actions Taken **** Spoke to Shift Manager and drywell control points, as well as RO performing test. Ensured no work group was in line of fire.
394887 | CR | 20190604 | CAQ | D | Damaged Threads on RHR-RV-25B Outlet Flange Joint Test Point | Y | N |  | N | YES | <D> **** Detailed Description **** While performing WO 02129659-07 to support a visual check for leakage on the outlet flange joint of RHR-RV-25, a cross-threaded pipe cap was removed from the test point revealing stripped threads. Of the 6 showing threads, 3 are damaged. As the Work Order Instructions state, this is a "Primary Containment Extension" system boundary. The pipe cap cannot be reinstalled and the test to pressurize the joint was stopped. <I> **** Actions Taken **** Test stopped, FIN team notified. <N> **** Equipment Description **** RV located at RB477 M/8.2 South Valve Room | 02-00-RHR-RV-25B
394888 | CR | 20190604 |  | 4 | TSW 47'1 Nalco corrosion monitor needs repair |  |  |  | N | YES | <D> **** Detailed Description **** During the performance of training it was noted that the faceplate was missing from the Nalco corrosion monitor at the 471' TSW hot leg corrosion coupon station. This is less than ideal as the electronics are open to the environment and could become damaged. Recommend repair or replacement. The equipment appears to still be functioning normally. <I> **** Actions Taken **** Chemistry specialist/supervision informed <N> **** Equipment Description **** TSW hot leg Nalco corrosion monitor - 471 Turbine bldg
394889 | CR | 20190604 | CAQ | B | Upon starting RHR-P-2B and opening RHR-V-24B per SOP-RHR | Y | N |  | N | YES | <C> RISK: MEDIUM CAUSE: UNCERTAIN Severity B, Investigation Template Required <D> **** Detailed Description **** Upon starting RHR-P-2B and opening RHR-V-24B per SOP-RHR -SPC, indication of flow was unchanged. Amps and pressure tracked as expected. RHR-FCV-64B did not close as expected. See pictures. <I> **** Actions Taken **** Secured RHR-P-2B. <N> **** Equipment Description **** MCR | 02-00-RHR-FI-603B
394890 | CR | 20190604 |  | 4 | E-TR-HSSF Leak |  |  |  | N | YES | <D> **** Detailed Description **** While verifying N2 tank level at HSSF, I noticed a leak on E-TR-HSSF. There was a thin film of oil on the bottoom of the transformer/concrete, approximately a cup of oil spread out over 100 in2. No flowing oil was visible. It looks to have been there a while. Please investigate. <I> **** Actions Taken **** Notified MCR. | 02-00-E-TR-HSSF
394891 | CR | 20190604 |  | 4 | AR closed with no assignments or notes on how it was correct |  |  |  | N | NO | <D> **** Detailed Description **** AR 00394699 was Closed as COMP-NA with no cross referenced WR or WO that fixed the issue on HPCS-B1-DG3. The AR was Priority CAQ. There were no notes to allow closure.
394892 | CR | 20190604 |  | 3 | COND-V-119A, COND-V-119B disc to body interference |  |  |  | N | YES | <D> **** Detailed Description **** After packing, when COND-V-119A / B are stroked full open the discs remain in the open position as a result of the disc resting on the body hinge pin boss due to wear on the hanger arm / disc stud hole. When the hanger arm shaft is moved to the point where the discs no longer contact the body the valves will close due to gravity. <I> **** Actions Taken **** Provided pictures to EOC for further evaluation of the condition. <N> **** Equipment Description **** TB 449 E/8/15.4 | 02-00-COND-V-119A,02-00-COND-V-119B
394893 | CR | 20190604 | CAQ | C | RHR-RV-88B leaking outlet flange gasket | Y | N |  | N | YES | <D> **** Detailed Description **** The outlet flange double oring seal was tested with ~39 psig on RHR-RV-88B. It was found to be leaking at the 12, 3, 6 and 9 oclock position on the flange, the worst leak being at the 6 position (bottom). Total leakage per the I&C testing equipment was 18 SCCM. Flange bolts felt tight. | 02-00-RHR-RV-88B
394894 | CR | 20190604 | CAQ | D | Peform partial TSP-LSV-C501 for CRD-P-1B | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-P-1B is tagged for CRD outage and is not available for load shed funtional verification. Per attachment 10.3 of TSP-DG2/LOCA-B501, initiated WR/CR to document need to perform test after CRD-P-1B is availavble to test. <I> **** Actions Taken **** Work to be performed oper WO task 02142197-05 | 02-00-CRD-P-1B
394895 | CR | 20190604 |  | 4 | R24 LL COND-V-119A/B/C |  |  |  | N | NO | <D> **** Detailed Description **** All materials were not on-site prior to the outage in support of COND-V-119A/B/C Scope. Specifically, key materials were not on-site nor were various gaskets. These materials on 119C were ordered on January of 2019, while 119A/B materials were not ordered until April of 2019. Future scopes must have materials ordered as soon as possible (MRs generated as soon as scope is approved following scope approval or after scope changes are approved). Additionally, systems should not be breached unless we have validated all parts are on site and have had eyes laid on the parts. <I> **** Actions Taken **** Generated CR for LL purposes.
394896 | CR | 20190604 |  | 3 | Damaged insulation on BS-V-8B |  |  |  | N | NO | <D> **** Detailed Description **** Under work order 02110998-08 Insulation was needed to be installed on the BS-V-8A. When craft arrived at the valve, it was noticed that the scaffold was covered with Calcium Silicate insulation from the side of BS-V-8B nearby. The insulation from the side of this valve was damaged beyond repair. Valve 8B now needs to be stripped of remaining Calcium Silicate insulation and will need to have new pad insulation fabricated and installed. Request Engineering and Operations to review the damaged insulation. Planning to generate a work order task to repair the insulation. <I> **** Actions Taken **** Notified supervision of the damaged found, took pictures and initiated condition report. <N> At the request of maintenance and supplemental maintenance supervision (see email in EDMS) the EPN in the title and body of CR was corrected. WO 02110992-21 created to correct condition. No further actions required.
394897 | CR | 20190604 |  | 3 | R24 LL RFW-V-10B Contingency Planning & Execution |  |  |  | N | NO | <D> **** Detailed Description **** Execution of the hard seat installation for RFW-V-10B has demonstrated that planning, preparation, and execution of contingent work orders must be improved. The hard seat installation contingency was not appropriately reviewed and planned for, reflected in the planned durations / resources for that scope (ex: original duration was 80 hours and multiple shifts beyond that were required). Additionally, tooling and equipment necessary to efficiently prepare the hard seat surface was not readily available / staged and would not line up when it did arrive on site. Finally, the full risks of the hard seat installation was not fully understood, leading to the need to perform a weld build-up on the swing arm backstop to prevent valve binding during operations. <I> **** Actions Taken **** Generated LL. Future contingencies (specifically level 5 contingencies) must be fully vetted, with equipment available to meet planned durations, prior to the outage. Additionally, consideration should be made as to whether perform level 5 contingencies as actual scope in an outage rather than a possibility (if we had the right equipment and tooling lined up we would have likely completed the scope in a significantly shorter duration).
394898 | CR | 20190604 |  | 3 | R24LL:Enhance the ECCS fill procedures and monthly OSPs |  |  |  | N | NO | <D> **** Detailed Description **** Recommend revising the SOP-RHR-FILL and OSP-RHR-M101,M102, and M103 procedures to ensure the OSP is performed in conjunction with the fill procedure. Both procedures require venting and NDE (if the system was drained). The two procedures should be performed concurrently if the system will be returned to operable status following the fill in order to avoid rework. Similar changes should be made to procedures for HPCS, LPCS, and RCIC. Also, the OSPs require determining the amount of air vented from the system using a stopwatch to measure how long it takes between opening the vent valve until a steady stream of water is observed. This step is not relevant when performing a system fill. Recommend providing guidance to address this as well.
394899 | CR | 20190604 | CAQ | D | FM dropped inside pipe downstream of RFW-FCV-10B |  |  |  | N | NO | <D> **** Detailed Description **** While setting up for installation of boring machine on RFW-FCV-10B, a piece of metal measuring approximately 2. 5x2.5.0.5 inches fell inside the piping, defeated the installed FME device and fell into the pipe. Workers stopped work and notified supervision. <I> **** Actions Taken **** FM piece was succesfully retrieved, writing this CR for trending. No further action required.
394900 | CR | 20190604 |  | 3 | (LL R24) COND-EJ-2A/C Replacements |  |  |  | N | NO | <D> **** Detailed Description **** (LL R24) During the removal of the COND-EJ-2A and COND-EJ -2C the expansion could not be removed due to COND-V-103A and COND-V-103C being open. A review of the clearance order did not have these valves listed. At no time was no issue with the clearance boundary concerning personnel safety. The job was stopped and a caution clearance was hung by operations to have these valves closed so the expansion joints could be removed. Recommend the clearance order for removal and re-installation of COND-EJ-2A, 2B, and 2C be revised to include these valves as part of the clearance and tagged closed. <I> **** Actions Taken **** Discussed with Operations, Mechanical Maintenance and initiated this lessons learned CR
394901 | CR | 20190604 |  | 4 | SO-V-256/4 operator missing lock screw. |  |  |  | N | YES | <D> **** Detailed Description **** SO-V-256/4 operator spins free due to missing lock screw. Unable to operate properly with out. <I> **** Actions Taken **** Informed Supervisor. | 02-00-SO-V-256/4
394902 | CR | 20190605 | CAQ | D | Fire Door R203 not latching properly | N | N |  | N | YES | <D> **** Detailed Description **** The R203 Fire Door at the A-6 stairwell exit 471 is not latching properly. It was not closed completely upon arrival to the door, and it did not latch when allowing the door to close on its own. <I> **** Actions Taken **** Spoke to PSRO office, initiated this CR & WR. | 02-00-R-DOOR-R203
394903 | CR | 20190605 |  | 4 | Work order 02111021 PMT task returned. |  |  |  | N | NO | <D> **** Detailed Description **** Work order 02073567-04 was returned back to planning. The work order does not clearly define which steps of referenced PPM 8.3.353 to perform while operations performs the procedure. Discussed the issues with the OCC prior to taking the package to status 23. <I> **** Actions Taken **** Generated CR to document issues encountered withwork order. Contaced OCC.
394905 | CR | 20190605 |  | 4 | Cond Booster pump reliefs lifted when starting a TSW pump |  |  |  | N | YES | <D> **** Detailed Description **** TSW-RV-117B and 117C lifted when starting a second TSW pump. TSW-V-3B and 3C were closed to isolate TSW leaking onto the TB 441 floor from entering the T4 sump. TSW-RV -117C was able to be reset and TSW-V-3C was restored to open but TSW-RV-117B would not reset. TSW-V-3B is still closed and out of its normal position. <I> **** Actions Taken **** isolated the TSW to the HX's and | 02-00-TSW-RV-117B,02-00-TSW-V-3B
394906 | CR | 20190605 |  | 4 | Unable to work CSP-SPV-9 |  |  |  | N | YES | <D> **** Detailed Description **** CSP-SPV-9 WO#02117710-10 Electrical conduit that supplies power to SPV-9 also supplies power through the same T-fitting to RFW-SPV-32A-2, which had a tag on it that read spared-closed. We would be unable to remove the conduit fitting with the 32A-2 wires in the conduit. We need additional direction on what to do with the 32A-2 wires. We also need mechanical support tasks to remove and re -install the piping that supplies air to the valves. <I> **** Actions Taken **** Stopped work and notified supervisor of the condition, returned the WO. <N> **** Equipment Description **** CSP-SPV-9
394907 | CR | 20190605 | CAQ | D | MS-V-22A indicates dual when closed | Y | N |  | N | YES | <D> **** Detailed Description **** MS-V-22A indicates dual when closed. This prevents completion of PPM 8.3.182. <I> **** Actions Taken **** Informed maintenance, OCC. Initiated CR/WR | 02-00-MS-V-22A
394908 | CR | 20190605 |  | 4 | Unable to work CSP-SPV-6 |  |  |  | N | YES | <D> **** Detailed Description **** CSP-SPV-6 WO#02117709-01 Electrical conduit fitting for splicing is located approx. 24 inches away from the valve. The wire supplied with the valve are only approx. 12 inches. We need additional direction on how to splice the wires so they can reach the conduit fitting. We need mechanical support tasks to remove and re-install the piping that supplies air to the valves. <I> **** Actions Taken **** Stopped work and notified supervisor. Returned the WO. <N> **** Equipment Description **** CSP-SPV-6
394909 | CR | 20190605 |  | 4 | Nicked Tubing by SS-V-750B | N | N |  | N | YES | <D> **** Detailed Description **** While installing the new valve at SS-V-42B Per. work order 02114723-01, welder nicked the tubing on the high pressure side of SS-V-750B with a grinder. It did not penetrate the tubing however the tubing should be evaluated for replacement <I> **** Actions Taken **** Welder stopped the job, put it in a safe condition and notified supervision. CR and Work request initiated | 02-00-SS-V-750B
394910 | CR | 20190605 |  | 3 | EDR-TK-4A and FDR-TK-9 x-fer to the CST with high TOC |  |  |  | N | YES | <D> **** Detailed Description **** EDR-TK-4A and FDR-TK-9 have been released to the CST with out of specification results for TOC. The water in these tanks has been processed for 72 hrs with no reduction in TOC concentration. High TOC precoats have been used and the septa have been backwashed and pre-coated multiple times. The issue was raised to the OCC due to a diminishing usable volume in the radwaste system. The decision was made by the group to release these tanks to the CST to allow radwaste processing to continue. A sample of the CST will be analyzed for TOC after the transfers have been made. EDR-TK-4A TOC = 1630 ppb FDR-TK-9 TOC = 504 ppb <I> **** Actions Taken **** Notified supervision, OCC, radwaste operator. | 02-00-EDR-TK-4A,02-00-FDR-TK-9
394916 | CR | 20190605 | CAQ | C | R-DOOR-R408 was found with cables routed under it | N | Y |  | N | NO | <D> **** Detailed Description **** Door R408 was found with an extension cable and phone cable routed under it. The cable was routed from TLC-11 into the overhead of the MCC room. This door is an essential fire barrier covered under LCS 1.10.5. <I> **** Actions Taken **** Notified MCR, entered LCS 1.10.5, issued barrier impairment, and added to hourly fire tour. <N> BIP 19-0261. L19-R-DOOR-R408-001.
394917 | CR | 20190605 | CAQ | D | MS-V-22A slow closure time not met | Y | N |  | N | YES | <D> **** Detailed Description **** per 8.3.182, MS-V-22A had a closure time of 75.19 seconds against an expected time of 20 - 60 seconds. This is not a Tech Spec or Regulatory commitment. But is used to determine whether or not the slow close stroke time requires adjustment. <I> **** Actions Taken **** informed OCC, Electrical shop, and shift manager <N> Added to T19-R24-MSIV-OUTAGE-001 for reference. Per system engineering the slower stroke time to close is acceptable. The acceptance criteria is not TS or otherwise a commitment related criteria. | 02-00-MS-V-22A
394918 | CR | 20190605 | CAQ | D | M&TE Rejected |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0065885 Starrett Dial Caliper- model 1202 8" found OOT & Rejected.EFIN Eval: CR #393295 generated for late EVAL. Usage #1-2 ID Measurements not taken Per W/O & Person In org 52233. No Impact. Usages #3-6 Information only Per Org 52233. No Impact. Rejected- Broken Beyond Repair. DEF #6998A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only. <N> Names removed from CR.
394919 | CR | 20190605 |  | 4 | Personal Medical Condition â€“ Transport Off-Site |  |  |  | N | NO | <D> **** Detailed Description **** On Wednesday, June 5, 2019 an Energy Northwest employee experienced a personal medical condition at the Palouse Building (B9). A 2222 call was placed at 4:42 a.m. A medical responder tone out was initiated by the control room per PPM 1.9.14. The patient was evaluated by medical responders. Hanford Fire Department (HFD) Medic 1923 arrived at 5:00 a.m. followed by Ladder 1923 and Engine 1913. The patient was further evaluated by HFD and transported to Kadlec Medical Center at 5:23 a.m. <I> **** Actions Taken **** The employee is from organization 52251. An acting supervisor left site to meet the patient at Kadlec Medical Center. Emergency Preparedness was notified of the event for ERO purposes. OI-34 completed.
394920 | CR | 20190605 | CAQ | D | SPVD Channel 5 Force Indication | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of 10.27.55, step 1.1.3 of attachment 9.3 directs using SPVD console to verify Force and Lift function for associated SRV load cells and LVDTs. While testing SPVD Channel 5, SRV 2B, Force indication was reading in a negative value while Max lift indication was increasing the in positive value. All other valves tested in attachment 9.3 displayed positive Force and Lift indications. <I> **** Actions Taken **** Contacted supervisor, engineering, operations. Directed to continue 10.27.55 to restore CIA-V-764 and CIA-V-766 to normal configuration, closed, and continue with procedure.
394921 | CR | 20190605 |  | 4 | CAS-C-1A oil level low. | N | N |  | N | YES | <D> **** Detailed Description **** Found CAS-C-1A oil level low & not in sightglass. There is a residual oil level line there giving the impression of oil present. There was low oil level recently in the last few weeks also. Recommend cleaning sight glass to remove likely hood of false readings, filling with oil, and looking for leaks. <I> **** Actions Taken **** Informed MCR, FIN, initiated AR | 02-00-CAS-C-1A
394922 | CR | 20190605 |  | 4 | TSP-DG2/LOCA-B501 RHR-P-2B breaker closure timing | Y | N |  | N | YES | <D> **** Detailed Description **** At 0043 this morning we performed step 7.2.28 of TSP -DG2/LOCA-B501. According to Histogram data per SOP -COMPUTER-OPS the DG2-8 shut at time 00:43:31.141 and RHR -P-2B breaker closure at time 00:43:37.184 this is a difference of 6.043 seconds. When day shift came in to review the data it was compared to data on EDNA trend. This data states that the time is about 5 seconds. I have attached the data to this CR. The specification per attachment 10.2 is 3.34 to 5.79. The HISTOGRAM data per the procedure is UNSAT <I> **** Actions Taken **** cr was created to document unsat test Computer engineering was contacted and notes from KPeters3 uploaded into general notes. The ENW.CGSHS points are equivalent to the MCR.CGS points. See IOD for more details. <N> This surveillance requires sub-second resolution to meet the criteria. The current pre-built data plots are only 1 sample / second (sps) for the data rate. High speed data streams will be required to ensure precise calculation of timing. MCR.CGS.X128-09 is equivalent to ENW.CGSHS.X128-09. MCR.CGS.X288-07 is equivalent to ENW.CGSHS.X288-07. ENW .CGSHS is the high-speed (~15sps) data stream associated with data on ENW.CGS and MCR.CGS. Data for this surveillance should be taken from ENW.CGSHS (corporate net)
394923 | CR | 20190605 |  | 3 | New rev. to 1.3.29 needs revision | N | N |  | N | NO | <D> **** Detailed Description **** New revision to 1.3.29 added DSA-V 81A and 81B to locked valve checklist. These valves are operated every shift to blow down the accumulators and sometimes up to3 times a shift for compensatory actions (6 times/day). These valves need to be removed from 1.3.29. <I> **** Actions Taken **** Contacted Operations manager and operations procedure writers.
394925 | CR | 20190605 |  | 4 | changed screens on RFW-CRT-L003 and it went blank | N | N |  | N | YES | <D> **** Detailed Description **** while working WR 29149215 changed screens on RFW-CRT-L003 and it went blank. <I> **** Actions Taken **** Notified supervisor <N> **** Equipment Description **** RFW-CRT-L003 | 02-00-RFW-CRT-L003
394926 | CR | 20190605 |  | 4 | TSP-DG2/LOP-B501 DO-TK-3B level check | N | N |  | N | NO | <D> **** Detailed Description **** Step 7.1.17 was not completed per TSP-DG2/LOP-B501. DO -TK-3B was checked per 7.1.18 of TSP-DG2/LOCA-B501 the end of day shift just prior to LOCA testing . In between the LOCA and LOP test SOP-DG2-STBY was completed. <I> **** Actions Taken **** CR to document <N> This surveillance requires sub-second resolution to meet the criteria. The current pre-built data plots are only 1 sample/second (sps) for the data rate. High speed data streams will be required to ensure precise calculation of timing. MCR.CGS.X128-09 is equivalent to ENW.CGSHS.X128-09 MCR.CGS.X288-07 is equivalent to ENW.CGSHS.X288-07 ENW.CGSHS is the high-speed (~15sps) data stream associated with data on ENW.CGS and MCR.CGS. Data for this surveillance should be taken from ENW.CGSHS located on the corporate eDNA system.
394929 | CR | 20190605 |  | 4 | RW 437â€™ Forklift Cannot Charge | N | N |  | N | NO | <D> **** Detailed Description **** The battery powered forklift on RW 437â€™ cannot be charged. The battery charger cannot be connected to MC-5D. It appears to be missing an adapter. <N> **** Equipment Description **** MC-5D
394930 | CR | 20190605 |  | 3 | Full Text Search - Control Room Logs | N | N |  | N | NO | <D> **** Detailed Description **** The sharepoint full text search for control room logs does not appear to work for log entries made after the logs were transitioned to eSOMS. . Please investigate and correct.
394931 | CR | 20190605 | CAQ | D | WOA-V-52E indicates duel position. | Y | N |  | N | YES | <D> **** Detailed Description **** WOA-V-52E indicates duel position, Locally it indicates closed. | 02-00-WOA-V-52E
394933 | CR | 20190605 | CAQ | D | Received RHR PMP 2B RM HVAC OUT OF SERVICE | Y | Y |  | N | YES | <D> **** Detailed Description **** Received RHR PMP 2B RM HVAC OUT OF SERVICE Annunciator BISI When starting RHR-P-2B in suppresion pool cooling per SOP-RHR-SPC. Per ARP verified RRA-FN-3( RRA-42-8F4E) was closed in and verified locally that RRA-FN-3 was running. BISI for RHR B RM HVAC OOS cleared on its own ~ 40 minutes later. <I> **** Actions Taken **** Informed CRS/SM | 02-00-RRA-RLY-80/FN3
394937 | CR | 20190605 | CAQ | D | CIA-TK-12A leaking at regulator | Y | N |  | N | YES | <D> **** Detailed Description **** CIA-TK-12A leaking at regulator lower threaded connection. When placing in service per SOP-CIA-OPS the connections were snooped checked and leakage was odserved from threaded connection. <I> **** Actions Taken **** Contacted supervision, isolated bottle and wrote AR/WR. | 02-00-CIA-TK-12A
394938 | CR | 20190605 | CAQ | D | RCIC Tank Level in Alarm Prematurely | Y | N |  | N | YES | <D> **** Detailed Description **** H13-P601.A4.3-6 â€œRCIC Condenser Vac Tank Level Highâ€ alarm is locked in. Ops 2 reports that the tank level is LT half full, so the alarm should not be in. The alarm was received while performing LSFT OSP-INST-B701 Section 7.16. Some minor mechanical agitation was externally applied to the level switch, to no effect. | 02-00-RCIC-LS-11
394940 | CR | 20190605 |  |  | HV-MO-31B breaker failure during PMT | N |  |  | N | YES | <D> **** Detailed Description **** During HV-MO-31B PMT 0210350 the breaker failed to energize. Will need repairs to breaker before PMT can be completed. | 02-00-HV-MO-31G
394941 | CR | 20190605 |  | 4 | Recirc A motor winding coolant leakage alarm in the MCR | N | N |  | N | YES | <D> **** Detailed Description **** Recirc A motor winding coolant leakage alarm in the main control room. This alarm is from RRC-LS-3A or RRC-LS-4A high level. The alarm came in and cleared on its own 2 hours later. No known work on this equipment was in progress at the time <I> **** Actions Taken **** Inform CRS <N> canceled by mistake when attempting to close the CR. | 02-00-RRC-LS-3A,02-00-RRC-LS-4A
394942 | CR | 20190605 |  | 3 | undeclared alcohol at the checkpoint |  |  |  | N | NO | <D> **** Detailed Description **** Undeclared alcohol at the checkpoint. Individual (org. 54113) was denied access and supervison was notified, Benton County was notified. <I> **** Actions Taken **** Shift Manager and Security Management notified. Benton County was called off. CR generated <N> **** Equipment Description **** Security Checkpoint
394943 | CR | 20190605 | CAQ | D | MT&E Found out of tolerance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** CalCode #0065702 Proto Model 6014Cwas found OOT, Usage #1: Per PPM 1.5.4 section 4.4.3 (a-c) Torque Wrench had acceptable post use verification @ +/- .06%. No Action Required.Usage #2 EFIN will have to do an Evaluation on this Torque Wrench. Person In org 52237 was notified concerning WO #0211198-01 & WO #0211689-01. DEF #7050A written. EDMS will be attached when complete. <N> DEF #7050A Name removed from CR.
394944 | CR | 20190605 |  | 4 | HV-MO-31B breaker failure during PMT | N | N |  | N | YES | <D> **** Detailed Description **** During HV-MO-31B PMT 0210350 the breaker failed to energize. Will need repairs to breaker before PMT can be completed | 02-00-HV-MO-31B
394945 | CR | 20190605 |  | 4 | S-CE-27A failed downscale | N | N |  | N | YES | <D> **** Detailed Description **** During a recent power transfer, S-CE-27A failed downscale. The Hi conductivity alarm on S-CR-24 pt 2 had been in due to RWCU 'A' being offline, but cleared and the display changed to "-OVER" Recommend investigating S-CE-27A for proper operation <I> **** Actions Taken **** Informed Chemistry | 02-00-S-CE-27A
394947 | CR | 20190605 |  | 3 | Add contigency task to PMIDs for future outages |  |  |  | N | NO | <D> **** Detailed Description **** Add contigency task to PMIDs for future outages. PMID 8682, 8683, 8684, 8685, 8687, 8688, 8689, 8690 for 8.3.182 need to have a task added if section 8.10 needs performed to adjust the slow close speed. <I> **** Actions Taken **** Wrote this AR to drive excellence <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
394949 | CR | 20190605 | CAQ | D | LOU not incorporated into work instructions. |  |  |  | N | YES | <D> **** Detailed Description **** CAT ID 39064 was ordered under WO 02145020-01 and the work order was not revised to include steps to satisfy the LOU. <I> **** Actions Taken **** CR written. Engineering notified. <N> AR EVAL 394934 and DNC AS 394934-01 have been created for accept as-is evaluation of this condition. CRD-AO-11 | 02-00-CRD-AO-11
394950 | CR | 20190605 |  | 3 | R24LL- RHR-RV-88B PMT- does not need LLRT test |  |  |  | N | NO | <C> MRT change request on 6/7/2019 from Severity C to NON-CAQ 3. <D> **** Detailed Description **** WO 02129667-10 step 4.1 had the retest of the RHR-RV-88B replacemtn do a LLRT on the outlet flange between the gaskets. This test is not required any more. A visual leak test with the system in service is prefered. Recomend changing the WOs for RHR-RV-88A and B replacement to only do a visual leak test with the system runnig in the future.
394951 | CR | 20190605 |  | 3 | Approved deviation from SWP-CAP-01 |  |  |  | N | NO | <D> **** Detailed Description **** CR 393438 was initiated on 5/14/19 and graded per SWP-CAP -06 as not a condition adverse to quality severity 3. Additional information revealed that this issue is being viewed by the NRC as a potential greater than minor non -cited violation. The CR was rescreening per SWP-CAP-06 on 6/5/19 and determined to by a condition adverse to quality severity B (medium risk, cause uncertain) and requires an investigation template. SWP-CAP-01 requires the investigation template be completed within 30 days from the date of initiation and does not take into consideration issues that are rescreened. It is not feasible to expect a quality product in 9 days, therefore, procedure deviation was approved to allow 30 days from the date the rescreen was approved. Performance Improvement Manager approved this deviation. <I> **** Actions Taken **** Recommend assignment to AR-PERFIMP to revise SWP-CAP-01.
394952 | CR | 20190605 |  | 4 | Report of Load Lift Over Workers |  |  |  | N | NO | <D> **** Detailed Description **** Received a report of a container being lifted to the TG roof was lifted in a manner that allowed individuals to be placed under the lifted load. The project manager conducted a stand-down with the mobile crane crew to address the concern and to re-emphasize ISPM-5 standards and requirements. <I> **** Actions Taken **** 1) Obtained reports from mobile crane crew for facts of the event. 2) Conducted a mobile crane crew stand-down to re-emphasize ISPM-5 standards and requirements for mobile crane use and lifting loads. 3) Project manager performed observation of mobile crane operations to ensure ISPM-5 standards and requirements for mobile crane use and lifting loads are being adhered to. 4) Increased the number of spotters to ensure personnel are kept out of the load path. 5) Reported these actions to Industrial Safety and requested additional observations during load lifting operations. 6) OCC was informed.
394953 | CR | 20190605 |  | 4 | (Non EN/CGS) Calibration Reports reflected torque screwdrive |  |  |  | N | NO | <D> **** Detailed Description **** (Non EN/CGS) Calibration Reports reflected torque screwdriver instead pf torque wrench in description Received email from customer on 06/05/2019 Email from Kim Rogers with Wagstaff Applied Technology that asset calibration reports for WEI-2413 and WEI-2414 were described as torque screwdrivers and should be torque wrenches. Generated customer complaint #189. <I> **** Actions Taken **** Reviewed original PO and model # to confirm the correct description and reprinted reports with the correct description and scanned to customer. Originals will be mailed to customer.
394954 | CR | 20190605 |  | 4 | R24LL Materials ordered after Planning Milestone |  |  |  | N | NO | <D> **** Detailed Description **** Planning milestone was 10/22/2018 for scope freeze material identification. Since the the 10/22/2018 date there has been 2,014 line item requests per 659 individual MR's to the start of R24 refuel outage on 5/12/2019. This shows we did not actually meet the Planning Milestone for the 10/22/2018 date given by Outage Management. This does not align with our Excellence Model, Organizational Excellence, Predictable, Accountable, Teamwork. This would also include Cost-effective Operaton which all leads to a successful outage. <I> **** Actions Taken **** Informed Supervisor and Outage Management.
394955 | CR | 20190605 |  | 4 | Thermo-wells installed in wrong pipe during pre-fab. | N | N |  | N | NO | <D> **** Detailed Description **** While performing pre-fab on Work Order 02111477-25 the thermos-wells from the supply and return lines were installed on opposing lines. The thermos-wells are ported such that the supply is now Â½â€ thread and the return is now Â¾â€. <I> **** Actions Taken **** Spoke with Engineering the thermometer will be used with a bushing. FCR will be issued to update drawings. <N> Williams Plant Services. | 02-00-TO-HX-1A
394956 | CR | 20190605 |  | 3 | (QA) Sawing/Grinding Without PPE Required By ISPM-16 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Site Support Contractor (SSC) pipefitters not wearing the required Personal Protective Equipment (PPE) when sawing and grinding, contrary to ISPM-16 "Personal Protective Equipment". ISPM-16 requires both goggles and a face shield when sawing and grinding because those operations create small particles that can get around regular safety glasses and into a worker's eye; however, no injuries were noticed during this observation. Requirements: (See full details in EDMS) Factual Basis: â€¢ Mid-morning on 6/5/19, a Quality Assurance (QA) auditor observed two SSC pipefitters each using a band saw to finish sawing through a different 4-inch metal I-beam. â€¢ The QA auditor also observed one of the pipefitters grinding on a 4-inch metal I-beam. â€¢ The auditor observed both the sawing and grinding operations created small metal particles. â€¢ Both individuals were wearing regular safety glasses, but neither wore goggles nor a face shield while each one was sawing. â€¢ The individual that was grinding was wearing a face shield, but was not wearing goggles. Insights: â€¢ The individual that had been grinding immediately accepted the coaching to wear goggles and went off to obtain goggles. â€¢ The Work Order Task (WOT) package 02047040-46 was open at the work site as required; however, it did not contain a Job Hazard Analysis (JHA), did not mention ISPM-16, and did not specify the PPE to use during the steps requiring metal to be cut. â€¢ The WOT package in Asset Suite was the same as the printed package (no JHA, etc.). <I> **** Actions Taken **** Actions taken: Provided coaching to both pipefitters. Contacted the acting SSC Superintendent. . THis is a Deficiency identified during the R24 Outage Quality Surveillance SR-19-01. . Quality recommends routing to AR-MNTSSC. <N> Williams Plant Services
394958 | CR | 20190605 |  | 3 | work delay on clean/inspect E-ATS-IN/2 R24 LL |  |  |  | N | NO | <D> **** Detailed Description **** During performance of WO#02112270-01, Electricians were performing Live-Dead-Live of components within E-PNL-IN/2 to verify the equipment is safe to work. 240 VAC Nominal was found across X207 (voltage sensing board). In step 4.10 and 4.11 the X207 board gets removed and replaced with a new voltage sensing board. As per the job hazard analysis warns of 240VAC on components within the panel, this is not acceptable for components that are going to be replaced. The clearance was evaluated for adequacy and work steps may need to be revised to allow for craft to remove fuses that supply power to X207 board <I> **** Actions Taken **** Notified Supervision, CORC and planning for evaluation of boundary revisions <N> **** Equipment Description **** E-PNL-IN/2 Room C213
394959 | CR | 20190605 |  | 3 | (Non EN/CGS) Calibration Report from subvendor had incorrect |  |  |  | N | NO | <D> **** Detailed Description **** (Non EN/CGS) Calibration Report from subvendor had incorrect calibration date and recall date asset# 546-28 -03-033. Received a phone call from customer from in regards to asset# 546-28-03-033 letting me know he was issuing a NCR for the following: (a) Required Condition/Origin of Requirement: PO:54078, ID# 546-28-03-033, Flowmeter. As required: Certificate of Calibration from Energy Northwest must match the Certificate of Calibration from the actual Subvendor. Actual condition: As received: Certificate of Calibration from subvendor has Calibration date of 5-20-19 and due date of 5-20-24. These dates do not match. The Calibration label on the item matches the Energy Northwest Certificate of Calibration and not the Subvendors Calibration dates. Recommend assign to AR-CALSERV (customer complaint CC-190) <I> **** Actions Taken **** In my evaluation I noted that the subvendorâ€™s calibration certificate had been corrected once to correct the model number before being issued to the customer. However, when this model# was corrected the subvendor changed the calibration date on the certificate from 5/17/19 to 5/20/19. This was not caught in our review process when ENSL management signed the calibration certificate. A corrected certificate was requested to the subvendor to correct the calibration date back to the original calibration date of 5/17/19. Then corrected copy of the ENW calibration certificate was issued to the customer to satisfy the closure of their NCR. See attached documentation loaded into EDMS once assignment is available to do so.
394960 | CR | 20190605 |  | 3 | Control Room network eDNA data rate may need to be increased |  |  |  | N | NO | <D> **** Detailed Description **** The pre-built eDNA surveillance plots and histograms were moved to the control room level 3 network and pointed to MCR and MCRBU data streams. This move was performed to migrate the surveillance data plots from corporate to provide increased assurance that the data remains valid and not manipulated from the source. The Corporate eDNA upgrade project would have required the rebuild of the surveillance plots and histograms due to the reconfiguration, so this seemed like the logical time to move them to Level 3 instead. The eDNA data streams available on the level 3 network (MCR/MCRBU) are running at a 1 sample/second (sps) sampling rate. This is in contrast to the high-speed data streams (ENW.CGSHS/ENWBU.CGSHS) on the corporate eDNA network that sample at approximately 15-20 sps. In most cases this slower sample rate is sufficient; however, over the last week, it has been discovered that there may be surveillances with criteria that require sub-second resolution. The original data source for all the data streams (MCR/MCRBU, ENW/ENWBU) is the Plant Process Computer. Since the originating source is the same, the data is equivalent between the eDNA systems, with the only difference being the sampling rate. Recommend to COMPENG for evaluation of short and long term solutions to be determine recommended path forward to support the surveillances. <I> **** Actions Taken **** Discussed with supervision, OPS, OCC, Cyber security, and IS (eDNA Project). It is recommended that all sub-second data requirements use corporate eDNA high speed data (ENW .CGSHS/ENWB .CGSHS) in the interim. | 02-00-PDIS-CPU-DATA1,02-00-PDIS-CPU-DATA2
394961 | CR | 20190605 |  | 3 | Evaluate Spray Nozzle System For The CISP |  |  |  | N | YES | <D> **** Detailed Description **** Please evaluate the design and installation of a permanent spray nozzle system that could be used to reduce contamination accumulation (and dose rates) on horizontal support beams, via sediment and the bottom portion of the CISP (Cavity In-Vessel Service Platform) that sits down in the Reactor Cavity. The current configuration is a never ending radiological nightmare for the following reasons: 1. It requires multiple decontamination efforts throughout IVVI exams to reduce dose rates that continue to increase as the CISP sits in the Reactor Cavity. These decontamination efforts are quite strenuous and difficult to perform. 2. There are horizontal support beams that cannot be accessed during these decontamination activities or while spraying the CISP down as itâ€™s being removed from the Reactor Cavity. This results in very high contamination levels up to 3.3 Rad/hr/100cm2 (R24), which requires a High Risk Plan to decontaminate. The decontamination of the CISP creates up to (15) bags of High Rad trash ranging from 1,000 â€“ 3,200 mrem/hr on contact and 120 â€“ 600 mrem/hr @ 30cm. It should also be noted that decontamination of the CISP after its removal from the cavity is very challenging and presents a significant radiological and heat stress hazard to the Laborers and RP Techs that it requires. The nozzles should be directed at the horizontal support beams under the CISP and the bottom of the CISP tub itself. The system could be designed to connect, via a Chicago fitting to a hose being supplied by condensate water. Boosting of the water pressure may be needed to achieve the nozzle PSI required to properly spray off the contamination, especially when the nozzles are underwater. This system could be used periodically during IVVI to reduce general area dose rates in the CISP and also right before and during its removal from the Reactor Cavity. If the plan is to use the CISP in support of IVVI for the distant future, this system could potentially reduce exposure numbers quite significantly by reducing dose rates on the CISP during IVVI, decontamination efforts and additionally while the CISP is staged on the Refuel Floor prior to installation into the Reactor Cavity and upon its removal and subsequent travels to the DSP post outage. <I> **** Actions Taken **** Contacted RP Supervision and ALARA planning <N> **** Equipment Description **** Cavity In-Vessel Service Platform | 02-00-NSSE-EQ-100
394962 | CR | 20190605 |  | 3 | Main exciter terminal block degradation |  |  |  | N | YES | <D> **** Detailed Description **** The main exciter terminal blocks have broken insulation pieces between some of the terminals. The terminals are for temperature indication so the broken terminal blocks have no impact to the operation of the exciter but should be replaced at the next available opportunity as further degradation could impact temperature indications. . The exciter field leads and Permanent Magnet Generator (PMG) leads are also terminated on these terminal blocks. The insulating material for these terminations is intact but some of the fasteners appear to be different and are not the original equipment as identified on Siemens drawings (this was confirmed with Siemens). Columbia does not have drawings for this location so did not recognize the difference in fasteners but the craft making the terminations questioned the connections which prompted reviewing the connections with Siemens. The existing cable lugs, terminal strip conductors and fasteners have been in service for greater than 20 years and do not impact the function of the exciter but should be replaced with OEM parts in the future to ensure compliance with the original design. . Recommend assigning to System engineer to work with Siemens to identify the replacement components and create CATIDs to ensure the parts are on hand for future maintenance <I> **** Actions Taken **** Discussed with craft, craft supervisor, Siemens and OCC. | 02-00-E-EXC-1
394963 | CR | 20190605 |  | 3 | Editorial change for PPM 16.4.7 |  |  |  | N | NO | <D> **** Detailed Description **** performed editorial pen and ink change to 16.4.7 step 7.1.4. removed CC from step. . Step 7.1.4 says " From verified copy of IMDS for OG-RR-601, TRANSFER channel 1 CC Hi-HI alarm setpoint and limits to table 7.5a" . the IMDS for OG-RR-601 hi hi alarm setpoints and limits do not say ""CC" . Pen and ink editorial was performed to line out CC from step 7.1.4 . <I> **** Actions Taken **** Wrote CR. needs to be assigned to maint procedures to incorporate the editorial change
394964 | CR | 20190605 | CAQ | D | LEFM transducer term blocks found broken | Y | Y |  | N | YES | <D> **** Detailed Description **** The ceramic termination blocks at RFW-FE-3 for LEFM transducers 1B7D (RFW-FE-3/Q) and 1B8D (RFW-FE-3/R) were found cracked and broken, likely due to thermal stress. This was discovered during performance of WO 02138014. The vendor who was on-site to support the maintenance believed that there would likely be no impacts to LEFM performance over the next cycle and, due to unavailability of parts on-site, recommended replacement of the term blocks at the next opportunity. <I> **** Actions Taken **** Discussed with EOC | 02-00-RFW-FE-3
394965 | CR | 20190605 | CAQ | C | CRD-V-113/3027 packing configuration | Y | N |  | N | YES | <C> MRT change request on 6/7/2019 from Severity D to C and assigned to AR-MECSHOP <D> **** Detailed Description **** CRD-V-113/3027 as-found packing configuration identified 6 rings of packing. This configuration is outside of PPM 10.2.79. However, the valve stuffing box configuration requires a 6 ring configuration otherwise the gland would bottom out. A bushing is unacceptable for this configuration. <I> **** Actions Taken **** Issued packing data sheet with 6 rings of packing (same as as-found). * This issue was addressed as part of completion of WOT 02082579-21. <N> installed 7 rings packing, 1 bottom / 3 die formed and 3 top wipper rings. got concurrance from valve engineer and Seal -Pro represenitive. Uploaded valve packing data sheet WO 02082579-21 Condition corrected. No further actions required. | 02-00-CRD-V-113/3027
394966 | CR | 20190605 |  | 4 | MS-MO-102B, failed to travel full open. |  |  |  | N | YES | <D> **** Detailed Description **** During packing re-torque and PMT-E4 on WR#29148493, it was noted that MS-MO-102B failed to fully open during the electrical stroke. When cycled open by the control room the valve only traveled between .125 and .250 inch. This was an unexpected response. <I> **** Actions Taken **** Gave 2, put in a safe condition. Notified the main control room and the MOV Engineer for assatance and trouble shooting plan. | 02-00-MS-MO-102B,02-00-MS-V-102B
394967 | CR | 20190605 |  | 4 | High speed data pre-built plots and histograms on corporate |  |  |  | N | YES | <D> **** Detailed Description **** During performance of TSP-DG2/LOCA-B501 last night, it was discovered that the real time plots and histograms that were migrated from the corporate network to TDAS/PPC do not have adequate sampling frequency to accurately time some surveillances. The issue was resolved using high speed data on the coporate network using EDNA trend. For surveillances such as the one completed last night, this requires operators to rebuild each plot, sometimes over four or five EDNA trend plots due to the amount of data. The prebuilt plots located on the T drive post-migration no longer work. This is an uneccessary and time consuming burden on control room staff. Please restore the prebuilt plots/trends and histograms on the T drive for use in future surveillances or increas the sampling frequency on TDAS/PPC to allow that to be used. <I> **** Actions Taken **** Discussed with SM. <N> **** Equipment Description **** MCR, RW 501' | 02-00-PPC-COMP-8715,02-00-TDAS-COMP-8715
394970 | CR | 20190605 | CAQ | D | CMS-LR-3 Point 2 SP wide range level may be degraded | Y | N |  | N | YES | <D> **** Detailed Description **** Over the last 5 days, Suppression pool level on the narrow range has varied between +1.7" to a low of -0.3" as seen on EDNA plots (See EDMS). Division 2 wide range level has tracked similar, but Division 1 has had long periods of reading stable level. This instrument is a required Main control room log, and may be required in some water management plan contingincies during vessel let down. Recommend performance of ISP-CMS-B302 to veriify accurate calibration. <I> **** Actions Taken **** Informed CRS, generated EDNA plot with 15 min avg to remove noise. | 02-00-CMS-LR-3
394971 | CR | 20190605 | CAQ | D | RPS-RLY-K3E didnt energize with MSIV open | Y | N |  | N | YES | <D> **** Detailed Description **** While performing OSP-MS/IST-Q701, RPS-RLY-K3E did not energize. Please fix this Ref WO 02115578-19 <I> **** Actions Taken **** Informed CRS/SM/OCC | 02-00-RPS-RLY-K3E
394972 | CR | 20190605 |  | 3 | R24LL Procedure Enhancement for SOP-MSIV-OPS |  |  |  | N | NO | <D> **** Detailed Description **** Based on some questions that came up during R24 it would be beneficial to add some enhancement notes to SOP-MSIV-OPS. . My thought is that the following two sentences taken from EC 9481 - MSIV Wetting should be added as a Note in section 5.5 and in the Precautions and Limitations step 4.7. This will help clarify when the 12-hour wetting clock is supposed to start. . â€œThe 12-hour wetting clock should start at the point when the water used to wet the internals of the MSIVs has been completely drained from the Main Steam Lines (MSLs). This is also the point at which the outboard MSIV could be stroked open without sending water to the condenser.â€ <I> **** Actions Taken **** CR written, EOC/OCC notified.
394973 | CR | 20190605 | CAQ | D | Packing leak CRD-V-126/3043 | Y | N |  | N | YES | <D> **** Detailed Description **** Packing leak CRD-V-126/3043 <I> **** Actions Taken **** Closed isolation valve, called HP's <N> **** Equipment Description **** RB 522 | 02-00-CRD-V-126/3043
394974 | CR | 20190605 | CAQ | D | CRD-FCV-2A limit switches need adjustment | Y | Y |  | N | YES | <D> **** Detailed Description **** During the performance of CRD-FC-600 loop calibration, 02101714-08, it was noticed that the indication in the control room showed dual indication throughout the entire stroke test of the valve. <I> **** Actions Taken **** Notified supervisor, wrote CR <N> **** Equipment Description **** crd-fcv-2a. | 02-00-CRD-FCV-2A
394975 | CR | 20190606 | CAQ | D | (QA) Weld Joint Design Criteria Clarification |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) WOT 02114717-01/MS-V-741A, Weld Record No. 2-13675 joint design required welds to be "Socket Weld 9/32â€ or to the Edge of the Socket, whichever is less.â€ Quality Control Inspector verified socket welds to be 3/8â€ in size therefore over-sized for weld nos. 2 and 3. Welds are ANSI B31.1 Code, Non Safety Related. . Upon discussion with the Welding Engineer it was clarified that the intended weld size was to be a minimum of 9/32" or to the edge of the socket, whichever is less. <I> **** Actions Taken **** The Welding Engineer amended the weld record for acceptance by QC upon issuance of Condition Report. No further action is required of this AR/CR. Notified Quality Control Level III, QC Supervisor, Williams Management and Welding Engineer. . <N> Williams Plant Services.
394978 | CR | 20190606 |  | 4 | CCTV12T not functioning as designed |  |  |  | N | YES | <D> **** Detailed Description **** Security CCTV12 Thermal no picture. Contact security at 2185 <I> **** Actions Taken **** CR/WR generated | 02-00-SEC-CCTV-12T
394979 | CR | 20190606 |  | 4 | Breaker in service for 2 years without PMT |  |  |  | N | YES | <D> **** Detailed Description **** Breaker WCH-CB-7E4E for WCH-CR-51A was replaced during R23. At that time, WCH-CR-51A was non-operational so the breaker remained open under a clearance order. When the chiller was later replaced and put into service, the PMT for the original work order was not performed although some applicable data was taken in the chiller PMT. Recommend action to work control to schedule the PMT. <N> Per UC, this PMT was scheduled in March 2019 and was not performed. PMT is scheduled again in Nov 2019. No additional action from WC needed. | 02-00-WCH-CB-7E4E
394980 | CR | 20190606 | CAQ | D | TMU-SR-1 Intake Sample Rack has E2 error | N | Y |  | N | YES | <D> **** Detailed Description **** TMU Intake Sampler, TMU-SR-1, has E2 error, but delivered sample and works as expected. Sample rack was de-energized during LOOP/LOCA testing and error may be related to this. <I> **** Actions Taken **** Performed operator rounds manual sample as directed by OPS4 logs. Sample was delivered to the container and sample valve repositioned when pushbutton released as expected. | 02-00-TMU-SR-1
394981 | CR | 20190606 |  | 3 | Editorial change to SOP-ELEC-IN2-START |  |  |  | N | NO | <D> **** Detailed Description **** Section 5.1 of SOP-ELEC-IN2-START documents starting up IN-2A when the manual bypass source is in effect. Step 5.1.1.f is not possible as the inverter is shutdown and will not be in service until the transfer is made back to the static switch. Please perform an extent of condition on E-IN-2B section and E-IN-3A/B sections as well. <I> **** Actions Taken **** OPS procedures group notifice. CR written
394982 | CR | 20190606 |  | 4 | Non-compliance with PPM 1.3.10A |  |  |  | N | NO | <D> **** Detailed Description **** As part of remote welding work for RFW-FCV-10A, workers were allowed to support work in a PAPR. This was not recognized until RP Supervision stopped the job. PPM 1.3.10A, Control of Ignition Sources, Sect 2.10, CAUTION STATEMENT, states do NOT wear Max Air PAPR respirators when performing Ignition Source Work. <I> **** Actions Taken **** Work using this machine willl require qualified full face respirator and welding PCs to perform work. Communicated this information to OCC and RP staff. Work was stopped and will continue only when the proper qualified workers are available.
394983 | CR | 20190606 |  | 3 | CR for procedure enhancement. (SOP-RHR-FILL) |  |  |  | N | NO | <D> I&C support task for RHR-SYS-B Fill/Vent needs to be updated to reflect the Revision changes in the SOP-RHR -FILL. The SOP was revised 05/6/19, causing errors when the Master 5 instructions directed steps for ops to perform that did not align correctly. Reference WO 02115612-13 in Data glance to review issues found. <I> CR generated to fix work instructions <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
394984 | CR | 20190606 | CAQ | D | "DC PUMP Failure" alarm on DG2. | Y | N |  | N | YES | <D> **** Detailed Description **** When running DG2 for LOP/LOCA testing, the "DC PUMP FAILURE" alarm can in each of three times when the diesel was hot-started to idle. This alarm did not occur during other starts. Pressures were normal. Please investigate. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** DG 2 room | 02-00-DG-ENG-1B1,02-00-DG-ENG-1B2
394985 | CR | 20190606 | CAQ | D | CAS-V-327B flange leakage | Y | N |  | N | YES | <D> **** Detailed Description **** Air leakage at valve flanges. Amount of leakage was small amount of air bubbles when flanges were snoop checked. | 02-00-CAS-V-327B
394986 | CR | 20190606 | CAQ | D | CRD-F-6B air leakage at downstream union connection | Y | N |  | N | YES | <D> **** Detailed Description **** Small amount of air leakage at pipe union connection immediately downstream of CRD-F-6. Air leakage caused small air bubbles when tested with snoop. | 02-00-CRD-F-6B
394987 | CR | 20190606 |  | 3 | R24 LL RFW-FCV-10B Welding Ceased due to Fire Prot. Concerns |  |  |  | N | NO | <D> **** Detailed Description **** Welding operations on RFW-FCV-10B was ceased when following review of ISPM-16, Personal Protective Equipment; ISPM-17, Respiratory Requirements; and PPM 1.3.10A, Control of Ignition Sources. By definition, an ignition source, includes all welding activities and does not delineate between manual (hands-on) welding and remote (automatic) welding. Individuals performing the welding activities were observed to be in non-hot work PCs (white vs orange) and were utilizing PAPRs. While the weldersâ€™ were positioned 2â€™ to 15â€™ away from the welding activities, they were not adhering to the procedure, as currently written. <I> **** Actions Taken **** Stopped work activities. Generated CR. Contacted RP, Industrial Safety, and Fire Protection. Proceeded towards qualifying the welders for respirator use. Recommend PPM 1.3.10A be revised to have allowances for remotely operated devices, including automatic/remote welding, automatic/remote machining, and automatic/remote pre/post -heat activities.
394993 | CR | 20190606 |  | 3 | Genie Lift E-EQ-SL4 Control Wiring Found Damaged | N | N |  | N | YES | <D> **** Detailed Description **** While performing work in the RFW-1B Pump room it was noticed that the Genie Lift E-EQ-SL4 Control Panel Wires are damaged. This damage was noticed while transitioning to job site. Individual inner wires of cable bundle are exposed but no conductors are visibile. These cables are connected to controls of the genie lift inside the the work area. I do not know the current operability of the genie lift as it was not in use while I was in the area. This peice of equipment should be tagged out till repairs can be done to fix wiring. <I> **** Actions Taken **** Discussed issues found tith supervision. Initiated CR to document findings. <N> **** Equipment Description **** RFW-1B E-EQ-SL4 Contacted maintenance to consider removing from service until it can be inspected/repaired.
394994 | CR | 20190606 |  | 4 | RRA-CC-8/9 hangers could not be painted | N | N |  | N | YES | <D> **** Detailed Description **** While attemping to paint TSW piping hangers associated with RRA-CC-8/9 under W/O 02106152-07, could not coat the carbon steel U bolts because they were used on stainless steel piping, per procedure could not coat stainless steel piping. <I> **** Actions Taken **** Informed Maintenance, OCC and engineering, cancelled the W/O because it couls not be done without getting paint on the stainless steel piping . This was evaluated as acceptable by Engineering in EOC action S-140: It is acceptable to allow cancellation of the painting task WOT 02106152-07 for RIE 264973-08. There is adequate information in the cancellation request to justify the cancellation with no further actions required. The u-bolts are the unpainted items and can be left unpainted to save dose (high dose in the steam tunnel) since the contact area between the pipe and u-bolts is small. <N> **** Equipment Description **** ST 501 H3/6.5 | 02-00-RRA-CC-9
394996 | CR | 20190606 |  | 4 | Report Only | N | N |  | N | NO | <D> **** Detailed Description **** While moving material on a scaffold rack on the 501'TG a small tube rolled and contacted the middle finger of the left hand of the employee. Employee reported and returned back to work with no issues. This is a report only. <I> **** Actions Taken **** Contacted SCC management and Site Support Contractor Manager. No further action is required. <N> Williams Plant Services.
394997 | CR | 20190606 |  | 4 | DLR RUN THROUGH X-RAY MACHINE | N | N |  | N | NO | <D> **** Detailed Description **** A project contractor with Org 52238 allowed their DLR to be run through a Security X-ray machine. <I> **** Actions Taken **** Stand-down held with project crew to reinforce EN standards and expectations. . No further action required.
394998 | CR | 20190606 |  | 4 | Missed opportunities for PMTâ€™s on RHR B | N | N |  | N | NO | <D> **** Detailed Description **** Missed opportunities for PMTâ€™s on RHR B Missed opportunities for PMTâ€™s on RHR B Poor communications caused delays in PMT's on RHR B. See attached in EDMS.
394999 | CR | 20190606 |  | 3 | Main Turbine thrust bearing calibration | N | N |  | N | YES | <D> **** Detailed Description **** Following thrust probe replacement under WO 02134693, actions taken to set the axial position of the shaft and instrumentation are not in agreement. This condition has resulted in challenges for calibration of the thrust probes. <I> **** Actions Taken **** Expanded team (Engineering, I/C, OEM) Informed EOC/OCC Started TIRP in accordance with PPI PPM 1.3.42 <N> **** Equipment Description **** Near Brg 5, LPB east end | 02-00-TG-DET-TP/A,02-00-TG-DET-TP/B,02-00-TG-DET-TP/C
395000 | CR | 20190606 |  | 3 | R24LL: CRD Surveillance optimization | N | N |  | N | NO | <D> **** Detailed Description **** Recommend combining OSP-CRD/IST-Q701 and OSP-CRD-B701 into one surveillance that has allowances to take credit for both TS surveilance requirments.
395002 | CR | 20190606 |  | 4 | MT-HOI-TRN/1 assembly and pendant issues | N | N |  | N | YES | <D> **** Detailed Description **** An off-site vendor performing maintenance on MT-HOI-TRN/1 provided a report on the crane's overall condition based on his observations. In the report, he calls out nuts not fully threaded to bolts used in assembly (done by Lampson) and weathering on the pendant controls that may cause the controls to short. The full report is with the Site Rigging Coordinator and Maintenance Training Supervisor. The observations need to be evaluated by on-site personnel and addressed as needed prior to the crane's next intended use in July. <I> **** Actions Taken **** Suspended use of the crane. Discussed with Site Rigging Coordinator. Initiated CR. | 02-00-MT-HOI-TRN/1
395003 | CR | 20190606 |  | 4 | E-EXC-1, term block lockplates installed under terminations | N | N |  | N | YES | <D> **** Detailed Description **** The main exciter terminal block on the Northwest side of the generator terminals T10, T20 and T30 has lockplates installed under the terminations. Lockplates are typically installed between the lug and the nut, the corners of the lockplate are bent up on the flat of the bolt or nut to prevent loosening of the fastener. This condition has existed for many years as new lockplates were not installed this outage and have not been used in this location for many years. Recommend lifting the leads for T10, T20 and T30 to remove the lockplate. See EDMS for pictures. <I> **** Actions Taken **** Discussed with FIN, recomended removal of the lockplates. This should be worked as a minor maintenance activity. | 02-00-E-EXC-1
395004 | CR | 20190606 |  | 4 | R24LL High noise during Turbine Blade removal | N | N |  | N | NO | <D> **** Detailed Description **** During the turbine blade removal activities that occurred 6/2 to 6/4 a high noise area was created. This area is permanently posted â€œhearing protection required while equipment is operatingâ€ at all entrances and on the Kelly building. Additional hearing protection required signage was posted during the evolution and audible decibel levels were monitored regularly. An enhancement to this process would be to provide a warning or announcement to the people in the immediate area that the activity would be commencing. <I> **** Actions Taken **** Recommend this CR be trending (closed) and reviewed during the planning outage lesson learned process following completion of R24 for potential action during R25.
395005 | CR | 20190606 |  | 3 | PPM 15.1.9 and PMID-RQ 16301-03 has errors | N | N |  | N | NO | <D> **** Detailed Description **** PPM 15.1.9 exercises the large plant fire protection valves under PMID 16301-01. PMID-RQ 16301-03 is for valve lubrication, but has various problems. 1) The procedure says 1Y and 5Y but Asset Suite D080 says 4Y. NFPA 25 suggests 1Y. 2) Asset Suite D080 says it is PM type SURV, but is actually ESSN; 3) The scope of RQ-03 is simply lubricating the valves. That is something the craft does annually for every valve that needs it. This scope should simply be part of PPM 15.1.19 PMID-RQ 16301-01 and does not need a separate RQ-03. See EDMS file for more details. This CR has no operability concerns. Assign to AR-TEFP to generate the needed corrective actions. <I> **** Actions Taken **** Discussed with various plant personnel. The main Mechanical Maintenance performer agrees.
395007 | CR | 20190606 | CAQ | D | Damaged HCU fuse | N | N |  | N | YES | <C> MRT change: CR Severity moved to CAQ D/TR (from 4/TR). <D> **** Detailed Description **** While re-installing fuses for lifting clearance O-CRD-HCU -3843-002. The fuse from tag 7762 EPN E-FUSE-HCU3843/FA was found damaged <I> **** Actions Taken **** Fuse not installed, CR and WR generated | 02-00-E-FUSE-HCU3843/FA
395008 | CR | 20190606 |  | 3 | Locked Valve Checklist 1.3.29 missing 6 valves between revs | N | N |  | N | NO | <D> **** Detailed Description **** When revision 82 was isued on 6/4/19, 6 valves were inadvertently removed. All the valves found in 'RB 548 RHR A HX Room' are gone and all of the valves previously listed in 'RB 548 RHR B HX Room' section are now in place of the missing valves and the 'RB 548 RHR B HX Room' section was deleted. The missing valves are: RHR-V-14A RCIC-V-137 RCIC-V-138 SW-V-175A SW-V-76A SW-V-78A . Addtionally, HPCS-V-86 is on the checklist twice. Recommend a thorough review of the procedure to ensure other valves are not missing <N> Notified Ops Procedure writers to correct PPM 1.3.29.
395009 | CR | 20190606 | CAQ | D | RRC-TR-650 pt 2 not working | Y | N |  | N | YES | <D> **** Detailed Description **** RRC-TR 650 pt 2 temperature indication is not working properly. It has large swings in temperature from 200F to upscale. Computer point X310 is showing the same indications. This point is required to supprot RRC pump starts per OSP-RRC-C103. This has been recently worked under 29143063 / 02129706. | 02-00-RRC-TR-650
395010 | CR | 20190606 |  | 4 | ES-TS-1A1 Found Out of Tolerance | N | N |  | N | YES | <D> **** Detailed Description **** While WO# 02113955-01 was being perfomred found ES-TS-1A1 to be out of tolerance by 20 degrees high. Trip point is 230 degrees F found at 250 degrees F <I> **** Actions Taken **** Notified supervision and ES-TS-1A1 was adjusted to the desired trip point of 230 degrees +- 4 degrees F. | 02-00-ES-TS-1A1
395011 | CR | 20190606 |  | 3 | LEFM cabinet filters |  |  |  | N | YES | <D> **** Detailed Description **** The LEFM cabinet filters are extremely dirty and need cleaning. PM 00026051 was generated to clean them but is setup on a bi-annual time frame. Recommend performing WO 02111856 and changing the frequency to every 3 months. I believe I was the last person to clean them approximately 1 year ago. We have had high temperature issues with this cabinet in the past. See pictures for detail. <I> **** Actions Taken **** cr | 02-00-RFW-CAB-FE3/FE4
395012 | CR | 20190606 |  | 3 | (R24LL) Ops outage Lesson learned to date (LLRT) |  |  |  | N | NO | <D> **** Detailed Description **** Attached to the EDMS is a list of ops lessons learned from One Note, specific to LLRT from start of the outage to date. <I> **** Actions Taken **** Reviewed the lessons learned and the LLRT log and identified the applicable lessons learned. This CR is ops trending only <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
395015 | CR | 20190606 |  | 4 | R24 LLA, TSW-HX-7 cleaning PM needs planned weld repair task |  |  |  | N | NO | <D> **** Detailed Description **** The model WO for the main generator hydrogen cooler cleaning (TSW-HX-7A, B, C, D) PM needs a planned and scheduled task for weld repair and a task for recoating the heat exchanger. The cooler heads degrade over an operating cycle and usually require repair and recoating. If these tasks are not planned and scheduled time is wasted perfomring inspections then scrambling to get a shop to perform the weld repair and machining. <I> **** Actions Taken **** Discussed with EOC, Initiated LL CR and initiated SMS AR to revise the model WO for the PM.
395016 | CR | 20190606 |  | 3 | E-EXC-1, add torque values to PM work orders | N | N |  | N | NO | <D> **** Detailed Description **** PM work orders that remove the exciter field leads and PMG leads at the exciter and at the WTA voltage regulator do not have torque values to ensure the connections are properly torqued when they are reassembled. The 2 year PM for the exciter inspection, 8 year PM for generator major inspection and calibration of the WTA voltage regulator need to have steps to torque the fasters in accordance with PPM 10.2.10 <I> **** Actions Taken **** Discussed with craft and supervisor, initiated CR to drive updating the PM model work orders.
395017 | CR | 20190606 |  | 4 | RWCU-42-8C6A will not remain closed in. | N | N |  | N | YES | <D> **** Detailed Description **** Disconnect closes in and the will slowly rool back open. Dicsconnect needs to be lubricated and/or inspected. This is for RWCU-V-102 and will be needed for RWCU system restart. <I> **** Actions Taken **** Informed supervision ad recomended that this be addressed. | 02-00-RWCU-42-8C6A
395019 | CR | 20190606 |  | 4 | ESD/Nine Canyon Knuckle abrasion |  |  |  | N | NO | <D> **** Detailed Description **** A 3 man crew of wind technicians were the process of replacing a yaw drive in a 1.3MW wind turbine. In the process of removing the bottom grease tray of the yaw drive, the assembly came loose catching one of the technicians fingers between it and the floor. The technician was wearing all his PPE including the proper gloves. He sustained a small abrasion on the knuckle. A band aid put on the knuckle and the Technician went back to work. <I> **** Actions Taken **** Per rquirments of ISPM 1
395020 | CR | 20190606 |  | 3 | R24LL TOC issues impacting RW systems |  |  |  | N | NO | <D> **** Detailed Description **** Multiple total organic carbons (TOC) intrusions have occurred this outage that has impacted the Rad Waste system ability to process water to support plant operations. The TOC issue is affecting the EDR and FDR trains in RW. The introduction of TOC liquids has occurred during previous outages. This could be caused by workers pouring TOC laden liquids into drains or equipment failures leading to TOC introduction. Benchmarking should be performed to understand how other plants both mitigate and respond to TOC events. .. Non-nuclear industries that utilize high purity water should be benchmarked for TOC removal processes. The site should consider using a temporary UV treatment skid during outages. This skid utilizes UV lights to break down TOCs into constituent components that can be removed by ion exchange. <I> **** Actions Taken **** RPM and Chemistry supervisor informed.
395021 | CR | 20190606 | CAQ | D | FP-THD-Zone 60 for E-TR-B | N | N |  | N | YES | <D> **** Detailed Description **** While performing CFT on FP-THD-ZONE 60 under WO # 02110833-02 . While resetting the zone under test craft had zones 57, 58, and 59 troubles come in at FCP-2. They are also tied back to the FSP-2 on T441 elevation. <I> **** Actions Taken **** Craft reset the panel for the zone 60 under test. Per 15.2.23 and all zones are clear of trouble. Contacted supervision and the Control room. Wrote CR. <N> **** Equipment Description **** T 441 FSP-2 panel RW 501 FCP-2 | 02-00-FP-THD-60/8
395022 | CR | 20190606 |  | 4 | R24 lesson learned (LL) - ASD work duration |  |  |  | N | NO | <D> **** Detailed Description **** R24 LL documentation. WO 02138133-01 to replace three LGMs and to match the capacitor configuration is a full 24 hour duration but only scheduled for 10hr. There are also not enough proficient and qualified ASD craft in the shop to ensure 24/7 continuity.
395023 | CR | 20190606 |  | 4 | FPC-DM-1A rapid pressurization while S/D due to leakby | N | N |  | N | YES | <D> **** Detailed Description **** FPC-DM-1A rapid pressurization while S/D due to leakby SOP FPC-DEMIN Section 5.3, step 5.3.3 says to verify demin pressure no GT 15#. If it is GT 15#, open vent valve for 30 seconds to depressurize, and reclose vent valve. If vessel rapid repressurization is observed, notify CRS. Vessel is repressurizing to system pressure (>100#) in under a minute. <I> **** Actions Taken **** Informed CRS | 02-00-FPC-FCV-15A
395024 | CR | 20190606 |  | 4 | Loss of CAS | N | N |  | N | YES | <D> **** Detailed Description **** The plant experienced at loss of Control Air pressure. All CAS air compressors are tagged off. SA-C-1 and the Temporary Air Compressor at CWPH is only source of air. When Ops 4 arrived, the Temporary Air Compressor was found in Unload mode but otherwise running normally. Coincidentally the Temporary Air Compressor had just been refueled by Facilities. When Ops 4 restored the compressor from Unload, CAS air header pressure was restored.
395025 | CR | 20190606 |  | 3 | Consider Revision to PPM 10.2.53 (Scaffolding) procedure |  |  |  | N | NO | <D> **** Detailed Description **** During R-24, an individual was mopping up water underneath a scaffold structure and hit his head on the scaffold deck/planks when he stood up. This injury was later classified as a lost time accident. To reduce the risk for similar injuries, consider revising PPM 10.2.53 (Scaffolding) to require crossarms installed in such a way to limit or restrict access underneath the scaffold for scaffolds where the deck height is about 6 feet high.
395027 | CR | 20190606 |  | 3 | ARP 4.603.A7 & A8 have descrepant information |  |  |  | N | NO | <D> **** Detailed Description **** Windows 1-2 and 1-3 in both ARP 4.603.A7 & A8 have descrepant information. For 4.603.A7 window 1-2 lists that setpoint for scram discharge volume level high as 529'7". Window 1-3 lists it as being 529'2". The same descrepancy is also in 4.603.A8. In addition some of the relays listed in window 1-2 for scram discharge volume high level of 4.603 .A8 are incorrect. K1C and K31C should be K1B and K31B. <I> **** Actions Taken **** Notified the control room.
395028 | CR | 20190606 |  | 4 | TSW-SR-34 Flow not sufficient | N | Y |  | N | YES | <D> **** Detailed Description **** TSW-SR-34 flow is low. Multiple flushes were clear and the flow remained low. There may be outage related line ups or activites that may be affecting the rack or there is something wrong with the flow indicator. CR393755 has already been written on this issue. <I> **** Actions Taken **** Notified CRS, Chemistry supervision <N> **** Equipment Description **** TSW-SR-34 on TG 441' | 02-00-TSW-SR-34
395029 | CR | 20190606 |  | 4 | False Floor crack between A and B bays |  |  |  | N | YES | <D> **** Detailed Description **** A ~6 inch crack in the False Floor of the Main Condenser was discovered during closeout of the Hotwell (WO 02108276-01). The crack is near the south wall of the Main Condenser, on the underside of a boxed depressions which allows communication between A and B bays (picture in EDMS). The crack does not impede the design function of the Main Condenser and does not appear to challenge the structural integrity of the false floor. Based on observation of similar crack propagations in the A bay, recommend repair in R25. | 02-00-COND-HX-9
395030 | CR | 20190606 |  | 4 | Near miss report only event. |  |  |  | N | NO | <D> **** Detailed Description **** Employee was torqueing a flange to 533 ft-lbs when the Â¾â€ drive torque wrench socket slipped off the bolt head. The torque wrench handle impacted the workerâ€™s hard hat, forcing his safety glasses into the bridge of his nose. The worker immediately reported the event to supervision and returned to work. <I> **** Actions Taken **** Event reported to supervision. R24 OCC team notified. Discussed Safety Guiding Principle of the Day "Summit Fever" with the work group on both shifts.
395031 | CR | 20190606 |  | 3 | LLRT has exceeded 150% of the original job dose estimate |  |  |  | N | NO | <C> MRT change: CR Severity moved from CAQ C to NON-CAQ 3 (not over 150%). <D> **** Detailed Description **** Due to higher than expected dose rates, multiple retests including the RHR-V-8 and the Containment Vacuum Breakers, and inexperience of the crew, the dose received for the LLRT group has exceeded its original estimate (5.087 Rem) by 150% (7.879 Rem) <I> **** Actions Taken **** Nightshift acting RPM and LLRT has been notified. Job Re-estimated to 9.337 Rem. <N> Pre-Outage LLRT/ Ops Valve L/U SSAC established goal is 6.900 p-Rem. (6.900 x 1.25 (125%) = 8.625 p-Rem Original dose estimate presented to SSAC was 7.043 p-Rem. Estimate revised to 7.462 p-Rem due to added scope. (7.462 x 1.25 (125%) = 9.328 p-Rem. Current actual dose, as of 6/7/19 0930 hrs, for R24 LLRT/ Valve Ops L/U is 9.377 p-Rem. Actual dose is currently 136% of established SSAC goal and 126% of revised estimate ( 133% of original estimate). High Risk Plans were implemented during R24 for vale lineups in RWCU HX RM and on the TIP mezzanine in conjunction with LLRT of RWCU-V-40. Dose rates were significantly higher than anticipated in these areas. The LLRT of RWCU-V-40 was not identified by the planner in the original scope dose estimate for this work. Complete details of dose overrun will be addressed in the ALARA Post Job Review. LLRTs of the DW personnel and equipment hatches remain to be performed.
395032 | CR | 20190606 |  | 4 | Drain valve for E-TR-B termination cabinet not needed |  |  |  | N | YES | <D> **** Detailed Description **** After investigation of the E-TR-B oil leak and cleaning up the low voltage termination cabinet it was determined that drain valve installation will not be required. This is based on inspection of the cabinet and there was no oil found in the bottom of the low voltage termination cabinet. After discussions with BPA and with the recent replacement of the bushings under WO 02107738 an oil leak will not get to the termination cabinet. If a leak is from the bushing or transformer tank it will fill up in the ledge between the transformer low voltage compartment and the terminal box and come down the seal between that connection. The purpose of this CR is to document not needing WO 02142051 implemented this outage or EC 17713. | 02-00-E-TR-B
395033 | CR | 20190606 |  | 4 | SMA-FL-1 is at end of roll |  |  |  | N | YES | <D> **** Detailed Description **** SMA-FL-1 is at end of roll and needs to be replaced. <I> **** Actions Taken **** N/A | 02-00-SMA-FL-1
395034 | CR | 20190606 |  | 4 | TSW leak, TO-HX-1A |  |  |  | N | YES | <D> **** Detailed Description **** While restoring TSW to TO-HX-1A, both 12" flanges on the HX head near TSW-V-17A and TSW-V-18A had active leaks with only leak-by pressure. This was prior to applying system pressure. Leak rate was a constant, pencil sized stream. <I> **** Actions Taken **** Informed SSS. Reopened TSW-V-784 to provide a drain path. | 02-00-TO-HX-1A
395035 | CR | 20190606 | CAQ | C | Electronic Dosimeter lost in the wetwell | Y | N |  | N | NO | <D> **** Detailed Description **** While working in the wetwell an EO lost his ED out of his pocket when he bent over to install a pipe plug. When he started to remove the tape from his outer PC's the HP tech noticed that it was missing. <I> **** Actions Taken **** Notified Shift Manager and OCC <N> Individual was in the Wetwell and had just checked their dosimeter, turned around and leaned over towards where they were working when the ED fell into the water. The individual immediately exited the Wetwell. RP assigned the individual 1.2 millirem, the amount of dose that the ED reading when it was checked. Form 19086 has been uploaded into EDMS.
395036 | CR | 20190607 |  | 3 | R24LL, CJW-TI-3A GT 120F |  |  |  | N | YES | <D> **** Detailed Description **** SOP-CAS-START Section 5.5.10 says to verify CJW-TI-3A LT 120F. The same temperature is prescribed for CAS-C-1B and 1C. eSOMS operator rounds has 150F as the high spec for all 3 CAS compressors. Current temperature is 128F and is approximately where it was prior to CAS compressors being tagged out for R24. <I> **** Actions Taken **** Informed supervision. Wrote CR. | 02-00-CAS-C-1A,02-00-CJW-TI-3A
395037 | CR | 20190607 |  | 4 | COND-HX-9 Steam Cutting Damage At Penetration 60 | N | N |  | N | YES | <D> **** Detailed Description **** Significant steam cutting damage was found to the pipe, weld-o-let and condenser wall at penetration 60 (Ref: M505-1). The damage was found when performing W/O 02143797-01 to repair a pin hole leak near HD-V-11. See EDMS pictures. | 02-00-COND-HX-9
395038 | CR | 20190607 | CAQ | C | Top Tier Drawing M524-3 Missing in Asset Suite | N | N |  | N | NO | <D> **** Detailed Description **** M524-3 is a legitimate Top Tier drawing but missing in the Controlled Documents Module. This occurred when issuing Rev 023 via EC 4533. The EC 4533 ADL shows that Major Rev 023 was processed but itâ€™s yellow, meaning invalid entry. When navigating from the ADL to the C010 panel an error message â€œDocument not foundâ€ is displayed. Something went abnormal in Asset Suite and the data needs to be restored. <I> **** Actions Taken **** Researched the SharePoint EN Docs library and the image is available with a time stamp of 5/6/2019 7:00AM. . The SW-SV-918 configuration is Safety Class AQ, Seismic 1M. . Discussed with the CEI Supervisor and Notified the #Document Control email Group. Recommend this action be assigned to the AR-RIM Primary Alert Group. <N> This has been corrected. A . inadvertently ended up in front of the number. The drawings is now retrievable in Asset Suite and no further actions are required. LMAR
395039 | CR | 20190607 |  | 4 | RHR-V-260B inadvertent bump | N | N |  | N | NO | <D> **** Detailed Description **** An HP technician inadvertently bumped RHR-V-260B while transiting the area. This valve was closed prior to being bumped and subsequently checked closed by operations. <I> **** Actions Taken **** Verified valve position <N> This valve was verified by operations to not have been mispositioned. It was bumped, but there was not movement of the valve.
395041 | CR | 20190607 | CAQ | C | CRD-HCU-1803 | Y | N |  | N | YES | <D> **** Detailed Description **** While performing WO #02082572-15 step 4.2.4 craft noticed a leak on a swagelok fitting on CRD-V-127 (Outlet Scram Valve) <I> **** Actions Taken **** Craft stop work and notified supervision, OCC & EOC, for evalution and remediation of the leak located on CRD-V-127. Craft did not complete the PMT on CRD-HCU-1803 <N> **** Equipment Description **** RX 522' M.0/8.2 | 02-00-CRD-HCU-1803
395042 | CR | 20190607 |  | 4 | Leak from flange TSW-V-17A | N | N |  | N | YES | <D> **** Detailed Description **** Upon restoration from maintenance, TSW-V-17A has a 1 drop per second leak from the downstream flange at the gasket. Recommend repair/replace as necessary. <I> **** Actions Taken **** Informed SSS, generated AR/WR. | 02-00-TSW-V-17A
395043 | CR | 20190607 |  | 3 | Missing Spherical Washers COND-EJ-2A/2C | N | N |  | N | YES | <D> **** Detailed Description **** During reassembly of the COND-EJ-2A and COND-EJ-2C it was identified that the control rods that came with the expansion joints were missing 4 each spherical washers 1â€ ID-Hardened Black oxide steel. (total 8) <I> **** Actions Taken **** Notified supervision, OCC, Supply Chain to procure initiated CR. | 02-00-COND-EJ-2A,02-00-COND-EJ-2C
395046 | CR | 20190607 |  | 4 | R471 NW MCC Room lights are failing | N | N |  | N | YES | <D> **** Detailed Description **** The fluorescent room lights are failing for the MCC room containing MC-S2-1A. Recommend replacing light bulbs. <I> **** Actions Taken **** Informed CRS/SM <N> This lighting is non-essential. | 02-00-E-CB-ELP7BB/4,02-00-E-CB-LP3DAB/1
395047 | CR | 20190607 |  | 4 | Received Oscillograph Started Alarm H13-P800.C4.4-3 alarm | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 237kV B: 237kV C: 237kV. E-TR-B is deengergized / inoperable for system outage. CGS currently lined up on 500 KV backfeed. The following sensors were tripped and are reset: J7 - 500kV Neutral Ground Overcurrent, J11 - SM-7 Undervoltage, J12 - SM-8 Undervoltage, J15 - 230kV Undervoltage, J16 - Main Generator Negative Sequence, J17/18 - Main Generator Under Frequency. Cause was trip of the Cal Pine to McNary #1 500kV line. No known equipment damage at this time. Line did not reclose automatically / remains open Emergent outage not required at this time. No RAS initiated. <I> **** Actions Taken **** Notified the CRS and Shift Manager. Submitted a CR to document.
395048 | CR | 20190607 |  | 4 | Error found in P-T Curve Calculation CVI 1012-00,4 | N | N |  | N | NO | <D> **** Detailed Description **** During development of the P-T curves for the extended period of operation, an error was found in CVI/CAL 1012 -00,4 â€œNEDC-33144P Rev. 0, Pressure-Temperature Curves for Energy Northwest Columbiaâ€ and reported to the vendor. The centerline elevation of the Water Level Instrumentation (WLI) Nozzle reported in document is incorrect. The reported value was 368 inches, but the actual value is 366 inches. This is a legacy issue do to poor image quality. The OEM was notified and has provided the following statement â€œThis is not a Part 21 concern because the WLI nozzle was not considered in the generation of the P-T Curves and therefore there is no potential for a substantial safety hazard or exceeding safety limits of the Technical Specifications.â€ <I> **** Actions Taken **** Initiated this CR to document the error in the calculation. The vendorâ€™s initiated in response to this finding is posted to EDMS. The correct information has been provided to the vendor for development of the next set of P-T curves so no further action is required. This is not a start-up issue. Recommend trend only.
395049 | CR | 20190607 |  | 4 | SA-PCV-2 loss of indication | N | N |  | N | YES | <D> **** Detailed Description **** SA-PCV-2 has no indication in the MCR. LIght bulbs have been checked. Locally SA-PCV-2 is in the neutral position (not gagged open/shut) and shut indicating fuse TB1A-F01 (EWD-78E-007) is cleared. SA and CAS are not cross -connected. <I> **** Actions Taken **** Configuration control being considered. <N> **** Equipment Description **** TB 441 | 02-00-SA-PCV-2
395050 | CR | 20190607 |  | 4 | (R24) COND-LCV-32B Packing gland bottomed out | N | N |  | N | YES | <D> **** Detailed Description **** Following a repack and during diagnostic testing of COND -LCV-32B it was discovered that the packing gland bottomed out while consolidating. With packing gland bottomed out there was still only minimal friction on the stem. Recommend valve be disassembled this time to find cause of problem and verify if packing is extruding into the system. <I> **** Actions Taken **** Contacted Component Engineering. <N> **** Equipment Description **** T -478- - -G5/5.6 - | 02-00-COND-LCV-32B
395051 | CR | 20190607 |  | 4 | MCR desktop monitor for DEH says virtual memory too low. | N | N |  | N | YES | <D> **** Detailed Description **** The DEH desktop computer. The one that sits on the RO desk now says windows virtual memory too low. â€œYour system is low on virtual memory windows is increasing the size of your virtual memory paging file. During this process, memory requests for some application may be denied.â€ <I> **** Actions Taken **** Informed CRS and computer engineering. <N> **** Equipment Description **** DEH monitor on RO desk in MCR.
395052 | CR | 20190607 |  | 3 | R24 lesson learned (LL) - Turbine (Siemens) support tasks | N | N |  | N | NO | <D> **** Detailed Description **** R24 LL documentation. The turbine support tasks to determ and reterm limit switches and valves as part of the disassembly and reassembly of the turbine should be included in the overall scope for Siemens to perform to include the pmt's. The support tasks were not part of the original outage scope and lacked detailed work instructions. Significant effort is being applied trying to ensure the necesary support is available to Siemens to minimize delays on reassembly. If this support work can't be included in the Siemens scope then improved work order task quality is required to include at a minimum work instructions, determ/reterm sheets and drawings. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
395053 | CR | 20190607 |  | 4 | PP60 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** PP 60 in the 441 GSB needs maintenance. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** security notification made, CR/WR generated <N> **** Equipment Description **** PP60 441 GSB Per discussion with Security LT, this issue does not affect any security function.
395055 | CR | 20190607 |  | 3 | Procedure enhancement for 1.3.84. | N | N |  | N | NO | <D> **** Detailed Description **** A procedure enhancement should be put in for 1.3.84. to state that manually scramming control rods from the RB 522 elevation using the individual HCU test switches is not a reactivity manipulation when the rod is verified to be full in. <I> **** Actions Taken **** Wrote CR
395057 | CR | 20190607 |  | 3 | (R24) TSW-V-251- wrong bonnet gasket | N | N |  | N | NO | <D> **** Detailed Description **** TSW-V-251 was disassembled for an internal inspection (license renewal). Asset Suite D030 panel installation information has this valve as a Borg Warner model 38040. The valve is actually a 1 Â½â€ 800# Velan model W-2054B-13MY (CID 14086). This EPN has been replaced at some point in the past and information was not updated in Asset Suite. After verification of the correct valve manufacturer and model number 2 bonnet gaskets were ordered whose description matched the installed valve, but not the model number. Upon receipt of the new gaskets (CID 34164 and 34165 both identical) it was noticed that they are not bonnet gaskets for any valve, but â€˜FGâ€™ style pipe flange gaskets. The removed bonnet gasket and dimensions are attached in EDMS as well as the comparison to the incorrect gaskets. The following is a summary of identified issues; The correct bonnet gasket for TSW-V-251 is still needed. Asset Suite needs to be updated to reflect the new valve. CIDâ€™s 36164 and 34165 are not correct for the description. <I> **** Actions Taken **** Notified supervisor
395058 | CR | 20190607 |  | 3 | Exposed wires in Drywell 501 going to panel | N | N |  | N | YES | <D> **** Detailed Description **** Red cable with exposed wires on end found on 501 elevation at approximately 338az. in Drywell. Wires traced back to panel TB-C508 at 501 el. 310az. Location wires enter panel are improperly sealed with a rag vice proper panel sealing material. Not sure if exposed wires are live so extreme caution should be taken around wires. <I> **** Actions Taken **** Informed Operations LLRT SRO. Pictures will be loaded into EDMS. <N> **** Equipment Description **** 501 elevation 315 az. for panel and 338 az for wire end. This is work in progress for non-intrusive testing of RRC -V-13B.
395059 | CR | 20190607 |  | 4 | Declutch lever found in Drywell 501 to SMB-0 Limitorque vlv. | N | N |  | N | YES | <D> **** Detailed Description **** Declutch lever for SMB-0 type limitorque valve motor found during cleamup of 501 elevation A RRC side. Not sure what valve is missing declutch lever. Paperwork has WO# 01158000 which seems to be a generic WO to procure parts. Not able to see any valves in area of discovery missing declutch lever. <I> **** Actions Taken **** Quick scan of valves in area of discovery for limitorques missing a declutch lever but none discovered. Photos of lever and paperwork loaded into EDMS. Informed Operations LLRT SRO. <N> **** Equipment Description **** 501 drywell Confirmed with R. Rhodes that this declutch lever was going to be for replacement on RCC-V-71A, WR 29148904. Work did not require replacement and old declutch lever was left installed.
395060 | CR | 20190607 |  | 3 | Editorial change to 16.4.7 | N | N |  | N | NO | <D> **** Detailed Description **** DUring performance of WO 02111930-01 made two editorial pen and ink changes: 7.11.38 Changed from table 7.9b to table 7.11a . 7.14.2 Changed from "IF reactor in NOT in Mode 4 or 5" to "IF Reactor is NOT in Mode 4 or 5" . Need assignment to MAint procedures to update procedure <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
395061 | CR | 20190607 |  | 3 | Difference in RFW-LR-608 and MS-LI-605 OOS | N | N |  | N | YES | <D> **** Detailed Description **** According to 10.27.39, RFW-LR-608 (pt 1) has a tolerance of + or - 3.5 inches and MI-LI-605 has a tolerance of + or -6 inches. During Rx cavity draindown, the difference was approximately 12 inches, which means one or both are out of tolerance. Recommend reviewing calibration procedure in 10.27.39 for better performance. <I> **** Actions Taken **** Ensured multiple indications are used during draindown including visual indication from refuel floor. <N> **** Equipment Description **** MCR | 02-00-MS-LI-605,02-00-RFW-LR-608
395063 | CR | 20190607 |  | 3 | R24LL:SOP-CAVITY-DRAIN need some sign offs changed to (ELEC) | N | N |  | N | NO | <D> **** Detailed Description **** SOP-CAVITY-DRAIN need some sign offs changed to (ELEC) Rev 001, Minor N/A Page 10 step 2.1.10 I and Page 11 step5.1.10 U need the sign off and Simultaneous Verification
395064 | CR | 20190607 | CAQ | C | EWD-46E-240 needs to be updated | N | N |  | N | NO | <D> **** Detailed Description **** EWD-46E-240 needs to be updated to annotate status of SW-V-70B, similar to NOTE 7 on EWD-58E-044. The subject drawing was not identified in EC 15808 (child of EC 12165). SW-V-70B is mechanically locked closed and its MCC breaker removed to maintain proper water chemistry and spray pond inventory. SOP-ELEC-AC-LU has been updated to reflect this change per AS 381813-02. AR 381813 does not contain an assignment to update the subject drawing. <I> **** Actions Taken **** initiated CR.
395065 | CR | 20190607 |  | 3 | R24 LL WO 02111957-20 SOP-Cavity-Drain | N | N |  | N | NO | <D> **** Detailed Description **** R24 LL WO 02111957-20 need support task for electricians (jumper install and removal) and SOP-CAVITY-DRAIN revised. 02111957-86 needs clarification of when this is worked or sequenced. Currently it is sequenced with task 20, but this was not valid. Is it sequence wrong or a contingency? There was a lot of confusion when or if task 86 needed to be performed during task 20. Electrical support was not identified or known to just prior to the task 20 <N> Assignment 01 complete. No further actions required.
395066 | CR | 20190607 |  | 4 | MS-V-165C AS Found Limit switch found labeled incorrectly. | N | N |  | N | NO | <D> **** Detailed Description **** MS-V-165C AS Found Limit switch set #2 found Labeled incorrectly. Label was labeled NO and should be NC. Actual contact state was NC. New switch is labeled correctly. No circuit or plants issues for old or new switches (No actions required). Labeling issue only.
395067 | CR | 20190607 |  | 4 | Dose Alarm | N | N |  | N | NO | <D> **** Detailed Description **** A radiation worker received a dose alarm when welding in the TB 471' heater bay. <I> **** Actions Taken **** Informed supervision interviewed the worker, filled ED alarm form, and wrote this CR. <N> **** Equipment Description **** MS-V-21A Williams Plant Services. Individual started as a fire watch below scaffold. When co-workers on scaffold were close to reaching their dose goal, the individual and co-workers traded position. Individual monitored dose prior to commending work on scaffod and again prior to welding. Individual failed to monitor more frequently once they started welding. Upon receiving alarm the individual put work in a safe condition notified co-workers, left the area and notified HP. Individual was restricted from the RCA pending interview with RP Supervisor and RPM. Dose alarm setpoint was 20mrem and total dose accrued was 21 mrem, RWP 30004277 / ALARA Task 021286100101. Individual understands mistake made and importance of monitoring dose. RPM authorized RCA restriction release. Follow-up survey is documented in VSDS under 201906-07-17. Form 26441 completed. Form and histogram uploaded into EDMS.
395068 | CR | 20190607 | CAQ | D | TG501 Door C420 damaged | N | N |  | N | YES | <C> CR reopened to cross reference additional WP 02145866, marked completion required box, then taken back to complete <D> **** Detailed Description **** A door on the TG 501 corridor is damaged and needs repair. The location is the hallway corridor door closest to the stairwell and main control room. The steel on the door is coming apart just off the lower hinge. The damage creates a sharp edge. <I> **** Actions Taken **** Laborers applied red tape to guard against the sharp edge. A more permanent fix is the desired outcome of this CR. Suggest maintenance remove and repair door. <N> **** Equipment Description **** TG 501 Corridor hallway door C420 near the main control roo m.
395069 | CR | 20190607 | CAQ | D | Release TK-4B and TK-9 to CST with High TOC | N | N |  | N | NO | <D> **** Detailed Description **** After several days of trying to clean up a TOC contamination to the RW system all 3 tanks (TK-9, TK-4A, and TK4B) are contaminated with high TOC's and no more clean up seams to be working. It was decided that during cavity drain down to the CSTs the contaminated tanks would be released and the CST TOC's would be monitored. TK-4B was released first then TK-9 was relesed. The resulting CST TOC value was 121 ppb. <I> **** Actions Taken **** OCC, Chemistry supervision and RWCR informed.
395070 | CR | 20190607 |  | 3 | Contaminated water spilled during hose disassembly | N | N |  | N | NO | <D> **** Detailed Description **** When taking apart the 3 inch drain hose used for draining the RFW and Main Steam line piping in the steam tunnel there was some residual water that spilled out from the hose on to the floor at the Rx 501 drywell step-off pad area. The water was quickly wiped up. However it appears that some of the contamination was spread around in the immediate area. After HPâ€™s checked the contamination levels, the floor had to be mopped several times over to decontaminate the walkway areas. The floor is now back to normal contamination levels after mopping. Additional help and dedicated HP support should have been used by the EO when disassembling the drain hose to avoid such an instance. The 3â€ drain hose was bagged and surveyed by HP for disposal. <N> Coached EO invvolved.
395071 | CR | 20190607 |  | 3 | TMOD EC 16868 restoration W/O CRS/SM milestone approval |  |  |  | N | YES | <D> **** Detailed Description **** It appears that TMOD EC 16868 restoration is effectively in-progress per R24 WO 02080273 (WOT 02080273-01 is FINISHED) and R24 WO 02078727 (WOT 02078727-01 is FINISHED) but the '460-R TMOD OPS' milestone has not yet been signed by the CRS/SM in Portal J. R24 WOT 02122004-01 (RESTORE TMOD EC 16868) remains at READY status but refers to WO 02080273 and WO 02078727. . Recommend the CRS/SM consider signing the TMOD EC 16868 '460-R TMOD OPS' milestone in Portal J. This is an administrative issue. | 02-00-MS-V-165C,02-00-MS-V-166C
395072 | CR | 20190607 |  | 4 | RCIC pump suction pressure high alarm in MCR. | Y | N |  | N | YES | <D> **** Detailed Description **** RCIC pump suction pressure high alarm came in the MCR. The RCIC system is aligned for overspeed testing with WO 02111845 and is isolated per O-RCIC-OVSP-R24-001. RCIC-P-3 is continuously running for this test and the RCIC suction pressure is very slowly increasing. <I> **** Actions Taken **** Wrote CR Informed CRS <N> Testing in progress for overspeed testing. RCIC-V-110 is closed, so this condition is not unexpected. There is no DNC at this time. | 02-00-RCIC-PS-21
395073 | CR | 20190607 |  | 4 | CAS-C-1A may be the source of Oil into T-2 Sump | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1A has had low oil levels on 2/6/19 (CR 389695), 5/22/19 (CR393946) and 6/5/19 (CR 394921). Leakage from the CAS compressors go to the RB T-2 Sump, which has had high TOCâ€™s last week (CR394829). This required the water to be pumped out to barrels. The T-2 sump pump (FDR-P-13) is currently Cautioned Tagged in Pull-to-Lock to prevent the high TOC water from being pumped to the FDR collection tank. The last sample of the T-2 sump (today) also had very high TOCâ€™s and it will need to be pumped to barrels again. <I> **** Actions Taken **** Wrote Local Clearance for CAS-C-1A to allow investigation by the FIN team and to limit use of the Compressor . Informed Chemistry regarding the issue . Informed FIN team | 02-00-CAS-C-1A
395074 | CR | 20190607 |  | 3 | EDR-LS-19A wrong Manufacturer listed on IMDS | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** went to replace EDR-LS-19A and the Planner orderd a Square D Level switch per IMDS and it turned out to be a non stocked Furnace level switch model #69L2163H Need engineering to update IMDS RW437 W6 sump WO# 0208590901 <I> **** Actions Taken **** Notified supervisor
395075 | CR | 20190607 |  | 4 | Foreign Material Removed from COND-HX-9 Hotwell |  |  |  | N | YES | <D> **** Detailed Description **** Several bags of foreign material were found in the Main Condenser Hotwell during the final closeout cleaning and inspection. Laborers and Engineering completed the cleaning and inspection tasks concurrently, and all material and debris found in the hotwell were removed prior to the final FME inspection. The bulk of the material removed was sludge; however, several objects were found and removed as well . These objects included but were not limited to a piece of unistrut approximately 12" in length; several segments of scaffold wire; several small metal pieces resembling weld filler material; several screws and nails; 2 metal washers; a plastic tag; two metal pins resembling tool parts; a small black plastic tool part identified as a TIG torch back end cap; a small plastic ceramic piece identified as a portion of a TIG torch cup; 2 long metal rods; a large quantity of corrosion products; and a variety of other small plastic and metal debris. See attached photos. <I> **** Actions Taken **** Removed all foreign material and debris found inside the Hotwell. Notified the Condenser HX Project Manager, OCC, and EOC. <N> **** Equipment Description **** TG 441' | 02-00-COND-HX-9
395076 | CR | 20190607 |  | 3 | EC 16785 MS-V-163B and 164B wrong bolts ordered/installed | N | N |  | N | YES | <D> **** Detailed Description **** EC 16785 MS-V-163B and 164B wrong bolts ordered/installed. A307 3/8 bolts (torque 9ft lb)were ordered and installedl that hold the 18 x18 (approx.). mounting plate. EC 16785 requires A 193 grade B7 3/8 bolts. Need planning to order the correct bolts. Work instructions will need to be changed. OR Engineering will need to approve the installed bolts. We can change these bolts out one by one and not dismantle any of the switches, but will need a clearance in place.Torque value on the EC bolts specâ€™d bolt are about 3 times what is install. <I> EOC Design determined ASTM A307 fasteners could be used in lieu of A193, Gr. B7 for the limit switches mounting (for MS-V-163B/164B). There is no existing calculation that requires update(s); but a computation (uploaded to EDMS) was performed. Provisions of PPM 10.2.10 for A307 should be applied for torqueing requirements. Maintenance notified and EC0000016785000C.FCR approved and uploaded to EDMS for EC 16785 (see email in EDMS). <N> Condition has been addressed. Error will be trended. | 02-00-MS-V-163B,02-00-MS-V-164B
395077 | CR | 20190607 |  | 4 | Trouble shooting MS-MO-115B identified pinched wires | N | N |  | N | YES | <D> **** Detailed Description **** Trouble shooting MS-MO-115B identified pinched wires in the Limitswitch compartment. <I> **** Actions Taken **** Repaired wires and loose connections via WR 29149395. No additional actions required. | 02-00-MS-MO-115B
395078 | CR | 20190607 |  | 4 | HV-V-31G - Degraded valve | N | N |  | N | YES | <D> **** Detailed Description **** After the seats were cleaned up, the seats were identified to be degraded beyond repair. The valve requires replacement in future outage. <I> **** Actions Taken **** Provide direction to craft to reassemble valve with new stem and plug . Generated WR to replace valve in future outage. | 02-00-HV-V-31G
395079 | CR | 20190607 |  | 3 | PPM 10.2.79 Packing procedure |  |  |  | N | NO | <D> **** Detailed Description **** PPM 10.2.79 packing procedure recommends the packing on MOV's to be consolidated to the preferred packing torque instead of the initially consolidated at the minimum torque value and then increase until the packing reaches 130% of running load current. Recommend revising procedure consolidate packing to the minumum valve per PPM 10.2.79 and then increase/consolidate upto 130% of running loads
395080 | CR | 20190607 |  | 4 | RFW-FCV-2A indicates 103% when closed. 2 actions needed | N | N |  | N | YES | <D> **** Detailed Description **** AOV worker indicated he needed valve stroked from MCR. Will not stroke with RFW-DT-1A trip in so work stopped. AOV worker indicated the valve full stroked in ~ 5 sec. Fast stroking the RFW min flow valves causes issues with the string driven position variable resistor. Suspect the valve position assembly needs to have the string untangled. In ADDITION suggest RFW-FCV-2A and 2B AOV packages be changed to reflect not to stroke these operators fast as this is not the first time this has happened. RFW-FCV-2B only needs work package updated. | 02-00-RFW-FCV-2A,02-00-RFW-FCV-2B
395081 | CR | 20190607 |  | 3 | Found gas valve for DEH-TK-1C leaking | N | N |  | N | YES | <D> **** Detailed Description **** During DEH accumulator charge up, found the Gas Valve for DEH-TK-1C with a small leak, the leak went away with the Cap installed. this gas valve should be replaced when parts are available. We were able to charge the accumulator. CATID 54918500 is the required part number that needs to be changed out. <I> **** Actions Taken **** Notified supervision, continued with PM. CATID - 54918500 is not in stock, this CATID has been used 65 time according to passport and should be a stocked part. | 02-00-DEH-TK-1C
395082 | CR | 20190607 | CAQ | D | E-CB-TRB breaker would close during overhaul but releases al | Y | N |  | N | YES | <D> **** Detailed Description **** During the overhaul of the CB-TRB mechanism service while trying to close the breaker as part of WO 02111568 the breaker would close but the controls were allowing the air to discharge and drain the tank. This breaker requires air to close and no air is required to open the breaker. It appears this a problem is with one of the breaker contacts not resetting and allowing air to leak by the close solenoid valve (52C). Currently this condition is being investigated and repaired under WO 0211568. This CR is to just document the condition with the circuit breaker. Currently, E-CB-TRB is under clearance for the OCB mechanism service and this condition will be repaired prior to returning the breaker to service. | 02-00-E-CB-TRB
395083 | CR | 20190607 |  | 3 | R24LL: PCR for TSP-RPS-B501 |  |  |  | N | NO | <D> **** Detailed Description **** SDV level high trip sections 7.5,7.6,7.7,7.8 need steps added prior to 7.5.6 (other sections similar) to 1) rotate push to cal knob to position (best at 7.5.3 after d) 2) reset the cal unit if digital indicators are not at ~0 best righ after power on at 7.5.5 pushing in press to cal knob in if not in correct position or trip not reset will result in tripping SDV 1/2 scram / -50" logic (1/4) and or -129" logic (1/4)
395084 | CR | 20190607 |  | 4 | SEC-CCTV-12 needs cleaned | N | N |  | N | YES | <D> **** Detailed Description **** SEC-CCTV-12 has a poor picture quality due to being dirty. Request electrical maintenance to service the camera. <I> **** Actions Taken **** Compensatory measures initiated; CR/WR Generated | 02-00-SEC-CCTV-12
395085 | CR | 20190607 |  | 4 | COND-42-3B6A failed to close | N | N |  | N | YES | <D> **** Detailed Description **** While lifting tags under clearance O-LPTURB-MANWAY-001 disconnect COND-42-3B6A would not close in. <I> **** Actions Taken **** Informed SSS and wrote CR | 02-00-COND-42-3B6A
395086 | CR | 20190607 |  | 4 | Small Godwin pump had alarm and vibration | N | N |  | N | YES | <D> **** Detailed Description **** The small Godwin pump currently being used to blowdown the circ water system was making a "chug-chug" sound and vibrating. Also, the panel displayed an "ECU Engine alarm". The pump sounds like it might be missing. Please investigate. <I> **** Actions Taken **** Shutdown the small Godwin and started the bigger one for blowdown use. Notified SMgt, wrote CR. <N> **** Equipment Description **** Smaller Godwin pump near CW pumphouse.
395087 | CR | 20190607 | CAQ | D | EDR-TK-4A sent to the CST with out of spec TOC | N | N |  | N | YES | <D> **** Detailed Description **** EDR-TK-4A was authorized to be sent to the CST with a TOC of 1240 ppb. The reject tank EDR-TK-5 is nearing full and water is rapidly coming to radwaste. <I> **** Actions Taken **** A volume dilution calculation was performed and the estimated CST TOC concentration following the transfer of EDR-TK-4A would be 148 ppb which is below the limit of 200 ppb . Chemistry supervision was consulted and concurred with the transfer. | 02-00-EDR-TK-4A
395088 | CR | 20190607 |  | 3 | R24 LL Rx buidling areas contaminated during Rx cavity drain |  |  |  | N | NO | <D> **** Detailed Description **** During drain down of the Reactor cavity and bellows three areas of the reactor building were contaminated: CRD pump room to 350,000 dpm/100cm2 RCIC pump room to 60,000 dpm/100cm2 2 samll areas in the SW floor area of 471 Rx to 5000 dpm/100 cm2 Needs some action to prevent recurrence. <I> **** Actions Taken **** Clean up of the area is in progress. <N> Reopened at operations request for additional actions. Reassigned to rad planning. Ops will correct the procedure under AR 395183 as well as 395063 but RP can research the option to flush prior to the work starting
395089 | CR | 20190608 |  | 4 | TO-42-2D3C Will Not Close | N | N |  | N | YES | <D> **** Detailed Description **** Disconnect TO-42-2D3C could not be closed when lifting O -E-GEN/TURBR24-001. Request electricians investigate/lubricate disconnect. <I> **** Actions Taken **** Wrote CR, notified production center and electricians. | 02-00-TO-42-2D3C
395090 | CR | 20190608 | CAQ | D | RRC-CB-RRA degraded | N | Y |  | N | YES | <D> **** Detailed Description **** Issues found during the performance of Surveillance; Breaker Operation was â€œSluggish.â€ Post Lubrication. Breaker failed to close on degraded voltage within criteria. Breaker Closes and charges at 97.5 VDC, Criteria is (89.5 Â± 0.5 VDC) Gap at bottom edges of MOVABLE and STATIONARY MAIN Contact. Out of tolerance, Measured 4-15/16 in. Acceptance criteria is GE 5-1/4 in. Found during the performance of WO 02113058-01 <I> **** Actions Taken **** Ordered/Place a demand on a replacement breaker, One is available. Notified OCC. <N> **** Equipment Description **** T -471- - -E1/14.5- | 02-00-RRC-CB-RRA
395092 | CR | 20190608 |  | 4 | TO-42-2C1B disconnect not staying closed in | N | N |  | N | YES | <D> **** Detailed Description **** When clearing tags and closing disconnect TO-42-2C1B, the disconnect opened on its own when the operator let go of the switch. This happened twice before staying closed. The disconnect still feels like it will pop open again with the slightest disturbance. <I> **** Actions Taken **** Informed supervision. Wrote CR. | 02-00-TO-42-2C1B
395093 | CR | 20190608 |  | 4 | Several 42 devices would not close and stay closed | N | N |  | N | YES | <D> During removal of tags per O-COND-HX-9/R24-001, MD-42-1B4C, MD-42-1B10C, MD-42-2P5D, and MD-42-2P8D would not close and remain closed. Attempted to cycle breakers a few times and 42 devices would not close. Door interlocks are not the problem, the breakers needs to be lubricated, cycled, and closed. <I> Attempted to cycle breakers. Notified supervision Initiated CR and WR <N> TB 441 | 02-00-MD-42-1B10C,02-00-MD-42-1B4C,02-00-MD-42-2P5D,02-00-MD-42-2P8D
395094 | CR | 20190608 | CAQ | D | EDR-TK-4B sent to CST with out of spec TOC | N | N |  | N | YES | <D> **** Detailed Description **** EDR-TK-4B was authorized to be sent to the CST with TOC = 616 ppb. This is above the specification limit of 200 ppb. The tank was authorized due to a large influx of water to radwaste and dwindling storage space. A dilution calculation was performed. The resulting CST TOC is estimated to be 160 ppb. <I> **** Actions Taken **** Notified supervision and RWCR | 02-00-EDR-TK-4B
395095 | CR | 20190608 |  | 3 | ESOMS clearance tag printing problem; cuts off text |  |  |  | N | YES | <D> **** Detailed Description **** There has been an ongoing problem with printing the clearance tags in ESOMS for a least 2.5 years. What happens is if the noun name or EPN takes near, or more than, an entire line on the tag, several characters get cut off. This leads to nown names missing information regularly; though EPN's being that long are rare, they can be impacted, but are generally are not. The exact reason for the missing text it not known. It is possible the printers max width is being exceeded, it could be a formatting issue, who knows. This is a basic task of printing information on a material. There is no doubt that this can be fixed. In this time we place a heavy emphasis on touch-read-read and verifying the information is correct and/or the noun name is a accurate match. It adds to the confusion when trying to match up wordy tranformer yard ground strap tags, for example. <N> **** Equipment Description **** Tag printing issue.
395097 | CR | 20190608 | CAQ | D | Drywell Equipment Hatch Bolt Damage | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02114006 and PPM 10.3.11 on 06/07/19, QC noted damage to 5 bolts during their inspection of each bolt for thread damage. Engineering was called out to examine the damage to the bolts. Engineers found some slight flattening of the threads. The damage would have a negligible impact on the ability of the fasteners to hold the hatch in place and prevent leakage during all design conditions. Further investigation found that the areas on the bolts with indication of damage were outside of the normally engaged area of the bolt (inboard or outboard of the nut). Therefore the condition identified would not prevent the equipment hatch from performing its current license basis design function and the bolts can be used. The three engineers included a statement in the work order package stating as such. No further actions necessary. See EDMS for photos of some of the bolt damage. <I> **** Actions Taken **** Notified the EOC. Contacted the QC hotline to discuss. Added a note in WO 0211406 PPM 10.3.11. <N> **** Equipment Description **** Drywell Equipment Hatch | 02-00-C-TK-1
395098 | CR | 20190608 |  | 4 | Flex conduit found degraded | N | N |  | N | NO | <D> **** Detailed Description **** During work on WO#02070243-02, found a flex conduit going to Term Box E near the HP Turbine slightly disconnected. The conduit is labeled ATU-413-1 Div A With supervisor concurrence, reconnected and tighted the flex up. <I> **** Actions Taken **** Notified supervisor, took pictures (see EDMS), corrected minor issue, wrote this CR. <N> **** Equipment Description **** Term Box E on North side of HP turbine
395099 | CR | 20190608 |  | 4 | SS-V-20 continously porting air | N | N |  | N | YES | <D> **** Detailed Description **** While performing a walkdown of the turbine building 471' heater bay, a loud air sound could be heard coming from the air actuator of SS-V-20. The air was porting from the blue painted portion of the valve. It might be a torn diaphragm. <I> **** Actions Taken **** Informed SSS and wrote CR. | 02-00-SS-V-20
395100 | CR | 20190608 |  | 4 | HD-LCV-3B2 instrument air leak | N | N |  | N | YES | <D> **** Detailed Description **** While performing a walkdown of the turbine building 471' heater bay, a loud air noise could be heard coming from the ground level from 12 feet away. Instrument air is leaking from the black box that has the three instrument air guages for instrument air in, air output and supply air. <I> **** Actions Taken **** Informed SSS and wrote CR | 02-00-HD-LCV-3B2
395101 | CR | 20190608 |  | 4 | Positive body count |  |  |  | N | NO | <D> **** Detailed Description **** A worker was released from the plant with a positive body count (9.3 nCi Co-60). Worker C7346D was working on bleed steam valves in the TG 471' TG buidling prior to obtaining an exit body count. Worker was body counted, surveyed showered body counted showered and whole body counted and surveyed again. The final body count took place with all new clothing and no shoes, lanyard, safety glasses or dosimetry. Worker released with RPM delegate and PGM concurrence. <I> **** Actions Taken **** 2 body counts, direct surveys obtained RPM approval. Wrote the CR <N> See positive whole body count log for additional informationn. No further action required.
395102 | CR | 20190608 |  | 4 | TSW-HX-4A,4B,&4C piping not Isolated from COND-M-P/1A,1B,&1C | N | N |  | N | YES | <D> **** Detailed Description **** While performing meggering accross insulating flanges in WO#02108851-19 it was discovered that there was no isolation between TSW-HX-4A,4B,&4C piping and COND-M-P/1A,1B,&1C. There are several scaffold poles that are installed up against the isolated stanchions and the newly installed guage on the TSW-HX-4B piping is laying against electrical conduit ACOMA-197-7. We are suposed to have greater than 1 Mohm when meggering across the isolation flanges and we are reading 0 which is a direct short. Need scaffold removed and guage isolated. <I> **** Actions Taken **** Informed my supervisor and the OCC. Wrote this CR Added photos to EDMS <N> **** Equipment Description **** On COND-M-P/1A,1B and 1C | 02-00-TSW-HX-4A,02-00-TSW-HX-4B,02-00-TSW-HX-4C
395103 | CR | 20190608 | CAQ | D | TOC Exceeds Limit for Two Tanks | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Tank 9 and tank 4A exceeded the TOC specification for transfer to the CST, at 340 ppb and 290 ppb respectively. Approval for transfer was given to provide space in the radwaste system for vessel level control. The TOC in the radwaste system is trending down as the RWCR determines how best to remove the contaminant. <I> **** Actions Taken **** Informed Specialist, discussed with RWCR, informed OCC
395104 | CR | 20190608 |  | 4 | PSR-SR-6 valve leaks | N | N |  | N | YES | <D> **** Detailed Description **** Minor leak PSR-V-SR6-V6 while opening/closing valve. <I> **** Actions Taken **** Informed supervision, wrote a CR. | 02-00-PSR-SR-6
395106 | CR | 20190608 |  | 3 | R24 LL Containment Vaccum Breakers LLRT Per WO 02113904 |  |  |  | N | NO | <D> **** Detailed Description **** CVB-V-1EF/1CD LLRTs could not be initially performed due to inability to reach test pressure conditions. Recommend that WO instructions be added to specify that the test flange could be either Plexiglass OR Aluminum (used in prior outages - See pictures in EDMS). Also additional instructions on how to setup the LLRT cart hoses/instruentation to ensure adeqaute test pressure conditions are attained is recommended. Recommend assignment to Tech Services Engineering.
395107 | CR | 20190608 |  | 4 | WO: 02111681-01 HD-LT-7B out of cal | N | N |  | N | NO | <C> MRT Change request: CR 395107 Severity moved from CAQ D/Trend Repair to Severity 4 NON-CAQ. <D> **** Detailed Description **** CR generated for tracking purposes. Transmitter HD-LT-7B found out of tollerance. Calibrated back into tollerance. <I> **** Actions Taken **** CR generated for tracking purposes
395108 | CR | 20190608 |  | 4 | E-B1-6 | N | N |  | N | NO | <D> **** Detailed Description **** During the monthly battery test of E-B1-6 (10.25.5A) we found that the opening for the spark arestor on cell 78 is cracked. This is not an opporability issue. The CR is for tracking only. <I> **** Actions Taken **** took pictures, notified supervision and initiated CR <N> **** Equipment Description **** E-B1-6
395110 | CR | 20190608 |  | 3 | Doble 6150 Training for Meter/Relay Technicians |  |  |  | N | NO | <D> We are seeing Schweitzer relays in the open phase project and the control room is going to be modified to use more of these Digital relays. The Doble 6150 is used to calibrate and program these relays. <I> Notified Supervision <N> CR at INPROG. Approved CR, moved to SRO for OPS Review. TREQ 19-0073 generated on 5/17. No further actions required for this CR.
395111 | CR | 20190608 |  | 3 | R24 lesson learned - MS-V-163B and 164B limit switch mods |  |  |  | N | NO | <D> **** Detailed Description **** R24 LL documentation. WO's 02080035-01 and 02115411-01 to modify existing limit switches for the 1B crossover Intercept and Reheat stop valves required significant enhancement to provide the necessary work instruction and parts to perform the work. The hardware originally planned in the EC was not readily available resulting in a last minute change to the EC. The preoutage support task to build the limit switch assemblies was cancelled - reason unknown. This resulted in an additional 24mhrs to the scheduled duration. The mounting plates had to be moved approximately two inches to one side due to interference DEH piping. Recommend incorporate these lessons learned in the future MS valve modification.
395112 | CR | 20190608 |  | 4 | Data Access Desktop is down |  |  |  | N | YES | <D> **** Detailed Description **** Data Access Desktop is down. This provides data for OSP -RCS-C105. Need to investigate and repair. <I> **** Actions Taken **** Contacted IS. <N> **** Equipment Description **** Data Access Desktop program. Data Access Desktop program was not down. There was an issue with one report which was related to bad data entered into eSOMs. The data was corrected and the issue resolved. Recommend NCAQ4 trend to ITMGMT.
395113 | CR | 20190608 |  | 3 | R24 lesson learned (LL) - DEH solenoid valve replacements |  |  |  | N | NO | <D> **** Detailed Description **** R24 LL documentation. WO 02111672-01 to change out 12 solenoid valves for the B crossover valves did not include a necessary mechanic support task to replace the o-rings and solenoid. It was also discovered that a second set of o-rings is required for each solenoid valve and only one set was reserved. This task can be difficult to complete in one day if the cross-over valves are not accessible due to disassembly of the turbine.
395114 | CR | 20190608 |  | 4 | Disconnect RWCU-42-8CA3B (RWCU-V-35) will not close | N | N |  | N | YES | <D> **** Detailed Description **** Electrical assistance is needed to repair/lubricate disconnect RWCU-42-8CA3B <I> **** Actions Taken **** Informed FIN | 02-00-RWCU-42-8CA3B
395115 | CR | 20190608 |  |  | HCU 50-43 Leaking at P6 Connector |  |  |  | N | YES | <D> **** Detailed Description **** HCU 50-43 is leaking at the P6 connecter. <I> **** Actions Taken **** Applied neo-lube, torqued to max spec of 200 in-lbs. Informed MCR <N> **** Equipment Description **** R522 | 02-00-CRD-HCU-5043
395116 | CR | 20190608 | CAQ | D | CRD HCU 50-43 Leaking at P6 Connector | Y | N |  | N | YES | <D> **** Detailed Description **** CRD HCU 50-43 is leaking at the P6 connector. <I> **** Actions Taken **** Applied neo-lube and tightened to max spec of 200 in-lbs Informed MCR <N> **** Equipment Description **** R522 | 02-00-CRD-HCU-5043
395117 | CR | 20190608 |  | 3 | Peer Verification using work requests |  |  |  | N | NO | <D> **** Detailed Description **** Per PPM 1.3.68 section 4.3, work that requires either no inspection from QC or peer verification only qualifies for work as minor maintenance and can be performed under a work request. QAP-ASU-07 section 4.1 for peer verification applicability does not reference work requests, only referring to work order tasks. This has led to some confusion on whether peer verification can be performed under work requests. Need to enhance QAP-ASU-7 to make clear that peer verification is allowed on work requests.
395118 | CR | 20190608 |  | 3 | Chem Permit #0873 needs updated |  |  |  | N | NO | <D> **** Detailed Description **** Chem Permit #0873 is for Compressor Fluid 24KT. The permit specifies â€œLimited Use: Air Compressor SAC-1â€. Sullair 24KT Fluid is used in CAS-C-1A/1B/1C per the vendor manual. PPM 10.2.13 also lists Sullair Fluid 24KT as the appropriate lubricant for the CAS compressors. The Chem Permit needs to be revised to include the CAS compressors as part of the acceptable use for this oil. The chem permit also states to keep out of plant floor drains which is appropriate. This may be the source of elevated TOC concentrations in radwaste processing.
395125 | CR | 20190608 |  | 4 | E-C1-7 lessons learned |  |  |  | N | NO | <D> **** Detailed Description **** While performing Procedure 10.25.18A, per work order 02111958-01, electricians recognized a warning sticker on the door of E-C1-7 charger that implies a voltage adjustment is required on E-IN-5 prior to placing E-C1-7 into equalize voltage range. Normal float voltage for this charger is 130.5 VDC. 10.25.18A requires voltage adjustment up into the 143 VDC range. It is unknown if the Warning sticker applies to the scope of work in 10.25.18A. A picture of the warning sticker will be attached to this CR <I> **** Actions Taken **** Notified Supervision, Notified Engineering support Write CR/WR <N> **** Equipment Description **** E-C1-7 ROOM c224 vital island
395126 | CR | 20190608 | CAQ | C | Missed QC Material Verification |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Parts/Material Verification in work step 4.1 of 02145021-01 was not satisfied by a Quality Control or Qualified Peer Verifier. The parts/material verification was signed off by a crafts person. The stock material in question is a one 1/2â€ U-bolt (Cat ID 0025144994), one piece of flat bar (CAT ID 0030009231) and one piece of half-round shim stock 2â€ long cut from Â½â€ pipe (CAT ID 0051002721). The half-round pipe and flat bar have been welded in place and the welds were inspected and signed-off by Quality Control. Engineering has been notified of this condition and is evaluating the condition. Facts: â€¢ CAT ID 0030009231 - Flat Bar Heat Number per Green Tag is JH0326. â€¢ Cat ID 0025144994 - U-Bolt Heat number MIC# 21522 NR per the Green Tag. U-Bolt Nuts MIC# 22111 NB per the Green Tag. â€¢ CAT ID 0051002721 - Â½â€ pipe Heat Number is 00A132342 per the Green Tag. â€¢ The three materials listed above were issued on Issue Ticket 42980200. <I> **** Actions Taken **** OCC, Site Support Contractor Manager and Quality Services has been notified. <N> Williams Plant Services. Based on the discussions with Williams supervision and the information provided in the CR along with the QC inspection performed per step 4.22 for the final weld inspection, there is reasonable assurance that the parts used are the same as those required per the WO to perform the job.
395127 | CR | 20190608 |  | 3 | Specified C/O Not Signed Onto |  |  |  | N | NO | <D> **** Detailed Description **** Welding was performed on a shim for a U-bolt using Work Order 02145021-01 without the craft or supervisor not signing onto the clearance order. Printed work package stated Clearance Not Required on page 4. Portal J requirement screen indicated a clearance was required. Task 01 was originally planned to replace the reducing valve, however the reducing valve was removed from task 01 and moved to task 09, leaving U-bolt welding (no system breach) as the only work on task 01. The revision to task 01 was not routed to CORC or OPSWC to remove the requirement of a clearance in portal J. The work order was reviewed by Operations post work and determined to not need a clearance due to no system breach, therefore, based on Operations instruction, this is a level 4 clearance error as the planner should have either routed to WC for requirement adjustment or removed the requirement. <I> **** Actions Taken **** Notified Operations, OCC, Site Support Contractor Manager and Rx/MM Manager. <N> Williams Plant Services.
395128 | CR | 20190608 |  | 3 | TG-MON-SPD still does not function | N | N |  | N | YES | <D> **** Detailed Description **** When starting TO-P-BLP per SOP-MT-START to allow Siemens to perform the "swing check" for shaft eccentricity at bearing 11 (exciter end bearing) it was observed that TG-MON-SPD did not indicate at all. No digits were lit up for turbine speed, most of the panel was blank. When switching channels on the instrument to its right (TG-EF-1) the LCD display would light up intermittently, but only when switching, the lcd would again go dark when a channel was selected. These observations occured AFTER WO 02119478 was taken to finished. If MT speed indication at this instrument is not corrected within the next ~48 hours, Columbia may be forced to go another cycle with equipment important to the health of the Main Turbine in a degraded condition. This equipment issue already nearly resulted in major bearing damage during the Forced Outage prior to R24. <I> **** Actions Taken **** Informed System Engineer and Ops Manager. | 02-00-TG-EF-1,02-00-TG-MON-SPD
395129 | CR | 20190608 |  | 4 | R24 LL: Schedule logic/duration |  |  |  | N | NO | <D> **** Detailed Description **** Schedule logic and duration for the start of the MT Seal Oil system for Exciter End "swing check" preparations were misunderstood during implementation. Original schedule had a duration of 14 hours from the start of the clearance lifts to having the MT Oil and MT Seal oil systems running in the state required to perform the Exciter end eccentricity measurments. One enhancement to shorten the duration would be to clarify the Seal Oil to SCW D/P requirements and expected system response when the SCW system is not yet running and the Main Generator is filled with air (not H2 or CO2).
395130 | CR | 20190608 | CAQ | D | E-CB-TRB cabinet Heater is On | Y | N |  | N | YES | <D> **** Detailed Description **** During WO 02111568-01 E-CB-TRB: OCB MECHANISM SERVICE, oil circuit breaker cabinet heater was on when it did not need to be. There is a deficiency tag dated 7/14/2011 stating that the thermostat does not cut the heater off. The deficiency tag (see EDMS) references W/R 29091099 which has been actioned to WO 02020047 (Status PLAN). Additionally, the fuses feeding the cabinet heater should have been pulled during SOP-WARMWEATHER-OPS step 6.8.2 â€œREMOVE the E-CB-TRB OCB Operating Housing Heater fuses as follows:â€ Recommend removing the E CB-TRB cabinet housing heater fuses per SOP-WARMWEATHER-OPS. Recommend scheduling/performing WO 02020047 â€œE-CB-TRB 23 DEVICE DOES NOT OPEN ON TEMP ABOVE SETPOINTâ€ to facilitate the repairs of the heater controlling thermostat. <I> **** Actions Taken **** Discussed with the System Engineer and Initiated CR | 02-00-E-CB-TRB
395132 | CR | 20190608 | CAQ | D | CRD-HCU-3031 has a leak from the N2 bottle | Y | N |  | N | YES | <D> **** Detailed Description **** The N2 bottle connection on CRD-HCU-3031 has a leak from the connection to the cylinder. <I> **** Actions Taken **** Isolated HCU per SOP-CRD-HCU. <N> **** Equipment Description **** RB 522 | 02-00-CRD-HCU-3031
395133 | CR | 20190608 | CAQ | D | CRD-HCU Accumulators will not hold a charge | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-5419 and CRD-HCU-3423 will not remain charged following pressurization, indicative of a small N2 leak somewhere on the HCU <I> **** Actions Taken **** Informed OCC | 02-00-CRD-HCU-3423,02-00-CRD-HCU-5419
395134 | CR | 20190608 | CAQ | D | 2 HCU-V-107â€™s are leaking by | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-V-107/5427 and CRD-V-107/3423 are leaking by. HCU-3047 has the V-107 plug removed. <I> **** Actions Taken **** Informed OCC | 02-00-CRD-V-107/3423,02-00-CRD-V-107/5427
395135 | CR | 20190608 |  | 4 | OG-SR-11A leak | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** OG-SR-11A had two leaks, one in the pump input fitting and one in the iodine charcoal filter. The leaks were discovered during the performance of PPM 16.4.4. <I> **** Actions Taken **** Tightened the fitting and the filter housing then re performed the leak check. Final leak check passed. <N> **** Equipment Description **** OG-SR-11A RW 452
395136 | CR | 20190608 |  | 4 | Tubes weld and tubesheet damage in A waterbox | N | N |  | N | YES | <D> **** Detailed Description **** During the ultrasonic testing under vacuum pull in the A waterbox of the main condenser, two tubes in the upper inlet module (LPAU) show weld and tubesheet damage (see pictures in EDMS). Itâ€™s believed that this damage is caused by foreign materials vibration against the two tubes and the tubesheet. Those tubes are going to be permanently plugged. This is for trending. | 02-00-COND-HX-9
395137 | CR | 20190608 |  | 4 | confirmatory grease evaluation for MS-MO-70D needed | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Per WO#02117213--01, electricians performed external PM of SMB-00 MOV. In the process of obtaining grease sample from motor pinion housing/main gear housing it appears as though the grease sample is possibly a mixture of MOV LL and Mobil 28. The Mobil 28 is naturally red in color and the MOV LL is more of a white/tan color. the sample taken from the gear housing is mostly red. Supervision and MOV engineer notified of the discrepency. <I> **** Actions Taken **** Notified Supervisor, Notified Engineer and Write CR/WR <N> **** Equipment Description **** MS-MO-70D
395138 | CR | 20190608 |  | 4 | Erratic functioning of SW reactor building elevator. | N | N |  | N | YES | <D> **** Detailed Description **** The elevator operator notified operations of erratic functioning of the SW RX elevator. Sometimes when the elevator is at the 606â€™ elevation and the 441â€™ elevation button is pressed, the doors close but the elevator doesnâ€™t move. Sometimes this doesnâ€™t occur and the elevator operates normally. It only occurs at the 606 with the 441 button pressed. Possible degradation of 441â€™ elevation button or elevator control panel wiring issue. Please investigate. <I> **** Actions Taken **** Notified MCR <N> **** Equipment Description **** SW Reactor Building Elevator | 02-00-MT-ELEV-2
395139 | CR | 20190608 |  | 4 | Small hole found in steam piping during vacuum pull | N | N |  | N | YES | <D> **** Detailed Description **** Discovered 1/4â€ x 1/16â€ split in steam piping downstream of BS-V-52B where the piping enters the condenser. The affected piping is located in the Heater Bay ~ 15â€™ to the right of the â€˜Câ€™ Bay entry hatch on TG 471â€™, ~3 â€™-4â€™ above the floor. This leak was discovered during vacuum pull. Air could be heard sucking through the hole. See pictures in EDMS folder. <N> This issue was discovered during a BOP walkdown while looking for vacuum leaks during vacuum pull. | 02-00-BS-V-52B
395140 | CR | 20190608 |  | 4 | Insect Bite |  |  |  | N | NO | <D> **** Detailed Description **** At beginning of night shift 06/08/2019 employee reported insect bite to left forarm. Report only, employee retuned to work. <I> **** Actions Taken **** Suspected area of insect was searched, no insect found. Employee returned to work. <N> **** Equipment Description **** CGS - Bldg 88
395141 | CR | 20190608 |  | 3 | R24 Lessons Learned RCA Coordinators Needed |  |  |  | N | NO | <D> **** Detailed Description **** Highly recommend utilizing 5 RCA Coordinators on each shift. Coordinators would work in unison with the work groups and the OCC to track task, remove barriers, and assist departments implement planned work to stay on schedule. In the field, the Coordinators would work in unison with each other and the OCC to identify roadblocks, and assist the work groups to move forward. For example, a job may need a confined space attendant, a high rad brief scheduled, or another work group is unaware they are holding up a job. Additionally, having RCA Coordinators would further allow supervisors to oversee their teams in the field ensuring procedural requirements are met and safety practices are followed. The competing priorities of both supervising workers in the field and coordinating the work is adding copious amount of time to our outage. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817. Transferred from RP to OTMG at RP mgmt request
395142 | CR | 20190608 |  | 4 | PRIMARY ACCESS CM 11 HP EQ 53253 Failure | N | N |  | N | YES | <D> **** Detailed Description **** FAILED COUNT TEST | 02-00-HP-EQ-53253
395143 | CR | 20190608 |  | 3 | R24LL Clean Tool Process not followed |  |  |  | N | NO | <D> **** Detailed Description **** GEN-RPP-04 Step 4.1.4 requires the completion of form 26796 prior to bringing tools and/or equipment into the RCA that will later be released from the RCA. This process is designed to allow RP and the work group come to an understanding of the process that will be followed to ensure the tools remain uncontaminated during the work, allows for identification of naturally occurring radioactive material and spurs assessment and discussion of the methods to be used to release the tools after use. When Siemens tools were brought into the plant for R24, this process was not followed. Consequentially there has been much debate about whether certain items can be released, what survey requirements will be, and no agreement was in place to control the tools in such a way that the toolâ€™s use in the RCA could be readily understood during the release process. In future outages the standard â€œclean tool processâ€ needs to be followed to facilitate success in the control and release of vendorâ€™s tools.
395144 | CR | 20190608 | CAQ | D | Both sets of CRD stabilizing valves have low flow | Y | N |  | N | YES | <D> **** Detailed Description **** While performing PPM 9.3.8 step 7.1.5 with the â€˜Aâ€™ stab valves in service, flow rate was 5.6gpm with a drive header D/P of 265 psid and a cooling header flow rate of 40gpm. These parameters were checked earlier in the shift with the same 5.6 gpm â€˜Aâ€™ stab flow and charging header D/P of 260 psid and cooling header flow of 70 gpm. The â€˜Bâ€™ stab valves were then placed in service and the stab flow rate was 5.65 gpm with drive header D/P of 260 psid and cooling header flow of 58gpm. <I> **** Actions Taken **** Both stab valves require adjustment to meet the required 5.8 to 6.2 gpm flow rate. An evaluation needs to be performed to determine if the low flow rate will satisfy the PPM 9.3.8 requirements to perform control rod stroke time measurement and adjustment. | 02-00-CRD-V-7A,02-00-CRD-V-7B
395145 | CR | 20190608 |  | 4 | COND-HX-9 PMT AH7 Manway Leak Identified | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02108276 TT (M) COND-HX-9 PMT Manway Leak Check. COND-MANWAY-AH7 was leaking. Ref: 08-00, 3, 2. | 02-00-COND-MANWAY-AH7
395146 | CR | 20190608 | CAQ | D | FP-P-1 small oil leak | N | Y |  | N | YES | <D> **** Detailed Description **** FP-P-1 has a small oil leak on connection to supply turbo. Leakage is very slow and manageable. Photo attached. FP-P-1 oil level is within its normal band. May just require tightening or a new piece of hose. <I> **** Actions Taken **** N/A | 02-00-FP-P-1
395147 | CR | 20190608 |  | 4 | CW HVAC B Panel Annunicator Horn Failed | N | N |  | N | YES | <D> **** Detailed Description **** The horn for the Circulating Water HVAC B alarm panel has failed. Alarm lights function as expected. <I> **** Actions Taken **** Retested with same results. | 02-00-POA-ANN-PNL/CWHVB
395149 | CR | 20190608 |  | 4 | SS-PI-4B1 requires replacement | N | N |  | N | YES | <D> **** Detailed Description **** While installing siphon on SS-PI-4B1 PER EC 17408, SS-PI -4B1 was found reading approximately 25 psig with no system pressure. Gauge requires replacement. <I> **** Actions Taken **** Contacted supervisor, wrote CR <N> **** Equipment Description **** TG 501 East | 02-00-SS-PI-4B1
395150 | CR | 20190608 |  | 4 | Insta Hot Water spout in GSB 441' Kitchen needs repaired |  |  |  | N | NO | <D> **** Detailed Description **** The insta Hot water spout does not turn off properly. Various times when the handle is turned to the off position the water does not stop flowing. The handle has to be readjusted multiple times to get it to stop flowing or tap on the top of it to get it to stop. <I> **** Actions Taken **** Not placed on handle Initiated this CR Notified Supervisor <N> **** Equipment Description **** GSB 441 Kitchen Insta Hot Spout
395151 | CR | 20190609 |  | 4 | CAS-C-1A High oil level. | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1A is not currently operating. Per our logs, the compressor oil level when in standby is specified to be between 1/8 and 1/2 of the sightglass. Oil level is currently at 3/4 of the sightglass. Please investigate as to whether this level is acceptable, and if it is not, reduce oil level. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 441 E | 02-00-CAS-C-1A
395152 | CR | 20190609 |  | 4 | TO-LOC-1 D/P has gone from 6.5 to 11 PSID in one shift | N | N |  | N | YES | <D> **** Detailed Description **** TO-LOC-1 D/P has risen from 6.5 PSID on dayshift to 11 PSID on nightshift. This may indicate the filter bags are getting clogged, and should be investigated prior to plant startup. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** Bowser room, TB 441 E | 02-00-TO-LOC-1
395153 | CR | 20190609 |  | 4 | DEH-EHC-1 Remains OFF with Temperature of 67 F | N | N |  | N | YES | <D> **** Detailed Description **** DEH-EHC-1 is controlled by DEH-TS-2 and DEH-RLY-6 (CVI-DWG 609-00,4). Following completion of maintenance DEH-EHC-1 remains OFF with an indicated tank temperature of 67 F. Minimum temperature to start a DEH pump per SOP-DEH-START is 70 F. <I> **** Actions Taken **** Checked and cycled the 208 VAC power to DEH-EHC-1 (EWD -46E-358) . Checked heater ON and OFF bulbs. | 02-00-DEH-EHC-1,02-00-DEH-TS-2
395154 | CR | 20190609 |  | 4 | WCH-CR-51A has "Oil Analysis Recommended" alarm | N | N |  | N | YES | <D> **** Detailed Description **** WCH-CR-51A has an "Oil Analysis Recommended" alarm in. Please investigate. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 507 | 02-00-WCH-CR-51A
395155 | CR | 20190609 | CAQ | D | CVB-V-1NP needs P16 position switch replaced | Y | N |  | N | YES | <D> **** Detailed Description **** During the PMT on 02111599 and 02109826 the P16 "front disc closed" blue light inthe control room did not light. After investigation the switch was found hard to depress and needs replaced per ppm 10.25.85. This is the lower switch on CVB-AO-1N2 actuator. The valve and actuator functions correctly with all other indications SAT. <I> **** Actions Taken **** notified control room since we were on the phone with them and supervisor. <N> Per email discussion with Ryan Perrault, the Air-to-Close light (Blue) did not light on H13-P813 due to CVB-POS -V/1NP/P16. Email attached to EDMS. | 02-00-CVB-AO-1N2,02-00-CVB-V-1NP
395156 | CR | 20190609 | CAQ | D | RPV Insulation Package RCIC injection bulkhead flange | Y | N |  | N | NO | <C> CR at INPROG. Approved CR, moved to SRO for OPS Review. <D> While inspecting the RCIC flange it was noted that the surface of the flange has signs of erosion on the inside of the sealing surface of the flange. <I> enerated CR and uploaded pictures to EDMS for documentation. QC accepted flange cleanliness for installation of the RCIC injection line. Work Order 02111957-01. Step 6.10.20 <N> Identified during QC inspection of flange for damage, & cleanliness. Inspector stated appx. 1/8 " depth with indications all the way around. . The erosion ring was first identified in R21 (See AR-CR 00395156) along with other pitting on the flange sealing surface. The flange was skim cut at that time to improve the sealing surface. An examination of the the current photos of the flange surface shows that there is still adequate gasket sealing surface, and no action is required at this time. Greg Silvan 6/9/19
395157 | CR | 20190609 | CAQ | D | RPV Insulation Package RCIC injection bulkhead flange | Y | N |  | N | NO | <D> **** Detailed Description **** While inspecting the RCIC flange it was noted that the surface of the flange has signs of erosion on the inside of the sealing surface of the flange. <I> **** Actions Taken **** Generated CR and uploaded pictures to EDMS for documentation. QC accepted flange cleanliness for installation of the RCIC injection line. Work Order 02111957-01. Step 6.10.20 <N> Identified by QC during his inspection of flange cleanliness and damage. Inspector stated appx. depth of 1/8" with indications all aound. . The erosion ring was first identified in R21 (See AR-CR 00395156) along with other pitting on the flange sealing surface. The flange was skim cut at that time to improve the sealing surface. An examination of the current photos of the flange surface shows that there is still adequate gasket sealing surface, and no action is required at this time. Greg Silvan 6/9/19
395158 | CR | 20190609 |  | 3 | R24 Lessons Learned Recommend Siemens provide Tool C-Van |  |  |  | N | NO | <D> **** Detailed Description **** Every outage free releasing the large amount of tools and equipment Siemens brings into the RCA is a very costly expense. Recommend utilizing a Clean Tool C-Van located at the Turbine Building west side roll up doors. Additionally, the enormous amount of material needing surveyed for free release puts EN at undue risk. Many times tools brought into RCA are never used, and items such as hydraulic oil are found in Siemens boxes without being properly labeled or tracked. Siemens should be responsible for this C-Van, this would include organizing, issuing, and controlling clean tools utilized inside the RCA. To ensure radiological controls are maintained, SAMâ€™s would be set up in front of C-Van to survey tools used inside the RCA back to the clean Siemens C-Van. We should set up a similar C-Van system on the TG 501â€™.
395159 | CR | 20190609 | CAQ | C | EWD-65E-012 Revision did not update HD-RLY-63X2AT relay tbl. |  |  |  | N | NO | <D> **** Detailed Description **** EWD-65E-012 Revision 8 shows contacts 113, 114 and 115,116 with a reference to EWD-65E-012. These contact pairs are still listed in the Table for HD-RLY-63X2AT. They have been changed to 221,222 and 225,226 on the current revision (8) of the EWD. <I> **** Actions Taken **** Wrote CR.
395162 | CR | 20190609 |  | 4 | repair flex conduit on RFT-B inboard speed probes box | N | N |  | N | YES | <D> **** Detailed Description **** flex conduit is broken where it connects to the rigid conduit comming from TB-SP-1B speed probe box. This on on the inboard side of RFT-B <I> **** Actions Taken **** wrapped tape around broken section to prevent FME and oil from enntering conduit <N> **** Equipment Description **** conduit coming from RFT-B inboard speed probes box
395163 | CR | 20190609 |  | 3 | MS-HX-1B incorrect Pop-a-plug referenced |  |  |  | N | YES | <D> **** Detailed Description **** Verified information from the WO in regards to pop-a-plug size was incorrect. Both CID 34102 & 34101 are too big to for tubing. Tubes were plugged with CID 30935 during R23. However, there are none in stock. Need CID 30935. <I> **** Actions Taken **** Reported issue to MM nightshift component group manager. Initiated this CR. <N> **** Equipment Description **** MS-HX-1B - -Drawings for MS-HX-1A need to be updated with correct plug dimensions to prevent future issues- - | 02-00-MS-HX-1B
395164 | CR | 20190609 |  | 3 | Design Specified Gasket Material is Difficult to Cut |  |  |  | N | NO | <D> **** Detailed Description **** Use Garlock 9900 gasket material in place of Garlock 3122 (or 3124) for Condensate Heat Exchanger internal partition plate cover gaskets. Gaskets for the partition plate covers must be fabricated from sheet gasket material to fit each partition plate cover location. Design drawings for COND -HX-1A, 1B, 1C, 2A, 2B, 2C, 3A, 3B, 3C, 4A, 4B, 4C, 5A, 5B, 6A and 6B all specify the use of Garlock 3122 (or 3124) for the internal partition plate covers. Garlock 3122 (and 3124) is a fine gasket material if cut straight using a shear. However, due to its brittle nature and stainless steel core, it is extremely difficult to cut using normal hand tools, saws or gasket cutters. In contrast, Garlock 9900 is relatively easy to cut and fabricate using normal hand tools and gasket cutters. Garlock 9900 is available in ENW inventory and is a commonly used gasket material for steam systems. Garlock 9900 is rated for 650 degrees and 1000 psig which is well beyond design specs.
395165 | CR | 20190609 |  | 3 | R24 LL Repeat Challenges on DEH-LS-7A/B/C Functional Checks |  |  |  | N | NO | <D> **** Detailed Description **** During the functional checks for DEH-LS-7A/B/C (02112338 -06), the field faced challenges resulting in the inability to perform the WO package. Coordination with Operations, Planning, and Engineering resulted in a solution that allowed testing to complete. During investigation of the issue, it was discovered that the last 2(?) times this test occurred, the test was determined to be not required and was not performed. Recommend the model WO task(s) for this evolution be evaluated for revision (to have the correct WO steps) or removed as a requirement (as it was not performed at least two times prior). <I> **** Actions Taken **** Generated CR.
395166 | CR | 20190609 |  | 3 | R24 LL - PM WO needs updated/Eng Input for future CATID/use |  |  |  | N | NO | <D> **** Detailed Description **** Model WO 02018109 - PMID 16146-01 should be updated to have the required nitrogen reserved/staged for the work. WO 02111636 performs the Accumulator Recharge of the DEH system with the unit shutdown in preps for system start. This WO task states to work with Ops and perform per SOP-DEH-OPS and SOP-DEH-START, following discussion with Operations SOP-DEH-START was the procedure to use. Also, there was no nitrogen ordered/reserved to use for charging the accumulators. Upon review, it was identified that CATID 19306 (Ultra high purity nitrogen, only the small 40 cu ft bottle) had been used previously. It was identified the equivalent larger size cylinder CATID 92001154 was the only ultra high purity nitrogen available, however there was no QL2 onsite. The proper Q level was eventually used, however for future outages it is recommended to order and have at least 4 of the large bottles (CATID 920001154). Recommend Engineering review this CATID as well and ensure this is the proper nitrogen to use. There is another similar NItrogen bottle CATID 92000573 (QL2), however I have not seen that it has been used in the past. <I> **** Actions Taken **** Generated CR.
395167 | CR | 20190609 | CAQ | C | Radioactive Material Left Unattended Outside Posted RCA | N | N |  | N | NO | <D> Contrary to GEN-RPP-04 step 4.5.1a. (2) tool bags were removed from the RCA without required RP survey or evaluation. Contrary to 11.2.15.7 Release of Material From Radiologically Controlled areas step 6.1, (2) tool bags were taken out of the RCA and subsequently the Protected Area without required HP surveys being conducted. Contrary to 11.2.7.1 Area Posting step 3.10.3, radioactive material in an amount less than 10 times the Appendix C values was left in an area that was not posted as a Radioactive Material Area without RP supervision approval. At 0606 the HP alternate access point received a phone call from a boilermaker at the Protected Area egress. The individual stated that they were alarming the GEM and that they had bags of tools from the condenser bay clean area. They stated the material was escorted from the clean area to outside the RCA. The HP technician told the individual to hold at the egress and someone would be there to help in a couple minutes. When the HP technician arrived they found the two tool bags on a chair near the portal monitors with no one in the area. The technician brought the bags back into the RCA and performed surveys on them. The bags contained: (1) purple painted drill, (1) staged for use sign, (2) flashlights, (1) adjustable wrench, (1) FME lanyard, (2) paint markers, assorted lengths of clear tubes with red caps. Surveys of the material resulted in (1) bag high alarming the SAM, (1) bag regular alarming the SAM, and the purple painted drill high alarming the SAM The following items cleared the SAM: (2) flashlights, plastic tubes, (2) paint markers, FME lanyard, staged for use sign See EDMS for pictures <I> Initiated CR. Returned material to RCA for proper control. <N> Williams Plant Services. CR at INPROG. Approved CR, moved to SRO for OPS Review. Event was reported in June 2019 CDE as a Rad Material Control (Outside RCA Inside PA) event.
395169 | CR | 20190609 |  | 4 | RFW-P-1A Min Flow Open | N | N |  | N | YES | <D> **** Detailed Description **** RFW-FCV-2A indicates full open despite its controller RFW -FIC-2A being in Manual and dialed to close the valve. RFW-FCV-2A fails Open on loss of CAS and the air lineup to the valve and controller has been checked. This issue needs to be corrected prior to placing the RFW pump in service to feed the Rx. | 02-00-RFW-FCV-2A
395170 | CR | 20190609 |  | 3 | PPI PPM 10.2.9 needs revision |  |  |  | N | NO | <D> **** Detailed Description **** Vacuum Pull or Other NDE methods is required to verify plug weld integrity as per National Board Inspection Code (NBIC). However, mechanical plugs (POP-A-Plugs) are not subject to this NBIC rule. This is stated in steps 4.6 and 4.7 of PPI PPM 10.2.9. On the other hand, Step 7.6.1.f requests a repeat of vacuum pull after installing the mechanical plug. This CR is to revise the procedure to either remove part (f) under step 7.6.1 or to add â€œas directed by Code Programs Engineer or System Engineerâ€ to part (f)
395172 | CR | 20190609 |  | 4 | E-TR-6/62 pressure reading is less than 0 | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-6/62 pressure indicates -0.4 psig. The low specification is 0. | 02-00-E-TR-6/62
395173 | CR | 20190609 |  | 3 | Several of the Equipment loads in Table 3.6-6 are incorrect. | N | N |  | N | NO | <D> **** Detailed Description **** Break 120-8 lists 1400 lbs for pump in the RCIC pumproom. CVI 02E51-06,8 states 5275 lbs for the RCIC pump and 1300 lbs for the base. Break 126-3, 5 lists 1500 lbs for pump in the RWCU Div. 2 pumproom. CVI 546-00,1,1 states 1200 lbs for pump, 3255 for motor and 350 for heat exchanger, for a total unit weight of 4805 lb. Five of the loads use a superscript k, meaning kips, which is redundant to the Kips in the header and can be removed. Example: 37k for RWCU-100a, 720 is 37000 lbs per 16-00,24. The incorrect information has been in the table since before initial startup. The requirement for analysis is to use the source material, not material in the FSAR, so this constitutes a legacy issue, not an operability issue. <I> **** Actions Taken **** Located correct information. Wrote CR
395175 | CR | 20190609 |  | 4 | Suppression Pool Closeout Inspection - Material | N | N |  | N | YES | <D> **** Detailed Description **** This is to document material retrieved from the suppression pool during the closeout inspection dive. All material has been removed, no foreign material remains. Closeout inspection results are satisfactory. Refer to pictures posted to EDMS. No further action required. <I> **** Actions Taken **** Notified EOC. Notified OCC. | 02-00-C-TK-1
395176 | CR | 20190609 | CAQ | D | DEH leak from MS-V-160D | N | Y |  | N | YES | <D> **** Detailed Description **** Inspections of DEH piping during SOP-DEH-START revealed a 60 drop per minute DEH leak from MS-V-160D (BV1) onto the actuator. <I> **** Actions Taken **** WR written. <N> **** Equipment Description **** Heater bay TB 471 | 02-00-MS-V-160D
395177 | CR | 20190609 | CAQ | D | EDR-TK-4A released to CST with out of spec TOC |  |  |  | N | NO | <D> **** Detailed Description **** EDR-TK-4A was sampled on 6/8/19 at 1445. The TOC was 416 ppb which is above the limit of 200 ppb per SWP-CHE-02. All other chemistry parameters were within limits. This batch was released to the CST and authorized by the shift manager due to the large volume of water coming into radwaste. Documentaion with a CR is required for this activity per CI-9.2 step 5.4. Recommend Category D-Trend.
395178 | CR | 20190609 |  | 4 | BS-LS-39A unable to get the switch to change state. | N | N |  | N | YES | <D> **** Detailed Description **** BS-LS-39A unable to get the switch to change state. found evidence of water damage to switches. <I> **** Actions Taken **** generate work request to replace switches. <N> **** Equipment Description **** BS-LS-39A
395179 | CR | 20190609 |  | 4 | Disconnect SO-42-S21B/2B will not close in |  |  |  | N | YES | <D> **** Detailed Description **** During the performance of SOP-SO-START the disconnect for SO-P-ASBU (SO-42-S21B/2B) would not close in. Electrician assistance is needed to repair the disconnect. This disconnect was replaced during R24 per WO 02072932 <I> **** Actions Taken **** Informed FIN team . Informed OCC | 02-00-SO-42-S21B2B
395180 | CR | 20190609 |  | 3 | PPM 15.2.16 errors | N | N |  | N | YES | <D> **** Detailed Description **** During performance of 15.2.16 for WO# 02113438-01, multiple errors and discrepancies were encountered. All discrepancies are documented in PPM 15.2.16 comments section, page 1. <I> **** Actions Taken **** This procedure needs to be revised to correct issues | 02-00-FP-THD-53B/3
395181 | CR | 20190609 |  | 3 | TMU-SR-1 Counter OMM | N | N |  | N | YES | <D> **** Detailed Description **** Omron H7CX counter manual needs to be added to the document panel <I> **** Actions Taken **** cr | 02-00-TMU-SR-1
395182 | CR | 20190609 |  | 4 | DSA-DY-1A Housekeeping Concern | N | N |  | N | NO | <D> **** Detailed Description **** During the restart evaluation walkdown for the diesel generators, it was noted there is debris surrounding the newly installed DSA-DY-1A unit in the DG1 room (inside the main entrance door to the right). This debris should be removed. See EDMS for photos. <I> **** Actions Taken **** Notified supervisor. Instructed to generate CR and a work request. Uploaded pictures to EDMS <N> **** Equipment Description **** DSA-DY-1A, inside DG1 room in front of the DSA tanks Next to electrical MCC 7A-A, can be seen on M587
395183 | CR | 20190609 |  | 3 | R24 LL: Draining RPV Cavity Bellows Overwhealms Drains | N | N |  | N | NO | <D> **** Detailed Description **** On 6/7/19 at approximately 1600, reactor was in mode 5 with reactor cavity drain in progress using SOP-CAVITY-DRAIN. RPV level was ~235â€ with a target of 220â€ which is just above the reactor flange. Reactor Maintenance requested ops drain the cavity outer bellows per step 5.1.11 kk. Operators in the field opened FPC-V-104 per procedure to initiate the drain to EDR and ultimately sump R-5. Shortly thereafter, the main control room received EDR Sump R-5 Hi-Hi Level alarm and began to receive reports from the field of water on the floor of the RB 501 and 471. The cause of this event appears to be over-whelming the drain from the outer cavity bellows to sump R-5, resulting in the backup of EDR drains on the RB 501 and 471. This is likely due to a clog. The clog may have suddenly cleared, leading to the rapid Hi-Hi Level alarm on EDR sump R-5. <I> **** Actions Taken **** he takeaway from this event is when draining the cavity bellows, care should be taken to slowly open FPC-V-104 while observing system response prior to full-opening the valve. Field operators should remain in close communication with the control room to be prepared to shut FPC-V-104 once the R-5 sump pump starts to pump water out. A procedure change will be requested as an actionable item from this lessons learned.
395184 | CR | 20190609 |  | 4 | RRC-CB-ASD/2B/1 need pressure to right side to engage latch | N | N |  | N | YES | <D> **** Detailed Description **** When installing the replacement breaker per WO# 02088280-01 the right side latch was approximately 1/4" away from the correct position to get engagement. The left latch was already in the correct position. With Engineering approval pressure was applied to the lower right side of the breaker until the latch engaged. The breaker was successfully racked in and out with good line and load side contact. <I> **** Actions Taken **** Engineering | 02-00-RRC-CB-ASD/2B/1
395185 | CR | 20190609 |  | 4 | evidence of packing leakage on MS-V-70D |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** it appears that there is a valve packing leak with no adjustment left. Inspection is per 10.25.4 and WO#02117213-01 <I> **** Actions Taken **** Write CR and notified Engineer <N> **** Equipment Description **** MS-V-70D
395186 | CR | 20190609 | CAQ | D | Two RW Tanks Exceed TOC Limit |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Two radwaste tanks, 4A and 9, exceeded the CST transfer limit of 200 ppb TOC at 263 ppb and 290 ppb respectively. CST is currently at 133 ppb TOC and these tanks should not challenge the CST limit <I> **** Actions Taken **** Informed SM, Chemistry Specialist, OCC.
395187 | CR | 20190609 |  | 4 | Drywell closure walkdown issues identified |  |  |  | N | NO | <D> **** Detailed Description **** During Pre-closure FME walkdowns with NRC Resident Inspector it was identified that electrical junction boxes along the railings next to MSRVs had missing fasteners and the covers were not secured. <I> **** Actions Taken **** Initiated this CR, informed management, started work request to fix prior to final drywell closure. <N> **** Equipment Description **** Electrical junction boxes along MSRV railing both side, A-B and C-D
395188 | CR | 20190609 | CAQ | D | Discrepancy found on the MSRs HP tube size |  |  |  | N | YES | <D> **** Detailed Description **** The ASME code data report and Westinghouse OMM of the MSRs indicate that the high pressure tubes sizes are 0.75â€ OD with 0.042â€ wall thickness this results in 0.666â€ ID size. However, while trying to plug one of the MS-HX-1B HP tubes, neither 0.66â€ nor 0.64â€ size plug could fit inside the tube (too big). Actual measurement were taken and the ID size measured was ~0.62â€. <I> **** Actions Taken **** Informed EOC and generated work request to document the actual tubes ID sizes of HP and LP bundles | 02-00-MS-HX-1A
395189 | CR | 20190609 | CAQ | D | Tubing clamps fell off on DEH tubing at MS-V-164B | N | Y |  | N | YES | <D> **** Detailed Description **** While doing a walkdown near MS-V-164B (MS-DT-1B Interceptor valve) it was discovered that the tubing clamps and unistrut channel on the 3 DEH tubing lines below the valve have come undone. The EDMS button for this AR CR shows the as found condition of the unistrut channel and clamps and also contains a photo of the same tubing clamps taken during a walkdown during the Forced Outage in 2018, which shows the tubing connected to the unistrut channel <I> **** Actions Taken **** Discussed this with Edward Schumaker - system engineer A work request to reattach the tubing clamps is being generated per this CR. <N> **** Equipment Description **** TG 501 above the main turbine | 02-00-MS-V-164B
395190 | CR | 20190609 | CAQ | D | MS-V-22B closed stroke time unsat | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02115578-19 and marked completion required box, then taken back to complete <D> **** Detailed Description **** Closing stroke time of MS-V-22B closed stroke time was measured at 2.409 seconds by TDAS during OSP-MS/IST-Q701 step 7.7.4. Specification is is 2.66 to 4.00 seconds. Time measured by stopwatch was recorded even faster at 2.21 seconds. Closing speed should be adjusted. <I> **** Actions Taken **** Notified SM. | 02-00-MS-V-22B
395191 | CR | 20190609 | CAQ | D | MS-V-28A closing stroke time unsat | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02115578-19 and marked completion required box, then taken back to complete <D> **** Detailed Description **** Closing stroke time of MS-V-22A was measured at 2.57 seconds by TDAS during OSP-MS/IST-Q701 step 7.6.4. SPecification is 2.66 to 4.00 seconds. Measured time by stopwatch was 2.45 seconds. MS-V-28A stroke time will need to be adjusted. <I> **** Actions Taken **** Notified SM. | 02-00-MS-V-28A
395192 | CR | 20190609 | CAQ | D | DEH leak on MS-V-160A | Y | Y |  | N | YES | <D> **** Detailed Description **** At 2000# DEH pressure (during DEH startup) a leak was identified on MS-V-160A on the 1.5 inch return line. <I> **** Actions Taken **** Initiated CR/WR. | 02-00-MS-V-160A
395193 | CR | 20190609 |  | 4 | RRC-IMD-ASD1A/1 |  |  |  | N | YES | <D> **** Detailed Description **** While performing W/O# 02134249-01, several GTO's were found to be shorted out due to their resistance value. The GTO's that need to be placed are as follows; LGM1C,1D,4A,4D,6B ,6C,6D,5C,2A,2B and 2D. Verified through step 4.22.2 <I> **** Actions Taken **** Notified supervisor, engineering and the OCC. intiated CR <N> **** Equipment Description **** ASD Building ( RRC-IMD-ASD1A/1 )
395194 | CR | 20190609 |  | 3 | TO-P-EOP was smoking and caused a ground on B2-1 |  |  |  | N | YES | <C> CR re-assigned as Severity 3 to MNTSSC at the request of Maintenance. <D> **** Detailed Description **** TO-P-EOP was started per SOP-MT-AOP/TEST, approximately 30 seconds after TO-P-EOP was started a B2-1 ground alarm came in. Local field operator reported TO-P-EOP was smoking. Placed TO-RMS-P/EOP to PTL to secure TO-P-EOP and opened the associated disconnect. <I> **** Actions Taken **** Informed CRS and secured TO-P-EOP. <N> WORK REQUEST 29149487 IS COMPLETE AND UPLOADED TO EDMS. Willaims Plant Services. | 02-00-TO-P-EOP
395195 | CR | 20190609 |  | 4 | PWC-TBIT-2 high turbidity alarm not actuating. | N | Y |  | N | YES | <C> MRT Change request: CR 395195 Severity moved from CAQ D/Trend Repair to Severity 4 NON-CAQ. <D> **** Detailed Description **** PWC-TBIT-2 high turbidity alarm is not actuating at 0.2 NTU's like it should. When starting the flocculator, neither ALARM 1 or 2 lit during the expected turbidity spikes as high as 0.5 NTU's. At this level, the signal to the flocculator should trip the flocculator if PWC-RMS-SS3 (high turbidity shutdown) is in ON. When placing PWC-RMS -SS3 to ON with tubidity at ~0.4 NTU's and the water being dumped, it was verified that no actions occured and the flocculator did not trip as required. Previous history on the Yokogowa shows that this function has been working properly and no high turbidity water was sent to the potable water storage tank. <I> **** Actions Taken **** Verified high turbidity signal was not being generated. | 02-00-PWC-TBIT-2
395196 | CR | 20190610 | CAQ | D | DSA-V-15A or DSA-V-16A possible leak by. | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of OSP-ELEC-M701 attachment 9.3 DSA-V -15A and DSA-V-16A Operability Check step 5 DSA-PI-9A increaced by 30 psig which is GT 10 psig change per step 8. <I> **** Actions Taken **** verified that DSA-PI-2A and DSA-PI-1A changed by less than 5 psig. They changed by 1 psig each. | 02-00-DSA-V-15A,02-00-DSA-V-16A
395197 | CR | 20190610 |  | 3 | R24 LL ALARA Planning - System Outage Window |  |  |  | N | NO | <D> **** Detailed Description **** Observed two instances where adding ALARA Tasks to System Outage Work Orders would have resulted in improved outage dose planning. The two instances were: â€¢ WO 02115589, RWCU SYSTEM OUTAGE WINDOW R24, system fill could have used an ALARA Task since the work is in the Rx 548 RWCU HX Room and Rx 522 RWCU Pump Rooms and Mezzanine. â€¢ WO 02115578, MSIV AND MS OUTAGE WINDOW R24, Task 23 needed an ALARA Task to provided dose for the Mechanics. <I> **** Actions Taken **** Informed Supervisor <N> Review list of AD System Outage Window model WOs. Identify which tasks need RWP holds added to them. Provide list to Operations Outage Planning.
395198 | CR | 20190610 | CAQ | D | EDR tanks released with TOC out of spec |  |  |  | N | YES | <D> **** Detailed Description **** EDR-TK-4A (263) and EDR-TK-4B (353 ppb) were released with out of spec TOC results. The reject tank EDR-TK-5 is full of really high TOC water. We did not want to add more to it. There were no resources available to revalve the reject tank to EDR-TK-2. <I> **** Actions Taken **** Calculation estimates for resulting CST TOC is below the limit of 200 ppb. | 02-00-EDR-TK-4A,02-00-EDR-TK-4B
395199 | CR | 20190610 | CAQ | D | rod 4219 posiion ind for 08 does not work | Y | N |  | N | YES | <D> **** Detailed Description **** 4219 position 08 does not appear - dashes and numbers on either side work fine. Stopping at 08 position is blank. will require fixing or checking S/U for need to bypass if this rod is supposed to be at 08 at any time. | 02-00-CRD-ROD-4219
395200 | CR | 20190610 |  | 4 | WO:02077111 LS missing a set screw and EPN TAG. |  |  |  | N | YES | <D> **** Detailed Description **** HD-LS-23A is missing an EPN tag for identification purposes. LS was verified correct by referencing mechanical drawings. Additionally the head of the switch is missing a head screw causing the whole LS head to rotate when attempting to remove the cover. inorder to remove the head a pipe wrench is needed for bracing, and angle pliers to remove cover. This LS needs a set screw installed <I> **** Actions Taken **** CR written to identify discrepancies and WR written to resolve issues. <N> **** Equipment Description **** 501 TB behind Moisture seperature 1A | 02-00-HD-LS-23A
395201 | CR | 20190610 |  | 4 | WO 02077111 valve handle missing retaining nut. Handle will |  |  |  | N | YES | <D> **** Detailed Description **** HD-LS-21A DRAIN valve HD-V-694 is missing the retaining nut for the handle wheel. The valve wheel will fall off if a nut is not reinstalled. <I> **** Actions Taken **** CR written and WR generated to fix issue. <N> **** Equipment Description **** 501 TB behind moisture seperate 1A | 02-00-HD-V-694
395202 | CR | 20190610 |  | 3 | HD-LCV-5B21 Seat Degraded |  |  |  | N | YES | <D> **** Detailed Description **** AOV program trending. HD-LCV-5B21 needs valve rebuild in R25. Replace all valve internals, Plug/Stem assembly. <I> **** Actions Taken **** Notified AOV program Owner. <N> **** Equipment Description **** 471 Htr. Bay. | 02-00-HD-LCV-5B21
395203 | CR | 20190610 |  | 4 | R-24 LL lack of resources at the warehouse |  |  |  | N | NO | <D> **** Detailed Description **** There have been multiple times that there are inadequate resources in the warehouse this outage and we are not able to get through on the phone for extended periods of time, or have to wait for extended periods to get parts up to building 26. In the past we have been adequately staffed around the clock for these emergent issues. <I> **** Actions Taken **** Notified my supervisor and wrote this condition report
395204 | CR | 20190610 | CAQ | D | Bypass Valve 1 Core Rod holder bent | Y | N |  | N | YES | <D> **** Detailed Description **** During BPV checks WO# 02115580-22 techs found Core Rod holder bent. Consider making a new core rod holder for replacement; current location of bent rod holder is at the WEST HP access point. <I> **** Actions Taken **** Email sent to the OCC, Nightshift and Dayshift I/C managers notified, initiated a WR and initiated a CR. Operations also has an understanding of the issue as described by the techs. | 02-00-MS-V-160D
395205 | CR | 20190610 | CAQ | C | MS-V-67A lost power while trying to open | Y | N |  | N | YES | <C> CR reopened and assigned to AR-SEEIC at the request of Engineering. <D> **** Detailed Description **** MS-V-67A lost power indication while trying to stroke open per OSP-RPV-R801 RPV leakage test. . MS-V-67A close light flickered momentarily indicating that a contact was closed when the RMS was taken to open, after about 1 second MS-V -67A lost position indication. Field operator reported that the MS-42-7BA3C electrical disconnect for MS-V-67A is closed, the overloads were reset with no return of control power. Suspect either a control power fuse or main line fuse may have been blown. This valve support RPV hydro testing. MS-V-67A appears to remain closed as indicated by GDS screen. <I> **** Actions Taken **** Dispatched EO to MC-7BA to investigate, disconnect was closed and nothing was abnormal, reset overloads with no success. Informed CRS | 02-00-MS-42-7BA3C
395206 | CR | 20190610 | CAQ | C | E-RLY-CR1AX Removed Relay Degradation | Y | N |  | N | YES | <D> **** Detailed Description **** E-RLY-CR1AX was replaced via WO 02144717. Bench testing revealed that the removed relay was degraded. This condition report is being initiated to document the condition of the relay for trending. This relay is part of the NSSSS logic for SGT-A start. The mode of failure of this relay would not have prevented the SGT-A train from performing its current license basis design functions. Essentially the relay "failed safe" and satisfied half the logic to initiate an SGT start. Manipulation of the RPS transfer switch satisfied the other half of the logic and the system auto started. Recommend assignment to component engineering to attach the failure investigation report and determine if preventive maintenance is necessary for similar relays. <I> **** Actions Taken **** Notified EOC and Checked with Component Engineering Supervisor | 02-00-E-RLY-CR1AX
395207 | CR | 20190610 |  | 3 | PCR for TSP-DG2/LOCA-B501 |  |  |  | N | NO | <D> **** Detailed Description **** check div 1 also TSP-DG1/LOCA-B501 TSP-DG2/LOCA-B501 steps 7.2.24 and 7.1.43 - event marker is initiated by the GE test switch so noting it here is redundant. Step 7.1.80 initiating the event marker here will require unplugging the GE test switch event marker jack before initiating manually then re installing the GE test switch plug when done. This event (DG to rated) is only timed by the event marker initiation and will not work in parallel to the GE switch which is already closed.
395208 | CR | 20190610 |  | 3 | Evaluate Battery Backup for PWC-TBIT-2 |  |  |  | N | YES | <D> **** Detailed Description **** PWC-TBIT-2 has a recent history of the set points changing after a power cycle (CR#395195, CR#384560, CR#385538). Recommend engineering evaluate adding a battery backup to this system to prevent this from occuring again. <I> **** Actions Taken **** Notified supervisor and wrote this CR. | 02-00-PWC-TBIT-2
395210 | CR | 20190610 |  | 4 | HD-LT-6B Need replacement |  |  |  | N | YES | <D> **** Detailed Description **** During the performance of HD-LT-6B loop calibration, 02111584-01, transmitter 6B was found out of tolerance and could not be adjusted per the IMDS. Recommend replacement. <I> **** Actions Taken **** Notified supervisor and intiated CR & WR to repair broken transmitter. <N> **** Equipment Description **** Heater bay 471'. Near/inside HCA/HRA | 02-00-HD-LT-6B
395211 | CR | 20190610 | CAQ | D | CRD-SV-120/5419 unusual | Y | N |  | N | YES | <D> **** Detailed Description **** adjustaed CRD-V-120/5419 needle valve 1 full turn closed and saw no change in rod W/D speed. Needle Valve is now 1/8 turn from closed "feel". This is unusual as compared to other valves adjusted this date. Rod speed remains too fast. 44 sec with band of 46-56 sec. | 02-00-CRD-SV-120/5419
395212 | CR | 20190610 | CAQ | D | MS-V-160D Core Rod Holder | Y | Y |  | N | YES | <D> **** Detailed Description **** During performance of SOP-DEH-START, both Core Rods for LVDT's were too far out of alignment in order to connect to the Core Rod Holder. Also, the Core Rod Holder is bent. <I> **** Actions Taken **** Notified Supervisor and EOC. | 02-00-MS-V-160D
395216 | CR | 20190610 |  | 4 | Additional work scope needed for ASD drive testing | N | N |  | N | YES | <D> **** Detailed Description **** Problem statement: Resistance checks across each chill box(es) are not included in the PMT testing for each ASD drive. These checks provide valuable information on the reliability the ASD system. WO 02142058-10 and WO 02138133-10 are the ASD PMT tasks <I> **** Actions Taken **** Contacted supervisor and notified engineering and planning <N> **** Equipment Description **** VR 441' F0/3.0 (ASD BLDG) VR 441' F0/3.0 (ASD BLDG) | 02-00-RRC-IMD-ASD1A/2,02-00-RRC-IMD-ASD1B/1
395223 | CR | 20190610 | CAQ | D | Unable to adjust Servo Bias on MS-V-160A | Y | Y |  | N | YES | <D> **** Detailed Description **** While performing att. 6.4 of SOP-DEH-START section 6.3.4 (leak check and stroking of BPV-4 using MOOG). Craft was unable to stroke valve by adjusting servo Bias screw, the MOOG may need to be replaced. <I> **** Actions Taken **** Wrote CR, contacted supervision | 02-00-DEH-V-160A
395225 | CR | 20190610 | CAQ | D | Excessive Quantity of Liquid Combustibles on RW 437â€™ | N | N |  | N | NO | <D> **** Detailed Description **** Contrary to 1.3.10C, Control of Combustibles, there is an excessive buildup of liquid combustibles on RW 437â€™ in the form of 55 gallon drums of oil. There is greater than 25 drums of oil and greater than 120 gallons of oil not located on oil collection risers. <I> Notified S. Cooper, Fire Marshall, to walk down the area and determine action to take. <N> Per discussion with S. Cooper a plan is in progress to remove excessive liquid combustibles on FRW 437'.
395226 | CR | 20190610 |  | 3 | PMT for TO-P-EOP Not Performed | N | N |  | N | YES | <D> **** Detailed Description **** Ops started TO-P-EOP prior to completion of PMT as described in WO 0207295403 being completed. <I> **** Actions Taken **** Notified supervisor. Wrote CR. WO 29149487 already exists to perform troubleshooting. <N> **** Equipment Description **** TO-P-EOP, turbine 481' C2/5.5 Reference CR 00395194 . The PMT called for in WO 02072954-03 is a start of TO-P-EOP per SOP-MT-AOP/TEST, rather than a bump start. This was the PMT test that was performed via another work order. WO 02072954-03 was cancelled to WO 02145300 which performed PMT on the rebuilt TO-P-EOP following rewind.
395227 | CR | 20190610 |  | 4 | Simulator Training losttime | N | N |  | N | NO | <D> Lost approximately 30 minutes on the first S/U JITT due to being unable to synchronize the generator. Work arounds were made to complete the following JITT sessions. SR 2797 initiated to track and repair the issue. Suggest closing to trend. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
395228 | CR | 20190610 |  | 3 | E-TR-B OPDS Loss of POT alarms | N | N |  | N | YES | <D> **** Detailed Description **** Set 1 & Set 2 Loss of POT alarms, Loss of Inst POT alarms in. <I> **** Actions Taken **** Informed MCR, initiated AR. <N> **** Equipment Description **** E TRB OPDS building
395229 | CR | 20190610 |  | 4 | E-TR-M2 Pressure Relief Trip 2 in | N | N |  | N | YES | <D> **** Detailed Description **** Main 2 Pressure Relief Trip 2 in. No visible oil leakage from relief valve & did not find a flag. <I> **** Actions Taken **** Initiated Ar, Informed MCR | 02-00-E-TR-M2
395231 | CR | 20190610 |  | 3 | Cost Error | N | N |  | N | NO | <D> **** Detailed Description **** On May 30, 2019, ESD presented preliminary cost numbers to senior management. These costs were associated with Calibration Lab outside work and were a benefit to Columbia. Approval was granted to transfer the costs from the Calibration Lab to Columbia. ESD then audited the numbers provided for accuracy and discovered a discrepancy. The dollar amount had increased approximately $26,000, and the percentage increase was over 40%. This error revealed a lack of predictability, lack of oversight and a lack of cost control. Enablers missed: Business Planning and Preparation Verification/Validation Supervisor Oversight Worker Practices Recommend: CAT 2 <I> **** Actions Taken **** ESD further validated the numbers with Asset Management, communicated the discrepancy to upper management, and wrote this CR. <N> After discussion with the Perfomance Improvement Department we were advised that ctegory 3 would be appropriate for this issue. All actions noted in the original CR have been addressed and completed. No further action necessary
395232 | CR | 20190610 |  | 3 | Unanticipated Dose Rate Alarm Inside Reactor Cavity | N | N |  | N | NO | <D> **** Detailed Description **** An Individual received a dose rate alarm of 501 mrem/hr with a set point of 500 mrem/hr while working in the reactor cavity removing tools, equipment and trash following flange torquing on the insulation package. It is believed the alarm occurred while the individual was moving a large trash bag full of Reactor Head skirting reading *700/150 mrem/hr into a skip pan for removal from the cavity. While working in the cavity, all personnel have their dosimetry relocated to just above the knee due to dose rate gradients coming from the cavity floor. This placed the workerâ€™s dosimetry closer to the trash bag than what would normally be encountered at chest level while carrying said item. Worker did not hear or feel his dosimetry alarm and remote monitoring via AlaraCast did not register an alarm. A histogram of the ED showed the alarm was 3 seconds long. It is possible, due to such a short duration that an alarm never occurred based on update increments in the 5-10 second range. <I> **** Actions Taken **** Contacted RP Supervision, initiated form 26441 (Electronic Dosimeter Alarm Investigation) <N> Form 26441 and Histogram have been uploaded into EDMS. No further action required.
395233 | CR | 20190610 | CAQ | D | CRD-HCU-3015 Outlet Scram valve packing leak | Y | N |  | N | YES | <D> **** Detailed Description **** Small packing leak on CRD-V-127/3015. THe leak is forming a bubble of water on the top of the gland follower, but did not appear to be dripping down on teh HCU parts below. Will likely seal up with reactor pressure. Can be retorqued to 15 in-lbs without affecting scram timing. | 02-00-CRD-V-127/3015
395234 | CR | 20190610 | CAQ | D | CRD-HCU-5039 Outlet Valve scram valve packing leak | Y | N |  | N | YES | <D> **** Detailed Description **** Small packing leak on CRD-V-127/5039. The leak is forming a bubble of water on the top of the gland follower, but did not appear to be dripping down on the HCU parts below. Will likely seal up with reactor pressure. Can be retorqued to 15 in-lbs without affecting scram timing. | 02-00-CRD-V-127/5039
395236 | CR | 20190610 |  | 4 | R24 LL: COND-HX-9 nozzles have shown a degrading trend | N | N |  | N | YES | <D> **** Detailed Description **** COND-HX-9 nozzles have shown a degrading trend during R24. EC 17826 was generated to repair the nozzle downstream of HD-V-11 and EC 17831 was generated to repair the nozzle downstream of BS-V-52B. At both of these locations there was significant erosion of the carbon steel material. An improved design for nozzles entering the condenser needs to be considered. <I> **** Actions Taken **** Discussed with EOC Design Engineering Supervisor, initiated AR EVAL 395235 | 02-00-COND-HX-9
395237 | CR | 20190610 |  | 4 | MT-HOI-40 will not travel | N | N |  | N | YES | <D> **** Detailed Description **** MT-HOI-40 will not travel, the hook will raise and lower using the pedant controller but no travel. The hoist is located on the <I> **** Actions Taken **** Turned the power off and on and checked breaker. We assisted the hoist off the stops which helps some time, but we were not successful. | 02-00-MT-HOI-40
395238 | CR | 20190610 |  |  | DLR ran through X-ray machine at PAAP |  |  |  | N | NO | <D> **** Detailed Description **** An individual from org code 52130 placed thier DLR on the conveyor belt while entering the protected area through the PAAP. <I> **** Actions Taken **** Supervisor contacted by security and individual reported to dosimetry.
395239 | CR | 20190610 |  | 4 | TO-V-128 lower handwheel does not move more than 1/4 turn | N | N |  | N | YES | <D> **** Detailed Description **** Attempted to shift LO Coolers from TO-HX-1B to TO-HX-1A per SOP-MT-OIL-OPS section 5.7.2. Guidance in procedure states that lower (lociking) handwheel should turn approx 2 -4 turns. We only got about 1/4 turn. Attempted further CCW movement with approved leverage device with no sucess. Previously in REV 12 of procedure, guidance was provided for 5 -10 turns, which has been changed per AR 366910. TO-V-128 is stuck and will not move past 1/4 turn CCW. Returned TO-V-128 to its original position. <I> **** Actions Taken **** CR & WR written. OPS Production staff notified. System Engineering discussed how this valve works with EOs in the PSRO office 6/10/19. | 02-00-TO-V-128
395240 | CR | 20190610 | CAQ | D | E-C1-7 Charger Equalize voltage is unstable. | N | N |  | N | YES | <D> **** Detailed Description **** While performing 10.25.18A, electricians began section 7.3 for testing the DSH Alarm card pickup and dropout voltage. When the float/equalize switch was moved to the equalize position, the charger DC voltage dropped from 123.5VDC to 0.00 VDC. After about 5-10 seconds we heard the charger pickup and the Voltmeter ran up to 116-130 VDC. The voltage never really stabilized while the switch was in equalize. With Supervisor, Engineering and Shift Manager Concurrence, 10.25.18A will be resumed using the FLOAT potentiometer to verify/calibrate the remaining Cards. It should be noted that 10.25.234 (section 7.3) states that the preferred method of equallizing E-C1-7 is to leave the switch in the FLOAT position. WO#02111958-01 <I> **** Actions Taken **** Notified Supervision, and Engineering for resolution. Contacted Shift Manager for Permission to annotate Continuous use procedure. <N> **** Equipment Description **** E-C1-7
395241 | CR | 20190610 |  | 4 | BS-MO-12A High Running Current during PMT | N | N |  | N | YES | <D> **** Detailed Description **** BS-MO-12A has high running current. PPM 10.25.74 requires the running current to be less than 130% of running amps (name plate) Name Plate = 2.7 amps ~ 130% = 3.51 amps Test data = 5.1 amps = 189% Attached evaluation shows this higher running amps allows for 1-1/2 strokes before it overheats/requires a cooldown period. <I> **** Actions Taken **** Review of history shows this valve has had a history of high running amps. Additionaly, the peak in-rush significantly has reduced over time showing the motor is starting to deteriate. A quick hand calc shows the motor is running at its maximum. A larger motor would eliminate this problem. | 02-00-BS-MO-12A
395242 | CR | 20190610 |  | 4 | MS-MO-115B High Running Current during PMT | N | N |  | N | YES | <D> **** Detailed Description **** MS-MO-115B has high running current. PPM 10.25.74 requires the running current to be less than 130% of running amps (name plate) Name Plate = 0.6 amps ~ 130% = amps Test data = 1.4 amps = 235% Attached evaluation shows this higher running amps allows for 2.5 strokes before it overheats/requires a cooldown period (Stroke = open/close or close/open <I> **** Actions Taken **** See attaached evaluation in EDMS Recommend replacing motor *** NOTE 16.7 cycles / strokes*** instead of what is identified in the CR cover page | 02-00-MS-MO-115B
395244 | CR | 20190610 |  | 3 | Obsolete warning on E-C1-7 charger | N | N |  | N | NO | <C> Removed name IAW with SWP-CAP-01 <D> **** Detailed Description **** Prior to performing Alarm / Trip Calibration on E-C1-7, electrician noticed a warning sticker concerning putting the charger in equalize mode. The sticker stated that the, "IN-5 DC Link voltage should be raised to 140VDC. This will assure the blocking diodes (CR1 and CR3) in E-IN-5 are properly biased...making voltage adjustments on this charger or inverter IN-5 are described in the electrical shop practice manual. " After talking to an Engineer I was told that this sticker was obsolete since there are no blocking diodes (CR1 and CR3) in the Ametek style inverter and there are no "Electrical Shop Practice Manuals" anymore. See attached picture in EDMS for more detail. <I> **** Actions Taken **** Contacted Engineer for resolution and proceeded with WO# 02111958-01. Generated CR for review. <N> **** Equipment Description **** E-C1-7
395245 | CR | 20190610 |  | 4 | TMU sample collection line fouled | N | N |  | N | YES | <D> **** Detailed Description **** The TMU sample collection line from PWC-V-748 is bio-fouled on the inside and collapsed, which results in poor purging of the sample line and potential for biologically contaminated samples collected for regulatory purposes & microbial analysis <I> **** Actions Taken **** Notified chemistry specialist <N> **** Equipment Description **** Flocculator building 33 | 02-00-PWC-V-748
395246 | CR | 20190610 | CAQ | B | CPT installed in Spectrum buckets donâ€™t not meet Spec | Y | N |  | N | YES | <C> RISK: Medium. CAUSE: Clear. Severity B - Cause and Actions created, Notes updated, No Investigation Template Required. <D> **** Detailed Description **** The intent of this CR is to document a potential part 21 and drive corrective actions for the potential nonconforming extent of condition. While investigating the failure of the GE 55-537290G002 coil for DMA-42-4A7D, report inferred that the control power transformer, CPT does not meet Columbiaâ€™s procurement specification 15209. Not meeting the procurement specification is potentially reportable under 10 CFR Part 21. Based on independent analysis and field investigations, the CPT secondary voltage appeared to be running high with a calculated turns ratio of 3.77:1 (See EDMS folder for the failure analysis report) The failure analysis report concludes that the GE 55 -537290G002 coil failure was due to overheating caused by the associated contactor control voltage being consistently outside of the coil rated voltage range. The continuously energized spectrum starters with similar coils, CPTs and exposed to similar conditions may be susceptible to premature failure. There are eight (8) EPNs that meet these criteria. These components should be considered operable but nonconforming. <I> **** Actions Taken **** Requested a failure analysis from Excelon labs Informed supervisor, manager, EOC and initiated this CR. Generated WRs to obtain CPT secondary voltages on affected EPNs <N> This is a medium risk issue because it affects multiple safety related equipment. The cause, extent of condition, and corrective actions are identified in the EQIT performed for CR 393270 as follows: Cause: High output voltage on the Control Power Transformer. Corrective actions: 1) WR 29148554 & WR 29148551, Performed investigations and replaced the starter coil 2) AR 00395246-05, Procurement Engineering to Perform Evaluation of a potential Part 21 of CPTs installed in spectrum buckets. 3) WR 29149519, FIN team to Inspect CPT primary and secondary voltage of all the eight MCC starters identified in the extent of condition. No Investigation template needed for this CR | 02-00-CRA-42-7B2B,02-00-CRA-42-8B6A,02-00-DMA-42-4A7D,02-00-RRA-42-7B2C,02-00-RRA-42-7B6F,02-00-RRA-42-7BB1E,02-00-WMA-42-7F3E,02-00-WMA-42-8F1E
395247 | CR | 20190610 |  | 4 | Hydrogen peroxide distribution line drip |  |  |  | N | YES | <D> **** Detailed Description **** There is a drip leak on an elbow of the hydrogen peroxide distribution line downstream of valve SWCF-V-501 (second elbow as line turns toward the SW pond 1B.) <I> **** Actions Taken **** Contained drip, notified chemistry specialist and supervisor. Recorded condition in accordance w/ PPM 12.14.1 <N> **** Equipment Description **** Distribution line, second elbow after SWCF-V-501 | 02-00-SWCF-TK-2
395248 | CR | 20190610 | CAQ | C | Rod XX when other rod is stroking. | Y | N |  | N | YES | <C> R reopened to add completion required check mark to referenced WO 02145391 per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** Every time Rod 26-15 gets to a position that ends in 2. For example 02,12,22,etc. Rod 30-11 indicates XX on the four rod display and the full in indication for rod 30-11 goes out. <I> **** Actions Taken **** Wrote CR Informed CRS/SM and OCC Inserted all control rods. Halted control rod stroke time testing. | 02-00-CRD-HCU-2615,02-00-CRD-HCU-3011
395249 | CR | 20190610 |  | 4 | BS-V-52B contributing to thru wall piping leak |  |  |  | N | YES | <D> **** Detailed Description **** it is highly suspected that leak observed has had contributiond from BS-v-52. This valve is a notorious leaker that had is PM changed to a 4 year inspection frequency <I> **** Actions Taken **** Wrote CR and OSCR to open, inspect and replace internals as needed. <N> **** Equipment Description **** T -478- - -B1/12.5- | 02-00-BS-V-52B
395251 | CR | 20190610 |  | 3 | (R24LL) Scope Addition Vacuum Pull Required WOs Not Flagged |  |  |  | N | NO | <D> **** Detailed Description **** Three scope addition WOs coded RA24 and having the attribute "Vacuum Pull = TES" in Asset Suite did not have the attribute flagged in the P-6 schedule. <I> **** Actions Taken **** Recommend S3 to Outage Management to change scope addition process to ensure WOs with the "Vacuum Pull = YES" attribute are flagged as such in the P-6 schedule.
395252 | CR | 20190610 |  | 4 | TMU-V-1C gearbox oil leak |  |  |  | N | YES | <D> **** Detailed Description **** There is a puddle of oil beneath the gearbox of TMU-V-1C and oil marks at the seams of the gearbox plate cover, indicating a leak past the gearbox seal. This is the same issue that was identified in 2014 under AR 306571 and the gearbox continues to leak. Oil was cleaned up and repairs were attempted under WO 02066125, but no intrusive work was performed due to a lack of documentation of the gearbox internals. If internal configuration cannot be safely determined, recommend an internal inspection/repair of the gearbox during the next TMU system outage (R25). | 02-00-TMU-V-1C
395255 | CR | 20190610 | CAQ | D | RFW-LR-608 oscillations (Upset range - TDAS X327) | N | Y |  | N | YES | <D> **** Detailed Description **** Following turnover it was noticed that at ~1740 RPV level (upset range â€“ RFW-LR-608, X327) started oscillating +/- 2 inches and has increased to +/-5 inches. While more subtle it does appear that MS-LI-605 (shutdown range level instrument) is also oscillating. There have been no significant change in reactor temperature or level when these oscillations started. These instruments were restored to normal calibration ~12-16hrs ago per PPM 10.27.26. Request IC investigate and repair as required. Current level band is 70-90â€ and current temperature band is 130-150F. <I> **** Actions Taken **** CRS/SM notified. OCC notified. | 02-00-RFW-LR-608
395256 | CR | 20190610 |  | 4 | Vehicle Trap arm needs maintenance |  |  |  | N | YES | <D> **** Detailed Description **** The barrier arm in the vehicle trap needs maintenance. The pin to the ram is backing out. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Trap closed, Security notification made, CR/WR generated <N> **** Equipment Description **** Securtiy vehicle trap
395258 | CR | 20190610 |  | 4 | GY-P-10B1 Leak at pump discharge union connection |  |  |  | N | YES | <D> **** Detailed Description **** Leak at pump discharge union connection. After tightening union fitting, leakage was approx 2 dpm. | 02-00-GY-P-10B1
395259 | CR | 20190610 |  | 4 | GY-P-11B1 Leak at pump suction union connection |  |  |  | N | YES | <D> **** Detailed Description **** Leak at pump suction union fitting. after tightening union fitting, leak rate is approx 1 dpm. | 02-00-GY-P-11B1
395260 | CR | 20190610 |  | 3 | R24LL for RCIC Overspeed Trip Testing (10.7.5) |  |  |  | N | NO | <D> **** Detailed Description **** Based on some questions that occurred during the performance of the overspeed trip testing it would be beneficial to revise the procedure 10.7.5 to better define which steps are required and which steps are not for typical/standard refueling outage overspeed trip testing. Goal would be to define 1) how much, if any, of section 7.1 is required for the standard refueling outage overspeed trip test, and 2) if the answer is some to modify the section 7.2 to incorporate those steps and then to revise the PM to only require that section as needing to be completed. . Recommendation would be for the maintenance procedure writer with the assistance of the RCIC system engineer to revise 10.7.5. <I> **** Actions Taken **** CR written and EOC notified. <N> Inspection steps have already been incorporated into the procedure. No additional changes required per Engineer.
395261 | CR | 20190610 |  | 4 | GY-CI-10A2 resistivity is low |  |  |  | N | YES | <D> **** Detailed Description **** While restoring RRC-IMD-ASD1A/2 to service it was observed that the coolant resistivity on GY-CI-10A2 was around 2.7 M ohms. Operations logs require resistivity to be greater than 5 M ohms. <I> **** Actions Taken **** Notified SSS and wrote CR | 02-00-GY-CI-10A2
395262 | CR | 20190610 |  | 3 | Procedure enhancement for OSP-CONT/IST-Q703 |  |  |  | N | NO | <D> **** Detailed Description **** Step 7.4.3 1) on page 16 says to N/A steps 2 through 12, and should say N/A steps 2 through 15 <I> **** Actions Taken **** Wrote CR. Discussed with Shift Manager
395263 | CR | 20190610 |  | 4 | SCW-TK-1 nitrogen blanket |  |  |  | N | YES | <D> **** Detailed Description **** request a smaller regulator rig installed on the N2 bottle by the SCW skid 441' west. the procedure calls for regulation at approx 2 psig, and the installed regulator is a 1000# regulator <I> **** Actions Taken **** intormed supervision initiated CR/WR | 02-00-SCW-TK-1
395264 | CR | 20190611 |  | 3 | RRC-CB-GY/P/10B1 is not in an electrical line up. |  |  |  | N | NO | <D> **** Detailed Description **** RRC-CB-GY/P/10B1 is tagged for a clearance and no restoration position is listed in an SOP. This is weak configuration control. <I> **** Actions Taken **** Wrote CR.
395265 | CR | 20190611 |  | 4 | RFW-TE-55/A1/A2 flex detached. |  |  |  | N | YES | <D> **** Detailed Description **** Flex conduit seperated from instrument. See photo in EDMS. <I> **** Actions Taken **** Generated CR. Notified I&C shop Sup. <N> **** Equipment Description **** RFW-TE-55A
395266 | CR | 20190611 | CAQ | D | Rod Position XX on Rods 26-15 and 30-11 | Y | N |  | N | YES | <D> **** Detailed Description **** During troubleshooting for CR 395248 probe MUX cards were swapped and rods 26-15 and 30-11 lost full in indication and indicate XX on the four rod display. Cards were swapped back and the XX indication and full in indication were restored. <I> **** Actions Taken **** CR to trend | 02-00-CRD-RPIS-1
395267 | CR | 20190611 |  | 4 | CW-42-6R1C disconnect for CW-V-6 wouldn't close |  |  |  | N | YES | <D> **** Detailed Description **** WHen closing CW-42-6R1C on a tag lift, the disconnect did not close. Repeated means of applying pressure to the door in certain spots did not yield it closing ever. Unit may need lubrication or other possible maintenance. <I> **** Actions Taken **** Informed SSS. | 02-00-CW-42-6R1C
395268 | CR | 20190611 |  | 4 | R24 lesson learned: Work delayed and resources wasted |  |  |  | N | NO | <D> **** Detailed Description **** While attempting to complete a job in the Steam Tunnel, it was discovered that all the valve parts and work package staged at the job site had been thrown away during clean up of the steam tunnel. This resulted in lost time and resources (12 to 15 manhrs) , the cost of a new valve, and extra dose to enter the steam tunnel extra times to complete work and look for parts. <I> **** Actions Taken **** Contacted all groups working in the steam tunnel for support, issued a new valve from stores to use parts for the existing valve. completed rebuild of valve Work package had to be reprinted and signatures caught up as the work package was also thrown away. <N> **** Equipment Description **** Steam tunnel clean up
395269 | CR | 20190611 | CAQ | D | WR: 29149525 MS-V-2A1 broke | N | Y |  | N | YES | <D> **** Detailed Description **** During investigate work under WR 29149525 section 7.2 and 7.7 were performed per 10.27.64 continues backfill. It was discovered while attempting to establish appropriate flow rates for plant conditions that metering valve MS-V-2A1 passes flow while valve is fully shut. This valve is the upstream metering valve and should be set to .48 g/hr per step 7.7.15. This step could not be completed because the valve does not adequately control flow. MS-V-2A1 needs to be replaced. <I> **** Actions Taken **** I&C supervision & operations notified of issue with the metering valve. Directed by supervision to use downstream valve to modulate flow to desired plant conditions (.36 g/hr) <N> **** Equipment Description **** E-IR-P-27 on 522 RX | 02-00-MS-V-2A1
395270 | CR | 20190611 |  | 4 | Broken Faucet in RW 487 Women's Locker Room Needs Fixed |  |  |  | N | NO | <D> **** Detailed Description **** A RMC Laborer came upon a broken faucet in the RW 487 (C346) women's locker room. Hot water was pouring out of the faucet, and the handle was completely broken off. Recommend replacing sink faucet. <I> **** Actions Taken **** RMC Laborer notified supervision and shut the water off. An out of service sign was placed on the faucet, and this CR/WR was initiated. Purell hand sanitizer (with MSDS label) was placed as a temporary solution to hand washing. <N> **** Equipment Description **** C346 women's locker room faucet on the RW 487
395271 | CR | 20190611 | CAQ | C | RCIC Overspeed Testing As-Left Trip Spring Force | Y | N |  | N | YES | <D> **** Detailed Description **** As-found / as-left for latch reset spring force for the trip hook of 7 lbs was less than the expected range of between 10-25 lbs per procedure 10.7.5 in step 7.1.10. The spring was then replaced with a new spring, and a second force gauge was used and the same force value of 7 lbs was obtained. . Based on a review of the EPRI Maintenance Guide the two relevant excerpts details the following: â€œNOTE: The corresponding required pull force for separation of the trip and throttle valveâ€™s trip hook should be less than 25 lbs (110 N)â€ and â€œVerify that the required pull force for separating the trip hook/latch-up lever is less than 25 lbs (110 N) from the full open position, and with maximum steam forces on the valveâ€. . A spring force value of 7 lbs in both cases is less than the specified 25 lbs. from the EPRI Maintenance Guide which also complies with step 7.1.10.g. This CR is being written to document the force being outside the expected range. The RCIC turbine will be overspeed tested prior to return to service to confirm the overspeed trip functions as designed. <I> **** Actions Taken **** CR written and EOC notified. <N> **** Equipment Description **** RCIC pump room | 02-00-RCIC-DT-1
395272 | CR | 20190611 |  | 3 | Dose Rate alarm received, dosimeter dropped. |  |  |  | N | NO | <D> **** Detailed Description **** An equipment Operator received a dose rate alarm when his dosimeter was dropped from an elevated permanant platform. During a clearance order activity above B condensate booster pump an equpment operator dropped his dosimeter from the platform. He heard the dosimeter alarm. He then proceeded off the platform, recovered his dosimeter, and exited the RCA with his clearance order crew mate via the main plant corridor to the RCA PAP. He then reported to HP. <I> **** Actions Taken **** This CR was documented, an ENW Electronic Dosimeter Alarm Investigation form was completed, and the individuals RCA restriction was released. The individual was asked to find a way to not drop his dosimeter again. <N> Form 26441 and histogram uploaded into EDMS. No further action required.
395276 | CR | 20190611 |  | 4 | Cavity Stairs |  |  |  | N | NO | <D> **** Detailed Description **** The Cavity stairs have treads that are bowed and have welds that are in the need of repair. Workers identified a stair tread that had a broken weld on the 5th step up. <I> **** Actions Taken **** Contacted the Carpenters to install scaffold to resolve the safety concern for the remainder of the outage. The Carpenters installed scaffold to support the 5th stair tread. The Stairs are safe to use. Recommend making repairs to the stairs prior to next outage. <N> **** Equipment Description **** Cavity Stairs
395279 | CR | 20190611 |  | 3 | R24 lesson learned (LL) - ESOMS temp lifts cause work delays | N | N |  | N | NO | <D> **** Detailed Description **** R24 LL documentation. The current procedure/practice does not allow someone to accept a temp lift unless they are already on the clearance order that the temp lift affects. This prevents the oncoming shift or other workers from signing on and performing work until the temp lift is rehung (whether administratively or actual). The ESOMS software that we are familiar with from other sites does not have this limitation. Recommend software update or program change to remove this limitation.
395281 | CR | 20190611 | CAQ | D | CRD 14-07 does not display a rod position ending in 2. | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02114218 and marked completion required box, then taken back to complete <D> **** Detailed Description **** CRD 14-07 displays blank on the four rod display for every rod position that ends in 2. For example 02, 12, 22, 32,and 42. All other rod positions display as expected. <I> **** Actions Taken **** Wrote Cr Informed CRS | 02-00-CRD-HCU-1407
395282 | CR | 20190611 |  | 4 | GY-F-10A1 small leak - 5 dpm | N | N |  | N | YES | <D> **** Detailed Description **** GY-F-10A1 has a small leak of approx 5 dpm. | 02-00-GY-F-10A1
395283 | CR | 20190611 |  | 3 | R24 lesson learned (LL) - peer verifications | N | N |  | N | NO | <D> **** Detailed Description **** R24 LL documentation. There have been numerous times when a peer verifier was required for the work task. This was covered by in-house craft. Nearly all drywell work requires a peer verifier to be available at or near the jobsite the entire time the task is working. The peer verifier only accounted for 1 hour of the total labor hours on the schedule but in reality was a full additional resource. This resulted in more dose and less shop productivity. Recommend training some temporary employees to be peer verifiers to fill that role.
395285 | CR | 20190611 |  | 4 | Kellman Blue service light on E-AY-TR/M2 | N | N |  | N | YES | <D> **** Detailed Description **** WHile walking donw the tranformer yard the blue service light was illuminate on E-AY-TR/M2. The data and communication were reviewed and it appears the Kelman is not collecting data and it needs repaired. This CR is being written to document the need for repair of the Kelman for E-TR-M2 under WO 02134478. | 02-00-E-AY-TR/M2
395287 | CR | 20190611 |  | 4 | Unable to vent from TSW auto vent (TSW-V-258) for RRA-FC-21 | N | N |  | N | YES | <D> **** Detailed Description **** Whilst lifting O-RRA-FN-21/TSW-001 EO was unable to vent from auto vent IAW with lift instructions. Suspect that this TSW piping may be clogged. EO placed a nitril glove on the vent port of the auto vent to see if any air was being set free from the system and there was no inlaflation of the glove. Investigate and correct. This may leave air in the CC unless the TSW flow can sweep it out. <I> **** Actions Taken **** Closed TSW-V-257 & wrote this AR. Informed supervision. | 02-00-TSW-V-258
395291 | CR | 20190611 |  | 3 | RRC-CB-RRA breaker replaced without proper documentation | N | N |  | N | YES | <D> **** Detailed Description **** While performing ESP-CBRRA-F101 per WO# 02113058 the currently installed breaker failed testing so a new breaker was ordered to replace it but the work order wasn't updated to reflect setting up the replacement breaker or replacing the current breaker. <I> **** Actions Taken **** Generated repair data sheet for breaker refurbishment. | 02-00-RRC-CB-RRA
395293 | CR | 20190611 |  | 3 | CSP-DO-C101 needs enhancment | N | N |  | N | NO | <D> **** Detailed Description **** Chemistry has the ability to digitally scan and send documents and is moving away from using a fax machine. Steps 7.17 and 7.18 contain notes that include the use of faxes. These notes should be re-written to remove the use of the faxes, and allow the use of digital scans so the Chemistry lab can remove its old fax machine from service. <I> **** Actions Taken **** Wrote CR
395294 | CR | 20190611 | CAQ | D | RCIC Drain License Renewal Exam Showed Corrosion Damage | Y | N |  | N | YES | <D> **** Detailed Description **** While performing WO 02114736-01 License Renewal (LR) inspection of RCIC drip leg drain piping, the as-found VT-1 exam identified that there was corrosion damage including localized crevice corrosion that was beyond minor surface corrosion (eg. staining or thin uniform layer). The craft and engineers determined that this degradation was minor and will have impact on the intended function of the pipe or fitting. The pipe was being replaced with new carbon and stainless steel under WOT 02114736-01 to restore full qualification of the pipe which had a through wall leak. Therefore, no functionality determination or other action is required. . The sockolet that attaches the 2-inch RCIC pipe to the 6 -inch has crevice corrosion on approximately 180 degrees of the sockolet seating surface. The external of the pipe and fitting had minor surface corrosion staining but no evidence of a pitting or other degradation. This pipe fitting degradation is consistent with that observed during the previous repairs for similar applications and consisted of insignificant wall loss. This inspection is required under LR Commitment No. 12, Chemistry Program Effectiveness Inspection. . No further action is required under this CR. It is recommended to trend the CR for AMP trending. <I> **** Actions Taken **** Discussed issue with Supervisor, Material Engineer and Maintenance. Wrote this CR. <N> **** Equipment Description **** Drip leg drain line located in TG 479 elevation. Replacement under 02114736 at finish. | 02-00-RCIC-V-26
395295 | CR | 20190611 |  | 3 | Cracked I Pad Screen |  |  |  | N | NO | <D> **** Detailed Description **** Electrical Maintenance shop needs a new ipad. The screen was cracked during R24 work. Touch capability has been altered. <I> **** Actions Taken **** report to supervision <N> **** Equipment Description **** building 17 electrical shop . Aaron Riggs has temporarily replaces the tablet with a spare. Once a charge code number has been given, Aaron will order a new tablet to replace the broken tablet.
395296 | CR | 20190611 |  | 4 | E-BU-R441/1 failed testing following SM8 outage | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-R441/1 failed testing following SM8 outage <I> **** Actions Taken **** Initiated work request <N> Non-essential lighting. FSIP issued and posted per PPM 1.3.10B. | 02-00-E-BU-R441/1
395297 | CR | 20190611 |  | 4 | E-BU-SWA3/3 failed testing following SM8 Outage | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-SWA3/3 failed testing following SM8 Outage <I> **** Actions Taken **** Initiated Work request Created FSIP# 19-0126 <N> Non-essential lighting. Impairment written and posted per PPM 1.3.10B. | 02-00-E-BU-SWA3/3
395298 | CR | 20190611 | CAQ | D | Door T-104 not meet criteria 15.3.17 | N | N |  | N | YES | <D> **** Detailed Description **** Performing 15.3.17 found Door-t-104 gap to not meet criteria per PPM , Gap larger than 1/4" top left side , to aprox 9 ". Also appears door has been bent. Door was held open for the outage to route a 2 1/2 potable water pipe for condensor work. Door is aprox 1/2' from touching the door stop at the top , the bottom half touches the stop as should. Door still works and closes, just has a larger gap. <N> BIP 19-0273. Non-essential fire barrier. | 02-00-T-DOOR-T104
395300 | CR | 20190611 |  | 4 | E-BU-T471/4 failed testing following SM8 outage. | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-T471/4 failed testing following SM8 outage. <I> **** Actions Taken **** Initiated Work Request. . Initiated FSIP# 19-1025 <N> Non-essential lighting. FPSI 19-0125. | 02-00-E-BU-T471/4
395302 | CR | 20190611 |  | 4 | E-BU-T471/3 failed testing following SM8 outage. | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-T471/3 failed testing following SM8 outage. <I> **** Actions Taken **** Initiated Work Request . Initiated FSIP# 19-0124 <N> Non-essential lighting. | 02-00-E-BU-T471/3
395303 | CR | 20190611 |  | 4 | E-BU-T471/2 failed testing following SM8 outage. | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-T471/2 failed testing following SM8 outage. <I> **** Actions Taken **** Initiated Work Request . Initiated FSIP# 19-0123 <N> Non-essential lighting. | 02-00-E-BU-T471/2
395304 | CR | 20190611 |  | 3 | R24LL: RHR-C use during OSP-RPV-R801, Document Thermal Cycle | N | N |  | N | NO | <D> **** Detailed Description **** During the RPV hydro per OSP-RPV-R801, RHR-C was used to fill the RPV. Per step 9.2.13c, this CR is being generated. This has been previously evaluated: During the RPV leakage test, Operations may use RHR-P-2C if the condensate system is not available to fill the RPV. This condition was evaluated in AR/CR 199385. The Engineering evaluation (AR/AS 199385-01) revealed that the usage factor for this thermal cycle was insignificant and inconsequential; i.e., 1x10-6 << 1.0 ASME Code requirement. For tracking purposes, these thermal cycles are documented in: 1) AR/CR 199385 (06/12/2009) 2) AR/CR 248160 (09/08/2012) 3) AR/CR 287779 (06/15/2013) 4) AR/CR 331635 (06/20/2015) 5) AR/EVAL 357017 (in progress) AR/EVAL 357017 will be resolved as part of License Renewal /Transient Cycles project. The RPV RHR-C Nozzle calculation which is a subset of RPV Design Report (AED CAL 72-2647 Rev.0) will account for this condition at RHR-LPCI Nozzle-C. After approval and issuance of AED CAL 72-2647 RPV Design Report, the PPI PPM OSP-RPV-R801 Reactor Pressure Vessel Leakage Test procedure will be updated to remove the Note and Step â€œa. OBTAIN Engineering concurrenceâ€, from the procedure. <I> **** Actions Taken **** Trend only. OPS informed.
395305 | CR | 20190611 |  | 4 | COND-HX-9 intermediate drains contained water / muddy silt | N | N |  | N | YES | <D> **** Detailed Description **** While installing screens over drains in intermediate water boxes, ND&E Inspected drains , permission had been given to close hatches, from engineer , found black silty water in drains appears the drains let water out due to A ,and C bays were completely dry, B bay had aprox 1 " of water <I> **** Actions Taken **** Contaceted supervisor | 02-00-COND-HX-9
395306 | CR | 20190611 |  | 4 | TO-M-EOP Lug connection found broken (F1, AF1) | N | N |  | N | YES | <D> **** Detailed Description **** While determing TO-M-EOP found the bolted splice connection of F1 and AF1 broken. Do not know if this was broken before the determ or if it was weak and broke while removing the tape from the splice. <I> **** Actions Taken **** Connections will be repaired during the re-term. | 02-00-TO-M-EOP
395307 | CR | 20190611 |  | 4 | CND-V-1C does not display proper flow. | N | N |  | N | YES | <D> **** Detailed Description **** During performance of COP-CW-FILL, Step 5.2.34 CND-V-1C had no water flow through the fire hose. When disconnected and the valve was reopened to a bucket the valve would allow approximately 60 drops a minute. | 02-00-CND-V-1C
395308 | CR | 20190611 |  |  | CR not required recommend deletion. |  |  |  | N | NO | <D> **** Detailed Description **** CR not required recommend deletion.
395309 | CR | 20190611 |  | 4 | E-BU-T441/3 failed testing following SM8 outage. | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-T441/3 failed testing following SM8 outage. <I> **** Actions Taken **** Initiated work request . Initiated FSIP# 19-0120 <N> Non-essential lighting. | 02-00-E-BU-T441/3
395310 | CR | 20190611 |  | 4 | E-BU-R548/4 failed testing following SM8 outage | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-R548/4 failed testing following SM8 outage <I> **** Actions Taken **** Initiated Work Request . Initiated FSIP# 19-0121 <N> Non-essential lighting. | 02-00-E-BU-T441/3
395311 | CR | 20190611 | CAQ | D | MS-FR-613 erratic | Y | Y |  | N | YES | <D> **** Detailed Description **** After starting RRC-P-1A, MS-FR-613 Total core flow began acting erratically. See point B018 on eDNA. <I> **** Actions Taken **** WR written. <N> **** Equipment Description **** MCR | 02-00-MS-FR-613
395312 | CR | 20190611 |  | 3 | R24LL 10.25.13 combersome to get through during outage | N | N |  | N | NO | <D> **** Detailed Description **** 10.25.13 for performing detailed test and inspects on the DHP style breakers is very combersome to get through during outage. When a clearance is posted on the cubicle or it is protected it doesn't allow the craft to complete the steps that require placing the breaker in the cubicle, so that task has to remain open until the clearance is lifted. Ops when lifting the clearance typically racks in the removed breakers, this caused several breakers to have to be racked back out so the remaining sections of 10.25.13 could be performed. I suggest breaking the sections of the procedure that cannot not be completed when there is a clearance in seperate tasks so that it can be scheduled accurately.
395315 | CR | 20190611 |  | 4 | Plug, boss, packing needs to be replaced on MS-BVS-DT/1C/1 | N | N |  | Y | YES | <D> **** Detailed Description **** Plug, boss and packing needs to be replaced on MS-BVS -DT/1C/1 <I> **** Actions Taken **** Orderer parts for replacement repair 0000026451, 0000026452, 0000026453./ need WR to fix. Contacted supervisor. Wrote cr. parts ordered on MR#281748 | 02-00-MS-BVS-DT/1C/1
395316 | CR | 20190611 |  | 3 | R24 LL Performance of SOP-GEN-AIRTEST | N | N |  | N | NO | <D> **** Detailed Description **** While attempting to get an update on progress of SOP-GEN -AIRTEST, a lack of certainty about who was performing what sections of the procedure became apparent. The turbine project team expected OPS was performing the SOP and OPS seemed to believe that Engineering and Siemens were performing particular inspections. Insufficient turnovers by the turbine team, engineering and OPS individually resulted in hours lost as each believed the other had the lead. A contributor is that the system engineer that typically leads this inspection effort has left site on a work related trip. <I> **** Actions Taken **** Documenting this condition as a lesson learned to prevent future reoccurrence.
395317 | CR | 20190611 |  | 4 | COND-V-120B- loose operator mounting fasteners |  |  |  | N | YES | <D> **** Detailed Description **** The internal mounting fasteners that hold the first gear operator (hand wheel attached to this one) to the second gear operator (attached to valve yoke) has loose mounting screws. These screws are internal to the unit and disassembly will be required. <I> **** Actions Taken **** valve yoke) has loose mounting screws. These screws are internal to the unit and disassembly will be required. Mechanics notified Supervisor. OCC notified. <N> **** Equipment Description **** T -453- - -F7/15.4- | 02-00-COND-V-120B
395318 | CR | 20190611 |  |  | HP technician inappropriately dressed for C-zone |  |  |  | N | NO | <D> HP technician assigned to assisit HP who is assisting Operations do #300 Drywell walkdown was dressed in labcoat and shorts. This in not in accordance with GEN-RPP-04 <I> Recorded picture of individual in area. Posted picture in DW trailer
395320 | CR | 20190611 |  | 2 | Injury resulting from higher than anticipated residual press |  |  |  | N | NO | <D> **** Detailed Description **** During the dissasembly of DEH-V-160A 0212549501 residual pressure was released resulting in an injury that required offsite medical treatment. <I> **** Actions Taken **** Contacted OCC, OCC health and the shift Manager
395321 | CR | 20190611 |  | 4 | Leak from H2-TI-1/5 unions during airtest. |  |  |  | N | YES | <D> **** Detailed Description **** During SOP-GEN-AIRTEST, medium leaks were discoverd on both sides of H2-TI-1/5, one union and one threaded joint. <I> **** Actions Taken **** Updated SOP-GEN-AIRTEST Picture in EDMS <N> **** Equipment Description **** TG 471 | 02-00-H2-TI-1/5
395322 | CR | 20190611 | CAQ | D | CRDM Weepage Note During RPV Leak Test | Y | N |  | N | YES | <D> **** Detailed Description **** Minor expected weepage was noted at CRDM locations 02-23, 34-11, and 38-19. Weepage trend was noted as decreasing. This weepage is expected based upon GEK-71316A and meets the acceptance criteria for the leak test. <I> **** Actions Taken **** Informed OCC. Informed control room. Informed RPV leak test coordinator. <N> Weepage was noted as 6 drops per minute or less with a decreasing trend for all three locations. . Leakage was evalauted per engineering using the GE guidance (see EDMS). Leakage was found to be aceptable and is expected to stop at rated pressure and temperature. | 02-00-CRD-DRVE-0223,02-00-CRD-DRVE-3411,02-00-CRD-DRVE-3819
395323 | CR | 20190611 |  | 3 | TMOD EC 16946 does not have an associated parent AR EVAL |  |  |  | N | NO | <D> **** Detailed Description **** Per SWP-CM-02, temporary configuration changes (TCCs) that are Temporary Modifications (TMOD) should have an assoicated parent AR type EVAL. Contrary to this direction, TMOD EC 16946 appears to exist without a parent AR type EVAL. This TMOD TCC appears to have been created associated with AR CR 374506 only with TCHG tracking assignment 374506-13 under that AR CR. This is an administrative issue only. TMOD EC 16946 is at ACTIVE-R status and is being removed (restored) per R24 WO 02123616.
395324 | CR | 20190611 |  | 3 | SOP-COND-FILL and SOP-COND-LU procedure changes |  |  |  | N | NO | <D> **** Detailed Description **** 5.2.5 states â€œIF SOP-COND/RFW-LU has been completed, THEN VERIFY the following vents and drains are closed per the lineupâ€ COND-V-400 (Zinc injection isolation) and RFW-V-400 (Zinc injection isolation) are to be open per the SOP-COND-LU but are shut in SOP-COND-FILL 5.2.5 and are not restored to open in the fill procedure. Per the chemistry procedure for Zinc Injection System (12.18.1) sections 6.3.10 and 6.4.7 these valves are to be open. COND-V-100/27 (RFP Bypass Hdr Drain) and RFW-V-721 (Upstream RFW-FCV-10A/B) are listed in SOP-COND-FILL 5.2.5 but are not listed on the LU procedure. COND-V-133A and COND-V-139B are listed as capped closed in the Fill procedure but not on the LU.
395325 | CR | 20190611 |  | 3 | TMOD EC 17782 has no AR type EVAL or TCHG assignment |  |  |  | N | NO | <D> **** Detailed Description **** Per SWP-CM-02, temporary configuration changes (TCC) that are Temporary Modifications (TMOD) should have an associated AR type EVAL and a TCHG tracking assignment. Contrary to this direction, TMOD EC 17782 appears to exist (INSTALLD status) without a parent AR type EVAL or any associated TCHG tracking assignment. This TMOD TCC appears to have been created associated with AR OSCR 393982. Suggest assignment to AR-EFIN for restoration of TMOD EC 17782 compliance with SWP-CM-02 / PPM 1.3.9. <N> Additionally, the WR or WO that will remove (restore) the Temporary Modification is not identified (e.g., cross -referenced to TMOD EC 17782 in Portal J). Per E-FIN input, this TMOD will remain installed until R25.
395327 | CR | 20190611 |  | 3 | TMOD EC 16285 tracking assignment is ENG vs TCHG |  |  |  | N | NO | <D> **** Detailed Description **** Per SWP-CM-02, tracking assignments for Temporary Modifications are to be TCHG assignments. Contrary to this direction, the existing tracking assignment for TMOD EC 16285 is an ENG assignment. TMOD EC 16285 is ACTIVE-R status - R24 WO 02107729. . Suggest AR-EFIN change AS 360803-02 from an ENG assignment to a TCHG assignment for restoration of compliance with SWP-CM-02 / PPM 1.3.9.
395328 | CR | 20190611 | CAQ | D | RRC-V-89B Packing Leak | Y | N |  | N | YES | <D> **** Detailed Description **** During other PMT checks in the Drywell mechanics identified that RRC-V-89B has a packing leak of 5 drops per minute. <I> **** Actions Taken **** Notified OCC, MCR, and initiated CR and WR <N> Per the initiator of this CR EPN should be 89B instead of 89A. . As per the note above, CAP changed the EPN to the correct letter | 02-00-RRC-V-89A
395329 | CR | 20190611 |  | 3 | TMOD EC 16701 has no AR type EVAL or TCHG assignment |  |  |  | N | NO | <D> **** Detailed Description **** Per SWP-CM-02, temporary configuration changes (TCC) that are Temporary Modifications (TMOD) should have an associated AR type EVAL and a TCHG tracking assignment. Contrary to this direction, ACTIVE-R status TMOD EC 16701 appears to have been created under an AR type CR (AR CR 370880) and its tracking assignment is an ASGN assignment under that AR CR. This is an administrative issue. WOT 02118048-10 is FINISHED status for restoration of this TMOD.
395330 | CR | 20190611 |  | 3 | TMOD EC 17086 has no AR type EVAL or TCHG assignment |  |  |  | N | NO | <D> **** Detailed Description **** Per SWP-CM-02, Temporary Configuration Changes (TCC) that are Temporary Modifications (TMOD) should have an associated AR type EVAL and a TCHG tracking assignment. Contrary to this direction, ACTIVE-R status TMOD EC 17086 appears to have been created under an AR type CR 9AR CR 376834) and its tracking assignmetn was an ENG assignment under that AR CR. Additionally, the ENG tracking assignment was advanced to COMPLETE though the TMOD was not advanced to CLOSED. This is an administrative issue. It appears that TMOD EC 17086 was physically restored via R24 WO 02124515.
395331 | CR | 20190611 |  | 3 | COND-V-100/27 and RFW-V-100/27 appear to be the same valve |  |  |  | N | NO | <D> **** Detailed Description **** Both EPNâ€™s are valid and active however there are no documents in portal J associated with RFW-V-100/27. SOP -COND/RFW-LU refers to the RFP Bypass header drain as RFW -V-100/27. However, SOP-COND-FILL, M504-2, and the EPN label in the field refers to this valve as COND-V-100/27. Please revise SOP-COND/RFW-LU to read COND-V-100/27, evaluate if RFW-V-100/27 is a unique plant component, and if not please remove it from active status in portal J. <I> **** Actions Taken **** Informed Supervision
395332 | CR | 20190611 |  | 3 | SOP-COND/RFW-LU and SOP-COND-FILL PCN |  |  |  | N | NO | <D> **** Detailed Description **** RFW-V-137 and COND-V-100/27 are shown on M504-2 as being closed and capped. SOP-COND/RFW-LU and SOP-COND-FILL (step 5.2.5) should be revised to reflect this, see CR 395331. The other valves listed in SOP-COND-FILL (step 5.2.5) should be evaluated and updated to read closed and capped as applicable. <I> **** Actions Taken **** Informed Supervision
395333 | CR | 20190611 |  | 4 | SSS office temperature controller |  |  |  | N | YES | <D> **** Detailed Description **** The temperature controller for the SSS office needs to be moved and it does not currently work reliably. The controller TIC-59 (no system is listed on the controller) is located behind the ice machine in the GSB lunchroom, which causes the controller to read erroneously high when the ice machine is running. This makes the temperature hard to control in the SSS office and everywhere else it controls in the GSB. This controller needs to be moved to a new location where it is not located behind an ice machine, a refrigerator, or a refrigerated vending machine. The temperature controller is also not working correctly. You have to remove the cover to get the temperature to change and the air does not always flow when you try and change the temperature setting. <N> **** Equipment Description **** TIC 59 GSB lunchroom behind the ice machine
395334 | CR | 20190611 |  | 4 | R24 LL lack of Communication for RPV Hydro |  |  |  | N | NO | <D> **** Detailed Description **** Offsite personnel that were not scheduled for 6/11/19 night shift were not notified until EOC turnover (1645) that they were required to be on-site for RPV Hydro at 1800. Both day shift and night shift counterparts for the VT-2 inspections were to be notified by 1500 whether or not to plan to come in to adequately make sure they would be ready to come on-site. For future outages, the EOC needs to verify who is on the schedule for both day and night shifts and validate that everyone has been communicated with to ensure proper turnover and to avoid any time pressure and/or delays in the schedule. <I> **** Actions Taken **** Discussed this with EOC
395335 | CR | 20190611 |  | 4 | R24 LL Excess Flow Check Valve Testing â€“ Poor Preparedness |  |  |  | N | NO | <D> **** Detailed Description **** During the RPV Leak Testing, Excess Flow Check Valve testing was to be performed in parallel (utilizing the pressurized system to meet the requirements of GT 85 psig; subject surveillances ISP-EFC-B107 and ISP-EFC-B106). B106 was performed on dayshift and was a planned 6 hour task. B107 started on nights but was a planned 32 hour task. With a constraint of 200Â°F and a warm up rate of ~6Â°F/hour (starting at ~125Â°F at the start of RPV hydro testing, 32 hours would have been impossible to meet without ceasing EFC work and/or depressurizing the RPV. Due to this inability to complete the testing prior to the 200Â°F constraint, the EFC scope was ceased and crews backed out. In order to complete EFC testing, RPV temperature will need to be below 200Â°F and above 85 psig, after the hydro. <I> **** Actions Taken **** Generated CR. This event requires a critique (poor job planning and prep, coordination, and task preview, resulting in rework and altering the plan for EFC testing). Note: PPM 3.2.3 has alternative pressurization line-ups that will allow EFC testing to continue after the RPV leak test is completed.
395336 | CR | 20190611 | CAQ | D | RRC-V-23B leak near the valve | Y | N |  | N | YES | <D> **** Detailed Description **** It was reported during the RPV hydro that approximately 30 DPM is leaking from the insulation near the RRC-V-23B valve. <I> **** Actions Taken **** Notified OCC Generated WR | 02-00-RRC-V-23B
395337 | CR | 20190611 | CAQ | D | RFW-V-65A and RFW-V-65B Leak (RPV Leakage Test) | Y | N |  | N | YES | <D> **** Detailed Description **** It was observed during the RPV Leakage Test that RFW-V-65A was leaking approximately 2 drops/second and RFW-V-65B was leaking less than 1 drop/minute. <I> **** Actions Taken **** Notiifed OCC and generated WR | 02-00-RFW-V-65A,02-00-RFW-V-65B
395338 | CR | 20190612 | CAQ | D | RRC-V-67B found with 20 dpm leak during RPV Hydro | Y | N |  | N | YES | <D> **** Detailed Description **** During RPV hydro VT-2 inspections, RRC-V-67B was found with an ~20dpm leak coming from the bottom center of the valve through the insulation. To determine origin of the leak, insulation will need to be removed. <I> **** Actions Taken **** Notified RPV Hydro SMEs. Notified EOC. <N> **** Equipment Description **** Drywell C 507 see drawing RCC-102-2 | 02-00-RRC-V-67B
395339 | CR | 20190612 |  | 3 | R24LL: SOP-GEN-AIRTEST revision needed |  |  |  | N | NO | <D> **** Detailed Description **** Engineering provided a main generator cutaway drawing showing hard to find generator air test leakage locations. This drawing needs to be included in the SOP to facilitate future testing. <I> **** Actions Taken **** Initiated this CR. Uploaded drawing to the EDMS document file for this CR.
395340 | CR | 20190612 | CAQ | D | TSP-CRD-C101 required for two maintenance rods | Y | N |  | N | YES | <D> **** Detailed Description **** TSP-CRD-C101 was performed with rods 30-15 and 30-11 fully inserted and disarmed due to RPIS problems. These rods will require scram time testing at GT 800 psig and prior to 40% RTP to comply with techinical specifications for scram time testing on rods which had maintenance performed on them. This CR is written to document compliance with step 7.5.12.c and d of TSP-CRD-C101. <I> **** Actions Taken **** Discussed with SM and SNE. | 02-00-CRD-HCU-3011,02-00-CRD-HCU-3015
395341 | CR | 20190612 | CAQ | D | TSP-CRD-C101 testing required on two non-maintenance rods | Y | N |  | N | YES | <D> **** Detailed Description **** TSP-CRD-C101 was performed with rods 26-11 and 26-15 fully inserted and disarmed due to an RPIS problem. These rods will require scram time testing when the RPIS issue is resolved. These two rods were not maintenance rods but were impacted by refueling operations. This CR documents compliance with TSP-CRD-C101 step 7.5.12.e. <I> **** Actions Taken **** Discussed with SM and SNE. | 02-00-CRD-HCU-2611,02-00-CRD-HCU-2615
395342 | CR | 20190612 | CAQ | D | CRD-HCU 02-39 A solenoid valve is de-energized | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU 02-39 "A" solenoid valve is de-energized this was discovered while performing OSP-RPS-M401 thermography check. A local check of the test switch verified it was in the correct NORM position however the slightest contact with the switch caused an audible enerigization of the "A" solenoid. Recommend inspecting the terminations of RPS -RMS-0239/TS/A to verify they are snug. If not may be a issue within the switch itself. | 02-00-RPS-RMS-0239/TS/A
395343 | CR | 20190612 |  | 3 | R24LL: SOP-GEN-AIRTEST Procedural Update |  |  |  | N | NO | <D> **** Detailed Description **** SOP-GEN-AIRTEST Major Rev. 5, step 5.3.3 is the calculation for determining the generator air leak rate, this needs to be updated to state P1 + A1. The blank formal needs the corresponding x to be changed to +. The formula also requires temperature to be in Kelvin not Celsius. The 2017 calculation was performed correctly. . Step 5.2.14 states the test is 24 hour (minimum) and a note states if LT 24 hours requires concurrence from engineer and CRS, the use of this note should be limited and the test performed a minimum of 24 hours. Data from 2017 shows that the leak rate lowers as the test prolongs, this can be attributed to higher accuracy of test conditions the longer it is performed. No procedure changes needed this is to document the benefit of performing the test to at least the recommended minimum. <I> **** Actions Taken **** Calculation will be performed in aliance with this CR for 2019 test. Procedure should be updated for R25.
395344 | CR | 20190612 |  | 4 | Cond-FIC-200A is reading erratic so it Cond-FQ-200A |  |  |  | N | YES | <D> **** Detailed Description **** Cond-FIC-200A reads 0-2000 gallons with no flow through it. (It has step changes and stays that way for a few seconds to about a minute). The sister instrument, Cond-FQ-200A has a fault code in during this. This is for Cond-DM-1A. Cond-DM-1A is the first demin to be placed in service after this outage. It was placed in service and Cond-V-76 was closed, (the CFD Bypass). Cond-FIC-200A is now step changing between 5700gpm and 6200gpm. The D/P cell for this may just need venting. The system is pressurized. Isolating the D/P cell and blowing down the line for about 10-15 minutes might clear this up. | 02-00-COND-FIC-200A
395345 | CR | 20190612 | CAQ | D | CIA 8.3.49 nitrogen leaks found | Y | N |  | N | YES | <D> **** Detailed Description **** While performing 8.3.49 CIA to ADS valve air supply leak check noticeable leaks were found on the following valves. CIA-V-736B, 708B, 744B, 710B, 46B, 709B and 30B. Valves inside of E-IR-74 also found leaking were valves 74, 22, 18, and 4. All the connections inside the rack connecting CIA-PS-39B to system were found leaking and the fittings possibly need to be replaced. <I> **** Actions Taken **** initiated cr/work request, notified operations | 02-00-E-IR-74
395346 | CR | 20190612 |  | 4 | MS-TCV-116C Regulator air leak |  |  |  | N | YES | <D> **** Detailed Description **** air operator regulator has 2 bad air leaks. one is on the supply line to the regulator (west side of regulator) compression fitting leaking, and the body gasket is leaking badly on the east side of the regulator body <I> **** Actions Taken **** informed supervision initiated CR/WR | 02-00-MS-TCV-116C
395347 | CR | 20190612 | CAQ | D | RRC-V-85B Packing Leak | Y | N |  | N | YES | <D> **** Detailed Description **** RRC-V-85B packing leak identified during RPV Hydro. Leak rate was approx 1 dpm. No record could be found of any past maintenance to RRC-V-85B. | 02-00-RRC-V-85B
395348 | CR | 20190612 |  | 4 | R24 LL Insulator Support during RPV Leak Check |  |  |  | N | NO | <D> **** Detailed Description **** Insulators / sheet-metalists were not on stand-by in support with RPV Leak Testing. Based on discussions with others familiar with past leak testing evolutions, insulators were with the VT-2 team to remove insulation as required. During R24, insulators were not a planned resource with the inspection team and as such, planning was necessary to generate the appropriate tasks to remove insulation for inspection (schedule delay). <I> **** Actions Taken **** Generated CR. Initiated WR to remove insulation.
395349 | CR | 20190612 |  | 3 | SOP-COND-FILL errors in valve EPNs |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.2.64 incorrectly refers to COND-V-110A. It should refer to RFW-V-110A. Step 5.2.66 incorrectly refers to COND-V-110B. It should refer to RFW-V-110B. <I> **** Actions Taken **** Wrote CR.
395350 | CR | 20190612 | CAQ | D | CIA-RO-18B Leak | Y | N |  | N | YES | <D> **** Detailed Description **** Restricting Orifice CIA-RO-18B (RX Building Truck Bay) fitting/cap leak (underside of pressure gauge) found during snoop checks. <I> **** Actions Taken **** Notified CRS. Initiated CR/WR. <N> **** Equipment Description **** CIA-RO-18B 441' Reactor Building Truck Bay | 02-00-CIA-RO-18B
395351 | CR | 20190612 | CAQ | C | CRD-HCU 3011, 2655, 3027 brass union air leak | Y | N |  | N | YES | <D> **** Detailed Description **** During PMT Leat Test, maintenance craft personnel found small air leaks on 3 CRD-HCU's (3011, 2655, 3027). Air is leaking in the same place on all 3. Small leak is at the 1/2" inch pipe threaded brass union (CID 52620113) which is located on top on the 127 air operator. Suggest engineering evaluate for further action. <I> **** Actions Taken **** Finding was brought up to component group manager and CR initiated. <N> Dsicussed with Maintnenace Foreman- Leakge was very small. Had to wait and observe before a small bubble would form. This leakage has no impact on operation or impact to reliability. Recommend no action since the leakage is insignificant. Makeup air to the system is more than adaquate and there is no impact on header pressure. . Reopened this CR. This CR is being closed to the WM process however the WR/WO were not checked 'completion required' IAW SWP-CAP-01. The boxes have now been checked and the CR reclosed. | 02-00-CRD-HCU-2655,02-00-CRD-HCU-3011,02-00-CRD-HCU-3027
395352 | CR | 20190612 |  | 3 | Cyber Security Qual Guide requirements |  |  |  | N | NO | <D> **** Detailed Description **** Cyber Security Qualification Directory 2.19 currently has requirements within the CSAD and CSAE qualifications to be part of the Critical Group (CSAJ). It is also required within the notes that other qual groups should also meet this requirement. The requirements appear to be reaching a greater population than what was intended. Recommend Information Services evaluate if the level of requirements meets the intent for all of the qual groups listed. <I> **** Actions Taken **** Discussed with Engineering and Cyber Security and initiated CR.
395353 | CR | 20190612 |  | 4 | R24 LL OSP-RPV-R801 RPV Pressure Test (Hydro) preparation |  |  |  | N | NO | <D> **** Detailed Description **** There was inadequate preparation and execution of the RPV pressure test to ensure the organization efficiently addressed identified leaks while at test pressure. Specifically, craft resources were not standing by, ready with packages and tools to correct minor packing leaks (e .g., MSIV packing leaks), insulation to positively identify leak locations removal (e.g., RRC-V-23B/67B), etc. Also, lines of communication and criteria for reducing Reactor pressure need to be clear and pre-established, especially when confronted with leaks/insulation removal delays.
395354 | CR | 20190612 |  | 3 | Engineering evaluation for OSP-RPV-R801 procedure change |  |  |  | N | NO | <D> **** Detailed Description **** During OSP-RPV-R801 it is required to have either both RRC pumps in service at 15hz or one in service at 30hz. Request engineering evaluate a lower flow than 30hz due to the elevated heat addition at 30hz which limits time for RPV hydro tresting opportunities.
395355 | CR | 20190612 | CAQ | D | CRD-HCU-3031 has a leak from the N2 bottle | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-3031 still has a leak from the N2 bottle. Following pressurization the HCU pressure dropped ~100# over 12 hours. Refer to WR 29149442 | 02-00-CRD-HCU-3031
395356 | CR | 20190612 |  | 4 | TSW Leak RW 507' | N | N |  | N | YES | <D> **** Detailed Description **** There is s small leak (apporx 1-2 drops per minute) on the TSW outlet line for WCH-CU-51B upstream TSW-TI-64. The leak is located where the 6" TSW piping meets with a support beam. <I> **** Actions Taken **** Initiated CR, EO walked down area for any additional leaks. <N> **** Equipment Description **** RW 507' piping upstream TSW-TI-64
395357 | CR | 20190612 |  | 4 | System start prior to NDE results during SDC recovery | N | N |  | N | NO | <D> **** Detailed Description **** During recovery from RPV hydrostatic test procedure (OSP -RPV-R801), RHR-B was recovered in SDC mode per section 5.2 of SOP-RHR-SDC. This section requires a warmup of the RHR system and isolation of the normal keep fill system during that time. Due to the low RPV pressure at the time of warmup there was not as much driving pressure to cause the warmup flow. This may have been a contributor to a system low pressure alarm that was received. The lowest visible pressure was 82# but required a fill verification to be performed prior to recovery (OSP-RHR-M102). The system was vented with the following results: RHR-V-622B = 2.56 seconds of air (LT required 6.1 seconds for additional venting), RHR-V-633=2.19 seconds of air (LT required 9.4 seconds for additional venting), RHR-V-741=No air. Since the low pressure alarm was received NDE inspection was required, however the pump was started prior to obtaining those results. This decision was made based on the need to restore SDC, NDE still en-route to the site, and satisfactory venting results. NDE results post pump start showed no signs of voids. This CR is written to document the decision. <I> **** Actions Taken **** OCC and OPS Mgr informed.
395358 | CR | 20190612 | CAQ | C | MT&E Found out of tolerance | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0066271 Megger Model DLRO 10 was found OOT during calibration cycle. DEF #7051A <I> EFIN TO EVALUATE THE TWO USAGES.
395362 | CR | 20190612 |  | 4 | Low Level Leaks during SOP-GEN-AIRTEST | N | N |  | N | YES | <D> **** Detailed Description **** Several low level leaks were discovered during SOP-GEN -AIRTEST. These are in addition to the medium level leak recorded in CR 395321. 1. Turbine End Bearing Bracket Man Way Covers. 2. All External Man Way Covers on Generator. 3. H2-V-25A Condition Monitor Return Block <I> **** Actions Taken **** Created WRs for the identified leakage areas. | 02-00-E-GEN-1,02-00-H2-V-25A
395363 | CR | 20190612 |  | 4 | CRD-DPI-7 RWCU Purge- High DP at 39 psid | N | N |  | N | YES | <D> **** Detailed Description **** CRD-DPI-7 was reading 39 psid. Filters need swapped and changed. | 02-00-CRD-DPI-7
395365 | CR | 20190612 |  | 4 | Excessive amounts of high TOC water into T2 | N | N |  | N | YES | <D> **** Detailed Description **** Excessive amounts of high TOC water into T2 from unknown sources. Having to sample and pump T2 to barrels for the 3rd time in 2 weeks. Normally, the only flow into T2 is from CAS compressor moisture blowdown, but that is only a small stream <I> **** Actions Taken **** Notified SSS, Having T2 sampled and pumped to barrels by laborers again. Recommend finding source of inleakage to T2 | 02-00-FD-SUMP-T2
395366 | CR | 20190612 |  | 3 | SOP-ELEC-BKR-OPS enhancement | N | N |  | N | NO | <D> **** Detailed Description **** SOP-ELEC-BKR-OPS Section 5.22 (Rack out of 4160/6900V grounding devices) requires change. Step 5.22.5 f should be deleted entirely. Grounding Devices do not have MOC switch functions. In fact, the MOC pin on grounding devices have been altered to ensure they are too short to mate up with the MOC channel. Having a conditional step that will be N/Aed 100 percent of the time leads to confusion about the intent of the step and can cause significant work delays, unneccesarrily. <I> **** Actions Taken **** validated MOC pins are too short to ever engage in the MOC channels. <N> **** Equipment Description **** SOP-ELEC-BKR-OPS
395367 | CR | 20190612 |  | 4 | R24 LL: Training Instructors/Staff as Craft Supervisors | N | N |  | N | NO | <D> **** Detailed Description **** The practice of using instructors/staff as craft supervisors, as opposed to hiring additional supplemental supervisors, should be evaluated. In-processing resources are decreasing while ramp-up of outage workers is pushed closer to outage. This meant fewer opportunities to break away from in-processing and prepare for supervisor duties and in some cases training, instead of supervising, during the first week of the outage. This is not excellence for planning/prep or supervisory oversight. The decision to not upgrade the pay of these individuals to grade 28 is also problematic. The rationale provided was that everyone has an outage job. This is somewhat true, but not everyone directs work in the field or is accountable for things like personnel safety and responding to injuries/events. Individuals filling supervisor roles & responsibilities should be appropriately compensated. <I> **** Actions Taken **** This LL applies to Maintenance, RP, and RMC Laborers where a total of nine individuals - all grade 27 non-supervisors - filled craft supervisor roles during R24.
395369 | CR | 20190612 |  | 4 | Emergent issue teams and priorities management | N | N |  | N | NO | <D> **** Detailed Description **** Over several shifts, an emergent issue team for BS-V-52B worked with Mechanical Maintenance to drive resolution. Past the point of discovery, the issue was downgraded, but there was little change in the level of direction or resource prioritization requested by the emergent team. This continued focus led to resources being diverted from other priorities â€“ emergent and scheduled â€“ that would have gone further to supporting plant start-up, like long cycle clean-up. We need to better identify downstream priorities and when an issue should not be a top priority any longer, emergent issue team or not. <I> **** Actions Taken **** Initiated at request of Mechanical Maintenance
395370 | CR | 20190612 |  | 4 | HP unfamiliarity and turnover increasing stay times | N | N |  | N | NO | <D> **** Detailed Description **** During the first half of R24, mechanics encountered HP technicians less familiar with plant systems and who were overly conservative with contamination control to the point that stay times were increased. Example being RHR-RO-10B where a breach took longer than necessary over concerns of water in the system despite a nearby downstream, lower elevation breach in the same piping. HP turnover quality in the heater bay has also varied leading to mechanics waiting while smears were re-performed. All of this contributed to more dose than necessary. <I> **** Actions Taken **** Initiated at request of Mechanical Maintenance
395371 | CR | 20190612 |  | 4 | Unnecessary Drywell Dose | N | N |  | N | NO | <D> **** Detailed Description **** On 6/5/19, removed air lines and an unplugged junction box led to increased drywell stay times for work on an RWCU drain line and MSRV testing. Air needed to be rerouted and communications from field-to-supervisor took longer than necessary while the craft looked for a working phone. Efforts to close out the drywell may not have considered what remaining work would need these resources. <I> **** Actions Taken **** Initiated at request of Mechanical Maintenance.
395373 | CR | 20190612 | CAQ | D | Leak found durring PMT of CIA-PRV-9A | Y | N |  | N | YES | <D> **** Detailed Description **** Found leak on 90 when performing snoop test of wo 021450210 (TT)(I) PMT LEAK CHECK CIA-PRV-9A. Need work instructions to isolate PCV and bottle to repair threaded connection leak. <I> **** Actions Taken **** wrote CR , contacted Supervisor | 02-00-CIA-PRV-9A
395375 | CR | 20190612 |  | 4 | The Observation mobile app is returning an error | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** When a user submits a new Observation in the DevonWay Observation mobile app, an error is returned. "Observation failure. Field geolocation in level H is undefined". <I> **** Actions Taken **** An update to the app was pushed out yesterday with an enhancement to support geolocation. The vendor has been notified of the issue. TrakWay Ticket TRAK-2019-2559. Very High Priority. Vendor resolved the issue with the new geolocation . No further action is necessary. <N> The vendor has resolved the issue with the geolocation attribute. No further actions are required for this CR. Recommend NCAQ 4.
395378 | CR | 20190612 |  | 3 | PPM 12.14.13 requires a revision | N | N |  | N | NO | <D> **** Detailed Description **** PPM 12.14.13 requires a procedure revision. Several steps within the procedure reference other steps within the procedure that do not exist. The following are the procedure steps that reference others that do not exist: 7.1.12, 7.3.13, and 7.3.17. Also, step 7.3.1 references Attachment 7.1, which is labeled as Attachment 7.1 on page 9, however it is referenced as Attachment 8.1 in the Attachments section of the procedure (page 8). <I> **** Actions Taken **** Initiated this AR/CR.
395380 | CR | 20190612 | CAQ | C | Drywell head as left LLRT GT admin limit. | Y | N |  | N | YES | <D> **** Detailed Description **** Drywell head as left LLRT was measured GT its admin limit, of 1685 SCCM with a admin limit of 50 SCCM. The LLRT test hose was verified to not be leaking. <I> **** Actions Taken **** Notified LLRT SRO, EOC <N> **** Equipment Description **** RB606 Cavity | 02-00-C-TK-1
395381 | CR | 20190612 | CAQ | D | The CRASH call to DOE EOC did not work during test | N | Y |  | N | YES | <D> **** Detailed Description **** The test CRASH call today found the phone not working at the DOE EOC. The phone rings but when answered only has dial tone. All other CRASH destinations are operable. <I> **** Actions Taken **** Notified. OPS, SCC, EP. Recommend closing this CR to the WR. <N> **** Equipment Description **** DOE
395382 | CR | 20190612 |  | 4 | MS-V-166C and MS-V-163 close limit switches sticking. | N | N |  | N | YES | <D> **** Detailed Description **** Upon mechanically latching the MT, MS-V-166C and MS-V-163C close limit switches did re-align after the valve was full open causing both limit switches to be made up, giving an indeterminate position indication on DEH-MON-2. See CR# 387889. <I> **** Actions Taken **** WR written. <N> **** Equipment Description **** TB 501. | 02-00-MS-V-163C,02-00-MS-V-166C
395383 | CR | 20190612 |  | 4 | E-LP-GSB/1 won't stay energized unless contactor button push | N | N |  | N | YES | <D> **** Detailed Description **** All circuit breakers on E-LP-GSB/1 are closed in and there is no power in the telecom room on the Service Bldg 420. The overhead light turns on if the red button on the contactor panel is pressed. The light goes off after the button is released. <I> **** Actions Taken **** Wrote this CR/WR and contacted the PSRO | 02-00-E-LP-GSB/1
395384 | CR | 20190612 |  | 4 | High CRD suction filter D/P. | N | N |  | N | YES | <D> **** Detailed Description **** P603.A7 5-8 CRD Suction Filter D/P high alarm received in the MCR. EO dispatched found CRD-DPIS-15 at 10 PSID (alarm at 9 PSID). Swapped to CRD-FU-10B. Request cleaning/changout of CRD-FU-10A. <I> **** Actions Taken **** Swapped to CRD-FU-10B. <N> **** Equipment Description **** RB 422 | 02-00-CRD-FU-10A
395385 | CR | 20190612 |  | 4 | Thread engagement for hytroc clamp nut on new MSR studs | N | N |  | N | YES | <D> **** Detailed Description **** New studs and Hytorc clamp nuts are being used on MSR 2nd stage manway covers for the first time under EC 17673. As the first cover was being installed, Boilermakers questioned the look of the thread and stud engagement. By design of the hytorc clamp nut (for the TN series), the stud does not protrude through the nut. Original reports were that 8-9 threads are engaged, leaving 3 to 4 threads exposed. As left condition is 10+ threads engagement. No further action required for the field. Request assignment to Engineering to look at whether the stud length can be better optimized. <I> **** Actions Taken **** Informed EOC and requested review, see EDMS Contacted hytorc vendor, see EDMS Engineering responded to inspect and inspected 2 of the 4 manways: The as left condition of the clamp nuts was covering 10 to 11 threads with some clamp nuts having all threads covered. Engineering provided input that the achieved thread engagement was sufficient - see the e-mail attached to the AR CR EDMS. <N> **** Equipment Description **** MSR 2nd stage manway coveres | 02-00-MS-HX-1A,02-00-MS-HX-1B
395386 | CR | 20190612 |  | 4 | Near miss reported | N | N |  | N | NO | <D> **** Detailed Description **** An EN employee had a near miss incident where a faulty chair wheel broke. Individual fell to the ground but was not injured. Chair is from Lesro Industries L-37742. See EDMS for photo of chair. <I> **** Actions Taken **** ISPM-1 was followed once incident was reported. Notified management, Facilities and Industrial Safety of the issue. Chair has been marked as â€˜out of serviceâ€™ and removed from employee's office. Provided coaching to employee on the requirement to report incidents when they happen (incident happend 6/10, wasn brought to leadership until 6/12).
395387 | CR | 20190612 | CAQ | D | CRD-V-101 excessively hard to operate on CRD-HCU-18-03 | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-V-101 excessively hard to operate on CRD-HCU-18-03. During operation CRD-V-101 very difficult to operate-more so than all others operated. Needs to be worked during next refueling outage. <I> **** Actions Taken **** Contacted Supervision and wrote this CR/WR | 02-00-CRD-V-101/1803
395388 | CR | 20190612 |  | 4 | R24 lesson learned (LL) - circuit breaker racking coordinati | N | N |  | N | NO | <D> **** Detailed Description **** R24 LL documentation. Lack of schedule activities to coordinate breaker racking activities has resulted in rework and schedule delays. On at least two occasions, major breakers were racked in before fit up checks had been performed resulting in Ops having to rack them back out. Additional tasks need to be created for breaker replacements such that breakers that are racked out in support of a clearance don't get automatically racked back in on the clearance release. The additional task for breaker fit up would be logically tied as a predecessor to racking the breaker in. <N> There are typically no tasks for breaker racking as it is called out as part of lifting the clearance order, so nothing to logic tie. I recommend the electricians simply post a work in progress tag on the breaker handle stating not to rack in the breaker until there task is complete.
395389 | CR | 20190612 |  | 4 | poor lug insulation on Control Power x-former MS-42-2R11A | N | N |  | N | NO | <D> **** Detailed Description **** electricians set up to perform insulation testing of control wiring for MS-MO-70D and noticed that one of the vendor provided wires landed on X2 of the control power transformer has deficient insulation on the lug. The lug itself appears to be electrically sound, but the factory insulation on the crimp barrel looks to have slid off of the barrel prior to crimping activities at the factory. <I> **** Actions Taken **** Took pictures and re-landed the wiring. Write CR and WR <N> **** Equipment Description **** MS-42-2R11A TG 471
395390 | CR | 20190612 |  | 3 | MS-V-234 | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** WHILE WORKING ON WO #02118080-01 ADDITIONAL DEFECTS WERE OBSERVED. EXCEPTIONAL AIR LEAK FROM THE TOP HAT SCREW ALONG WITH A "SMUSHED" RUBBER STEM PROTECTOR. IT IS ALSO BELIEVED THAT A NEW LIMIT SWITCH IS NEEDED DUE TO POSSIBLE FAILED CONTACTS. HOWEVER REPLACEMENT SWITCH IDENITY IS UNKNOWN. <I> **** Actions Taken **** NOTIFIED SUPERVISION <N> **** Equipment Description **** MS-V-234
395391 | CR | 20190612 |  | 3 | SWP-CHE-02 revision needed | N | N |  | N | NO | <D> **** Detailed Description **** The 2019 Interim Guidance for BWR Water Chemistry Guidelines issued by EPRI on 3/25/19. There are 10 technical white papers based on 21 issues that were identified and categorized as High Priority, High Impact for which R&D has either been completed, operating experience exists and techincal bases can be developed. These issues need to be incorporated into SWP-CHE-02. Assign to AR-CHEM. <I> **** Actions Taken **** Wrote this CR to track the implementation of the procedure revision. The change was identified as part of the review of AR OER 392002
395392 | CR | 20190612 |  | 4 | DEH-P-1B trip | N | N |  | N | YES | <D> **** Detailed Description **** While performing The Standby DEH pump Auto Start Test per SOP-DEH-START, DEH-P-1B auto started as expected. After flagging the running pump (B), the lights went out and pressure lowered. DEH-P-1A was then taken to start. <I> **** Actions Taken **** Restarted DEH-P-1A. <N> **** Equipment Description **** TB 471 | 02-00-DEH-P-1B
395394 | CR | 20190612 |  | 4 | No closure path exists for NICM AS 381944-02 | N | N |  | N | YES | <D> **** Detailed Description **** No path for closure of NICM AS 381944-02 (NICM for ISFSI junction box straps) could be identified (R24 SOP-OPS-05 Restart Evaluation Process). No restoration WR/WO or accept as-is AR EVAL exists cross-referenced to AR EVAL 381944 or any of its assignments. Reference SWP-CM-02. . The WR associated with this AR CR 395394 is to repair the 'numerous' ISFSI junction boxes that 'have degraded closing latches' so that the NICM for stainless steel straps to 'hold the junction boxes tightly closed until the latches can be repaired' can be restored. <N> **** Equipment Description **** ISFSI junction boxes with stainless steel straps added as a Non-Intrusive Compensatory Measure.
395395 | CR | 20190612 |  | 3 | TSP-CRD-C101 enhancement | N | N |  | N | NO | <D> **** Detailed Description **** During conduct of TSP-CRD-C101 it was beneficial to have 2 teams locally at the Rx 522â€™. One team (RO and SRO) to setup and scram a rod from the HCU and then another team (2 EOs, or EO and RO/SRO) to recover HCUs that had already been scram timed. This was found to be an efficient method during R24. Revise TSP-CRD-C101 with a note to include this information for future outages.
395396 | CR | 20190612 |  | 4 | Potential DEH-V-165A leak | N | N |  | N | YES | <C> CR reopened so operations could add notes. <D> **** Detailed Description **** During performance of SOP-DEH-START section 5.13 fyrequel was observed on the stem of DEH-V-165A. Its is not collecting at a rate to cause active dripping. A stain was observed on the floor near this valve inidcating a potential prior leak. <I> **** Actions Taken **** OCC informed, will be sending out additional resources to investigate. <N> Concerning leak status for DEH. The WR has already been closed concerning this leak (leak not active), however OE tells us to monitor this over time even if a leak appears to have stopped - AR 207245. I have confirmed with Operations and the System Engineer that periodic walk downs will continue to occur while the heater bay and turbine deck are accessible. No further action required. | 02-00-DEH-V-165A
395397 | CR | 20190612 | CAQ | D | Two radwaste tanks released to CST with out of spec TOC | N | N |  | N | NO | <D> **** Detailed Description **** EDR-TK-4A was sampled on 6/12/19 at 0830 and EDR-TK-4B was sampled on 6/12/19 at 0714. Both tanks had high TOC at 956 ppb and 630 ppb respectively. Both tanks were released to the CST due to no room for reprocessing. Documentation with a CR is required for this activity per CI-9.2 step 5.4. Recommend Category D-Trend.
395398 | CR | 20190612 |  | 4 | (Non EN/CGS) CC-191 Certificate missing PO on External Data |  |  |  | N | NO | <D> **** Detailed Description **** (Non EN/CGS) Calibration Report missing PO number on external certificate attached Received an email in regards to the calibration report documentation for the following item on Intermech PO # 390000-0199. Item 4 - Energy NW asset number is ITM-WTP-062 The PO # was not written on page 3 of the calibration report for asset number ITM-WTP-062. Customer requested ENSL write the purchase order number on page 3 of the calibration report for the asset number listed above and email the corrected calibration report. Recommend assign to AR-CALSERV Cat. 4 for trending. See EDMS for Corrected copy. <I> **** Actions Taken **** Corrected certificate package with PO on page 3 and resent to customer with CC-191. Reveiwed PO for customer requirements in its entirety.
395399 | CR | 20190612 | CAQ | C | TMU-SR-1 Not Collecting Samples. | N | Y |  | N | YES | <D> **** Detailed Description **** The eSOMs log for OPS4 indicates the TMU composite sampler, TMU-SR-1, screen shows zero and manual sample did not work on 6/11/19 and 6/12/19. REMP personnel and Environmental Services verified on 6/12/19 at 1300 that the TMU-SR-1 manual sample did not work, and noticed TIME control mode is flashing which is out of the ordinary. The sampler has only delivered Â¾ gallons or 2.8 liters since 5/30/19 (13 days). Per the IMDS, the sampler should deliver 25mls every 75 minutes. This should result in 480 ml/day or 6.24 liters (1.6 gallons) in 13 days. TMU-SR-1 is an ODCM table 6.3.1-1 3a and EFSEC 332 required sampler. CR394980 and WR29149368 were written on 6/6/19 for a different issue. The condition of the sample rack not functioning as expected may be related to cycling the power supply during station divisional testing. <I> **** Actions Taken **** CR written and generate WR check box marked. <N> Recommend adding: â€œNOTIFY REMP personnel via e-mail at â€œREMP PROGRAMâ€ and/or extension 2360 or 5097â€ in SOP-ELEC-SM7 | 02-00-TMU-SR-1
395400 | CR | 20190612 |  | 4 | Permanent repair for upper TGB membrane roof needed |  |  |  | N | YES | <D> **** Detailed Description **** During R24, degradation of the upper Turbine Generator Building (TGB) roof was identified (AR CR 394426, AR CR 394438, and AR CR 394437) and temporary repairs were implemented under WO 02144915. These temporary repairs are being tracked via Non-Intrusive Compensatory Measure (NICM) AS 394710-02. This AR CR and its associated WR are for a WO to complete permanent repairs of the upper TGB membrane roof for restoration/closure of the NICM implemented during R24. | 02-00-T-BLDG-MISC
395401 | CR | 20190612 |  | 3 | R24LL: Minor enhancement to SOP-DEH-START |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.7.2 has you verify that the BPV solenoids are energized, to aid in this step if a parenthesis containing ( Digital Output Status chassis 2 slot 7). This would aid in the performance of this step. <I> **** Actions Taken **** Generated procedure change CR
395402 | CR | 20190612 |  | 4 | RFW-CRT-L003 indicates I/O faults | N | N |  | N | YES | <D> **** Detailed Description **** RFW-SCAN-L040A and RFW-SCAN-L040D have blinking OK lights indicating a fault detected. RFW-CRT-L003 also indicates I/O faults (alarms â€œAny faultâ€, â€œAny I/O faultâ€, â€œAt least one I/O faultâ€). Faults should be cleared prior to startup. | 02-00-RFW-CRT-L003,02-00-RFW-SCAN-L040A,02-00-RFW-SCAN-L040D
395403 | CR | 20190612 |  | 4 | RFT-PLC-3A faulted DI module | N | N |  | N | YES | <D> **** Detailed Description **** RFT-PLC-3A appears to have a faulted Discrete Input module. Recommend investigating and attempting to clear faults prior to startup. | 02-00-RFT-PLC-3A
395404 | CR | 20190612 |  | 4 | TG-TE-BM7A indicating 445degF | N | N |  | N | YES | <D> **** Detailed Description **** Main Turbine bearing no. 7 thermocouple 1 (TG-TE-BM7A) is indicating 445degF. Prior to R24 it was indicating normally (see computer point T1 1310A). TG-TE-BM7B (bearing no. 7 thermocouple 2) is indicating normally at 93degF. | 02-00-TG-TE-BM7A,02-00-TG-TE-BM7B
395405 | CR | 20190612 |  | 4 | RRC-CB-ASD/1B/1 closing fuse box | N | N |  | N | YES | <D> **** Detailed Description **** RRC-CB-ASD/1B/1 cubicle side of closing fuse box left side broken. Needs replaced. <I> **** Actions Taken **** Supervision notified. <N> **** Equipment Description **** ASD bldg at RRC-CB-ASD/1B/1 breaker cubicle | 02-00-RRC-CB-ASD/1B/1
395406 | CR | 20190612 |  | 3 | Filled RPV with RHR-P-2C per OSP-RPV-R801 and 3.2.3 |  |  |  | N | YES | <D> **** Detailed Description **** CR to document using RHR-P-2C to fill the RPV for pressurization per OSP-RPV-R801. Step 9.2.13.c requires to CR to document the thermal cycle on the RPV nozzle. <I> **** Actions Taken **** CR | 02-00-MS-RPV-3
395407 | CR | 20190612 |  | 3 | HWC-E/1-1 requires labels to be made | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WO#02104439-02, HWC-E/I-1 and its spare were found to be linear per work order instruction, but out of tolerance low (per vendor OMM). There is currently no IMDS for this instrument to tell us the required accuracy for our use. Recommend creating IMDS with tolerances. <I> **** Actions Taken **** Documented as found/as left readings (no changes made). Notified supervisor per WO steps, wrote this CR. | 02-00-HWC-E/I-1
395408 | CR | 20190612 |  | 4 | CM-11 at 487 Mens bathroom |  |  |  | N | YES | <D> **** Detailed Description **** CM-11 out of service due to high voltage low <N> **** Equipment Description **** Rw 487 mens bathroom | 02-00-HP-EQ-63090
395409 | CR | 20190612 |  | 3 | Main Generator leakage is GT 500 SCFD | N | N |  | N | YES | <D> **** Detailed Description **** Per step 5.3.5 of SOP-GEN-AIRTEST, this CR is being generated to document that the main generator hydrogen leakage has been calculated to be greater than 500 SCFD. The final leakrate, with the hyrdrogen dryer skid isolated, was calculated to be 1129 SCFD. Leak locations include: Turbine end bearing bracket man way covers, external man way covers on generator, H2-V-25A Condition monitor return block, and H2-C-1/1 dryer skid compressor. An ODMI has been requested for this leakage. <N> **** Equipment Description **** TG 501' West Side Chagne the ownership from SEEIC to Ops staff to track the ODMI only | 02-00-E-GEN-1
395410 | CR | 20190612 |  | 4 | Excessive drift times for Intercept/Reheat Stop valves | N | N |  | N | YES | <C> Found CR at INPROG status. Reviewed and approved. Duplicate of CR395413 <D> While performing SOP-DEH-START step 5.10.7 several of the valves required greater than 5 minutes to drift closed. Step 5.10.8 suggests replacing DEH-V-163C. Times are as follows: MS-V-163A 6min 9sec MS-V-165A 14min 47sec MS-V-163B 17min 28sec MS-V-165B 10min 15sec MS-V-163C GT 45min MS-V-164C 13min 47sec MS-V-165C 13min 39sec <I> System engineer informed. <N> Main Turbine Intercept and Reheat Stop valves DEH supply isolation vavles | 02-00-DEH-V-163C,02-00-MS-V-163A,02-00-MS-V-163B,02-00-MS-V-163C,02-00-MS-V-164C,02-00-MS-V-165A,02-00-MS-V-165B,02-00-MS-V-165C
395411 | CR | 20190612 |  | 4 | hd-spv-31a air leak | N | N |  | N | YES | <D> **** Detailed Description **** during a heater bay walkdown hd-spv-31a leaking by and needs replacement. audible air leak from 20 feet. <I> **** Actions Taken **** notified supervisor | 02-00-HD-SPV-31A
395412 | CR | 20190612 |  | 4 | ms-ao-234 air leak from spring adjuster | N | N |  | N | YES | <D> **** Detailed Description **** during a heater bay walkdown ms-ao-234 air leak was found from the air operator spring adjuster gasket. audible leak from 6'. <I> **** Actions Taken **** notified supervisor | 02-00-MS-AO-234
395413 | CR | 20190612 |  | 4 | Excessive drift times for Intercept/Reheat Stop valves | N | N |  | N | YES | <D> **** Detailed Description **** While performing SOP-DEH-START step 5.10.7 several of the valves required greater than 5 minutes to drift closed. Step 5.10.8 suggests replacing DEH-V-163C. Times are as follows: MS-V-163A 6min 9sec MS-V-165A 14min 47sec MS-V-163B 17min 28sec MS-V-165B 10min 15sec MS-V-163C GT 45min MS-V-164C 13min 47sec MS-V-165C 13min 39sec <I> **** Actions Taken **** System engineer informed. <N> **** Equipment Description **** Main Turbine Intercept and Reheat Stop valves | 02-00-MS-V-163A,02-00-MS-V-163B,02-00-MS-V-163C,02-00-MS-V-164C,02-00-MS-V-165A,02-00-MS-V-165B,02-00-MS-V-165C
395414 | CR | 20190612 |  | 4 | OSP-RPV-R801 RHR-C Injection |  |  |  | N | NO | <D> **** Detailed Description **** OSP-RPV-R801 step 9.2.13.c directs a CR to evaluate thermal stresses due to using RHR-C for injection. <I> **** Actions Taken **** Submitted CR. <N> Duplicate of CR 395406.
395415 | CR | 20190612 |  | 4 | bs-v-5a local solenoild air leak | N | N |  | N | YES | <D> **** Detailed Description **** during a heater bay walkdown, bs-v-5a has an auduble air leak from 20'. Ithe local solenoid is leaking. This may be bs-spv-5a however the location of this epn does not match asset suit local in field solenoid. <I> **** Actions Taken **** notified supervisor | 02-00-BS-V-5A
395416 | CR | 20190612 |  | 4 | ms-ao-189 spring adjuster backed out and air leak | N | N |  | N | YES | <D> **** Detailed Description **** during a heater bay walkdown ms-ao-189 has an audible air leak from 10'. Also it was noticed that the spring adjuster is backed out ~4 turns. This needs to be repaired and the gasket replaced. <I> **** Actions Taken **** notified supervisor | 02-00-MS-AO-189
395417 | CR | 20190612 |  | 4 | E-CB-LP2DB/8 is trip free and will not reset. | N | N |  | N | YES | <D> **** Detailed Description **** E-CB-LP2DB/8 is trip free and will not reset. This lighting panel is in the transformer yard and provides transformer yard lighting. This breaker was found trip free when lifting local C/O for fixture replacements. WO 02136055. <I> **** Actions Taken **** Hung local C/O for configuration control. | 02-00-E-CB-LP2DB/8
395418 | CR | 20190612 |  | 4 | SS-V-11B is closed when it should be open. | N | N |  | N | YES | <D> **** Detailed Description **** During performance of SOP-FWH-INTERLOCK-TEST, SS-V-11B exhibited unusual behavior. Initially, SS-V-11B was open, as expected. After jumpers were installed per procedure to simulate BS-V-9C and BS-V-9D in the open position, SS-V-11B stayed open, as expected. After HD-LS-2BHT was actuated and released per procedure, SS-V-11B went closed, as expected. When BS-V-9D was opened at step 5.5.17.c, SS-V-11B opened, as expected. However, while BS-V-9D was still stroking open, SS-V-11B finished going open, then stroked closed, and open, and closed again, and is still closed. With BS -V-9D open, SS-V-11B should be open, too. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-SS-V-11B
395419 | CR | 20190612 |  | 4 | E-CB-LP3CB/5 is trip free and will not reset. | N | N |  | N | YES | <D> **** Detailed Description **** E-CB-LP3CB/5 is trip free and will not reset. This lighting panel is in the transformer yard and provides transformer yard lighting. This breaker was found trip free when lifting local C/O for fixture replacements. WO 02136055. <I> **** Actions Taken **** Initiated CR and WR <N> **** Equipment Description **** Transformer Yard | 02-00-E-CB-LP3CB/5
395420 | CR | 20190612 |  | 3 | Heater Bay WIFI repeaters for portable phones removed | N | N |  | N | NO | <D> **** Detailed Description **** While preparing for COND-LCV-32B AO diagnostic testing 02139748-03, it was discovered that the WIFI repeaters for the portable cell phones were removed. This limits the communication severly. There are only two phones in the heater bay. Neither are near the work area in this task. Good communication is essential especially with this job having a local clearance where techs are seperated by distance and need to clearly comminicate for valve manipulations. Recommend this task to remove repeaters be the last to be done when there is other work to be performed that rely on this form of communication. <I> **** Actions Taken **** Notified supervisor, initiated CR <N> **** Equipment Description **** heater bay 471
395421 | CR | 20190612 |  | 3 | Bad megger tests on isolation flanges for TSW-HX-4A, 4B, 4C | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Per work order 02108851-19 there is supposed to be greater than or equal to 1 Mohm resistance across the new isolation flanges put between COND-M-P/1A, 1B, 1C and the new TSW HX piping that was installed per RIE 264973-3. The megger readings are 0 across every isolation flange which indicates a direct short to building ground and no isolation across the flange. Need to have engineering evaluate the system and identify areas where isolation from building ground needs to occur. <I> **** Actions Taken **** Notified supervisor wrote CR <N> **** Equipment Description **** COND-M-P/1A,1B,and 1C
395422 | CR | 20190613 |  | 4 | RCC-V-72A will not close. | N | N |  | N | YES | <D> **** Detailed Description **** During clearance lift of O-CRA-FANS/R24--001 and SOP-CRA -OPS RCC-RMS-V/72A was placed in AUTO. Valve indication went DUAL and did not show full closed as expected with one CRA fan running. When CRA-RMS-FC/2A was placed in NORMAL -after-OFF RCC-V-72A changed to full OPEN indication. RCC-RMS-V/72A was placed in CLOSED with no change in RCC -V-72A indicated position. <I> **** Actions Taken **** Checked and changed light bulb in the closed indication with no change in indicated postion. Placed RCC-RMS-V/72A in AUTO per SOP-CRA-OPS section 5.4.3 and started CRA-FC -2A. | 02-00-RCC-V-72A
395423 | CR | 20190613 |  | 4 | MS-V-165A had a very small pool of DEH fluid under it | N | N |  | N | YES | <D> **** Detailed Description **** MS-V-165A had a very small pool of DEH fluid under it. while performing testing it was noted when reopening the DEH isolation valve for MS-V-165A approximately 2 tablespoons of oil was noted under the valve. original inspection didnt show a sourece or drip but later inspection with supervisor present showed a very small drop forming on the upper corner of the electrical solonoid. New oil rags were placed under the deh valve block on 6/13/19 at 0010. <I> **** Actions Taken **** wrote CR/WR | 02-00-MS-V-165A
395424 | CR | 20190613 |  | 3 | (LL R24) RFW-V-32A/32B Re-torque Bonnet Bolts |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** One of the prerequisites to perform the Re-torque of the Bonnet Bolts for RFW-V-32A/32B was to verify the new bonnet gaskets had been installed. RFW-V-32A/32B work was scoped out of the outage (WO 02085915 and WO 02085917). OSP-RPV -R801 â€œReactor Pressure Vessel Leakage Testâ€ STEP 9.3.6 is a conditional step that indicates â€œ-â€œIF bonnet gaskets have been replaced on RFW-V-10A(B) or RFW-V-32A(B), THEN INSTRUCT Maintenance to tighten the pressure bonnet studs on the applicable RFW check valve(s) per the applicable Work Order.â€ The EOC was contacted to determine whether or not this task needed to be performed. EOC determined the task did NOT need to be performed. Maintenance notified engineering that the task would be canceled. Later the EOC determined that the re-torque did need to be performed regardless of whether the valves were worked on or not. Planning was contacted to take the task back to ready status and remove the prerequisite to verify the new bonnet gaskets had been installed. By this time the announcement was made that the steam tunnel could no longer be accessed at this time. â€¢ Recommend assignment to operations to have OSP-RPV-R801 â€œReactor Pressure Vessel Leakage Testâ€ step 9.3.6 revised to have the valve bonnet studs re-torqued regardless of whether they have been replaced or not. Additionally the model work order(s) for these valves and the RFW-V-10A/10B need to be revised to remove the prerequisite(s) to verify new bonnet gaskets have been installed. <I> **** Actions Taken **** Discussed issue with component manager and initiated CR <N> WO 02111927-17 Documented "Zero movement" during R24 re -torque of the RFW-V-32A/B valves which were not worked WO 02111927-16 Documented considerable movement of RFW-V -10A/B valves which were worked during R24 RFW-V-10A - 1.5 turns RFW-V-10B - 0.5 turns
395426 | CR | 20190613 | CAQ | D | EDR-TK-4B sent to the CST with out of spec TOC |  |  |  | N | NO | <D> **** Detailed Description **** EDR-TK-4B was authorized to be sent to the CST with a TOC of 663 ppb (spec is LTE 200 ppb). The reject tank EDR-TK-5 is nearing full and water is rapidly coming to radwaste, leaving no additional room to reprocess without potentially contaminating the newly introduced water. <I> **** Actions Taken **** Contacted RWCR and Ops and determined that further reprocessing was not possible with current water inventory in radwaste.
395427 | CR | 20190613 | CAQ | D | SW-PT-32B needs recalibration | Y | Y |  | N | YES | <D> **** Detailed Description **** While monitoring system parameters for the Standby Service Water system, it was noticed that SW-PT-32B was reading ~10psig with SW-P-1B secured. SW-PT-32B measures the discharge pressure off SW-P-1B. SW-V-2B was disassembled and removed (WO 02111475-01) during R24 for planned maintenance and this discrepancy appears to have started after restoring the system post maintenance. This pressure transmitter is used for quarterly IST testing of SW-P-1B (OSP-SW/IST-Q702). OSP-SW/IST-Q702 is also used for SW operability PMT. OSP-SW/IST-Q702 was performed for PMT following SW-V-2B re-assembly. While still within an acceptable band, IST results did show a step change in the negative direction (CR 394611). It is unclear the total impact the current degraded SW-PT-32B would have on IST testing results. Recommend SW-PT-32B be re-calibrated to ensure OSP-SW/IST -Q702 quarterly testing results for SW-P-1B are accurate to allow for proper trending of SW pump integrity. <I> **** Actions Taken **** Notified SM and Supervisor | 02-00-SW-PT-32B
395428 | CR | 20190613 |  | 3 | R24 LL Protective Glove while in CA. |  |  |  | N | NO | <D> **** Detailed Description **** Recommend evaluation of potential budget savings of switching to Unitech â€œGriptechâ€ gloves when working in a CA. This would eliminate the waste associated with wearing a second glove over the currently used rubber gloves as the Griptechs are able to be laundered. The Griptechs also offer different levels of cut resistance.
395429 | CR | 20190613 |  | 4 | MS-MO-110B Handwheel Dislodged from Upper Housing | N | N |  | N | YES | <D> **** Detailed Description **** During the Reterm of MS-MO-110B under WO #02134730-03, it was discovered that the handwheel had become dislodged from the upper housing. <I> **** Actions Taken **** Put the motor operator in a safe condition, notified supervisor, emailed engineering, took a picture for documentation, generated CR so a WR could be generated for mechanics to fix. <N> **** Equipment Description **** located in "B" SJAE Condenser Room on scaffold | 02-00-MS-MO-110B
395433 | CR | 20190613 |  | 4 | CF-P-41A and 41B failed to run properly | N | N |  | N | YES | <D> **** Detailed Description **** CF-P-41A and 41B failed to run properly when attempting to add Scale Inhibitor from CF-TK-41. When starting CF-P-41A the pump showed no flow through the flow gauge and no discharge pressure. The pump then sounded like rocks in a blender and was promptly secured. CF-P-41B was then attempted and the pump showed no signs of degradation but also had no indications of it pumping anything. CF-P-41B was shutdown with SOP-CW-CHEM section 5.7. The lines to both of these pumps are potentially plugged preventing them from being able to add chemicals to CW. <I> **** Actions Taken **** Stopped both pumps to prevent damage. | 02-00-CF-P-41A,02-00-CF-P-41B
395434 | CR | 20190613 |  | 4 | Low Cooling Water Flow on CRD-FCV-2A | N | N |  | N | YES | <D> **** Detailed Description **** Shifted to CRD-FCV-2A per WO 02101714-06 and cooling water flow went to 0 gpm. Request FIN adjust. <I> **** Actions Taken **** Shifted back to CRD-FCV-2B | 02-00-CRD-FCV-2A
395435 | CR | 20190613 |  | 4 | Turbine oil found in sense line | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WO#02111831-31, the poly line for test gauges hooked up to SCW-V-541 was found to contain approximately 10-15 mL of turbine oil. <I> **** Actions Taken **** Notified PSRO and supervisor. Wrote this CR. | 02-00-SCW-V-541
395436 | CR | 20190613 |  | 4 | HD-V-33B did not reposition during testing | N | N |  | N | YES | <D> **** Detailed Description **** During SOP-FWH-INTERLOCK-TEST, page 40, step 5.14.14. HD -V-33B is expected to reposition back to open after the solenoid valve is latched. HD-V-33B remained closed during this step. <I> **** Actions Taken **** Notified SRO, and initiated CR/WR | 02-00-HD-V-33B
395437 | CR | 20190613 |  | 4 | Tax Impact on LRE |  |  |  | N | NO | <D> **** Detailed Description **** The revenue LRE was lower than anticipate for the Tieton project. The result was lower revenue primarily because the revenue figure doesnâ€™t include sales tax which was previously included in the LRE. The resulting change was approximately $18k in lower overall margin for this Project. Tieton is still expected to end the year with $274k in positive margin on $1,341k in Revenue (20% overall margin). The Manager and Tech rep did not know that tax was not included in the LRE calc., Tax has been included all fiscal year. <I> **** Actions Taken **** Notified ESD GM. Recommend cat 4 trend for CR
395441 | CR | 20190613 |  | 4 | SAS Camera Monitors | N | N |  | N | YES | <D> **** Detailed Description **** SAS Camera Monitors not funcitoning as intended. Please contact Security at 2185 for more information. <I> **** Actions Taken **** Notified I&C. Notified Security Management. Generated CR/WR. <N> **** Equipment Description **** Secondary Alarm Station - Main Control Room
395443 | CR | 20190613 |  | 3 | (R24 LL) ASD Lessons Learned |  |  |  | N | NO | <D> **** Detailed Description **** (1) ASD work needs to start much earlier in the outage. Leaving this until later in the outage caused discovery leading to initiation of a Cat-1 emergent issue unnecessarily. (2) Every activity on ASD needs to be treated like it is a High Priority Discovery item (3) ASD procedures, model work orders and work instructions lack consistency across the different channels. This has led to important information sometimes being left out and caused work delays and rework. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
395444 | CR | 20190613 |  | 3 | Vibration Analyzer |  |  |  | N | NO | <D> **** Detailed Description **** Analyzer has a faulty charging port. It seems to be time to implement new Analyzers. Existing analyzer was found plugged in, but had a low battery and was not being charged. After moving charging cable around several times it finally began charging. However, any slight bumps lead to it no longer charging. This can lead to us beliveing we have a vib meter ready to go at any time and finding it de-enegized with no battery life. <I> **** Actions Taken **** cr initiation <N> **** Equipment Description **** CSI-Analyzer ID-0064769 Cal due date 7-16-19
395446 | CR | 20190613 |  | 3 | R24 LL:Stack Mon. Nozzle Inspection and Sample Line Cleaning |  |  |  | N | NO | <D> **** Detailed Description **** WO 02121185-01 and 02121185-05 were planned to inspect PRM-RSM-1 and to clean the Stack Monitor sample line, respectively. Task 05 of the WO called out to build scaffolding all the way up to PRM-RSM-1 for sample line cleaning, while task 01 incorporated actions for the nozzle inspection that didnâ€™t require scaffold (using a scope to inspect the nozzle, instead of going up to PRM-RSM-1). Task 05 of the WO needs to be updated to remove the requirement for scaffolding; cleaning of the transport lines is accomplished via flushing with high volume air from PRM -SR-2. As a result of the scaffolding being in place for task 05, task 01 was not completed as planned. The scaffolding got in the way of the spotting scope. Need to optimize and coordinate these two tasks for future outages. <N> **** Equipment Description **** PRM-SR-1 PRM-SR-2 PRM-RSM-1 Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
395448 | CR | 20190613 |  | 4 | CW water box mud in T2 sump | N | N |  | N | NO | <D> **** Detailed Description **** CW water box mud in T2 sump. This CR references unknown water intrusion into T2 sump. On 6-12-2019, Laborers pumped 10 barrels of high TOC water out of sump T2. After pumping the sump down, it was noticed that there is a large quantity of what appears to be the same kind of mud that was cleaned out of the CW water boxes in the days prior. The recessed floor area around the CW intake water boxes drains to sump T2 <I> **** Actions Taken **** Information only, reference CR #395365 for the need to pump T2 sump to barrels.
395449 | CR | 20190613 |  | 3 | PPM 3.2.3 Procedure change - RCIC-V-63/ RCIC-V-76. |  |  |  | N | NO | <D> **** Detailed Description **** PPM 3.2.3 requied a reset of the seal in to allow opening either RCIC-V-76 or RCIC-V-63 at step 6.2.2. Language was added to allow this reset similar to OSP-RVP-R801. PPM 3.2.3 should be changed to add the same steps under 6.2.2 as OSP-RPV-R801 R030, MR001 step 9.2.8 and 9.2.25. <I> **** Actions Taken **** Created verbal PCN to place RCIC-RMS-S25 in RESET and back into NORMAL.
395450 | CR | 20190613 |  | 4 | (QA) Warehouse Hygrothermograph Failed |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Building 78 Hygrothermograph had an audible alarm and the chart paper had not recorded since the paper was replaced on 5/26/19. At time of walkdown Building 78 HVAC was functioning with normal building temperatures. Factual Basis: â€¢ SWP-MMP-01, Control of Ageable Items, section 3.3.1.c, relies on temperature monitoring to ensure storage requirements. â€¢ Various Warehoused materials may have temperature storage Limitations On Use, for example CID 16001482, Quality Level 1 CarboGuard Epoxy with a storage requirement of 40 -100 degrees. â€¢ During Quality Walkdown, noted that the Building 78 Hygrothermograph ID # 59534 had an audible alarm and the chart paper has not recorded data since the paper was replaced on 5/26/19 Insights: â€¢ At time of walkdown Building 78 HVAC was functioning with normal building temperatures. The Supply Chain Services Manager notified Maintenance of the failed Hygrothermograph <I> **** Actions Taken **** Notified SCS Management, Initiated AR-CR. This is a Deficiency identified during the Special Processes Audit AU-SP-19.
395453 | CR | 20190613 |  | 4 | Wet -56 sprinkler head leaking | N | N |  | N | NO | <D> **** Detailed Description **** Operator was looking for a leak in TG 471 heater bay, I got location from him and went on a search, Found water seeping oit of sprinker head and running down pipe to the foor. <N> **** Equipment Description **** Wet -56 sprinkler head leaking TG 471 B/8
395454 | CR | 20190613 |  | 4 | Wet-67 Fire system leaky union | N | N |  | N | NO | <D> **** Detailed Description **** walk down of fire pipe, found water seeping from a union on fire line Wet-67 between generator and doghouse TG 501 <N> **** Equipment Description **** Wet-67 between generator and doghouse TG 501
395455 | CR | 20190613 |  | 3 | WO 02111831-13 does not capture proper R24 scope of work |  |  |  | N | YES | <D> **** Detailed Description **** This CR does not affect the function of installed plant equipment (main generator shaft ground system). R24 WO 02111831-13, E-GEN-1 REPLACE SHAFT GROUNDING BRUSH, scope of work does not address Main Generator (E-GEN-1) Ground Brush System ground brush element/holder abnormal wear issues. The intent of this R24 work activity was to replace the Main Generator shaft ground brush holder assembly (brush holder, brush element, ground cable, and associated resistor banks) with new and perform a re -alignment of the brushes. The WO 02111831-13 was planned to only replace the brush elements per PPM 10.25.95. In addition, parts limitations on use were not incorporated into the WO instructions to address like-for-like replacement of the ground brush system. This loss of work scope appears to be due to inadequate consolidation of WO 02125385 and WO 02086351 into one R24 coded WO 02111831-13. . Ultimately, only the ground brushes elements were replaced under R24 WR 29149619 so as to minimize outage schedule impacts (lifting E-GEN-1 clearance). . Recommend a new WO be generated from this CR to replace the entire ground brush system to address the entire scope of work as previously identified in WO 02125385 and WO 02086351. Note: CGS will continue to replace main generator ground brush elements at an accelerated rate (every one to two months versus every 3+ months) until the affected ground system components are replaced and properly re-aligned with the generator shaft. The ground system will continue to function as designed in its current state as it has done so over the last fuel cycle. <I> **** Actions Taken **** worked with the EOC/OCC, maintenance, and maintenance planning to identify what work scope could be performed in R24. Generated CR to drive proper scope of work for some future system outage. Reference information uploaded to EDMS. <N> **** Equipment Description **** main generator shaft ground brush system. | 02-00-E-GEN-1
395456 | CR | 20190613 | CAQ | C | ODCM surveilance 16.11.4 missing sign sheet |  |  |  | N | NO | <D> **** Detailed Description **** Procedure PPM 16.11.4, "Monthly composite particulate sample analysis" minor rev 002 was released without surveilance cover sheet. Subsequently, WO task 02133425-01 was completed through dataglance without signature for CRS/Shift manager review after completion. The cover sheet must be restored to procedure through new revision. <I> **** Actions Taken **** Wrote CR and reviewed procedure native file
395459 | CR | 20190613 |  | 3 | SOP-RW/FDR-OPS procedure enhancement. |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Recommend a procedure enhancement to SOP-RW/FDR-OPS section 5.1 "Normal Proccessing of FDR-TK-6" The note at the beginning of the procedure allows skipping steps 5.1.1 to 5.1.14. when FDR is in the recirculation mode. Tank selection ( FDR-TK-9, EDR-TK-41 or EDR-TK-4B ) steps 5.1.5 and 5.1.6 should occur after step 5.1.14. Recommend moving these 2 steps to after step 5.1.14 and renumbering steps, and changing note. <I> **** Actions Taken **** Submitted this AR
395460 | CR | 20190613 |  | 3 | 437 Radwaste walk down behind shield wall. |  |  |  | N | NO | <D> **** Detailed Description **** Housekeeping deficiencies were identified in the 437â€™ RW behind the shield wall. Examples of items found include: Tarp on floor is wet from leak above. Need to change laundry and trash. Light bulbs tubes are in the DAW barrel. <I> **** Actions Taken **** Initiated this CR to address the housekeeping concerns. Discussed situation with Rad Ops supervisor and talked to Operations about investigating the source of the leak. <N> **** Equipment Description **** 437 Radwaste
395461 | CR | 20190613 |  | 4 | COND-P-2A Motor Trip | N | N |  | N | YES | <D> **** Detailed Description **** While starting COND-M-P/2A for an uncoupled run per WO# 02077541 task 15, the motor immediately tripped. P840.A4 1-1 (Booster Pump A Motor Trip) alarmed until the RMS was taken back to off. The trip was not due to an overcurrent condition. <I> **** Actions Taken **** WR written. <N> **** Equipment Description **** TB 441. | 02-00-COND-M-P/2A
395462 | CR | 20190613 |  | 4 | Multiple HD-QSVâ€™s leaking | N | N |  | N | YES | <D> **** Detailed Description **** During performance of PMT leak checks for HD check valves the following EPNs were found to be leaking at the gasketed joint; HD-QSV-32B, HD-QSV-33A, HD-QSV-31A and HD-QSV-31B. <I> **** Actions Taken **** Mechanics notified Supervisor. OCC notified. <N> **** Equipment Description **** 32B T -482- - -F3/6.1 - 33A T -486- - -A9/10.6- 31A T -482- - -E7/6.3 - 31B T -482- - -F1/6.2 - | 02-00-HD-QSV-31A,02-00-HD-QSV-31B,02-00-HD-QSV-32B,02-00-HD-QSV-33A
395465 | CR | 20190613 | CAQ | D | RPS-POS-33T/2B AS Found out of tolerance, but switch was rep | Y | N |  | N | NO | <D> **** Detailed Description **** RPS-POS-33T/2B AS Found out of tolerance, but switch was replaced per WO 02118077-01. Switch was set close to setting and ESP-RPS-B302 set the switch for the final AS Left setting.
395467 | CR | 20190613 | CAQ | C | Data Glance eWP WO data did not transfer to Portal J |  |  |  | N | NO | <D> **** Detailed Description **** On 6/7/2019 work order task 02111864-04 was taken to complete in eWP. On 6/11/2019 a follow-up check (on the work order task) revealed the documents tab inside Portal J never received a QAR document. This document is normally generated through the completion process of eWP. IS was contacted and they discovered eWP received an error when creating the QAR document. IS stated the error was likely caused by an incorrect revision in the compiled documents. IS removed the old revision and re-sent the package through the QAR process and the correct documentation was uploaded into Portal J. These type of errors should be addressed before essential QAR data gets deleted inside eWP. This leaves questions on how long eWP retains data and how error codes are handled/evaluated. Request IS support to address these issues. <I> **** Actions Taken **** Notified IS and got inital QAR error solved, communicated issue to supervision, and documented the condition in this CR. Uploaded WOT to EDMS, Record error can be seen on electronic page 13/15. <N> Package 02111864-04 had an error during the QAR process. IT was notified and corrected the error and added the package back into the QAR process. The QAR was generated. An incorrect document revision was not the issue as indicated in the CR description. IS performs a periodically check for QAR poller errors, research them, and resolve them.
395468 | CR | 20190613 |  | 4 | Maintenance needed for Eyewash Station #13 |  |  |  | N | YES | <D> **** Detailed Description **** The eyewash station located in the 437â€™ RadWaste Building (south side) is below the manufacture recommended pressure setting of 87 psi. The station needs to be recharged. <I> **** Actions Taken **** Wrote CR and discussed with E&RP Manager. <N> **** Equipment Description **** Eyewash Station #13.
395469 | CR | 20190613 |  | 3 | R24 LL CW blowdown records retention |  |  |  | N | NO | <D> **** Detailed Description **** The instruction for records retention in SOP-CW-OPS, attachment 6.8 Blowdown Flow Monitor Out of Service Logsheet is not robust enough to guarantee control of temporary logs when the eDNA data point is out of service, typically outages. The CW blowdown flow records are required by Columbiaâ€™s NPDES permit for monthly reporting to WA Dept of Ecology and should be maintained for at least six years per WA State Common Records Retention schedule. Recommend SOP-CW-OPS procedure steps 5.7.3, 5.11.13 and Attachment 6.8 be modified to require CWBD alternate flow measurements be logged in an electronic temporary log (ESOMS) instead of a paper log. <I> **** Actions Taken **** Discussed with Ops Coordinator and E&RP.
395470 | CR | 20190613 |  | 4 | Exam failure |  |  |  | N | NO | <D> **** Detailed Description **** A trainee failed the 2019 SRO Cert examination. Remediation and re-evaluation will be conducted IAW TDI-02. <I> **** Actions Taken **** Notified supervision. Reviewed TDI-02. Developed remediation plan.
395471 | CR | 20190613 |  | 3 | R24 LL E-MC-2R temp. power |  |  |  | N | YES | <D> **** Detailed Description **** AR 389158 was issued to install Meltric 60 amp MC buckets in E-MC-2R compartment 1B and 13B to support R24 TG 471 heater bay temporary power during refueling outages. This installation was done as a TASM and should be converted to a permanent change. Similar TASMs have been installed in prior refueling outages and are detailed in AR 346815 and AR 381191. . With MC buckets already configured to support the power feed, the intent of this CR is to evaluate this configuration and if acceptable, complete the relevant design change. Recommend 3 level assignment to AR-DEI for resolution. <I> **** Actions Taken **** Wrote this CR <N> **** Equipment Description **** E-MC-2R, TG 471'-0" | 02-00-E-MC-2R
395472 | CR | 20190613 |  | 4 | GY-P-11B1 LEAK AT PUMP DISCHARGE UNION CONNECTION | N | N |  | N | YES | <D> **** Detailed Description **** During restart evaluation walkdown, leak at pump discharge union connection GY-P-11B1 . Puddle forming in the floor under the connection , moisture noted at the discharge union connection .Refer to pics attached in EDMS. <I> **** Actions Taken **** Notified supervisor, EOC and created WR to fix the leak. | 02-00-GY-P-11B1
395473 | CR | 20190613 |  | 3 | Missing egress dose entries for Multipack 29000887 |  |  |  | N | NO | <D> **** Detailed Description **** There is no impact to the plant since the radiation exposure of the wetwell diver was monitored, and a dose estimate was logged in Total Exposure Setup (TES) module of Asset Suite for the individual. The shortcoming is that the 5 DRD egress readings for multipack 29000887 are blank on 5/22/2019. This causes additional work to investigate/estimate the DRD final doses, and does not allow others to use those DRDs until the missing entries are filled. The process for issuing special dosimetry is in PPM 11.2.6.7, and it states that corrections can be made in the H304 panel of TES. I recommend assigning to Radiation Support group to complete an exposure investigation form per HPI-4.30.
395474 | CR | 20190613 |  | 3 | PPCV is out again |  |  |  | N | YES | <D> **** Detailed Description **** PPCV is out again. Multiple red ice cubes indicate for TDAS Remote and PPCRS MUXs and an error light illuminates on PPC-COMP-7515. This issue reoccured multiple times within a month. Need a permanent fix. <I> **** Actions Taken **** SM/Engineer informed | 02-00-PPC-COMP-8715
395475 | CR | 20190613 |  | 4 | TOA-FL-1A is at End of Roll. | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FL-1A is at EOR. Alarm received at HVAC panel. Both filters appear to be relatively clean. Recommend investigating possibillity of a problem with the advancement function. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 501E | 02-00-TOA-FL-1A
395476 | CR | 20190613 |  | 4 | OSP-RPV-R801 initial pressure | Y | N |  | N | NO | <D> **** Detailed Description **** During the preparation steps for the performance of OSP-RPV-R801 on June 13th it was noted the installed test pressure gauges at MS-LS-27 were reading 2 psig different than the installed MS-PI-9 pressure gauge. This was recognized to be a change from the original test performed on June 11th. During the original Hydro performance the installed pressure gauges were reading 20 psi higher than the installed MS-PI-9. The potential impacts on the data for the hydro need to be evaluated. <I> **** Actions Taken **** informed OCC/ENG and initiated CR
395477 | CR | 20190613 |  | 4 | HP turbine insulation configuration |  |  |  | N | YES | <D> **** Detailed Description **** The insulation placed on the HP Turbine over the steam seals should be modified. Currently, the insulation spans the gap between the HP turbine casing and the bearing pedestal. This captures steam that may escape from the Sealing Steam gland or flange and contains it such that it gets drawn into the bearing pedestal across the oil seals. This contributes to high moisture in the turbine lube oil. Also, there is a Yellow and Magenta HP rope tied to a Sealing Steam pipe and is covered by the insulation. The rope needs to be removed by Health Physics before Sealing Steam system is started and melts the rope. <I> **** Actions Taken **** documented in startup walkdown checklist informed EOC <N> **** Equipment Description **** Bearing 1 governor pedestal and Bearing 2 pedestal | 02-00-MS-DT-HP
395478 | CR | 20190613 |  | 4 | H2-FIS-1/1 has locked in low flowrate alarm |  |  |  | N | YES | <D> **** Detailed Description **** While purging CO2 through the H2 Dryer Skid unable to verify flow on H2-FIS-1/1 (SOP-H2/CO2-OPS 5.1.10.c). It reads â€œLow Alarm 1 Flowrateâ€ and â€œLow Alarm 2 Flowrateâ€. Valve lineup verified. There is a note that it may indicate lower than normal but should still be able to verify flow. Verified pressure at the inlet and outlet filters. Unable to verify purged air out of the H2 Dryer Skid. | 02-00-H2-FIS-1/1
395479 | CR | 20190613 | CAQ | D | RCIC-POS-SS/1 Sticking RCIC-MO-1 diable swtch for overspeed | Y | N |  | N | YES | <D> **** Detailed Description **** RCIC-POS-SS/1 is sticking in the depressed position (which opens the contact preventing opening of RCIC-V-1 when the RCIC turbine trips on mechanical overspeed). During overspeed trip testing ppm 10.7.5 the limit switch for RCIC-POS-SS/1 had to be physically moved back into position. See EDMS for photo. This limit switch roller should be in contact or nearly in contact with the metal swing arm when the mechanical overspeed trip is reset. The mechanical overspeed trip is reset in the picture and the limit stick is shown stuck in the tripped position. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** RCIC Pump Room | 02-00-RCIC-POS-SS/1
395480 | CR | 20190613 |  | 3 | Procedure enhancement for SWP-PRO-01 |  |  |  | N | NO | <D> **** Detailed Description **** Reccomend changing step 4.3.3 to allow inititals to be transferred to the new revision if the person that is transferring the initials is the same person that originally initialed the old procedure. . During R-24 the Locked valve checkilist (1.3.29) changed 4 times and the final product with the transferred initials is cumbersome. . <I> **** Actions Taken **** Wrote CR
395481 | CR | 20190613 |  | 3 | SOP-COND/RFW-LU errors |  |  |  | N | NO | <D> **** Detailed Description **** Four valves have incorrect EPNs: RFT-V-724A should be RFW-V-724A per M985-1 RFT-V-725A should be RFW-V-725A per M985-1 RFT-V-724B should be RFW-V-724B per M985-2 RFT-V-725B should be RFW-V-725B per M985-2 <I> **** Actions Taken **** Wrote CR
395482 | CR | 20190613 | CAQ | D | Unplanned Loss of power to floculator building | N | Y |  | N | YES | <D> **** Detailed Description **** There was a loss of power to the floculator building on 6/13/2019, this caused an auto start of FP-P-110 subsequent loss of potable water. Recommend facilities investigate and correct the loss of power issue. <I> **** Actions Taken **** Shutdown FP-P-110 and informed CRS <N> **** Equipment Description **** facilities power supplt to floculator building Update: Facilities power has been restored. FP-P-110 was placed back in Auto and declared Functional at 0451, 6/14/19. Reference LCS tracking sheet L19-FP-P-110-004.
395483 | CR | 20190613 |  | 4 | Revision to PPM 3.2.3 was performed not per SWP-PRO-02. |  |  |  | N | NO | <D> **** Detailed Description **** AR 395449 documented revision to PPM 3.2.3 by Verbal PCN. Per SWP-PRO-02 section 5.5, the revision process must be initiated in Automated Process Workflows and initial approvals obtained on or before the next business day. No process was initiated in APW prior to implementation of the PCN. <I> **** Actions Taken **** Coaching provided to individual. Submitted this CR for trending.
395484 | CR | 20190613 |  | 4 | BS-SPV-52B making excessive noise |  |  |  | N | YES | <D> **** Detailed Description **** The solenoid for BS-SPV-52B is making a loud repetitive clicking noise. This appears to be a repeat of the same issue from CR 00366297 from 2017. Please investigate/repair. See EDMS for video. | 02-00-BS-SPV-52B
395485 | CR | 20190613 |  | 4 | BS-DVSPV-6B continuously venting air |  |  |  | N | YES | <D> **** Detailed Description **** BS-DVSPV-6B has contnuous air flow coming from its vent tube. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-BS-DVSPV-6B
395486 | CR | 20190613 |  | 4 | rft-mo-1a needs lower bushing replaced |  |  |  | N | YES | <D> **** Detailed Description **** during PM inspection on wo 02111107 we found the lower bushing (53) galled. This bushins is in item (5) turnbuckle. Reference CVI DWG 02-1119-00,11. Bushing needs replaced <I> **** Actions Taken **** notified supervisor and system engineer | 02-00-RFT-MO-1A
395487 | CR | 20190614 |  | 3 | Personal Medical Condition - Transport Off-Site |  |  |  | N | NO | <D> **** Detailed Description **** On Wednesday, June 13, 2019 an Energy Northwest employee experienced a personal medical condition at the Deschutes building Lobby. A 2222 call was placed at 2317. A medical responder tone out was initiated by the main control room per 1.9.13. The patient was evaluated and treated by the medical responders and Hanford Fire Department. Hanford Fire Department (HFD) arrived at 2335. The patient was further evaluated and transported to Kadlec Medical Center at 2345. An oxygen bottle was partially expended during the treatment, recommend replacing the bottle. <I> **** Actions Taken **** The employee is from Orginization 52622. A supervisor left the site to meet the patient at Kadlec Medical Center. <N> Inventory of the First Responder cabinet on the first floor of the Deschutes building was conducted following a man down event on June 13, 2019 and the oxygen tank was replaced. No further action required.
395488 | CR | 20190614 |  | 4 | Personal Medical Condition - Transport Off-Site |  |  |  | N | NO | <C> Duplicate of CR395487 <D> **** Detailed Description **** On Thursday June 13, 2019, an Energy Northwest employee experienced a personal medical condition in the PEC (Deschutes Bldg.) first floor lobby. A 2222 call was placed at 23:16. A medical first responder tone out was initiated by the main control room per PPM 1.9.14. The patient was evaluated and treated by the medical first responders. Hanford Fire Department (HFD) Medic 1923 and Ladder 1923 arrived at 23:31. The patient was further evaluated by HFD and transported to Kadlec Medical Center at 23:48. <I> **** Actions Taken **** Notification was provided to OCC Management. A supervisor left site to meet the patient at Kadlec Medical Center.
395489 | CR | 20190614 |  | 3 | MT TTVs Servo Drives Need to be Reset |  |  |  | N | YES | <D> **** Detailed Description **** Require MT TTV servo drivers to be reset for MT testing <I> **** Actions Taken **** CR/WR | 02-00-DEH-MON-2
395490 | CR | 20190614 |  | 4 | RCIC-V-65 | Y | N |  | N | YES | <D> **** Detailed Description **** While getting readiy to perform check valve testing on RCIC-V-65 it was discovered that the insulation was re -installed prior to completing the check valve diagnostic testing. During the final checks to confirm the leads and test points were intack it was discovered the test point stud was also knocked off. <I> **** Actions Taken **** Generated CR to document the need to re-attach the stud. generated WR 29149693 to re-attach the stud. Contacted OCC. | 02-00-RCIC-V-65
395491 | CR | 20190614 | CAQ | D | AMA-AH-51 Will Not Maintain Temperatures in TSC |  |  |  | N | YES | <C> CR reopened to edit completion required button. <D> **** Detailed Description **** The OCC and EOC were relocated to the TSC on 06/13/19. Temperatures were high and were not being controlled. Inspection by a system engineer revealed the cooling coil refrigerant line encased in ice. It is suspected that the coil internal to AMA-AH-51 is also iced over and not tranferring heat. Please investigate and repair. <I> **** Actions Taken **** Notified the EOC system engineering manager. | 02-00-AMA-AH-51
395492 | CR | 20190614 | CAQ | C | Outside Radiation posting down due to High winds. |  |  |  | N | YES | <D> **** Detailed Description **** The RCA, RMA, RA located on the eastside of the PAP was blown down due to high winds and inadequate posting practice. <I> **** Actions Taken **** Adusted the rad rope and added ty wraps to prevent the rope from failing. <N> **** Equipment Description **** East of the HP PAP.
395493 | CR | 20190614 |  | 4 | repair broken linkage pin on RFT-ASM-1A |  |  |  | N | YES | <D> **** Detailed Description **** during reassembly of feedback linkage on RFT-ASM-1A, the connection bolt broke. (item 10 on CVI DWG 1119-00,3) . Part needs to be fixed or replaced. (see I&C for details). Broken part is in Mech shop. see mech shop supervision <I> **** Actions Taken **** wrote this CR and informed supervisor and OCC <N> CR was edited to remove a proper name from the body description. | 02-00-RFT-ASM-1A
395494 | CR | 20190614 |  | 3 | R24LL: SOP-COND-FILL procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.2.12 opens the selected condensate booster pump suction bypass valve to start filling the long cycled piping. Remove the words â€œthe selectedâ€ and (N/A pump not used)â€ in Step 5.2.12 since all suction bypass valves must be opened to vent all three condensate booster pumps. Note: Step 5.2.70 verifies closed all three condensate booster pump suction bypass valves. <I> **** Actions Taken **** Discussed procedure enhancement with the Operations Procedure supervisor.
395495 | CR | 20190614 |  | 4 | MD-V-84 (AOV) indicates stuck in mid-position |  |  |  | N | YES | <D> **** Detailed Description **** MD-V-84 (AOV) indicates stuck in mid-position locally and dual position and in the control room. Valve was rebuilt per WO 02118045 this outage. The as-left valve flow scan task 05 was cancel-requested. Locally valve isolation V-43 verified open, air regulator has 38 psig and SPV is hot to touch (expected conditions). Based on mid-positon of AOV locally, likely valve packing is too tight. | 02-00-MD-V-84
395496 | CR | 20190614 |  | 4 | Excessive leakage during COND-DM-1F Precoat. |  |  |  | N | YES | <D> **** Detailed Description **** While trying to precoat COND-DM-1F, there was too much leakage into the precoat tank to maintain level while adding resin without it overflowing. This was seen when adding the first 6 bags of P22H. With the recirc bypass fully open, level continued to go up until it overflowed prior to the tank being clear of resin. This was from an initially low tank level. Since it overflowed with 6 bags, the precoat cycle was allowed to finish without attempting the remaining 18 bags of P42H. <I> **** Actions Taken **** stopped the precoat cycle early. | 02-00-COND-DM-1F
395497 | CR | 20190614 |  | 4 | TG-42-3B1E Main Turbine Turning Gear Bkr would not Close |  |  |  | N | YES | <D> **** Detailed Description **** During tag lift on TG-42-3B1E The disconnect would not close. The disconnect felt crunchy at the beginning like the linkage was binding and spongy at the end. The disconnect would not click into the closed position and likely needs to be lubricated. Please investigate <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** TB 471' | 02-00-TG-42-3B1E
395498 | CR | 20190614 |  | 4 | Filled RPV with RHR-P-2C per OSP-RPV-R801 and 3.2.3 |  |  |  | N | YES | <D> **** Detailed Description **** CR to document using RHR-P-2C to fill the RPV for pressurization per OSP-RPV-R801 on 6/14/19. Step 9.2.13.c requires to CR to document the thermal cycle on the RPV nozzle. This is the fourth time we have injected with RHR -SYS-C this outage for OSP-RPV-R801 and PPM 3.2.3. <I> **** Actions Taken **** Submitted CR. <N> This is the same issue as CR's 395414 and 395406. 395406 has the assignment to change the operations procedure to correct this issue. | 02-00-MS-RPV-3
395499 | CR | 20190614 |  | 4 | TO-LOC-1 Filter D/P High |  |  |  | N | YES | <D> **** Detailed Description **** TO-LOC-1 filter D/P is high out of spec. OPS logs have the high spec at 15 psid. CurrentLy at 16 psid and increased approximately 1 psid during this shift. <I> **** Actions Taken **** Informed supervision. Wrote CR. | 02-00-TO-LOC-1
395503 | CR | 20190614 |  | 4 | Leakage from COND-V-659 | N | N |  | N | YES | <D> **** Detailed Description **** Leakage noted from cap of COND-V-659 about one drop per second. Cap tightened leak reduced to 2 drops per minute. <I> **** Actions Taken **** SSS informed. | 02-00-COND-V-659
395504 | CR | 20190614 |  | 4 | MCR Tag printer not working correctly | N | N |  | N | YES | <D> **** Detailed Description **** The small caution tag printer in the MCR is not correctly printing tags <I> **** Actions Taken **** contacted IS with the issue <N> **** Equipment Description **** Small caution tag printer in the MCR
395505 | CR | 20190614 |  | 3 | Form 26813 R5 includes direction that cannot be completed | N | N |  | N | NO | <D> **** Detailed Description **** Form 26813 R5 (Decision Making Matrix) includes direction that cannot be completed. The direction to "2. Forward a copy to Asset Management - Business Strategy & Risk Supervisor." cannot be completed because this supervisor position no longer exists. Please update Form 26813 R5 to either remove or revise this direction.
395507 | CR | 20190614 | CAQ | C | OSP-RPV-R801 RHR-C Injection | N | N |  | N | NO | <D> **** Detailed Description **** OSP-RPV-R801 step 9.2.13.c directs a CR to evaluate thermal stresses due to using RHR-C for injection. This CR is for the HYDRO occuring on 6/14/19 and is not a duplicate CR. <I> **** Actions Taken **** OPS Informed.
395509 | CR | 20190614 |  | 4 | ASD UPS TROUBLE | N | N |  | N | YES | <D> **** Detailed Description **** MCR received ASD-UPS TROUBLE (4.602.A13 drop 3-5). Operator was dispatched to ASD building. Lights in the ASD building were ON indicating PP-ASD1/3 was powered. UPS inverter alarm lights were not lit on either unit, and the inverters did not indicate power was coming from battery (see photo for indications). There was a vertical bar on the inverters' LCD screen, what it indicated was not able to be determined (see photo). The upper portion of the LCD bar was blinking, and the bar did not appear to indicate a full value of whatever parameter it is. Please investigate. <I> **** Actions Taken **** Notified CRS <N> **** Equipment Description **** ASD Building The bar graph on the side of the inverter mimic display is for UPS output. T. Mclaen 6/14/19
395510 | CR | 20190614 |  | 3 | SOP-ELEC-125V-START, Revision Change | N | N |  | N | NO | <D> **** Detailed Description **** SOP-ELEC-DC-LU requires that E-DISC-DPS17/2D be locked ON. SOP-ELEC-125VDC-START only requires that E-DISC-DPS17/2D be ON per Step 5.8.1 and 5.8.4. Revise SOP-ELEC-125VDC-START to lock ON E-DISC-DPS17/2D.
395511 | CR | 20190614 | CAQ | D | RRC-V-23B and RRC-V-67B body-to-bonnet leakage | Y | N |  | N | YES | <D> **** Detailed Description **** Durning the 6/14AM RPV hydro, minor body-to-bonnet leakage was identified for RRC-V-23B and RRC-V-67B. | 02-00-RRC-V-23B,02-00-RRC-V-67B
395512 | CR | 20190614 |  | 3 | R24 LL delays following RPV hydro |  |  |  | N | NO | <D> **** Detailed Description **** After leaks were identified during the hydro it was evident that there should have been someone assigned as a lead to coordinate repair activities. Following the RPV hydro Engineering should provide a detailed list of WRs and WOs including VPDS for all tasks that require torqueing. After a list has been provided to maintenance a coordination lead should be identified and responsible to coordinate between Operations, Maintenance, and HP. During R-24 several man hours were spent coordinating repair activities and less than adequate communication was displayed over the span of three shifts, this poor communication and lack of clear direction resulted in multiple delays. <N> Valve packing data sheets and torque values were prepared immediately following the hydro (same day/shift). These were provided to the EOC/OCC, maintenance supervisors/FINN team via email. Delays were due to EOC decisions trying to determine if they should fix the leaks or let them leak. The emails are attached in EDMS for documentation.
395513 | CR | 20190614 |  | 4 | WEA-FN-1C power indicating light on MCC burnt out and stuck | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of CSP-INST-D201, Chemistry Daily Channel and Source Checks, it was noted that the power on indicating light was burnt out. This gives no indicating light on when it is powered on and would mask an indication of electrical isolation which would in turn cause an error on WEA-SUM-1 and an entry into an RFO sample. <I> **** Actions Taken **** RWCR operator notified and light was attempted to be replaced but the light was stuck. CRS and chemistry supervision informed. | 02-00-WEA-42-8E5D
395515 | CR | 20190614 |  | 4 | H2-PUIT-1 not indicating correctly |  |  |  | N | YES | <D> **** Detailed Description **** During the performance of SOP-H2/CO2-OPS, Section 5.1, Step 5.1.7, when the meter was taken to display 2 the percentage indicated 90.8% with CO2 admitted for approximately 5 minutes. The display seems to show a ratio of CO2 with respect to H2. At approximately a 6 percent drop in Cardox level this percentage read 96%. The amount of CO2 added was not in accordance with the OE that refers to a drop in Cardox level of approximately 20% establishs a 95% purity in the generator. Additionally the 3 screen seems to show Air content with respect to CO2. This value was approximately 100 percent at the start of CO2 initiation and dropped to 13% after approximately 16% of the cardox unit was used. 13% was the lowest percentage displayed on channel 3 after using 21-22% of the cardox unit. Based on the unreliable indication of channel 2, there is no way of verifying CO2 purity in the generator. <I> **** Actions Taken **** Informed SM. Filled generator with more than adequate CO2 based on OE. | 02-00-H2-PUIT-1
395516 | CR | 20190614 |  | 4 | COND-DM-1D precoat tank level rose ~1' every 30 minutes |  |  |  | N | YES | <D> **** Detailed Description **** During precoat of COND-DM-1D, precoat tank CF-TK-4 rose approximately 1â€™ in 30 minutes. Level rose even with COND-V-323 fully open per SOP-CFD-BW/PC step 5.8.19. I was able to add 16 bags of 22H and let tank clear, then opened CF-V-147 per SOP-CFD-BW/PC step 5.8.13 to lower tank level and continue with addition resin additions with same results. <I> **** Actions Taken **** CR & WR written. MCR staff, Chemistry and OCC Rep notified via email | 02-00-COND-DM-1D
395517 | CR | 20190614 | CAQ | D | EDR-TK-4A sent to CST with TOC above normal limit |  |  |  | N | NO | <D> **** Detailed Description **** EDR-TK-4A tank sample at 0930 had TOC results of 313 ppb. THis is above the limit specified in SWP-CHE-02. Per CI-9.2 step 5.2.2.a Chemistry supervision was contacted and gave permission to release the tank to the CST and transfer was documented with CR. PER P&I 4.2 of CI-9.2 this transfer is not predicted to result in excedding CST of Rx water normal range for the parameter. <I> **** Actions Taken **** Informed Chemistry Supervision and Radwast Control Room. Wrote CR
395518 | CR | 20190614 |  | 4 | COND-DM-1D significant leakage in valve gallery from RW487 |  |  |  | N | YES | <D> **** Detailed Description **** Following Backwash and Precoat of COND-DM-1D during pressurization of vessel per SO-CFD-BW/PC step 5.8.30, there was significant leakage from overhead in RW467 valve gallery. Leaking coming from floor area of RW487. <I> **** Actions Taken **** MCR, HP notified. CR &WR written | 02-00-COND-DM-1D
395519 | CR | 20190614 | CAQ | D | Startup Transformer Oil Max Level Alarm | Y | N |  | N | YES | <D> **** Detailed Description **** Main Control Room received a Startup Transformer Trouble alarm. Local alarm was OIL MAX LEVEL. Level gauge was at the high level mark. Startup Transformer temperatures were: H2 winding 62C, oil temperature 50C, Y2 winding 54C, and X2 winding 43C. Ambient temperature was approximately 60F. No fans were running at the time. <I> **** Actions Taken **** Notified MCR | 02-00-E-TR-S
395520 | CR | 20190614 | CAQ | C | CRD-RV-81 (equalizing valve) did not respond as expected. | Y | N |  | N | YES | <C> MRT Change request: CR 395520 from D/Trend Repair to Severity C CAQ and assigned to AR-SENSSS. <D> **** Detailed Description **** CRD-RV-81 (CRDH Equalizing valve) did not repond as expected when valving in to support scram time testing. CRD-RV-81 was isolated via CRD-V-149. Cooling water header pressure was 1040#, Exhaust Header pressure was at 0#. When opening CRD-V-149, there was no audible flow noise and no change in Exhaust/Cooling water pressure. Suspect CRD -RV-81 may be stuck CLOSED or CRD-V-149 may have stem/disk seperation. NOTE: Significant Audible flow noise was present when Valving in CRD-RV-80. Flow was expected due to CRD-V77A(B) being OPEN to provide a vent path. Exhaust and Cooling header pressures were taken from CRD-PI-10 and 7. <I> **** Actions Taken **** informed MCR <N> **** Equipment Description **** Rx 522 | 02-00-CRD-RV-81,02-00-CRD-V-149
395521 | CR | 20190614 | CAQ | D | RRC-V-23B and RRC-V-67B packing gland misaligned | Y | N |  | N | YES | <D> **** Detailed Description **** Waldown of RRC-V-23B and RRC-V-67B identified the packing gland is misaligned (cocked). RRC-V-67B is a one stage packing design (misaligned) - RRC-V-23B is a three stage packing configuration. The upper two stages are misaligned. - no leaks were identified (no pressure in the system) <I> **** Actions Taken **** Reported to the EOCC and OCC. Provided recommendatoins on how to perform the repair. This was incorporated into the WO. No signs of degradation to the stem or packing. Any packing adjustments may impact the clearnace between the stem and follower. | 02-00-RRC-V-23B,02-00-RRC-V-67B
395522 | CR | 20190614 |  | 3 | Lessons learned from RF 24 |  |  |  | N | NO | <D> **** Detailed Description **** PROBLEM STSTEMENT: While performing model WO 02112003-12 (installation of the clam shell links) there are obsolete Cat ID's for High Temp RTV Sealant (2203790) and DOW Silicone Grease (89202113). The new Car ID for the High temperature RTV is 26801(RTV 106) and the new Cat ID for the DOW Silicon Grease is 89202113.Engineering was contacted and approved the new Cat ID items. This information needs to be added to the model work order to ensure a better planned product for RF25. <I> **** Actions Taken **** Stopped work and contacted supervisor. Contacted engineering to verify the correct material Ordered correct material to perform the work.
395523 | CR | 20190614 |  | 4 | TSW-PCV-20, upper gland follower broke | N | N |  | N | YES | <D> During the Temporary leak seal injection of TSW-PCV-20's upper packing box, one gland flange ear broke at approximately 2500psi injection pressure / gland stress. The VPDS for this valve has a minimum stress of 2000psi and a prefered stress of 3000psi. The current condition of the valve is leak free. Suggest implementing a NICM to install a split carbon / aluminum bushing between the gland and the bottom of the actuator plate. This would maintain gland position and allow the valve continued operation and reinjection option if a leak develops in the future. Operation of the valve will be verified under WO#02120309 -05. Notified the EOC and SSS. See EDMS for pictures. <I> Notified EOC and SSS Uploaded pictures to EDMS. <N> TG 441 Aux boiler room | 02-00-TSW-PCV-20
395524 | CR | 20190614 |  | 4 | RFW-TE-52B and 23B do not contact |  |  |  | N | YES | <D> **** Detailed Description **** RFW-TE-52B and 23B do not contact the cup within the well to provide an accurate reading <I> **** Actions Taken **** wrote cr spoke with engineering discussed with manager | 02-00-RFW-TE-52B,02-00-RFW-TE-53B
395528 | CR | 20190614 | CAQ | C | RRC-M-P/1B Oil Leak Was Not Repaired | Y | N |  | N | YES | <D> **** Detailed Description **** At the beginning of R24, two oil puddles were found on the RRC-P-1B insulation (AR-CR 00393483), and task 16 was added to work order 02124487 to identify and repair the leak. A review of that work order task, however, showed that the leak was not identified or repaired. A large amount of oil was found at the bottom of the motor but the source was not identified because of the quantity of oil and the fact that there was not active leaking at the time. No CR was written. There was a statement added to the work package that said, â€œEC in progress to fix lower leak.â€ The only EC work on this motor (WO 02136481) was to install external oil reservoirs, and it only leak checked the new reservoirs and their piping. It had no instructions to locate and repair any additional leaks. In addition, there was no indication in this package (WO 02136481) that there was any attempt to locate or repair additional leaks. Itâ€™s reasonable to assume that the oil leak from the RRC -M-P/1B lower reservoir was neither located nor repaired. . Oil loss from the RRC-M-P/1B lower reservoir was known and tracked throughout the last cycle and the oil level in this reservoir remained high enough to last the entire cycle even though it got very low. With the addition of the external oil reservoirs, there should be enough oil capacity to last the next cycle â€“ if the leak rate doesnâ€™t increase significantly. This is not likely due to the low pressures in this reservoir. Oil, however, will continue to leak into the drywell if it isnâ€™t located and repaired. <I> **** Actions Taken **** Consulted with EOC. | 02-00-RRC-M-P/1B
395529 | CR | 20190614 |  | 4 | Declared Firearms |  |  |  | N | NO | <D> **** Detailed Description **** Visitors (common carry with freight for the warehouse) declared firearms at the roadblock. <I> **** Actions Taken **** Benton County, Shift Manager, & Security Management notified. Access was denied.
395530 | CR | 20190614 |  | 4 | CRD-DPI-7 reading high D/P. |  |  |  | N | YES | <D> **** Detailed Description **** CRD-DPI-7 is reading 36 psid. It appears that CRD-F-7A is currently in service. Please swap out filters as required. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** Rx 522 | 02-00-CRD-DPI-7
395531 | CR | 20190614 | CAQ | D | DG Building Roof is Degrading and Needs Repair | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During a walkdown of the DG Building roof on 6/14/19, degraded conditions noted previously in CR 356232 (10/11/16) and CR 368492 (7/29/17) were inspected. The inspection identified that the extent of degraded roof membrane (membrane that had become separated from the substrate beneath) had become more wide spread. The separated membrane had grown from approximate 3 ft radius around west roof drain to an approximate 20-25 ft radius. Large 10-15 ft radius and small 4-5 ft radius areas of separated membrane was also noted over the entire DG Building roof and no longer isolated to the west roof drain. Small tears in the membrane and membrane patching were noticed at several roof penetrations. <I> **** Actions Taken **** Performed walkdown of DG Building roof to assess degraded conditions reported in the past and generated this CR <N> **** Equipment Description **** DG Building Roof
395532 | CR | 20190614 |  | 3 | Work Order Worked Using Old Rev of MSDS |  |  |  | N | NO | <D> **** Detailed Description **** The Material Safety Data Sheet (MSDS) attached to MASTER7 for Fyrquel EHC in work order (02145295-01) was not updated to the current revision in the Dolphin system per ISPM-11. Personnel need to ensure they are using the most current revision of the MSDS or Safety Data Sheets (SDS) when working with or around chemicals. <I> **** Actions Taken **** Recommend extent of condition is performed to ensure up to date MSDSâ€™s and or SDSâ€™s are used in work packages.
395533 | CR | 20190614 | CAQ | D | MS-V-166B open indication remains lit after turbine unlatch | N | Y |  | N | YES | <D> **** Detailed Description **** Following unlatch of main turbine, MS-V-166B open indication remains lit. This valve should have green closed indiction under this condition. | 02-00-MS-V-166B
395534 | CR | 20190614 | CAQ | D | MS-V-166B indicates duel when turbine is tripped. | N | Y |  | N | YES | <C> Duplicate of CR 395533 <D> **** Detailed Description **** MS-V-166B indicates mid position with the main turbine tripped. This valve indicates needs to work for quarterly valve stroking when at power. <I> **** Actions Taken **** Wrote CR | 02-00-MS-V-166B
395535 | CR | 20190614 |  | 4 | LL R24 MSIV Packing consolidation missed opportunity |  |  |  | N | YES | <D> **** Detailed Description **** For packing to perform optimally, it must be consolidated. The outage retorque WO's are good and need to be performed every outage but we should expand by taking advantage of the strokes that are performned during an outage to further consolidate the MSIV packing to minimize or eliminate future packing leaks by coordinating resources with the schedule <I> **** Actions Taken **** Wrote CR to capture | 02-00-MS-V-22A,02-00-MS-V-22B,02-00-MS-V-22C,02-00-MS-V-22D,02-00-MS-V-28A,02-00-MS-V-28B,02-00-MS-V-28C,02-00-MS-V-28D
395536 | CR | 20190614 |  | 4 | Air leaks on multiple BS QSVâ€™s |  |  |  | N | YES | <D> **** Detailed Description **** While performing PMT leak checks on BS non return check valve air operators, QSVâ€™s and associated fittings, the following discrepancies were identified: BS-QSV-21A- Solenoid leaks at gasket joint and Â¾ X1/2â€ bushing leaks on bottom side of Tee. BS-QSV-10A- Solenoid leaks at gasket joint and 1â€ plug. BS-V-10B- Solenoid leaks at gasket joint, Â¾ X Â½â€ bushing leaks and Â½â€ NPT X 3/8â€ Swagelok leaks. BS-QSV-13A- Solenoid leaks at gasket joint. BS-QSV -5A- Solenoid constantly venting. <I> **** Actions Taken **** Mechanics notified Supervisor. OCC notified. <N> **** Equipment Description **** 21A T -487- - -B3/7.3 - 10A T -487- - -D4/9.0 - 10B T -487- - -D2/9.2 - 13A T -487- - -D2/8.5 - 5A T -487- - -D2/7.8 - | 02-00-BS-QSV-10A,02-00-BS-QSV-10B,02-00-BS-QSV-13A,02-00-BS-QSV-21A,02-00-BS-QSV-5A
395537 | CR | 20190614 | CAQ | C | CSP-V-10 Disc maginet became disloged. | Y | N |  | N | YES | <D> **** Detailed Description **** performing ISP-CSP/IST-B101 Opened CSPV-10 to check break away torque. indication light for open illuminated. released to close , close light did not illuminate, small gap between disc and seat was noticed. Opened valve again to clean and investigate per procedure. noticed the maginet missing from its spot, found the maginet attached th the seat. <I> **** Actions Taken **** contacted system engineer, supervisor <N> The magnetic latches are to assure valve closure and are designed to be capable of maintaining the valve in a closed position. The missing magnet would not have an impact on the sealing surface as the primary sealing surface was not impacted. LLRT was also performed 5/22/19 on CSP-V-9 and 10, with both valves passing with a leak rate of 592 SCCM with an Admin leak of 2100 SCCM. This provides reasonable expectation that CSP-V-10 could perform its close function with the missing magnet. The missing magnet did not affect the ability for CSP-V-10 to perform its open function due to the breakaway torque value being measure at 60 ft-lbs. Per ISP-CSP/IST-B101, the breakaway torque value needs to be LT 108 ft-lbs. Both Open and Closed functions were not impacted, therefor there is reasonable expectation that CSP-V-10 is capable to perform as designed with the degraded condition. | 02-00-CSP-V-10
395538 | CR | 20190614 |  | 4 | COND-TE-521B is leaking oil out the threads |  |  |  | N | YES | <D> **** Detailed Description **** The larger diameter thread have oil puddled on them. Since the system has been operating there is a teaspoon size puddle. Oil may be getting into the encloser. <I> **** Actions Taken **** Wrote AR and contacted I/C shop | 02-00-COND-TE-521B
395539 | CR | 20190614 |  | 4 | Cond-P-2B has a leak on the hose off the mechanical pump |  |  |  | N | YES | <D> **** Detailed Description **** The suction steel braided hose comming off the mechanical lube oil pump is leaking while the electric oil pump is operating. It could eventually suck air while it is in operation. <I> **** Actions Taken **** Wrote AR and contacted supervisor | 02-00-COND-P-2B
395540 | CR | 20190614 |  | 4 | Insulation smell in Wellhouse #2 (Bldg 40) |  |  |  | N | YES | <D> **** Detailed Description **** After we lost one phase of facilities power, a smell of burning insulation was noticed in Wellhouse #2. The only pump running in that building was PWC-P-103 (jockey pump). Investigate the condition of PWC-P-103. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** Building 40 (Wellhouse #2). PWC-P-103 was found not running with PWC-RMS-P/103 in the On position. PWC-RMS-P/103 was placed in the Off position at the direction of the CRS. | 02-00-PWC-P-103
395541 | CR | 20190614 | CAQ | C | CSP/CVB air operator cat I.d's need additional piece parts |  |  |  | N | YES | <D> **** Detailed Description **** During the PM rebuilds on the CVB-Air operators we have found several degraded fiberglass air cylinders. The internal linings of the cylinders are bubbling and cause internal binding and slow stroke times during the surveillances. The purpose of this CR is an action to create 4 cat i.d's with the intent to have replacement fiberglass cylinders (only). These fiberglass cylinders are piece/parts needed for CID 0054917513, 0054917520, 0054917534, 0054917541. Example PMID where these will be used: 00002996. Once created and able to purchase, update the Bill of Materials for the 3 CSP-AO's (7ab, 8ab, 10ab ect) and the 9 CVB-AO's (1a1, 1a2, 1b1, 1b2) ect.... Recommend a stock of 4 <I> **** Actions Taken **** notified supervisor | 02-00-CSP-AO-7A,02-00-CSP-AO-7B,02-00-CVB-AO-1A1,02-00-CVB-AO-1A2,02-00-CVB-AO-1B1,02-00-CVB-AO-1B2,02-00-CVB-V-1AB
395542 | CR | 20190614 |  | 3 | Lesson learned R24: HCA RWP available to OPS |  |  |  | N | YES | <D> **** Detailed Description **** We did not expect a HCA in the heater bay, but one was found at the begining of the outage between the 6A/B HX's. Operations needed to go in there a number of times, it is generally driven by clearances or procedures. WO's are not always available with the ALARA task informoration. If a HCA occurrs, we need to have a readily available HCA entry task/RWP for entering these zone(s) that arise as it can easily become a 1hr+ boonedoggle to do just find a task/rwp for the job. Consideration of an 'emergent activities' RWP that supports HRA/HCA would be a viable option. <N> **** Equipment Description **** Lessons learned R24. Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
395543 | CR | 20190614 |  | 3 | Revision needed for PPM 16.4.12 |  |  |  | N | NO | <D> **** Detailed Description **** Temp Mod EC-17782 removed control power to AR-CB-P1A breaker tripped indication. PPM 16.4.12 has steps to verify breaker status and is affected by the changes made from Temp Mod EC-17782. PPM 16.4.12 steps 7.1.16 & 7.1.20 needs to be revised to do the breaker status verification at the breaker cubicle on E-SL-11. <I> **** Actions Taken **** Discussed with Operations, Procedure Writer, Maintenance I&C, E-FIN and wrote CR <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
395546 | CR | 20190614 |  | 4 | Two control rods have pressure corrected data | Y | N |  | N | YES | <D> **** Detailed Description **** Two controls rods (26-15 and 30-11) have pressure corrected data for scram time testing and must be scram time tested again prior to exceeding 40% RTP. Rod 30-11 is a maintenance rod. This CR written for tracking purposes per TSP-CRD-C101. <I> **** Actions Taken **** Discussed with SM. <N> **** Equipment Description **** 522' Rx | 02-00-CRD-HCU-2615,02-00-CRD-HCU-3011
395547 | CR | 20190614 |  | 4 | Recirc B system Vibration alarm in with pump secured |  |  |  | N | YES | <D> **** Detailed Description **** Recirc B System Vibration alarm in in with the RRC-P-1B secured. Vibration panel on the Reactor 522 elevation indicates that alarm source is RRC-VBI0P1B/XE pump thrust, currently with RRC-P-1B secured panel is indicating +24 mils. <I> **** Actions Taken **** Informed CRS. | 02-00-RRC-P-1B
395548 | CR | 20190614 |  | 4 | Need to add oil to RRC-M-P/1B upper reservoir prior to RXSU |  |  |  | N | YES | <D> **** Detailed Description **** Based on a review of the as-left oil level information in WO 02124487 the RRC-M-P/1B upper reservoir oil level was left at -0.4", this was confirmed to be the current value based on a discussion with the control room as well. We should add oil to the upper reservoir prior to drywell closeout to ensure we have sufficient margin for the next cycle. . Request an add of 2 gallons to the RRC-M-P/1B upper reservoir. The upper reservoir is approximately 4.25 gallons per inch. 2 gallons of oil should bring the oil level to approximately a level of 0 inches. <I> **** Actions Taken **** CR written and EOC/OCC notified. <N> **** Equipment Description **** Drywell | 02-00-RRC-M-P/1B
395549 | CR | 20190614 |  | 4 | MD-V-83 Indicates intermediate |  |  |  | N | YES | <D> **** Detailed Description **** MD-V-83 currently indicates intermediate. The valve should indicate full open or full closed depending upon turbine latched condition. Request maintenance investigate and repair. This is a PPM 3.1.1 required signature item. <I> **** Actions Taken **** Notified nightshift OCC Ops Rep and SM. | 02-00-MD-V-83
395550 | CR | 20190614 |  | 4 | ASD/B input transformer trouble alarm in |  |  |  | N | YES | <D> **** Detailed Description **** ASD/B input transformer trouble alarm in local reading are all less than alarm set point for liquid temperature, winding temperature , internal pressure, and oil level is in the normal range. Only other alarm cause would be rapid pressure this has no external gage to validate with. Determine cause of lock in alarm and correct. <I> **** Actions Taken **** Informed CRS | 02-00-RRC-TR-ASD/B/1
395551 | CR | 20190614 |  | 4 | ASD/B output transformer trouble alarm in |  |  |  | N | YES | <D> **** Detailed Description **** ASD/B output transformer trouble alarm in local reading are all less than alarm set point for liquid temperature, winding temperature , internal pressure, and oil level is in the normal range. Only other alarm cause would be rapid pressure this has no external gage to validate with. Determine cause of lock in alarm and correct. <I> **** Actions Taken **** informed CRS | 02-00-RRC-TR-ASD/B/2
395552 | CR | 20190615 |  | 4 | CO2 Hose reel light is out. |  |  |  | N | YES | <D> **** Detailed Description **** CO2 hose reel light is out on the TB 501 E. Please replace the bulb. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 501 E
395553 | CR | 20190615 |  | 3 | Evaluate BS-V-13B for a mod/repair Open Pos Sw arm |  |  |  | N | YES | <D> **** Detailed Description **** BS-V-13B gets identified as indicating dual due to the Open Position Switch arm occasionally rolling past the valves actuating arm due to the Position switch and it's arm not being adjustable. Long term fix for this valve is to either lengthen this arm or modify the mounting plate to allow for adjustment of the mounting of the Postion Switch. <I> **** Actions Taken **** Electrical Supervision informed. Included notes referencing this CR in lates work order evaluating Dual valve position indication. <N> AR type EVAL needed for evaluation? | 02-00-BS-V-13B
395554 | CR | 20190615 | CAQ | D | SRM C frequent spikes causing SRM fast period alarm | Y | Y |  | N | YES | <D> **** Detailed Description **** SRM C has been experiencing frequent small spikes causing SRM fast period alarm to annunciate on H13-P603. This is often concurrent with other alarm causing activities, however it has also had small spikes with no other activities in progress. Suspect this is due to some sort of electrical noise interference. <I> **** Actions Taken **** Informed CRS | 02-00-SRM-LI-601C
395555 | CR | 20190615 |  | 3 | Daisy Chained Extension Cord |  |  |  | N | NO | <D> **** Detailed Description **** Communication cabinet for Reactor Camera's and Computers on RB 471 NE have extension cords that are daisy chained from the North wall to the South Wall. <I> **** Actions Taken **** Initiated a CR <N> See pictures in EDMS.
395556 | CR | 20190615 |  | 4 | SOP-COND-FILL, Condensate Temperature LT 90F |  |  |  | N | NO | <D> **** Detailed Description **** Per SOP-COND-FILL, Section 5.4, Filling piping between RFW-V-112A/B and RFW-V-65A/B, Step 5.4.6 directs raising condensate temperature GE 90F. COND-P-4 indicated 72F and could not be raised due to current plant conditions. This CR satisfies step 5.4.6 to initiate a CR if Condensate temperature is GT 60F but LT 90F. <I> **** Actions Taken **** Discussed issue with CRS
395557 | CR | 20190615 |  | 4 | Outlet Not functioning |  |  |  | N | NO | <D> **** Detailed Description **** Outlet 3DA-B-6 on the RB 471 NE is not functioning <I> **** Actions Taken **** Created a CR <N> **** Equipment Description **** RB 471 NE by floor machine and scissor lift
395558 | CR | 20190615 |  | 3 | eDNA trend real time plots keep crashing |  |  |  | N | YES | <D> **** Detailed Description **** Real time plots required by TSP-RB-B501 for fan 1B1 (files located on the T drive) only run for a few minutes before crashing with an error message that the eDNA trend application has stopped working. It has gotten progressively worse over the course of the shift. At the beginning of shift, plots would run for 15-20 minutes before crashing, but now it seems to crash within 3 minutes of starting a plot. <I> **** Actions Taken **** Notified SM. <N> **** Equipment Description **** eDNA on corporate computer system being run on the STA comp See notes document in EDMS. Unable to recreate the issue. It was most likely a local PC issue or network issue that cleared up by itself.
395559 | CR | 20190615 | CAQ | C | EWD-65E-013, EWD-64E-039 Drawing Errors |  |  |  | N | NO | <D> **** Detailed Description **** This is a document error only. There is no impact on the proper operation of any plant equipment. EWD-65E-013 (Zone G/10) - Ladder Diagram incorrectly cross references EWD-64E-038 for HD-RLY-63X2BT 225-226 contacts. Should be EWD-64E-039. EWD-64E-039 (Zone E/1) HD-RLY -63X2BT development shows contacts 225-226 open in shelf state. Should be shown as closed. <I> **** Actions Taken **** Notifed the EOC Design Engineering Manager
395560 | CR | 20190615 |  | 4 | TO-P-BLP Failed to Start at 0 RPM |  |  |  | N | YES | <D> **** Detailed Description **** While making preparations to place the MT on the turning gear per SOP-MT-START the TO-P-BLP was taken to AUTO and it failed to auto start on speed LT 600 RPM with the TO-P-BOP supply adequate oil pressure. Started TO-P-BLP by placing it to RUN. <I> **** Actions Taken **** Left caution tags on to start TO-P-BLP at LT 600 RPM on a MT trip. | 02-00-TO-P-BLP
395561 | CR | 20190615 |  | 3 | Revise OG-RIT-601B IMDS for new HVPS setting |  |  |  | N | NO | <D> **** Detailed Description **** During the calibration of OG-RIT-601B, the HVPS was adjusted to optimize performance. The IMDS need to be revised to show the NEW HVPS setting of 814 VDC. Markup has been uploaded into EDMS.
395562 | CR | 20190615 |  | 3 | Work order didnt close correctly in eWP |  |  |  | N | NO | <D> **** Detailed Description **** WO 02112006-01 didnt go to the ops closeout screen in dataglance when it was set to finished and released to supervisor. It had to be released in portal J <I> **** Actions Taken **** Contacted IS help desk and talked to an eWP administrator. <N> Analyst received call from IS Duty Officer that user could not perform an Ops review on a package. The package had a status of Supervisor Review (3500) in DataGlance, and H/OPS in Asset Suite. The package should have been displayed on the Operations Review screen in DataGlance, but it wasn't. The Analyst checked the routing records in the database â€“ there was only one approval routing record, which was for the supervisor routing. The user indicated that the package should have gone from working to Ops review automatically. Since there was no Ops routing record, the Analyst initiated one from the Supervisor Completion screen, but wasnâ€™t able submit it. The Analyst couldn't see anything else unusual with the data. Finally, the user indicated that they would go ahead and set the task to FINISHED in Asset Suite. . LSMITH3 Released for Operability in DataGlance on 06/16/19 and was taken to Finished in Asset Suite by JBARTH on 6/15/19.
395568 | CR | 20190615 | CAQ | D | CIA air leaks found during 8.3.49 | Y | N |  | N | YES | <D> CIA leaks need to be fixed on CIA-V-TK/18b regulator outlet 1/4" pipe npt CIA-V-TK/15B 1/4" pipe tee inlet/solenoid side cia-v-tk/15A 1/4" pipe tee inlet cia-v-tk/5a 1/4" pipe tee solenoid side <I> Wrote CR. Informed OPS WC SM and OCC <N> truck bay | 02-00-CIA-V-TK/15A,02-00-CIA-V-TK/15B,02-00-CIA-V-TK/18B,02-00-CIA-V-TK/5A
395569 | CR | 20190615 | CAQ | D | CIA leaks in truck bay during 8.3.49 | Y | N |  | N | YES | <D> Cia leaks need to be fixed on CIA-V-TK/18B REGULATOR OUTLET Â¼â€ PIPE NPT CIA-V-TK/15B Â¼â€ PIPE TEE INLET/SOLENOID SIDE CIA-V-TK/15A Â¼â€ PIPE TEE INLET CIA-V-TK/5A Â¼â€ PIPE TEE SOLENOID SIDE <I> WROTE CR. INFORMED OCC <N> TRUCK BAY | 02-00-CIA-V-TK/15A,02-00-CIA-V-TK/15B,02-00-CIA-V-TK/18B,02-00-CIA-V-TK/5A
395570 | CR | 20190615 | CAQ | D | CIA LEAKS FOUND DURING 8.3.49 | Y | N |  | N | NO | <D> **** Detailed Description **** Cia leaks need to be fixed on CIA-V-TK/18B REGULATOR OUTLET Â¼â€ PIPE NPT CIA-V-TK/15B Â¼â€ PIPE TEE INLET/SOLENOID SIDE CIA-V-TK/15A Â¼â€ PIPE TEE INLET CIA-V-TK/5A Â¼â€ PIPE TEE SOLENOID SIDE <I> **** Actions Taken **** WROTE CR <N> **** Equipment Description **** TRUCK BAY | 02-00-CIA-V-TK/15A,02-00-CIA-V-TK/15B,02-00-CIA-V-TK/18B,02-00-CIA-V-TK/5A
395571 | CR | 20190615 | CAQ | D | RCIC turbine oil level low. | Y | N |  | N | YES | <D> **** Detailed Description **** RCIC trubine oil miniscus is below the add mark. RCIC is currently INOP but the turbine oil level needs to be restored to the NOL per the OPS 2 logs. Please add oil as required. <I> **** Actions Taken **** Notified supervisor. | 02-00-RCIC-DT-1
395572 | CR | 20190615 |  | 4 | MD-V-84 Indicates intermediate | N | N |  | N | YES | <D> **** Detailed Description **** MD-V-84 currently indicates intermediate. The valve should indicate full open or full closed depending upon turbine latched condition. Request maintenance investigate and repair. This is a PPM 3.1.1 required signature item. <I> **** Actions Taken **** SM informed | 02-00-MD-V-84
395573 | CR | 20190615 | CAQ | D | LEFM path 1B8 no signal | Y | Y |  | N | YES | <D> **** Detailed Description **** LEFM path 1B8 has no signal. Both transducers (RFW-FE-3/M, RFW-FE-3/R) were replaced under WO 02138014. Failure of this path was recognized once the appropriate section of SOP-COND-FILL was performed this morning (~1am) to fill the RFW lines. It is possibly unrelated, but one of this pathâ€™s transducers has a broken termination block (ref. CR 394964). Failure of this path limits LEFM to operation in check mode and hence reactor thermal power to 3537MWth. <I> **** Actions Taken **** Discussed with EOC | 02-00-RFW-FE-3,02-00-RFW-FE-3/M,02-00-RFW-FE-3/R
395576 | CR | 20190615 |  | 3 | R24LL CIA to ADS Leak test procedure needs improvement | N | N |  | N | NO | <D> **** Detailed Description **** PPM 8.3.49 (CIA to ADS Valve Air Supply Leak Check) was not originally on the outage schedule and added in later. Its performance has identified multiple leaks that have been fixed, however the test could not be run to conclusion. Feedback from the I&C technicians and the system engineer indicate that improvements need to be made in procedure performance. Recommend that stakeholders get together after the R24 outage and identify improvements to the setup and performance of a test that validates capability of the backup N2 system to ADS to meet design basis requirements.
395577 | CR | 20190615 |  | 4 | Rad Waste Elevator | N | N |  | N | YES | <D> **** Detailed Description **** The Rad Waste elevator door gets stuck while trying to close on the 487 level. The door attempts to close and at 2 inches from full close it will stop and not continue. It ends up being mechanically forced and will operate normally after for a while. It has been stuck twice today on day shift. The elevator operator will activate the call button when stuck which rings in on the 2222 line in the control room. All the control room can hear is the elevator alarm. If an emergency existed, it would be difficult to hear the report over the alarm. This also ties up the 2222 line for actual emergencies if there were any. <I> **** Actions Taken **** CR was created | 02-00-MT-ELEV-4
395578 | CR | 20190615 |  | 4 | HD-RLY-63X2BT/1 COVER CRACKED FREE FROM BASE | N | N |  | N | YES | <C> Found CR at INPROG. Reviewed and approved. <D> WHILE REMOVING HD-RLY-63X2BT RELAY FROM ITS BASE IN E-IR-4 IT CONTACTED THE OUTER COVER OF RELAY HD-RLY-63X2BT/1 MOUNTED DIRECTLY BELOW IT CAUSING THE OUTER COVER TO CRACK FREE FROM THE BASE.RELAY WIRING TO BASE AND CIRCUIT BOARD STILL ELECTRICALLY SOUND BUT NEEDS TO BE EVALUATED. <I> CONTACTED SUPERVISION AND DIRECTED TO WRITE CR.THE COVER IS CURRENTLY BEING HELD IN PLACE WITH TWO SMALL PIECES OF RED DUCT TAPE. INFORMED OPERATIONS ABOUT COVER THAT IS BROKE FREE FROM BASE. <N> RELAY LOCATED IN E-IR-4 SIDE GUTTER ON TG 501' (F.5/ 7 )
395579 | CR | 20190615 |  | 4 | MS-V-234 Posistion Switches | N | N |  | N | NO | <D> **** Detailed Description **** while adjusting limit switches it was discovered that field wiring termination points did not match wiring diagram. This resulted in improper indication in the Main Control Room. <I> **** Actions Taken **** cr initiated proper indication now recieved, after many adjustments. <N> **** Equipment Description **** MS-V-234
395580 | CR | 20190615 |  | 4 | CO2 Fire Suppression Discharge Horn lamp is burned out. | N | N |  | N | YES | <D> **** Detailed Description **** The CO2 Fire Suppression Discharge Horn lamp on the TG 501W is burned out. This lamp is normallly on. Please replace. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 501W
395581 | CR | 20190615 |  | 4 | Exciter housing (doghouse), needs relamp. | N | N |  | N | YES | <D> **** Detailed Description **** The exciter housing has a burned out light in the middle section. Please relamp. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 501W
395582 | CR | 20190615 |  | 4 | SS-V-7B no indication following tag lift. | N | N |  | N | YES | <D> **** Detailed Description **** SS-V-7B no indication following tag lift. Disconnect SS -42-2P6A which is the disconnect for SS-V-7B does not feel like it is closing correctly. Recommend fixing disconnect to see if it fixes the problem. <I> **** Actions Taken **** Wrote Cr Informed CRS | 02-00-SS-V-7B
395583 | CR | 20190615 |  | 4 | HD-QSVâ€™s failed PMT leak checks | N | N |  | N | YES | <D> **** Detailed Description **** While performing leak checks on multiple HD QSVâ€™s leaks were discovered on the following EPNâ€™s; HD-QSV-31A, HD -QSV-32B, HD-QSV-31B and HD-QSV-33A- leaking at body gasket joint. <I> **** Actions Taken **** Mechanics notified supervisor. OCC notified. <N> **** Equipment Description **** 31A- T -482- - -E7/6.3 - 32B-T -482- - -F3/6.1 - 31B-T -482- - -F1/6.2 - 33A- T -486- - -A9/10.6- | 02-00-HD-QSV-31A,02-00-HD-QSV-31B,02-00-HD-QSV-32B,02-00-HD-QSV-33A
395584 | CR | 20190615 |  | 4 | SCW-RMS-P/2 green indicator light broken in socket. | N | N |  | N | YES | <D> **** Detailed Description **** Green indicator light for SCW-P-2 RMS is broken in the socket, light can not be changed out. Requires Elect Maint support. <I> **** Actions Taken **** CR & WR written | 02-00-SCW-RMS-P/2
395585 | CR | 20190615 |  | 4 | Need I&C support to restore from Temporary CW Blowdown | N | N |  | N | YES | <D> **** Detailed Description **** WO 02111561 installs and removes Temporary CW Blowdown. There was a task added (task 13) for I&C support to install temporary flow indications and temporary pH indication per SOP-CW-OPS section 5.9. No I&C support task was added for Temporary CW Blowdown removal per section 5.10. I&C support is needed to perform the removal task. <I> **** Actions Taken **** Informed I&C supervisor, Informed Operations Production Manager | 02-00-CW-PHR-1
395586 | CR | 20190615 |  | 4 | E-RLY- 86XUOA will not reset. | N | N |  | N | YES | <D> **** Detailed Description **** After landing terminal 4 on E-RLY-UNIT/TRIP/2 per SOP -ELEC-BACKFEED E-RLY- 86XUOA will not reset. E-RLY- 86X1UOA will reset momentarily but then trips due to E-RLY- 86XUOA tripping. Lifted terminal 4 back off of E-RLY-UNIT/TRIP/2 due to unkown locked in source and reset E-RLY- 86XUOA and E-RLY- 86X1UOA succesfully with wire determed . The AMT lockout tile on the DEH screen does not illuminate with the wire landed or lifted however H1 .P820.B1 drop 4-6 ANT-MOTORING LO CKT FAILURE alarm is illuminated. Per step 2 of the ARP DEH-RLY-AMT/1 and DEH-RLY-AMT/1 DIGITAL OUTPUT STATUS both show OFF. edna point T529 has shown a state of 1 since May 12. This point typically shows 0 when no lockout exists. Investigate E-RLY- 86X1UOA not being able to reset. This will impact starting the MT and synchronizing the generator. . <N> This CR/WR can be canceled. On DEH screen depressed GEN LOCKOUT RESET display and reset trip. This button also cleared the H13.P820.B1 drop 4-6 ANT-MOTORING LO CKT FAILURE alarm. Wrote CR 00395590 to update ARP and SOP-ELEC -BACKFEED | 02-00-E-RLY-86XUOA
395587 | CR | 20190615 |  | 3 | R24LL: Operational suggestion for cleaning up CSTs | N | N |  | N | NO | <D> **** Detailed Description **** Operational suggestion for cleaning up CST's- While in either Short or Long Cycle cleanup, recommend cycling between drawing water into the hotwell from CST's and rejecting water to the CST's from the hotwell by adjusting Hotwell level control valve automatic setpoint. This will allow water from CST's (which notoriously gets bad toward the end of a refueling outage) to be cycled through the Condensate FIlter Demineralizers, cleaniing up more of the system prior to Reactor startup. <I> **** Actions Taken **** Operational suggestion only
395588 | CR | 20190615 |  | 4 | ASD Genius block RRC-CRM-L31B indication out | N | N |  | N | YES | <D> **** Detailed Description **** While investigating ASD issue related to CR 395550, CR 395551, for ASD input and output transformer alarm, CR 395509 â€œUPS trouble alarmâ€, it was found out that Genius Block, RRC-CRM-L31B located in panel RRC-CP ASD/1 indication is out. Input , output transformer and UPS circuit has common connection to this genius block terminal 9. The probable cause could be common for all three issues and could be because of common connection to genius block. Recommend troubleshooting and replace Genius block as necessary. <I> **** Actions Taken **** Notified EOC. | 02-00-RRC-CRM-L31B
395589 | CR | 20190615 |  | 4 | (NRC) Steam tunnel needs painting on next entry | N | N |  | N | NO | <D> **** Detailed Description **** Inappropriate graffiti was noted on the entry into the steam tunnel during closeout in R24. This graffiti will need to be painted over during R25, or the next FO with steam tunnel access. <I> **** Actions Taken **** Initiated CR.
395590 | CR | 20190615 |  | 3 | PCR: H13.P820.B1 drop 4-6 ANT-MOTORING LO CKT FAILURE | N | N |  | N | NO | <D> **** Detailed Description **** H13.P820.B1 drop 4-6 ANT-MOTORING LO CKT FAILURE alarm ARP needs to be updated to reflect that automatic actions that can take place are the E-RLY- 86X1UOA and E-RLY- 86XUOA will trip. Also in order to clear alarm and reset trip you need to go to the TRIP/FIRST OUT DISPLAY ON DEH SCREEN and depress GEN LOCKOUT RESET display and reset trip. This should also be a note in SOP-ELEC-BACKFEED STEP 6.2.13 when re-landing terminal 4 on E-RLY-UNIT/TRIP/2. Having this reset prior to landing lead prevents E-RLY- 86XUOA from tripping. <N> Also add step to verify anitmotoring trip is reset on DEH screen
395591 | CR | 20190615 | CAQ | C | DW closeout discrepancies | Y | N |  | N | NO | <C> CR Re-opened to add additional notes. <D> **** Detailed Description **** DW closeout per SOP-ENTRY-DW had the following deficiencies: 1) step 6.4.5 lists 4 extinguishers that need to be removed. There were only 3 the one that was not there was the one at C501 160 AZ. 2) There was a piece of permanent metal covered insulation recovered that was found on the C501 near the MSLs that was labeled RWCU-V-1. 3) Two pieces of inslulation were not attached but loose on top of RCIC-V-63. 4) A small yellow poly bag was adrift on the C501 around the MSLs, on the inboard side, but could not be retrieved due to it's location. <N> Further review and investigation determined that the 4th fire extinguisher was removed from the drywell. See docs in EDMS.
395592 | CR | 20190615 | CAQ | D | RFT-P-EOP/1A Rotated backwards on Bump Start Following Work |  |  |  | N | YES | <D> **** Detailed Description **** 250 VDC cubicle RFT-42-S21B3D was replaced under WO 02072952. A bump start rotation check was performed under WOT 0207295210. Based on available documentation it is not clear whether the pump is rotating correctly. Any CAQ is required to have the CR submitted PRIOR to the end of the shift. <I> **** Actions Taken **** Found the appropriate WO to attach to this CR. The OCC, Control Room and OPS production are all informed. | 02-00-RFT-42-S21B3D,02-00-RFT-P-EOP/1A
395593 | CR | 20190615 | CAQ | D | DSA-ENG-C/2C less than half full | Y | N |  | N | YES | <D> **** Detailed Description **** While on operator rounds it was observed that DSA-ENG-C/2C was 7/16 full of diesel. Operator logs require the level to be between half full and full. <I> **** Actions Taken **** Notified CRS ans wrote CR | 02-00-DSA-ENG-C/2C
395594 | CR | 20190615 |  | 4 | Combustible Material <18 inches Below Sprinkler Heads |  |  |  | N | NO | <D> **** Detailed Description **** Per ISPM-10, combustible materials are required to be stored no less than 18 inches below sprinkler heads for the fire protection system. Contrary to this requirement, sixteen items were found resting on top of the cabinets adjacent to the whole body counter (Yakima/GSB). Items included (1) knee pad, (2) boxes of paper water cups, (2) gloves, (2) yellow raincovers, (1) roll of yellow rope, (1) RCA TRIP ticket dated from 2015, (1) piece of paper, (2) lanyard cards, (1) clear orange lanyard attachment, (1) pair of safety glasses, (1) piece of paperwork for Scott Air Packs, and (1) plastic paper tray. <I> **** Actions Taken **** All items were removed. ISPM-10 requirements were covered with technicians working in the area. As left condition is in compliance with ISPM-10.
395595 | CR | 20190615 |  | 4 | Remove FME covers left on piping inside exciter doghouse |  |  |  | N | NO | <D> **** Detailed Description **** Two FME covers are currently installed on piping inside the generator exciter doghouse. The covers are on piping that is not used. The covers need to be removed from the doghouse. <I> **** Actions Taken **** Wrote CR. <N> **** Equipment Description **** MG exciter doghouse - TG 501'
395596 | CR | 20190616 |  | 3 | E538-24 and EWD-63E-095 do not match the field |  |  |  | N | NO | <D> **** Detailed Description **** During implementation of WO 02118080-01 it was identified that the existing as-found field wiring for the limit switch on MS-V-234 does not match the drawings E538-24 and EWD-63E-095. The drawings show that the pink wire should be landed on TP-4 however the wire is landed on TP-6. Recommend AR to AR-DESDFTE to update drawings to match the field. <I> **** Actions Taken **** Discussed with
395597 | CR | 20190616 | CAQ | C | RCIC-P-3 Overloads Tripped. | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of OSP-RCIC/IST-B501 section 7.1, following manual initiation and opening of RCIC-V-13 the RCIC Low Discharge pressure alarm actuated as expected. RCIC-P-3 started and Discharge pressure remained steady at 36 psig on RCIC-PI-604. Per Step 7.16 a fill verification for the RCIC system was briefed and about to leave the MCR to perform when RCIC-P-3 Overload alarm came in. Time between low pressure alarm and overload alarm was Approx. 5 minutes. CRO2 immediately went to investigate. In the MC-7B room a burnt electrical smell was evident. <I> **** Actions Taken **** RCIC-42-7B6C was opened. Visual inspection behind the door showed Thermal Overload red flag dropped. RCIC-P-3 locally was not hot to the touch and had no abnormal indications. RCIC-P-3 did run continuously from 6/7/19 at 0255 to 6/14/19 at 0046 due to O-RCIC-OVSP-R24-001. | 02-00-RCIC-P-3
395598 | CR | 20190616 | CAQ | D | CIA-SPV-1A failed to operate during retest | Y | N |  | N | YES | <D> **** Detailed Description **** while performing OSP-CIA/IST-R702 for PMT it was observed that CIA-SPV-1A/2A/3A did not have there light indicate while the programmer went thru all positions, all other SPVs initiated. Believe that it could be a fuse failer. <I> **** Actions Taken **** initiate CR/WR, inform supervisor. | 02-00-CIA-SPV-1A
395600 | CR | 20190616 |  | 3 | SCW-DPI-1 reading higher than logs require |  |  |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was observed that SCW -DPI-1 was reading 38psig. Logs require between 25 and 30psig. <I> **** Actions Taken **** Notified CRS and wrote CR. <N> The same system pressures were measured in 2017 during startup from R23 (reference CR 331987). Recommend assigning to OPS procedures to revise SOP-SCW-START and OPS and procedures to provide a note explaining the differential pressure can be high following initial start or when the generator is off line. | 02-00-SCW-DPI-1
395601 | CR | 20190616 |  | 4 | TO-LOC-1 differential pressure high |  |  |  | N | YES | <D> **** Detailed Description **** While on operator rounds it was observed that TO-LOC-1 differential pressure was 16.5psig. Operator rounds require differential pressure to be between 0 and 15psig. <I> **** Actions Taken **** Wrote CR and notified CRS | 02-00-TO-LOC-1
395603 | CR | 20190616 |  | 4 | SS-V-7B Has no indicating lights and disc is loose. |  |  |  | N | YES | <D> **** Detailed Description **** The disconnect for SS-42-2P6A has sloppy operation and the light on BD A are out. Please investigate. | 02-00-SS-42-2P6A,02-00-SS-V-7B
395605 | CR | 20190616 | CAQ | D | RFW-FE-3 Manifold Cover Issues | Y | Y |  | N | YES | <D> During WO#02138014-10, the manifold cover for RFW-FE-3 8Down path was found to have several deficiencies: 1. The lower right bolt was found to be broken off. The shank of the bolt is seized in the hole. 2. The lower left bolt has been crossthreaded at some point in the past and was unable to be reinstalled. 3. The manifold cover sealing O ring was absent. These issues do not affect the function of the LEFM system directly, but may cause degradation of the signal paths over time. <I> Notified supervision and EOC. Ordered new bolt (screw) to replace the cross threaded one. Working with EOC to develop a plan for the cover gasket seal. . Found in INPROG status, moved forward. . | 02-00-RFW-FE-3
395606 | CR | 20190616 |  | 4 | BS-DV-2A2 did not open during SOP-FWH-INTERLOCK-TEST |  |  |  | N | YES | <D> **** Detailed Description **** During the performance of SOP-FWH-INTERLOCK-TEST, BS-DV-2A@ did not move from full closed when HD-LS-2AHT was actuated. BS-DV-2A2 should have gone full open. BS-DVSPV-2A2 was not hot to the touch. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-BS-DV-2A2
395607 | CR | 20190616 | CAQ | D | RFW-FE-3 Manifold Cover Issues | Y | Y |  | N | YES | <C> Duplicate CR 395605 <D> **** Detailed Description **** During WO#02138014-10, the manifold cover for RFW-FE-3 8Down path was found to have several deficiencies: 1. The lower right bolt was found to be broken off. The shank of the bolt is seized in the hole. 2. The lower left bolt has been crossthreaded at some point in the past and was unable to be reinstalled. 3. The manifold cover sealing O ring was absent. These issues do not affect the function of the LEFM system directly, but may cause degradation of the signal paths over time. <I> **** Actions Taken **** Notified supervision and EOC. Ordered new bolt (screw) to replace the cross threaded one. Working with EOC to develop a plan for the cover gasket seal. | 02-00-RFW-FE-3
395608 | CR | 20190616 | CAQ | D | CSP-V-800/26 difficult to operate | Y | N |  | N | YES | <D> **** Detailed Description **** CSP-V-800/26 was very difficult to operate, and was only able to be opened 2-3 turns. Additionally, there was a significant amount of slack in the yoke bushing (about 1 turn, and the bushing was observed to move while operating), and some pieces of debris fell out of the area between the handwheel and yoke bushing while operating. CSP-V-800/26 has been restored to locked closed and capped, pictures of the debris in EDMS. <I> **** Actions Taken **** Informed supervision, generated AR/WR. Pictures in EDMS. | 02-00-CSP-V-800/26
395609 | CR | 20190616 | CAQ | D | E-FUSE-IR67/TB2F17 Clearing | Y | N |  | N | YES | <D> **** Detailed Description **** E-FUSE-IR67/TB2F17 supplies power to CIA-SPV-1A, -2A, -3A and their indicating lights on CIA-CP-1 (see EWD-24E-005B). Fuse was replaced per PPM 1.3.47 and amber lights lit on CIA-CP-1 for CIA-SPV-1A, -2A and -3A. When the programmer CIA-PROG-1A cycled back to CIA-SPV-1A following reset, none of the lights for CIA-SPV-1A, -2A or -3A lit. Remaining SPV lights lit as expected. <I> **** Actions Taken **** E-FUSE-IR67/TB2F17 is an F09B 250 V 5A fuse. | 02-00-CIA-CP-1,02-00-CIA-PROG-1A,02-00-E-FUSE-IR67/TB2F17
395610 | CR | 20190616 |  | 4 | MD-V-81, 83, 84, 85, 86, and 87 issues |  |  |  | N | YES | <D> **** Detailed Description **** MD-V-83 WR 29149734: Valve has so much internal friction that the valve isnâ€™t returning to open. It has a regulator setting of 37psi and currently the Heise guage/regulator setup is installed for testing on the diaphragm. The AMDS is has incorrect data such as the stroke length, serial number, and bench set. This needs resolved for functional OR diagnostic testing. A markup copy is in the WR package. I recommend looking at the dataglance work order we did this outage. â€¢ MD-V-84 WR 29149696: The valve stem connector (marriage block) is missing. This is why the valve doesnâ€™t stroke because the stems arenâ€™t coupled together. Also, the limit switch trip plate is missing. My guess is they both got thrown away in the massive cleanup. The valve rebuild work order (see dataglance) had a note that it was left uncoupled for testing. Since Devon cancelled their flowscan task, now we sit with missing parts and a valve that doesnâ€™t work. The AMDS is has incorrect data such as the stroke length, serial number, and bench set. This needs resolved for functional OR diagnostic testing. A mark up copy is in the WR package. â€¢ MD-V-81, 85, 86, 87 valves were left with either 50 or 100% packing torque and the stroke lengths not set. These valves will either leak externally via packing, not stroke because they were never setup, and or leak internally if we donâ€™t perform functional (or diagnostic testing) per PPM 10.24.235. This is due to the flowscan testing tasks cancelled and the mech shop assumed these tests would happen. My recommendation is to have I/C perform the flowscan testing on all the valves. Especially since the work orders are already done for them. We still need parts for MD-V-84. <I> **** Actions Taken **** Notified OCC and emergent work manager, initiated CR | 02-00-MD-V-81,02-00-MD-V-83,02-00-MD-V-84,02-00-MD-V-85,02-00-MD-V-86,02-00-MD-V-87
395611 | CR | 20190616 | CAQ | C | R24 â€“ RFT-M-EOP/1A Rotated CW TT Elementary Shows CCW |  |  |  | N | YES | <D> **** Detailed Description **** When performing WO 02072952-10 Bump RFT-P-EOP/1A to verify correct motor rotation, the bump concluded that motor RFT -M-EOP/1A rotated in the clockwise direction. Top Tier Elementary Diagram E526-3 Zone B/3-5 states that the rotation is counterclockwise. Since other R24 work has experienced swapped motor lead errors, the Work Order Task was revised to swap wires to have the motor rotate in the counterclockwise direction. When performing another bump the motor did not run at all. <I> **** Actions Taken **** Informed the OCC/EOC. Researched CVI OMM 12-00,16. Took photographs of nameplate data that has model A3DBC- 137 embossed on the nameplate. This model number was compared to Figure1 Definitions of Model Designators from the OMM which concluded that the motor does in fact rotate clockwise. Validation of the OMM and nameplate data also concluded that the pump also rotates clockwise. Revised the work order to swap the wires back the way they were since the previous bump task validated that the motor did rotate clockwise. Note that E520-3 Zone B/13-14 for TO-P-EOP has the same rotation statement that was also confirmed to be incorrect. See photo and PDF in the AR EDMS. . Recommend this action be assigned to AR-DESDFTE to revise E526-3 and E520-3. <N> **** Equipment Description **** This is rework being addressed by WO 02072952. | 02-00-RFT-42-S21B3D
395612 | CR | 20190616 |  | 4 | Oil leak from TO-FLT-1A |  |  |  | N | YES | <D> **** Detailed Description **** When starting RFT-A lube oil a leak from the upper flange of TO-FLT-1A was discovered. The leak was sufficiently large to require AOP and MOP shutdown. <I> **** Actions Taken **** Informed CRS/SM | 02-00-TO-FLT-1A
395613 | CR | 20190616 |  | 4 | SEC-XD-4 Out of Service due to Power Failure in PAAP/PEC |  |  |  | N | YES | <D> **** Detailed Description **** At approx midnight on 6/16/2019 there was a power failure to the PAAP and Descuttes buildings which caused the PAAP generator to start. Power was restored to the search area when the generator started , however Explosive Detector #4 did not power back on. <I> **** Actions Taken **** OCC, Shift Manager and Facilities were contacted. Security conducted operability testing on search area equipment. I&C support will be needed to look into the power issue with XD-4 | 02-00-SEC-XD-4
395616 | CR | 20190616 |  | 4 | Air leak MD-TC-4B regulator |  |  |  | N | YES | <C> Found at INPROG. Reviewed and approved. <D> Air leak on the copper fitting going into the regulator. Piping seams bent going into fitting. <I> CR . Found in INPROG status, moved forward. . | 02-00-MD-TC-4B
395617 | CR | 20190616 |  | 3 | Procedure enhancment SOP-TSW-LU |  |  |  | N | NO | <D> **** Detailed Description **** TSW-V-270E through H and TSW-V-692 do not seem to exist. We were unable to find these valves in the plant or on any drawing. Also unable to find an EC removing these valves. Two ARs reference a change to this portion of TSW but do not directly mention these valves. AR 4500 AR 4337. Recommend revising the procudere <I> **** Actions Taken **** Informed CRS/SM
395618 | CR | 20190616 |  | 4 | Normal Emergency Lighting | N | N |  | N | YES | <D> **** Detailed Description **** W/O# 02111932-01, While performing PPM 10.25.64 attatchment 9.11, Fixture 1 had its quartz lamp replaced and during testing when the HID fixture lamp came back on the quartz lamp should have gone out but didnt. <I> **** Actions Taken **** Re-performed test per ppm 10.25.64 (failed to extinguish again) notified supervisor of the issue, intiated CR <N> **** Equipment Description **** Heater bay Fixture 1 per ppm 10.25.64
395619 | CR | 20190616 |  | 4 | GY-F-10A1 Charcoal filter glycol leak | N | N |  | N | YES | <D> **** Detailed Description **** GY-F-10A1 Charcoal filter has an O-ring leak. Prior to RRC-P-1A start, an Operator noticed the drip tray under the filter assembly was full of glycol. Identified leak rate was approximately 1-2 drops/min. After monitoring for a few minutes, about 15-20 drops fell at once, all off of the filter assembly handle. The leak rate then slowed down again. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-GY-F-10A1
395621 | CR | 20190616 |  | 3 | SOP-COND/RFW-LU needs revision |  |  |  | N | NO | <D> **** Detailed Description **** SOP-COND/RFW-LU includes valves that have been removed. Portal J shows the status for the following valves as DEFUNCT: RFT-V-25B, RFT-V-26B, RFT-V-27B, RFT-B-28B, RFT -V-29B. These valves should be removed from the lineup procedure when the next revision is issued, see page 26 of SOP-COND/RFW-LU . This is not urgent and will not prevent MODE 2 transition. <I> **** Actions Taken **** Wrote this CR.
395623 | CR | 20190616 |  | 4 | RFW-TE-55A broken | N | N |  | N | YES | <D> **** Detailed Description **** RFW-TE-55A broken. It appears this element was stepped on and the wiring is exposed from the conduit <I> **** Actions Taken **** contacted supervision and wrote this CR/WR | 02-00-RFW-TE-55A
395624 | CR | 20190616 |  | 4 | Phone in TG 471' (X 2686) by Bypass valves, no ringback. | N | N |  | N | NO | <D> **** Detailed Description **** Craft paged and were awaiting a call back...craft paged mulitple times then called different people in which someone answered which identified the installed phone at X2686 int eh TG 471' Heater bay has no audiable ringback. <I> **** Actions Taken **** Notified OCC for phone not having ringback as craft were awaiting a call back. <N> **** Equipment Description **** Phone in Heater bay by bypass valves at X2686.
395625 | CR | 20190616 |  | 3 | SOP-FWH-LU needs revision |  |  |  | N | NO | <D> **** Detailed Description **** Pages 53 and 54 need revisionsto EPNs starting at BS-V-8A and continuing through HD-V-33B. The lineup should be identifying the SPVs. <I> **** Actions Taken **** Wrote this CR to initiate the procedure change.
395626 | CR | 20190616 | CAQ | D | SRM C fast period erroneous alarms | Y | Y |  | N | YES | <D> **** Detailed Description **** SRM C fast period alarms are erroneously coming in 5-6 times an hour. The alarm appears to be coming in at the same time as the SR 21 alarms while I&C was testing the sample rack. It is unclear why these alarms are coming in together. This alarm is P603-A7 tile 5-6. <I> **** Actions Taken **** Wrote CR Informed CRS | 02-00-SRM-DET-1C
395627 | CR | 20190616 |  | 3 | Personal Protective Clothing are Turning Shoes/Socks Yellow |  |  |  | N | NO | <D> **** Detailed Description **** -The new yellow booties worn into Contaminated Areas are bleeding the yellow color onto Radworkers Shoes/Socks/Pants. This needs to be addressed . A new style is currently being used that are thinner compared to the previous style. <I> **** Actions Taken **** -Notified Supervision -Initiated Condition Report
395628 | CR | 20190616 |  | 4 | while performing W0# 021295704 PPC computer issues | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** On Sat. 6-16-19 I had to perform a computer point calibration and found about 6 muxâ€™s red on PPC The 8715 error light was on reset the system and on the OS90 it would hang when starting CVT, Disk & Events It was hanging up on starting and stopping (Disk) The system came up and is green the U1 screen for now and was able to perform the loop/computer adjustment. <I> **** Actions Taken **** Notified supervisor and computer engeneering via E-Mail No ERDS impact. <N> Assignment -01 cancelled because this CR is a duplicate of CR 393415.
395629 | CR | 20190616 |  | 3 | TSW-PCV-20 IMDS/AMDS VALUES NOT CORRECT AS PER ENGINEERING | N | N |  | N | YES | <D> **** Detailed Description **** while performing 02120309-05 we found that TSW-PCV-20 valve stroke does not match IMDS/AMDS. <I> **** Actions Taken **** Mike Rhodes asked us to write CR to evaluate. <N> There is no issue with the valve's function at 67% open per the AOV engineer. The valve does not operate above 67% open during normal operation. This is a legacy documentation issue that results in valve setup limiting travel to 67% open. | 02-00-TSW-PCV-20
395630 | CR | 20190616 |  | 4 | BS-DV-2A2 will not open from the MCR | N | N |  | N | YES | <D> **** Detailed Description **** BS-DV-2A2 will not open with the pushbutton in the MCR | 02-00-BS-DV-2A2
395631 | CR | 20190616 |  | 4 | Floor needs to be painted between 6A and the 6B FW heaters |  |  |  | N | NO | <D> **** Detailed Description **** The floor has degraded from the RFW-V-10B water leak. The repair should be scheduled during the R-25 outage or a long forced outage. <I> **** Actions Taken **** (1) Informed supervision (2) Wrote this CR. (3) Informed the ENW painters. (4) I have pictures. <N> **** Equipment Description **** Floor directly underneath RFW-V-10B.
395632 | CR | 20190616 |  | 4 | HD-V-32D has no position indication | N | N |  | N | YES | <D> **** Detailed Description **** HD-V-32D has no position indication in the MCR or at IR-16. <I> **** Actions Taken **** Replaced bulbs in the MCR, verified no indication at the IR <N> reopened / closed to adjust the RXSU coding. | 02-00-HD-V-32D
395633 | CR | 20190616 |  | 4 | HD-V-31D has no position indication | N | N |  | N | YES | <D> **** Detailed Description **** HD-V-31D has no position indication in the MCR or at IR-16. <N> reopened / closed to adjust RXSU coding. | 02-00-HD-V-31D
395634 | CR | 20190616 |  | 4 | R24LL - EOC Manager phone x8558 should be disconnected | N | N |  | N | NO | <D> **** Detailed Description **** For R24, the EOC Manager position was eliminated from the EOC manned positions but the EOC Manager phone number (i.e., x8558) was not disconnected / eliminated. During R24, OCC and station personnel often called x8558 rather than the phone number of the actual person in the EOC that they knew they wanted / needed to talk to (i.e., x8519 for System Engineering Supervisor, x8433 for Design Engineering Supervisor, or x6075 for Technical Services Supervisor). . For future outages, x8558 should be disconnected or eliminated if the EOC Manager position will not be manned in the EOC. <N> During R24 when personnel called x8558, there was a 1 in 3 chance they would actually reach the EOC Supervisor they wanted / needed to reach. This was an unnecessary inefficiency. Reopened to add the following notes from Sys Eng Mgr: Eng will not be disabling this number for EOC. That was finalized in the EOC 4.0 critique.
395636 | CR | 20190616 | CAQ | D | CRD-HCU-1419 alarm on low N2 pressure in early. | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-1419 alarmed on low N2 pressure at 1020 psig. Recommend recalibrating pressure switch. <I> **** Actions Taken **** Notified supervisor and recharged HCU 1419. <N> **** Equipment Description **** Rx 522 | 02-00-CRD-HCU-1419
395637 | CR | 20190616 |  | 4 | R24LL -Engineers Allowed to go on business trips in R24 | N | N |  | N | NO | <D> **** ANONYMOUS CR - Detailed Description **** Despite an all-hands on deck mantra for R24, several Engineers were allowed to go on company busiiness trips during R24. Some absences were of no impact, others were of great impact and potentially resulted in work being deferred (MG ground brushes) or work being complicated and extended (MG Air Test). This is of no fault of the Engineers, but station leadership who decided the trips were of more importance than the outage. <I> **** Actions Taken **** None required <N> Reivewed and sent on for processing. - The two instances noted in this CR are characterized to be of great impact as a direct consequence of the System Engineer being absent (offsite) while performing work on the Main Generator Ground Brushes and during performance of SOP-GEN-AIRTEST. For the sake of clarity, the following facts are provided as of means of adequately capturing the R24LL from these two work tasks: -Main Generator Ground Brushes: WO 02111831-13 was not properly planned to perform a ground brush system replacement with brush-to-shaft realignment, the work instructions had no detail for the work just simple steps to remove and reinstall. In addition, the work order was assigned to Siemens when it should have been assigned to plant electricians who would have identified the lack of instruction during the walkdown. The mounting hardware for the brush holder assembly and mounting plate are not easily accessible (hardware has the potential to be become FME) and there are open questions on how to properly perform this activity. The deferral of this work has to do with planning and preparation for the scope of the task, and has nothing to do with the System Engineer being physically offsite on the date(s) of implementation. -Main Generator Air Test: During performance of SOP-GEN -AIRTEST, engineering support was provided as needed or directed by the procedure. Engineering obtained field data at ~4 hour intervals during the test, observed higher than expected leak rates over the 24 hour period, determined that the Hydrogen skid was a primary source of leakage and recommended isolating the Hydrogen Skid while maintaining the system pressurized for an additional 8 hours to determine a more precise representation of Main Generator leakage. This confirmed a lower, more representative calculation of leakage attributable to the Main Generator. SOP-GEN-AIRTEST should be performed by OPS with engineering in a support function. Operations handed this procedure to Siemens to perform which resulted in requiring additional engineering support as Siemens does not normally implement plant operating procedures. - Engineering support of the work activities mentioned was vigilant and timely - any insinuation that work delays or deferrals incurred during R24 are attributable to the absence of 1 specific individual is an exaggeration of the reality of the situation and an affront to the Operations, Maintenance, and Engineering teams actively engaged and directly supporting the successful implementation of R24 scope.
395638 | CR | 20190616 |  | 3 | EWD Drawing Update Required |  |  |  | N | NO | <D> **** Detailed Description **** During investigations for the cause of CRA-FN-1A2 trip (AR CR 394038) it was discovered that EWD-23E-002 requires to be updated. Back in 2003, AR EVAL 4253 was initiated to change fuses and overloads for Non-1E CRA fans. All CRA -FN-1A2 100amp fuses were replaced with new 90 amp fuses under WO# 01096012 on 5/10/2005. The purpose of this CR is to revise drawing EWD-23E-002 so it matches what is installed in the plant. There is NO operation concern to the equipments involved and NO POD is required. It would be important to check on other associated drawing of the components involved in the MALT. The EPNs included CRA-M-FN/1A1, CRA-M-FN/1A2, CRA-M-FN/1B1, CRA-M-FN/1B2, CRA-M-FN/1C1, CRA-M-FN/1C2, CRA-M-FN/2A1, and CRA-M-FN/2B1. <I> **** Actions Taken **** Notified SM, EOC and initiated this CR
395639 | CR | 20190616 |  | 3 | SOP-MT-OIL-OPS P&L Conflict with TO-P-BOP Mod |  |  |  | N | NO | <D> **** Detailed Description **** SOP-MT-OIL-OPS P&L conflict with WO 02145446-03. SOP-MT -OIL-OPS requires TO-EX-1A, 1B, 4A, 4B to be running when hydrogen is in the main generator. TO-EX-1A(1B) are required to be off when securing the bearing oil pump to prevent high level flood out of the exhauster. Recommend clarification on P&L for this condition. Reference P&L 4.2, 4.3, and 4.4. <I> **** Actions Taken **** Engaged engineering to help clarify the requirement. Notified the OCC. Recommend procedure change to clarify P&L. <N> System Engineering has concluded that the two vapor extractor systems have differing roles and only the TO-EX-4A and 4B are required for Generator operation based on language in two separate parts of the OEM operations document.Â In addition, a representative from Siemens was consulted and they agree that the generator seal oil system is made to operate independent of turbine lube oil. -Engineering (Proper names removed) SD Metzger 6/17/19
395640 | CR | 20190616 |  | 4 | COND-RV-184 leaking | N | N |  | N | YES | <D> **** Detailed Description **** COND-RV-184 (RV on Condensate supply to CRD) was found leaking at apporximately 0.5 gpm. <I> **** Actions Taken **** Notified Main Control Room and supervision, initiated this CR. | 02-00-COND-RV-184
395641 | CR | 20190616 |  | 4 | MD-V-84 upper limmit switch not resetting | N | N |  | N | YES | <D> **** Detailed Description **** During consolidation and testing on MD-V-84, found that the upper limit switch would not reset. <I> **** Actions Taken **** Informed OCC, Wrote WR to correct issue/replace switch | 02-00-MD-V-84
395644 | CR | 20190616 |  | 3 | Potential procedure conflict leads to unclear performance |  |  |  | N | NO | <D> **** Detailed Description **** On 06/15/2019, the drywell was being up-posted to a very high radiation area (VHRA) in preparation for running the TIP detectors. The LHRA locks were removed from the personnel and equipment hatches and replaced with VHRA locks. Security locks were present on the hatches, providing two independent locks. This was in compliance with PPM 11.2.7.3 section 6.6.1(a); however, this was not in compliance with section 6.6.4 of the same procedure. Section 6.6.4 requires both a LHRA lock and a VHRA lock to be present on VHRA doors or gates. PPM 11.2.7.3 should be revised to align these two steps. <I> **** Actions Taken **** Upon identification, the LHRA locks were re-placed on the hatches to restore compliance with PPM 11.2.7.3. VHRA locks were present and controlled by HP at all times. This appears to be an administrative issue - control for the personnel and equipment hatches were adequate to prevent unauthorized entry into the drywell.
395645 | CR | 20190616 |  | 3 | Calibrated test equipment destroyed |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During cleanup activities on the 501â€™ reactor building elevation it was noticed that Calibrated test equipment was destroyed. Thermocouples attached to a fluke module were cut and discarded. This was a calibrated set of thermocouple wires. These thermocouple wires were ran into a CA for leak rate MSIV testing and these wires needed to be de-conned and returned to I&C. It appears that another work group cut these wires which in turn requires more time and money to re-create this test equipment. This could potentially impact the test results of the MSIV Leak rate testing due to these wires being unable to be post-test verified by the Calibration lab. See attached pictures. Contact Jim Cantrel for WOT numbers. <I> **** Actions Taken **** Notified supervision and manager wrote this CR <N> **** Equipment Description **** calibrated Test equipment . 11/191/19 EFIN has perfromed an evaluation on the damaged equipment. The M&TE was not damaged however the equipment was still connected to thermocouple wires and collecting data. No further evaluation required and as EFIN noted there was no impact to sfaety related systems.
395646 | CR | 20190616 |  | 3 | SOP-CW-OPS procedure revision required |  |  |  | N | NO | <D> **** Detailed Description **** SOP-CW-OPS step 5.9.3 directs placing caution tags on temporary instruments and temporary power when establishing temporary blowdown. Section 5.10 which removes the instruments and power does not remove the caution tags. The caution tags should be removed after step 5.10.7.e.2. <I> **** Actions Taken **** Initiated CR. E-mailed the Ops Procedure group supervisor.
395647 | CR | 20190616 |  | 4 | calibrate computer point F029 |  |  |  | N | YES | <D> **** Detailed Description **** RFW-P-1A pump casing metal temp computer point looks like it needs calibrtion. Ambient pump casing temperature is 75 Deg F; RFW-TR-1 point 5 reads 76 Deg F; computer point F029 reads 70 Deg F. Instrument Master Data sheet says the temperature should be +/- 4 Deg F between elements. <I> **** Actions Taken **** wrote this CR <N> **** Equipment Description **** computer point F029
395648 | CR | 20190616 |  | 4 | OG-RC-5B Heater Does Not Energize |  |  |  | N | YES | <D> **** Detailed Description **** The â€˜Bâ€™ OG Recombiner heater does not turn on when the heater switch is turned to ON. OG-TC-2B does not appear to be energized, indicating that a fuse is possibly cleared. The power supply PP-3CA ckt 9 was verified shut. The green OFF light for OG-RC-5B heater is lit. | 02-00-OG-RC-5B
395650 | CR | 20190617 |  | 3 | OG-TC-2B Repeated Failures |  |  |  | N | YES | <C> MRT Change request: CR 395650 moved from 4/Trend Repair to Severity 3 and assigned to AR-SEBOP. "To look at repeat failures" <D> **** Detailed Description **** OG-TC-2B has been replaced three times since 2009. Separately, the fuse associated with it has blown 3 times in the same period. The controller is obsolete, and difficult to acquire. <I> **** Actions Taken **** Engineering needs to evaluate what is causing these repeated failures of important plant equipment, and find a viable long term solution. Also, they should look at OG -TC-2A. It has a similar history. | 02-00-OG-TC-2A,02-00-OG-TC-2B
395651 | CR | 20190617 |  | 3 | RFW-DT-1A & RFW-DT-1B oil filter pm needs PMT |  |  |  | N | YES | <D> **** Detailed Description **** While performing maintenance on TO-FLT-1A/1B on the A feed water system and 1C/1D on the B feed water system there is no post maintenance testing on either system. These filters have been an issue in the past with leakage around the top gasket area and require a re-torque. A PMT task should be created for mechanics to work with operations during startup of these system and to allow a re-torque to stop any identified leakage. We should also figure out what a maximum torque allowable with the new style of gaskets being used. <I> **** Actions Taken **** Notified control room and planning of the issue and notified my supervisor. Recommend planning add PMT task to both filter units | 02-00-TO-FLT-1A
395652 | CR | 20190617 |  | 4 | MS-V-TV/4 trip return line leaking ~60 drops per minute |  |  |  | N | YES | <D> **** Detailed Description **** Throttle valve 4 trip header return line O-Ring protruded and leaking ~60 drops per minute. This is not isolable on line, would require multiple valve isolations to isolate, may be best to secure the DEH system to correct. <I> **** Actions Taken **** DEH is leaking onto the floor, actions taken to limit the progression of the leakage to floor drains. Pictures in EDMS. | 02-00-MS-V-TV/4
395653 | CR | 20190617 |  | 4 | RFW-DT-1A turning gear causing high vibes |  |  |  | N | YES | <D> **** Detailed Description **** The RFW-DT-A turning was locked wired to remain engaged and its now causing high vibes. Upon investigation, you can see that its trying to disengage. <I> **** Actions Taken **** Informed MCR | 02-00-RFW-DT-1A
395654 | CR | 20190617 |  | 4 | OG-RF-20A failed to start on system startup |  |  |  | N | YES | <D> **** Detailed Description **** OG-RF-20A failed to start on step 5.3.14 of SOP-OG-START. Low oil pressure trip reset was pressed, but it still did not start. Currently has full oil level in the sightglass. <I> **** Actions Taken **** Informed supervision. Wrote CR. | 02-00-OG-RF-20A
395655 | CR | 20190617 |  | 4 | OG-RF-20C shut down early |  |  |  | N | YES | <D> **** Detailed Description **** While performing SOP-OG-START section 5.3.16, OG-RF-20C shut down unexpectedly after running for about three minutes. After it shut down the oil level in the sight glass was observed to be empty. After the oil level returned to about 1/8 full in the sight glass the (low compressor oil press shutown reset push button (GY-PS -20C3) was depressed and the compressor restarted for about a minute and then shutdown again. The oil level in the sight glass before the system was started was totally full. <I> **** Actions Taken **** Wrote CR and informed SSS | 02-00-OG-RF-20C
395656 | CR | 20190617 |  | 4 | RFT-AO-TNG/1A not engaging turning gear |  |  |  | N | YES | <D> **** Detailed Description **** Air cylinder configuration does not allow the proper engagement of the turning gear, it is about Â½â€ short of having the ability to fully engage the turning gear and in the past has had to be tied back with tie wire multiple times to allow the turbine to be rolled on the turning gear mechanism. These air cylinders have been problematic over the years and need to be addressed to be controlled automatically. <I> **** Actions Taken **** Notified the main control room and my supervisor. Suggest adding a bronze threaded bushing on the end of the ram to compensate for the length needed to engage the turning gear. <N> AR type EVAL needed? | 02-00-RFT-AO-TNG/1A
395657 | CR | 20190617 |  | 4 | RFT-AO-TNG/1A not engaging turning gear |  |  |  | N | YES | <D> **** Detailed Description **** Air cylinder configuration does not allow the proper engagement of the turning gear, it is about Â½â€ short of having the ability to fully engage the turning gear and in the past has had to be tied back with tie wire multiple times to allow the turbine to be rolled on the turning gear mechanism. These air cylinders have been problematic over the years and need to be addressed to be controlled automatically. <I> **** Actions Taken **** Notified the main control room and my supervisor. Suggest adding a bronze threaded bushing on the end of the ram to compensate for the length needed to engage the turning gear. <N> AR type EVAL needed? | 02-00-RFT-AO-TNG/1B
395658 | CR | 20190617 |  | 4 | R-24 LL Janitorial needs to be throughout the entire outage |  |  |  | N | NO | <D> **** Detailed Description **** R-24 is not complete, yet the janitorial staffing for night shift seems to have ended. There are still 175 people on site supporting night shift for the outage with less than adequate cleanliness. This lack of resources seems to have been a trend the entire outage and should be addressed for R-25 <I> **** Actions Taken **** Notified my supervisor and initiated the CR
395659 | CR | 20190617 |  | 4 | COND-P-2B Needs Oil Added |  |  |  | N | YES | <D> **** Detailed Description **** COND-P-2B is low (approx 1/4) and needs oil added | 02-00-COND-P-2B
395660 | CR | 20190617 |  | 4 | OG-RF-20B refrigerant low in sightglass |  |  |  | N | YES | <D> **** Detailed Description **** While performing SOP-OG-START section 5.3.15 it was observed that the refrigerant piping sight glass was only half full while OG-RF-20B was running. This may be normal or not. The refrigerant piping sightglsss for OG-RF-20C was totally full while it was running. <I> **** Actions Taken **** Wrote CR and informed SSS | 02-00-OG-RF-20B
395661 | CR | 20190617 |  | 4 | COND-P-2A Needs Oil Added |  |  |  | N | YES | <D> **** Detailed Description **** COND-P-2A oil sump level is low and requires oil addition. | 02-00-COND-P-2A
395662 | CR | 20190617 |  | 4 | Cond-DM-1A has leakby past its boundry valves to CPR-TK-14 |  |  |  | N | YES | <D> **** Detailed Description **** Cond-V-210A on Cond-DM-1A was rebuilt and the clearance order lifted. The fill/vent procedure was performed with PMT and Instrument vents. CPR-TK-14 had a level increase of several thousand gallons during the instrument venting with Cond-V-210A open to provide the pressure. The intrument venting adds a tiny amout of water. Cond-V-210A was open a few extra hours due to paperwork issues. The only way we could have this kind of level rise is leakage from one of Cond-DM-1A's boundry valves. A backwash was performed after the F/V. It seemed normal. At the start of the Precoat procedure, it was noted that it took significantly longer to repressurize the Backwash header. (1.5-2 min vs a few seconds). Backed out of Precoat Procedure. | 02-00-COND-DM-1A
395665 | CR | 20190617 |  | 4 | RFW A feed pumps room housekeeping/oil on lagging | N | N |  | N | YES | <D> **** Detailed Description **** Housekeeping issue in RFP A pump room include insulation (calcite) chunks dust all over top of turbine oil reservoir. Insulation duct taped to steam piping that will be ot today, tools, old oil spray covers, and miscellaneous equipment. Additionally, oil soaked lagging still exists on the pump casing lower half. This was supposed to be replaced by WO 0214424202 (at finished) but several peices are still on the turbine with significant oil impegregnated. The pump will be placed in service in the next day and the area will become a high rad area within a few days. become a high rad area. <I> **** Actions Taken **** Notified OCC Discussed with Ops OCC Manager regarding replacement of oil impregnated lagging prior to starting up RFW-P-1A. <N> 1) Williams (WPS) did not remove any Cal-Sil insulation in this room. But, there were some chunks and dust that was cleaned up by our Insulators when they went in there to evaluate this cndition. 2) The red duct tape was installed by others. The duct tape is holding the oil pigs to the piping. We think this was Siemens. 3) Williams (WPS) removed and replaced all of the insulation pads that were identified by the Fire Marshal a few weeks ago. He marked all of the insulation pads that he thought needed to be replaced, based on how oil soaked they were. They were marked with a red X. Goeff Schneider was there on night shift when the FM did his evaluation and identification. 4) None of the tools in the room belong to WPS. | 02-00-RFW-P-1A
395666 | CR | 20190617 |  |  | Temp Diesel TO-P-EOP leaking collant |  |  |  | N | NO | <D> **** Detailed Description **** The south temporary diesel generator stagged by the CST tanks appears to have a coolant leak. This leak is approx 3-4 cups and I could not determine if it is an active leak. The leak is into a bermed area and NOT to the ground. This DG is stagged for back up power to TO-M-BOP. . Verified not leak. canceled <I> **** Actions Taken **** Notified OCC. <N> I walked down the leak. Fluid does NOT come from inside the diesel engine itself. This was spilled diesel fuel that most likely occured when the engine was recently filled with fuel.
395667 | CR | 20190617 |  | 4 | Nitrogen addition required in E-TR-1/11 | N | N |  | N | YES | <D> **** Detailed Description **** Nitrogen level in E-TR-1/11 is low and requires addition | 02-00-E-TR-1/11
395668 | CR | 20190617 |  | 4 | MS-TCV-116C Regulator air leak | N | N |  | N | YES | <D> **** Detailed Description **** Air operator regulator has two air leaks. one is on the upply line to the regulator (west side of regulator) compression fitting leaking, and the body gasket is leaking on east side of regulator. Refer to WR 29149581 | 02-00-MS-TCV-116C
395670 | CR | 20190617 |  | 3 | Records Submitted without signed Transmittal | N | N |  | N | NO | <D> **** Detailed Description **** A Record was submitted to Records Control without a signed transmittal form. Please Refer to SWP-REC-02 Section 4.3.2 for the proper submittal process. <I> **** Actions Taken **** Notified my supervision. Sending Records back to Facilities for transmittal correction and re-submittal.
395671 | CR | 20190617 |  | 3 | Steam Tunnel camera damaged | N | N |  | N | YES | <D> **** Detailed Description **** The steam tunnel camera was inadvertenly removed from the steam tunnel during cleanup. The error was caught and the camera was returned to the steam tunnel. The removal or replacement damaged the camera. The camera still functions currently, but it appears to have a damaged gear for horizontal movement. Moving the camera on the horizontal plain a obvious stutter/stall is observed. <I> **** Actions Taken **** Worked with HP to verify the camera was reinstalled in the steam tunnel and that the camera was orientated correctly. During verification, the issue was found. <N> **** Equipment Description **** Steam Tunnel 501 level Discussed with OCC. Turned over to emergent work management. Tied to 1000# steam tunnel entry for replacement.
395672 | CR | 20190617 |  | 3 | IS systems not communicating as expected | N | N |  | N | NO | <D> **** Detailed Description **** Examples: Search D080 in portal J for the ESP-RPS-B301. Given that the surveillance was completed on 06/13/19, we expect to see a QAR with the associated WO number. However, you only see the last performance with a credit WO date of 06/14/17. If you do the look ahead in D080, youâ€™ll find the WO that did this in R24. It hasnâ€™t moved to the history. I thought that when an item was taken to field work complete in eWP, portal updated with that date and time as the credit WO date. That didnâ€™t happen in this case. And in the process of maintaining 1.3.40 and 3.1.1, I canâ€™t tell you how many items like this we have run across. Additionally, the DAD reports arenâ€™t getting what they need for PPM 3.1.1 and 1.3.40 . Also, after a surveillance is closed out in eWP, itâ€™s supposed to update eSOMS log entries. Sometimes it does, sometimes it doesnâ€™t, which is why you see manual entries annotated in the log. It also should update the attributes for a surveillance entry, but it doesnâ€™t consistently do that either, and is almost useless since the work breakdown structure for R24 had so many tasks under one surveillance. So, things are being annotated as complete surveillances that are really partials. In some cases thatâ€™s what Portal and DAD are seeing for completion dates. <I> **** Actions Taken **** Notified I.S. and Ops team of concerns/issues DMod request has been submitted to resolve some of these issues with SV credit dates and the DADs reports. . We have passed examples of this on to IS, and there have been CRs written, specifically against DAD and how itâ€™s communicating, but it seems to be a combination of all three systems. Ops Coord has also been working to try and figure this out without success. <N> Moving due date to involve DAD and eSOMS analysts. Moving this ou tas higher priorities were assigned approved by ITBOA supervisor.
395673 | CR | 20190617 |  | 4 | MS-V-125B and MS-V-147 loss of indication | N | N |  | N | YES | <D> **** Detailed Description **** MS-V-125B and MS-V-147 have lost indication in the MCR. The valves should be closed and the green lights are out. <I> **** Actions Taken **** Replaced bulbs, no change | 02-00-MS-V-125B,02-00-MS-V-147
395674 | CR | 20190617 |  | 4 | HD-V-31A and HD-V-31C indicate full open | N | N |  | N | YES | <D> **** Detailed Description **** HD-V-31A and HD-V-31C indicate full open but should indicate closed | 02-00-HD-V-31A,02-00-HD-V-31C
395675 | CR | 20190617 |  | 4 | BS-DV-2A1 and BS-DV-5B will not stay open | N | N |  | N | YES | <D> **** Detailed Description **** S-DV-2A1 and BS-DV-5B will not stay open. Both will open with the OPEN button depressed but go closed when the OFF button is pushed. | 02-00-BS-DV-2A1,02-00-BS-DV-5B
395676 | CR | 20190617 |  | 4 | TG-TNG-1 Main turbine turning gear will not start. | N | N |  | N | YES | <D> **** Detailed Description **** TG-TNG-1 will not start locally. The main turbine zero speed alarm is not illuminated in the main control room. (4.820.B1 tile 2-7) This alarm is required for the turning gear to engage. The zero speed switch was previously jumpered out per EC 16701. It appears that the zero speed switch is not being made up. Turbine generator zero speed relay needs one of two pressure switches (TO-PS-ZA1 or ZA2) to be made up in order to actuate the TGX/ZSX. Recommend investigating. <I> **** Actions Taken **** Wrote CR Informed CRS | 02-00-TG-TNG-1
395677 | CR | 20190617 | CAQ | C | PPM 3.1.2 - Low condensate temperature for startup |  |  |  | N | NO | <D> **** Detailed Description **** PPM 3.1.2 requires condensate temperature to be GT89F. Temperature cannot be raised and is currently 75F. PPM 3.1.2 Note31 requires a CR to document this condition.
395678 | CR | 20190617 | CAQ | C | (QA) POC review of POD cannot be located |  |  |  | Y | NO | <D> **** Detailed Description **** Confirmation that POD 350062, â€œRWCU-V-4 Stroke Time Non -conformance Operabilityâ€ was reviewed at a POC meeting cannot be located. Factual Basis: â€¢ This POD was originated on 5/26/16. Meeting material before 2018 is stored on the coordinator site and has limited access. â€¢ PPM 1.3.66 Revision 032 section 6.2 states, â€œPODs are required to be reviewed by POC, typically at the next regularly scheduled POC meeting.â€ â€¢ PPM SWP-IRP-01 Revision 020 section 2.5.24 requires POC to review â€œAll Prompt Operability Determinations (POD) and revisions to PODs, in accordance with PPM 1.3.66.â€ Insights: â€¢ PODâ€™s are required to be reviewed at POC to ensure that an independent review is performed and the PGM is advised on all matters related to nuclear safety. If the POD cannot be confirmed to have been reviewed at POC, this requirement may not have been satisfied. Recommend assignment to AR-POC <I> **** Actions Taken **** Notified POC Chairman and Supervision <N> Closure of assignment 01 was reviewed and approved by the POC chair.
395683 | CR | 20190617 |  | 4 | RFT-V-22B Manual Trip Valve Leaking Oil | N | N |  | N | YES | <D> **** Detailed Description **** RFT-V-22B Manual Trip Valve on RFW-CP-RFT/1B (TB 441) is leaking oil. A puddle had formed on the ground beneath the valve. All oil present was wiped up off the floor, cabinet door, and the valve itself. An absorbent pad was placed on the ground with a date and time to be able to quantify leakage. After wiping everything off and placing the pad, oil had already started to collect on the valve again. <I> **** Actions Taken **** Wiped up oil, placed a timed and dated absobent pad, and informed supervisor. | 02-00-RFT-V-22B
395684 | CR | 20190617 | CAQ | C | Lost information from weld record DG |  |  |  | N | NO | <D> **** Detailed Description **** folloeing the acceptance of final visual of welds for WO 02126225-02 on weld record 2-13611the tablet froze up. Supervisor forced checked in the package and all the information( welder sign-offs filler material information and QC signature was lost. Spoke with inspector and reperformed sign-offs to complete the task. Supervisor signed for the nightshift welder as he was gone at the time. <I> **** Actions Taken **** generated CR for documentation of DATA GLANCE ISSUE
395686 | CR | 20190617 |  | 3 | No support task for I&C for SOP-OG-START 5.1.21 |  |  |  | N | NO | <D> **** Detailed Description **** This CR is to document support need for SOP-OG-START. In the future we need a WO with work instructions to perform retorque of Rosemount vent plugs to support venting of OG -LT-7A and OG-LT-8A. <I> **** Actions Taken **** Need WO for PV of torque, wrote CR contacted supervisor <N> **** Equipment Description **** OG-LT-7A, 8A Added task 16 to WO 02146003 for R25, will be carried to future outages.
395687 | CR | 20190617 |  | 4 | TO-P-BLP missing access hole cover |  |  |  | N | YES | <D> **** Detailed Description **** While on rounds it was discovered that the Bearing Oil Lift pump contains a warning that reads "to avoid possible injury access hole cover must be in place during operation". See attached photo. The pump is currently running with no cover. I do not recall nor do the EOs I spoke with whether that cover is always off or not. A cover not was seen in the vicinity of the pump. Recommend reinstalling the cover or a plexiglass window to prevent injury. <I> **** Actions Taken **** Notified SSS | 02-00-TO-P-BLP
395688 | CR | 20190617 |  | 3 | Change DWG EWD-63E-095 for MS-V-234 indication switch |  |  |  | N | NO | <D> **** Detailed Description **** While performing WO 02118080-01 found field configuration different from EWD-63E-095. Field changes were made per WR 29075010 on 6/21/19. Indication switch wiring was changed from a NC switch to an NC switch. See EDMS form marked up DWG.
395690 | CR | 20190617 |  | 4 | RFT-V-23B has ~4 drop per minute oil leak | N | N |  | N | YES | <D> **** Detailed Description **** RFT-V-23B has ~4 drop per minute oil leak Located on B RFP skid TB 441' | 02-00-RFT-V-23B
395691 | CR | 20190617 |  | 4 | C408 maintenance needed | N | Y |  | N | YES | <D> **** Detailed Description **** C408 High alarm rate request electrical support. <I> **** Actions Taken **** High Alarm rate, notified supervision, CR/WR generated <N> **** Equipment Description **** 501 elevation (control room door) notify security prior to work. | 02-00-W-DOOR-C408
395692 | CR | 20190617 |  | 3 | RFW-DPI-4 main startup valve dP | N | N |  | N | YES | <D> **** Detailed Description **** RFW-DPI-4 main startup valve dP is indicating 0 psid. Feedwater pressure is 190 psig and Reactor pressure is 0. <N> UPDATE In the field RFW-DPT-4 was found to be isolated by it's instrument isolation valves. The valves were V199 which was closed, V198 which was open, and V197 which was closed. On 5/23/19 RFW-DPR-4 was isolated per WO# 02117516 -10. The planned work was removed from the outage and the rest of the WO tasks were cancelled, including the task to return it to service (task 11). Therefore required RFW-DPT-4 was left isolated. The plan is to restore the RFW-DPT-4. | 02-00-RFW-DPI-4
395694 | CR | 20190617 |  | 3 | (R24LL) Control Room def. tags closure tracking untimely |  |  |  | N | NO | <D> **** Detailed Description **** A process to monitor, track and disposition control room deficiency tags is not in place or not implemented. As a result, there was a last-minute scramble to determine disposition statuses of open control room deficiencies by the emergent issue team prior to mode change. All of the last-minute items, excepting 4 brand new ones, were found to have had either been completed or had ongoing actions for disposition. These could have been identified and tracked sooner or continually through the outage. <I> **** Actions Taken **** Suggest that Operations implement an on-going method to review of open control room deficiencies that doesnt wait until the last minute to search for resolution.
395695 | CR | 20190617 |  | 4 | Doors need replaced. | N | N |  | N | YES | <D> **** Detailed Description **** Door C-420, T-114, T-109, and T-205 are normally removed for outage . This outage they were propped open, result is all 4 need to be replaced, they have appear to have been struck by carts entering thru. All non fire doors. There is sharp shards of metal , and doors do not fully close or open without excessive force, reccomend to remove doors until new replacement doors arrive. <I> One portion of a door has been taped up, however issue needs addressed due to current exposed metal. When taped up, it prevents the door from closing properly and is hard get closed and then open due to the thickness of the tape. <N> Added pictures of T109, T114, T205 and C420 to EDMS tab. | 02-00-T-DOOR-T109,02-00-T-DOOR-T114,02-00-T-DOOR-T205,02-00-W-DOOR-C420
395696 | CR | 20190617 |  | 3 | TO-PS-ZA1 setpoint | N | N |  | N | YES | <D> **** Detailed Description **** While investigating TO-PS-ZA1 (WR 29149826) pressure was 11.1 psi. Last Refueling Outage contacts were open. Recommend Engineering to evaluate and lower Trip setpoint. <I> **** Actions Taken **** cr . Possible ISCR, review ISCR history . | 02-00-TO-PS-ZA1
395697 | CR | 20190617 |  | 4 | Using Wrong Time Entry Charge Codes |  |  |  | N | NO | <D> **** Detailed Description **** Treasury reviewed GENBU and UNIT2 charges for ESD and discovered five employees where charging to the wrong work orders. Below is the fully burdened numbers for Business Development: From Columbia to Business Development: $15,955.16 From GENBU to Business Development $516.74 Total $16,471.90 <I> **** Actions Taken **** Wrote this CR per general manager direction.
395698 | CR | 20190617 |  | 4 | Staged insulation thrown away |  |  |  | N | NO | <D> **** Detailed Description **** During a walk down of RFW-P-1A it was discovered that a staged bag of material and tools for MS-V-172A had been discarded. This bag had a staged for sign as well as the bag was labeled â€œstaged for MS-V-172Aâ€. Included in the bag were all the blanket insulation required to reinsulate the valve as well as the tools to install the insulation. New blankets will now have to be fabricated before they can be installed. There were no resources planned for this extra work. <I> **** Actions Taken **** Notified supervision, took measurements for required insulating blankets and initiated CR. CR IS FOR TRACKING PURPOSE ONLY <N> **** Equipment Description **** MS-V-172A
395699 | CR | 20190617 | CAQ | D | B27 - Fire Door FP-Door-S165 Found impaired | N | N |  | N | YES | <D> **** Detailed Description **** Fire protection inspection in Yakima Building found fire door S165 impaired. The door handle and latch have been completely removed. No work request initiated to repair this fire door. Not clear if this is accidental or planned work. This indicates a lack of attention to ISPM-10 requirements that all fire doors must automatically close and latch. <I> **** Actions Taken **** WR written to repair door. <N> **** Equipment Description **** FP-DOOR-S165
395700 | CR | 20190617 |  | 4 | Evidence of air leakage on replaced HD-QSV solenoid | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Electricians went into the Heater Bay to "Snoop Check" newly installed QSVs. The associated EPNs are HD-QSV-31A, HD-QSV-31B, HD-QSV-32A, HD-QSV-32B, and HD-QSV-33A. Engineering is looking for a quantifiable description of how much leakeage is present, but due to lack of training on air volume calculations by the electric shop, we are not able to provide a detailed measurable leak rate. I have attached a video of HD-QSV-32A as a representative example of all five QSVs. <I> **** Actions Taken **** Tightened two mounting bolts to the maximum manufacturer rating of 50 in/lbs,Notified Supervision, Write CR and attach video. <N> **** Equipment Description **** Various in Heater Bay TG 471
395702 | CR | 20190617 | CAQ | C | REMP ST-101B found to be OOS and not sampling | N | Y |  | N | NO | <C> MRT Change request: CR 395702 Severity moved from Severity 3 to Severity C CAQ. <D> **** Detailed Description **** REMP composite water sampler Station 101B was found to be out of service and not collecting samples due to an unexpected loss of power to floculator bldg. at approximately 20 :00 on 6/13/19 and was restored at 04:51 on 6/14/19. However, this amount of time exceeded the battery backup on ST-101B, causing it to lose its program. Environmental Services personnel reinitialized the sampler program and restored sampler to operation on 6/17/19 at 0837. ST-101B was OOS for ~84.5 hours. Station 101B samples storm drain water flowing into evaporation pond 3 and 4. ST-101B is not an ODCM required sampler but is an EFSEC 332 requirement. Recommend assignment to Environmental Service. <I> **** Actions Taken **** Reinitiated sampler program and restored sampler to operation. Contacted Facilities. Wrote CR.
395703 | CR | 20190617 |  | 4 | TO-EX-4A abnormal noise getting worse | N | N |  | N | YES | <D> **** Detailed Description **** TO-EX-4A has a nearly continuous â€œmarbles rattlingâ€ sound. It was written up a year ago with the sound occurring for 5-10 seconds every minute or so. The condition has worsened. As mentioned in the previous CR, the cause is not readily apparent. Please investigate. <I> **** Actions Taken **** Notified CRS | 02-00-TO-EX-4A
395704 | CR | 20190617 |  | 3 | Need instructions to test TO-P-BOP Automatic Transfer Switch | N | N |  | N | NO | <D> **** Detailed Description **** As part of EC 17844, an automatic transfer switch has been installed at TO-42-1A1C which is the normal power to TO-P -BOP. Currently, TO-P-BOP is running to maintain the main turbine on the turning gear for plant startup. . The next opportunity to test the ATS is after the TO-P-BOP is secured (SOP-MT-START Step 5.3.22). The ATS should be tested with TO-P-BOP off but before proceeding with the Turbine Overspeed test (SOP-MT-START Step 5.3.28). . The diesel generators should be installed to the ATS emergency supply per EC 17844 prior to rolling the main turbine. With the diesel generators running, phase rotation can be verified by looking at indicator lights on the ATS. . With TO-P-TOP secured, the ATS can be tested by opening the disconnect at TO-42-1A1C. The ATS should recognize the loss of normal power and transfer to the emergency source. During this test, TO-P-BOP should not start (and does not need to verify the ATS functionality) because the shaft driven main oil pump is supplying bearing pressure and TO -P-BOP autostart permissive will not be satisfied. . This CR is written to drive develop of the ATS test instructions.
395705 | CR | 20190617 | CAQ | D | Jet Pump Loop A Flow indication low in the MCR | Y | N |  | N | YES | <C> MRT Change request: CR 395705 Severity moved from 4/Trend Repair to Severity D CAQ. <D> **** Detailed Description **** Jet Pump A Loop Flow as read on MS-FI-611A on P602 in the Main Control Room is reading 2 Mlbm/hr with RRC-P-1A running. For comparison, Jet Pump B Loop Flow as read on MS-FI-611B is reading 20 Mlbm/hr with RRC-P-1B running. JP -1DP through JP-20DP as read on P-619 in the MCR are consistenly reading between 2-7%. See attached graph of Jet Pump A and B Loop Flow from eDNA in EDMS. <N> MS-FI-611A is a non-safety related indication. It can be used as input in OSP-RRC-D701 and can be used for flow adjustments per ABN-RRC-LOSS. | 02-00-MS-FI-611A
395706 | CR | 20190617 |  | 4 | R24LL - Work deferred RPS-RMS-S1 | N | N |  | N | YES | <D> **** Detailed Description **** This work was deferred from R24 due to craft using the simulator for a wlkdown location versus the actual main control room. These two locations are not the same in regards to this piece of equipment. There is significanly more wiring in the MCR than in the simulator (increased scope) This work was also deferred from FO 18-01. <I> **** Actions Taken **** CR written per the dirction of Ops manager at OSP meeting 6/17/19 for R24LL | 02-00-RPS-RMS-S1
395707 | CR | 20190617 |  | 3 | (Non EN/CGS) Commercial Customer Complaint CR | N | N |  | N | NO | <D> **** Detailed Description **** (Non EN/CGS) Recommend assign to AR-CALSERV. Two Flowmeter calibrations sent to subvendor not calibrated to requested range. . Received a message call from customer in regards to asset# 546-28-03-033 & 546-28-03-032 letting me know he was reviewing the ranges the flowmeters were calibrated to and they did not match what they had requested on their CPW request form. In my evaluation I noted that the subvendorâ€™s calibration certificate we have over looked the customer's request on for calibration range. See sheet see page 5 block 17.(range) on the 546-28-03-033 subvendor calibrated it to 75gpm the request was 200gpm. On the 546-28-03-032 subvendor calibrated it to 110gpm and the request was 200gpm. Contacted the subvendor to ask and said these flowmeters were set to a span of 0-75gpm and 0 -110gpm and even if requested 0-200gpm they would have reset back to what they were originally set to. <I> **** Actions Taken **** The customer technical rep was contacted to determine a path forward since the flowmeters passed their QC review process and have already been released to the field to be used. contacted subvendor to find out more details on why they did not ask about the requested range. Contacted the customer again to discuss how they want to proceed with calibrations and ranges requested. will upload customer concurrances into EDMS once available and will load the original requests into EDMS as well for back up documentation. <N> CC-192 customer complaint completion notes were documented in the description of the plan assignment for this CR. The notes should have been also captured in the completion notes as well. Completed Customer Complaint form CC-192, contacted vendor and customer requests. I loaded complaint and calibration certificates into EDMS. The complaint form documents the evaluation, resolution and problem identification.
395708 | CR | 20190617 |  | 3 | CI-13.12 needs a procedure enhancement | N | N |  | N | NO | <D> **** Detailed Description **** CI-13.12 needs a procedure enhancement. There is a numbering issue in Section 4.5 Liquid Nitrogen Addition. Step 4.5.4 is listed, but no information/action is contained in this step. This issue does not prevent performance of the procedure or affect any safety aspects of the procedure. <I> **** Actions Taken **** Initiated this AR/CR. Notified the procedure sponsor of this AR/CR.
395710 | CR | 20190617 |  | 3 | Incorrect sealant used on HD-QV-33A gasket, body to solenoid | N | N |  | N | YES | <D> **** Detailed Description **** While performing PMT for 02112195-01 PMT HD-QV-33A, noted that that the gasket sealant was white instead of black (CAT ID 92900164) as directed by the work instructions. Near by the location was staged some Loctite 580 (white sealant). Need Engineering to evaluate if HD-QV-33A can be left as is or if system has to be tagged out and a new gasket /sealant installed. Or does of the component need to be replaced. | 02-00-HD-QSV-33A
395711 | CR | 20190617 |  | 4 | RFW-DT-1A has only 2oo3 speed probes operating | N | N |  | N | YES | <D> **** Detailed Description **** RFW-DT-1A active probe 2 indicates 0 RPM on the turning gear. The other 2 indicate 6 rpm. As indicated on RFT -COMP-2. | 02-00-RFW-DT-1A
395712 | CR | 20190617 |  | 4 | Misapplied Accounts Receivable Payment |  |  |  | N | NO | <D> **** Detailed Description **** Payment received from two vendors were applied against the incorrect outstanding invoice for each company. The outstanding balances were correct but resulted in an incorrect aging statement. <I> **** Actions Taken **** EN has reconciled with both vendors on invoice aging. Accounting clerk has been coached. The topic was discussed at department W30 regarding error prevention tool use, questioning attitude and attention to detail . Recommend no further actions at this time.
395713 | CR | 20190617 |  | 4 | Temporary wiring hanging out of E-IR-3 | N | N |  | N | YES | <D> **** Detailed Description **** Observed Temporary wiring hanging out of Electrical panels on E-IR-3. There is no wor inprogress sign. Discussed with I&C Shop and Electrical shop. They both stated tath they did not know of any work going on in E-IR-3. any work they were doing in E-IR-3. <I> **** Actions Taken **** WROTE CR. This is installed for SOP-FWH-INTTERLOCK -TEST which is currently in progress | 02-00-E-IR-3
395715 | CR | 20190617 |  | 4 | CW-FN-36 vibrational reset button seized. | N | N |  | N | YES | <D> **** Detailed Description **** Tried to reset vibrational, button seized in place. <I> **** Actions Taken **** Informed MCR, initiated AR. | 02-00-CW-FN-36
395716 | CR | 20190617 | CAQ | D | FP-P-2A & 2B seal water pressure low. | N | Y |  | N | YES | <D> **** Detailed Description **** Seal water pressure has been steadily lowering. FP-P-2B currently in use and after blowdown pressure was LT 45#. Started FP-P-2A to maintain screen cleanign and found its seal water pressure at 40#. <I> **** Actions Taken **** Informed MCR, Initated AR. | 02-00-FP-P-2A,02-00-FP-P-2B
395717 | CR | 20190617 |  | 4 | Emergent Work not well managed for R24 |  |  |  | N | YES | <D> **** Detailed Description **** There were 5 WOâ€™s added to R24 on 6/16/19 (see list of WOâ€™s below). These entailed replacement of 5 Bleed Steam Quick Acting Solenoid Valves. It appears that these solenoid valve issues were identified in May of 2017. O-BS-QSV-IR3-001 02112303 BS-QSV-21A, SOLENOID VALVE REPLACEMENT 02112457 BS-QSV-13A, SOLENOID VALVE REPLACEMENT 02112965 BS-QSV-10B, SOLENOID VALVE REPLACEMENT HC O-BS-QSV-IR3 -002 02112301 BS-QSV-10A, SOLENOID VALVE REPLACEMENT 02114233 BS-QSV-5A QSV LEAKS OUT VENT PORT â€“ REPLACE <I> **** Actions Taken **** Informed Operations Production Manager Informed OCC <N> The only WO that was added to R24 scope was 5A (02114233). All others were not approved via the OSCR process. WO 02112303 was not scoped into R24 by engineering. WO 02112457 was not scoped into R24 by engineering WO 02112965 did not have final PO 7 notes added by engineering WO 02112301 did not have final PO 7 notes added by engineering This was not an emergent work management issue. | 02-00-BS-QSV-10A,02-00-BS-QSV-10B,02-00-BS-QSV-13A,02-00-BS-QSV-21A
395719 | CR | 20190617 |  | 4 | Blade Vibration Monitoring System has wrong lights for start | N | N |  | N | YES | <D> **** Detailed Description **** SOP-MT-START Step 5.1.3.c specifies that only the BVMS #4 light should be lit. Presently only the #3 light is lit. The procedure requires this CR to be written. | 02-00-MS-VMP-1
395720 | CR | 20190617 |  | 4 | TV4 SPC health indicates fail for SPC A and SPC B. | N | N |  | N | YES | <D> **** Detailed Description **** On DEH monitors in main control room TV4 SPC health indicates fail for SPC A and SPC B. Requst I/C to reset failures. | 02-00-MS-V-TV/4
395721 | CR | 20190617 |  | 4 | SCW diff press high locked in. | N | N |  | N | YES | <D> **** Detailed Description **** SCW High diff pressure alarm locked in (setpoint is GE 33 psid). Local indication at SCW-DPI-1 reads 32.5 psid. ARP directs operation of SCW-V-523 (SCW-P-1/2 Min flow). With valve full open no change in d/p. <I> **** Actions Taken **** Informed MCR of actions and results. <N> This condition was previously identified in CR 395600. When the system was initially started the differential pressure was approximately 38 psid. The pressure can be adjusted with SCW-V-523 but the response is slow. Recommend waiting until after generator is online to make final adjustments as increased temperatures in the stator windings will result in increased cross sectional area of the coils and decreased differential pressure. | 02-00-SCW-DPS-26
395722 | CR | 20190617 |  | 4 | MS-LS-24L leak | N | N |  | N | YES | <D> **** Detailed Description **** A puddle of water was observed in the condenser bay south side. While attempting to locate the source, a puff of steam was seen coming from MS-LS-24L. This is an intermittent leak. MS-LS-24L is the MS Trap Station #13 Level Switch. <I> **** Actions Taken **** Initiated CR. Notified control room and HP. | 02-00-MS-LS-24L
395723 | CR | 20190617 | CAQ | D | Received reactor building stack rad alert | N | Y |  | N | YES | <D> **** Detailed Description **** At 22:08 on 6/17/19, received 4.602.A.4 drop 3-8 reactor building stack rad alert. PRM-RIS-1 composite channel reads 2.9 e-6 without the purpe pump light lit. Event log indicates composite channel over the high level and the amber alert alarm light is lit. Completed steps 1 through 3 of the ARP with no other abnormalities. Requested chemistry to perform a confirmatory grab sample. Secured ventilating the drywell. <I> **** Actions Taken **** Notified SM and requested cemistry obtain grab sample. | 02-00-PRM-RIS-1
395725 | CR | 20190617 | CAQ | D | MS-FI-611A reading low | Y | N |  | N | YES | <D> **** Detailed Description **** Jet pump loop A flow is reding low. Individual JP flows look good and are in alignment with the loop B. This impacts the total core flow signal. <I> **** Actions Taken **** Notified the CRS <N> **** Equipment Description **** MS-FI-611A Jet pump A loop flow MS-FI-611A is a non-safety related indication. It affects the indicated total core flow which impacts ability to pass OSP-RRC-D701 which is required above 25% RTP. Also affects ability to adjust flow per ABN-RRC-LOSS.
395726 | CR | 20190618 |  | 4 | MD-TK-2 alarm did not come in with tank high level | N | N |  | N | YES | <D> **** Detailed Description **** MD-TK-2 level was noted to be high due to water coming out of the overflow vent and MD-LIC-1 indicating full scale. The alarm on 4.840.A1 window 7-4 was not in. Suspect MD -LS-6 failure. <I> **** Actions Taken **** Tank level was lowered by placing MD-LCV-1A and MD-LCV-1B in service when main condenser vacuum was established during plant startup. This allowed tank level to be restored to normal by vacuum dragging water from the tank to the main condenser. | 02-00-MD-LS-6
395727 | CR | 20190618 |  | 4 | COND-V-619 suspected seat leakage | N | N |  | N | YES | <D> **** Detailed Description **** Significant seal water flow was noted through MD-FG-1A with isolation valve COND-V-619 closed. <I> **** Actions Taken **** Initiated CR. | 02-00-COND-V-619
395728 | CR | 20190618 |  | 4 | Remove red duct tape from RFT-A piping/lagging on governor | N | N |  | N | YES | <D> **** Detailed Description **** Red duct tape was identified on piping and lagging to the RFT-A governor block assembly. It looks like the duct tape is holding the lagging on the piping. The duct tape should be removed and the lagging/insulation repaired. <I> **** Actions Taken **** Notified Operations production SM. <N> **** Equipment Description **** RFT-A governor block piping
395729 | CR | 20190618 |  | 3 | IMDS for MD-LS-6 & EWD 72E025 list wrong alarm |  |  |  | N | NO | <D> **** Detailed Description **** W/R 29149900 references the alarm for MD-LS-6 is 4.840.A1 Window 7-4. However, the IMDS for MD-LS-6 and drawing 72E025 list the alarm as 840.A1 Window 9-1. Verified through PSRO that the correct alarm is 4.840.A1 Window 7-4. The IMDS and drawing 72E025 need to be updated. <I> **** Actions Taken **** Wrote CR
395730 | CR | 20190618 |  | 4 | STM DUMP VLVS NOT FULL CLOSED alarm is not in alarm. | N | N |  | N | YES | <D> **** Detailed Description **** STM DUMP VLVS NOT FULL CLOSED alarm is not in alarm. All the dump valves are open for plant shutdown. The STM DUMP VLVS NOT FULL CLOSED alarm should be in alarm if at least one dump valve is not full closed. H13-P840.A2.9-6. This has been previously documented by CR 388780 and WR 29146582, but was never corrected. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-ANN-ANN-A/A2
395731 | CR | 20190618 |  | 4 | CND-V-1A is leaking by to T-2 sump | N | N |  | N | YES | <D> **** Detailed Description **** CND-V-1A is leaking by to T-2 sump at about 10 drops a minute. It was leaking a steady pencil stream and the valve was tightened and the leakby slowed. <I> **** Actions Taken **** Informed Supervision. | 02-00-CND-V-1A
395732 | CR | 20190618 |  | 4 | MS-V-166B is leaking | N | N |  | N | YES | <D> **** Detailed Description **** With reactor pressure at 140 PSIG MS-V-166B is leaking. Leakage appears to be coming from the stem area. <I> **** Actions Taken **** Notified OCC | 02-00-MS-V-166B
395733 | CR | 20190618 |  | 3 | R24 LL: Proactive Process to Manage WOs LT45 does not exist | N | N |  | N | NO | <D> **** Detailed Description **** OCC focused on WOâ€™s w/a status < 45 as they began to build up early on resulting in an emergent issue to understand the list and drive progress. Suggest modeling outage process with online process such that a defined accountable person is responsible for managing this control activity from the outage start rather than when an issue or bow wave forms. This includes oversight of said activity. This recommendation is a proactive approach to managing an inherent process risk in both online and outage operations. Alternatively, if the resources available during online operations are not available during an outage, pre-identify expediters to keep bulk work or task monitoring from becoming a focus of the OCC. <I> **** Actions Taken **** Managed issue. Reviewed as a team for future learning.
395734 | CR | 20190618 |  | 4 | E-TR-N1 83E emergency transfer power alarm failed to acuate | N | N |  | N | YES | <D> **** Detailed Description **** while performing testing on the E-TR-N1 contol power transfer switch the alarm 83E failed to come in or alkarm in the main control room. Same condition was documented in other WR but cancelled to WR 29138640 which stated they tested it satisfactory and completed the WR. It has failed the test and repeated its failure recommend further investigation. <I> **** Actions Taken **** WR/CR | 02-00-E-TR-N1
395738 | CR | 20190618 |  | 3 | EC 16701 Past Review for bypass of TG-RLY-ZSX | N | N |  | N | YES | <D> **** Detailed Description **** A past review was conducted of EC 16701 where a jumper was installed across TG-RLY-ZSX which is the Zero speed relay for main turbine turning gear (TG-TNG-1) (Ref. AR 00370880 and 00370874). In 2017, it was documented under WR 29138491. Both pressure switches (TO-PS-ZA1 and ZA2) had input voltage 120 VAC but were not closing on Turbine Gear Bearing Oil Pressure. System pressure at the time was about 32 PSIG per the WR. During R-24, both pressure switches were replaced, and still did not work (both replaced under WO-02118048). Both these switches had SAT calibrations per WO 02118048. We should have had a PS actuation per IMDS at 13.0 (+/- 0.5) PSIG increasing. IMDS for TO-PS-ZA1 mentions that the switches work on pulsating oil pressure and to perform oil pressure tests by isolating air source (i.e. Air Accumulators). If Air source bleeds into the oil system, the switches will have no way to actuate via the accumulators. The recommendation is to come back to this problem from a mechanical perspective at some future outage. Past work order history reveals we have not taken a closer look at what physically actuates these switches and addressed the problem. At this point, a TMOD (EC 17848) will be placed back across TG-RLY-ZSX. <I> **** Actions Taken **** Notified BOP Supervisor, Design Engineering and EOC | 02-00-TO-PS-ZA1,02-00-TO-PS-ZA2
395741 | CR | 20190618 |  | 4 | GY-TIC-17 reading high out of spec. | N | N |  | N | YES | <D> **** Detailed Description **** GY-TIC-17 is reading 39.5 F with a high spec. of 35.5 F. Regen. cool down is in progress with 2 reefers in service. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** RW 452 | 02-00-GY-TIC-17
395742 | CR | 20190618 |  | 4 | Water leak on MS-V-166B | N | N |  | N | YES | <D> **** Detailed Description **** 1-2 GPM leak on MS-V-166B. <I> Same leak as 00395732. Cancel this AR. | 02-00-MS-V-166B
395746 | CR | 20190618 |  | 4 | E-TR-M3 DGA samples should be taken quarterly | N | N |  | N | YES | <D> **** Detailed Description **** Based on the recommendations from SD Myers and the current issues with E-TR-M3 it is recommended that a PM be created against PMID 00021625 to perform samples on a quarterly basis. This is being done to support monitoring of E-TR-M3 associated with AR-CR 393438 <I> **** Actions Taken **** Actions taken: Initiated AR-SMS 395744 to generate new quarterly PM for taking transformer oil samples. | 02-00-E-TR-M3
395750 | CR | 20190618 |  | 3 | PPM 15.1.4 steps marked NA incorrectly | N | N |  | N | NO | <D> **** Detailed Description **** PPM 15.1.4 FP-P-110 Operability Test (performed 6/13/19) WO 02132945 During performance of this test, place-keeping errors were made and some steps marked N/A incorrectly. This was discovered during the final supervisor review and close out of the WOT. The errors were discussed and reviewed by the shift manager who had signed off completion of the procedure. The shift manager discussed the procedure errors with the performer to fully understand what was done and how it was accomplished. He validated that all required steps were performed, plant component status control was maintained, and required test data and results were all satisfactory. . Independent verifications of affected valves were performed SAT at the completion of the test per step 7.35. <I> **** Actions Taken **** Discussed with shift manager who signed off the procedure. Discussed with Ops CIC
395753 | CR | 20190618 |  |  | MS-V-110B- new bonnet ordered is incorrect |  |  |  | N | NO | <D> **** Detailed Description **** CID 28791 (Bonnet , Valve) ordered / procured for MS-V-110B does not fit our valve. <I> **** Actions Taken **** Supervisor notifed by craft.
395754 | CR | 20190618 |  | 3 | Production over safety steaming main turbinewith no TO-P-EOP |  |  |  | N | YES | <D> **** Detailed Description **** Energy Northwest has tolerated six years of bad wiring for safety related components at Columbia Generating Station. An example is a RHR valve that ran backwards and jammed hard into the seat until it cleared fuses. The emergency oil pump for the main turbine being wired wrong and causing substantial damage and delay s the culmination of such tolerance. Two rented diesels hooked to an AC bearing oil pump does not replace the DC emergency oil pump that is a backup for the bearing oil pump. There is no pump redundancy now. The bearing lift pump is not reliable as well due to no Auto start. This could be the cause for bearing damage identified during R24. CGS procedure SOP-MT-OIL-OPS requires TO-P-EOP to be in AUTO <I> **** Actions Taken **** To summarize the main turbine has no emergency oil pump, faulted bearing lift pump, and a bearing oil pump with substantially altered wiring from plant design. <N> Re-opened and assigned as a 3 to AR-PGM (by agreement) to address the safety concern. | 02-00-TO-P-EOP
395755 | CR | 20190618 |  | 4 | 3 Pieces of M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** 3 Heise Gauges model CM2500psi were NOT used during Calibration cycle. They were bought in 2018 to be ready for R24 Hydro testing. Other pieces of M&TE were used instead. These are now Suspended again until Calibrating at the first of R25. Calcode #0068416. DEF #7052A written. Calcode #0068414. DEF #7053A written. Calcode #0068415. DEF #7054A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only
395756 | CR | 20190618 | CAQ | D | Security IDS 16 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security IDS 16 has a pin out and needs maintenance. Zone not operating by design. <I> **** Actions Taken **** CR/WR initiated. Security supervision notified. | 02-00-SEC-IDS-EVAL/16/17
395760 | CR | 20190618 | CAQ | D | FP-SYS-D53B leaking | N | N |  | N | YES | <D> **** Detailed Description **** after clearance O-FP-SYS-D53B was lifted on 6/16/19, found water dripping from ball drip , the clearance was hanging for 29 days, my thought is the orings and gasket dried out on the priming chamber during that time, and needs to be replace. | 02-00-FP-V-D53B/361
395761 | CR | 20190618 |  | 4 | small bore tubing support to RFT-V-722B | N | N |  | N | YES | <D> **** Detailed Description **** The small bore unitstrut type support that holds the horizontal bend (2 90s) back from where the tubing ties into RFT-V-722B is loose in the clamp. It seems this support has had some unique setup in the past. <I> **** Actions Taken **** Contacted Engineering to do a check in the field for proper setup and if any action is warranted. An inspection of the tubing support condition was performed by the EFIN Civil/Stress Engineer. The existing condition of the tubing support is acceptable and the support is fully functional for the associated Seismic Category 2 application. No further actions are required. | 02-00-RFT-V-722B
395762 | CR | 20190618 |  | 3 | Procedure enhancement | N | N |  | N | NO | <D> **** Detailed Description **** Recommend changing OSP-RCIC/IST-B501 step 7.10.2.c to install a jumper between termination BBB4-5(H13-P621) and RCIC-RLY-K19 terminal #2(H13-P621). . Recommend having Engineering peer check this change.
395766 | CR | 20190618 |  | 4 | OG-TC-2A No Display | N | N |  | N | YES | <D> **** Detailed Description **** The display for OG-TC-2A appears to be unpowered. Reference AR 00395650. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** T441 | 02-00-OG-TC-2A
395767 | CR | 20190618 |  | 4 | MS-PCV-13B / MS-PCV-11B not operating properly | N | N |  | N | YES | <D> **** Detailed Description **** MS-PCV-13B and MS-PCV-11B are indicating closed with MS-V-12B in closed. Normally one of these valves is open when the other is closed. The valves were locally observed to be closed. | 02-00-MS-PCV-13B
395769 | CR | 20190618 |  | 3 | BVM computer has CMOS error and will not startup | N | N |  | N | YES | <D> **** Detailed Description **** When attempting to start up the Blade Vibration Monitoring System (BVM) computer in preparation for turbine roll nearing the end R24, the computer failed to boot. The screen displays a "CMOS error". The battery requires replacement. Requesting IT provide a new battery and peform replacement. [OEM tech support for accessing the battery location in the rack is currently available onsite.] <I> **** Actions Taken **** discussed with I/C craft that was present. Discussed with OEM Discussed with Comp Eng <N> **** Equipment Description **** TG501 | 02-00-MS-VMP-1,02-00-MS-VMP-2
395770 | CR | 20190618 |  | 3 | R24LL No task to un-pin COND springcans | N | N |  | N | YES | <D> **** Detailed Description **** There was no W/O task to un-pin the suction and discharge piping springcans for the Condensate booster pumps on W/O 02115569. Task 30 installed the pins in the springcans. Need to go remove these following completion of pipe fill. <N> Task 73 added to WO 02146000 for R25. Will be copied to future outage work orders. | 02-00-COND-P-2A,02-00-COND-P-2B,02-00-COND-P-2C
395771 | CR | 20190618 |  | 3 | PMT for RFW-V-65B packing leak is not going to be performed | N | N |  | N | YES | <D> **** Detailed Description **** R24 hydro identified RFW-V-65B had a packing leak (CR 395337 . WO 02145406 "RFW-V-65B PACKING LEAK (IDENTIFIED DURING RPV LEAKAGE TEST)". PPM 10.25.74 (PMT requirements are to perform Level 1 (electricallly stroke valve twice), Level 2 (Record static bus voltage just prior to stroking and monitor motor current (at MCC) and stroke time. Motor Load signatures are optional) and Level 5 Verify running load and total thrust: Monitor current and record static bus voltage just prior to stroking. Monitor running load and total thrust for GL 89-10 MOVs per PPM 10.25.132. Based on available margin, an engineering justification may be done in lieu of measuring thrust. For packing adjustments, total thrust may not be required depending on available margin. <I> **** Actions Taken **** Due to current plant conditions, the PMT will not be performed (OCC direction). The following actions were provided to mechanical maintenance (Ensure/measure the gland follower is not cocked, Torque packing to specified value on the packing data sheet while ensuring the packing gland folllower does not become cocked. | 02-00-RFW-M-V/65B,02-00-RFW-MO-65B,02-00-RFW-V-65B
395772 | CR | 20190618 |  | 3 | (FP) TCPs left open while WO task is at finished. | N | N |  | N | NO | <D> **** Detailed Description **** Steps to close the two Transient Combustible Permits were skipped in the WO package and permits left with no closure notes added. These TCPs are outage constrained permits for Fire Protection. <I> **** Actions Taken **** Emailed responsible owners, wrote CR.
395773 | CR | 20190618 |  | 3 | (FP) FPSI left open while WO task is at finishe | N | N |  | N | NO | <D> **** Detailed Description **** Task to close the Fire Protection System Impairment was signed off as complete and the permit was left with no closure notes added. This FPSI is an outage constrained permit for Fire Protection. <I> **** Actions Taken **** Emailed responsible owner, wrote CR. <N> Williams Plant Services.
395774 | CR | 20190618 |  | 3 | (FP) BI left open while WO is at Complete. | N | N |  | N | NO | <D> **** Detailed Description **** Task to close the Barrier Impairment was signed off as complete and the permit was left with no closure notes added. This BI is an outage constrained permit for Fire Protection. <I> **** Actions Taken **** Emailed responsible owner, wrote CR.
395775 | CR | 20190618 |  | 3 | 15B.2 references a note that does not exist | N | N |  | N | NO | <D> **** Detailed Description **** 15B.2 Section 3.6.4.5 states that smoke/fire dampers shall be furnished and installed... as per note 17 on Drawing M826. EC 9525 deleted note 17 on Drawing M826 when WMA -FD-1/2 were disconnected from WOA-SMD-1A/1B but failed to update 15B.2. <I> **** Actions Taken **** Wrote CR to document need to update 15B.2. This is a document only issue. Assign to AR-DMC.
395776 | CR | 20190618 |  | 4 | COND-PI-15BG indication (~900-950 psig) | N | N |  | N | YES | <D> **** Detailed Description **** Currently with COND-P-2B in service the Booster pump header pressure on F066 computer point shows ~640 psig. Local COND-PI-15BG Gauge (COND-P-2B Discharge Pressure) needs calibrated as it is reading ~250-300 psig high. <I> **** Actions Taken **** This gauge s indication only. Generating to document offset if using as part of monitoring. | 02-00-COND-PI-15BG
395777 | CR | 20190618 |  | 4 | TSC Janitor closet hot water valve broken | N | N |  | N | YES | <D> **** Detailed Description **** TSC Janitor closet hot water valve broken, will not shut completely. Suspect internal damage. Recommend replacement of hot water valve at janitor sink OSC/TSC <I> **** Actions Taken **** Isolated valve just upstream of hot water valve with screwdriver. Informed Janitor supervisor <N> **** Equipment Description **** OSC/TSC janitor closet sink hot water valve Elev 441
395778 | CR | 20190618 |  | 4 | (R24LL) Ops outage Lesson learned to date (Vacuum Pull) | N | N |  | N | NO | <D> **** Detailed Description **** Attached to the EDMS is a list of ops lessons learned from One Note, specific to R24 Vacuum pull. This CR is Ops trending only and R24 LL <I> **** Actions Taken **** Transferred information from One Note to CR data This CR is for Ops trending only and R24 LL
395779 | CR | 20190618 | CAQ | D | Malfunction on SEC-IDS-5 6 | N | N |  | N | YES | <D> **** Detailed Description **** CAS received a malfunction on IDS 5 6, request electrical support to investigate. <I> **** Actions Taken **** Compensatory measures initiated; CR/WR Generated | 02-00-SEC-IDS-EVAL/5/6
395780 | CR | 20190618 |  | 3 | PRNM Service on PDIS-CPU-DATA1 will not run | N | N |  | N | YES | <D> **** Detailed Description **** The UnvSrv64.exe program that recieves PRNM data from the local PRNMRCVR.exe program will not function correcctly. This CR should go to Computer Engineering to investigate. This data is engineering trend data and does not affect operations. PRNM Data is still working on PDIS-CPU-DATA2. This issue is preventing completion of WR 29149930 to implement unrelated software changes on this computer. <I> **** Actions Taken **** Working with vender to resolve. | 02-00-PDIS-CPU-DATA1
395781 | CR | 20190618 |  | 4 | C204 Human Performance Error | N | N |  | N | NO | <D> **** Detailed Description **** At 14:23, an individual from Org. Code 52233 did not ensure that door C204 was secured after entering the Vital Island. These actions do not align with SWP-SEC-03 subsection 4.7 "Personnel Use of Vital Area Doors" <I> **** Actions Taken **** Security Supervision notified. Individual was escorted out of the vital area and subsequently offsite. Meeting was held with the individual's supervisor and a statement was taken.
395782 | CR | 20190618 |  | 3 | Procedure 10.25.25 Revision Needed | N | N |  | N | YES | <D> **** Detailed Description **** See Attached EDMS <I> **** Actions Taken **** Notified Supervision and marked up procedure for EDMS <N> **** Equipment Description **** . Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
395783 | CR | 20190618 |  | 3 | Procedure 10.25.32 Revision Needed | N | N |  | N | YES | <D> **** Detailed Description **** See Attached EDMS <I> **** Actions Taken **** Notified Supervision and marked up procedure for EDMS <N> **** Equipment Description **** . Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
395784 | CR | 20190618 |  | 3 | Procedure 10.25.35 Revision Needed | N | N |  | N | YES | <D> **** Detailed Description **** See Attached EDMS <I> **** Actions Taken **** Notified Supervision and marked up procedure for EDMS <N> **** Equipment Description **** . Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
395785 | CR | 20190618 |  | 3 | Procedure 10.25.111 Revision Needed | N | N |  | N | YES | <D> **** Detailed Description **** See Attached EDMS <I> **** Actions Taken **** Notified Supervision and marked up procedure for EDMS <N> **** Equipment Description **** . Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
395786 | CR | 20190618 |  | 3 | Procedure 10.25.23 Revision Needed | N | N |  | N | NO | <D> **** Detailed Description **** See Attached EDMS <I> **** Actions Taken **** Notified Supervision and marked up procedure for EDMS <N> **** Equipment Description **** . Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
395787 | CR | 20190618 |  | 3 | Procedure 10.25.30 Revision Needed | N | N |  | N | NO | <D> **** Detailed Description **** See Attached EDMS <I> **** Actions Taken **** Notified Supervision and marked up procedure for EDMS <N> **** Equipment Description **** . Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
395788 | CR | 20190618 |  | 3 | Procedure 10.25.36 Revision Needed | N | N |  | N | NO | <D> **** Detailed Description **** See Attached EDMS <I> **** Actions Taken **** Notified Supervision and marked up procedure for EDMS <N> **** Equipment Description **** . Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
395789 | CR | 20190618 |  | 4 | MS-V-163B leakoff line union steam leak | N | N |  | N | YES | <D> **** Detailed Description **** There is an S4 steam leak from MS-V-163B leakoff line union. Attempt to tighten before steam cut. <I> **** Actions Taken **** Informed FIN supervision. <N> **** Equipment Description **** TG 501 catwalk above B LP turbine | 02-00-MS-V-163B
395790 | CR | 20190618 | CAQ | D | Received reactor building stack rad alert | Y | Y |  | N | NO | <D> **** Detailed Description **** At 16:00 on 6/18/19, received 4.602.A.4 drop 3-8 reactor building stack rad alert. PRM-RIS-1 composite channel reads 2.0 e-6 without the purpe pump light lit. Event log indicates composite channel over the high level and the amber alert alarm light is lit. Completed steps 1 through 3 of the ARP with no other abnormalities. Requested chemistry to perform a confirmatory grab sample. After restoration of OG system the indication when back to normal. THis CR is for trending purpose. See EDMS for the DNA plot. <I> **** Actions Taken **** Takes the action from the ARP and informs Chemist to take a sample.
395791 | CR | 20190618 |  | 4 | RFW-FI-2A indicates no flow with RFW-P-1A in service | N | N |  | N | YES | <D> **** Detailed Description **** RFW-FI-2A indicates no flow in the main control room with RFW-P-1A in service. <I> **** Actions Taken **** Wrote CR. Suspended raising pressure in the RPV. | 02-00-RFW-FI-2A
395792 | CR | 20190618 |  | 3 | PPM16.11.2 needs an enhancement |  |  |  | N | NO | <D> **** Detailed Description **** On page 6 the note just before step 6.5 states that the SJAE is not in service until the Hogger pumps are removed from service. That is not entirely correct. It should state that the SJAE sample should not be taken until the AR-P-1A and AR-P-1B are removed from service .The SJAE system can be in-service but the pumps can still be on for quite a while after the SJAE system is placed in service. Operations have to turn the pumps off and they can't get to it right away sometimes. When they remove the hogger pumps from service it is all SJAE then and the sample will be valid. <I> **** Actions Taken **** Notified Chemistry supervision, and procedure sponsor.
395793 | CR | 20190618 |  | 4 | Steam flashing near COND-HX-5B | N | N |  | N | YES | <D> **** Detailed Description **** A loud banging noise near could be heard near COND-HX-5B. The noise was investigated and repeated, loud banging sounds could be heard coming from COND-HX-5B and the nearby elbows of the adjoining 18â€ HD(5)-2 line. The 18â€ HD(5)-2 line could be seen to move 1-2â€ coincident with noise (video in EDMS). This may be an indication of steam flashing in the line. Recommend further investigation and repair, as necessary. <I> **** Actions Taken **** Notified System Engineer. Notified EOC. | 02-00-COND-HX-5B
395794 | CR | 20190618 |  | 4 | Off gas train A recombiner heater failed. | N | N |  | N | YES | <C> MRT Change request: CR 395794 Severity moved from Severity D CAQ to Severity 4 NON-CAQ. <D> **** Detailed Description **** Off gas train A recombiner heater failed. On H13-P672 in main control room the red light is off for the A Train Recombiner Heater. OG-TRS-602 indicates 150Â° F for A train and 370Â° F for B train. Breaker at PP-3CA is on for heater. OG-TC-2A display on is off also at N64-P001. See WR 29149918 and AR 395766. | 02-00-OG-RC-5A
395795 | CR | 20190618 | CAQ | D | LPRM 56-17D failed upscale | Y | N |  | N | YES | <D> **** Detailed Description **** During rod withdrawal for plant startup LPRM 56-17D failed upscale and caused an APRM upscale alarm. Upon investigating the LPRM power trend it was apparent the LPRM output went from about 5% and trending up slowly to 130% which is maximum scale. <I> **** Actions Taken **** The LPRM was bypassed with high voltage off per SOP -APRM/LPRM-OPS. SNE notified. <N> **** Equipment Description **** LPRM 56/17D | 02-00-LPRM-DET-56/17D
395796 | CR | 20190618 |  |  | LPRM 56-17D failed upscale |  |  |  | N | YES | <D> **** Detailed Description **** LPRM 56-17D failed upscale during start up, placed LPRM 56-17D in HV/OFF BYPASS to returm APRM-2 reading to normal value. <I> **** Actions Taken **** Informed CRS <N> **** Equipment Description **** LPRM 56-17D
395797 | CR | 20190618 | CAQ | D | LEFM system going in and out of failure | Y | Y |  | N | YES | <D> **** Detailed Description **** While beginning WO#02140521-01, the LEFM system status screen in the main control room was going back and forth between Check+ and Failure (approx. 1-3 min in Check+ and <10sec on Failure). At RFW-CAB-FE3/FE4, the system was exhibiting the same behavior. The Event Screen for CPU1 indicates that Loop 1 is throwing a â€œFlatness Ratio Highâ€ alarm, which puts Feedwater A into Failure Mode. <I> **** Actions Taken **** Notified engineer and supervisor and Ops. Wrote this CR. | 02-00-RFW-CAB-FE3/FE4
395798 | CR | 20190618 |  | 3 | RFW-P-1A pump axial thrust monitor erratic (RFW-VBI-XE/P1A) | N | N |  | N | YES | <D> **** Detailed Description **** Received TURBINE A VIBRATION trouble alarm (H13-P840.A1 drop 7-1). Alarm due to RFW-VBI-XE/P1A (pump axial thrust displacement) erratic indication; both channels are rapidly movi ng from ~ 10 mils in the normal direction to 20 mils in the counter direction. Both channels are trending together. This alarm occurred as RFW-P-1A speed was being raised to maintain RPV injection as RPV pressure was raised and continues with stable RPV pressure of 956 psig. RFW-P-1A RPM currently 3200 RPM in MDEM control with discharge pressure of 1150 psig. Bearing oil pressure is normal at 19.5 psig and oil cooler outlet temperature of 113 deg. F. Minimum flow valve (RFW-FCV-2A) is in manual @ 80% output; discharge flow indicates between 0 and 1,500 gpm on RFW-FI-2A (flow appears to be cycling with Startup Flow Control valve movement). All other vibration / displacement channels are normal. <I> **** Actions Taken **** Submitted CR and WR. Notified the CRS and Shift Manager. . The pump coupling is visibly randomly moving axially ~0.2" both directions. | 02-00-RFW-VBI-XE/P1A
395799 | CR | 20190618 |  | 4 | Steam leak at #7 turbine bearing gland area | N | N |  | N | YES | <D> **** Detailed Description **** Steam leak at #7 turbine bearing gland area. This gland and piping was disassembled during the outage for the MS-DT-1C overhaul. Steam leak is either from the gland bolting area or the supply or return flanges. Seal steam pressure is curently 1.3# so this is not seal supply excessive pressure issue. Steam is deflecting off low pressure housing onto bearing area, making it difficult to observe exact location of leak. | 02-00-MS-DT-1C
395800 | CR | 20190618 |  | 3 | Quarterly CORC Caution Tag Audit (WO 02132646) (CR 1 of 2) |  |  |  | N | NO | <D> **** Detailed Description **** Quarterly CORC Caution Clearance Audit 10CFR50.59 The Quarterly CORC Caution Tag Audit (WO 02132646) has documented the caution clearances that have been hanging for GE 30 days. There are 32 new Caution clearances added to this total since the last audit: C-CBD-TEMP-BLOW-001, C-CL-RMS-BP/1 -001, C-CL-V-101 -001, C-CW-V-62 -001C-DEH -AMT/LEAD -001, C-DW-QUENCH-R24-001, C-FDR-P-15A/B -003, C-FPC-BYPASSR24-001, C-FP-UVD-11/R24-001, C-GPWH-HX-2 -001, C-MD-TK-2/R24 -001, C-MT-ELEV-1-606-001, C-NSSE-EQ-94 -001, C-PRA-EUH-92B -001,C-PWC-V-114/119-001, C-PWC-V-417 -001, C-PWC-V-451 -001, C-PWC-V-571-001. <I> **** Actions Taken **** Wrote CR, note that to see all data go to next CR.
395801 | CR | 20190618 |  | 3 | Quarterly CORC Caution Tag Audit (WO 02132646) (CR 2 of 2) |  |  |  | N | NO | <D> **** Detailed Description **** Quarterly CORC Caution Clearance Audit 10CFR50.59 The Quarterly CORC Caution Tag Audit (WO 02132646) has documented the caution clearances that have been hanging for GE 30 days. C-RFWA-SEAL-R24-001, C-RFWB-SEAL-R24-001, C-RHR-SDC-BYP51-003, C-RHR-SDC-BYP52-003, C-RHR-SDC-BYP59 -003, C-RHR-SDC-WIC-001, C-RPS-BYPASSR24-001, C-SA-V-22 -002, C-SCW-SHUTDOWN -001, C-SMA-TCV-1 -001, C-TSW-V-681 -001, C-TMU-V-1C -001, C-TMU-V-7A/B -003, C-WEA-FN-1B -002, . Request Technical Services/Systems Engineering Manager (or designee) to determine whether a 50.59 review is required. See CR 395800 for 1st part. <I> **** Actions Taken **** Wrote 2 CR's for Caution Audit.
395802 | CR | 20190618 |  | 3 | Quarterly CORC Danger & Local Tag Audit (WO 02132644) |  |  |  | N | NO | <D> **** Detailed Description **** Quarterly CORC Danger & Local Clearance Audit 10CFR50.59 The Quarterly CORC Danger & Local Tag Audit (WO 02132644) has documented the danger & local clearances that have been hanging for GE 30 days. 13 new clearances have been added to this total since the last audit: L-HCO-T-S5 -001, L-MT -CRA-1 -002, L-MT-ELEV-1 -001, L-MT-ELEV-3 -001, L-TOA-HC -2A/K -001, L-WEA-FU-9E -002, L-WOA-HC-1/O -002, D-CPR-V -365 -001, D-PWC-P-102 -002, D-TOA-FN-1A -004, O-DEH-V -75/R24 -001, O-DRYWELL-R24 -001 O-MT-HOI-16 -001, . Request Technical Services/Systems Engineering Manager (or designee) to determine whether a 50.59 review is required. <I> **** Actions Taken **** Wrote CR
395803 | CR | 20190618 |  | 3 | Wrong frequency for TSP-CONT-C804 |  |  |  | N | NO | <D> **** Detailed Description **** TSP-CONT-C804 is listed as w12 frequency in portal J. It is specified in Tech Specs to be done per the Primary Containment Leakage Rate Testing Program, which has it as an as needed frequency. . Also the Primary Containment Leakage Rate Testing Program Plan says that this must only be done within 7 days of opening the airlock doors. It should also say 7 days after final closure if that is what it means. <I> **** Actions Taken **** Wrote CR. Contacted EOC <N> Closed to SMS-AR action 00399704
395804 | CR | 20190618 |  | 4 | HD-LIC-5A22 Output is 100% with no indicated Level | N | N |  | N | YES | <D> **** Detailed Description **** The Dump Valve for HD-TK-5A is controlled by HD-LIC-5A22. The Output signal for HD-LIC-5A22 is at 100% indicating that the Dump Valve is open. However, there is no water level indicated on HD-LIC-5A22, so the Dump Valve should be shut and its controllerâ€™s output should be at zero. | 02-00-HD-LIC-5A22
395805 | CR | 20190618 |  | 4 | HD-LIC-5B22 Output is 100% with no indicated Level | N | N |  | N | YES | <D> **** Detailed Description **** The Dump Valve for HD-TK-5B is controlled by HD-LIC-5B22. The Output signal for HD-LIC-5B22 is at 100% indicating that the Dump Valve is open. However, there is no water level indicated on HD-LIC-5B22, so the Dump Valve should be shut and its controllerâ€™s output should be at zero. | 02-00-HD-LIC-5B22
395806 | CR | 20190618 |  | 4 | RFW-DT-1B HP/LP stop valves bad indication | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of 8.3.381 section 6.6 RFT B stop and Governor valve preoperational checks, the HP and LP stop valves indicating lights did not indicate full open on H13-P840 when local observation showed them at full open. This is a prerequsite step to performing the uncoupled overspeed testing of RFW-DT-1B. <I> **** Actions Taken **** Informed CRS/SM, investigated locally | 02-00-RFT-LMS-20SS1/1B,02-00-RFT-LMS-20SS2/1B
395807 | CR | 20190618 |  | 4 | TMU-P-1C has excessive packing leakage | N | N |  | N | YES | <D> **** Detailed Description **** TMU-P-1C has excessive packing leakage. Please evaluate and adjust as necessary. <I> **** Actions Taken **** WR/CR | 02-00-TMU-P-1C
395808 | CR | 20190619 |  | 4 | Steam tunnel camera would not come on | N | N |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was observed that the steam tunnel camera for 501TG building would not come on. <I> **** Actions Taken **** Informed SSS and wrote CR <N> **** Equipment Description **** Steam tunnel
395810 | CR | 20190619 |  | 4 | CF-MX-4 precoat tank agitator did not start | N | N |  | N | YES | <D> **** Detailed Description **** While performing a CFD precoat the CF-MX-4 agitator is suppose to turn on after you press the start button. It did not. The start, stop buttons and a relay COND-RLY -62/TDR18 are the components on the electrical diagram. Without knowning relay specifics it was not known weather the relay was energized or not. <I> **** Actions Taken **** Informed CRS and got permission to move forward. | 02-00-CF-MX-4
395811 | CR | 20190619 | CAQ | D | 1000# steam tunnel entry leaks | N | N |  | N | YES | <C> CR reopened to cross reference additional WO 02044837 marked completion required box, then taken back to complete <D> **** Detailed Description **** During the 1000# steam tunnel entry the following leaks were identified. RFW-V-65A was leaking 1 DPM at the packing, RFW-V-65B following packing torquing was still leaking 1 DPM, Swaglok connection downstream of RFW-V-908A was identified to be leaking but was tightened and the leak stopped. This CR is to track work for future outages. <I> **** Actions Taken **** Adjusted/tightened when possible wrote CR | 02-00-RFW-V-65A,02-00-RFW-V-65B
395812 | CR | 20190619 |  | 3 | create WO instructions for I&C 8.3.381 support |  |  |  | N | NO | <D> **** Detailed Description **** step 6.8.30 of Reactor Feedwater Turbine Uncoupled Overspeed Test 8.3.381 has I&C perform a calibration of the feed water turbine overspeed device RFT-RLY-99T1X/1B. This is not a simple task and needs to have work instructions created. ****ALSO****this task should be performed/scheduled prior to mechanical overspeed testing. This would prevent us from delaying start up. <I> **** Actions Taken **** wrote this AR
395813 | CR | 20190619 |  | 3 | Step S33 in PPM 3.1.2 needs enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Step S33 in PPM 3.1.2 references a superseded surviellance (TSP-MSRV/IST-R701). <I> **** Actions Taken **** Wrote AR.
395814 | CR | 20190619 |  | 3 | R24LL Look at the OSCR Deferral process for outages to defer |  |  |  | N | NO | <D> **** Detailed Description **** Look at the OSCR Deferral process for outage to defer individual tasks instead of the whole work order so that task that still need to be completed do not get remvoed from the outage schedule. Initial action to this CR needs to go to myself, David Weller. <I> **** Actions Taken **** Initiated this CR. <N> After reviewing procedure OMI-2.1 for the Deferral of work from a Refueling outage there are no changes to the procedure. This CR is closed.
395815 | CR | 20190619 |  | 4 | TMU quarterly EBU inspection | N | N |  | N | YES | <D> **** Detailed Description **** Failed fixture found during EBUTMU01. Low battery capacity. Recomend replacing with LED EBU. <I> **** Actions Taken **** iniciate CR and WR. Notified supervision. <N> **** Equipment Description **** TMU pumphouse | 02-00-E-BU-TMU375/1
395816 | CR | 20190619 | CAQ | D | Drywell Shield Door Lower Locking Pin Overextended | Y | N |  | N | YES | <D> **** Detailed Description **** During closure of the Drywell Personnel Shield Door the locking pins were overextended in the closed direction. The lower locking pin was overextended to the point it became unscrewed and did not come open when the hand wheel was taken back in the open direction. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** Drywell Personnel Access Shield Door Rx 501
395817 | CR | 20190619 |  | 3 | quarterly HID lighting inspection |  |  |  | N | YES | <C> CR Re-Opened. <D> During performance of 10.25.64 we found that fixture #3 ELP-8AD-3 functioned with circuit #6 not #3 as listed. Circuit #3 had a local tag on it (we did not operate circuit #3) Tag 01-05986 <I> CR. notified supervision <N> E-ELP-8AD/3 CR at INPROG. Approved CR, moved to SRO for OPS Review. Non-essential lighting.
395818 | CR | 20190619 |  | 4 | MS-V-166A â€“ No open Indication | N | N |  | N | YES | <D> **** Detailed Description **** MS-V-166A has no open indication when latching the main turbine following the transition to mode one. | 02-00-MS-V-166A
395819 | CR | 20190619 |  | 4 | Seal steam leakoff lline B RFW turbine LP stop | N | N |  | N | YES | <D> **** Detailed Description **** 10-15 DPM leak from the seal steam leakoff line between BS-V-60B and SS-RO-7B (can be seen from west side of RFW -DT-1B below BS-V-60B. leak from under lagging, makes it difficult to pinpoint leak exact locatiopn. | 02-00-BS-V-60B
395820 | CR | 20190619 |  | 3 | Two instrument isolation valves out of position | N | N |  | N | YES | <D> **** Detailed Description **** While performing a RFW-DT-1B Panel lineup during the uncoupled testing of RFT-P-1B, two instrument isolation valves were found out of the normal position. Valve 61 was found open (should have been closed) and Valve 27 was found closed (should have been open). Both valves have been placed in their required normal positions. Status control had not yet been regained following RFT-B the maintenance activity. <I> **** Actions Taken **** Wrote CR. | 02-00-RFW-DT-1B
395823 | CR | 20190619 |  | 4 | R24 LL: Late ID of Outage materials after 5/12/19 start | N | N |  | N | NO | <D> **** Detailed Description **** After the start of R24 on 5/12/19, there has been 1,060 MR's created and 1,988 line items requested between 5/12/19 and 6/19/19. This creates unexpected cost and Supply Chain's ability to meet outage milestones. We should be more predictable and accountable for our planning and walkdowns to correctly meet milestones. In R23 during the same time period there were 88 MR's created and 376 line items requested. This equates to a 91% increase over R23 for material requests this outage. Also associated with these late ID materials are the unplanned high expediting costs. Material identification needs to be accurate and timely to be successful and not impact the outage schedule. <I> **** Actions Taken **** Notified my supervision and outage management. <N> Note that these represent emergent items ordered after 5/12/19 date.
395824 | CR | 20190619 |  | 3 | Procedure enhancements OSP-RCIC/IST-C701 and -B501 | N | N |  | N | NO | <D> **** Detailed Description **** Section 7.6 of the B501 procedure states in a NOTE that OSP-RCIC/IST-C701 may be used to satisfy the requirements of this section. However, there are several # sign steps in the B501 section 7.6 that do NOT have corresponding # sign steps in the C701 procedure. The # sign steps should be the same or equivalent if one procedure is satisfying the other. <I> **** Actions Taken **** Reviewed both procedures that were performed for R24. Discussed with CRS and OCC Ops Rep to confirm that all required # sign step requirements were met. Intiated CR to improve the procedures. All # sign requirements were met for the LSFT B501 procedure.
395825 | CR | 20190619 |  | 3 | Procedure enhancement for CSP-INST-D201 | N | N |  | N | NO | <D> **** Detailed Description **** On page 6 the BD-RAD-24 information that we acquire could include the TSW operability status. If we don't check that status (either on the recorder or the TSW-RIS-5) we will still get data for flow and activity. It may not be apparent for new chemistry technicians that the rack is not functioning and an ODCM requirement could be missed. <I> **** Actions Taken **** Chemistry supervisor/specialist informed
395826 | CR | 20190619 |  | 3 | MALT EC 13532 needs revised or converted to standard design | N | N |  | N | NO | <D> **** Detailed Description **** During the planning of WOs for replacement of the 500KV expansion couplers it was identified that the parts in EC 13532 could not be purchased through BPA. While reviewing the EC it was also determined that some details with the installation were not included (i.e. vibration dampener and bus saddle) in the design. The purpose of the CR is to revise the EC and determine all parts required for the installation of new expansion couplers prior to R25. <I> **** Actions Taken **** Discussed with Design engineering manager and EFIN supervisor and prepared this CR. This is an administrative issue and it has no impact on equipment installed at the station.
395828 | CR | 20190619 |  | 3 | HD-LCV-5A21 Degraded Condition | N | N |  | N | YES | <D> **** Detailed Description **** AOV Program Trending. HD-LCV-5A21 appears to have Magnatite build up in the internal trim assembly. Needs open/inspect and refurbishment in R25 or earliest oppurtunity. <I> **** Actions Taken **** Notified AOV program owner and documented findings on trace analysis. <N> **** Equipment Description **** 571' Htr. Bay | 02-00-HD-LCV-5A21
395829 | CR | 20190619 |  | 3 | (QA) Unauthorized Coating Used In TSW Side Of Heat Exchanger | N | N |  | Y | YES | <D> **** Detailed Description **** (QA) Two Work Order Tasks (WOT) applied â€œCeramAlloy CL Gray/Blueâ€ to the internals of Plant Service Water (TSW) side of Heat Exchangers that was not authorized via the Chemical Permit, Engineering Evaluation, or approved procedure. (See EDMS for details) <I> **** Actions Taken **** Notified OCC Operations Manager due to Control Room critical evolutions, Quality Management, initiated AR-CR. This issue was identified during the Special Processes Audit AU-SP-19. | 02-00-TSW-HX-7A,02-00-TSW-HX-7B,02-00-TSW-HX-7C,02-00-TSW-HX-7D,02-00-TSW-HX-8
395830 | CR | 20190619 |  | 3 | R24LL - Chemistry Sample required prior to drywell inerting | N | N |  | N | NO | <D> **** Detailed Description **** The SOP-CN-CONT-INERTING procedure has a step 5.1.2 that states "REQUEST Chemistry sample and analyze the Primary Containment noble gas, iodine, and particulate within 8 hours prior to start of the PURGE, per PPM 16.11.3." The NOTE just prior to that step says the sampling takes approximately 2 hrs. The 2 hour task for chemistry does not appear in the Schedule and is not tied as a "Predecessor". This causes a 2 hour delay in starting to intert containment which also impacts when a Nitrogen delivery for CN-TK-1 will be needed. Recommend a task in the schedule for the Chemistry sample and tied as a predecessor to the INERT task for Ops. <I> **** Actions Taken **** Discussed with outage scheduler.
395833 | CR | 20190619 |  | 3 | PPM 12.5.44 requires a procedure enhancement | N | N |  | N | NO | <D> **** Detailed Description **** PPM 12.5.44 requires a procedure enhancement. The "Termination of Cross Tie SP-8 to SP-1" section on page 6 should be the start of a new section, i.e. 5.5, but it is continued from the previous section 5.4. <I> **** Actions Taken **** Initiated AR/CR and notified the procedure sponsor.
395834 | CR | 20190619 |  | 3 | Self imposed limitation | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The standards lab was unable to calibrate a customers instrument due to self imposed limitations even though the limited equipment is specifie dto perform much more accurately <I> **** Actions Taken **** Contactedcustomer to verify their requirements. Contacted an outside vendor to ge a quote on having the unit calibrated off site. Discussed with subject matter expert as to reasons for limitations. (unit does not have a history of performing at specified tolerances) <N> Uncertainty budget reviewed and accepted. Budget details have been uploaded into the EDMS panel. Assignment is complete.
395835 | CR | 20190619 |  | 4 | MS-PCV-9A found with air line disconnected | N | N |  | N | YES | <D> **** Detailed Description **** While investigating a packing leak it was discovered that the air control line to the actuator was disconnected and capped off. Histoy shows the last work done on this valve was performed in 2013 and the PMT was cancelled <I> **** Actions Taken **** Recommend restoring the air line and torquing down on the packing nuts to stop the leakage <N> **** Equipment Description **** T -455- - -G1/12.9- | 02-00-MS-PCV-9A
395836 | CR | 20190619 |  | 4 | Multiple non-return valves indicate the wrong position | N | N |  | N | YES | <D> Multiple non-return valves indicate the wrong position per SOP-FWH-START. BS-V-5A, BS-V-7A, BS-V-5B and BS-V-7B indicate mid position when they should indicate closed. HD-V-32A indicates full open and it also should be closed. These indications are consistent between the instrument racks and the MCR. The valves were not inspected locally. This is per steps 5.1.17 thru 5.1.20 of SOP-FWH-START. (WR not generated since Portal J crashed on CR submission) <I> Wrote CR Informed CRS <N> Stuck at in-prog moved forward upon notification from the author. | 02-00-BS-V-5A,02-00-BS-V-5B,02-00-BS-V-7A,02-00-BS-V-7B,02-00-HD-V-32A
395837 | CR | 20190619 |  | 3 | MS-TCV-116B Degraded | N | N |  | N | YES | <D> **** Detailed Description **** AOV Program Trend. MS-TCV-116B Diagnostic data indicates internal valve issues. Possible Magnatite build up. Also during the last run cycle leading up to R24 an active packing steam leak was observed. Valve was repacked in R24. Diagnostic data and visual observation indicate the valve needs to be opened and inspected. The plug/Stem Assembly and valve trim should be replaced. Also due to the steam leak the Actuator needs new elastomers and the Positioner needs to be replaced in R25. The Limitswitches should also be inspected, repaired/Replaced as needed. <I> **** Actions Taken **** Notified AOV program owner and documented findings via this CR and diagnostic test report. <N> **** Equipment Description **** 501' TB | 02-00-MS-TCV-116B
395838 | CR | 20190619 |  | 3 | Insufficient radiation evaluation in EC 14871 for CIM | N | N |  | N | NO | <D> **** Detailed Description **** EC 14871 installed Rosemount transmitters inside the bioshield in the TG501 and TG471 areas for Cycle Isolation Monitoring (CIM). Although the high radiological exposures were identified, the EC did not adequately assess the impact on the transmitters. The EC identified TG501 dose rates were 5-1200 mrem/hr and TG471 dose rates were 20-2000 mrem/hr based on survey results, while the electronics in the transmitters have a generic capability of 10^3 rads per EPRI report 1021067. This generic capability would provide a 10 year life for the transmitter in a radiation field of approximately 10 mrem/hr. At the levels indicated during the HP survey, the life of the transmitters would range from 0.05 years (for 2000 mrem/hr) to 22 years (for 5 mrem/hr). This oversight may be the cause for several failures of these transmitters within the first cycle of operation (CR 383469). Per discussion with EQ Engineer. <I> **** Actions Taken **** Initiated CR. Discussed with EQ Engineer, EOC, and Design Engineering.
395840 | CR | 20190619 |  | 4 | MS-BVS-DT/1B/2 sensor stuck in guide tube needs WO | N | N |  | N | YES | <D> **** Detailed Description **** At end of R22 it was identified that MS-BVS-DT/1B/2 bushing/sensor was stuck in the guide tube. this was broken because of failing to hold the probe assembly to keep it from rotating during removal activity. WO 02076740 changed the wiring to use a spare sensor, but it appears that a WR/WO was never generated to repair the broken sensor. This should be scoped into a future outage to replace this broken sensor. <I> **** Actions Taken **** Wrote CR and generated a WR | 02-00-MS-BVS-DT/1B/2
395841 | CR | 20190619 |  | 4 | HD-LIC-6A and HD-LIC-6B are controlling very high | N | N |  | N | YES | <D> **** Detailed Description **** FWH-6A is currently indicating off scale high and FWH-6B is controlling at +5 in to +6 in. Both HD-LIC-6A and HD-LIC -6A2 indicate their valves are full open but they are having no effect on level. HD-LIC-6B and HD-LIC-6B2 also indicate full open but they are at least controlling level on scale. <I> **** Actions Taken **** Wrote CR Informed CRS and OCC | 02-00-HD-LIC-6A,02-00-HD-LIC-6B
395842 | CR | 20190619 |  | 3 | Main Turbine Vibration during startup | N | N |  | N | YES | <D> **** Detailed Description **** During initial turbine roll, when performing Step 5.3.19 of SOP-MT-START which increases turbine speed from 800 RPM to 1750 RPM, vibration levels escalated rapidly when ascending above 1575 RPM. Bearing 7 peaked at approximately 9.1 mils when at 1735 RPM and settled at around 7.3 mil at 1800 RPM (FSNL). Bearing 8 peaked at approximately 7.7 mils when at 1735 RPM and settled at around 6.4 mils at 1800 RPM (FSNL). One other value to note is that Bearing 5 peaked at 5.1 mils when 1800 RPM was achieved, and settled at 4.8 mils at 1800 RPM (FSNL). This is higher vibration level than recommended, but is fairly close to pre-outage levels. OSP-MT-B401 was performed which trips the turbine and relatches three times. Following completion of the procedure, the vibration levels settled out a little lower (Bearing 7 at 7.1 mils, Bearing 8 at 5.9 mils, and Bearing 5 at 4.4 mils). <I> **** Actions Taken **** Discussed with MCR, EOC, and engaged EOM vibration expert. Contacted turbine PM to ready Level 5 contingency balance Work Order. <N> CORRECTION: Bearing 4 is at roughly 5.1 mils, NOT Bearing 5. (TYPO) | 02-00-MS-DT-1C
395843 | CR | 20190619 | CAQ | C | R24 CRDM Exchange Project exceeded dose estimate | N | N |  | N | YES | <C> AR is being changed from Sev. 3 to a CAQ C by MRT due to Potentially adverse to regulatory compliance <D> **** Detailed Description **** The dose estimate of 6.850 P-Rem for R24 CRDM Exchange was presented to SSAC for challenge on 03/12/19. This work finished with a dose expenditure of 10.490 P-Rem, or 153% of estimated dose. Unforeseeable scope growth and higher than anticipated dose rates were the main contributing causes for this dose over run. <I> **** Actions Taken **** Notified RPM and documented CR. <N> **** Equipment Description **** Control Rod Drive Mechanisms Drywell Undervessel
395844 | CR | 20190619 | CAQ | C | R24 LLRT exceeded dose estimate | N | N |  | N | NO | <C> AR is being changed from Sev. 3 to a CAQ C by MRT due to Potentially adverse to regulatory compliance <D> **** Detailed Description **** The dose estimate of 7.043 P-Rem for R24 LLRT was presented to SSAC for challenge on 04/02/19. This work finished with a dose expenditure of 10.571 P-Rem, or 150% of estimated dose. Unforeseeable scope growth and higher than anticipated dose rates were the main contributing causes for this dose over run. <I> **** Actions Taken **** Notified RPM and documented CR.
395845 | CR | 20190619 |  | 4 | corrosion found on E-EQ-B1/9 battery | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** while performing quarterly inspection of spare station batteries in Bldg 19, electricians noted corrosion and discoloration of intracell connector between cell 12 and 13. An attempt was made to clean the connector but the corrosion runs deeper than just the surface material. Cleaning would be too intrusive. The connector needs to be replaced and monitored for trending degradation. WO#02114098-01 <I> **** Actions Taken **** Notified engineer, notified Supervisor Write CR and WR to replace connector. <N> **** Equipment Description **** E-EQ-B1/9 BLDG 19
395846 | CR | 20190619 |  | 4 | TG-H2IS-1 ch 4 failure (Exc Doghouse) Start up constraint | N | N |  | N | YES | <D> **** Detailed Description **** TG-H2IS-1, Channel 4 is indicating "Fail". Per ARP (4.800.C3) this is due to an internal failure or connection issue. Channel 4 was recently recalibrated via WO 02111649, as a result of displaying 95% LEL on 4-21-19. This is preventing MG synch to grid. Past failures of TG -H2IS-1 have been mitigated by setting up a temporary H2 monitor locally at the Exciter. See WR# 29122544 for past occurances. Several failures of Channel 4 have occurred over the last 10 years. <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** TG 471W Per the TG-H2IS-1 IMDS, channel 4 input is from TG-H2E-EXC/1 | 02-00-TG-H2IS-1
395849 | CR | 20190619 |  | 3 | MT turbine lock out on Volts/Htz relay. | N | N |  | N | YES | <D> **** Detailed Description **** Last observed inditcation on the pride relay was 1.36v/hz. This is the only dropped flag on the lock. Investigate and correct. Also obeserved were some unusual indications on the voltage whilst trying to sync the MG. System engineer was actively investigaing in the field when turbine tripped. <I> **** Actions Taken **** Followed appropiate ABNs and procedures | 02-00-E-GEN-1,02-00-E-RLY-59/81G1
395850 | CR | 20190619 |  | 4 | 2 Gas Monitor Rejections | N | N |  | N | NO | <D> **** Detailed Description **** 2 Industrial Scientific Gas Monitors model iTX have been Rejected- Parts No Longer Available. Used for personal safety only. No Plant Impact. Calcode #0065647. DEF #7055A written. Calcode #0066751. DEF #7056A written. No Action Required.
395852 | CR | 20190619 |  | 4 | RFW-VBI-XE/P1A is reading erratic. | N | N |  | N | YES | <D> **** Detailed Description **** RFW-VBI-XE/P1A is reading erratic. Currently A RFW-DT-1A is in speed control at 2800 RPM. No abnormal noises or rubbing reported locally. Reading were ranging from +13 mils to -20 mils on RFW-VBI-XE/PIA. <I> **** Actions Taken **** Informed CRS/SM | 02-00-RFW-VBI-XE/P1A
395854 | CR | 20190619 |  | 4 | Low pressure out of Filter/Regulator for HD-E/P-6A2 | N | N |  | N | YES | <D> **** Detailed Description **** Upon investigating the High trip of RFW-HX-6A, it was discovered that the air supply to HD-E/P-6A2 is at 0 psig. All other air supply indicators nearby are at least 20 psig. <I> **** Actions Taken **** WR written. Entered ABN-FWH-HILEVEL/TRIP <N> **** Equipment Description **** TB 501 east IR 6A | 02-00-HD-E/P-6A2
395855 | CR | 20190619 |  | 4 | E-LP-5DA circuit 18 tripped | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing forklift battery inspection on the 437 a portable demin water pump was plugged into a receptacle fed from E-LP-5DA circuit 18. The circuit breaker tripped shortly after plugging the pump in. <I> **** Actions Taken **** Notified SSS and obtained permission for a one time reset of the breaker. Cycled the breaker to the off position to reset it then back to the on position. Breaker tripped free again. Notified SSS of the condition, notified supervision, wrote CR <N> **** Equipment Description **** E-LP-5DA-18 CIRCUIT BREAKER
395857 | CR | 20190619 |  | 4 | Level 1 Filing Not Completed in the MCR | N | N |  | N | NO | <D> **** Detailed Description **** The Level 1 procedure filing in the main control room was not performed today due to the critical evolution (start up) that was in process. <I> **** Actions Taken **** The PSRO was contacted in regards to the filing and recommended that the filing wait until tomorrow. The CR is being initiated for trending purposes only.
395859 | CR | 20190619 |  | 4 | TRS Link Non-Seg Thermal Windows | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02113448-01 IR -STARTUPTRANSFORM: E-TR-S THERMOGRAPHY @ 20% POWER, two of the thermography window covers are missing (western-most for E-DISC-LINK/S/Y1 and eastern-most for E-DISC -LINK/S/X3). Windows were too dirty to obtain thermal images. Link images were obtained from the next closest windows. Additionally, the remaining windows with covers have dirt on the inside. During the next refuel outage, replace the thermal windows for the western-most for E-DISC-LINK/S/Y1 and eastern-most for E-DISC-LINK/S/X3. Also clean the inside windows of the remaining thermal windows. PM was completed using alternate windows. | 02-00-E-TR-S
395860 | CR | 20190619 | CAQ | D | IRM C reading is erratic. | Y | Y |  | N | YES | <D> **** Detailed Description **** IRM C reading is erratic on both IRM-LR-603C on H13 P603 and H13 606 IRM C. <I> **** Actions Taken **** Informed CRS/SM | 02-00-IRM-DET-2C
395862 | CR | 20190619 |  | 4 | E-EXC-1 Base adjuster alarms | N | N |  | N | YES | <D> **** Detailed Description **** During the investigation to the trip E-GEN-1 associated with AR-CR 00395849 the following alarms were shown on the base adjuster daughter boards for E-EXC-1 at the WTA regulator cabinet. Daughter Board A â€œAnalog Output Failureâ€ Daughter Board B â€œSister Board Failureâ€ These alarms were identified by the system engineer during a walkdown of the WTA cabinet after the generator lockout. | 02-00-E-EXC-1
395863 | CR | 20190619 |  | 4 | Main generator tripping base adjuster issue | N | N |  | N | YES | <D> **** Detailed Description **** During R24 sync , Main Generator tripped on 86LO Volts/Hz. WTA base adjust programmable module replacement alarm displayed â€œanalog output failureâ€ .The cause could be the base adjuster for this trip. Base adjuster provides voltage to the field. Base adjuster might needs to be reset or replaced. <I> **** Actions Taken **** Notified EOC | 02-00-E-EXC-1
395864 | CR | 20190619 |  | 3 | Inadequate markup provided for PPM 10.2.236 |  |  |  | N | NO | <D> **** Detailed Description **** The markup for overhaul of HCV-V-54 under assignment AR -347474-46-13 installed under EC-13094 in 2017 was a copy of several pages of the OMM. The markup did not take into account that the valve is installed on the outside and on top of the Reactor Building 672 feet off the ground, nor did it provide any needed plant conditions for maintenance, such as breaching secondary containment. The seat is required to be replaced every 10 years per PMRQ 26509. Recommend keeping valve in place and replacing internals from the installed maintenance platform vice renting a big crane. <I> **** Actions Taken **** Initiated CR, this is an administrative issue for a ten year PM, see EDMS.
395865 | CR | 20190619 |  | 3 | MS-TCV-115B Degraded | N | N |  | N | YES | <D> **** Detailed Description **** AOV Program Trending. Diagnostics indicates unusual internal valve friction. need to open/Inspect repair/Replace valve stem/plug assembly and internals in R25. <I> **** Actions Taken **** Notified AOV program owner and documented via this CR and diagnostic report. <N> **** Equipment Description **** 501' TB | 02-00-MS-TCV-115B
395866 | CR | 20190619 |  | 3 | Lack of spare parts/ gaskets for HCV-V-54, HCV-EQ-2 |  |  |  | N | NO | <D> **** Detailed Description **** As part of EC-13094, installed in 2017, a BOM was not created for materials needed for maintenance and refurbishment of new HCV-V-54. Need Materials and parts identified and Cat ID's issued in order to create procedures and plan maintenance/ repairs. <I> **** Actions Taken **** Initiated CR, this is an administrative issue for four year PMs.
395867 | CR | 20190619 | CAQ | C | No PM initiated for new HCV-EQ-2 | N | Y |  | N | NO | <D> **** Detailed Description **** HCV-EQ-2, Weather shroud that blows off at +/- 2psid was installed under EC-13094 but no AR-SMS has been generated to determine planned maintenance that needs to be performed. In order to access HCV-V-54 for maintenance in a 4-year PM, HCV-EQ-2 needs to be moved which could affect the operability of HCV-EQ-2. <I> **** Actions Taken **** Initiated CR, this is an administrative issue.
395868 | CR | 20190619 |  | 3 | CVI OMM 1260-01,3,3 not in Asset Suite |  |  |  | N | NO | <D> **** Detailed Description **** OMM for HCV-V-54, a Twinline double door check valve is not available in Asset Suite. HCV-V-54 was installed under EC-13094. The OMM is needed to reference in order to plan maintenance. <I> **** Actions Taken **** Initiated CR, this is an administrative issue. <N> See assignment 01 response. The CVI information is considered to be confidential and therefore, cannot be uploaded to Asset Suite. Anyone looking for this information will need to go to Document Control to view the information. No further actions are needed. The parent AR is now closed.
395869 | CR | 20190619 | CAQ | C | No PM initiated for 3V Battery in HCV-RIS-RAD/1 | N | Y |  | N | NO | <D> **** Detailed Description **** The RM-1000 contains a 3v coin style replaceable Lithium battery that has a self-life of five years. HCV-RIS-RAD/1 was installed under EC-13094 in 2017 but no AR-SMS has been generated to determine planned maintenance that needs to be performed for the replaceable battery in the radiation monitor. Will also need a CAT ID for the battery. <I> **** Actions Taken **** Initiated CR, this is an administrative issue.
395870 | CR | 20190619 |  | 4 | RFW-HX-6A tripped on high level. | N | N |  | N | YES | <D> **** Detailed Description **** HD-E/P-6A2 low pressure caused no response from level control valves. This caused a high level trip and will impact power ascention | 02-00-HD-E/P-6A2
395871 | CR | 20190619 | CAQ | D | FP-PI-D58 reading high | N | N |  | N | YES | <D> **** Detailed Description **** The Deluge 58 systems priming chamber PI is reading 260psi which is well above the expected 175psi. piping should be vented or gauge replaced. <N> **** Equipment Description **** TG 441 N. E. side | 02-00-FP-PI-D58
395872 | CR | 20190619 |  | 4 | TG-H2IS-1 channel 4 fail light on. | N | N |  | N | YES | <D> **** Detailed Description **** TG-H2IS-1 channel 4 fail light on and won't reset locally. <I> **** Actions Taken **** MCR notified <N> **** Equipment Description **** tb471 west side on wall under main generator | 02-00-TG-H2IS-1
395873 | CR | 20190619 |  | 4 | E-CB-LP5DA/23 found trip free. | N | N |  | N | YES | <D> **** Detailed Description **** E-CB-LP5DA/23 (outside lightining normal position is ON) was found trip free position. Obtained supervisor permission reset it and attempting to close in. It instantly tripped. <I> **** Actions Taken **** reset and ttempted closing failed. Informed supervision. | 02-00-E-CB-LP5DA/23
395874 | CR | 20190619 |  | 4 | E-LP-5DA/18 found off and failed to shut. | N | N |  | N | YES | <D> **** Detailed Description **** E-LP-5DA/18 was found off and HP requested closing (they had need of it, powers receptacles). Attempted to close it (normal position is ON) and it would not stay close and juts returned to open position (not tripped). <I> **** Actions Taken **** Found E-LP-5DA/18 found OFF and failed in attempt to close it. Informed HP and informed supervision. | 02-00-E-LP-5DA
395875 | CR | 20190619 |  | 4 | HD-LCV-6A2 slight binding on opening stroke. | N | N |  | N | YES | <D> **** Detailed Description **** During stroking of valve HD-LCV-6A2 in accordance with WR 29149990, slight binding appeared to be occuring during the opening stroke. The valve was observed to stroke 3 times and the same slight jerky motion was observed each time. See EDMS video. <I> **** Actions Taken **** Notified EOC/OCC engineering and operations. <N> **** Equipment Description **** T -445- - -C7/10.7- | 02-00-HD-LCV-6A2
395876 | CR | 20190620 |  | 4 | RWCU blowdown pressure high/low alarm back in. | N | N |  | N | YES | <D> **** Detailed Description **** RWCU blowdown pressure high/low alarm back in following shutting down the RWCU letdown path. (H13.602.A5-5.7) <I> **** Actions Taken **** Depressurized the Blowdown piping downstream of RWCU-FCV-33 per SOP-RWCU-OPS section 5.5. Alarm cleard and returned after approx. 1 min. | 02-00-RWCU-FCV-33
395877 | CR | 20190620 |  | 4 | TSW-SR-34 Inop | N | Y |  | N | YES | <D> **** Detailed Description **** TSW-SR-34 inop due to low flow. <I> **** Actions Taken **** Informed the CRS and chemistry supervision. | 02-00-TSW-SR-34
395878 | CR | 20190620 |  | 4 | Limit Switch Cover labeled RCIC-V-76 found on Rx501 | Y | N |  | N | I DONT KNOW | <C> CR Changed from a CAQ D to a Non CAQ 4 by MRT <D> **** Detailed Description **** Limit Switch Cover and Stem Protector with labeling for RCIC-V-76 found on the Rx501. <I> **** Actions Taken **** Electrical Supervision and the OCC informed Posted a sign on the Limit Switch cover to have it saved. . Reviewed work history and a lube/inspect full PM was performed on RCIC-MO-76 under WO 02110811. A torque switch replacement, followed by a diagnostic test was then performed (OSCR 394352). Step 7.6.3 of PPM 10.25.132 (Diagnostic Testing), instructs restoration of the actuator after test equipment is removed. This would include reinstallation of the torque switch cover. The subject torque switch cover found on RX 501 did not have its T valve installed supporting the idea of it being removed and installed on a different cover. Also, a walkdown of RW 507 identified a spare actuator without its cover installed. The valve engineer had discussion with the day and night shift supervisors for the job and the technician who performed the work verifying the cover was reinstalled. The dust cover is not a critical component per Flowserveâ€™s Evaluation Critical Components List (ECC) â€“ ECC 0001 Rev 7. These covers are interchangeable amongst other similar actuators. The switch out of these covers is not a QC activity and is not traced within the work package. This evidence provides high confidence that the limit switch cover on RCIC-MO-76 is currently in place within the drywell. <N> **** Equipment Description **** Rx501 on a cart near the staged scaffold stacked from R24 Drywell work.
395882 | CR | 20190620 |  | 4 | Discrepancy between manual and field setting for voltage reg | N | N |  | N | YES | <D> **** Detailed Description **** Discrepancy between manual and field setting for voltage regulator base adjustor upper board. ADCP in the field was set to 3764, manual calls for 3476. On the bench with a setting of 3476 the check sum value was E612, which does not match the check sum value in the manual of E504. Field value of 3764 was used. This was discovered during replacement of components under WR 29149988. <I> **** Actions Taken **** Contacted OCC/EOC <N> Please assign 3 to SEEIC | 02-00-E-EXC-1
395883 | CR | 20190620 |  | 4 | CW pH Control is not controlling the CW pH | N | N |  | N | YES | <D> **** Detailed Description **** The CW pH controller is not controlling the pH of the CW system. Set point is 8.2. pH is slowly dropping indicating that there is acid leaking by the control valve or the controller is not working. The CW acid system that controls CW pH was placed back into service on 6/18 at 2120. The CW pH has slowly dropping since this was put into service. Make up water, TMU, is 8.1 pH. The DVS, scale control and inhibitor, is low pH but after the manual addition, the DVS effect levels out. Current CW pH is approximately 7.9. A CW sample was checked for comparison and read the same as the continuous pH meter. During the R24 outage with the acid system down, the pH rose slowly. <I> **** Actions Taken **** Recommend having maintenance repair the system or temporarily shut the system down and wait for the system pH to rise, then restart the system. Once power and heat to the CW system is back to near normal, the controller should have no problem controlling the pH. The acid controller keeps the pH in the best range for the corrosion and inhibitor (DVS) to function. <N> **** Equipment Description **** CW Continuous pH Meter
395884 | CR | 20190620 | CAQ | D | Received Recirc B System Vibration high alarm | N | N |  | N | YES | <C> CR reopened to cross reference additional WR 29150824, marked completion required box, then taken back to complete <D> **** Detailed Description **** eceived Recirc B System Vibration high alarm, vibration panel indicates the point in alarm is RRC-VBI-P1B/XE reading +46 mils, Temperatures on RRC-TRS-601 for RRC-P-1B are stable not raising. <I> **** Actions Taken **** Informed CRS. | 02-00-RRC-VBI-P1B/XE
395887 | CR | 20190620 |  | 3 | (Planning) No FMR hold on WO 02130589-01 WOA-SMD-1B |  |  |  | N | NO | <D> **** Detailed Description **** No FMR hold on WO 02130589-01 WOA-SMD-1B. Ensure there is a Fire Marshal Review FMR) hold on the model for this WO, otherwise the task will go directly to records after the supervisor review and bypass the FMR review. <I> **** Actions Taken **** Added FMR review to this task still need model corrected by planning.
395890 | CR | 20190620 |  | 3 | (R24) No TV/GV transfer due to LT 1750rpm turbine speed. | N | N |  | N | YES | <D> **** Detailed Description **** During startup from R24 main turbine speed failed to reach 1750rpm preventing the TV/GV transfer. The turbine was subsequently manually tripped and placed on the turning gear . <N> AR-EVAL 395927 initiated to evaluate permanent design change to mitigate re-occurrence of this issue. | 02-00-E-GEN-1
395894 | CR | 20190620 |  | 4 | CW automatic pH control is controlling low | N | N |  | N | YES | <D> **** Detailed Description **** The automatic CW pH controller (CW-PHIC-1) is set at 8.2 however local indication is 7.42 and the Chemistry grab sample is 7.5. There appears to be an issue with the automatic controller. <I> **** Actions Taken **** Informed Chemistry Taking manual control of the pH controller CW-PHIC-1 Hanging a Caution tag on controller for PCS Informing FIN | 02-00-CW-PHIC-1
395895 | CR | 20190620 | CAQ | D | Management CR review quorum not met |  |  |  | N | NO | <D> **** Detailed Description **** An Engineering representative was not in attendance at the Management Condition Report Review meeting. This is not in accordance with SWP-CAP-06. Acting PGM approved continuing without quorum. This CR is to document the deviation from the procedure. <I> **** Actions Taken **** Recommend D-Trend. No further actions necessary.
395897 | CR | 20190620 |  | 3 | SOP-MT-START - ramp rate minimum not met |  |  |  | N | NO | <D> **** Detailed Description **** During performance of SOP-MT-START the minimum ramp rate of 80 rpm per minute (step 5.3.19g) was not complied with. Ramp rate (from eDNA and report from operators) was 60 rpm per minute. <I> **** Actions Taken **** Operators and supervisors benched until the issue can be investigated. <N> individuals were interviewed, issue is understood, and coaching provided. Ops requesting a 3 so we can change the procedures.
395898 | CR | 20190620 |  | 3 | R24 LL: Refuel Outage startup challenges |  |  |  | N | NO | <D> **** Detailed Description **** Challenges during R24 startup may have had precursor events in previous outages that may have not been addressed. Recommend a review of refueling outage performance (last 10?) to identify startup plant challenges and anomalies for resolution (procedure changes, corrective work, evaluation). Examples from R24 may be main generator voltage regulator base adjuster issue and DEH ramp up to TV/GV transfer. Recommend assign to System Engineering
395903 | CR | 20190620 |  | 3 | R24 LL â€“ Mechanical plugs (POP-A-PLUG) installation training |  |  |  | N | NO | <D> **** Detailed Description **** Itâ€™s recommended to have a training or refresher training to boilermakers and in-house mechanics on how to install mechanical plugs (POP-A-PLUG) in all heat exchangers. This training (or refresher) could be done onsite before an outage in coordination with Curtiss-Wright (EST group). Recommend action to FWHs and Condenser Project Manager for planning this activity for R25. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
395904 | CR | 20190620 |  | 4 | Declared Prohibited Item at the Security Checkpoint |  |  |  | N | NO | <D> **** Detailed Description **** BPA Contractor had pepper spray on their keychain while attempting to enter the SDOCA. <I> **** Actions Taken **** BPA contracted employee declared the item after being asked by security. The individual was not allowed access to site. Ops Manager notified via the OCC, Security Supervision notified, Benton County notified, generated CR and Security opened SEL.
395906 | CR | 20190620 |  | 3 | R24 LL â€“ Heat Exchangers tubes plugging task |  |  |  | N | NO | <D> **** Detailed Description **** Plugging tubes on any heat exchanger including the Main Condenser and MSRs should not planned as a contingency task. Plugging tubes should be planned into the WO package. In addition, in R24, after completing tubes plugging activity based on eddy current testing (ECT) results, the contingency task for tubes plugging was at Finish status for all FWHs and the main condenser WOs. The ultrasonic testing is performed during vacuum pull which usually results in more tubes to plug. With the contingency plugging task is at Finish (after field work completion) we had to recreate new tasks and new Weld Records to plug tubes after sonic testing. Therefore, itâ€™s recommended to add the tubes plugging activity as a step under the Perform ECT task, Perform Leak test task and as a step under the Perform Sonic Testing task. Recommend action to Mechanical planning. Recommend action to Mechanical planning.
395909 | CR | 20190620 |  | 4 | Leak on CO-HX-1 Steam Supply Line | N | N |  | N | YES | <D> **** Detailed Description **** On rounds a leak was found on an Aux Boiler steam line between AS-V-18 and AS-V-12. The line is located approximately 18 feet up next to the handrail on the deaerator platform. The leak was approximately 1 drop / 4 sec. <I> **** Actions Taken **** Notified SSS. Notified laborers who mopped and placed a bucket under leak. <N> **** Equipment Description **** Aux. Boiler Room
395911 | CR | 20190620 |  | 3 | Dwg update needed for Printer output parameter |  |  |  | N | NO | <D> **** Detailed Description **** This is for documentation purpose only and this change is not performance related and does not impact any SSC. This is a request for updating printer parameter output for ASD drives as listed in EWD-3E-207 and EWD-3E-209 .Markup of the dwg is attached in EDMS. Printer output (PO) selects six items to be displayed by the data logger on the printer. P05 and P06 needs to be updated to DC link current and inverter firing angle respectively. .This change will be an enhancement since it allows collecting data necessary for understanding operation of ASD drives . <I> **** Actions Taken **** Notified EOC. <N> What are the requested EWD changes based upon? What are the subject printer EPNs? Is an AR EVAL needed? . CVI OMM 02B35-20,13,6 Section GEH-6014 4-20 defines the variable settings 08 (Link Current) and 12 (Inverter Firing Angle) and is the bases for revising EWD-3E-207. An AR EVAL to provide plant modification is not necessary and the variable change can be accomplished by a Work Request. . EWD-3E-207 can be updated via an ADOC following completion of the change in the field.
395912 | CR | 20190620 |  | 4 | Incorrect gasket installed in RFW B seal steam line | N | N |  | N | NO | <D> **** Detailed Description **** During investigation and repair of a seal steam leak on a 2" 150 lb flange, it was found that a 1 1/2" 300 lb gasket was installed. Indication on the gasket removed showed impressions that it was not centered or fully sealed. See EDMS for pictures. Gasket was replaced with correct gasket on WR#29149963. <I> **** Actions Taken **** Notified Mechanical department manager and PSRO
395913 | CR | 20190620 |  | 3 | PPM 12.14.10 requires a procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** PPM 12.14.10 requires a procedure enhancement. Section 7.2 numbering sequence is incorrect. <I> **** Actions Taken **** Initiated this AR/CR. Informed the procedure sponsor.
395915 | CR | 20190620 |  | 4 | Maintenance Truck with license# 92949C needs oil changed |  |  |  | N | NO | <D> **** Detailed Description **** The information center on Maintenance Truck with license# 92949C says "oil change required"
395917 | CR | 20190620 |  | 4 | OCC Management Text Messages not Received by Some People |  |  |  | N | NO | <D> **** Detailed Description **** On the morning of 6/20/19 at 0118 and 0024, the OCC sent out notifications regarding a voltage regulator replacement that were not received by everyone. AT&T customers did not get the 0118 and 0024 text alerts. However, they did receive the 0430 text alerts. It was verified that the texts were sent to the destination cellular carriers. Text receipt by carriers other than Verizon are not guaranteed, but considered best effort and cannot be tracked. Should a cellular carrier have an outage or the user was in a location with poor or no service, then the text message might not be delivered timely or at all. Per WCI-9, this notification system is a non-accountable communication system, meaning that personnel cannot assume that messages will be delivered. Please assign this CR as a NCAQ 4. <I> **** Actions Taken **** Followed up with an email to Night Shift OCC Mgr.
395918 | CR | 20190620 |  | 4 | COND-P-1A and COND-P-1C low oil level | N | N |  | N | YES | <D> **** Detailed Description **** On rounds COND-P-1C lower oil level was approx. 1/4'' below midline. Rounds state level should be maintained +/- 1/8'' midline. COND-P-1A upper oil level approx. 1/4" below midline. This pump is currently OFF. <I> **** Actions Taken **** Notified SSS <N> **** Equipment Description **** Condensate Pump area
395919 | CR | 20190620 |  | 4 | Combustables in area where not allowed (NRC Identified) |  |  |  | N | NO | <D> **** Detailed Description **** NRC idenified combustables in IR P0021 room, RB501. Door has sign that stated no un-attended combustables are allowed. <I> **** Actions Taken **** Wrote CR and directed operator to remove combustibles. no action required, CR for tracking only. . This material has been removed from this area.
395922 | CR | 20190620 |  | 3 | (NRC) R24 divison 2 battery covers still in place | N | Y |  | N | NO | <D> **** Detailed Description **** The NRC resident questioned the presense of battery covers still in place on the division 2 batteries following R24. <I> Battery covers verified removed.
395923 | CR | 20190620 |  | 4 | RFW-P-1B Servo 1 Alarm in | N | N |  | N | YES | <D> **** Detailed Description **** While starting RFW-P-1B per SOP-RFT-START, Servo 1 Current Foldback Fault alarm came in for RFW-P-1B. The alarm code is P2 fSV1 MBF Current Foldback. The alarm was able to be acknowledged but then came back in shortly after. <I> **** Actions Taken **** Notified CRS Initiated CR and WR | 02-00-RFW-P-1B
395924 | CR | 20190620 |  | 4 | RFW-TMP-P/1B thermocouples were not reinstalled on the pump | N | N |  | N | YES | <D> **** Detailed Description **** RFW-TMP-P/1B thermocouples were not reinstalled on the pump. after energizing and not seeing proper indications it was noted that the thrmocouples were on the frame severeal appeared to be disconnected. <I> **** Actions Taken **** wrote CR/AR informed in field supervisor. | 02-00-RFW-TMP-P/1B
395925 | CR | 20190621 | CAQ | D | MS-PS-3D found OOT | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of ISP-MS-X311, MS-PS-3D was found OOT. As-found trip was found at 149 psig (Tolerance of 136.3 psig to 148.3 psig). Adjusted per step 7.2.37 to an as-left value of 140.4 psig. <I> **** Actions Taken **** Contacted Ops, supervisor, wrote CR for trending.
395926 | CR | 20190621 |  | 4 | Building 76 and building 80 water gong malfunction | N | N |  | N | YES | <D> **** Detailed Description **** While performing 15.1.23 fire protection inspection the water gong for Systems76 and 80 did not operate. Water was flowing out of the drain but not enough to accuate the gong. <I> Non-essential fire protection. <N> **** Equipment Description **** Warehouse 76 and 80
395928 | CR | 20190621 |  | 4 | Contamination found on Protected Equipment area signs |  |  |  | N | NO | <C> Updated the title and description at request of department - added Protected Equipment Sign <D> **** Detailed Description **** Operator alarmed ARGOS exiting HP PAP. Upon survey contamination was found on the hands, paperwork and pants of the Operator with contamination levels up to 10k dpm/pa direct frisk. Operator informed HP that all he did was remove protected equipment area signage from RHR-B-P door. Upon investigation Protected Area signs stored in the storage cabinet in the Aux boiler room, TG 441 were up to 120k dpm/pa direct frisk. <I> **** Actions Taken **** Informed HP Supervision and SM. Discarded affected signs
395929 | CR | 20190621 |  | 3 | Worker injured loading barrels |  |  |  | N | NO | <D> **** Detailed Description **** Laborer injured nose when barrel cart slips from load resulting in a laceration. Worker taken offsite for medical treatment by HP Supervision <I> **** Actions Taken **** Informed SM, Indsutrial Safety, and RPM
395930 | CR | 20190621 |  | 4 | XD 6 | N | N |  | N | YES | <D> **** Detailed Description **** XD 6 failed its daily operability test <I> **** Actions Taken **** unit taken out of service, CR/WR generated | 02-00-SEC-XD-6
395931 | CR | 20190621 | CAQ | D | 2 Pieces of M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** 2 RAD Dig. Battery Torque Wrenches- model DB-RAD 500-2 Passed Closeout Calibration and are now Suspended until R25. Calcode #0068112. DEF #7057A written. Calcode #0068136. DEF #7058A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
395932 | CR | 20190621 | CAQ | D | RCIC-DT-1 outboard bearing oil level low. | Y | N |  | N | YES | <D> **** Detailed Description **** RCIC-DT-1 outboard bearing oil level miniscus is just below the standby (low) oil line. Please add oil. <I> **** Actions Taken **** Notified supervisor. | 02-00-RCIC-DT-1
395933 | CR | 20190621 |  | 4 | SS-PCV-39 not controlling | N | N |  | N | YES | <D> **** Detailed Description **** During steam plant S/U, SS-PCV-39 was found to not be controlling pressure. On SS-PI-39, pressure oscillates between 0 and 3 psig at about a 1 second period. Per SOP -SS-START step 5.1.32, SS-V-38 (Inlet to PCV-39) was shut and SS-V-41 was throttled. Oscillations slowed but are still at about a 2 second period and same magnitude. Possible leakby past SS-V-38. <I> **** Actions Taken **** WR written. <N> **** Equipment Description **** TB 471? | 02-00-SS-PCV-39
395934 | CR | 20190621 |  | 4 | Bypassed Gland Seal on BRG 5 | N | N |  | N | YES | <D> **** Detailed Description **** BRG 5 gland seal pressure was between 0 and 5 psig and unable to control between 1-3 psig. Bypassed per 4.820.B2 7-6. <I> **** Actions Taken **** WR written. Caution tag being developed. | 02-00-SS-PCV-4C
395935 | CR | 20190621 |  | 3 | R24LL: Need Backpressure Target prior to Turbine Roll |  |  |  | N | NO | <D> **** Detailed Description **** We had two unsuccessful attempts during Main Turbine roll to achieve the target speed of 1750 rpm for the TV/GV transfer. Engineering correlated Main Condenser Backpressure to previous startups where we successfully synced to the grid with no issue. They recommend reducing Main Condenser Backpressure below 2 inches Mercury. Ops started some cooling tower fans to lower condensate temperature and lower main condenser backpressure. . Recommend the following changes to PPM 3.1.2 (Reactor Startup): . 1. Add a step to the BOP section after Mode 1 but before rolling the turbine to reduce Condensate Temperature to 80-110 degF (the normal startup temperature band for condensate is 80-125 degF which is appropriate so we begin injection greater than 89 degF (see PPM 3.1.2 step B15 and note 31). . 2. Add a step prior to Turbine roll to verify Main Condenser Backpressure is less than 2 inches Mercury. <N> Cooling tower fans were shutdown after the 86lockout on the main generator on 6/19 - approx 14:00. The fans were restarted on 6/21 approx 00:00. See EDMS for plot of backpressure vs time with comments. . Recommend adding a note to the turbine startup procedure to include this information to prevent startup delay in the future.
395936 | CR | 20190621 |  | 3 | x352-12 cycling and filling alarm typer (m turb trip) | N | N |  | N | YES | <D> **** Detailed Description **** this has 3 parts for the fix 1) stop input to the alarm typer - computer engineering 2) correct issue 3) restore point to service for record This is a mn turbine trip alarm that has been cycling each time the turbine is latched. It outputs to the alarm typer which is using up paper and could eventually fill the buffer and stall out the plant computer. Further data no longer in EDNA - so 9/8/2003 paper file indicates number 18024 source from TO-PS-1AST - which was replaced by new DEH control system - DO card Trip tricon 4U output 11 to opto isolator DEH-ISOL-03/12 (which flashes dimly intermittantly) SEE EWD-48E-042 could be DO card issue or opto isolator. DO card LED is off and no flashes noted. | 02-00-DEH-ISOL-03/12
395937 | CR | 20190621 |  | 4 | Trip tricon trouble alarm. | N | N |  | N | YES | <D> **** Detailed Description **** Trip tricon PI card fault during turbine start up. This causes MP fault. All speeds look fine and all MP functioning as expected. Requires I&C to perform diagnostic scan to clear alarms. expected fault since the 3 speed probes do not start indicating at exactly the same time - but alarm masks other issues with trip computer. <I> The alarms on associated with turbine speed sensors. | 02-00-DEH-CHS-TRIP
395938 | CR | 20190621 | CAQ | D | CRD-HCU-5435 low pressure. | Y | N |  | N | YES | <D> **** Detailed Description **** 4.603.A7 6-7 (Accumulator Trouble) was received for HCU 54-35. <I> **** Actions Taken **** EO added N2 per SOP-CRD-HCU to restore normal pressure. <N> **** Equipment Description **** RB 522 | 02-00-CRD-HCU-5435
395939 | CR | 20190621 |  | 4 | OG-LIC-5A/B Struggling To Control | N | N |  | N | YES | <D> **** Detailed Description **** OG-LIC-5A and 5B are both struggling to maintain level in the offgas condenser. See video. <I> **** Actions Taken **** Informed MCR Requested I&C backfill instruments. <N> **** Equipment Description **** T441 | 02-00-OG-LIC-5A,02-00-OG-LIC-5B
395940 | CR | 20190621 |  | 4 | Generator Condition Monitor Alarming | N | N |  | N | YES | <D> **** Detailed Description **** TG-ID-1 flow dp is at 4.5. Normal is 1.5.An alarm is in, presumably for that reason. Additionally, the chart recorder is out of paper. <I> **** Actions Taken **** Informed MCR Adjusted flow and reset the alarm. Condition is now cleared. | 02-00-TG-ID-1
395941 | CR | 20190621 | CAQ | D | MS-DPIS-810D | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of ISP-MS-Q928. MS-DPIS-810D was found out of tolerance. As found trip 133psi. Adjusted to 128 psi per surveilance. <I> **** Actions Taken **** Notified ops. Calibrated the DPIS per surviellance and initiated CR | 02-00-MS-DPIS-810D
395942 | CR | 20190621 |  | 3 | R24LL - Revise step A52 in PPM 3.1.2 for clarity |  |  |  | N | NO | <D> **** Detailed Description **** Step A52 in PPM 3.1.2 Reactor Plant Startup directs operations to verify any drained feedwater heaters have their vent and drain valves tightly closed. This step is met when performing system valve lineups on restoration from maintenance. This step should be revised for clarity. Suggested wording as follows: Verify that feedwater heaters that have had maintenance (draining) performed have had valve lineups to ensure vent and drain valves are tightly closed". Additionally, this step should be moved to earlier in PPM 3.1.2, to allow for any necessary valve lineups to be performed ALARA. <I> **** Actions Taken **** Initiated CR. Disposition to Ops Procedures.
395943 | CR | 20190621 |  | 4 | small oil leak found in Union fitting EPN RFT-SV-20TPF/1B | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** small oil leak found in Union fitting EPN RFT-SV-20TPF/1B. During PMT task 02109787-04, electricians identified a small droplet of oil on the Union style coupler associated with RFT-SV-20TPF/1B. It was wiped and we attempted to tighten the fitting per work instruction. We got very little movement on the fitting. We decided to wait 2 hours and come back to the Control Cabinet and see if any improvement was made. After 2 1/2 hours, we saw that there was a droplet hanging on the bottom side of the Union. OPS was notified. This CR is for evaluation of the leak and trending. I estimate the current leak is approximately 1 drip per three hours. <I> **** Actions Taken **** Notified OPS and Write CR/WR <N> **** Equipment Description **** RFT-SV-20TPF/1B RFW-CP-RFT/1B
395945 | CR | 20190621 |  | 3 | 4.800.C4.10-4 needs updated |  |  |  | N | NO | <D> **** Detailed Description **** The second note refers to TMR 09-012 which has been removed for some time. The note is no longer useful or applicable and needs to be removed.
395946 | CR | 20190621 | CAQ | D | RRC-P-1A high vibe | N | N |  | N | YES | <D> **** Detailed Description **** During power ascention, at 31% Rx power 4.602.A6 alarm was received. RRC-VBI-P1A/MLBXY (motor lower brg x and y) was in alarm and downscale. <I> **** Actions Taken **** Created a temp log to monitor vibes. Alarm reset locally. This was a single channel alarm, so only associated with the instrumentation and not the actual pump/ motor. <N> **** Equipment Description **** RB 522. | 02-00-RRC-VBI-P1A/MLBXY
395947 | CR | 20190621 |  | 3 | R24 LL, inability to isolate DEH delayed restoration/startup |  |  |  | N | NO | <D> **** Detailed Description **** During plant restoration from an outage there is a significant amount of DEH work to bring the system back online. There were two events impacting the DEH system during R24 which required the DEH system be shut down. [Reference CR AR 395223 associated with DEH-V-160A and CR AR 395652 associated with MS-V-TV/4.] The inability to isolate sections of the system for corrective maintenance for the event in CR AR 395223 caused almost 25 hours of suspending the system restoration for startup and became critical path. The DEH system was critical path for the leak repair to the trip line connection on MS-V-TV/4 in CR AR 396652 and delayed entering Mode 2 by 10 hours. Due to three DEH shutdowns for emergent maintenance in R23 (see R23LL CR AR 369425), EVAL AR 369422 was created to explore isolation strategies and propose a means for changes that will allow for online maintenance of commonly encountered issues such the events described above so that they can be mitigated while system restoration continues in parallel. The proposal was taken to PHCSC during Cycle 24 and was rejected. <I> **** Actions Taken **** Discussed with supervisor, manager, VP Eng, and PGM <N> **** Equipment Description **** DEH system - hydraulic Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
395948 | CR | 20190621 |  | 3 | (PCR) PPM 4.602.A6 procedure change required. |  |  |  | N | NO | <D> **** Detailed Description **** While responding to an alarm on RRC-P-1A high vibrations, it was discovered that a few step in the procedure were missing. This specific procedure uses a table to guide you through the rest of the procedure. This step was go to step 2C, but step 2C is non- existent. It looks like a few steps were deleted when going to revision 33. The control room had to use the corresponding ARP for RRC-P-1B high vibration alarm.
395949 | CR | 20190621 |  | 4 | COND-CB-C1A | N | N |  | N | YES | <D> **** Detailed Description **** During performance of PMT WO 02076090-07 MOC switch contact engagement on S-2 and S-3 were found to be questionable. See attatched photos. <I> **** Actions Taken **** Informed supervisor and initiated CR | 02-00-COND-CB-C1A
395950 | CR | 20190621 |  | 4 | DEH trouble alarm reflashing | N | N |  | N | YES | <C> CR Changed from a CAQ D to a Non CAQ 4 by MRT, does not effect DEH operation. <D> **** Detailed Description **** LP3 xover reheat temp fault coming in and clearing. this temp not used for control - suggest substitute at 32Â°F at engineering workstation (same as others) | 02-00-TG-TE-SMT3RH
395951 | CR | 20190621 |  | 4 | FLM walkdown <30% power. | N | N |  | N | YES | <D> **** Detailed Description **** During the less than 30% power FLM Walkdown, the following leaks were identified: -MS-V-12A: W2, Wet packing -MS-V-TV/4: no active leak. Appears to be residual from previous leak. -MS-V-163A: S3, Small steam leak from stem seal area. West side. -MS-V-168B: W2, Wet packing area -Leak above HD-V-5B31 at 20dpm valve epn not visible W3 -RFW-V-118: W3 Packing leak 20dpm -COND-V-100/26: W3 packing leak at 15dpm -MS-V-743: W3, packing leak at 20dpm R. Rhodes 6/21/19 <I> **** Actions Taken **** Informed OCC and Mechanical Maintenance. | 02-00-COND-V-100/26,02-00-HD-V-5B31,02-00-MS-V-12A,02-00-MS-V-163A,02-00-MS-V-168B,02-00-MS-V-743,02-00-RFW-V-118
395952 | CR | 20190621 |  | 4 | AST did not get data on first attempted scram time on 30-11 | N | N |  | N | NO | <D> **** Detailed Description **** During performance of TSP-CRD-C101, scram time surveillance test, the Auto Scram Timer (AST) system did not see all the odd reed switch pulses and indicated that the data was bad for control rod 30-11. <I> **** Actions Taken **** Reviewed the raw data file and confirmed only 46 transitions (correlates to 23 pulses) and was missing one pulse. The overall scram time of the rod was less than 2.4 seconds, and all the intermediate positions passes assuming the worst case scenario of missing the 1st pulse. This is indicative of a failure of the AST to see all the pulses for some reason, or perhaps an issue in the test circuitry that delayed the start of pulse data collection that missed a pulse. The control rod was successfully scram timed and AST was able to collect the data on the 2nd attempt. The data on the 2nd attempt lined up within 0.01 seconds for the data collected during first scram attempt. Hence, this rod was able to be declared successfully scram times and is Operable. Control rod 30-11 had previously been scrammed at 0 psig during the outage and AST was able to collect that data with no issues at that time. Recommend close to trend to see if data collection problem with this control rod persists. This is issue with AST and not the control rod position indication. There is no DNC. <N> **** Equipment Description **** AST in control room
395953 | CR | 20190621 | CAQ | D | SEC-IDS-11 12 not function as designed | N | N |  | N | YES | <D> **** Detailed Description **** SEC-IDS-11 12 not function as designed. Request electrical maintenance to investigate. Contact security for more information x2185 <I> **** Actions Taken **** Compensatory measures initiated; CR/WR Generated | 02-00-SEC-IDS-EVAL/11/12
395954 | CR | 20190621 |  | 4 | Hydrogen peroxide delivery changed by carrier |  |  |  | N | NO | <D> **** Detailed Description **** Scheduled bulk delivery of Hydrogen Peroxide on 6/24/2019 moved to 6/25/2019 by carrier due to a lack of available drivers within the chemical transport company. <I> **** Actions Taken **** Notified security, schedulers, chemistry, and Env. Services personnel in attempt to accommodate date change. CR written for trending.
395955 | CR | 20190621 |  | 4 | RFW-P-1A pulse input card fault RFW-P-1A on single CPU | N | N |  | N | YES | <D> **** Detailed Description **** RFW-P-1A indicates pulse input card fault and indicates on single cpu only. Main control room alarms currently in are PI-TR-PI-ERROR and PI-TR-DUELMODE. RFW-P-1A appears to still be responding as expected. This was written up before the outage under AR-CR 00393145 <I> **** Actions Taken **** Wrote CR Informed CRS | 02-00-RFW-P-1A
395956 | CR | 20190621 | CAQ | C | Step change in MS-RV-1B tail pipe temperature | N | Y |  | N | YES | <C> AR/CR Changed from a CAQ D TRNDREP to a C/SENSSS by MRT 6/25/2019 , due to needing more actions taken <D> **** Detailed Description **** At 1405 MS-RV-1B had a step change in tail pipe temperatures. MS-RV-1B went from 139F to 218F. All other relief valve temperatures have not changed. <I> **** Actions Taken **** Wrote CR Informed CRS | 02-00-MS-RV-1B
395957 | CR | 20190621 |  | 3 | Arc chute removal from the RCA |  |  |  | N | NO | <D> **** Detailed Description **** NISP-RP-07 attachment 4 should be included in work orders removing arc chutes to avoid unnecessary confusion due to naturally occuring background radiation. <I> **** Actions Taken **** informed supervisor and initiated CR
395958 | CR | 20190621 |  | 3 | BFR Inservice performed at a higher power level then desired |  |  |  | N | NO | <D> **** Detailed Description **** This CR is for documentation and does not affect the functionality of CGS or Ashe equipment. All equipment involved has been tested satisfactorily. Ashe 4888 & 4885 Breaker Failure Relays (BFR) In-Service testing was performed at a higher power level then desired. - In-Service testing of 500 kV line protection relays and Breaker Failure Relays (BFRs) is desired to be performed between 20 and 25% power. This is the list risk time to perform the testing (measuring current and voltages). In the event of an error the risk at these power levels would have the potential to initiate a Turbine trip and not a scram. Testing at higher power levels (between 40 and 60% power in this case) introduces the risk of a scram in the event an error is performed. - Discussed the issue with the Ashe Relay Protection (SPC) Engineer and the OCC. A plan was developed to perform the BFR in-service testing with the BFR lockout relays cut out. BFR in-service testing was performed successfully error free with CGS oversight. All protection schemes have been restored. - This CR is to document this occurrence and to drive actions to modify the PMs performing in-service checks to also include BFR in-service testing if the BFR is worked on. This will ensure that all in-service testing is done at the least risk option/power levels. - PMs affected are PMRQs 18867-02 BPARLYSET1, INSERVICE CHECKS and 18868-02 BPARLYSET2, INSERVICE CHECKS <I> **** Actions Taken **** See Description. All In-service testing was performed sat. <N> **** Equipment Description **** Ashe 4888 & 4885 CGS Generator output breaker Breaker Failu re Relays. Located in the Ashe 500 kV Control House
395959 | CR | 20190621 |  | 3 | eWP; Tablet locked up and data lost during 02132883-01 |  |  |  | N | NO | <D> **** Detailed Description **** Tablet locked up and data lost on pages 7 through page 16 of ESP-SM8UV-M401, WO 02132883-01. Used a hard copy to back out (restore system) of the ESP prior to the TS allotted time. Scanned copy of what was retained in Data Glance and the restore portion of ESP-SM8UV-M401 back into Data Glance. Loaded a new copy of ESP-SM8UV-M401 in Data Glance. The entire ESP-SM8UV-M401 will need to be re-performed. <N> There are no indications of what caused the tablet to lock up. The audit trail didn't show any abnormal issues with the tablet locking up or a document being replaced. . Recommend to trend this issue since this is the only recorded tablet locking up.
395960 | CR | 20190621 |  | 4 | COND-LCV-1B Sticking | N | N |  | N | YES | <D> **** Detailed Description **** COND-LCV-1B will occasionally bind/ stick and then jump to a new position. It is still functioning. <I> **** Actions Taken **** Informed MCR | 02-00-COND-LCV-1B
395961 | CR | 20190621 |  | 3 | Oil leaking from RFW-DT-1B turbine bearing | N | N |  | N | YES | <D> **** Detailed Description **** During PMTâ€™s for other WOâ€™s in the Room it was noticed that oil was leaking form the turbine bearing seal on RFW-DT -1B. Hard to quantify the amount of leakage due to the airflow, attached in EDMS is a video The A RFW-DT was then looked at and no oil was noticed to be leaking at the same location. <I> **** Actions Taken **** Generated CR and notified EOC Added to PCL. <N> **** Equipment Description **** turbine bearing | 02-00-RFW-DT-1B
395962 | CR | 20190621 |  | 4 | FLM walkdown post outage at <75% | N | N |  | N | YES | <D> **** Detailed Description **** During the less than 70% power FLM Walkdown, the following new leaks were identified: -MS-V-181A: S3, steam leak under lagging. Throughwall leak -COND-V-139C: Seat leak into scupper -HD-V-18C: W4 packing leak <I> **** Actions Taken **** Attempted retorque on HD-V-18C packing and unsuccessful. Permission obtained to backseat the valve. Leakage reduced to 15 dpm. | 02-00-COND-V-139C,02-00-HD-V-18C,02-00-MS-V-181A
395963 | CR | 20190621 |  | 3 | R24LL: DC bucket bump start tasks need caution tags |  |  |  | N | NO | <D> **** Detailed Description **** During R-24, TO-P-EOP was damaged when it was started following the DC bucket replacement. There was a bump start task on the schedule to check for phase rotation but the task was not performed. . For all future DC bucket replacements, I recommend adding a caution tag to the appropriate control switch indicating that a bump check for phase rotation is required prior to operation of the component. The caution tag should refer to the work order task that is performing the bump start/check.
395966 | CR | 20190621 |  | 4 | R24 LL Revise 2 year VPI RCIC OSP-RCIC/IST-Q702 to on-line |  |  |  | N | NO | <D> **** Detailed Description **** OSP-RCIC/IST-Q702 Procedure VPI section was revised in 2015 to remove outage-related valves (valve inside containment) to a separate PM and surveillance (AR 310100-05). All remaining vavles can be done on-line. Currently this procedure delays start up by 4 hours when hydrogen water chemistry is out of service and reactor temperature is GT 200 F. Procedure requires RCIC in normal standby lineup (Rx Pressure GT 70 PSIG) and is performed prior to 150# if not current. but is flagged as mode 4/5 only. Surveillance can be done in any mode and should be done on-line and aligned with normal RCIC on-line quarterly surveillance. <I> **** Actions Taken **** Submitted SMS/AR 395965 to change UCR from outage to daily
395967 | CR | 20190621 |  | 4 | Failed Thermocouple causing DEH Trouble Alarm | N | N |  | N | YES | <D> **** Detailed Description **** Frequent DEH Trouble Alarms are being caused by an erratic temperature indicator. LP3 XOVER RH is coming in and clearing repeatedly. It is found on Analog Input Status DEH-CAB-00 Chassis 1 Slot 4 with a tag of â€œaSMT LP3 XVER RHâ€. | 02-00-DEH-CAB-00
395968 | CR | 20190622 | CAQ | D | CCH-CR-1B oil level high | Y | Y |  | N | YES | <C> CR reopened to cross reference additional WP 02124750, marked completion required box, then taken back to complete <D> **** Detailed Description **** During the 4th set of logs (36 hours after start up) oil level is observed to be high out of spec. The upper sight glass appears to be full. OSP-CCH/IST-M702 states that oil level may be high under no load conditions. Chiller does appear to be running with a very light load. Oil level is higher than what I would expect even a low load oil level to be. <I> **** Actions Taken **** Informed CRS | 02-00-CCH-CR-1B
395969 | CR | 20190622 |  | 4 | TSW-TIC-14B is not controlling temperature at the setpoint | N | N |  | N | YES | <D> **** Detailed Description **** TSW-TIC-14B is not controlling temperature per the set point, there is an offset of about 30 degrees from the set point to the actual control temperature e.g. 85 degree set point and controller maintains 115 degree. Recommend preforming a calibration on TSW-TIC-14B. <I> **** Actions Taken **** Informed CRS | 02-00-TSW-TIC-14B
395970 | CR | 20190622 |  | 4 | E-BU-R441/5 is broken and needs to be replaced or repaired | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing work in WO#02131845-01 E-BU-R441/5 was found with a survice alert light on and a broken test button. The service alert indicated a posible board failure and or transfer circuit malfunction. Fixture should be repaired or replaced with a new LED style fixture. A scaffold will possibly be needed. <I> **** Actions Taken **** Informed supervision and wrote this CR Non-essential lighting. <N> **** Equipment Description **** HPCS pump room on the 441 Mezz
395971 | CR | 20190622 |  | 4 | warehouse XD needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security warehouse X-ray 2 key cylinder needs maintenance. Contact security for details <I> **** Actions Taken **** unable to test X-ray 2, notified supervision, CR/WR generated <N> **** Equipment Description **** Warehouse 76 security X-ray machine key cylinder on counsel | 02-00-SEC-XR-2
395972 | CR | 20190622 | CAQ | C | OSP-MS-Q702 Not Performed on Cycle 25 Startup | Y | N |  | N | YES | <D> **** Detailed Description **** OSP-MS-Q702, Bypass Valve Testing, was not performed before exceeding 25% RTP following the startup from R24. There was work performed on the bypass valves during R24 (ref WO 02111690, 02111689) and this surveillance should have been performed during the startup. Entered SR 3.0.3. <I> **** Actions Taken **** Performing OSP-MS-Q702 under WO 02126650 within 24 hours. | 02-00-MS-V-160A,02-00-MS-V-160B,02-00-MS-V-160C,02-00-MS-V-160D
395973 | CR | 20190622 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Plant controller response was normal, off site voltages E-TR-S A: 238kv B: 239kv C: 240kv E-TR-B A: 119kv B: 119kv C: 118kv sensor J7 500 KV overcurrent tripped and was reset BPA reported momentary open and reclose of Wautoma-Rock Creek 500Kv line no equimpment damaged or outage needed this occured at 0231 <I> **** Actions Taken **** Followed ARP
395974 | CR | 20190622 | CAQ | D | RHR-FIS-10B out of calibration | Y | N |  | N | YES | <D> **** Detailed Description **** RHR-FIS-10B was found out of calibration during the performance of ISP-RHR-X304 CC. The switch reset was out of tolerance and the indicator was out of tolerance. <I> **** Actions Taken **** Notified CRS and Supervision and calibrated RHR-FIS-10B to within tolerances per the surveillance instructions. <N> **** Equipment Description **** rx 501 IR-H22-P021 | 02-00-RHR-FIS-10B
395976 | CR | 20190622 |  | 4 | During power ascention 4.602.A6 alarm was recieved. | N | N |  | N | YES | <D> **** Detailed Description **** During power ascention, at 93% Rx power 4.602.A6 alarm was received. RRC-VBI-P1A/MLBXY (motor lower brg x and y) was in alarm and downscale with the alert lamp indicating. Camera observation of this data point shows the vibrations coming in up to 4 PK-G periodically ( alarms should come in at 3.0 per ARP) but not alarming. This alarm was reset. A short time later the alarm reflashed with both the alert and danger lamps flashing. Recommend investigate and correct. <I> **** Actions Taken **** Reset first alarm. Wrote this CR | 02-00-RRC-VBI-P1A/MLBXY
395977 | CR | 20190622 |  | 4 | Monthly Chemical Storage area inspection discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** The monthly inspection of Mechanical Maintenance chemical storage areas discovered the following discrepancies: Chemicals found outside of flammable liquid storage cabinet in GSB shop. Red cans in bldg 113 and 114 had excessive combustibles and needed to be emptied. Chemicals restored to chemical locker and red cans emptied. <I> **** Actions Taken **** Notified appropriate personnel to resolve. All discrepancies resolved, no further action required.
395978 | CR | 20190622 |  | 4 | RRC-VBI-P1A/PXY green lights flashing | N | N |  | N | YES | <D> **** Detailed Description **** RRC-VBI-P1A/PXY green lights are flashing. Per 4.602.A6 drop 2-4, a flashing green light is indicative of a NOT OK condition on the module. The green lights stopped flashing when the reset button was depressed. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-RRC-VBI-P1A/PXY
395979 | CR | 20190622 |  | 4 | RFT-PI-4G/1B is High out of spec at 141 PSIG. | N | N |  | N | YES | <D> **** Detailed Description **** RFT-PI-4B/1B (B RFP trip oil pressure) is High out of spec at 141 PSIG. The High spec per PPM 3.1.10 (operator logs) is 140 PSIG. This is a long standing problem, reference WR# 29108991. Please investigate/repair/adjust or REVISE logs if this is an acceptable pressure value. Note: CRS/SM permission is required to enter the B RFT control cabinet, to view this pressure. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TG 441 inside B RFT cabinet | 02-00-RFT-PI-4G/1B
395980 | CR | 20190622 |  | 4 | Main Turbine Bearing 8 TC2 failed high | N | N |  | N | YES | <D> **** Detailed Description **** Shortly after 0900 hrs on 21June2019, Bearing 8 TC2 failed high. The other thermocouple on Bearing 8 is steady at approximately 168 degF after reaching 100% Rx power. [See EDMS for eDNA image. Note Bearing 7 TC1 was already documented as being invalid in CR AR 395404.] <I> **** Actions Taken **** Informed EOC | 02-00-TG-TE-BM8B
395981 | CR | 20190622 |  | 4 | SO-PI-279 reading High out of spec | N | N |  | N | YES | <D> **** Detailed Description **** SO-PI-279 is reading High Out of Spec at 140PSIG. Per PPM 3.1.10 (operator logs) the high spec for pressure is 135 PSIG. WR#29136786 addressed this issue coming out of R 23. <I> **** Actions Taken **** Informed MCR Added to weekend issues list. <N> **** Equipment Description **** TG 441 SO skid | 02-00-SO-PI-279
395982 | CR | 20190622 |  | 4 | Hard ground and Indication of no rotation on EOP during test | N | N |  | N | YES | <D> **** Detailed Description **** During SOP-MT-AOP/TEST the start of the EOP gave an 500 ohm ground on S2-1. After start pump drew 70 amps current with a locked in ground. Operators took action to place the pump switch in pull to lock. With pump stopped S2-1 resistance went back to near infinity. Operator reports from the field that the pump shaft never turned. Susect there may be problem with the pump itself or the disconnect as that the motor was refurbushied. Investigate and correct. <I> **** Actions Taken **** Wrote this CR. Pictures placed in EDMS of what the operators were looking at. Tagged out / turned over to electrical maint for investigation. | 02-00-TO-P-EOP
395983 | CR | 20190622 | CAQ | C | High Vibrations on RHR-P-2B OSP-RHR/IST-Q703 | Y | N |  | N | YES | <D> **** Detailed Description **** During OSP-RHR-IST-Q703 vibrations for MUW were 0.5341. This exceeds the ACTION HI value of 0.322. Page 33 of 44 on the attached OSP. <I> **** Actions Taken **** CR created, declared RHR-P-2B inoperable and available <N> Vibration experts and CGS Vibration Engineer have reviewed the vibration data collected on RHR-P-2B collected on June 22nd, 2019. Even though the data contains ski slopes (artificially inflates the overall value) in the spectral data, we can still see valid information that shows the condition of the motor and pump. Based on the information collected, motor and pump new vibration data is trending nornmal with past information. Motor bearing temperaure are also normal. Motor and pump condition is SAT. | 02-00-RHR-P-2B
395984 | CR | 20190622 |  | 4 | Health and Safety Concern - RFW-P-1B! | N | N |  | N | YES | <D> **** Detailed Description **** Health And Safety Concern regarding RFW-P-1B. The shaft connecting the turbine and pump is flinging oil all over the room. This represents many health and safetly concerns. Oil is being sprayed all over the room to the point that it is difficult to walk in certain parts of the room without slipping, even with slip resistant shoes. There are oil puddles forming on the floor due to all the oil being released. The lagging in the general vecinity of the oil leak is saturated and represents a fire hazard. The oil is atomizing to the point that if a flashlight is shined in the room you can see the particles floating in the air and when Eqipment Operatpors enter the room for inspections and log taking, we are breathing that in; it may even be an explosive atmosphere. We had this same exact issue after R23. <I> **** Actions Taken **** CR/WR Generated. Supervison Notified. Added to PCL. Notified WWM. Requested dayshift craft supervisor evaluate temporary collection / shield for area. | 02-00-RFW-P-1B
395985 | CR | 20190622 |  | 4 | RRC-TR-650 pt 2 indicates +OVER | N | N |  | N | YES | <D> **** Detailed Description **** RRC-TR-650 pt 2 indicates +OVER. This instrumentation was indicating normally during plant startup after being worked during R24 (refer to cross-references). According to the trend history on RRC-TR-650, the signal appeared to become erratic on 6/22/19 dayshift before failing to +Over. Computer point X310 also indicates incorrect temperature of 635 degrees F (acutual RRC-P-1B suction temperature should be ~ 530 degrees F). <I> **** Actions Taken **** Submitted CR and Work Request. Notified the CRS and Shift Manager. | 02-00-RRC-TR-650
395986 | CR | 20190622 |  | 4 | CF-P-41A dirty oil | N | N |  | N | YES | <D> **** Detailed Description **** CF-P-41A oil appears to have contaminats floating on the surface. <I> **** Actions Taken **** Wrote CR/WR | 02-00-CF-P-41A
395987 | CR | 20190623 |  | 4 | RRC-TR-ASD/B 1&2 pressure high | N | N |  | N | YES | <D> **** Detailed Description **** During rounds RRC-TR-ASD/B/1 and RRC-TR-ASD/B/2 were found out of spec high at 4.5 PSI and 5.0 PSI respectively. <I> **** Actions Taken **** Wrote CR/WR | 02-00-RRC-TR-ASD/B/1,02-00-RRC-TR-ASD/B/2
395988 | CR | 20190623 |  | 4 | TO-TK-2 above log spec | N | N |  | N | YES | <D> **** Detailed Description **** TO-TK-2 level is at about 1.25", outside of the 0-1" log range. The level increase is likely due temperature changes over the last few days while starting up the plant. <I> **** Actions Taken **** Informed CRS. | 02-00-TO-TK-2
395989 | CR | 20190623 |  | 4 | SCW-PI-457 out of band low | N | N |  | N | YES | <D> **** Detailed Description **** Stator cooling tank gas pressure on SCW-TK-1 is reading near atmospheric, the band is 2-5.5 psig. The tank normally maintains by H2 migrating into SCW system, so this may take some time since we have only just started up. Otherwise this CR is for trending. <I> **** Actions Taken **** Informed CRS. | 02-00-SCW-TK-1
395990 | CR | 20190623 |  | 4 | AR-P-1A / AR-P-1B west oil levels out of band | N | N |  | N | YES | <D> **** Detailed Description **** AR-P-1A and 1B west bearing oil levels are below the shutdown spec. Operator logs state it must be greater than the red line when off. Oil level for the two west bearings are at the red line, not above it as it should be. | 02-00-AR-P-1A,02-00-AR-P-1B
395991 | CR | 20190623 | CAQ | D | Door C-214 did not Close during ppm 15.1.2 | N | Y |  | N | YES | <C> CR reopened to cross reference additional WP 02137595, marked completion required box, then taken back to complete <D> **** Detailed Description **** During step 7.1.3 of ppm 15.1.2 Door C-214 (entrance to SM-8 switchgear room) did not close. This may be due to the room HVAC. This door should close under all plant conditions, do not close WR without adjusting door. <I> **** Actions Taken **** Informed Supervision <N> **** Equipment Description **** RW 467' vital island Non-essential fire door. BIP 19-0294 posted. | 02-00-W-DOOR-C214
395992 | CR | 20190623 |  | 4 | AR-V-18 very difficult to operate. | N | N |  | N | YES | <D> **** Detailed Description **** While attempting to move AR-V-18 in the closed direction to lower vacuum it was noted that the valve did not seem to want to move. pressure was lowered by holding the valve arm tightly in the closed position while tightening the handle tightly to hold it in the position. of note I do not remeber having to loosen the locking handle with a pipe wrench to unlock it in the past. This makes me think this has been a problem in the past tht wasnt adressed. <I> **** Actions Taken **** Called out the infileld supervisor to ensure i was operating the valve and locking mechanism correctly and my assesment was the same as his. valve was operated as described and was able to lower to 23 inches of vacuum from 25 inches of vacuum. | 02-00-AR-V-18
395993 | CR | 20190623 | CAQ | D | CIA-PRV-3A regulator body nitrogen leak | Y | N |  | N | YES | <D> **** Detailed Description **** There is a nitrogen leak from the body of the pressure regulator CIA-PRV-3A. See EDMS for photos and repair or replace. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** Rx 441 Railroad Bay | 02-00-CIA-PRV-3A
395997 | CR | 20190623 |  | 4 | TOA-FN-2A making squeal noise | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FN-2A was started to maintain a 3/2 lineup in TB HVAC. FN-1A is not available due to being tagged out. The fan start was fine and vanes are controlling DP well. There is a mild squeal coming from the fan. The fan door was opened, it appears to working fine but it is making noise. All the belts appeared in normal working order from a distance. | 02-00-TOA-FN-2A
395998 | CR | 20190623 |  | 4 | COND-RV-184 leakby to drain | N | N |  | N | YES | <D> **** Detailed Description **** COND-RV-184 is piped to a drain all by itself and there is a light but present steady stream coming from it. Maybe a gallon every 10 minutes or so. It was leaking like this at lower power with high condensate pressure and at the current 100% power, visually similar leakage. Needs to be worked. | 02-00-COND-RV-184
395999 | CR | 20190623 |  |  | OPS-FLEX-A106 Issue with replacing SOP-FLEX-Equipment-Storag | [5 empty] | <D> SOP-FLEX-EQUIPMENT-STORAGE was Superseded by OSP-FLEX-A106 however flow meters FLEX-FE-07 and FLEX-FE-08 identified in ABN-FSG-002 are not part of the inventory list as they were in SOP-FLEX-EQUIPMENT-STORAGE.
396000 | CR | 20190623 |  | 4 | Received GEN END DIFF EXP LONG/SHORT 4.820.B2 8-1 alarm. | N | N |  | N | YES | <D> **** Detailed Description **** Received GEN END DIFF EXP LONG/SHORT 4.820.B2 8-1 alarm. TG-MON-DE2 as read on TG-XR-TSI Pt. 30 is reading 0.66 inches. Contacted turbine system engineer for guidance. | 02-00-TG-MON-DE2
396001 | CR | 20190623 | CAQ | D | DG2 DC Fuel Pump Failure alarm received on DG2 start. | Y | N |  | N | YES | <D> **** Detailed Description **** During start of DG2 for OSP-ELEC-M702, recieived DC Fuel Pump Failure alarm 4.DG2.10-2. Verified both DC fuel pumps running with pressures indicated 52 psi. Alarm setpoint is 26 psi. Unable to determine if DO-PS-5B1 or 5B2 is the source of the alarm. When DG2 was placed in rated, fuel pump pressures were indicating 62 psi and 64 psi. Please investigate. Also ref CR#394644, WR# 29149192. <I> **** Actions Taken **** Informed CRS/SM | 02-00-DO-PS-5B1,02-00-DO-PS-5B2
396002 | CR | 20190623 |  | 4 | SCW-V-413 Handwheel nut retaining screw missing | N | N |  | N | YES | <D> **** Detailed Description **** SCW-V-413 (SCW-P-2 Suction valve) was found to have its handwheel nut completely loose. The nut was tightened down, but the retaining screw was missing and could not be found on the SCW skid. Due to vibrations, the handwheel nut was found loose again several hours later. Please replace handwheel nut retaining screw. SCW-V-413 operation does not appear to be affected by the loose handwheel nut. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TG 441 W | 02-00-SCW-V-413
396003 | CR | 20190623 |  | 4 | TG-XR-TSI display needs to indicate to a thousand of an " |  |  |  | N | YES | <D> **** Detailed Description **** TG-XR-TSI display needs to indicate to a thousand of an inch. ARP responsed requires a thousand of an inch display for the required actions. <I> **** Actions Taken **** SM informed. | 02-00-TG-XR-TSI
396004 | CR | 20190623 | CAQ | D | CRD-FI-4A is indicating LT 0.12 GPH | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-FI-4A is indicating less than 0.12 GPH which is low out of spec. The needle is not pegged low so some flow may still exist, but is below the readable scale. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** R522SE | 02-00-CRD-FI-4A
396005 | CR | 20190623 |  | 3 | Lessons Learned - Near SCRAM due to MT expansion Alarm |  |  |  | N | NO | <D> **** Detailed Description **** The station should reconsider the maintenance of the Operations System Study Guide (Otherwise know as the 'Lux Book"). During the MT expansion alarm, the crew was faced with a decision to SCRAM and Trip the turbine. The study guide provided a quick reference document to refresh the operators on the expansion indication. This information was obtained in 60 seconds. This document coupled with prompt feedback from engineering enabled the crew to make a well informed decision. Recommendation - continue with the great engineering response - maintain the study guide current and keep a copy at the ready in the main control room.
396007 | CR | 20190623 |  | 3 | PCR: 4.820.B2, 8-1 |  |  |  | N | NO | <D> **** Detailed Description **** 4.820.B2 8-1 procedure enhancent is needed. See EDMS for the recommendation. <I> **** Actions Taken **** SM/Eng informed.
396008 | CR | 20190623 |  | 4 | TO-M-EOP,Need vib disc installed, Engineering identify locat | N | N |  | N | NO | <D> **** Detailed Description **** Took vibration readings on TO-M-EOP, Need Engineering to valid points vibs were taken and identify vib points if they were incorrect . Install vib disc's at the locations identiified by Engineering.. <N> **** Equipment Description **** TO-M-EOP
396009 | CR | 20190623 |  | 4 | ASD Bldg. House keeping following outage. | N | N |  | N | NO | <D> **** Detailed Description **** ASD Bldg. has many House keeping issues following the Outage. The South East corner has testing equipment, tool bags, and other items that need to be stored elseware. There is a 3/8 inch piece of sheet metal found leaning against the wall next to the Battery Backup. This was moved to the floor in the South East corner. The rest of the Bldg. has extension cords and other equipment spread about, these need to be cleaned up.
396010 | CR | 20190623 | CAQ | D | RHR A Discharge Pressure High alarm IN | Y | Y |  | N | NO | <D> **** Detailed Description **** 4.601.A4 drop 3-1 RHR Pump A Discharge Pressure High/Low alarm IN. RHR-PI-612A indicates 500 psig. Discharge pressure has been drifting up during startup. Pressure was vented per ARP via RHR-V-74A and RHR-V-73A. Alarm Clear. Alarm is Expected during Heat up. CR wirtten for trending.
396011 | CR | 20190623 |  | 4 | 4.800.C4 3-1 TR-M3 Trouble alarm recieved | N | N |  | N | YES | <D> **** Detailed Description **** 4.800.C4 3-1 TR-M3 Trouble alarm recieved. Dispatched an Operator to investigate. On local panel Cooler Group 2 and 3 failure alarm was in. The Alarm for Cooler Group 3 cleared immediately when alarm reset toggle was pushed, all fans and the pump were running. Cooler group 2 alarm stayed locked in, all Fans were still running but the pump was off with the its' overload tripped. <I> **** Actions Taken **** With CRS direction, reset the overload per ABN-TRANSFORMER, Cooler group 2 alarm cleared. | 02-00-E-TR-M3
396012 | CR | 20190623 |  | 4 | ASD Printers need paper | N | N |  | N | YES | <D> **** Detailed Description **** The ASD printers for the ASD1A/1 and ASD1B/1 drives need the paper replaced. | 02-00-RRC-XR-1A1,02-00-RRC-XR-1B1
396013 | CR | 20190623 |  | 4 | Time and date incorrect for ASD1A/2 drive printer | N | N |  | N | YES | <D> **** Detailed Description **** Set the correct time and date for RRC-IMD-ASD1A/2's printer. Currently the printer is printing out the incorrect date and time. | 02-00-RRC-XR-1A2
396014 | CR | 20190623 |  | 4 | ASD building housekeeping | N | N |  | N | NO | <C> Duplicate of AR 396009 <D> **** Detailed Description **** During the performance of WR 29150032 it was noticed that there is still lots of equipment in the building from R24s outage work. This equipment needs removed and taken to the tool crib or wherever it belongs. Also there is a sheet of metal that was leaning against the south wall that was layed on the floor so it would not fall onto the ASD inverter. <N> **** Equipment Description **** ASD Building
396015 | CR | 20190623 |  | 4 | TO-EX-4A became nosier and DP was oscillating. | N | N |  | N | YES | <D> **** Detailed Description **** TO-EX-4A was written up for making a rattling noise that was getting worse on 6-17D (AR#395703). It was found tonight making an even louder rattling noise and TO-dPIS-18 was bouncing around more than the standard oscillation. The noise was worse than it was the prior night and the oscillations had become worse to the point were it was difficult determing what DP was. <I> **** Actions Taken **** Informed CRS. Swapped to TO-EX-4B (which is a magnitude quieter with lstandard pressure oscillations). | 02-00-TO-EX-4A
396016 | CR | 20190623 |  | 3 | Procedure enhancement ABN-SRV |  |  |  | N | NO | <D> **** Detailed Description **** remove the requirement to be LT 90% power prior to closing a stuck open SRV as evaluated in CR 391225
396017 | CR | 20190623 |  | 3 | ABN-TRANSFORMER step 7.4.11.a doesnt reflect EC17761 |  |  |  | N | NO | <D> **** Detailed Description **** ABN-TRANSFORMER step 7.4.11.a doesnt reflect EC17761. while responding to a transformer alarm it was noted that during step 7.4.11.a that cooler groups 1 and 2 were in manual, This step has you verify that the switches are in manual. Cooler group switches1 and 2 are in manual per SOP-ELEC-500KV/TRANS-LU page 18. Recommend putting a note in ABN-TRANSFORMER step 7.4.11.a . Also recommend putting a placard that states these two switches are in a differant position due to the EC, <I> **** Actions Taken **** wrote CR
396018 | CR | 20190623 |  | 3 | R24 LL PPM 1.3.64 requirment for COH/WOH |  |  |  | N | NO | <D> **** Detailed Description **** Requirment to have WOH sign off a clearance prior to the end of shift as required in PPM 1.3.64 step 3.4.8 was not adhered to. This resulted in lost time to get both WOH's and COH's off clearances after work was completed. This same requirment exsists for use of Satellite files Need to improve perfromance or revise the requirement
396019 | CR | 20190623 |  | 4 | E-TR-M2 cooler group 2 oil pump tripped, OL wont reset | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-M2 cooler group 2 oil pump tripped, OL wont reset. responded to cooler group two alarm on E-TR-M2. the relay would not go to the off position to reset it. informed the MCR <I> **** Actions Taken **** responde to the alarm per ABN-TRANSFORMER, was unable to rest the OL , informed the MCR. | 02-00-E-TR-M2
396020 | CR | 20190624 | CAQ | D | 48-09D LPRM failed upscale | Y | N |  | N | YES | <D> **** Detailed Description **** 48-09D LPRM failed upscale. see attached plot <I> **** Actions Taken **** B/P 48-09D Entered ABN-LPRM | 02-00-LPRM-DET-48/09D
396021 | CR | 20190624 | CAQ | C | DEH OPC press fault (SPV for LDA /OPC protection) | N | Y |  | N | YES | <C> FOLLOW SWP-CAP-01 TO RESOLVE WITH ANOTHER AR/CR <D> **** Detailed Description **** this alarm is indicative of the BS-PT-10 output. DEH cab 04 chassis1 slot 3 indicates 153 psig (seems normal for 100% power). This should scale in between 12-16ma and be well within the AI scaling for this input (see AI scaling sheet 14 of control program). This OPC pressure fail alarm inputs to the LDA actuation (see sheet 45) and leaves us with a single input from gen MW xducer for this function. Appears issue may actually be in the triplication (in or out) of the cab4 / chassis 1/ slot 3 AI 3721 card. Perhaps diagnostic scan can determine more or reset this alarm and restore more robust function. see EDMS for program sheets <N> mALM_OPC_PRESS â€œOPC PRESSURE FAILâ€ is an expected alarm due to implementation of a temporary configuration change to address the non-conforming condition described in CR 382832. Ref. AR-EVAL 384074 and SOP-DEH-OPS section 6.1.3. No additional actions or corrective maintenance is recommended at this time. -Markos P. 2019-6-24 | 02-00-DEH-CAB-04
396029 | CR | 20190624 |  | 4 | Chemical Storage Locker discrepancies | N | N |  | N | NO | <D> **** Detailed Description **** Chemical Storage Locker 02-0057-DEH discrepancies. Bag of miscellaneous work items and PCs stashed in maintenance work bag in chemical storage locker. <I> **** Actions Taken **** Storage locker cleaned out ro remove items not belongging in locker and returned to tool crib for proper storage.
396030 | CR | 20190624 |  | 3 | (Non EN/CGS) CC-193 Instrument not expedited when requested | N | N |  | N | NO | <D> **** Detailed Description **** (Non EN/CGS) Instrument not expedited when requested. Instrument MTC-QA1305130543 was received on June 10 and paperwork reference â€œexpeditedâ€. The expedite request wasnâ€™t noticed until June 26. <I> **** Actions Taken **** Issued CR and started customer claimt process. <N> Assign to: AR-CALSERV completion notes should have been entered into the plan assignment but were added to the description of the plan assignment and should have also been copied to the completion notes. The expedite request was realized on 6/18/19 when customer emailed. When the document was researched to review where the expedite request was noted, there was not a specific request to which expedite the customer wanted per their contract. see plan assignemnt note
396031 | CR | 20190624 |  | 4 | Overhead lights burned out in MCR SM Office | N | N |  | N | YES | <D> **** Detailed Description **** The Main Control Room SM office has 2/3 of the overhead lamps burned out and the lighting and the remaining lights are very dim. Request replacing the lamps at next opportunity. Also, one of the light switches (toggle) is broken and needs to be replaced. The switch appears to be in the 'on' position. <I> Contacted FIN team and Electrical Component Manager. Existing lighting is sufficient for safety. <N> **** Equipment Description **** Main Control Room Shift Manager Office - Lights LIght Switch - just inside door to entrance for C412.
396032 | CR | 20190624 | CAQ | D | E-C0-1A AC power light is burned out. | Y | Y |  | N | YES | <D> **** Detailed Description **** E-C0-1A AC power light is burned out. Please replace. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** RW 467 VI | 02-00-E-C0-1A
396033 | CR | 20190624 |  | 3 | Several MCR front panel alarms not coded as such in WR's |  |  |  | N | NO | <D> **** Detailed Description **** WRs 29148968 5/24/19, 29149996 6/20/19, 29150045 6/21/19, 29142289 04/30/2018, 29149167 05/31/2019. These WR's all corespond to an equipment deficiency that causes a MCR front panel alarm that is locked in. Please recode the problem type as CA to help ensure that the problems get the needed attention. <I> **** Actions Taken **** Wrote this AR due to locked in front panel alarms.
396034 | CR | 20190624 | CAQ | D | FP-V-W13/247 can not be operated. | N | N |  | N | NO | <D> **** Detailed Description **** While performing 15.1.23, step to open FP-V-W13/247. can not be performed. water flows thru valve causing pressure switch to accuate in the main control room. As left fire system will accuate, but no alams will be received in control room <I> **** Actions Taken **** reperformed main mrain test in attempt to remove debris causing clapper to not reset. <N> **** Equipment Description **** FP-System Wet 13
396035 | CR | 20190624 | CAQ | C | Different units for AR-RIS-21 readouts | N | Y |  | N | YES | <C> CR reopened to add completion required check mark to referenced WO 02137870 per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** AR-RIS-21 reads locally in mR/hr at P604. AR-RIS-21 indication on SW-RR-1 reads in R/hr. While AR-RIS-21 reads about 30 mR/hr, SW-RR-1 shows the same reading at about 30 R/hr. Recommend adjusting SW-RR-1 to reflect the magnitude of mR the local AR-RIS-21 reads out in. <I> **** Actions Taken **** Submitted CR for corrective action. | 02-00-SW-RR-1
396036 | CR | 20190624 |  | 4 | COND-DPI-23B is currently reading downscale, | N | N |  | N | YES | <D> **** Detailed Description **** COND-DPI-23B is currently reading downscale, This is the COND-HX-5B DP indication. Appears the instrument may be isolated. <I> **** Actions Taken **** Informed CRS/SM | 02-00-COND-DPI-23B
396037 | CR | 20190624 | CAQ | C | OSP-INST-H101 MS GE 5.4 PSID | Y | Y |  | N | YES | <D> **** Detailed Description **** The readings for MS-DPIS-810A, B, C, D were noted to be greater than 5.4 PSID on the 10/23 OSP-INST-H101s at the beginning of the down power to support the sequence exchange. OSP-INST-H101 was signed for closeout originally at 10:13 on 6/23/2019 <I> **** Actions Taken **** Initiated CR <N> **** Equipment Description **** Rx 501 | 02-00-MS-DPIS-810A,02-00-MS-DPIS-810B,02-00-MS-DPIS-810C,02-00-MS-DPIS-810D
396038 | CR | 20190624 |  | 3 | PPM 4.CW.PNL procedure revision required |  |  |  | N | NO | <D> **** Detailed Description **** EC 16616 removed the ability of CW-PHITS-1 to close CBD -LCV-1. Remove "CBD-LCV-1 Closes" from PPM 4.CW.PNL windows 1-1 and 1-2. <I> **** Actions Taken **** Initiated CR. Informed Operations Procedure group supervisor.
396039 | CR | 20190624 |  | 4 | Crack in existing rail car weld | N | N |  | N | NO | <D> **** Detailed Description **** Existing weld on rail car trunnion support was found to have a crack in the toe approximately 1" long. <I> **** Actions Taken **** Contacted vendor for disposition of weld. <N> **** Equipment Description **** N/A
396045 | CR | 20190624 |  | 4 | Offgas Train A Recombiner Heater cycling (OG-TC-2A). | N | N |  | N | YES | <D> **** Detailed Description **** The Offgas train 'A' recombiner heater is cycling excessively as indicated by cycling of the ON / OFF indicating lights by the heater control switch on H13-P672. The approximate cycle time is 6 seconds on / 13 seconds off. The heater is for OG-RC-5A (offline Offgas Recombiner). Suspect issue with the temperature controller (OG-TC-2A). Verified that OG-TC-2A set at 350 deg. F per SOP-OG-START. The red temperature (process variable) display on OG-TC-2A shows a steady 372 deg. F and the red "out" light on the bottom right of the controller is cycling with the same frequency as the heater indiction in the main control room. The other temperature indications for OG-RC-5A in the Main Control Room are (as indicated on OG-TRS-602 pt 1-3) are 392 / 418 / 468 deg. F., respectively. Frequent cycling could damage associated heater contactors. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. Identical conditions were documented by WR 29137079. Caution tagged heater RMS in OFF to prevent cycling. | 02-00-OG-TC-2A
396046 | CR | 20190624 |  | 3 | PCN not processed per SWP-PRO-02 |  |  |  | N | NO | <D> **** Detailed Description **** PCN 19-0013 did not receive initial reviews and approval within one business day per SWP-PRO-02, step 5.5.1.d. While this PCN failed to meet the required outcome of step 5.5.1.d, the MCR staff followed guidance per the first Note of section 5.5.1 which allows a delay in completion of PCN paperwork if the change is essential to Plant operation. This Note contradicts the step in question and does not properly explain how to continue the PCN process. <I> **** Actions Taken **** Issue was discussed with Document Control, RIM, and SM. Clarification is needed in SWP-PRO-02 for the PCN process. Operations Procedure Group will coordinate with RIM to revise SWP-PRO-02, section 5.5 to ensure that the PCN process is easier to understand and handoffs in responsibilties due to Plant needs are addressed.
396047 | CR | 20190624 |  | 3 | Ops exceeded budgeted overtime in June 2019 |  |  |  | N | NO | <D> **** Detailed Description **** Operations department (52220) budgeted amount for Overtime in June was $434.8K, As of 6/24/2019 the actual overtime has reached $673K. Operations should investigate the details and numbers to determine and understand the causes for exceeding the budgeted amount for overtime. This is administrative/process issue and is not plant equipment related. <I> **** Actions Taken **** Discussed with Ops Manager and Financial Budget Rep.
396048 | CR | 20190624 |  | 4 | TO-EX-3B not running | N | N |  | N | YES | <D> **** Detailed Description **** Investigation of TO-EX-3B operation revealed it isn't running. Red light is on in the control room. This is likely the cause of the loss of oil from turbine seal area. Similar issue happened with TO-EX-3A a few years ago. <I> **** Actions Taken **** Informed CRS/FIN. . This could be contributing to the leakage from RFW-P-1B coupling area, CR 395984. <N> **** Equipment Description **** TG 441 RFT B roo | 02-00-TO-EX-3B
396050 | CR | 20190624 |  | 4 | E-TR-M3 cooler group 2 pump overload | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-M3 cooler group 2 pump was found to have it's overload tripped. The overload would not reset per the ARP. The E-TR-M3 cooler group 2 trouble alarm could not be reset. Note: SM permission, and a 2B45S Key are required for Transformer yard entry <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** Xfmr Yard, 2B45S key required for entry | 02-00-E-TR-M3
396051 | CR | 20190624 | CAQ | B | Fatigue Rule violation |  |  |  | N | NO | <C> Risk: Medium Cause: Uncertain Investigation Template Recommended <D> **** Detailed Description **** On Sunday, 6/16/19, a technician supporting the station for R-24 came in 2 hours early to perform duties for the EN standards lab. Shop supervision was not informed and time was not captured in eSoms at the time the hours were worked. Entering the time in eSoms showed that the tech had violated the "No more than 72 work-hours in any 7-day period" rule. The tech ultimately worked 74 hours in the 7-day period. <I> **** Actions Taken **** Informed maintenance managementa and the site FFD coordinator. Initiated CR. <N> Actions Taken: Established a R24 lesson learned to reinforce fatigue requirements with ALL temp outage workers pre -outage as well as with ENSL leadership to ensure they do not contact their techs that are here for the outage. Cause: Work involved was a temp worker from Cal Lab. Cal Lab Management asked worker to conduct business for ENSL without coordinating with Maintenance. This work pushed individual over limits and resulted in the violation.
396055 | CR | 20190624 |  | 4 | Near miss reported |  |  |  | N | NO | <D> **** Detailed Description **** An EN employee had a near miss incident when a faulty chair armrest broke. Individual put weight on armrest when repositioning and armrest came off. There was no injury to the employee. Chair is from Neutral Posture model #NPS8500. See EDMS for photo of chair. <I> **** Actions Taken **** Individual notified supervisor immediately and ISPM-1 was followed. Notified management, Facilities, and Industrial Safety of the issue. Chair has been marked as â€˜out of serviceâ€™ and removed from employees office. Information Services (IS) performed a walk down of all locations owned by IS and removed any defective chairs.
396056 | CR | 20190624 | CAQ | D | IDS 20 | N | N |  | N | YES | <D> **** Detailed Description **** Pin out on pole 190 | 02-00-SEC-IDS-E/S/20/21
396058 | CR | 20190624 |  | 4 | emergency lighting needs replaced. | N | N |  | N | NO | <D> **** Detailed Description **** WO 02140981-01 4 loghts were found out and out of reach. 606 fixture 3,4,5,8. <I> **** Actions Taken **** cr wr <N> **** Equipment Description **** ELP-8BA
396059 | CR | 20190624 | CAQ | C | Reoccurring issue HPCS-LS-1A unable to reset trip | Y | N |  | N | YES | <C> AR Owed to Group changed from AR-LIC to AR-SENSSS by MRT 6/27/2019 <D> **** Detailed Description **** Reoccurring issue HPCS-LS-1A unable to reset trip after survalance performance of ISP-HPCS-Q901. WO to replace switch 02137603 needs to be implamented. Unable to reset trip without mechanically agitating switch when performing ISP-HPCS-Q901 WO 0213595001.This is an reoccurring issue See CR 388210 for previous identified issue. HPCS-LS-1A should be replaced and line flushed to clear out debris. <I> **** Actions Taken **** Contacted CRS, SM and supervision <N> HPCS-LS-1A will transfer from the Condensate Storage Tank (CST) to the Suppression Pool on a low level in the CST. When tested, the switch was able to demonstrate successfully its ability switch to the suppression pool on low level. It was not, however, able to reset on rising CST level, and would not have been able to allow the suction source to switch back to the CST. Since the suppression pool, not the CST, is the safety related source, the inability to switch back would not have jeopardized the ability of the HPCS system to meet its safety requirements. The HPCS system was capably of starting and injecting to the core from its safety related water source at all times. Greg Slvan, System Engineer 6/25/19 | 02-00-HPCS-LS-1A
396060 | CR | 20190625 |  | 4 | XD-03 Failed Operability Test | N | N |  | N | YES | <D> **** Detailed Description **** XD-03 not functioning as designed and requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** XD-03 placed out of service. Security supervision notified. Initiated CR/WR | 02-00-SEC-XD-3
396061 | CR | 20190625 |  | 4 | TG-MON-CE is still eratic. | N | N |  | N | YES | <D> **** Detailed Description **** During downpower on 6/23, TG-MON-CE Computer point T079 changed from 0.811 " to 0.894 " and then back to 0.797 " and steady when power was returned to 100%. TG-XR-TSI pt. 29 is still eratic as well as shown on recorder during down power. Review of data trend was performed under WO# 02101716. <I> **** Actions Taken **** Notified Supervisor. | 02-00-TG-MON-CE
396062 | CR | 20190625 |  | 4 | WCH-Cont-51A alarm locked in | N | N |  | N | YES | <D> **** Detailed Description **** While performing rounds it was noted that WCH-CONT-51A had an, Oil Analysis recommended, locked in alarm. <I> **** Actions Taken **** crs informed, AR/WR initiated. | 02-00-WCH-CONT-51A
396063 | CR | 20190625 |  | 4 | TSW-FG-3A placement configuration | N | N |  | N | YES | <D> **** Detailed Description **** TSW-FG-3A is installed with its display up against an angle iron stantion and is very difficult to read. <I> **** Actions Taken **** Initiated CR. Informed Ops supervision <N> AR type EVAL needed? | 02-00-TSW-FG-3A
396064 | CR | 20190625 |  | 4 | Off gas pressure indications not functional | N | N |  | N | YES | <D> **** Detailed Description **** OG-PI-1A and OG-PI-1B are broken and do not provide any indication of system pressure. <I> **** Actions Taken **** initiate CR, informed ops supervision | 02-00-OG-PI-1A,02-00-OG-PI-1B
396065 | CR | 20190625 |  | 3 | Chemical Feed issues are an Operator Burden | N | N |  | N | YES | <D> **** Detailed Description **** The CF pumps (CF-P-41A/B and CF-P-42A/B) and their ability to add chemicals to CW have been an ongoing problem for a while. In the past year, we have 16 easy to find CRâ€™s to document these issues (AR 382952, 383466, 384083, 386536, 386632, 386671, 387783, 387817, 389360, 389393, 390101, 390281, 391065, 392625, 392959, 395433). The solution is to have Equipment Operators batch add chemicals for 1-2 hours per shift until a quick fix can be made. This lasts until the next CR is written and batch adds are required again. We are quickly becoming reliant of this method vs the normal and its taking Operations away from their normal duties and its susceptible to failing just as the pumps did. Relying on batch adds as a long term solution puts us 1 step away from not being able to add any chemicals. | 02-00-CF-P-41A,02-00-CF-P-41B,02-00-CF-P-42A,02-00-CF-P-42B
396066 | CR | 20190625 |  | 4 | RRC-VD-R673 communications failed | N | N |  | N | YES | <D> **** Detailed Description **** Comm link between main control room and the local ASD drives is not functioning. Control room video display does not have status nor fault data from the local drives. | 02-00-RRC-VD-R673
396067 | CR | 20190625 | CAQ | D | Drywell Oxygen concentration is trending up. | Y | N |  | N | YES | <D> **** Detailed Description **** Drywell Oxygen concentration is tredning up. Over the past 4 days O2 concentration has gone from 0.7% to 0.9% at a steady pace. Recomend investigating and correcting the cause of inleakage to containment. <I> **** Actions Taken **** Wrote this AR. Informed CRS. | 02-00-C-TK-1
396071 | CR | 20190625 |  | 4 | System Failure -- Oracle Database connections | N | N |  | N | NO | <D> **** Detailed Description **** At approximately 01:00 AM on 2019Jun25, the AIX Server120 ran up to 90% of page file capacity resulting in numerous blocked Oracle database connections. Neither the server nor the databases crashed â€“ they were hung due to virtual memory shortage. <I> **** Actions Taken **** The AIX operating system automatically killed several running Oracle jobs and Dave Briggs allocated more space to the page file to bring it down to 59% capacity. <N> The issue was caused by an error handling block within the indexing code. The error handling entered a continuous loop causing DB connections to be denied. The indexing script has been corrected to account for the condition. Recommend NCAQ 4.
396073 | CR | 20190625 |  | 3 | R24 LL ALARA In-Progress Review for SAC shield doors |  |  |  | N | NO | <D> **** Detailed Description **** During R24, the 40% In-Progress Review (IPR) for ALARA Task 02120003-03-01, OPEN/CLOSE N2A / N2B SAC DOORS, INSUL, SUPPORT, was missed because 68% of the estimated dose was accumulated within the 3.5-hour duration it took to open the N2 SAC shield doors. Opening SAC shield doors is a short-duration evolution which may meet the criteria in PPM 11.2.2.14 for an Alternate In-progress Review Plan. For future planning, an IPR performed at the completion of SAC door opening, the natural half-way point, should be considered. <I> **** Actions Taken **** Wrote CR. Notified RPM. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
396074 | CR | 20190625 |  | 4 | R24 LL Multi-pack became unusable due to ED cal due date |  |  |  | N | NO | <D> **** Detailed Description **** Multipack 29000890 being used by a Diver on RWP 30004258 had to be prematurely returned in TES and a new Multipack assembled and issued because one of the electronic dosimeters assigned to the original Multipack had reached its Calibration Due Date, which rendered the Multipack unusable for further RCA entries. The assembly of Multi-pack dosimetry per PPM 11.2.6.7 should take into consideration the calibration due date of electronic dosimeters assigned to the Multi-pack, so that the Multi -pack remains usable throughout the planned use period. <I> **** Actions Taken **** Wrote CR Notified RPM
396075 | CR | 20190625 |  | 4 | TDAS KVM in P605 non-responsive | N | N |  | N | YES | <D> **** Detailed Description **** KVM share device has lights on, but nothing is displayed. This could be the KVM Switching device or the Monitor. This CR should go to Maintenance for repair. <I> **** Actions Taken **** Tried switching from one shared computer to another, using both the keyboard control key and the manual switch button on the KVM Switching device. Still nothing displayed on the monitor. The indicator light on the device would move using the manual switch, but not the keyboard control key. Verified that there is a spare in the warehouse. (CID 6821) | 02-00-TDAS-CRT-1,02-00-TDAS-KBD-1
396076 | CR | 20190625 |  | 3 | R24 Outage Total Dose Goal Exceeded |  |  |  | N | NO | <D> **** Detailed Description **** The R24 Outage Total Dose Goal (stretch goal <125 Rem and Goal <130 Rem) was exceeded with an actual value 180.390 Rem. This value is based on the dose estimate, actual electronic dosimeter data and is subject to change. Current DLR period ends 06/30/19. There were several factors for the overrun, some of them being average effective dose rates (~16% higher), added emergent work (~9 Rem) and execution issues with some planned work.
396078 | CR | 20190625 |  | 4 | RP Condenser R Meter Calibration Service Provider Changed |  |  |  | N | NO | <D> **** Detailed Description **** The previous vendor Fluke Biomedical for calibration services for RPs Condenser R Meter/Chamber Calibration Standard (Health Physics Instrument for Irradiator/Calibrator calibrations) changed. After the instrument was submitted in March 2019 Fluke (Victoreen instrument manufactureâ€™s parent company) announced in May 2019 that they would no long be providing calibration services the Victoreen Model 570 Condenser R Meter and Chamber set. They have provided this service for the past 20+ years, but will no longer maintain accreditation for this equipment due to the age and obsolescence of this instrument. Another accredited laboratory K&S Associates, Inc. is an authorized, and industry recognized, calibration laboratory and has offered to provide calibration services for the instrument for the foreseeable future. Although the instrument is very old, it is still a dependable and accurate standard and this model is still commonly used in the nuclear and medical field. However it will eventually require replacement at some point in the next 3-5 years. This is Class G non-plant HP instrumentation. <I> **** Actions Taken **** Discussed this issue with Rad Support Supervisor. Arrangements were made with K&S for calibration of the instrument and it has been sent in for service. In the longer term RP will consider possible replacement models for this calibration standard and will plan for funding as necessary in the normal annual department FY budget planning process. A suitable replacement standard is generally around $30k. This CR written to document the change in laboratory calibration services, reason for the change, and why replacement must be budgeted. No further action needed.
396079 | CR | 20190625 |  | 4 | Turbine Side SO & H2 D/P LOOS | N | N |  | N | YES | <D> **** Detailed Description **** On rounds turbine side seal oil and H2 D/P calculated value was 10.5 PSID (taken from SCW-PI-534 and SO-PI-201). Band on logs is GE 12 to LE 15 psid. Reactor was at 100% power. <I> **** Actions Taken **** Notified CRS | 02-00-SO-PI-201
396080 | CR | 20190625 |  | 3 | T471 West end house keeping |  |  |  | N | NO | <D> **** Detailed Description **** T471 West end housekeeping is not satisfactory. Multiple work in progress signs from work performed in R24 that is complete; however the signs, trash, temporary lighting, and scaffold platforms remain in place. <I> **** Actions Taken **** Informed supervision and maintenance.
396081 | CR | 20190625 |  | 3 | Classification of Power Panel |  |  |  | N | NO | <D> **** Detailed Description **** Documentation only does not affect operability of equipment. EC 16611 which deactivated the existing PRM stack monitor equipment did not revise MEL to change classification of E-PP-7BC when the Augmented Quality loads on E-PP-7BC were de-energized. There are now no Safety-Related or Augmented Quality loads on the power panel per EWD-46E-332 rev 14 and it should be reclassified as non-safety related. Leaving the power panel classified as Augmented Quality would keep it in the Environmental Qualification program and require eventual replacement of circuit breakers due to expiration of qualified life. <I> **** Actions Taken **** Discussed with reponsible Design Engineering personnel. Suggest assign to Design Engineering.
396083 | CR | 20190625 |  | 3 | (R24LL) Ops outage Lesson learned to date (RPV Hydro) |  |  |  | N | NO | <D> **** Detailed Description **** Below are comments from One Note, specific to R24 RPV Hydro â€¢ RPV hydro - Re-arrange steps in the prep phase to make sure everything is aligned and taken care of before closing MS-V-1 and 2 â€¢ RPV hydro - Opening RCC-V-8 early is better. The procedure tells you to consider it, but it can't hurt to just get it taken care of. Hydro was performed with 1 RRC pump at 30Hzâ€¦.this seemed to be a lot more heat load than 2 pumps at 15Hz, but we are writing a CR to have it evaluated if we really need 1 pump to be at 30Hz once we are at test conditions. <I> **** Actions Taken **** Initiated R24LL <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
396084 | CR | 20190625 |  | 4 | Rotometers cloudy on SR-9 and SR-48 | N | N |  | N | YES | <D> **** Detailed Description **** Rotometers for several sample points in the chemistry lab RW 487' are cloudy are difficult to read. These need to be cleaned or replaced. <I> **** Actions Taken **** Wrote CR/WR | 02-00-PSR-SR-48,02-00-PSR-SR-9
396085 | CR | 20190625 |  | 3 | (R24LL) Ops outage Lesson learned to date (Clearance order r |  |  |  | N | NO | <D> **** Detailed Description **** Below are comments from One Note, specific to clearance order items â€¢ Danger clearances were not written to lift leads to make RCC-V-104 throttleable for SOP-RCC-FILL to the containment and to reterm leads for RCC-V-104 following the system fill. â€¢ O-RWCU-V-34-001 contained a valve up high out of reach (RWCU-V-911), CO had to be re-written. â€¢ Tagging of TSW-V-44 (TSW-PCV-20 bypass) requires a scaffold build. â€¢ Clearances that support draining of a system for maintenance need to be more specific to the maintenance that it is supporting. Example would be the RHR B drain clearance which included draining the entire system down to the pump casing drain when there was no work scheduled down to that elevation. Draining an entire system unnecessarily costs time and therefore money as craft are on hold waiting for a complete drain and then extra time on the recovery side to fill. The condensate system drain is another example where we likely did not have to do a complete system drain to perform work. <I> **** Actions Taken **** Initiated CR <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
396087 | CR | 20190625 |  | 3 | SOP-MT-AOP/TEST revision to align with NEIL guidance |  |  |  | N | NO | <D> **** Detailed Description **** Nuclear Electric Insurance Limited (NEIL) Loss Control Manual, section 2.2.4.3.2.7 provides a SHALL requirement for off-line testing of emergency lubricating oil pump (EOP) on a frequency of every fuel cycle. Currently, this testing is performed under SOP-MT-AOP/TEST which simulates pressure decay by operating test valve TO-V-116 to slightly bleed off pressure until TO-P-BOP starts and then continues until TO-P-EOP starts. NEIL bulletin 14-02 which is provided under the Loss Control Manual provides guidance for performing this off-line testing by â€˜actuating pressure decayâ€™ and validating the starting logic to test the ability of the EOP to provide adequate pressure to the turbine-generator centerline as specified by the OEM. NEIL interprets â€˜actuating pressure decayâ€™ to mean stopping the running oil pump to actually cause a loss of pressure and observing that the EOP starts at the correct setpoint. This does not align with the current test method used at Columbia which simulates loss of the running oil pump by throttling of TO-V-116. This condition report is generated to document this potential misalignment with implementation of a SHALL requirement and to work with Columbiaâ€™s NEIL loss control representative to ensure complete compliance with this requirement in the future. NEIL representatives did not identify any concerns with functionality or operability of TO-P-EOP, but just with test method for compliance with Loss Control Manual 2.2.4.3.2.7 requirements. Recommend assignment to Plant Programs to coordinate responses to NEIL. <I> **** Actions Taken **** 1) Discussed with NEIL Loss Control Lead 2) Discussed with manager 3) Initiated this condition report
396088 | CR | 20190625 |  | 3 | R 24 LL |  |  |  | N | NO | <D> **** Detailed Description **** Add Control room communication requirement and late date columns to schedulle just like you have on daily schedule. Have a PMT coordinator in the OCC so all work that needs to be completed during a PMT does not get skepped. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
396090 | CR | 20190625 |  | 3 | WO Model 02128545 for Capping of liners needs improvements. |  |  |  | N | NO | <D> **** Detailed Description **** HPI-16.2 (Operation of Liner Grapple) has guidance for safe operation and pre-operational checks for use of grapple. HPI-16.2 should be attached for referenced in the model work order to perform capping and processing of Liners. <I> **** Actions Taken **** Discussed concern with WO Planning, and HP Supervision.
396091 | CR | 20190625 | CAQ | C | CAPR removal approved by PARB |  |  |  | N | NO | <D> **** Detailed Description **** CR 271826 documents a Significant Condition Adverse to Quality (SCAQ) with a Corrective Action to Preclude Repetition (CAPR). On 6/25/19 PARB approved removal of this CAPR based on a change to a Technical Specification (TS). Based on the change to the TS the problem identified in CR 393449 will no longer be a problem. Currently SWP -CAP-01 does not list a criteria for changes to TS as a basis for removing a CAPR. <I> **** Actions Taken **** This CR is written to document the approved deviation and to revise SWP-CAP-01 to modify the criteria. Recommend C to AR-PERFIMP.
396093 | CR | 20190625 |  | 3 | Additional MD valve leakby and MWe loss | N | N |  | N | YES | <D> **** Detailed Description **** Following startup for Cycle 25, it was noted that MD-V-83 and MD-V-84 were experiencing higher downstream temperatures than prior to R24. MD-V-83 downstream temp rose 25 F to 213 F and MD-V-84 rose 60 F to 250 F. Losses from MD-V-83 are now 0.6 MWe and losses from MD-V-84 are now 3.2 MWe. These valves were each leaking by 0.3 MWe prior to R24. <I> **** Actions Taken **** Initiated CR. Notified Systems Engineering and E-FIN. Recommend review of isolation possibilities or online maintenance. | 02-00-MD-V-83,02-00-MD-V-84
396095 | CR | 20190625 |  | 3 | EC17117 TMU-P-1B Replacement incorrectly scoped | N | N |  | N | NO | <D> **** Detailed Description **** The TMU-P-1B is being replaced under EC17117. It was presented to Design Sub-Committee as a similar replacement to EC16858 Replace TMU-P-1A. EC16858 was a simple direct replacement modification. DSC agreed to have Minor Mods perform the design change. However, after beginning the design development, it was identified that the pump replacement included a new DynaSeal being installed that no longer requires potable water for lubrication, and the starting permissive to be removed. These changes are quite extensive and increased the affected drawing impacts from 5 to 50 drawings, causing a significant amount of additional work not planned or budgeted. As a result, it has caused schedule slips and strain on meeting the work management schedule. Per GBP-FIN-28 this project should have been Capitalized and not performed by Minor Mods. Proper presentation and assessment of the scope is critical for ensuring future success. The same changes will impact future replacements of TMU-P-1C and TMU-P-1A. Recommend CR to Reactor Maintenance for review of applicability to future modifications. <I> **** Actions Taken **** Discussed with Design Engineering and initiated CR.
396096 | CR | 20190625 |  | 3 | SCW High D/P and Top Coil Alarms | N | N |  | N | YES | <D> **** Detailed Description **** SCW high D/P has been locked in since yesterday and high since the system was placed in service following R24. See AR 395600 . Ops attempted to clear the alarm by throttling open SCW-V-523 as directed by the SOP, but with the valve full open the high d/p alarm would not clear. On 6/25, High Generator Top Coil Delta T alarm, P820-B3, 6-4 was received. SCW-V-523 was throttled shut 5 turns which caused operating pump discharge pressure, #2 SCW pump, to increase to approximtely 85 psi. D/p correspondingly increased to approximately 35 psid and the top coil delta T alarms cleared. There are no visible problems with TSW -TCV-4. OEM states this condition may be indicative of foreign material preventing adequate stator cooling flow. Investigate and determine cause of high d/p and restore system to normal operation. <I> **** Actions Taken **** Discussed with CRS and SM. Recommended swapping SCW pumps to see if better performance can be obtained from the standby pump. <N> **** Equipment Description **** 441" TG | 02-00-SCW-DPI-1
396097 | CR | 20190625 | CAQ | D | HCU 14-19 Low Pressure Alarm | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-14-19. After investigation, Rod Accumulator Trouble Alarm P603-A7 drop 6-7 was for CRD-HCU-14-19 low pressure. <I> **** Actions Taken **** Dispatched OPS-2 to investigate. Recharged HCU. <N> **** Equipment Description **** RB 522 Alarm was noted to come in early with accumulator pressure at approx 1010 psig. | 02-00-CRD-HCU-1419
396098 | CR | 20190625 |  | 4 | All Lights are out in MC-S2-1A room on the R471 | N | N |  | N | YES | <D> **** Detailed Description **** All Lights are out in MC-S2-1A room on the R471. The lights are still very dimley lit. Please repair replace as necessary. <I> **** Actions Taken **** wr/cr <N> **** Equipment Description **** lighting in reactor Non-essential lighting.
396099 | CR | 20190625 | CAQ | D | CRD-HCU-1411 accumulator trouble alarm. | Y | N |  | N | YES | <D> **** Detailed Description **** RD-HCU-1411 accumulator trouble alarm. Alarm due to water <I> **** Actions Taken **** wrote CR for tracking purposes | 02-00-CRD-HCU-1411
396100 | CR | 20190625 |  | 4 | Received RFT A/B Trouble alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received P840-A1.3-4, RFT A/B Trouble alarm. Further investigation of the RFT-COMP-1 shows RFW-P-1A PLC Pulse Impact Card Fault and RFW-P-1A on Single CPU Only! fault. These are P1 TR PI ERROR and P1 TR DUAL MODE code faults. Both feed pump controllers remain in Automatic controlling appropriately. The alarms were acknowledged on RFT-COMP-1 alarm screen and the RFT A/B Trouble alarm remains locked in. <I> **** Actions Taken **** Notified CRS and initated CR and WR <N> **** Equipment Description **** MCR | 02-00-RFT-COMP-1
396101 | CR | 20190626 |  | 4 | E-EXC-1 seal pushed out | N | N |  | N | YES | <D> **** Detailed Description **** The rubber seal on the base of E-EXC-1 dog house has been pushed out on the north side due to D/P between internal and external pressures. The seal was able to be pushed back in place, but it is obvious that the housing is not in contact with the seal, thus the seal is not a seal at all. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-E-EXC-1
396102 | CR | 20190626 |  | 4 | CF-P-41A green slime in gear oil | N | N |  | N | YES | <D> **** Detailed Description **** There is a green slimy/scale looking substance on the surface of the oil in the gearbox of CF-P-41A. This is not normal. It may be chemical inleakage of some sort, has a similar green color to other piping leak location. | 02-00-CF-P-41A
396103 | CR | 20190626 |  | 4 | BS-V-39A continues to indicate open | N | N |  | N | YES | <D> **** Detailed Description **** Trap Station 16 BS-V-39A continuously indicates open with a High Level on H13-P831 Bd T. BS-V-39A has a history of excessive cycling with a recent Temp Mod to hard wire the valve closed. Recommend further evaluation or repairs. <I> **** Actions Taken **** Dispatched operators to investigate instrument rack indications. Instrument rack investigation did not reveal anything remarkable. | 02-00-BS-V-39A
396104 | CR | 20190626 |  | 4 | Recirc A System Vib High Alarm Repeatedly Alarming | N | N |  | N | YES | <D> **** Detailed Description **** Recirc Pump A High Vibration Alarm comes in several times a shift (H13-P602.A6.2-4). Each time, it is RRC-VBI -P1A/MLBXY, which is for the Motor Lower Bearing X and Y (radial axis). It comes in and clears and must be reset locally on the RB 522. No other vibrations are indicated as being abnormal. This is not related to a specific pump Hz. It has occurred several times at 100% and also occurred several times during power ascension with flow. <I> **** Actions Taken **** Notify CRS. Dispatch Operator to reset alarm after verification of vibrations on local camera. Initiated CR and WR <N> **** Equipment Description **** RB 522 | 02-00-RRC-P-1A,02-00-RRC-VBI-P1A/MLBXY,02-00-RRC-VMP-1
396111 | CR | 20190626 |  | 3 | R24LL ASD/RRC work | N | N |  | N | NO | <D> **** Detailed Description **** Each of the four ASD drives was planned and executed differently from each other during the planning process. This is likely the result of copying past work which was developed independently. This resulted in multiple delays, work instruction revisions and temp lifts to get the work performed during R24. The sequence of initial troubleshooting, testing, and repairs needs to be developed and standardized and then all drives written to that standard. Recommend planning, engineering, and ops work control develop a standardized work instruction and tagging scheme for this scope of work for future outages before any planning is started. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817. Planning assigned one planner for all RRC ASD work for R25. Barring unexpected turnover, this should resolve PMT conflict issues.
396113 | CR | 20190626 |  | 3 | Higher than normal flows to #3 and #4 Evap Ponds | N | N |  | N | NO | <C> As per MRT, this was changed from a 4/TR to 3/ENV to document investigation and provide results to maintenance to correct. <D> **** Detailed Description **** On startup the flow to the #3 and #4 Evaporation Ponds increased from approximately 5 gal/hr to 100 gal/hr. This is maintaining at this level. Evaporation Ponds are currently able to take this increased flow. <I> **** Actions Taken **** Reported to Chemistry. Need to invenstigate the source of the water. <N> **** Equipment Description **** #3 and #4 Evaporation Ponds Per conversation with Environmental Services, volumetric flow rate to ponds 3 and 4 as much higher than reported in the CR. Volumetric flow rate values over the last few days as follows: 6/17/2019 - 241 GPH; 6/19/2019 - 857 GPH; 6/21/2019 - 1142 GPH; 6/24/2019 - 1284 GPH. There is a flow to ponds 3 & 4 that needs to be accounted and stopped. Source of leak was identified via CR 00396676--cross referenced to this CR.
396114 | CR | 20190626 |  | 4 | 2 Pieces of M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** 2 Industrial Scientific Gas Monitors have been Rejected- No parts available. Used for personal safety only. No Plant Impact. Please assign to Maintenance Calcode #0065205. DEF #7059A written. Calcode #0065617. DEF #7060A written. No Action Required.
396115 | CR | 20190626 | CAQ | C | M&TE found out of tolerance |  |  |  | N | I DONT KNOW | <C> Changed to C to AR-EFIN to complete the EFIN evaluation. ENG CRG representative agreed. <D> **** Detailed Description **** CalCode 006060 Fluke model 700P29 found OOT Used in the OOT Range, EFIN needs to Evaluate within the 20 Days allowed according to PPM 1.5.4. DEF #7061A evaluate the two usages.. .DEF #7061A
396116 | CR | 20190626 |  | 4 | DLR through X-Ray machine |  |  |  | N | NO | <D> **** Detailed Description **** At approximately 0545 on 6/26/19 a WPS employee ran another WPS employees DLR through the X-Ray machine. The employee gave their DLR to another employee to turn in it for them and that employee forgot that it was in their lunchbox prior to sending it through the X-Ray machine. The employee should have turned it in to their management instead of relying on another employee to turn it in for them, as they were directed. <I> **** Actions Taken **** Contacted supervision
396120 | CR | 20190626 |  | 4 | Generator "doghouse" has air leak with red duct tape | N | N |  | N | YES | <D> **** Detailed Description **** The generator "doghouse" has an air leak with red duct tape attached to attempt to stop the leak (see EDMS pictures). The duct tape is totally ineffective and is not an authorized temporary change. There is significant "windage" leakage that should be repaired per the previous backup generator system engineer. The previous backup SE said this is most probably windage leakage and not a hydrogen leak due to the large size of the leak. <I> **** Actions Taken **** Generated CR and WR to remove the duct tape and repair the leak. The previous backup SE said the doghouse doors can be temporarily opened as a TASM to relieve pressure during the repair activities. <N> **** Equipment Description **** Main generator | 02-00-E-GEN-1
396121 | CR | 20190626 |  | 3 | EC 17007 places plant in high-risk scenario |  |  |  | N | YES | <D> **** Detailed Description **** EC 17007 removed the closing air line for AR-V-1 and placed a gag on the valve to maintain the valve open. This was due to AR-V-1 being a single point vulnerability that caused a plant transient. WO 0212512901 will remove the remaining air supply line for the opening side of the valve and leave the gag as the single point to maintain AR-V-1 open. The removal of the air supply line will be performed on-line. This action places the plant back in a single point vulnerability, solely relying on the gag to prevent a plant transient. PPM 1.3.76 ranks the installation of a gag as a high risk activity if the gag is installed on a valve in an operating system and would result in plant trip or transient if gag failed to prevent motion (Activity 27). One of our focus areas is â€œRisk Management is core Businessâ€. How is this the proper action given that this leaves the plant in a high risk activity for the life of the plant? Recommend revising the EC to remove the internals of the valve and flanging the body to remove any chance for another transient due to AR-V-1. <I> **** Actions Taken **** Spoke with work management and component manager Wrote CR | 02-00-AR-V-1
396122 | CR | 20190626 |  | 3 | OSCR and SMS process needs revised |  |  |  | N | NO | <D> **** Detailed Description **** After Submittal, OSCR or SMS are normally routed through work management, engineering and Radiological planning, but are NOT required to be routed through the applicable end user. OPS, work management and engineering determine the ability to move work from outage to online without consulting the shops. One example is the AOV diagnostic testing of MS-PCV-11A was moved from outage work to online work without the shops input. The impact of this decision adversely affects shop resources. The remainder of the loop was calibrated during R24, at which time MS-PCV-11A was part of the test. Performing the diagnostic testing separately requires additional resources that would have been minimized had the diagnostics been performed during the outage with the rest of the loop. Recommend revising the OSCR and SMS process to include routing to the responsible shop to ensure all aspects of the change are understood and accounted for before being approved.
396124 | CR | 20190626 | CAQ | D | FDR-P-15A tripped | N | N |  | N | YES | <D> **** Detailed Description **** While pumping FDR-SUMP-T4 with FDR-P-15A & 15B, the T-4 High-High alarm began actuating and clearing very rapidly, with a rapid relay clicking sound in the RWCR front panel (probably 10 or more clicks per second), and after 10-15 seconds FDR-P-15A tripped (both sets of light indications went out), and the relay noise stopped. FDR-SUMP-T4 pumping was continued on FDR-P-15B only. Recommend investigate and repair FDR-P-15A. <I> **** Actions Taken **** Informed MCR, generated AR/WR. | 02-00-FDR-42-3C1C,02-00-FDR-P-15A
396125 | CR | 20190626 |  | 3 | R24LL: CRD HCU Refurbishments |  |  |  | N | NO | <D> **** Detailed Description **** CRD HCU refurbishments are performed each outage per PPM 10.5.9. During R-24, there were 18 HCU's refurbished. Since PPM 10.5.9 contains some PMT steps within the procedure, task 01 on each work order was not able to be closed until the PMT tasks on that work order were completed. This is because task 01 says to perform PPM 10.5.9. . The impact was that mechanical maintenance had 18 activities ride the schedule for several days. . To improve predictability and daily adherence to the schedule, I recommend modifying the model work orders for HCU refurbishments so that Task 01 can be closed after the maintenance is completed. This can be accomplished by revising Task 01 on the model work order to state "perform HCU refurbishment per PPM 10.5.9 up through step X.XX. This way task 01 can be closed. For scheduling purposes, the PMT tasks complete the PMT steps within PPM 10.5.9 so there is no reason to keep task 01 open until the PMT tasks are completed.
396126 | CR | 20190626 |  | 3 | R24LL: Ineffective use of Resource Curves |  |  |  | N | NO | <D> **** Detailed Description **** For R-24, there were many explanations for why work was not getting done per the schedule that centered around not having sufficient number of qualified individuals to work the tasks. For example, welding requires a specific qualification to perform. The mechanic shop realized that they had too much welding work in the schedule given the number of qualified welders they had. This was too late to move this work to the site support contractor and some of the work was removed from scope. . The "R24 Day Resource and Qual" spreadsheet can be used to see what qual groups are scheduled for each day of the outage. This spreadsheet tool is available prior to the outage so we should be able to detect a problem with qualifications prior to the beginning of the outage. . Recommend the following actions: . 1. Outage Management conduct familiarization training for all shop managers (including supplemental personnel managers) to ensure they understand how to use the Resource and Qualification spreadsheet. . 2. Outage Management publish Qualification curves with the "Resource Profiles" in pdf format of all the qualification groups in the schedule. This would make it very easy for a shop manager to quickly see how many man-hours are required each day for a particular qual group. . 3. Adjust the T-2 MRM content to include a discussion on qualification groups during the shop report outs so that we can challenge if there looks like alot of man-hours required for a particular qualification group.
396127 | CR | 20190626 |  | 3 | R24LL SOP-COND-OPS enhancement |  |  |  | N | NO | <D> **** Detailed Description **** R24 LL Revise SOP-COND-OPS section 5.5.2 to prevent tripping and then restarting condensate, modify step â€œuâ€. to 3 substeps as follows. If Condensate no longer required: VERIFY Condensate Filter Demineralizers have been removed from service per SOP-CFD-SHUTDOWN. VERIFY COND-V-670 is CLOSED (Suction Supply to CRD) (SB 438 H3/3.6, above hot water heater SPWH-HX-1). SHUTDOWN condensate per SOP-SOND-SHUTDOWN
396128 | CR | 20190626 | CAQ | D | HT-HTP-FP/7AG (HT-H-SW71/A) | Y | N |  | N | YES | <D> **** Detailed Description **** w/o# 02113213-02, During performance of the work order step 4.6E, the resistance criteria was not met. the criteria is GT 1000 M ohms and our reading was 19.5 M ohms <I> **** Actions Taken **** notified supervisor and intiated CR <N> **** Equipment Description **** HT-H-SW71/A
396130 | CR | 20190626 | CAQ | D | HT-HTP-FP-7AG (HT-H-SW71/B) | Y | N |  | N | YES | <C> This CR was changed from a "C" level to a "D/TR" due to the REP/REGE assignments being cancelled. <D> **** Detailed Description **** w/o# 02113213-02 During performance of steps 4.9D and 4.9E the resistance criteria was not met. the criteria is GT1000 M ohms and our readings were 82 and 19.1 M ohms <I> **** Actions Taken **** notified supervisor and intiated CR <N> **** Equipment Description **** HT-HTP-FP/7AG
396131 | CR | 20190626 | CAQ | D | CW/TSW Halogenation Cancelled 6/26/19 Due to BD Flow Issues | N | Y |  | N | YES | <D> **** Detailed Description **** The halogenation scheduled for 6/26/19 was cancelled when after the blow down was secured there was still flow indication on the blow down flow meter. As per the NPDES Permit halogenations can only occur if the Blow down flow is closed and has no flow. Flow meter CBD-FT-1 indicated a flow of negative 200 gpm. EDNA indicated a positive flow of 200 gpm (numbers were fluctuating). This uncertainty in flow lead to the decision to not halogenate. Flow meter CBD-FT-1 is an NPDES Permit compliance reporting flow meter and should be corrected as soon as possible. <I> **** Actions Taken **** Repair or investigate the flow meter problem and correct. <N> **** Equipment Description **** CBD-FT-1 CW Blow Down Flow Meter
396133 | CR | 20190626 |  | 3 | Main Transformer cooler group pump water intrusion | N | N |  | N | YES | <D> **** Detailed Description **** AR 396019 (E-TR-M2) and AR 396011 (E-TR-M3) identified problems with Cooler group #2 for each transformer and the overloads tripping without being able to be reset. During the investigation each of the cooler group pump electrical termination covers were removed and water was found in the termination box based on the WR for each Cooler group. The termination box for the cooler group pumps for each transformer are the lowest point in the system and would gather water. All conduits and boxes we opened, inspected and tightened prior to performance of the Deluge test. This water inside of this conduit is most likely from the deluge test which was performed after all of the terminal boxes and conduits were inspect for each main transformer. The purpose of this CR is to open up the other junction boxes for the other main transformer pumps and remove any water inside of the enclosure. | 02-00-E-TR-M1,02-00-E-TR-M2,02-00-E-TR-M3
396135 | CR | 20190626 |  | 3 | Strong Sewer Gas Oder in BLDG. 32 Breakroom |  |  |  | N | NO | <D> **** Detailed Description **** There is a strong sewer gas odor in the breakroom of Building #32. This building is outside the Protected Area North of the plant. Caution signs are being posted on the interior and exterior doors communicating â€œNO ACCESSâ€ until the problem can be resolved and/or further notice. Industrial Safety will monitor air quality and potential hydrogen sulfide gas level danger. <I> **** Actions Taken **** Contacted Facilities, EN Industrial Safety, WPS Industrial Safety, Rx/MM Manager and WPS Site Manager.
396136 | CR | 20190626 |  | 3 | PPM 12.14.11 requires an enhancement |  |  |  | N | NO | <D> **** Detailed Description **** PPM 12.14.11 requires a procedure enhancement. There are two sections that have issues with numbering in the procedure. Section 7.9, the first step of the section at the bottom of page 11 does not have a number sequence assigned to it and is skipped which throws off the numberin sequence of the rest of the section. Section 7.12, the only step in this section is listed as step 6.7.1, which does not follow the proper sequence. <I> **** Actions Taken **** Initiated AR/CR. Notified the procedure sponsor.
396138 | CR | 20190626 | CAQ | C | M&TE Found out of Tolerance |  |  |  | N | I DONT KNOW | <C> Changed to C to AR-EFIN to complete the Evaluation. ENG CRG resprentative agreed. <D> **** Detailed Description **** Calcode #0066939 Votes Infinity Contacts Cable Assembly- model 85006 found OOT & adjusted within specs. EFIN will need to Evaluate the two usages. DEF #7062A written. Completed DEF will be attached EDMS. <I> **** Actions Taken **** EFIN to Evaluate usages
396141 | CR | 20190626 |  | 4 | SP-13b conductivity >10% difference from meter/recorder. | N | N |  | N | YES | <D> **** Detailed Description **** Performed weekly cross checks of SP-13b feedwater conductivity grab sample (0.064 uS) against PSR-CITS-3B meter (0.055 uS) and S-CR-1 pt .3 recorder (0.057 uS) and found >10% difference in values. <I> **** Actions Taken **** Contacted supervisor and wrote CR/WR. Verified meter and recorder are within 20% of grab sample and are still operable. <N> **** Equipment Description **** TG 441' Chemistry sample room | 02-00-PSR-CITS-3B,02-00-S-CR-1
396142 | CR | 20190626 |  | 4 | NANTeL Web Service Is Not Functioning |  |  |  | N | NO | <D> **** Detailed Description **** The NANTeL Web Service which uploads certifications to NANTeL and downloads certification completion data to PQD is not functioning. <I> **** Actions Taken **** Notifiied Information Services, Training Managment and Information Services Management and drafted a Broadcast Message to communicate the issue. <N> Nantel interface was fixed on 6/26. Issue resolved. recommend ncaq4.
396143 | CR | 20190626 | CAQ | D | DEA-FN-13, 23, 33 Exhaust Duct Holes | Y | Y |  | N | YES | <D> **** Detailed Description **** While performing a system walkdown of the DGHVAC system, the system engineer noted 3 approximately 3/4" holes each on the ductwork downstream of DEA-FN-13, 23 and 33. While the system engineer could not reach the holes to check for air flow, it appears that the hole would allow a small percentage of the exhaust air to return to the room. DEA -FN-13, 23, and 33 function to prevent the buildup of oil fumes in the oil transfer pump rooms. These fans are not credited to provide any cooling function. They do not perform a safety related function. These holes do not affect the safety related function of the diesel generators as it has been determined that a complete loss of function would not result in a fire or explosion risk. In this case only a small percentage of air is returning to the room. The majority of air is being exhausted to the atmosphere. See EDMS for photos. <I> **** Actions Taken **** Discussed the impact to the plant with the shift manager prior to initiating the CR. | 02-00-DEA-FN-13,02-00-DEA-FN-23,02-00-DEA-FN-33
396144 | CR | 20190626 |  | 4 | R24 LL Application of the 10 30 60 Rule |  |  |  | N | NO | <D> **** Detailed Description **** Consider broader application of the 10 30 60 Rule online beyond system outage windows to strengthen use of and understanding of the importance of its use.
396145 | CR | 20190626 | CAQ | B | Qualification Discrepancies for ASCO NP-1 Valves | Y | N |  | N | YES | <C> RISK: MEDIUM CAUSES: UNCERTAIN, INVESTIGATION TEMPLATE REQUIRED <D> **** Detailed Description **** During review of recent industry activity, it was identified that the CGS qualification documents had the following discrepancies: . 1. The documents did not provide discussion on the difference in aging affects based on applications which use air vs. nitrogen as a process medium. . 2. The documents used non-conservative temperature rise values in the thermal life calculation for plant conditions. This impacts qualified life of continuously energized ASCO valves. . 3. The documents include thermal aging calculations based on the weak link elastomer being the core disc; however, the review determined that the weak link material is the diaphragm on the NP8316. This impacts qualified life of continuously energized ASCO valves. . An effort was made to recalculate the thermal life for the applicable valves based on the above criteria; this resulted in a significant decrease in qualified life. The new qualified life would be approximately 23 years (NP8316) and 30 years (NP8320). These qualified life values are based on plant design temperature of 104 deg. F which provides significant conservatism. Recommend assignment to AR-PPROG to update the affected QIDs and PMs. <I> **** Actions Taken **** A review of the installed EQ related ASCO solenoid valves was performed to identify any components which have been installed in a continuously energized application for greater than the recalculated qualified life. The components identified in the equipment list for this AR have been installed for ~35 years based on review of the installation history and MWR database. Although these have been installed for greater than the recalculated qualified life, there is a large amount of conservatism in the plant temperatures used for the thermal aging calculation (~17 deg. F). This margin, if removed, would take the qualified life to at least 57 years for either the NP8316 and NP8320 solenoid valves. Therefore, there is no impact to the qualified status of any installed component. | 02-00-FPC-SPV-1,02-00-ROA-SPV-10,02-00-ROA-SPV-11,02-00-ROA-SPV-12,02-00-ROA-SPV-13,02-00-ROA-SPV-15,02-00-ROA-SPV-17,02-00-ROA-SPV-200,02-00-SGT-SPV-2A,02-00-SGT-SPV-2B
396146 | CR | 20190626 |  | 4 | mc-s2-1a lighting | N | N |  | N | YES | <D> **** Detailed Description **** lights require repair/replacement. light level is very low PFSS lighting <I> **** Actions Taken **** informed MCR initiated CR/WR <N> **** Equipment Description **** MC S2-1A room lighting
396147 | CR | 20190626 |  | 3 | Revise OSP-SLC/IST-Q701, remove ref to PMID 23618 and 23619 |  |  |  | N | NO | <D> **** Detailed Description **** Revise OSP-SLC/IST-Q701, remove ref to PMID 23618 and 23619. Both PMID's are retired.
396148 | CR | 20190626 |  | 3 | Revise instructions/discription for PMID 17131-01, 02, 03 |  |  |  | N | NO | <D> **** Detailed Description **** Revise instructions/discription for PMID 17131-01, 02, 03 for the electrical support task. The electrical support tasks instructions/discriptions do not match OSP-SLC/IST -Q701 Prerequisites. It is not clear what the scope intent of PMID 17131-01 is. Once the instructions/discriptionof RQ 01 is updated ensure that it is clearly written in OSP. -SLC/IST-Q701
396150 | CR | 20190626 |  | 3 | (QA) 5 R-24 WOT Records Show Inadequate Supervisor Reviews | N | N |  | Y | I DONT KNOW | <D> **** Detailed Description **** (QA) Five R-24 Outage Work Order Task (WOT) Records show inadequate Supervisor reviews, contrary to MI-3.6.4 "Work Package Closure". Supervisors did not catch WOT instructions missing initials on blank lines, and did not catch cover sheet missing initials and names of persons that initialed for performing steps in WOT instructions. The consequence is that the Quality Assurance Records (QARs) for five WOTs do not meet the station's standards because they are missing evidence of task completion and the identification of performers. Requirements: â€¢ MI-3.6.4 rev 023 section 3.2 "Work Package Review" step 3.2.3 requires Supervisor to "verify all retained pages calling for signatures or initials have an entry". â€¢ MI-3.6.4 step 3.2.5 states, "If initials appear anywhere in the package, verify that initials and name are recorded in the â€œRecord Initials of Performerâ€ section of the WOT." Factual Basis: The following QARs in the Records Management module in Asset Suite show: â€¢ QAR WOT 0213600401 steps 4.12 through 4.16 are blank (missing initials/date) â€¢ QAR WOT 0213802401 steps 4.18 through 4.20 are blank (missing initials/date) â€¢ QAR WOT 0213802501 at least 12 steps were initialed/dated by a performer that did not record their initials up front in the "Work Performed By" section â€¢ QAR WOT 0213802601 at least 12 steps were initialed/dated by a performer that did not record their initials up front in the "Work Performed By" section â€¢ QAR WOT 0214393701 one step was initialed/dated by a performer that did not record their initials up front in â€¢ the "Work Performed By" section Insights: â€¢ All of the above WOTs are shown in Data Glance as "eWP step: Record Completed". â€¢ Most of the WOT steps above with no initials were steps to be performed by a Supervisor. â€¢ All the missing initials up front in the "Work Performed By" sections were for steps performed by a Supervisor. Prior to eWP, a Maintenance administrative person reviewed the WOT packages for blanks not filled in; however, no administrative person is included in the current EWP review cycle. <I> **** Actions Taken **** Contacted the Mechanical Maintenance Component Group Manager. . Recommend routing this CR to Mechanical Maintenance. . This Deficiency was identified during the R-24 Outage Quality Surveillance SR-19-01.
396151 | CR | 20190626 |  | 3 | Unable to update iPads with new version of Mobile Rounds |  |  |  | N | NO | <D> **** Detailed Description **** After upgrading eSOMS mobile to the latest version, some of the iPADS will not accept the new verision of the application.
396152 | CR | 20190626 |  | 3 | (QA) Multiple work orders not planned for scheduled work |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Multiple work orders have not been planned for scheduled work inside of T-13. As of 6/26/19, over 100 scheduled work orders inside of T-13 have a status of not planned (status 22), returned to planner (status 23) or hold for approval (status 25). Planning work late in the schedule process impacts the clearance order, radiation protection, supply chain, senior reactor operator and other groups by requiring a rapid turnaround on review, work on and approval of the work orders for that group. This also creates a risk to not performing the work as scheduled due to not being ready which could impact equipment reliability, correction of conditions affecting quality and require an additional unplanned out of service window to perform this work. Requirements: â€¢ WCI-4 (Online Work Control Process) section 3.4 states that all planning be completed by the end of the T-14 week. Factual Basis: â€¢ Nine work orders in the T-7 work week are still at status 22 and one of those work orders will correct a condition adverse to quality (02145603 GROUT FILL PARTIAL BORES IN TMU/CBD VLV BOX #9, 12, 13 ROOFS). â€¢ Fifteen work orders in the T-8 work week are still at status 22 and three are conditions adverse to quality (02103786 CRD-V-506B PACKING LEAK OF 1 DROP PER MINUTE, 02136698 Evaluating Extent of Condition for RHR-HX-2A Pitting and 02131805 RHR-C Rm Cooler Flow Low / Temp Hi, H13-P812.R2, 2-2, alarm). â€¢ In the T-11 RCIC system outage work week there are seventeen work orders that are at status 22. Insights: â€¢ Discussions with planning personnel indicated a shortage of planners during the R-24 outage impacted the ability to complete the online planning work load. â€¢ No condition reports have been initiated by a line organization to address this issue and there is no formal recovery plan to correct this issue. This issue is considered a Deficiency identified during continuous monitoring surveillance SR-19-04. Recommend assignment to Maintenance. <I> **** Actions Taken **** Discussed with the Planning Lead and Work Control Manager. Initiated this CR. <N> Cancelled by mistake. Re-opened and taking to complete by request from the Maintenance Support Manager.
396154 | CR | 20190626 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | NO | <D> **** Detailed Description **** The following sensors were tripped and is reset: J7sensor - 500 Kv neutral ground overcurrent. BPA reports the following: a. Cause was Lighting in area b. Relaying involved a ASHE-MARION line and reclosed automatically c. <damaged equipment> no d. line reclosed e. <emergent outage needed?>no f. <230kv or 115kv involved>no g. <line equipment outage needed>no h. <Does the outage affect the 230kv or 115kv grid>no i. 1653 is the time of event j. 25 KV k. RAS did not initiate. l. Frequency did not change.
396156 | CR | 20190626 |  | 4 | Evaporator B Drain Level High system response abnormal | N | N |  | N | YES | <D> **** Detailed Description **** MCR received Evaprator B Drain Tank Level High alarm (4.840.A3 Drop 8-3). Locally HD-LIC-12B was indicating GT +6" level. HD-LIC-12B was already in manual and the as found output signal was 17.5 psig. Per the ARP output signal was lowered to 8 psig to open the drain valve to the LP 5 A(B) heater. After about 7 min, no change in level was observed, and output was lowered to 3 psig to open the dump valve to the condenser. There was no change in level for about five min, and output signal was placed back to about 17.5 psig to evaluate the situation. While/after the drain valves were closed, level indicated +5 inches. Output signal was again lowered to open the drain valves, level dropped quickly and controller set back to close drain valves at 0". level began to climb again and was GE 6" inches when it was checked a couple hours later. Maintence on HD-LIC-12B/ leak investigation needed. <I> **** Actions Taken **** Notified MCR | 02-00-HD-LIC-12B
396157 | CR | 20190626 |  | 4 | Multiple Oscillograph alarms due to electrical storm | N | N |  | N | NO | <D> **** Detailed Description **** Received multiple Oscillograph Started, H13-P800.C4.4-3, alarms between 18:00 and 19:00 on 06/26/19. BPA Dittmer and Munro report that these were due to lightning strikes / thunder storm activity moving through the area. All relaying involved resulted in automatic re-closure of affected lines and no damage reported as of creation of this AR/CR. Plant controllers and equipment response was normal. No emergent outages required or RAS initiated. One occurence (18:36) did affect the Midway- Benton 115KV line (automatically re-closed). E-TR-B supply voltage 120/119/119kV. E-TR-S supply voltage 240/240/240kV. The following sensors were tripped and reset: J7 - 500KV Neutral Ground Overcurrent; J9 - 115KV Neutral Ground Overcurrent. <I> **** Actions Taken **** Notified CRS and Shift Manager. Submitted AR / CR to document these occurrences.
396158 | CR | 20190626 |  | 3 | R24 LL - CW Tower Scrubbing |  |  |  | N | NO | <D> **** Detailed Description **** Do not scrub multiple Circ Water Cooling Towers clean of algae just prior to shutdown. As a result of knocking algae off of at least three towers, the released algae plugged the CW pump screens. This caused the CW bays of secured pumps to be much higher than running pumpsâ€™ and running pump bays to be barely above minimum required while non-running bays were almost overflowing. When all pumps were finally secured, it caused the overflow of CW into the electrical vault and eventual water migration through electrical conduits to various places including the RW 437. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
396159 | CR | 20190626 |  | 3 | R24 LL - Main Condenser Vents tagged early |  |  |  | N | NO | <D> **** Detailed Description **** The Main Condenser vent valves were Danger tagged OPEN too early. We attach firehoses to the Main Condenser vents for the initial drain of CW to storm drains in the Transformer Yard. After this initial drain, Main Condenser vents need to act as actual vent paths and pass air into the condenser. The problem was that the vent valves were Danger tagged OPEN, making it impossible to shut the vent valves and remove the firehoses without making a huge mess on T441. The firehoses on the vents kinked and collapsed, precluding a proper vent on the Main Condenser. When workers opened the Main Condenser Manway, the vacuum was broken, the condenser finished draining and CW basin level shot up, causing the MCR to secure TMU unnecessarily because they believed that Main Condenser CW side work was already in progress. Recommend not Danger tagging the Main Condenser vents until after the firehoses are removed. This allows the firehoses to be used for initial draining and then removed when needed to allow air to enter the vents. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
396160 | CR | 20190626 |  | 3 | R24 LL - Godwin Pumps as Temp CW Blowdown |  |  |  | N | NO | <D> **** Detailed Description **** Using the Godwin pumps as temporary CW blowdown pumps worked well and was much more reliable than the old method of using submersible pumps. By varying the speed of the Godwin pump we were able to precisely control CW basin level. Having two Godwin pumps available (one in service with a standby) allowed for routine maintenance on the pumps. <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817. Action complete. No additional actions required.
396161 | CR | 20190627 |  | 4 | SS-V-38 leaks by | N | N |  | N | YES | <D> **** Detailed Description **** SS-V-38 leaks by when closed which allows flow to SS-PCV-39 and cycles header pressure due to the PCV system non functional. Air isolated to SS-PCV-39 to fail it closed and isolate this path. repair or replace SS-V-38 | 02-00-SS-V-38
396162 | CR | 20190627 |  | 3 | Main Generator shaft ground brushes appear to be misaligned | N | N |  | N | YES | <D> **** Detailed Description **** Main Generator shaft ground brushes appear to be misaligned, the right brush as viewed from the back side appears to be at an angle that would have it riding on the shoulder. Please evaluate if they can be adjusted for a better ride. Pictures attached <I> **** Actions Taken **** wrote CR/WR <N> **** Equipment Description **** Main Generator shaft ground brushes t 501
396169 | CR | 20190627 |  | 4 | Added Scope |  |  |  | N | NO | <D> **** Detailed Description **** Work Order 02120017-03 Re-installation of Deadman onto railcar in support of Siemens transporting Turbine Rotor. Welded pads were severely degraded from the previous welding and removing of pads, had to perform extensive weld build-up prior to reinstall. (40 hours of grinding and welding) During inspection of weld area a section of existing weld was noted to have a crack and porosity in the weld. It was determined by Siemens for us to repair and have the area Q.C. and NDE inspected before completion. <I> **** Actions Taken **** Notified project P.M. <N> **** Equipment Description **** Railcar
396170 | CR | 20190627 | CAQ | D | TEA-SR-26 shows "No ISOK Control". | N | Y |  | N | YES | <D> **** Detailed Description **** While performing CSP-INST-D201 & CI-15.2 found TEA-SR-26 RM-2000 display shows "No Isok Control". <I> **** Actions Taken **** Verified the functionality of the sample rack TEA-SR-26 was not challenged by the Operational lights for Channel 1 & 2 were still illuminated. Contacted Supervision and Chemistry Specialist. CI-15.2 requires a CR & WR written. <N> **** Equipment Description **** RW 525' | 02-00-TEA-SR-26
396175 | CR | 20190627 |  | 4 | TOA-FN-2A is noisy. | N | N |  | N | YES | <D> **** Detailed Description **** From outside the fan compartment a squealing sound can be heard coming from inside the compartment of TOA-FN-2A. After entering the compartment there was a high pitched squeal that sounded like the belts were squealing on the motor sheave. Verified the fan rotor was rotating freely. Belts do not appear to be loose. Please investigate and correct. <I> **** Actions Taken **** Informed supervisor and wrote AR/WR. <N> **** Equipment Description **** T 501 F9/15.4 | 02-00-TOA-FN-2A
396176 | CR | 20190627 |  | 4 | HSSP-CP-P2 red beacon would not clear | N | N |  | N | YES | <D> **** Detailed Description **** While performing WO 02108589-01 15.2.46 step 7.3.4 HSSF -CP-P2 red beacon would not clear. Backed out of procedure and OPs is investigating. | 02-00-HSSF-CP-P2
396177 | CR | 20190627 |  | 3 | 15.2.46 needs to be revised, step 4.1 qual SFAY needs to be |  |  |  | N | NO | <D> **** Detailed Description **** 15.2.46 needs to be revised, step 4.1 qual SFAY needs to be changed to SFAU. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
396178 | CR | 20190627 |  | 4 | No Apparent Grounding on Scaffold Under Main Generator |  |  |  | N | YES | <D> **** Detailed Description **** On rounds it was noticed that the scaffold under the generator bushings, scaffold tag number 4386, had no apparent grounding device installed. There are two grounding cables next to the hydrogen drier that are not connected to anything. See photos. <I> **** Actions Taken **** Notified CRS <N> **** Equipment Description **** TB 471 W, under main generator bushings
396180 | CR | 20190627 | CAQ | D | FP-V-CO2/905 Packing Leak When Adding CO2 to Cardox Unit | N | N |  | N | YES | <D> **** Detailed Description **** FP-V-CO2/905 packing began leaking part way though addition of CO2 to Cardox Unit. <I> **** Actions Taken **** Informed supervision, wrote CR | 02-00-FP-V-CO2/905
396181 | CR | 20190627 | CAQ | D | 50.59SCREEN-19-0082 Contains an Error |  |  |  | N | NO | <C> As per MRT, changed to CAQ D from non-CAQ 4. <D> **** Detailed Description **** 50.59SCREEN-19-0082 for Condition Report 00395109 contains an error. Question 3 on the screen was correctly answered No, but the Basis for Conclusion incorrectly stated, â€œ. . . the presence of this foreign material in primary containment does affect the operation of any safety systems.â€ The statement should have read, â€œ. . . does not affect the operation of any safety systems.â€ <I> **** Actions Taken **** Completed 5059SCREEN-19-0096 to correct 5059SCREEN-19-0082 (See EDMS folder). <R> NRC Identified.
396183 | CR | 20190627 |  | 4 | Employee reported back strain |  |  |  | N | NO | <D> **** Detailed Description **** Employee reported tightness in back following work activities <I> **** Actions Taken **** Employee reported to their manager. Was escorted and seen by Occ Health
396184 | CR | 20190627 |  | 3 | CVI ISO 317-00,5146,1 Item 3 has wrong pipe schdule |  |  |  | N | NO | <D> **** Detailed Description **** Item 3 on drawing CVI ISO 317-00,5146,1 specifies the use of 1/4â€ Sch. 160 A106 Gr. B pipe. This is incorrect because Sch. 160 does not exist for 1/4â€ pipe. Calculation ME-02 -85-42 is the pipe stress calculation for the piping associated with drawing 317-00,5146,1 and it specifies 1/4â€ Sch. 80 A106 Gr. B pipe because Sch. 160 is not available. The drawing should be updated to reflect what is in the pipe stress calculation. Also while researching this issue it was discovered that AED SPC 15b.1 needs to be updated to reflect this change as well because page 15b.1-225 specifies Sch. 160 for 3/4â€ and smaller piping. This is a documentation issue only and has no impact on any SSCs at Columbia Generating Station. <I> **** Actions Taken **** Notified my supervisor and wrote this CR
396185 | CR | 20190627 | CAQ | C | (QA) Completed R-24 WOT in Records is Different Than in eWP |  |  |  | Y | I DONT KNOW | <D> **** Detailed Description **** (QA) Completed R-24 Work Order Task (WOT) Instructions page 7 for WOT 02136004-01 in Asset Suite Records Management module is different than same page shown in eWP (Data Glance). The Quality Assurance Records (QARs) for WOTs in the Records Management module are automatically created from eWP (Data Glance) and should contain the same WOT documents in both locations. Factual Basis: QAR WOT 0213600401 in the Records Management module in Asset Suite shows: â€¢ Steps 4.12 through 4.16 are blank (missing initials/date) on WOT Instructions pages 6 and 7 WOT 02136004-01 is at "eWP step: Record Completed" in Data Glance and shows: â€¢ Step 4.12 is blank (missing initials/date) on page 6, but steps 4.13 through 4.16 on page 7 are initialed/dated Insights: â€¢ The Data Glance Project Manager briefly looked into this, but could not understand why both locations do not have the same version of WOT Instructions page 7, and cannot investigate further because today is his last day here. â€¢ AR-CR 396150 was initiated on 6/26/19 to Maintenance to address the blanks on steps 4.12 through 4.16 on the WOT instructions and issues with other WOTs; however, only step 4.12 is blank in both locations for this WOT. <I> **** Actions Taken **** Contacted the Data Glance Project Manager and the Assistant IS Manager. . Quality recommends this CR be routed to IS Management. . This Deficiency was identified during the R-24 Outage Quality Surveillance SR-19-01.
396186 | CR | 20190627 |  | 3 | Scheduled work delayed-New equipment needed |  |  |  | N | NO | <D> **** Detailed Description **** During the evolution of WO#0210-8279-02, Drywell scaffold c-van remove, scheduled work had to be delayed due to not having an aluminum/steel deck trailer. We need to have an all metal deck trailer in order to stage the scaffold cvan on the trailer while loading it and unloading it during refueling outages/projects. Currently all truck trailers on site have wood decks on them and when staged inside the RX truck bay has to be placed on the Fire Tour Log and in-turn requires extra resources. Request that ENW purchase an Aluminum/steel deck trailer for future use. <I> **** Actions Taken **** Initiated Condition Report
396190 | CR | 20190627 |  | 4 | Request to Move Smoking Area |  |  |  | N | NO | <D> **** Detailed Description **** The current smoking area NW of bldg 62 is allowing smoke to be drawn in to the Security CAS and the smell is bothersome to the Officers inside. <I> **** Actions Taken **** Spoke to CRS about moving the area back to its original place now that the generators are no longer there NE of the GSB. Generated CR.
396191 | CR | 20190627 |  | 4 | Outlets in Security Breakroom are not working as designed | N | N |  | N | YES | <D> **** Detailed Description **** The three outlets on the E wall of the Security GSB breakroom are not working as designed. Outlet #'s: LP -5ADA-4, LP-%ADA-19, LP-%ADA-15. The outlets did not have power the breakers were checked and reset by qualified personnel. After the breakers were reset the microwaves had power but when attempting to use one at a time each lost power immediately. <I> **** Actions Taken **** Generated CR/WR to evaluate power supply for the outlets. <N> **** Equipment Description **** Three Outlets on E wall of the Security GSB Breakroom.
396192 | CR | 20190627 | CAQ | C | AED CAL SW-1037-1 has incorrect size for SW-FE-39 | Y | N |  | N | NO | <D> **** Detailed Description **** This is an administrative issue only. AED CAL SW-1037-1 indicates that the orifice flanges for SW-FE-39 as 2â€ while the actual size is 1 Â½â€ per AED MEC M524-2 Flow Diagram and CVI ISO 317-00,39,1 piping isometric. SW-FE-39 is Safety Related and Seismic 1 and is used to indicate flow for RRA-CC-10 which is the cooling coil for the DIV 2 MCC Room Fan Cooler RRA-FC-10. EC CMR 17864 has been prepared and has evaluated that 1 Â½â€ orifice flanges for SW-FE-39 and determined that there is significant margin in the pipe stress analysis and is acceptable for AED CAL SW-1037-1 and is qualified to perform it function with regards to SW B system and DIV 2 MCC Room. <I> **** Actions Taken **** Discussed with my supervisor, prepared EC CMR 17864, and contacted the Main Control Room.
396193 | CR | 20190627 | CAQ | D | NO QC VALIDATION IN WORK ORDER |  |  |  | N | NO | <C> As per MRT, changed from non-CAQ 4 to CAQ D. <D> **** Detailed Description **** PLANNING IDENTIFIED A WORK ORDER (01194253) THAT WAS PLANNED APPROXIMATELY TWO YEARS AGO THAT SHOULD HAVE HAD STEPS FOR QC TO INSPECT A PLATE THAT WAS BEING FABRICATED <I> **** Actions Taken **** PLANNER WAS COACHED, AND WORK ORDERS WERE RE-REVIEWED FOR QUALITY AND CORRECT STEPS. NO FURTHER ACTION REQUIRED. WORK ORDER TASK WAS RE-CREATED SO QC COULD BE INVOLVED IN INSPECTION.
396194 | CR | 20190627 |  | 4 | PPC Points G113 & G113AV reading 10 MWE lower than recorder | N | N |  | N | YES | <D> **** Detailed Description **** DEH signal T3 1230A and Red Pen on E-RECT-W/VAR/G1 are reading around 1192 MWE. G113 & G113AV, which are fed from the same signal as the Red Pen, are reading around 1182 MWE. This CR/WR should go to Maintenance to calibrate the G113 computer point. Operations: CTP Caclulation is currently using T3 1230A for MWE input. Do not switch over to using G113 for MWE until this point gets calibrated. <I> **** Actions Taken **** Verified CTP is not using this signal. Wrote this CR. | 02-00-PPC-COMP-8715,02-00-TDAS-COMP-8715
396196 | CR | 20190627 |  | 4 | PMRQ 17695-01 due but not performed in R24 | N | N |  | N | YES | <D> **** Detailed Description **** The calibration of components prescribed in the equipment list (MAIPD00071) include GEN end DIFF EXP. This instrument was removed from its mount in R24 and remounted to support outage work, but appears not to have been calibrated. PM WO 02111510 was generated to satisfy PMRQ 17695-01 and has a due date of 5/25/2019; however, the work did not make R24 scope. This PM has an A04 frequency and was last performed in R22/2015. For 25% grace, the late date should be 5/25/2020. However, the late data in passport shows 5/15/2021 which equates to 50% grace. The impact of not performing this PM activity in R24 is that the instrument appears to have an approximate 100 mil (conservative) bias. This condition may have contributed to allowing the GEN END DIFF EXP LONG/SHORT 4.820.B2 8-1 alarm for registering LONG during the downpower performed on 23June2019 (reference CR AR 396000). <I> **** Actions Taken **** Reviewed outage scoping for R24 and confirmed requested for scope by engineer with bundling opportunity with WO 02115227 and LPC work since Brg 8 pedestal cover would be removed. | 02-00-TG-MON-DE2
396197 | CR | 20190627 |  | 4 | Air Conditioning Unit on CW-PNL-P1B Not Working | N | N |  | N | YES | <D> **** Detailed Description **** The air conditioning unit (CW-AC-PNL/1B) is not working. This unit is mounted on the side of cabinet CW-PNL-P1B which stores instrumentation for the CW-M-P/1B and CW-P-1B remote monitoring system (vibration, temperature, motor amperage). This system is for monitoring and trending only. System appears to be working fine at this time. Cabinet is warm to touch. Instruments in cabinet can fail due to overheating. Recommend I/C to troubleshoot and repair as necessary. <I> **** Actions Taken **** Verified CW-PNL-P1B was still working and reporting data to server. Notified FIN I/C Maintenance Supervisor. | 02-00-CW-AC-PNL/1B
396198 | CR | 20190627 |  | 3 | RCC-42-8C7D Found In Mid-Position | N | N |  | N | YES | <C> As per MRT this is Non-CAQ 4 and not CAQ D. CR reassigned as severity 3 and assigned to OPSST at the request of Operations. <D> **** Detailed Description **** RCC-42-8C7D was found in a position midway between On and Off. The disconnect does not sound like it is closing properly when taken to On, and will, after a few seconds, pop back to a mid position. The control room does have light indication when while the disconnect is closed. <I> **** Actions Taken **** Cycled disconnect Left in Off Informed MCR <N> This issue is a disconnect issue and not human performance; no further actions required. | 02-00-RCC-42-8C7D
396199 | CR | 20190627 |  | 4 | RCC-V-72B disconnect found open after maintenance on MC-8C | N | N |  | N | YES | <C> As per MRT, this is a non-CAQ 4 instead of CAQ D. <D> **** Detailed Description **** On 6/27/19 at approximately 1530, workers had just completed a starter inspection on RCC-V-71B in MC 8C. While performing their housekeeping inspection one worker noticed that a disconnect switch for another nearby component (RCC-V-72B) on the same MC was in a mid position. The workers reported the condition to the CRS who in turn had the disconnect restored to its normally closed postion. During the process of reclosing RCC-V-72B disconnect the disconnect reopened on its own a few moments later. The disconnect was cylced open and closed several times. It was clearly sluggish and lacked the snap action that is expected of this type of disconnect. The inadvertent opening of the disconnect may be contributed to the vibration from seating of a nearby bucket during reinstallation (RCC-42-8C7A for RCC-V-71B). <I> **** Actions Taken **** Notified the control room. Observed the action of the disconnect when attempting to reclose. Generated WR to have the disconnect lubricated. <N> **** Equipment Description **** MC-8C R501 | 02-00-RCC-42-8C7D,02-00-RCC-V-72B
396200 | CR | 20190627 |  | 4 | ARGOS Out Of Service At GSB PAP | N | N |  | N | YES | <D> **** Detailed Description **** ARGOS HP-EQ-42782 located at the RCA exit point at the GSB PAP is out of service due to a "Low Background Rate" fault on foot detector 2a. Detector was vacuumed and a visual inspection preformed with no damage being found. <I> **** Actions Taken **** Placed ARGOS out of service, notified RP Supervision and initiated WR. <N> **** Equipment Description **** GSB PAP RCA Exit point | 02-00-HP-EQ-42782
396201 | CR | 20190628 |  | 3 | Procedure enhancement CSP-INST-H201 |  |  |  | N | NO | <D> **** Detailed Description **** CSP-INST-H201 section 7.4 incorrectly lists ARM-RIS-1 as required insturmentation per RFO 1.3.7.5. Recommend deleting this statement and listing ARM-RIS-1 as listed in PPM 13.14.11 EP equipment. <I> **** Actions Taken **** Informed CRS
396202 | CR | 20190628 | CAQ | D | Excessive run times EDR-P-18A (T7 sump pump) | N | N |  | N | YES | <D> **** Detailed Description **** Excessive run times EDR-P-18A (T7 sump pump) Possibly caused by sticking level switch EDR-LS-18 Investigate and repair as necessary <I> **** Actions Taken **** Informed MCR, RWCR operators | 02-00-EDR-P-18A
396203 | CR | 20190628 |  | 3 | TSW-V-3B not in SOP-TSW-LU position | N | N |  | N | NO | <C> CR was inadevertantly closed by CAP. Reopened for disposition. <D> **** Detailed Description **** During clearance order walkdown for upcoming maintenance, noted that TSW-V-3B (TSW supply to offline oil cooler for COND-P-2A) was closed vs. required position of open (per SOP-TSW-LU). <I> **** Actions Taken **** Notified Shift Management. Opened TSW-V-3B to place it in SOP lineup. <N> The following information was found in trying to determine the reason TSW-V-3B was out of position: 1) L-TSW-RV-117B-001 and C-TSW-RV-117B-001 were both lifted on 6/7/19, repositioning TSW-V-3B to open. 2) Partial SOP-COND-FILL was performed for COND-P-2A per the lift instructions of O-COND-P-2A/R24-002 on 6/15/19, TSW-V -3B was verified open. 3) L-TSW-PCV20-002 was lifted on 6/17/19. During restoration of TSW, some relief valves were lifting to include at least TSW-RV-117E, and possibly TSW-RV-117 A-D. Actions were taken by a group of Equipment Operators to reseat the RVs, which could have been the cause of TSW-V-3B getting repositioned (further investigation is required to determine the facts of this scenario).
396210 | CR | 20190628 |  | 3 | Procedure enhancement to SOP-RFT-START |  |  |  | N | NO | <D> **** Detailed Description **** Due to the design, TO-EX-3A(3B) control room indication is driven by switch position, not motor condition. This has resulted in thinking the exhauster was running when it was not. Add the following substep (or similar) to SOP-RFT -START steps 5.1.4.L and 5.2.4.L: VERIFY LOCALLY that TO -EX-3A(3B) is running. <I> **** Actions Taken **** Reference WR 29150114, 29136495, 29121910
396211 | CR | 20190628 |  | 3 | SCW procedure changes have led to improper system operation | N | N |  | N | NO | <D> **** Detailed Description **** AR/CR 396096 describes receiving a valid high temperature alarm on the main generator. This is a result of operating the system (leaving pump min flow valve full open) per procedure based on faulty dp indication (air saturated instrument). This CR is to document the shortcomings of our procedure as it has been changed over the years. SCW-V-523 is the min flow valve for the SCW pumps. Opening this valve lowers d/p and flow across the generator, and closing the valve raises d/p and flow. In PPM 2.5.5 Rev 18 (the original SCW procedure), SCW-V-523 started as full open when filling the system, and then was THROTTLED CLOSED to RAISE differential pressure (flow) to 28 psid. This was to ensure adequate flow to the generator stator based on a baseline flow resistance across the coils. Revision 30 of PPM 2.5.5 made a subtle change to the wording, stating to throttle SCW-V-523 to ADJUST d/p to 25-26 psid. Our current procedure, SOP-SCW-OPS, further muddies the water by stating â€œIF NECESSARYâ€¦.adjustâ€¦â€, while the valve is full open . AR/CR 271930 then took this line of thinking and incorporated it into a response to a high d/p alarm, having us adjust (open) the valve to lower d/p. It appears we lost sight of what problems high and low d/p indicate. A LOW d/p means we donâ€™t have enough flow to the generator. A HIGH d/p could mean some sort of restriction in flow across the stator coils, which also means we donâ€™t have enough flow to the generator. Neither of these circumstances should lead us to open the min flow valve and further reduce flow. Recommended action is to remove procedure steps referencing SCW-V-523 from 4.GAP.1.6-1 and 4.820.B3.3-6. Recommend setting initial SCW-V-523 position per system engineer evaluation of this AR/CR and or AR/CR 396096. <I> **** Actions Taken **** Discussed with FIN supervisor, emailed copy of this CR to system engineer.
396212 | CR | 20190628 |  | 4 | DEH turbine monitor screen 2 needs fixed | N | N |  | N | YES | <D> **** Detailed Description **** DEH turbine monitoring screen 2 differential expansion governor end arrow does not show when in the green band. Most likely a wonderware issue where the arrow remains in the background in that field. As I remember thee arrow does arrear when out of the green field. see edms for pic change will also apply to the simulator computors | 02-00-DEH-COMP-2,02-00-DEH-COMP-3,02-00-DEH-COMP-4,02-00-DEH-COMP-RO
396217 | CR | 20190629 |  | 3 | OSP-RPS-S401 no longer works as written |  |  |  | N | NO | <D> **** Detailed Description **** The procedure is currently written to compensate for broken equipment (RPS-RLY-K10F) which was fixed in R24. These steps are not conditional and prevent successful task completion. Recommend resurrecting a previous revision. Also note this proceduralized workaround is in OSP-MS-S701 but the associated steps are conditional and can be manipulated although unnecessarily error-likely.
396218 | CR | 20190629 | CAQ | D | Rod Accumulator Trouble Alarm P603-A7.6-7 for HCU 54-35 | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-5435 alarm was low pressure. <I> **** Actions Taken **** OPS2 re-pressurized per SOP-CRD-HCU | 02-00-CRD-HCU-5435
396219 | CR | 20190629 |  | 4 | Received momentary main gen condition monitor overheat alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received momentary main gen condition monitor overheat alarm. Alarm was a momentary drop and immediately returned to the normal level. Per the ARP the alarm was reset. This CR is for trending purposes. <I> **** Actions Taken **** Wrote CR Informed CRS | 02-00-TG-ID-1
396220 | CR | 20190629 |  | 4 | BS-V-39A HI LEVEL and OPEN indications always on | N | N |  | N | YES | <D> **** Detailed Description **** BS-V-39A HI LEVEL and OPEN indications are always on, and the CLOSE indication is always off. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-BS-V-39A
396221 | CR | 20190629 |  | 4 | MS-V-147 has no OPEN or CLOSE indication | N | N |  | N | YES | <D> **** Detailed Description **** MS-V-147 has no OPEN or CLOSE indication; verified the light bulbs work. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-MS-V-147
396222 | CR | 20190629 |  | 4 | BS-V-56 OPEN indication is always on. | N | N |  | N | YES | <D> **** Detailed Description **** BS-V-56 OPEN indication is always on. The valve appears to be operating normally except for the OPEN indication. The HI LEVEL indication lights up, the CLOSE indication then goes out, then the HI LEVEL indication goes out, and then the CLOSE indication comes on after a time delay. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-BS-V-56
396223 | CR | 20190629 |  | 4 | Unable to verify annunciater per WO instructions | N | Y |  | N | YES | <D> **** Detailed Description **** During performance of WO#02132300-01, annunciator on P840 -A4,9-5 was unable to be verified. The alarm has been disabled under CR#00391487 and WR#29147769 and is due to be reenabled upon completion of EC#16616. <I> **** Actions Taken **** Notified ops and supervisor. Wrote this CR. | 02-00-CW-PHITS-1
396224 | CR | 20190629 |  | 3 | ESP-BAT-W101 Inconsistent with SWP-PRO-01 |  |  |  | N | NO | <D> **** Detailed Description **** ESP-BAT-W101 precaution 4.6 is inconsistant with SWP-PRO-01 requirements for use of NA. The precaution 4.6 states that steps for partial testing may be NA'd by the craft supervisor, while SWP-PRO-01 requires the shift manager to make this determination for safety related, TS, and LCS equipment. Plant batteries fall into this category. Recommend revising ESP-BAT-W101 to be consistant with SWP -PRO-01 and evaluating other battery surveillances for compliance. <I> **** Actions Taken **** Submitted CR for revision.
396225 | CR | 20190629 |  | 4 | RRC-IMD-ASD1A/1 printing illegible | N | N |  | N | YES | <D> **** Detailed Description **** Roughly 80% of the paper printed by RRC-IMD-ASD1A/1 is coming out without ink and is therefore illegible. <I> **** Actions Taken **** Notified CRS, Wrote CR/WR | 02-00-RRC-IMD-ASD1A/1
396226 | CR | 20190629 |  | 4 | GY-CI-10A1 / GY-CI-10A2 RESISTIVITY out of spec | N | N |  | N | YES | <D> **** Detailed Description **** GY-CI-10A1 / GY-CI-10A2 RESISTIVITY found out of spec at 4.997 and 4.640 respectively <I> **** Actions Taken **** Notified CRS, Wrote CR/WR | 02-00-GY-CI-10A1,02-00-GY-CI-10A2
396227 | CR | 20190629 |  | 4 | RRC-IMD-ASD1B/2 printing illegible | N | N |  | N | YES | <D> **** Detailed Description **** Roughly 60% of the paper printed by RRC-IMD-ASD1B/2 is coming out without ink and is therefore illegible. <I> **** Actions Taken **** Wrote CR | 02-00-RRC-IMD-ASD1B/2
396228 | CR | 20190629 |  | 4 | Seal oil side-to-side D/P OOS low | N | N |  | N | YES | <D> **** Detailed Description **** Side-to-side D/P on the seal oil system has a spec range of +2 to -2" WG. Currently, one D/P gauge is reading -2.5", while the other is at -2". These numbers appear to be trending worse. Please investigate. <I> **** Actions Taken **** Notified SMgt, wrote CR. Adjusted per SOP-SO-OPS. No additional action required. <N> **** Equipment Description **** TB 441 seal oil room | 02-00-SO-PCV-217
396229 | CR | 20190629 | CAQ | D | B-DOOR-G201 requires maintenance | Y | Y |  | N | YES | <D> **** Detailed Description **** The door striker plate on B-Door-G201fell off and needs to be reattached. The striker plate is sitting on top of outside card reader. Call x2185 for more information <I> **** Actions Taken **** CR/WR Generated | 02-00-B-DOOR-G201
396230 | CR | 20190629 |  | 4 | ASD 1A/1 and 1A/2 Resistivity | N | N |  | N | YES | <D> **** Detailed Description **** ASD 1A/1 and 1A/2 resistivity are below 5 MOhm. Filters need replaced. <I> **** Actions Taken **** Initiate CR and inform CRS <N> **** Equipment Description **** ASD Building | 02-00-GY-CI-10A1,02-00-GY-CI-10A2
396238 | CR | 20190630 |  | 4 | SS-PCV-4E Degraded Control | N | N |  | N | YES | <D> **** Detailed Description **** SS-PCV-4E is inconsistently controlling seal steam pressure to LP turbine bearing 7. Pressure is being regulated at a nominal value of 1.8, but several times a day, it drops to LE 0.8, which annunciates in the MCR. See attached EDNA plot of points T062, T058, and T060. Recommend evaluating the controller for adequate operation and re-calibration. <I> **** Actions Taken **** Submitted CR for evaluation. | 02-00-SS-PCV-4E
396239 | CR | 20190630 |  | 4 | Excessive amount of time to do chemical add from CF-TK-41 | N | N |  | N | YES | <D> **** Detailed Description **** Excessive amount of time to do chemical add from CF-TK-41. currently adding 40 gallons per shift and it is taking 4 to 6 hours. Current level at the start was 611 gallons. 1.5 hours later the level was 609. verified the valves from the tank are open. the tank has a 4 inch pvc to vent. request we evaluate is the tank empty? is the line clogged there is a flushing connection. with a higher tank level during the outage we were adding a 100 gallons a shift in less than 30 minutes. I think the level is too low to be effectively drained. <I> **** Actions Taken **** wrote wr/ cr | 02-00-CF-TK-41
396240 | CR | 20190630 |  | 4 | eDNA point x332 for BPV-2 position degraded | N | N |  | N | YES | <D> **** Detailed Description **** BPV-2 (MS-V-160C) computer point x332 has deviated from the other BPV points x347, x299, and x314. It curretnly reads about -14%. The deviation can be noted on PPC/TDAS screen P7 or via eDNA. Recommend recalibration of this point. <I> **** Actions Taken **** Submitted CR for action | 02-00-MS-V-160C
396241 | CR | 20190630 |  | 4 | H2 & CO levels around main generator skirt | N | N |  | N | YES | <D> **** Detailed Description **** Ventis MX-4 monitor detected 15-25% LEL H2 and 350-500ppm CO around generator skirt, on the south side in the vicinity of TSW-V-270A. CO indication may be interference from H2. Recommend investigate and repair as necessary. | 02-00-E-GEN-1
396242 | CR | 20190630 |  | 4 | OPS4 log 508, E-TR-6/61 leak check unable to be done | N | N |  | N | YES | <D> **** Detailed Description **** OPS4 log 508,"E-TR-6/61 leak check" was unable to be done. there was no container to check or rags to inspect per the log. Investigation into the WR and Wo's was not conclusive that the leak was repaired during the outage ( I couldnt find it). Please evaluate if this leak was repaired and if so delete the log. <I> **** Actions Taken **** wr/cr, bigger team . Per ASSETSUITE notes, we fixed the oil leak under WOT 02111305-01 on 05/15/2019. <N> Oil leak on E-TR-6/61 was repaired under WO 02111305 during R24. See completion notes. | 02-00-E-TR-6/61
396243 | CR | 20190630 |  | 4 | E-TR-M2 Fan 10 overload was reset. | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-M2 Fan 10 overload (52F-10) was reset. O/L tripped last night and gave a group 4 trouble alarm, O/L was reset per ABN transformer and restarted. CR for Trending only <I> **** Actions Taken **** wrote CR for trending | 02-00-E-TR-M2
396244 | CR | 20190630 | CAQ | D | Spurious Rod accumulator alarms on rod 18-43 | Y | N |  | N | YES | <D> **** Detailed Description **** Rod 18-43 trouble alarm came in sporadically, An EO was dispatched to the HCU, nothing out of the ordinary was reported. This CR can be closed to trend. <I> **** Actions Taken **** Discussed with shift supervision | 02-00-CRD-HCU-1843
396245 | CR | 20190630 | CAQ | D | CIA-TK-4A pressure is reading too high - GT 3000 psi | Y | N |  | N | YES | <D> **** Detailed Description **** The pressure for CIA-TK-4A, as read on CIA-PRV-4A gauge, is reading too high per ppm 3.1.10, OPS 2 Tour Operating Logs. When the bottle is disconnected and the pressure is bleed off, it still reads 900 psi. Pressure could be trapped between CIA-PRV-4A and CIA-SPV-4A, or the gauge needs to be replaced. See EDMS screeen picture <I> **** Actions Taken **** informed CRS | 02-00-CIA-PRV-4A
396292 | CR | 20190701 |  | 4 | E-TR-M3 H0 bushing WO cancelled | N | N |  | N | YES | <D> **** Detailed Description **** AR-CR 393698 identified a crack on the H0 bushing for E -TR-M3 in R24. During R24 glyptol was put on the bushing crack to protect it from the environment. This was just a repair until the bushing could be replaced under the WO as part of that CR but the WR was cancelled. This CR is being generated to create a new WO for replacing the H0 bushing in the future. | 02-00-E-TR-M3
396298 | CR | 20190701 | CAQ | C | (QA) Inadequate Safety Related Coating Change Management | Y | N |  | Y | NO | <D> **** Detailed Description **** (QA) Recent changes to implement a new Safety Related Service Level 1 coating were not effectively implemented causing work delays and removal of Drywell work from the outage. Uncoated components in the Drywell do not match design and may require additional surface preparation in the drywell from any rust buildup potentially adding dose to original job estimates. (See EDMS for details) <I> **** Actions Taken **** Discussed with Coatings Engineer, Lead Painter, and Quality Management. This is a Deficiency identified during the Special Processes Audit, AU-SP-19
396300 | CR | 20190701 |  | 4 | ROA-HV-1 THROUGH WALL LEAK | N | N |  | N | YES | <D> **** Detailed Description **** During walk down of work on RX 572â€™ water was discovered on the floor south of ROA-HV-1. A simple examination of the area showed that the water was likely coming from a rusty section of wall on the HVAC unit approx. 8 ft high. Closer examination of the location revealed that there is a through wall hole in this rusted area. The rusted out section of wall was covered with red duct tape that has been painted to match the surrounding area. There is significant rust/degradation in this area (approx. 4â€ high by 6â€ wide). See pictures in EDMS <I> **** Actions Taken **** Notified PSRO and WPS safety of the leak and water on the floor. Took pictures, initiated CR and WR. . See cross-referenced AR's and WR's. It appears we have been doing a lot of band-aid fixes over the years on this H&V unit, canceling repair WR's to pad cleaning WO's, etc. It's time to really fix this. <N> **** Equipment Description **** ROA-HV-1
396302 | CR | 20190701 | CAQ | C | (QA) Finding 25 PMT WOTs Not Performed as Specified in ECs | Y | Y |  | Y | NO | <D> **** Detailed Description **** (QA) Post Modification Test (PMT) requirements for thermography on Safety-Related (SR) replacement Buckets within 25 PMT Work Order Tasks (WOTs) were not planned and/or implemented as specified by Design Engineering within 2 Engineering Changes (EC). In some instances, when flaws or insufficient information in the PMT requirements in the EC became apparent, testing requirements were omitted by planning or modified in the field, resulting in deviating from the design documents. As a result, EC-specified Thermography testing for 14 PMT WOTs was not performed by qualified Non-Destructive Examination (NDE) personnel similar to a former Quality Finding AR-CR 368190 "(QA) Thermography PMTs Performed by Unqualified Personnel" from the 2017 Special Processes audit AU-SP-17. Not implementing testing requirements specified in design documents are non-compliances with 10 CFR 50 Appendix B Criteria III â€œDesign Controlâ€ and Criteria XI â€œTest Controlâ€. This is a Finding identified during performance of the Special Processes Audit AU-SP-19. Additional details are included in the EDMS for this CR. <I> **** Actions Taken **** Discussed this issue with Design Engineering, Maintenance, and the Shift Manager. <N> Quality recommends assignment to AR-CPMPROJ
396303 | CR | 20190701 |  | 3 | R24 LL - Cold DEH fluid preventing DEH start |  |  |  | N | NO | <D> **** Detailed Description **** Find a way to keep DEH barrels GT 70 deg F for tank fill/start. Blanket htrs/immersion htrs? <I> **** Actions Taken **** Notified Outage group <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817. Action complete.
396305 | CR | 20190701 | CAQ | D | M&TE Found out of Tolerance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0063678 Proto Torque Wrench- model 6062C 40 -200in/lb found OOT & adjusted within specs. Per PPM 1.5.4 section 4.4.3 (a-c) Torque Wrench had acceptable post use verifications @ +/- .06%. No Action Required. DEF #7063A written. No Plant Impact. No Action Required.
396307 | CR | 20190701 |  | 4 | PWC-V-382 failed backflow test | N | Y |  | N | YES | <C> RT Change request: CR 396307 moved from D/Trend Repair to Severity 4 NON-CAQ. <D> **** Detailed Description **** Water is continually discharging from pressure relief valve. <I> **** Actions Taken **** Generate work request to repair backflow assembly. <N> **** Equipment Description **** Circ Water Pump House, north wall, near roll up door. | 02-00-PWC-V-382
396310 | CR | 20190701 | CAQ | C | (QA) Unqualified Worker Evaluated Thermography Results |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) One Safety-Related (SR) Work Order Task (WOT) was performed, initialed, and dated by an unqualified worker, contrary to RXM-SPS-04 â€œQualification/Certification of Personnel to Perform Thermal/Infrared (TIR) Examinationsâ€. One non-NDE person performed, initialed, and dated one "NDE" step to evaluate Thermography results in one WOT. This is a procedure use and adherence issue. Requirement: â€¢ RXM-SPS-04 rev 001-001 step 4.1 states, â€œAll personnel employed by Energy Northwest and designated Contract personnel performing TIR examinations are to be qualified and certified to the appropriate levels in accordance with the requirements of this procedure.â€ â€¢ RXM-SPS-04 steps 5.1.1, 5.1.2, and 5.1.3 requires qualification/certification to Levels I, II, or III, respectively, in order to evaluate Thermography results. Factual Basis: â€¢ WOT 02035819-04 "(PMT) CRA-42-7B5B (CRA-FN-2A2)" implements Engineering Change (EC) 12165. â€¢ QAR for WOT 02035819-04 shows step 4.5.1 has the letters "NDE" just left of the line to initial/date; however, this step to evaluate Thermography results was performed and initialed by an individual not qualified/certified as NDE staff, contrary to RXM-SPS-04. This is considered a Deficiency identified during special processes Audit, AU-SP-19. Quality recommends assignment to AR-MNTSSC <I> **** Actions Taken **** Discussed with Site Support Contractor <N> Williams Plant Services.
396312 | CR | 20190701 |  | 3 | House keeping on scaffolding under Main generator |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** There is a large bag of what appears to be garbage and several extension light and drop cords running up and around scaffolding. Whne removing a SRPD needs to be used instead of dosimeter due to the magnetic field <I> **** Actions Taken **** discussed with infield supervisor. wrote CR <N> WR written and cross referenced.
396313 | CR | 20190701 | CAQ | C | M&TE Found out of tolerance | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0063314 Dresser Sensor- model HQS-1 25â€ found OOT & adjusted within specs. EFIN will need to Evaluate the two usages. DEF #7064A written. <I> Once efin compeltes the evaluation, a new CR will be required to be written. Please make action to eFIN to generate a new CR so an IOD can be completed. <N> Re-opened to attach deficiency report per Tool Crib attendants request.
396317 | CR | 20190701 | CAQ | C | (QA) Steps Not Followed As Written in 2 SR WOT Instructions |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Two Quality Assurance Records (QARs) for Safety -Related (SR) Work Order Tasks (WOTs) each show steps not followed in WOT Instructions regarding how long the bucket needs to run loaded prior to taking thermography readings during Post Modification Testing (PMT). The design requires the bucket to be loaded for a certain period of time to allow all bucket components to reach a stable operating temperature prior to performing the PMT thermography scans. Not stopping work when unable to follow the Work Instructions as written and not resolving the issue before continuing is non-compliant with SWP-PRO -01 "Procedure and Work Instruction Use and Adherence". Requirements: â€¢ SWP-PRO-01 rev 032 step 2.6 states, "If a document cannot be used as written, then the activity is stopped and the issue is resolved before the user continues." â€¢ QAR for WOT 02035960-04 shows Task Instructions step 4.0 NOTE states, "Motor should run at least 30 minutes prior to performing Thermography." â€¢ QAR for WOT 02035960-04 shows Task Instructions step 4.5 states, "Motor should run at least 30 minutes prior to performing Thermography." â€¢ QAR for WOT 02036697-04 shows Work Order Instructions section 2.0 "Precautions and Limitations" step 2.3 states, "CCH-P-1A will be required to run a minimum of 30 minutes . . . prior to obtaining the Thermography readings." Factual Basis: â€¢ QAR for WOT 02035960-04 shows Task Instructions step 4.5 initialed and dated showing "Approximate time the load has been in service" is filled in with "20 Minutes". â€¢ QAR for WOT 02036697-04 shows Task Instructions step 4.6 initialed and dated showing "Approximate time the load has been in service" is filled in with "10 Minutes". Insight: â€¢ Out of close to 100 WOTs reviewed, the above 2 WOTs are the only ones that did not meet the specified minimum run time before Thermography. This issue identifeid as a Deficiency during performance of Special Processes Audit AU-SP-19 Quality recommends issuing to AR-MNTSSC <I> **** Actions Taken **** Discussed with Site Support Coontractor <N> Williams Plant Services
396318 | CR | 20190701 | CAQ | C | (QA) Improper Use of Pen & Ink Changes in 2 SR WOTs |  |  |  | Y | NO | <C> MRT Change request: CR 396318 moved from Severity 3 to Severity C CAQ and assigned to AR-MNTSSC <D> **** Detailed Description **** (QA) Pen and Ink changes made to two Safety-Related (SR) Work Order Tasks (WOTs) deviated from modification testing requirements specified in an Engineering Change (EC). Both changes were noncompliant with MI-1.8 "Conduct of Maintenance" due to being changes in intent or scope, and the changes resulted in non-compliances with SWP-TST-02 "Plant Modification Testing" that ensures plant modification testing is identified, documented and performed in accordance with written and approved instructions, which incorporate the requirements contained in applicable design documents. The result of the "Pen and Ink" changes is thermography was performed by non-NDE individuals for two WOTs above, and no baseline temperature data was recorded by qualified NDE staff to meet test steps in SWP-TST-02 that were specified within EC 12165. This is also noncompliant with 10 CFR 50 Appendix B Criteria XI â€œTest Controlâ€ Requirements: â€¢ 10 CFR 50 Appendix B Criterion XI â€œTest Controlâ€ states, â€œA test program shall be established to assure that all testing required to demonstrate that structures, systems, and components will perform satisfactorily in service is identified and performed in accordance with written test procedures which incorporate the requirements and acceptance limits contained in applicable design documents.â€ â€¢ SWP-TST-02 rev 002-001 step 5.3.2 NOTE states, "Once modification testing is specified within an EC or implementing WO, it should be considered mandatory and revised only with the appropriate re-reviews and re -verification." â€¢ MI-1.8 rev 069 step 18.3.6 states, "Minor editorial changes that do not change intent or scope may be made to the existing work instructions via a pen and ink change, initialed and dated." contrary to MI-1.8 step 18.3.6. step 18.3.6. â€¢ QAR for WOT 02035960-05 "(SH) New CRA-42-8B4D - Inspect Shading Coil - CR 350036" shows: o "NDE" was lined out on step 4.10.2.2, which required thermography by qualified NDE staff. Since the scope is defined by the EC, scope was changed by these "Pen and Ink" changes, contrary to MI-1.8 step 18.3.6. The "Pen and Ink" changes were also contrary to SWP-TST-02 step 5.3.2 because the WOT step prior to the change was mandatory and any change would require re-review and re-verification. Insights: â€¢ While the decisions by the planner and/or the craft supervisor to make field changes to the WOTs may have made sense, these decisions resulted in bypassing the proper steps to obtain concurrence from Design Engineering to have the ECs revised to align with the desired actions from the ACE resolution to use "Information Only Thermography" for SR replacement buckets. This issue identifeid as a Deficiency during performance of Special Processes Audit AU-SP-19 Quality recommends assigning to AR-MNTSSC <I> **** Actions Taken **** Discussed with site support contractor <N> Williams Plant Services
396319 | CR | 20190701 | CAQ | C | (QA) Improper Use of N/A on Steps in 6 SR WOTs |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Quality Assurance Records (QARs) for six Safety -Related (SR) Work Order Tasks (WOTs) show, the improper use of Not Applicable (N/A) nine times, contrary to station procedures. The actual consequences are WOTs not meeting all requirements in associated Engineering Changes (ECs), including requirements for testing specified within the ECs. These nine examples are noncompliant with SWP-TST-02 "Plant Modification Testing" that ensures plant modification testing is identified, documented and performed in accordance with written and approved instructions, which incorporate the requirements contained in applicable design documents. These are also noncompliant with 10 CFR 50 Appendix B Criteria XI â€œTest Controlâ€. This issue identified as a Deficiency during performance of Special Processes Audit AU-SP-19 Quality recommends assigning to AR-MNTSSC Additional Information in EDMS. <I> **** Actions Taken **** Discussed with site support contractor <N> Williams Plant Services
396320 | CR | 20190701 |  | 3 | R24LL - NICMs need to be scoped into future outages |  |  |  | N | NO | <D> **** Detailed Description **** At present, TMODs are scoped into outages for removal with a goal of leaving an outage with zero temp mods installed (or as close as possible). NICMs are not treated this way and as such, do not get hte attention that hey need to ensure that the equipment defficiency is corrected during an outage. Suggest adding a scoping goal to R25 and future outages to eliminate some , or all, of the NICMs installed in the plant. This speaks to equipment reliability, as the NICM is installed to compensate for a degredation in the plant that is likely not being addressed if the NICM is not being removed. In short, NICMs need to be treated more like TMODs and the equipment needs to be fixed. <I> **** Actions Taken **** LL generated. Suggest sending to OTM for inclusion into outage goals. <N> er agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
396321 | CR | 20190701 | CAQ | B | (QA) ARMA - Unsat Procedure Use and Adherence Behaviors |  |  |  | Y | NO | <C> MRT Change request: CR 396321 moved from Severity C to Severity B CAQ (Medium Risk) assigned to AR-MNTSSC RISK: Medium. CAUSE: Unknown. Investigation Template Required. <D> **** Detailed Description **** (QA) Multiple examples of unsatisfactory Procedure Use and Adherence (PU&A) behaviors by Supplemental Planners, Craft, and Supervisors were identified during a review of completed Safety Related (SR) bucket replacement Work Order Tasks (WOTs). Behavioral issues included not following WOT instructions as written, improper use of Not Applicable (N/A), improper use of "Pen and Ink" changes, and unqualified workers performing/initialing WOT steps. These behaviors resulted in multiple WOTs not meeting all testing requirements in related Engineering Changes (ECs), including requirements for testing specified within the ECs. These examples are noncompliant with SWP-TST-02 "Plant Modification Testing" and 10 CFR 50 Appendix B Criteria XI â€œTest Controlâ€. Requirements: â€¢ 10 CFR 50 Appendix B Criterion XI â€œTest Controlâ€ states, â€œA test program shall be established to assure that all testing required to demonstrate that structures, systems, and components will perform satisfactorily in service is identified and performed in accordance with written test procedures which incorporate the requirements and acceptance limits contained in applicable design documents.â€ â€¢ SWP-TST-02 rev 032 NOTE after step 5.3.2 states, "Once modification testing is specified within an EC or implementing WO, it should be considered mandatory and revised only with the appropriate re-reviews and re -verification." Factual Basis: The following conditions were identified during the Special Processes Audit AU-SP-19: â€¢ (QA) Steps Not Following As Written in 2 SR WOT Instructions (AR-CR 396319) â€¢ (QA) Improper Use of N/A on Steps within 6 SR WOTs (AR-CR 396318) â€¢ (QA) Improper Use of Pen & Ink Changes in 2 SR WOTs (AR -CR 396317) â€¢ (QA) Unqualified Worker Evaluated Thermography Results (AR-CR 396310) Insights: â€¢ While the decisions by the planner and/or the craft supervisor to make field changes to the WOTs may have made sense, these decisions resulted in bypassing the proper steps to obtain alignment with Design Engineering to have the ECs revised to align with the desired actions from the ACE resolution to use "Information Only Thermography" for SR replacement buckets. â€¢ Personnel did not demonstrate the right threshold for expanding the team and following established change processes when issues with the ECs were identified that challenged planning and execution of the PMTs for SR bucket replacements. â€¢ ARMA AR-CR 388037 identified a recurring theme involving gaps in PU&A. This issue identified as an Area Requiring Management Attention (ARMA) during performance of Special Processes Audit AU-SP-19 Quality recommends assigning to AR-MNTSSC <I> **** Actions Taken **** Discussed issue(s) with site support contractor <N> Williams Plant Services
396322 | CR | 20190701 | CAQ | C | (QA) Quality-Affecting Information In Manuals |  |  |  | Y | NO | <C> MRT Change request: CR 396322 moved from Severity 3 to Severity C CAQ and assigned to AR-CPROG <D> **** Detailed Description **** (QA) The Maintenance Weld Program Manuals contain Quality -Affecting information for Special Processes and regulatory requirements that should be contained in plant procedures. At Columbia, manuals are controlled by GBP-PRO-03, Preparation, Review and Approval of Corporate Procedures, Department Instructions and Manuals, which is not designed or intended to meet ANSI N18.7-1976 â€œAdministrative Controls and Quality Assurance for the Operational Phase of Nuclear Power Plantsâ€ requirements. The inclusion of Quality-Affecting information manuals results in a situation where a revision can take place without receiving the reviews required by ANSI N18.7 or consideration for reduction in commitment, effect on regulatory requirements, 10 CFR 50.59 screening, etc Additional information in EDMS This issue identified as a deficiency during performance of Special Processes Audit AU-SP-19 Quality recommends assigning to Engineering <I> **** Actions Taken **** Discussed with Engineering
396323 | CR | 20190701 | CAQ | D | Generator for TEC failed to start | N | Y |  | N | NO | <D> **** Detailed Description **** While performing monthly PM WO 02136811 on the TEC emergency generator, the engine for the generator failed to start. <I> **** Actions Taken **** Stopped work, notified supervisor, department manager, IS manager and EP. Created WR 29150262 for Facilities to troubleshoot.
396324 | CR | 20190701 | CAQ | C | Incorrect labeling on EWD |  |  |  | N | NO | <D> **** Detailed Description **** On the following EWDs the Elementary portions of the drawing has incorrect lable for the open and close indication. The labels are reversed. This is a document only issue. See E/8 of EWD-56E-007, 008, 009, 010, 011,012. <I> **** Actions Taken **** Notified MOV Engineer, Drafting
396325 | CR | 20190701 |  | 4 | DW-V-100/62 has slow leak | N | N |  | N | YES | <D> **** Detailed Description **** DW-V-100/62 has slow leak and is slowly migrating out of the contaminated area into a clean area. It is leaking 4-5 drops per minute approxiatmately. <I> **** Actions Taken **** Contacted HP and wrote this CR | 02-00-DW-V-100/62
396327 | CR | 20190701 |  | 3 | PWC-CP-102 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** PWC-CP-102, the pump controller for PWC-P-102, needs to be on a regular maintenance (PM) schedule. The controller mechanicals are very balky to operate because lubrication and adjustment has not been done. Also, the controller internals are very dusty. Please repair/adjust/lubricate this controller and place it on a regular PM schedule. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** #2 Wellhouse building. AR SMS written and cross referenced. Recommend keeping PWC equipment as run to maintenance. | 02-00-PWC-CP-102
396328 | CR | 20190701 | CAQ | D | M&TE Fould Out of Tolerance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #44850 Ametek Torque Screwdriver- model TC5000-4 found OOT in the Counter Clockwise Range. Used in the Clockwise Range only. Rejected- Damage occurred when tightening the chuck for counter-clockwise test and as found data couldnâ€™t be taken. Obsolete and will be replaced. No Plant Impact. No Action Required. DEF #7065A written.
396332 | CR | 20190701 | CAQ | C | Foreign Material CRâ€™s did not follow process of PPM 10.1.13 | Y | Y |  | N | YES | <D> **** Detailed Description **** During R-24, RCIC-V-111 and RCIC-V-112 were identified to have a seat ring retaining screws missing internally to the valves under CRâ€™s 394184 and 394185. In both instances the CRâ€™s do not specifically state that the missing screws were internal to the valves. Both CRâ€™s were screened by CRG to the Mechanical shop. An assignment was created for the mechanical shop to document the efforts taken to locate the screws. Once the mechanical shop documented their actions, the Mech shop closed the assignments and the CRâ€™s. Another assignment should have been generated for Engineering to evaluate the FM being left within a system per PPM 10.1.13 step 7.9 (Page 28). This did not occur. The FME Coordinator identified that the foreign material being within the RCIC system has not been resolved while reviewing FME related CRâ€™s to ensure that the process laid out within PPM 10.1.13 was followed Both of these events were not considered reactor start up constraints the assumption is that because WO# 02111380, and WO# 0211379 were going to fix both valves prior to start up. This assumption does not address the foreign material left within the RCIC system. Within both CRâ€™s (DNC attribute field /A015 screen) OPS classified the equipment as degraded/ non-conforming (DNC) and the issues were being tracked under LCO Sheet T19-R24 -RCIC-SYS-001. The FME cord. reviewed the LCO sheet and noted that it does not discuss foreign material within the RCIC System, only that the valves were degraded and non -conforming, but would be fixed under the associated WOâ€™s. From what the FME coordinator can find, at no time was the foreign material addressed within the RCIC system from an operability perspective. Due to the location of RCIC-V-111 and 112 being on the exhaust leg from the RCIC Steam turbine, the most likely place the foreign material ended up is within the suppression pool. <I> **** Actions Taken **** Validated that the wet well cleanliness dive did not remove the screws from the wet well by reviewing pictures taken of debris removed during the dive. (Pictures located in the EDMS of AR# 395175). Discussed with Maintenance programs leadership, Mechanical shop manager, mechanical shop supervisor, Engineering Supervisor. Discussed with the shift manager. | 02-00-RCIC-V-111,02-00-RCIC-V-112
396334 | CR | 20190701 |  | 3 | E-CB-M2/52P2 will not reset. | N | N |  | N | YES | <D> **** Detailed Description **** While trying to reset E-TR-M2 cooler group 2 pump 2 circuit breaker per WR 29150094, E-CB-M2/52P2 would not rotate counter-clockwise to the reset/off position. The knob will only move between the tripped free position and the ON position. It will not move to the reset / off position. This device appears to have failed and needs replacement. See picture in attributes screen of the work request. <I> **** Actions Taken **** Informed supervisor and wrote this AR/WR. <N> **** Equipment Description **** Outside, E-TR-M2 control cabinet. | 02-00-E-CB-M2/52P2
396335 | CR | 20190701 | CAQ | C | SW-M-P/1B shows elevated water level in upper reservoir oil | Y | Y |  | N | YES | <D> **** Detailed Description **** The last oil sample from the upper oil reservoir of SW-M -P/2B shows 2137 ppm of water. This is considered to be an elevated water level for this type of bearing (spherical roller). Motor bearing temperatures, motor winding temperatures, and vibration data were reviewed by engineering and are normal with no degrading trends. Similar condition was reported in AR 323861, 6/5/2015. POD evaluated condition and provided limit for water content in lubricant. Based on the SW-M-P/1B run time history, bearing loads, and lubricant condition, the remaining bearing life at the current water level of 2137 ppm would be approximately 6625 hours. The previous evaluation under AR 323861 for the similar condition provided a maximum water level limit in the upper bearing reservoir 30,000 ppm which equates to ~3.3% of remaining bearing life. If water levels were to reach 30,000 ppm the expected remaining life of the bearings would be ~1300 hours which is still above the 720 hours required for SW mission time. Additional oil samples are needed to approximate water intrusion rate in oil. <I> **** Actions Taken **** Discussed with Shift Manager, System Engineer, and Engineering Supervision. <N> EPN in CR description should be SW-M-P/1B, not 2B. | 02-00-SW-M-P/1B
396337 | CR | 20190701 |  | 4 | ROA-HV-1 Holes Torn in ROA-AD-5 Flex Boot | N | N |  | N | YES | <D> **** Detailed Description **** During a follow-up examination of ROA-HV-1 triggered by CR 396300, ROA-HV-1 Through Wall Leak, the system engineer discovered that the flex boot that connects ROA-HV-1 to ROA-AD-5 has holes in it at the four corners. These holes are estimated to be in total, less than 4 square inches. The holes will allow air into the ROA-HV-1 unit just upstream of the ROA-FN-1A and 1B. This will have no discernable impact on reactor building pressure or temperatures. This is not a part of the secondary containment boundary and is located downstream or "inboard" of the ROA isolation valves. Photos attached in EDMS. <I> **** Actions Taken **** Notified my supervisor then called the shift manager to discuss the impact to the plant. | 02-00-ROA-AD-5,02-00-ROA-HV-1
396338 | CR | 20190701 |  | 4 | ROA-HV-1 Corroded Patch About to Fail | N | N |  | N | YES | <D> **** Detailed Description **** During a follow-up examination of ROA-HV-1 triggered by CR 396300, ROA-HV-1 Through Wall Leak, the system engineer discovered that another rusty area on the north side of the unit is close to disintegrating due to corrosion. That area is estimated to be 2 inches square. The exterior appears to be caving in towards inside of the unit. There is no breach in the skin of the air handler unit at this time but the area should be repaired at the next available opportunity. This is not a part of the secondary containment boundary and is located downstream or "inboard" of the ROA isolation valves. Photos attached in EDMS. <I> **** Actions Taken **** Notified my supervisor then called the shift manager to discuss the impact to the plant. | 02-00-ROA-HV-1
396339 | CR | 20190701 |  | 4 | RFT-VSC-B1 heatsink temperature elevated | N | N |  | N | YES | <D> **** Detailed Description **** Since 6/16/2019 RFT-VSC-B1 heatsink temperatures, as determined from computer point RB31026, have been higher than normal and higher than temperatures of the other three RFT electric actuator positioners. Heatsink temperatures have come down since RFW-P-1B was placed in service but are still 25-30degF hotter than normal/others (ref. eDNA plot in EDMS). Note, the unit has heatsink warning and fault setpoints of 176degF and 194degF respectively, for comparison the highest temperature observed was ~164degF. RFT-VSC-B1 is one of two redundant governor actuator positioners for RFT B (RFT-VSC-B2 being the other). There is no current impact on RFT B operation due to the elevated heatsink temperature. | 02-00-RFT-VSC-B1
396340 | CR | 20190701 | CAQ | D | CIA-PRV-3A leaking | Y | N |  | N | YES | <D> **** Detailed Description **** A Leak was found on CIA-PRV-3A. A previous CR (395993) was written for this regulator, however it is leaking from a different location. Video was taken of the leak and attached to CR. <I> **** Actions Taken **** CR/WR generated. Supervision notified. | 02-00-CIA-PRV-3A
396341 | CR | 20190701 |  | 3 | Evaluate COND-P-1B for excessive leakoff | N | N |  | N | YES | <D> **** Detailed Description **** Evaluate COND-P-1B for excessive leakoff Pump seal leakoff is much more than it was last cycle, approx 3-5 gpm <I> **** Actions Taken **** Informed MCR Leakoff normally flows to T4, little to no plant impact | 02-00-COND-P-1B
396364 | CR | 20190702 |  | 4 | MOT-MO-1-1 scope & basis was not updated |  |  |  | N | NO | <D> **** Detailed Description **** The MOT-MO-1-1 scope & basis was not updated to support he LCS changes. This does not impact any PM's dates or field work. This CR is administrative only. <N> MOT-MO-1-1 Rev 24 incorporated the changes identified in AR 396364.
396367 | CR | 20190702 |  | 3 | (QA) Typo found in Basis for Certification of Level II PT Ev |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) A Quality Auditor identified a typographical error in the Basis for Certification for one Level II Penetrant Testing (PT) Certification Evaluation record form that incorrectly identified the candidate had met all of the requirements for Magnetic Particle Testing (MT) certification rather than PT. Factual Basis: â€¢ RXM-SPS-01, Qualification and Certification of Personnel to Perform Nondestructive Examination, requires the NDE Level III verify that the information and documentation of previous training and experience used as the basis for certification of Level I and II candidates is valid. The method by which the verification was accomplished is required to be documented in the candidateâ€™s certification records. Insights: â€¢ The Principal Level III Examiner had completed a certification review form for the individual two days prior and had used the MT form as a background for the PT certification. The MT should have been changed to PT to reflect the correct information but was overlooked. Upon notification of the oversight, the typo was manually corrected via appropriate means. . This issue is condsidered a Deficiency identified in the performance of the Special Processes Audit, AU-SP-19 Quality recommends assigning to AR-RXMAINT <I> Discussed with the corresponding department.
396368 | CR | 20190702 |  | 3 | (QA) Eye examination was expired for vendor NDE inspector |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) An annual eye examination for a vendor NDE technician had expired April 20, 2019. The expired examination was not identified during initial review of NDE personnel certifications prior to R24. The examiner did not perform or sign for any inspections during R24. Factual Basis: â€¢ SPS-10-2, Utility Oversight of Examination Vendors, Rev 004/002, requires the NDE Level III verify that the examiner has a current eye examination as required by applicable codes and procedures. Insights: â€¢ Upon identification by Quality, a current eye examination by vendor Level III personnel was provided dated 4/9/2019 (expiration 4/9/2020). The examination was reviewed and approved by the CGS NDE Level III and ANII. â€¢ No inspections were performed by the inspector in question; no inspections were impacted by the oversight. . This issue is condsidered a Deficiency identified in the performance of the Special Processes Audit, AU-SP-19 Quality recommends assigning to AR-RXMAINT <I> Discussed with the corresponding department.
396369 | CR | 20190702 |  | 3 | (QA) Retired MI-3.4 Still In Station Procedures |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) PPM 10.2.14, Maintenance Coatings Program, and SWP -SPS-03, Service Level 1 Protective Coatings Program were not revised to eliminate retired MI-3.4. Factual Basis: â€¢ SWP-PRO-02, section 5.4.7.c.13 states â€œENSURE impacts included a review of all other affected procedures for applicable changes by using Attachment 8.4, Procedure Implementation Impact Determination.â€ â€¢ MI-3.4, Coatings Daily Work Practices, Revision 19, was taken to history on 7/12/17. The Procedure Revision Form (23761A) section for other procedure, instruction or form revisions to be issued in parallel is blank. â€¢ PPM 10.2.14, Revision 30, step 4.3 still prescribes use of MI-3.4 â€¢ SWP-SPS-03, Service Level 1 Protective Coatings Program, Rev 5, section 1.0 purpose and References 6.15 still lists MI-3.4 . This issue is condsidered a Deficiency identified in the performance of the Special Processes Audit, AU-SP-19 Quality recommends assigning to Maintenance <I> Discussed with the corresponding department.
396371 | CR | 20190702 |  | 3 | PPM 12.14.11 requires a procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** PPM 12.14.11 requires a procedure enhancement. In section 7.1, the sixth step is listed as 7.1.1, but should be 7.1.6. <I> **** Actions Taken **** Initiated this condition report.
396372 | CR | 20190702 |  | 4 | XR 3 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** XR 3 needs maintenance. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Unit taken out of service, security notification made, CR/WR generated | 02-00-SEC-XR-3
396379 | CR | 20190702 |  | 3 | Cool Tower outage concrete work |  |  |  | N | NO | <D> **** Detailed Description **** Set up seperate tasks for the cooling tower outside concrete repair work from the inside concrete repair work. The outside repairs can be done without being on a clearance and will allow the work to start prior to the CW cleanance being hung. <N> **** Equipment Description **** CW-CT-1A CW-CT-1B CW-CT-1C CW-CT-2A CW-CT-2B CW-CT-2C Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817
396380 | CR | 20190702 |  | 3 | R24LL Main Condenser shell side engineering inspection |  |  |  | N | NO | <D> **** Detailed Description **** Break up the engineering inspection tasks of the shell side of the main condenser into areas to match support activities. Tasks should be seperated to include upper shell side inspection, side of tube inspection, false floor inspection and hot well inspection <N> **** Equipment Description **** COND-HX-9 Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817
396382 | CR | 20190702 |  | 3 | R24LL Engineering Inspection of Water Side of Main Condenser |  |  |  | N | NO | <D> **** Detailed Description **** Break up the engineering inspection of the Main Condenser water side so the as found conditions and FME close out are not in the same task. As found inspection should be a seperate task from the FME close out inspection. <N> **** Equipment Description **** COND-HX-9 Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817
396385 | CR | 20190702 |  | 4 | CAS-C-1B has low oil | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1B oil level is below the minimum spec of 1/8" in the sightglass. Please add oil. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 441 E | 02-00-CAS-C-1B
396386 | CR | 20190702 |  | 4 | R24LL Machining of the RFW-HX-6B manway |  |  |  | N | NO | <D> **** Detailed Description **** Machining off the internal manway of the RFW-HX-6B was not able to be perfromed because we did not have the right tooling or qualified mechanics to perform the work. Mechanical Maintenance agree to perform the work for R24, however when the time came to perform the work, they did not have the tooling or qualified mechanic. The PM for RFW-HX-6B was differed. <N> **** Equipment Description **** RFW-HX-6B
396387 | CR | 20190702 |  | 4 | HWC-XI-501 has been broken for years | N | N |  | N | YES | <D> **** Detailed Description **** HWC-XI-501, the trend display on the P500 panel, has been broken since 2015 (see AR for this unit). Please either repair/replace this unit, or remove the readings for it in the Ops 3 logs. NOTE: This display is referenced in SOP -HWC-START. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 471 W | 02-00-HWC-XI-501
396388 | CR | 20190702 |  | 4 | OG-PI-1A and OG-PI-1B are not functional. | N | N |  | N | YES | <D> **** Detailed Description **** OG-PI-1A and OG-PI-1B are not functional, and have not been for years. Please either repair/replace these indicators, or remove them from the Ops 3 logs. <I> **** Actions Taken **** Notified SMgt, wrote CR. . If AR-ASSGN 00260253-04 determines no sensing line change will be made for these instruments, then remove and cap the connections for them. <N> **** Equipment Description **** TB 441W at off gas panel. | 02-00-OG-PI-1A,02-00-OG-PI-1B
396389 | CR | 20190702 |  | 3 | R24LL Engineering inspection of Main Condenser piping |  |  |  | N | NO | <D> **** Detailed Description **** Task need to created and scheduled for engineering to inspect the bleed steam, extraction steam, and desuperheated steam piping of the main condenser. <N> **** Equipment Description **** COND-HX-9 Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817
396392 | CR | 20190702 |  | 3 | R24LL Main Condenser Housekeeping |  |  |  | N | NO | <D> **** Detailed Description **** Add tasks to WO's to allow for housekeeping inspections periodically in the main condenser shell side to keep FME from building up. R24 was like R23 where there was excessive material left in the condenser until the close out inspection <N> **** Equipment Description **** COND-HX-9 Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817
396393 | CR | 20190702 | CAQ | C | (QA) PPM 10.1.26 Not Aligned With SWP-CM-02 | N | N |  | Y | NO | <C> MRT Change request: CR 396393 Severity moved from 3 to Severity C CAQ. <D> (QA) PPM 10.1.26 "Temporary Leak Sealing" does not contain all the specified requirements for a procedure governing a Procedurally Controlled Temporary Change (PCTC), contrary to SWP-CM-02 "Temporary Configuration Changes" (TCCs). The detailed instructions in PPM 10.1.26 do not include logging/tracking, tagging in field, notifications and authorization/signoff for install and removal, time frame the temporary repair may remain installed, and actions required to extend the time frame. This is a procedure alignment issue that could hinder the ability to track and restore temporary configuration changes. . This issue is condsidered a Deficiency identified in the performance of the Special Processes Audit, AU-SP-19 Quality recommends assigning to Maintenance See EDMS for details <I> Discussed with the corresponding department. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
396394 | CR | 20190702 | CAQ | C | (QA) Missing WO 02088287-01 Package Documentation |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Documentation of completed PPM 10.1.25, Chemical Cleaning and Chemical Decontamination of Plant Systems and Components, attachment 8.1, Chemical Cleaning Data Sheet and the accompanying MSDS for chemicals used during the performance of WO 02088287-01, Perform Chemical Decon of RHR Loop A, were not placed in the Work Order Package. These documents were found but were not part of the WO Package as required by PPM 10.1.25. Requirements: â€¢ Section 7.0 of PPM 10.1.25 states, â€œPlace Attachment 8.1 and any related documents e.g., reports, evaluations, or test results in the Work Order Package,â€ and to, Maintain the Work Order Package in the permanent plant file in accordance with the appropriate Plant Records Procedure(s) a requirement of ANSI N45.02.03 Records - Copies Of Approved Procedures, Reports Shall Be Prepared & Placed With Other Project Records. â€¢ Step 6.5.4 of PPM 10.1.25, Chemical Cleaning and Chemical Decontamination of Plant Systems and Components states, â€œObtain Chemical Permits, per SWP-CHE-05, for the chemicals to be used and attach an MSDS for those chemicals to Attachment 8.1.â€ This issue is condsidered a Deficiency identified in the performance of the Special Processes Audit, AU-SP-19 Quality recommends assigning to Maintenance <I> Discussed with the corresponding department.
396395 | CR | 20190702 |  | 3 | (QA) Incorrect Reference Stated in PPM 10.1.25 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Two references in PPM 10.1.25 {R-3561} and {R-3571} were incorrectly changed and do not align with the correct source documents. Changing of references could result in Columbia Generation Station (CGS) losing track of regulatory requirements. Factual Basis: â€¢ Major Revision 6 of PPM 10.1.25, Chemical Cleaning and Chemical Decontamination of Plant Systems and Components, correctly identified in the references ANSI N-45.2.3-1973 as the standard for cleanliness requirements that CGS is committed to. â€¢ In Revision 7 of PPM 10.1.25 reference to ANSI N-45.2.3 - 1973 {R-3561}, {R-3571} was changed to ASME NQA-1-2012 and an additional reference to ANSI 3.2-2012 was added; neither of these are standards that CGS is committed to. â€¢ {R-3561} refers to ANSI N45.02.03 section 03.02.01 â€œCleanness - Work Areas Shall Be Kept Sufficiently Clean & Orderly That Construction Activity Can Proceed In An Efficient Manner That Will Produce & Maintain Quality. â€¢ {R-3571} refers to ANSI N45.02.03 section 04 â€œRecords - Copies of Approved Procedures, Reports Shall Be Prepared & Placed with Other Project Records.â€ Insights: Revision 7 changes were meant to add references. The new references added ASME NQA-1-2012 Quality Assurance Requirements for Nuclear Facility Applications and ANSI 3.2-2012 Quality Assurance Program neither of which are requirements for CGS. These actions were inappropriate and additionally, the old reference to ANSI N-45.2.3 â€“ 1973 should not have been removed. . This issue is condsidered a Deficiency identified in the performance of the Special Processes Audit, AU-SP-19 Quality recommends assigning to Maintenance <I> Discussed with the corresponding department.
396396 | CR | 20190702 |  | 4 | Door Knob to TB 501 West Labyrinth Free Spins |  |  |  | N | NO | <D> **** Detailed Description **** The door knob for the LHRA door on the TB 501 West free spins in the counter-clockwise direction. The latch engages properly and the lock functions as designed, but a faulty door knob may lead to confusion over whether the door set is working as intended. The door is currently locked shut as required by PPM 11.2.7.3 <I> **** Actions Taken **** Supervision was notified of the issue - verified that the latch was fully engaged and the lock was functioning.
396397 | CR | 20190702 | CAQ | C | (QA) PMT WOT for SR Bucket Not in Records |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Post Maintenance Testing (PMT) Work Order Task (WOT) 02036312-04 for Safety-Related (SR) replacement bucket testing is not in Records, and there is no Condition Report (CR) in the system, contrary to MI-3.6.4 "Work Package Closure". There is no actual consequence because the separate completed WOT documents can be viewed within eWP. Requirement: MI-3.6.4 rev 022 step 3.2.1e states, "Administrative personnel generate CRs for all work packages that have not been received for processing within 60 days from status FINISH for job types that are required to be sent to permanent file." Factual Basis: â€¢ Asset Suite shows this PMT WOT with the dates and status shown below: o Finished status on 6/26/18 o Complete status on 9/11/18 o Closed status on 1/12/19 â€¢ eWP shows this PMT WOT with the dates and status shown below: o WO Completion on 6/1/18 o WO Completion on 6/26/18 â€¢ eWP also shows this WOT is at "eWP step: Supervisor Review Complete" Insights: â€¢ WOT 02036312-04 Task Completion screen Comments dated 6/26/18 state, "The Task was statused in Asset Suite causing the DataGlance package to be "STUCK", Syncing with AS. This issue has already been reported in CR00379169.â€ â€¢ This may be an issue similar to AR-CR 379169 "eWP Asset Suite and DataGlance Status Mismatched tasks"; however, WOT 02036312-04 is not listed in the spreadsheet of affected WOTs in the EDMS for AR-CR 379169, for which the last Corrective Action completed on 6/14/18 (before WOT 02036312-04 was taken to Finished status). Every WOT in the spreadsheet in the EDMS has been lined through suggesting resolution was complete for those WOTs. â€¢ The eWP Support group has been notified, and is working on correcting this issue. . This issue is condsidered a Deficiency identified in the performance of the Special Processes Audit, AU-SP-19 Quality recommends assigning to Maintenance <I> Discussed with the corresponding department. <N> Work performed by In-house Electricians.
396398 | CR | 20190702 |  | 3 | (QA) Incorrect section referenced in PPM 1.3.76 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) the following steps incorrectly refer to non-existent Section 1.1 of PPM 1.3.76, â€œIntegrated Risk Managementâ€ revision 055-000: â€¢ Steps 5.2, 5.3, and 5.4 first notes refers to Section 1.1 â€¢ Step 5.4 third note refers to Section 1.1 â€¢ Step 5.4.4 b and step 5.5.3 d both refer to Section 1.1 twice Incorrect referenced could lead to errors in procedure performance. Insights: The same steps in the previous revision of PPM 1.3.76 (054-001) referred the user to Section 5.3 Step 5.4.4 b in the previous revision of PPM 1.3.76 (054 -001) also referred the user to Section 5.1 for determining if a challenge meeting is required. . This issue is condsidered a Deficiency identified in the performance of the Special Processes Audit, AU-SP-19 Quality recommends assigning to Operations
396399 | CR | 20190702 |  | 4 | need scaffolding built to reach fixture ELP-7FC. | N | N |  | N | YES | <D> **** Detailed Description **** while performing WO#02131881-01 Quarterly HID lighting test, light ELP-7FC (fixture 5) in the cable spreading room (radwast 487") was burnt out, need scaffolding built to reach it. <I> **** Actions Taken **** wrote CR and noted it in comments section of work order. <N> **** Equipment Description **** Radwaste 487' (cable spreader room) | 02-00-E-ELP-7FC
396400 | CR | 20190702 | CAQ | D | RCIC-PI-64 | Y | N |  | N | YES | <D> **** Detailed Description **** RCIC-PI-64 was installed to measure the pressure in the abandoned steam condensing mode piping as a means of detecting potential raduikttuc hydrogen buildup. Normally this gauge reads 0 psig. Today (the first measurement taken after the outage), the gauge was reading 4.9 psig. This pressure increase is most likely the result of other activity as it seems too sudden to be the likely result of radiolytic hydrogen formation. As a precaution, however, this should be sampled and tested for hydrogen and then vented to return the pressure in the piping to zero to allow for future monitoring . A valve (RCOC-V-905) and port exists next to the pressure gauge to allow for sampling. See the drawing in the EDMS folder. NOTE: RCIC-PI-64 is located at the top of the stairs in the northwest corner of RX 572â€™. <I> **** Actions Taken **** Informed the shift manager. | 02-00-RCIC-PI-64
396401 | CR | 20190702 |  | 3 | Procedure enhancement for PPM 12.14.12 |  |  |  | N | NO | <D> **** Detailed Description **** PPM 12.14.12 Section 6.3 has a formatting error which makes necessary restoration steps conditional. As written substeps under step 6.3.6.f are only performed if mechanical maintenance support is required, however substeps 6.3.6.f.3 through 6.3.6f.7 are necessary to restore the component before removing clearance tags and admitting system pressure in the following steps. Recommend reformatting substeps 3 through 7 to read as G through K to remove error trap. <I> **** Actions Taken **** Initiated CR
396402 | CR | 20190702 | CAQ | D | RRC-P-1B Seal Purge Flow High Out of Range | Y | N |  | N | YES | <D> **** Detailed Description **** The RRC-P-1B seal purge flow rate on RRC-FIS-39B is reading 5.5 gpm. The normal range for the purge flow is 3 to 5 gpm. Although the pump manufacturer has stated that the purge flow rate can run this high for extended periods, they recommend that it be maintained in the 3 to 5 gpm range. RRC-FC-2B should be adjusted to bring the purge flow into this recommended range. <I> **** Actions Taken **** Discussed the issue with the shift manager. | 02-00-RRC-FC-2B
396403 | CR | 20190702 |  | 4 | RCC Flow Mismatch | N | N |  | N | YES | <D> **** Detailed Description **** There is a mismatch between the RCC flow into containment (RCC-FI-4) and the flow out of containment (RC-FI-28) in the Main Control Room. RCC-FI-4 is reading around 2,500 gpm and RCC-FI-28 is reading around 2750 gpm. Based on reading taken last cycle, RCC-FI-4 should be reading around 50 to 100 gpm higher than RCC-FI-28. This appears to be an indication only issue that should be investigated and corrected. <I> **** Actions Taken **** Discussed the issue with the shift manager. | 02-00-RCC-FI-4
396404 | CR | 20190702 | CAQ | C | Received 4.814.J1 drop 3-1 Containment noble gas rad alert | Y | N |  | N | YES | <D> **** Detailed Description **** CMS-RIS-12A channel 1 had 2 short duration spikes above the alert value and now appears to have stabilized at approximately 1.0E-05 micro Curries/CC. Normally this instrument reads 8E-07 to 1.5E-6. CMS-RIS-12A channel 2 remains unchanged and steady with a few random spikes non concurrent with channel 1 spikes. CMS-SR-21 for CMS-RIS -12B is currently isolated and shutdown for investigation of oxygen in-leakage to the drywell. There are no indications of a leak in the drywell. Picture of trace in EDMS. <I> **** Actions Taken **** Followed AARP,Informed CRS and SM. | 02-00-CMS-RIS-12A
396405 | CR | 20190702 | CAQ | C | M&TE found out of tolerance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0066287 Baker Computer EXP4000 found OOT and needs adjustment. EFIN to Evaluate the 3 usages. DEF #7066A written. <I> Once EFIN completes their evaluation, a new CR will be required to be written. Assign action to EFIN to generate a new CR so an IOD can be completed. <N> RE-opened to attach Deficiency report per Tool Crib Attendants request.
396406 | CR | 20190702 |  | 3 | E937-3 has an incorrect power supply listed |  |  |  | N | NO | <D> **** Detailed Description **** E937-3 say that HT-HTP-FP8 CKT 8 powers BFP8-41. HT-HTP -FP8 CKT A powers BFP8-41. See 322-00,16,2, 322-00,34,6, E937-6 and E937-3.
396410 | CR | 20190702 | CAQ | C | LEVEL 1 FILING ERROR IN CONTROL ROOM |  |  |  | N | NO | <C> MRT Change request: CR 396410 moved from D/Trend to Severity C CAQ and assigned to ITMGMT (Conduct Extent of Condition). <D> **** Detailed Description **** DOCUMENT CONTROL PERSONNEL MISFILED A LEVEL 1 PROCEDURE WITHIN THE CONTROL ROOM. ERROR WAS CAUGHT DURING PERFORMANCE OF A WEEKLY AUDIT. <I> **** Actions Taken **** CORRECT LEVEL 1 PROCEDURE WAS FILED IN THE CORRECT LOCATION. MISPLACED LEVEL 1 PROCEDURE WAS FOUND AND REMOVED. SUPERVISION WAS NOTIFIED AND CR WAS ISSUED
396412 | CR | 20190702 |  | 4 | Chem Lab IPM Out of Service |  |  |  | N | NO | <D> **** Detailed Description **** RW 487' Chem Lab IPM-8 (HP-EQ-C015122) Out of service due to low beta counts. <I> **** Actions Taken **** Work request written, informed HP supervision. <N> **** Equipment Description **** RW 487'
396413 | CR | 20190702 |  | 4 | Boundary dose rate for RMA exceeds PPM 11.2.7.1 values | N | N |  | N | NO | <D> **** Detailed Description **** CVAN RMC-CV-0246 was found at Building 167 with an on -contact dose rate of 2 mrem /hr. This exceeds the boundary dose rate limit in PPM 11.2.7.1 (section 3.10.2) of 1.6 mrem/hr for posted RMAs outside of the protected area. The CVAN contains the old RHR 2A pump that was removed from the main plant RCA prior to R24. The fence around Building 167 is controlled via lock and key, and it is not considered readily accessible to members of the public. <I> **** Actions Taken **** An area posting was established around the CVAN where boundary dose rates did not exceed 1.6 mrem/hr. Radiological operations supervision was notified of the issue. . Boundary dose rate exceeds CGS's PPM 11.2.7.1 values but is still within regulatory limits.
396414 | CR | 20190702 |  | 3 | Storage PM for UTC 538493 needs to be cancelled |  |  |  | N | YES | <D> **** Detailed Description **** Per W.O.#02077541-08 step 4.16 the Storage PM for UTC 538493 to be cancelled. Recommend acton for the component or system engineer to have the storage PM cancelled. <I> **** Actions Taken **** Initiated Condition Report and documented number in W.O.# 02077541-08. | 02-00-COND-M-P/2A
396415 | CR | 20190702 |  | 4 | SSS Office Ceiling Damage |  |  |  | N | NO | <D> **** Detailed Description **** One of the ceiling tiles and support bars has come loose in the SSS/production office of the Yakima building. No one was present in the office when the tile came loose, and it was discovered shortly after the SSS returned from the EO center. Recommend the ceiling be repaired. <I> **** Actions Taken **** Submitted CR for corrective action. <N> **** Equipment Description **** SSS office ceiling
396416 | CR | 20190702 |  | 4 | Near miss - traffic accident avoided |  |  |  | N | NO | <D> **** Detailed Description **** An employee in an EN vehicle was performing weekly air sample collection in Franklin County on Tuesday. While traveling on one of the main 2-lane roads in the farm area, the employee slowed and signaled for a left-hand turn. An aggressive driver suddenly passed on the left. The employee had been alert and aware of the aggressive driver who had followed the EN vehicle for some time so an accident was avoided. Recording incident in CR as a near miss. <I> **** Actions Taken **** Wrote CR for near miss. Individual demonstrated good situational awareness to avert accident, notified supervision. Notified management and industrial safety.
396418 | CR | 20190702 |  |  | Ethics ***SENT TO ECP***** |  |  |  |  | NO | <C> See ECP for contents of CR CR initiated anonymously, reviewed for SCWE content. Moved and Forwarded CR to AR-ECP. <D> **** ANONYMOUS CR - Detailed Description **** ***SENT TO ECP***** See ECP for contents of CR CR initiated anonymously, reviewed for SCWE content. Moved and Forwarded CR to AR-ECP. <I> **** Actions Taken **** initiated CR <N> **** Equipment Description **** NA see 2019 CE-4
396420 | CR | 20190702 |  | 4 | CW Electrcal Building 1 & 2 |  |  |  | N | YES | <D> **** Detailed Description **** While performing WO #02141031-01 SWP-MAI-02 inspection of assigned areas, the doors of the CW Electrical Building 1 & 2 do not operate properly and needs mechanical maintenance attention. <I> **** Actions Taken **** Notified Mechanical maintenace, initiate CR and notified Control Room Supervisor <N> **** Equipment Description **** CW Electrical Buildings 1 & 2 (Building 38 & 39)
396421 | CR | 20190702 | CAQ | D | SW-TI-2B position 3 display erratic | Y | Y |  | N | YES | <D> **** Detailed Description **** SW-TI-2B position 3 display is erratic. While taking H101's position 3 from SW-TE-2G displayed an error number (-177). The channel was reported INOP to MCR. Later in the day as a followup, I checked the display which reported accurately in range with the other positions. As the instrument appears to be working this CR is for trend purposes. <I> **** Actions Taken **** Informed MCR, | 02-00-SW-TE-2G,02-00-SW-TI-2B
396423 | CR | 20190702 |  | 3 | Confidential Information found in uploaded WOT Packages |  |  |  | N | NO | <D> **** Detailed Description **** Confidential information was found in four manually uploaded WOT Packages. The packages were part of hard copy records received and were flagged but not processed. correctly. The WOTs were reviewed and all associated image files relocated to a locked location with limited access. Other images processed during the time frame were verified to not contain confidential information. Recommend assignment to ITMGMT <I> **** Actions Taken **** Relocated files from unlocked to a locked folder with limited access. Discussed the issue at D15. Segregated all Confidential Work Packages stored in the Records vault that require manual indexing to a different drawer.
396424 | CR | 20190702 |  | 3 | Degraded fill supports on CW-CT-2B | N | N |  | N | YES | <D> **** Detailed Description **** Two sections of fill on CW-CT-2B have separated from the support channel and have begun to collapse. The fill is currently supported, but separation of the fill from the fill support channel is expected to continue throughout the cycle. In the event of a complete separation from the fill support, the majority of the fill section would likely remain in the vicinity, supported by the internal cooling tower support beams and adjacent sections of fill. Due to the location of the degraded fill, and the condition of the adjacent fill, it is unlikely that failure of the fill support would result in a sudden clogging of the CW screens; however, fill failure adversely impacts cooling tower thermal performance and increase potential foreign material in the CW system. The degraded fill is located on CW-CT-2B, between columns 10-11, 3 rows up from the bottom, and between columns 11 -12, 2 rows up from the bottom. The remaining cooling towers were walked down and no other instances of external fill failure could be found. Pictures in EDMS. <N> Reference CVI 223-00,5 for CW-CT-2B column locations. | 02-00-CW-CT-2B
396425 | CR | 20190702 |  | 4 | CW-FN-31 shroud missing 4 bolts | N | N |  | N | YES | <D> **** Detailed Description **** The access section on the shroud of CW-FN-31 is missing 4 bolts and is beginning vibrate noticeably. Recommend prompt replacement of missing bolts to prevent excessive vibration of the access hatch and the backing out of additional bolts. | 02-00-CW-FN-31
396426 | CR | 20190702 |  | 4 | ERB W467/9 failed quarterly inspection 02131878-01 | N | N |  | N | YES | <D> **** Detailed Description **** Emergency Remote Ballast W467/9 needs a replacement ballast Scaffold will need to be built to access this. <I> **** Actions Taken **** Informed supervisor, wrote CR <N> **** Equipment Description **** W467/9 Valve Room B Q0/11.8 | 02-00-E-ERB-W467/9
396427 | CR | 20190703 |  | 4 | GY-TK-10A2 Glycol Drain Hose Connection Leak | N | N |  | N | YES | <D> **** Detailed Description **** GY-TK-10A2 glycol 2" rubber drain hose connection has a leak. It is a minor leak but leakage is continual as is evident by accumulation on the floor below the connection. GY-TK-10A2 level is not trending down at an abnormal rate. Note: 2A SM Key required for entry <I> **** Actions Taken **** Informed MCR | 02-00-GY-TK-10A2
396428 | CR | 20190703 |  | 4 | Minor Leak Glycol Leak on GY-P-10A1 Suction | N | N |  | N | YES | <D> **** Detailed Description **** Minor glycol leak on the threaded union connection of GY -P-10A1 suction, below GY-ST-10A1 strainer. See EDMS for picture. GY-TK-10A1 level is stable, this is not active leakage. Note: 2A SM key required for entry. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** ASD Building | 02-00-GY-P-10A1
396429 | CR | 20190703 | CAQ | D | CRD-HCU-42-59 Low pressure alarm recieved | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-42-59. After investigation, Rod Accumulator Trouble Alarm P603-A7 drop 6-7 was for CRD-HCU-42-59 low pressure. <I> **** Actions Taken **** Dispatched OPS-2 to investigate. <N> **** Equipment Description **** RB 522 | 02-00-CRD-HCU-4259
396430 | CR | 20190703 |  | 4 | CW Pump Bay Level Low Alarm | N | N |  | N | YES | <D> **** Detailed Description **** MCR received CW Pump Bay Level Low Alarm (H13-P840.A4.7-4. CW-LI-4 indicated CW-A Bay level at 439â€™. TMU-LI-2A indicated CW-C Bay level at 443â€™. Ops 4 reported locally CW basin levels were 5.5/5/6 for A/B/C bays respectively. CW-LI-4 was observed to be erratic and change by 3-5 feet over a span of a minute. Recommend Maintenance repair CW -LI-4 as required. | 02-00-CW-LI-4
396431 | CR | 20190703 | CAQ | D | CRD-HCU-14-19 Low pressure alarm received | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-14-19. After investigation, Rod Accumulator Trouble Alarm P603-A7 drop 6-7 was for CRD-HCU-14-19 low pressure. <I> **** Actions Taken **** Dispatched OPS-2 to investigate. Recharged HCU. <N> **** Equipment Description **** RB 522 | 02-00-CRD-HCU-1419
396432 | CR | 20190703 | CAQ | D | CRD-HCU-14-51 High Water Level alarm received | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-14-51. After investigation, Rod Accumulator Trouble Alarm P603-A7 drop 6-7 was for CRD-HCU-14-51 high water level. <I> **** Actions Taken **** Dispatched OPS-2 to investigate. Removed excess water from HCU. <N> **** Equipment Description **** RB 522 | 02-00-CRD-HCU-1451
396445 | CR | 20190703 |  | 4 | M&TE Found out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0065278 Hytorc Hydraulic Torque Wrench- model HY -5MXT found OOT & adjusted within specs. Not used during Calibration cycle. DEF #7067A written. No Action Required.
396446 | CR | 20190703 | CAQ | D | Surveillance may have failed due to MTE out-of-tolerance | N | Y |  | N | YES | <D> **** Detailed Description **** On 05-13-19 16.2.3, TEA noble Gas Monitor Channels 1 and 2 - CFT, may have failed due to MTE out-of-tolerance. The as-found during the calibration found the MTE used in this surveillance out-of-tolerance. When the OOT values were added to the data taken in the surveillance, the device failed the surveillance. ODCM actions required. Reference AR/CR 396313. <I> **** Actions Taken **** Wrote this CR. Informed main control room. <N> Re-opened to attach Deficiency report per Tool Crib Attendants request. | 02-00-TEA-FT-13
396448 | CR | 20190703 |  | 3 | Badge photos not imported into corp database | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** 4 badge photos were not imported into Oracle database on s121 <I> **** Actions Taken **** Will retake badge photos and will also work on manual import of complete image table. Researching underlying cause. Not determined yet if photos were exported from IEBS/Security, or if PuTTY script or the Datapump import itself failed. Not a BadgeSync app issue. <N> ITMGMT. NCAQ 3.
396449 | CR | 20190703 | CAQ | D | cctv 42 needs maintenance | N | Y |  | N | YES | <D> **** Detailed Description **** cctv 42 at the ISFSI needs maintenance. Contact security at ext 2185 for further details. <I> **** Actions Taken **** posted compensatory measure, security notification made, CR/WR generated | 02-00-SEC-CCTV-ISFSI/42
396450 | CR | 20190703 |  | 4 | FY19 Nine Canyon Annual Plant Performance report error | N | N |  | N | NO | <D> **** Detailed Description **** The FY19 Nine Canyon Annual Plant Performance was sent out with a transposed number. <I> **** Actions Taken **** The transposed number was corrected and the report was re -sent. The Supervisor and Manager will be reviewing and aproving the report before sending in the future. recommend Cat 4 trend ESD
396453 | CR | 20190703 | CAQ | C | HPCS DG Gov Oil Almost Low OOS | N | N |  | N | YES | <D> **** Detailed Description **** The HPCS diesel governor oil level is currently at the upper scribe. Per the daily Ops logs, oil level is supposed to be â€œapproximately 1/4 inch above line in sight glassâ€ when in standby. See picture. According to WR# 29148513, this is a satisfactory condition with the current governor, and is merely a procedure issue. In that case the logs should be updated to reflect the actual equipment in the field. <I> **** Actions Taken **** Informed MCR <N> After rechecking the governor oil level OPS 2 determined that the "upper scribe" was actually the bottom of the oil level miniscus appearing as a line on the sight glass. Governor oil level was verified to be SAT. DG-ENG-1C is Operable. | 02-00-HPCS-EHO-1C
396455 | CR | 20190703 |  | 4 | Door closure mechanism damage on door M104 in building 63 | N | N |  | N | YES | <D> **** Detailed Description **** Due to a temp power cable going through the doorway this door cannot close all the way. The wind caused the door to open beyond its range of motion causing the door closure to get ripped from the door frame. Request mechanical maintenance to access and repair as needed. <I> **** Actions Taken **** Worked with mechanic shop to temporary wedge the door closed to prevent additional damage. CR/WR generated <N> **** Equipment Description **** South East corner mechanical room door for building 63
396456 | CR | 20190703 |  | 4 | E-AY-TR/M1 is in caution | N | N |  | N | YES | <D> **** Detailed Description **** It appears that E-AYTR/M1 is providing a caution alarm based on CO2 levels in the transformer DGA sampling. The purpose of this CR is to update the CO2 caution limit up which makes it consistent with the other new main transformers in which the CO2 level has been changed in the past. This has no impact on operation of the transformer and this change will still be within IEEE C57.104-2008 Condtion 2 limits for CO2. A confirmatory Manual DGA sample should be obtained to confirm the value obtained from the Kelman is a good value. Typically these manual samples have been lower than the Kelman DGA samples. <I> **** Actions Taken **** Generated CR and updated Kelman DGA settings. | 02-00-E-AY-TR/M1
396457 | CR | 20190703 |  | 4 | Added scope to Low pressure rail car restraints | N | N |  | N | NO | <D> **** Detailed Description **** While performing the NDE Magnetic Particle Testing in the area of the new welds on the rail car under work order 0212-0017-03, a crack was found on the deck of the rail car, with in the 1/2" tollerance of the inspection zone. No cracks were found in the welds themselves. <I> **** Actions Taken **** Contacted weld engineer and had both the package and the weld documents revised. Contacted QC to review and sign the new revisions.
396461 | CR | 20190703 |  | 4 | Abnormalities during conversion of contractor to employee | N | N |  | N | NO | <D> **** Detailed Description **** On June 24, 2019 an active Contractor was hired as an employee and thereby entered into Peoplesoft. The automated process that create entries in Asset Suite from new Peoplesoft data is designed to detect the situation where a contractor is hired as an employee and halt creation of new data in A/S, flagging the person instead as a candidate for employee number conversion. In this case, this person was not correctly flagged and a new (incomplete) profile with the new employee number was created in A/S. This supposedly can only happen if a profile was created manually. No one claims to have done so however, and there are no indications that the automated processes failed. File AR396461_Emp.txt in EDMS contains Emp# details. <I> **** Actions Taken **** The new profile was manually removed from Asset Suite and the old employee number was converted to the new. Other data cleanup in A/S was also necessary. Further investigation of this condition will be pursued only if and when it is observed to happend again.
396467 | CR | 20190703 |  | 3 | CI-13.12 procedure enhancement | N | N |  | N | NO | <D> **** Detailed Description **** CI-13.12 should be revised to include the following enhancements. 1. Section 4.5 should have a caution statement added to not operate the dewar fill/vent valve until they have warmed to room temperature. 2. Section 4.6 for X-cooler operation should be removed. 3. Section 4.12 should be revised to align with the the new digital spectrometer operation and clarify how to establish the proper settings for spectrometer operation. Assign to AR-CHEM. <I> **** Actions Taken **** None
396469 | CR | 20190703 |  | 3 | Evaulate ppm 16.2.3 for revision. | N | N |  | N | NO | <D> **** Detailed Description **** section 7.2 of 16.2.3 performs as found loop check of TEA-FT-13 and if the as found is out of tolerance to generate a CR and WR. this is not a $ Step. then a current souce is used to simulate Process flow to perform the rest of the CFT. In the CC, sect 7.2 the as left for TEA-FT-13 is a $ step. The question is, Is it really necessary to check the Flow transmitter in the CFT and if it is then should it be a $. If the TEA FT-13 check is required then the calibration should be added to this procedure to calibrate the Flow transmitter if the as found is out of tolerence. Request engineering evaulate and an assingment be made to Maint programs to revise procedure. <I> **** Actions Taken **** Wrote CR
396470 | CR | 20190703 |  | 3 | CS-CPU-CGS78 issues | N | N |  | N | YES | <D> **** Detailed Description **** while performing w/o # 02137821-01 for ams-4 calibration the lap top CS-CPU-CGS78 has had several issues. On power up it would ask for a pass word with out showing any of the ams-4 icons for calibration. It also will not give you the full view on the screen. When the charger is plugged in it seems to go into a power save mode which makes diffecult to see the screen without unpugging it. The last performance it worked after much frustration. The left port seemed to work most of the time. <I> **** Actions Taken **** told supervisor wrote this cr recommend new cables be made for laptop <N> Closed to WR 29150332 | 02-00-CS-CPU-CGS78
396471 | CR | 20190703 |  | 4 | Gem 5 HP-EQ-42738 at Security PAAP failed Rad Cal | N | N |  | N | NO | <D> **** Detailed Description **** During the annual Rad Calibration of HP-EQ-42738 , 5 of the 8 detectors had efficiencies below the acceptance criteria. body detectors # 2,3,7,8 were below the minimum efficiency of 5% ranging from 1.2 to 4.2 %. Detector #1 did not obtain ant source counts and had a 0% efficiency with the minimum being 8% <I> **** Actions Taken **** Tagged monitor out of service Notified HP Supervision and Rad support Specialist Wrote CR Wrote Work Request <N> **** Equipment Description **** HP-EQ-42738 at Security PAAP
396474 | CR | 20190703 |  | 3 | Standard Out of Tolerance (Calibration) | N | N |  | N | NO | <D> **** Detailed Description **** Asset Number: 0063395 Make: Hart Scientific Model: 5650 NOD #: Not yet assigned Assign to AR-CALSERV Reverse Traceability Report initiated. No CGS Equipment calibrated with the Standard since it's last calibration (6/23/2017). <N> NOD# 20-01 issued
396476 | CR | 20190703 |  | 3 | Technically incorrect markups provided twice | N | N |  | N | NO | <D> **** Detailed Description **** CR-380667 CAQ C was written to revise PPM 15.1.20. The first revision used the markup in the EDMS and after several months of routing came back because it was technically incorrect. Another markup was provided, but it also was not verified or validated so it also contains errors, inconsistencies, and questionable configuration control (see EDMS). This places us at risk for a procedure with an errors in it to be issued. <I> **** Actions Taken **** Recommend an SME from the Mechanical Shop be assigned to verify and validate the current markup and address the concerns listed in the EDMS. Work is scheduled for 1-20-20, therefore the revised procedure needs to be issued by December to prevent rescheduling. <N> The Technician did a field walkdown and provided a nearly correct markup but did not perform verification as proper valve configuration for FP-V-P66/34 was missed. See EDMS
396477 | CR | 20190703 |  | 4 | CF-TK-41 has loose scale deposits on inside wall. | N | N |  | N | YES | <D> **** Detailed Description **** While investigating why CF-P-41A(B) and CF-P-42A(B) are clogging up and not pumping per WR 29150069 and 29140135 CF-TK-41 was opened to check on tank level. While looking inside, scale that looks similar to the algae on the dry cooling tower decks was noticed on the walls of the tank. Pictures and a video were taken and are in the EDMS. A work order was cancelled last year to drain and clean out the tanks because it wasnâ€™t considered a problem. Each time the mechanics take apart a non-pumping chemical feed pump small pieces of material are found inside which are similar to the scale found inside the tank today. Please plan for draining and cleaning of the inside of CF-TK-41 and 42 and do not allow the cleaning to be cancelled. <I> **** Actions Taken **** Informed supervisor and wrote this AR/WR. <N> **** Equipment Description **** Outside at CWPH | 02-00-CF-TK-41,02-00-CF-TK-42
396478 | CR | 20190703 |  | 3 | New RRC Pump Sleeve to Shaft overlay insp did not pass | N | N |  | N | NO | <D> **** Detailed Description **** The final liquid penetrant (PT) examination of the new RRC Pump Head Assembly being procurred failed to meet the examination criteria. This is the 4th failure of this type. The sub-contractor who performed the stellite welding of the sleeve to the pump shaft is being replaced. Another sub-contractor is in the process of being qualified by the pump vendor. The new application process will use laser technology which is a much more controlled. The Vendor NCR number is 200188227. <I> **** Actions Taken **** Notified RXMM Supervision, Engineering and Supply Chain Meeting with vendor - Recovery plan in progress EN will be applying additional oversight to verify the process is acceptable.
396479 | CR | 20190704 | CAQ | D | Received SLC tank high level alarm | Y | Y |  | N | YES | <D> **** Detailed Description **** Received SLC tank high level alarm, 4.603.A8 5-8. SLC tank level per SLC-LI-601 had a level increase to greater than 5100 gallons. Local indication is also elevated to approximately to approximately 5100 gallons. SLC tank level point X077 indicates level is 5050 gallons. Bubbler flow rate is normal. Demin makeup supply to the SLC tank was verified closed. Recommend performance of ISP-SLC -X301, Standby Liquid Control Tank Level â€“ CC. <I> **** Actions Taken **** Notified CRS Dispatched Operator to investigate local indication | 02-00-SLC-LI-601
396480 | CR | 20190704 |  | 4 | CRO1 Hourly 0100 logs missed |  |  |  | N | NO | <D> **** Detailed Description **** CRO1 Hourly logs for time 0100 were missed on 7/4/19. Data was gathered from recorders and input into logs late. No readings were out of spec. <I> **** Actions Taken **** Notified CRS and SM that hourly logs had been missed. Updated logs with recorder data from time 0100.
396490 | CR | 20190704 |  | 4 | CAS-C-1C oil at min spec | N | N |  | N | YES | <D> **** Detailed Description **** The oil level for CAS-C-1C is at the minimum spec of 1/8 sightglass. Per logs "operable untli oil level is out of sight low". See photo <I> **** Actions Taken **** Informed MCR | 02-00-CAS-C-1C
396491 | CR | 20190704 |  | 3 | PPM 1.3.81 Enhancement for Bump Covers |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** PPM 1.3.81 (Plant Component Status Control) requires the use of Simultaneous Verifications (SV) for Bump Cover Installation and removal (Step 6.4.7). This is not in alignment with Standard-01, in regards to activities that warrant the use of SV. See EDMS doc for snap shot of Standard-01 and 1.3.81. Removing the SV requirement for Bump cover installation/removal will reduce the manpower constraint associated with bump covers and allow more timely response to Bump hazard mitigation, as well as strengthen our ability to promptly address/audit out of date bump covers in the field. Please remove the SV requiements from step 6.4.7 and Attachment 9.5 of PPM 1.3.81. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** PPM 1.3.81
396492 | CR | 20190704 |  | 4 | CAS-C-1C needs oil added |  |  |  | N | YES | <C> Duplicate of CR 396490 <D> **** Detailed Description **** While performing rounds it was noted that CAS-C-1C was at the minimum spec for oil level and some oil will need to be added soon. <I> **** Actions Taken **** Inform CRS and initiate AR/WR. | 02-00-CAS-C-1C
396493 | CR | 20190705 |  | 4 | SEC-XR-02 Requires Maintenance |  |  |  | N | YES | <D> **** Detailed Description **** Warehouse X-Ray 2 requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervision notified. XR-02 taken out of service. Initiate CR/WR. | 02-00-SEC-XR-2
396500 | CR | 20190705 |  | 4 | CMS-RIS-27B had a comm loss | N | Y |  | N | YES | <D> **** Detailed Description **** CMS-RIS-27B had a momentary Communication loss. This may have been caused by a short duration loss of power to CMS -RIT-27B duration appeared to have been for approximately 1 second per the display screen on CMS-RIT-27B. CMS-RIT-27B comm loss was reset at CMS-RIT-27B by depressing the reset push button. CMS-RIT-27B display rebooted and communication was re-established with CMS-RIS-27B in the MCR. <I> **** Actions Taken **** Informed CRS and followed ARP. | 02-00-CMS-RIT-27B
396501 | CR | 20190705 |  | 3 | 4.851.S2 drop 5-5 needs enhancement | N | N |  | N | NO | <D> **** Detailed Description **** Board RAD 23 trouble ARP needs enhancement for step 4. dealing with a CMS-RIS-27B COMM LOSS. Attached a modified copy of the procedure in EDMS. Same enhancements will need to be made to RAD board 22 trouble alarm in 4.851.S1 drop 5-5. The button referenced in the ARP is not on the new CMS-RIT-27B. <I> **** Actions Taken **** Had other Operators validate procedure enhancement.
396502 | CR | 20190705 | CAQ | D | RHR-V-112B indicates intermediate on H13-P601 | Y | N |  | N | YES | <D> **** Detailed Description **** RHR-V-112B indicates intermediate on the vertical section of H13-P601 (both red and green position indicating lights illuminated) . RHR-V-112B is the RHR-B Shutdown Cooling return manual isolation valve - located in primary containment. This valve is locked-open per SOP-RHR-LU and ppm 1.3.29 (Locked-Valve Checklist) and previously did indicate full open . Suspect limit switch issue - recommend adding to forced outage work list (drywell entry required). Note: RHR-B was the last SDC system used prior to plant startup - refer to log entry 6/17/19 @ 13:48. <I> **** Actions Taken **** Submitted CR and WR to document the issue. Notified the CRS and Shift Manager. | 02-00-RHR-POS-V/112B/O
396503 | CR | 20190705 |  | 4 | Isolate TOA-AW-1A auto drain due to leak by past TOA-V-33A. | N | N |  | N | YES | <D> **** Detailed Description **** Isolate TOA-AW-1A auto drain due to leak by past TOA-V-33A. TOA-V-33A, the air-operated auto-drain valve for TOA-HVAC -1A airwash basin, leaks by at rate of approximately 5 gpm when it indicates closed; need to repair or replace basin drain valve. Caution Tagged and Close TOA-V-92 to isolate TOA-V-33A to prevent wasting demin water that is continuously draining | 02-00-TOA-V-33A
396504 | CR | 20190705 |  | 3 | Gaps in Protected Equipment Schemes Described in PPM 1.3.83 |  |  |  | N | NO | <D> **** Detailed Description **** During the T-5 review for the 8/12/19 workweek, we noted we will be conducting annual and two-year maintenance on E-GEN-DG4 (DG-4). DG-4 is part of our FLEX equipment described in LCS 1.11.1, PPM 5.6.1 SBO/ELAP and 5.6.2, Station Blackout (SBO) and Extended Loss of AC Power ELAP Attachments. PPM 1.3.83 lists SSC's to post when protecting DG-4, but is silent on what to protect when removing DG-4 from service. DG-4 is used to provide power to either MC-7A or MC-8A to charge the station SR batteries. FLEX-GEN-DG5 is the other 480 V FLEX generator capable of providing power to either MC-7A or MC-8A to charge the station SR batteries. PPM 1.3.83 should include protecting FLEX-GEN-DG5 when E-GEN-DG4 is OOS. It should also describe under what conditions E-GEN-DG4 should be protected (i.e., maintenance on FLEX-GEN-DG5). Standard OPS protection scheme P-E-DG-4-001 tags FLEX-GEN-DG5 as protected. <I> **** Actions Taken **** Reviewed applicable procedures to verify contents. <N> **** Equipment Description **** FLEX-GEN-DG5 E-GEN-DG4
396505 | CR | 20190706 | CAQ | D | Rod Accumulator Trouble Alarm P603-A7 drop 6-7 CRD-HCU-5435 | Y | N |  | N | YES | <D> **** Detailed Description **** Alarm is due to low Ns pressure. <I> **** Actions Taken **** Ops 2 repressurized the accumulator per SOP-CRD-HCU | 02-00-CRD-HCU-5435
396506 | CR | 20190706 |  | 4 | SAS AIM Video Workstation | N | N |  | N | YES | <D> **** Detailed Description **** The video workstation located in the Secondary Alarm Station requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** System rebooted and returned to service. Initiate CR/WR <N> **** Equipment Description **** SAS video workstation
396510 | CR | 20190706 |  | 4 | Lighting Panel Tamper 437' RW | N | N |  | N | YES | <D> **** Detailed Description **** The lighting panel tamper on the 437' Radwaste is not functioning as designed. Contact Security at extension 2185 for further details. <I> **** Actions Taken **** Security Supervision notified, CR/WR generated for Electrical support to look at the Panel Tamper. | 02-00-SEC-TAS-TSSAT
396511 | CR | 20190706 | CAQ | D | FDR-V-609 Took Multiple Attempts to Open | N | Y |  | N | YES | <D> **** Detailed Description **** FDR-V-609 took 3 tries to indicate full open on H13-P632 per WO#02142896. The stroke time open was 3:65 seconds recorded for the third time. <I> **** Actions Taken **** Informed CRS/SM of preconditioning. | 02-00-FDR-V-609
396512 | CR | 20190706 |  | 4 | Fail Mode alarm light lit on DEH-AC-IR/Trip | N | N |  | N | YES | <D> The Fail Mode alarm light is lit in addition to the High Control alarm light on DEH-AC-IR/Trip <I> Initiated this CR. <N> TB 471' East . Since the alarms are expected and cannot be eliminated by reprogramming the controller, the procedural requirement for Operations to initiate a CR was removed. Only System Engineer notification was retained for trending purposes. Assignment 03 of 264673 was created as a PCRA assignment to modify procedure PPI PPM 3.1.10, Page 74 of Revision 088, Bullet 1 of part â€œ(59)â€ as applicable. | 02-00-DEH-AC-IR/TRIP
396513 | CR | 20190706 | CAQ | D | MS-EV-VPI console signal conditioner cards found OOT. | N | Y |  | N | YES | <D> **** Detailed Description **** During performance of ISP-MS-M201, as found VPI voltage checks for signal conditioner cards 1 through 9 were found OOT. Adjusted all SCU to within tolerance per step 7.1.4. <I> **** Actions Taken **** Informed Ops, supervision, system engineer, wrote CR. <N> **** Equipment Description **** 467 Remote Shutdown Room | 02-00-MS-EC-VPI
396514 | CR | 20190706 |  | 3 | ISP-MS-M201 requires procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Table 7.2a requires documentation of valve position indication on H13-P601 for MS-RV-1B which currently has a notation that states indication has been bypassed per EC -17264. Dual indication for MS-RV-1B has been repaired and no longer shows dual indication. Procedure requires enchantment to remove note from table 7.2a <I> **** Actions Taken **** Discussed with SM, wrote CR. <N> Procedure changes have been incorporated. No futher actions required.
396515 | CR | 20190706 |  | 3 | R24 Lessons Learned (CRDM Exchange) |  |  |  | N | NO | <D> **** Detailed Description **** See attached EDMS <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817
396516 | CR | 20190706 |  | 3 | E-TR-S needs a gas analyzer reading added to OPS-4 logs. |  |  |  | N | YES | <D> **** Detailed Description **** E-TR-S now has a gas analyzer and needs a log reading checking its operation added to the OPS-4 logs. The reading preferably should be added just after the winding temp. readings or just after the oil level reading. <I> **** Actions Taken **** Initiated this AR. . DGA monitor was added to E-TR-S under WO 02066036. OPS 4 rounds need to have this added to check like we do for the main transformers. | 02-00-E-TR-S
396517 | CR | 20190706 |  | 4 | HT-HTP-FP/6 ckt 24 low temp. light flashing. | N | N |  | N | YES | <D> **** Detailed Description **** HT-HTP-FP/6 ckt 24 low temp. light flashing. Please cal/repair as necessary. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** CWPH | 02-00-HT-HTP-FP/6
396518 | CR | 20190706 |  | 3 | Several barrier impairments remain open |  |  |  | N | NO | <D> **** Detailed Description **** BI 17-0647 (WO 02114513), BI 18-0457 (WO 02109865), BI 19 -0029 (WO 02113307) are all for R24 and are still open with no closure notes in the plant logging system. The associated work orders are all at finished. <I> **** Actions Taken **** Verified associated WO status at FINISHED.
396519 | CR | 20190706 |  | 4 | Metal Pallet Incorrectly Staged with No Information |  |  |  | N | NO | <D> **** Detailed Description **** There is an empty metal pallet on the deck near the Condensate Pumps, TB 441 which has no information on it. Likely left over from the outage. It needs to be removed from the plant or given a staging placard it is supposed to be there. <I> **** Actions Taken **** Initiated CR since owner of the pallet is unknown. This is a housekeeping issue and potential trip hazard. <N> **** Equipment Description **** TB 441 Condensate Pump Area
396520 | CR | 20190706 |  | 3 | PDU Box left plugged in, WO task at finished |  |  |  | N | YES | <D> **** Detailed Description **** PDU is still stagged with the cable routed and plugged in to a welding receptacle. Contact information show a "not working" email Name. Please see pictures attached. this need to be moved to its storage location, unplugged, and find out why it wasnt done as part of the WO that put it in place. PDU was installed under WO 02119702 (assuming the WIP sign is accurate). see picture. <I> **** Actions Taken **** wrote CR <N> **** Equipment Description **** PDU box on the 501 This PDU was set up by ENW electricains prior to R24 to support MT-CRA-1 and the Main Hoist Upgrades. EC 17337
396521 | CR | 20190706 |  | 4 | CW HVAC Annunciator not annunciating audibly. | N | N |  | N | YES | <D> **** Detailed Description **** POA-ANN-PNL/CWHVB annunciation is more brief and much less audible than expected. | 02-00-POA-ANN-PNL/CWHVB
396522 | CR | 20190707 | CAQ | B | Unplanned high level trip of FWH 1C at 0016 | N | N |  | N | YES | <C> RISK: Medium. CAUSE: Uncertain. Severity B, Investigation Template Required <D> **** Detailed Description **** Unplanned high level trip of FWH 1C with the subsequent trips of FWH 2C, 2B, 2A, and 3C in that order. Unknown cause of the FWH high level trips. Evaluate this transient per 1.3.79. <I> **** Actions Taken **** Wrote CR Informed Ops management <N> Underlying cause of FWH trips is unclear. This CR screens as a Severity "B" with investigation template (EQIT). | 02-00-COND-HX-1C
396527 | CR | 20190707 |  | 4 | HD-LIC-4C down button semi-responsive | N | N |  | N | YES | <D> **** Detailed Description **** The down button would not consistantly respond to operator input. Excessive force was required some times to achieve a response during recovery of COND-HX-3C. The rubber over the button is also torn. Suspect that the contacts inside the switch may ditry. Please correct. <I> **** Actions Taken **** This piece of equipment still performs its function at this time but may become more semi-responsive over time. | 02-00-HD-LIC-4C
396528 | CR | 20190707 |  | 4 | HD-LIC-4C2 Process varible indication stops at -5.3" when it | N | N |  | N | YES | <D> **** Detailed Description **** HD-LIC-4C2 Process varible indication stops at -5.3" when it should be downscale. The level indcation on HD-LIC-4C was down scale at the time and lowering level indcation was seen on the COND-HX-3C and COND-HX-2C at the time suggesting that the level was truely below the indicating range. Please correct the indication to allow for more precise control. <I> **** Actions Taken **** Wrote this CR. | 02-00-HD-LIC-4C2
396529 | CR | 20190707 |  | 3 | R24 Lessons Learned (Drywell) |  |  |  | N | NO | <D> **** Detailed Description **** See attached EDMS <N> Per agreement with CAP Supervisor, this CR is being reopened and assigned a Severity 3 to evaluate for any lesson learned action. Reference CR 396817.
396530 | CR | 20190707 | CAQ | D | Accumulator Trouble Alarm P603-A7 drop 6-7, CRD-HCU-4259 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-4259. Dispatched OPS-2 to investigate. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-4259 low pressure. OPS2 re-pressurized per SOP-CRD-HCU. Alarm is now clear. <I> **** Actions Taken **** informed CRS/Sm | 02-00-CRD-HCU-4259
396531 | CR | 20190707 | CAQ | D | FP-PI-W6A reads abnormally high. | N | N |  | N | YES | <D> **** Detailed Description **** FP-PI-W6A is reading approximately 204 psig. Header pressure as read on FP-PI-W6B is reading about 162 psig. Per 15.1.1 section 7.1, the system pressure should be within 20 psig of header pressure. Recommend attempting to restore system pressure or , if necessary , replacing the over-ranged/damaged gauge. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 441 W | 02-00-FP-PI-W6A
396532 | CR | 20190707 |  | 4 | SEC-XR-03 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** SEC-XR-03 requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Equipement taken out of service. Security supervision notified. Initiate CR/WR | 02-00-SEC-XR-3
396533 | CR | 20190708 |  | 4 | PAP IPM-8 removed from service on nonfunctional detector | N | N |  | N | YES | <D> **** Detailed Description **** IPM-8 HP-EQ-32777 at the primary access point was removed from service due to the fourth detector on panel 3 returning a "N/A" for the last back and front counts. This event occurred during the weekly response check of the instrument. No visible damage was noted with the detector. <I> **** Actions Taken **** IPM-8 was removed from service. RP supervision notified of the event. | 02-00-HP-EQ-32777
396534 | CR | 20190708 |  | 4 | Unable to operate MS-V-173A | N | N |  | N | YES | <D> **** Detailed Description **** MS-V-173A is difficult to operate, feels like it seized. Attempted to use an approved leverage device at supervisors discretion and was still unable to close the valve. <I> **** Actions Taken **** Informed SSS. Wrote CR | 02-00-MS-V-173A
396535 | CR | 20190708 |  | 4 | MS-V-169A Broken/Stripped Handwheel | N | N |  | N | YES | <D> **** Detailed Description **** The handwheel for MS-V-169A can be slid up and down the stem without operating the valve. Valve operates normally when proper torque is applied to stem. <I> **** Actions Taken **** Informed SSS. Wrote CR. | 02-00-MS-V-169A
396536 | CR | 20190708 |  | 4 | TSW-V-65C stiff to operate | N | N |  | N | YES | <D> **** Detailed Description **** While blowing down TMU pump strainers TSW-V-65C was very stiff to operate. The stem threads seemed to bind and needs some lubrication. <I> **** Actions Taken **** Informed SSS | 02-00-TMU-V-65C
396537 | CR | 20190708 |  | 4 | BS-DVSPV-2C1 and BS-DVSPV-2C2 do not appear to have power. | N | N |  | N | YES | <D> **** Detailed Description **** BS-DVSPV-2C1 and BS-DVSPV-2C2 do not appear to have power. They are cold to the touch and donâ€™t feel like an SPV that has power. When trying to reset COND-HX-2C from a high level trip both BS-DV-2C1 and BS-DV-2C2 did not shut as excepted when latching the BS-SPV-8E and BS-SPV-8F per ABN-FWH-HILEVEL/TRIP. BS-V-8E and BS-V-8F still indicate full closed. When they should have opened or at least indicated mid position. Air pressure appears to be passing by BS-SPV-8E and 8F as the pressure regulator has pressure. When comparing this to COND-HX-2A which did reset as expected it was found that the associated BS-DVSPV-2A1 and BS-DVSPV-2A are hot to the touch. Also BS-V-8A and BS -V-8B changed to duel indication when they were reset. <I> **** Actions Taken **** Wrote CR Informed CRS <N> Maint troubleshoot/data collection to verify status of E -IR-5 fuses for low pressure heater 2C. (TB6B-F03, TB6BF04, TB7BF01-1, TB7BF01-2) is completed satisfactory. All fuses checked are good and voltage readings are as expected. WR 29150367 was completed. | 02-00-BS-DVSPV-2C1,02-00-BS-DVSPV-2C2
396538 | CR | 20190708 |  | 4 | MS-V-171A Steam Leak | N | N |  | N | YES | <D> **** Detailed Description **** MS-V-171A appears to have a smalll steam leak from packing. <I> **** Actions Taken **** Wrote CR | 02-00-MS-V-171A
396542 | CR | 20190708 |  | 4 | Temp lighting grounding / sparking |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Temporary lighting in alpha SJAE room was grounding / emitting sparks due to cord in contact with hot piping. <I> **** Actions Taken **** Unplugged and removed temp lighting. Informed SSS. Wrote CR.
396554 | CR | 20190708 |  | 3 | R24LL: Form number 26470 should be revised |  |  |  | N | NO | <D> **** Detailed Description **** The FME TIC sheet form (Form # 26470) should have a space for the owner of The equipment on the form to make tracking them easier. another issue was also identified, The second column on the second page also says "Pre-Use" twice instead of "Post use". <I> **** Actions Taken **** Author recomends this CR be screened to AR-MNTPROG. A non-caq severity level 3.
396556 | CR | 20190708 |  | 4 | R24LL Lack of cordination affected FME Resources. |  |  |  | N | NO | <D> **** Detailed Description **** There was a lack of cordination/ communication between various work groups, which impacted FME. Due to this lack of cordination/ communication FME monitors were told to be at a certain location within the plant for a job that would start at a certain time. The various work groups would not be able to get all of the support groups needed, so they would cancel the job for the time being and not inform FME which left FME monitors waiting in the plant for hours. This occurence happened approximetly once a shift throughout the whole outage. The FME cordinator would follow up with the various work groups when the job was identified as not going to happen. The usual responce from the various work groups was that HP did not have enough resources to support various jobs in the Turbine building. <I> **** Actions Taken **** FME program started to challange requests for FME support during the outage to ensure that all other support was already obtained, discussed issue with Williams supervisors, Siemens Supervision, HP supervisor, and outage management. Author recomends severity non-caq 4 / Trend.
396558 | CR | 20190708 |  | 3 | WO 02134239 can not be worked online, needs recode to outage |  |  |  | N | NO | <D> **** Detailed Description **** See emails attached to EDMS docs for background information. Question arose during CORC phase of this WO when it was scheduled during last cycle (pre R-24) regarding the safety of workers working on the relief valve that shares a common discharge stack with two other in service steam relief valves. The decision was made to perform the maintenance in R24. The work did not occur in R24 and was recoded to daily. This work should now be recoded to forced outage or R25.
396562 | CR | 20190708 |  | 4 | R24 LL Confined Space DSR qual usage |  |  |  | N | NO | <D> **** Detailed Description **** The first week of the outage, 412 individuals onsite were qualified Confined Space DSR/Entry Supv (SFAY). A review of confined space permits between 04/01/19 and 06/21/19 identified that only 115 (28%) of those individuals actually used the qual and signed as a DSR. Additionally, the top 10 users accounted for over 50% of the DSR signatures. This is a poor return on the initial and requal investment made by the company, and if so few people are using the qual, their proficiency is likely very low. Unlike the general entrant/attendant qual (SFBI) which only requires a transferable NANTeL CBT, SFAY requires an onsite CBT, NANTeL CBT, and a 1.5 hour practical exercise with requal requirements. Groups assign this qual broadly to gain flexibility, but 28% usage is beyond any reasonable need for flexibility. Cutting down the assignment of SFAY would save outage in-processing costs going forward. <I> **** Actions Taken **** Shared information with heavy users of SFAY during outages, Industrial Safety, and Training.
396576 | CR | 20190708 |  | 4 | RW 467 RWCU Pre Coat Area, Higher than expected dose rates |  |  |  | N | YES | <D> **** Detailed Description **** Dose rates in the RW 467 RWCU Pre-Coat Area have increased to 22 mrem-hr. performing an MWR flush will lower the dose <I> **** Actions Taken **** Dose rates in the RW 467 RWCU Pre-Coat Area have increased to 22 mrem-hr. performing an MWR flush will lower the dose rates. <N> **** Equipment Description **** RW 467 Pre-Coat Tank Room | 02-00-EDR-PIPE-MISC
396577 | CR | 20190708 |  | 3 | Procedure enhancement for 15.2.14 |  |  |  | N | NO | <D> **** Detailed Description **** 15.2.14 step 7.4.2.h Says repeat from step 7.4.2b but it should be step 7.4.2a so that the visual inspection gets done on all detectors in the zone. <I> **** Actions Taken **** Wrote CR. Added procedure hold to WO 02126627-14
396578 | CR | 20190708 |  | 3 | Secondary codes not consistently entered for FME events |  |  |  | N | NO | <D> **** Detailed Description **** Condition Report Secondary codes used for trending have not been consistently entered for FME events. A search of condition reports was conducted with the following criteria. From January 1st through the end of R24 . The following words were also used in this search: â€œFM,â€ â€œFMEâ€ Foreign Materialâ€ and Dropped. A total of 108 items were identified. A search of the DAT program using the secondary trend codes of â€œFMEâ€ and â€œFMFâ€ identified a total of 52 CRâ€™s coded. <I> **** Actions Taken **** Discussed with Maint. Programs leadership reviewed various lists. Added exel spread sheet to EDMS of this AR. Author recommends a Non-Caq, severity level 3 to AR-MNTPROG so the list gleamed from the search can be reviewed and corrected as needed. <R> NRC Identified.
396580 | CR | 20190708 |  | 4 | PWC-V-137 | N | N |  | N | YES | <D> **** Detailed Description **** PWC-V-137, backflow preventer assembly, was found to have a one drop per two second leak coming from the relief valve of the assembly. This assembly is known to have an issue with the relief valve o-ring. Need to repair the relief valve and test the assembly. This will be done under the current work order 02109924-01. <I> **** Actions Taken **** cr written, supervisor notified, parts ordered. <N> **** Equipment Description **** 525 RW | 02-00-PWC-V-137
396581 | CR | 20190708 |  | 4 | Oil leakage identified during WO#02001147 | N | N |  | N | NO | <D> **** Detailed Description **** Oil leakage identified during WO#02001147. This is transformer yard walkdown. System engineer has been notified and this CR is for trending and information. E-V -M1/DH/W had 5-10 mls, E-V-M2/DH/E had 5-10 mls, E-V -M2/DH/W had ~5 mls and E-V-M3/DH/W had 5-10 mls leakage. <I> **** Actions Taken **** Contacted system engineer and initiated this CR for trending and info
396582 | CR | 20190708 |  | 3 | RRC EDNA points reading -99 | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The following EDNA points have been reading -99 since at least January 2019. They are all the RRC Elbow Tap DP points: B037DP, B129DP, B131DP, B038DP, B039DP, B130DP, B026DP, B040DP Recommend I/C perform calibration of these points to determine cause. Problem may also be process computer related. <I> **** Actions Taken **** Initiated CR. <N> Initiated WR 29151521 and assigned to FIN I&C to investigate.
396583 | CR | 20190708 |  | 4 | Increasing trend, Main Turbine Brg 7 vibes approaching alarm | N | N |  | N | YES | <D> **** Detailed Description **** Since startup from R24, there has been an increasing trend in Main Turbine Bearing 7 vibration levels. The highest vibration readings occur in the late afternoon of each day and predominately correlate with condenser backpressure. If the current trend continues, the daily peak vibration levels will reach the ARP value of 7 mils for alarm level within the coming weeks (PPI PPM 4.820.B1, Drop 7-6). This trend CR is for management awareness of an apparent degrading trend with station wide implications. A graphic has been placed in the EDMS of the parent AR. An ACMP and ODMI exist for this condition. <I> **** Actions Taken **** Opened discussions with OEM Discussed with Supervisor <N> **** Equipment Description **** Bearing 7, East end of "LPC" | 02-00-MS-DT-1C
396591 | CR | 20190708 |  | 4 | SS-V-11A indicates dual position when it should be open | N | N |  | N | YES | <D> **** Detailed Description **** SS-V-11A indicates dual position when it should be open. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-SS-V-11A
396592 | CR | 20190708 |  | 4 | SS-V-11C indicates dual position when it should be open | N | N |  | N | YES | <D> **** Detailed Description **** SS-V-11C indicates dual position when it should be open <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-SS-V-11C
396593 | CR | 20190708 |  | 4 | MT-CRA-2 cab indicator light not working | N | N |  | N | YES | <D> **** Detailed Description **** During weekly MMP-HOI-C101 it was observed that the power indicator light is not working, this could be due to a burned out light bulb. <I> **** Actions Taken **** Notified my supervisor, initiated this condition report and generated a work request. Will notify main control room, this does not affect operability of the crane. | 02-00-MT-CRA-2
396594 | CR | 20190708 |  | 4 | Leakby past BS-DV-1B may be contributing to Condenser tube e | N | N |  | N | YES | <D> **** Detailed Description **** While reviewing photos from the R24 condenser inspection, it was noted that the COND-HX-1B dump line nozzle was directly above a section of tubes with noticeable steam droplet impingement erosion (SDIE) (see EDMS for picture). It is possible that BS-DV-1B may be leaking by, allowing this isolated area of tubes to be subject droplet impingement. Recommend inspecting BS-DV-1B for leakby in R25. The SDIE was originally identified by NDE and the degraded tubes were plugged in R24. The scope of eddy current testing was expanded to include all exterior tubes and no other instances of SDIE were identified (AR 394323). | 02-00-BS-DV-1B
396597 | CR | 20190708 | CAQ | C | Low megger reading on cable AP3CB-0007 | Y | N |  | N | YES | <D> **** Detailed Description **** Cable diagnostic on low voltage cable AP3CB-0007 from E-PP-3CB ckt 7 to E-TR-S (ALTERNATE SUPPLY) under WO 0210368001 did not meet specified acceptance criteria of GE 645.16 Mohms. Contacted Engineering per work instruction. Per CCMP-01-01 page 21 a second minimum acceptance criteria was specified. The minimum criteria is 12 Mohm. Actual readings are well above this criteria with lowest 1 minute reading of 65.5 Mohm. Engineering directs no further action. Recommend track and trend only. <I> **** Actions Taken **** Contacted Engineering. Initiated CR - no WR required. <N> **** Equipment Description **** Alternate supply from E-PP-3CB ckt 7 to E-TR-S | 02-00-E-CB-PP3CB/7
396598 | CR | 20190708 | CAQ | C | CMS-SR-21 failed o-ring | Y | N |  | N | YES | <D> **** Detailed Description **** While performing WR# 29150137, Drywell Oxygen Concentration Going Up, it was found that the center o-ring, on the back of CMS-SR-21, between the two detectors, failed. See attached pictures. There is no PM to replace this o-ring or some of the others on this sample rack. Recommend engineering evaluation for PM. <I> **** Actions Taken **** Wrote CR, | 02-00-CMS-SR-21
396602 | CR | 20190708 |  | 4 | Fire sprinkler leaking water onto the floor |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** One fire sprinkler head in the GSB/Yakima building adjacent to the HP P-10 gas skid is leaking water onto the floor at the rate of approximately 1 drop every few seconds. <I> **** Actions Taken **** Water cleaned up and a bucket was staged to catch further leakage. <N> **** Equipment Description **** Fire protection sprinkler head mounted on the ceiling near the P-10 gas skid in the GSB/Yakima building.
396603 | CR | 20190708 | CAQ | C | No PV in procedure for replacement of gauges for CIA-PRV's |  |  |  | N | YES | <C> MRT Change request: CR 396603 moved from Severity 3 to Severity C CAQ and assigned to AR-MNTPROC. Peer Verification are quality affecting. <D> **** Detailed Description **** CIA-PRV's are Safety related components and to replace the gauge that is part of the regulator, Peer Verification is required. ICP-CIA-X101 does not have peer verification for the replacement of these gauges. During the last performance of this procedure (WO 02105018) two gauges were replaced the gauges for CIA-TK-1A and CIA-TK-14B . Procedure sould be updated <N> **** Equipment Description **** Wrote CR | 02-00-CIA-PRV-14B,02-00-CIA-PRV-1A
396604 | CR | 20190709 |  | 4 | Safe-T-Rack tool missing 480V socket |  |  |  | N | YES | <D> **** Detailed Description **** When attempting to remotely rack a breaker on SL-71, we noticed that the socket for the 480V breakers (Small, spring-loaded hex head) that fits into the racking motor, was not with the kit. A thorough inspection of all the cases and the tool chest of TB 471 and the cases in the service building, did not produce this tool. Until the tool is found (or until replacement sockets are on site), this will prevent remote racking of 480V power circuit breakers. <I> **** Actions Taken **** Notified SMgt, wrote CR. . Tool was found, no longer an issue. <N> **** Equipment Description **** Normally stored in tool chest TB 471 W.
396606 | CR | 20190709 |  | 3 | R24 LL Temp Power Pre-Outage Installs Procedure Changes |  |  |  | N | NO | <D> **** Detailed Description **** R24 successfully installed more temp power pre-outage freeing up significant outage resources. This was supported by temp power associated procedure changes made before R24 for Div 2. This Lessons Learned CR is to drive the review of Div 1 temp power procedures for changes needed to support more pre-outage temp power installations for R25 and other future Div 1 outages. <I> **** Actions Taken **** Discussed with Supervision.
396608 | CR | 20190709 | CAQ | D | Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-1419. Dispatched OPS-2 to investigate. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-1419 was due to low nitrogen pressure. OPS2 re-pressurized per SOP-CRD-HCU and the alarm is now clear. <I> **** Actions Taken **** Informed CRS/SM | 02-00-CRD-HCU-1419
396609 | CR | 20190709 |  | 4 | PTZ 35 | N | N |  | N | YES | <D> **** Detailed Description **** PTZ 35 has no picture and is not fuctioning as intended. Please contact Security at 2185 for details. <I> **** Actions Taken **** Notified Electrical Maintenance and Security Management. Generated CR/WR. | 02-00-SEC-CCTV-35
396610 | CR | 20190709 | CAQ | D | SEC-Door-C204 | N | N |  | N | YES | <D> **** Detailed Description **** Door C204 is not functioning as intended. Contact Security at 2185 for details. <I> **** Actions Taken **** Notified Electrical Maintenance and Security Management. Generated CR/WR. | 02-00-W-DOOR-C204
396611 | CR | 20190709 |  | 4 | INFO CR: HSSF CAB Annunciator Alarm | N | N |  | N | YES | <D> **** Detailed Description **** Per CI-14.4 CR required for this alarm. Recieved alarm HS YI184-STAT STOP (Hydrogen System E-Stop Activated). This is a hig priority alarm with tele comm to the vender. YV-170 indicates closed. <I> **** Actions Taken **** CR written. Chemistry supervision and MCR/CRS informed of conditions. <N> See cross referenced CR 396615 and WR 29150397. | 02-00-HSSF-CAB-CHEM/LAB
396614 | CR | 20190709 |  | 3 | Revision required to PPM 16.1.11 and MWO |  |  |  | N | NO | <D> **** Detailed Description **** Steps 5.2.3 and 5.2.4 of PPM 16.1.11 are no longer required, since new temp/humidity sensors were installed, and the CC/RC procedure does not replace these sensors anymore. Also, the PM MWO 02120836 needs to have task 07 (OBTAIN CALIBRATED SPARES FOR PRM-TS-3 AND 4) canceled. <I> **** Actions Taken **** Initiated CR. Also recommend looking at already generated PM work orders to ensure the 07 task does not get added. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
396615 | CR | 20190709 |  | 4 | Received H2 Water Chem Trouble alarm (H13-P840.A3 drop 7-6) | N | N |  | N | YES | <D> **** Detailed Description **** Received H2 Water Chem Trouble alarm (H13-P840.A3 drop 7-6) . Dispatched OPS3 to investigate the H2 Water Chem Trouble alarm. Chemistry reports H2 WTR CHEM TROUBLE alarm is due to HS YI184-STAT STOP alarm message HYDROGEN SYSTEM E -STOP ACTIVATED with indication that HSSF-V-YV170 is closed. OPS3 also reports indication of HSSF-V-YV170 closed and Hydrogen pressure currently 157# and down slow. <I> **** Actions Taken **** Informed CRS. Entered ABN HWC and commenced SHUTDOWN of HWC per ABN. | 02-00-HSSF-V-YV170
396616 | CR | 20190709 |  | 4 | SEL 451 COMM Fail lignt illuminated in east ODPS building. | N | N |  | N | YES | <D> **** Detailed Description **** SEL 451 COMM Fail light is illuminated on panel OPDS-RLY -B4/5E in the east ODPS building (building 44). <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** East ODPS building. | 02-00-OPDS-RLY-B4/5E
396617 | CR | 20190709 |  | 3 | EC implemented without notification or assignment to OPSPROC |  |  |  | N | NO | <D> **** Detailed Description **** EC 09590 installed a DGA (Gas Analyzer) on E-TR-S during R24. Along with the other DGA units in the Transformer Yard, this new component requires monitoring per PPM 3.1.10, . Valves E-V-TR/S/1, E-V-TR/S/2, E-V-TR/S/3, E-V -TR/S/4, and E-V-TR/S/5 were installed as part of this EC and do not have configuration controls in place as no procedure revision was assigned to OPSPROC to revise SOP -ELEC-230KV-LU. This is another instance of inadequate planning of an EC; reference CR 394512 and CR 394833. <I> **** Actions Taken **** AR 396516 was submitted by an Equipment Operator requesting the DGA unit be added to Form 27156 (OPS-4 logs). SOP -ELEC-230KV-LU will be revised to add the valves installed by EC 09590. <N> AR 017341-12 to update OPS procedures per EC 9590 was completed on 5/31/2013 with comment from the OPS Procedures Supv that the SOP-ELEC-230kV-LU was not updated as it did not involve the main transformers and were updated. These procedures were requested to be updated per the EC 9590 and the identified assignment.
396618 | CR | 20190709 | CAQ | C | Documentation discrepancy for SGT-SPV-2A and 2B |  |  |  | N | NO | <D> **** Detailed Description **** C93-0078 Rev. 0 and AED SPC 329 have conflicting information with respect to the normal state of SGT-V-2A and 2B. C93-0078 states SGT-V-2A and 2B are normally closed and the associated solenoid pilot valves are normally energized. Per AED SPC 329, the SGT-V-2A and2B are normally open. C93-0077 also indicates these valves are normally open. <I> **** Actions Taken **** Discussed with design engineering supervisor. Initiated CR.
396623 | CR | 20190709 |  | 4 | TOA-FL-1B is at end of roll | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FL-1B is at EOR. Please replace filter media. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 501E | 02-00-TOA-FL-1B
396626 | CR | 20190709 |  | 3 | Certain procedures still need to be revised related to OPDRV |  |  |  | N | NO | <D> **** Detailed Description **** License amendment 251 implemented TSTF-542 in April 2019 to eliminate the mode of applicability in TS related to Operations with the Potential for Draining the Reactor Vessel (OPDRV) yet a number of procedures still have not been updated to reflect the change. A list is provided below: PPM 6.2.2 - New Fuel Handling, Railroad Bay to Refuel Floor (step 4.9) 4.812.R1 - 812.R1 Annunciator Panel Alarms (Pg 8, 12, & 30) 4.812.R2 - 812.R2 Annunciator Panel Alarms (Pg 6, 11, &31) OSP-EDR/IST-Q702 - EDR Secondary Containment Valve Operability (step 1.2) OSP-FDR/IST-Q702 - FDR Secondary Containment Valve Operability (step 1.2) <I> **** Actions Taken **** Discussed with Ops Procedure Supervisor <N> Highlighted sections of affected procedures are attached to EDMS . This issue was identified during QA Operations & Technical Specification Audit AU-OP-TS-19.
396630 | CR | 20190709 | CAQ | C | REMP air sampler found with no power | N | Y |  | N | NO | <D> **** Detailed Description **** REMP air sample Station 48 located at the Ringold Fish Hatchery in Franklin County was found with no power during weekly filter change out on 7/9/19. Sampler run time for the week was only 94 hours. The main breaker was found off. Investigation found that â€œPhase Errorâ€ alert was sent to Big Bend Electric system @1:55pm on 7/6/19. Big Bend Electric personnel fixed the error @11am on 7/8/19 and failed to turn the main breaker at the station back on. REMP personnel turned on the breaker and returned sampler to operation. Station 48 is both an ODCM and EFSEC 332 required air sample location. Recommend AR be assigned to AR-ENLAB to report incident as a sample deviation in the annual REMP report per ODCM 6.3.1 A.1. <I> **** Actions Taken **** Turned the breaker on, returned station to service, consulted Ringold Fish Hatchery staff. Confirmed station operational on 7/9/19. Wrote CR.
396631 | CR | 20190709 |  | 3 | FP Zone 1 Detector Replacement wiring issues | N | N |  | N | NO | <D> **** Detailed Description **** During FP detector replacement task, per WO# 02126624, for FP Zone 1, Craft noted two issues with as-found wiring. 1) The terminal points on the existing detector bases do not exactly match the associated wiring drawing (217-00,84,23). The drawing shows wiring connected to terminal points 1a and 1b, with no jumper between the two points. The actual detector base has a metal, vendor installed jumper between the points. The drawing shows a wire connected to terminal point 4. The actual detector base has terminal points 4a and 4b; with the wire connected to point 4b. There is also a metal, vendor installed jumper installed between these two points. 2) The two wires connected to FP-FS-1 are reversed, as shown on EWD-62E-034A. Wire 1-W1-N2 is connected to terminal point NO and wire 1-W1-P2 is connected to terminal point C. The associated capacitor in the FS is also reversed. The drawing discrepancies noted above, do not affect proper operation of the detectors or flow switch; drawing configuration issue only. <I> **** Actions Taken **** Discussed issues with FP Engineering Wrote CR
396632 | CR | 20190709 |  | 3 | Wrong DLR | N | N |  | N | NO | <D> **** Detailed Description **** Upon exit of from RCA, noticed that the wrong DLR had been issued. <I> **** Actions Taken **** Submitted DLR to HP lead at exit of RCA. Contacted other individual who may have been issued my DLR. Contacted my manager of the DLR swap. <N> RP distributed department DLRs which were then distributed to employees within their department to the respective individuals. In this case, the individual was given or took the wrong DLR. The individual logged into the RCA five times before noticing they didn't have the correct DLR.
396634 | CR | 20190709 |  | 4 | NRC Identified Tool left in the overhead. | N | N |  | N | NO | <D> **** Detailed Description **** During a walkdown the NRC DBAI inspectors identified a tool (appeared to be a wrench) left in the overhead. This was in the corridor outside of the DG3 room. The tool was sitting on a cable tray and was to high in the overhead to be retrieved without a ladder. This tool should be retrieved. <I> **** Actions Taken **** DIscussed with Operations Personel in the Shift support supervisor office. Tool removed.
396635 | CR | 20190710 |  | 4 | CAS-C-1C momentary elevated CO levels | N | N |  | N | YES | <D> **** Detailed Description **** Following performance of WO 02115458, the 1000 hour maintenance for CAS-C-1C received the high CO alarm in the MCR and local indication were 13 ppm of CO approximately 30 minutes after starting CAS-C-1C. This was for a short duration and CO levels started trending down, alarm was in for about 5 minutes. Within 1 hour CAS-C-1C CO level was 4 PPM and continuing to trend down. <I> **** Actions Taken **** Verified no one was using breathing air discussed indication with CRS and night shift maintenance supervisor, it was determined to leave CAS-C-1C running. | 02-00-CAS-C-1C
396636 | CR | 20190710 | CAQ | D | Received 4.FCP.1 drop 5-4 RW 487 Gen area trouble alarm | N | Y |  | N | YES | <D> **** Detailed Description **** Received 4.FCP.1 drop 5-4 RW 487 Gen area trouble alarm multiple time throughout the shift. Equipment Operator was unable to determine the source of the trouble alarm for zone 24 Ionization Detectors during investigation of the trouble alarm. Alarm is locked in currently. <I> **** Actions Taken **** Informed CRS <N> **** Equipment Description **** one of the zone 24 ionization detectors
396638 | CR | 20190710 |  | 3 | MT&E Found out of tolerance | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0059534 Omega Hygrothermograph- model CT485B found OOT & rejected. used during Calibration cycle at Warehouse 3 Building 79 w/o 02132989. No plant impact. DEF# 7068A.
396645 | CR | 20190710 |  | 4 | R24LL Safety Messages not consistently sent outside OCC |  |  |  | N | NO | <D> **** Detailed Description **** Important safety messages or information are sometimes communicated in OCC turnover or other briefings and may not get out to the groups working in the field in a timely manner. Recommend increased safety personnel visibility and participation in work group D15s outside the OCC to ensure all may benefit from important information in a more timely manner. <I> **** Actions Taken **** None <N> Internal and Supplemental Safety Personnel attended D15 meetings. PI Manager reviewed this CR and determined no additional actions are necessary at this time.
396646 | CR | 20190710 |  | 3 | R24LL Critical Path Time Lost Through Shift Turnover |  |  |  | N | NO | <D> **** Detailed Description **** In many cases, an unacceptable amount of time was lost when critical path activities were in progress through shift turnovers. In most work groups, shift turnover for all resources is scheduled at the same time in the morning and evening. For critical path jobs requiring shiftly radiation briefs, contaminated area dress out, etc. time is lost between day and night shifts for personnel to exit work areas and on-coming crew to get back to work. Recomend those affected work groups establish some overlapping shift turnover approach similar to refuel team where 4 staggered crews are established across 24 hour periods such that very little time is lost getting the next crew to the work location before the previous crew leaves. <I> **** Actions Taken **** None
396649 | CR | 20190710 |  | 3 | Lack of scheduling and planning of 0213936001 RDCS lockup |  |  |  | N | NO | <D> **** Detailed Description **** This WO should have been on the schedule for the Instrument Shop to perform. There are also qualified individuals that need the exposure to this system.
396651 | CR | 20190710 | CAQ | C | QCI Hold Point Needs to be added |  |  |  | N | YES | <C> CR Changed from a NON-CAQ 3 to a CAQ C by MRT <D> **** Detailed Description **** During the planning of WO 02129877, the planner mistakenly identified the EC and Work Order as not needing QC Inspection , due to PWTI that stated Quality Class 2, and Parts Acquired being QL3. <I> **** Actions Taken **** Work Order was returned, and QCI hold point added. Planner was coached. | 02-00-WEA-RMS-CP25/TEST
396652 | CR | 20190710 |  | 4 | CW-CT-1C high level | N | N |  | N | YES | <D> **** Detailed Description **** while performing rounds it was noted that CW-CT-1C had a high level. The level is currently 14 in. <I> **** Actions Taken **** Initiate CR and inform CRS. | 02-00-CW-CT-1C
396655 | CR | 20190710 |  | 3 | Error in PPM 15.2.46 |  |  |  | N | NO | <D> **** Detailed Description **** A typographical error exists in PPM 15.2.46 â€œHSSF UV/IR Flame Detectors Functional Testâ€. The qualification for HSSD Site Access Training in section 4.1 should be â€œSFAU Hydrogen Storage & Sup Fac Accâ€, and not SFAY. <I> **** Actions Taken **** Initiated CR to correct the procedure.via an editorial change. <N> This is not a qualification event. Access to HSSF is controlled via key by qualified individuals, access would not be possible by a non qualified individual performing PPM 15.2.46. ***General Notes*** An assignment has been created under the Maint. Procedure revision data base. No assignment is needed within Asset Suite. a link to the Maint. Database has been added to the EDMS of this AR.
396656 | CR | 20190710 |  | 3 | PWC report needs alignment with Engineering Calc |  |  |  | N | NO | <D> **** Detailed Description **** During review of the PWC report for Washington Department of Health, it was noted that the Contact Time being reported is not in alignment with Engineering Calculation ME-02-94-60. The calculation was revised in April 2017, but the PWC report has not been updated to reflect the new calculation. The Contact Times being reported are conservative compared to the new Engineering Calculation, therefore there has not been any violation with regards to Contact Time or Inactivation Ratio on the reported data. The revised Contact Time calculation (ME-02-94-60) should be reviewed and incorporate the appropriate data into the formulas used in the spreadsheet for PWC reporting. Assign to Chemistry for review of the calculation and resolution. <I> **** Actions Taken **** Informed Chemistry Supervision and wrote this CR.
396657 | CR | 20190710 | CAQ | D | DSA-V-77B doesnâ€™t appear to open fully | Y | N |  | N | YES | <D> **** Detailed Description **** DSA-V-77B, the air dryer drain valve, is a ball valve; it doesnâ€™t appear to open fully; may be damaged internally. Please investigate and repair as necessary. | 02-00-DSA-V-77B
396658 | CR | 20190710 | CAQ | D | MT&E found out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0064819 Fluke 743B- model 743B found OOT & Adjusted. Was used during Calibration cycle. DEF #. 7069A <N> Re-opened to attach Deficiency report per Tool Crib Attendants request.
396661 | CR | 20190710 |  | 3 | Additonal local passwords discovered in PeopleSoft |  |  |  | N | NO | <D> **** Detailed Description **** Users found in PeopleSoft HR with local passwords that do not need them. This condition allowed the possibility of users being able to keep passwords longer than our 90 day requirement to change. <I> **** Actions Taken **** IDs were reviewed and local passwords removed. Contacted supervision. Recommend NCAQ3 ITMGMT
396662 | CR | 20190710 |  | 4 | Oil leak from transformer in substation SH-F0 | N | N |  | N | YES | <D> **** Detailed Description **** During the Dry Season Stormwater Inspection required by the site Stormwater Pollution Prevention Plan (SWPPP), an oil leak was observed near the base of the red transformer in substation SH-F0. The leak appears to have made it to the ground. This equipment is owned by Bonneville Power Administration (BPA) but is leased to Energy Northwest. The oil leak needs to be diagnosed and repaired and the contaminated soil/residual oil removed and disposed of in accordance with GBP-ENV-18. See pictures in EDMS Docs. <I> **** Actions Taken **** Spoke with Facilities transformer coordinator and wrote this CR. Recommend assignment to F&CE for evaluation. <N> **** Equipment Description **** EPN unknown - equipment is located in the SH-F0 substation
396666 | CR | 20190710 |  | 3 | SOP-SYS-FLUSH WOs need support tasks |  |  |  | N | NO | <D> **** Detailed Description **** To minimize cycling the organization to obtain review/signatures for planned maintenance it is recommended that engineering support task be added to work orders that require engineering signature in order to start work associated with SOP-SYS-FLUSH. Engineering Support tasks are reviewed weekly to identify upcoming work. . WOT 02142060-01 is an example of cycling engineering with a last minute request to review a flush plan which resulted in a delay from the preferred start time of field work is. The flush plan has been reviewed and approved as of this time. <I> **** Actions Taken **** this CR should be the driver to update SOP-SYS-FLUSH work orders to add engineering support task.
396670 | CR | 20190710 |  | 3 | ICP-MS-PRM Procedure Enhancements |  |  |  | N | NO | <D> **** Detailed Description **** Surveillances ICP-MS-PRM-X301, 302, 303 and 304 cause RRC -V-19 or 20 to momentarily isolate which stops flow to SP-1 in the chemistry lab. The surveillances should have a step to inform Chemistry of isolations so that any perturbations in samples and loss of flow to the sink is explained. This will prevent unnecessary troubleshooting from Chemistry due to parameter changes and flow variances. <I> **** Actions Taken **** Contacted work week manager, wrote this CR. <N> ***General Notes*** This issue is being addressed through the Maintenance procedure revision backlog. an assignment has been created in this back log. No further actions within asset Suite are needed. a link to the back log assignment has been created within the EDMS of this CR.
396671 | CR | 20190710 |  | 4 | LPCS Safety system window critique did not meet min attendee |  |  |  | N | NO | <D> **** Detailed Description **** PER WCI-10 step 4.4 it is expected that individuals involved in the preparation and implementation of a safety system window attend the critique. This expectation was not meet and will require the LPCS critique to be re-scheduled <I> **** Actions Taken **** Notified Supervisor Re-scheduled meeting
396672 | CR | 20190710 |  | 4 | E-MC-7BC1 backside lower busbar | N | N |  | N | NO | <D> **** Detailed Description **** E-MC-7BC1 per 10.25.105 step 7.1.8.e the backside lower busbar A & B phase each have 1 location of arcing. Per Engineering this does not affect the electrical integrity. <I> **** Actions Taken **** With Engineering approval completed this PM and Engineering to evaluate for next PM cycle. <N> The depth of arcing spot is not significant to affect the electrical integrity of the bus. So it does not require urgent/ immediate replacement. However it is something we need to plan on replacing in the future. This condition will be considered for monitoring and trending
396673 | CR | 20190710 |  | 4 | CW-VBE-P1C/PSY Accelerometer appears to have failed | N | N |  | N | YES | <D> **** Detailed Description **** Accelerometer CW-VBE-P1C/PSY monitoring the lower pump shroud of CW-P-1C appears to have failed. The Online Watch feature in AMS Machinery Health Manager Software shows 1.079 Volts DC and zero as a vibration value on 7/10/2019. Normal operating voltage range should be between 8 and 12 volts DC. Recommend I/C to troubleshoot and repair/replace as needed. <I> **** Actions Taken **** Verified data in Online Watch part of AMS Machinery Health Manager. | 02-00-CW-VBE-P1C/PSY
396675 | CR | 20190710 |  | 4 | PWC-FU-1 poor filtering | N | N |  | N | YES | <D> **** Detailed Description **** During investigations to support evaporator pond level increases over the cycle, there is indication that PWC-FU-1 is not filtering as efficiently as needed. Recommed cleaning the filter media or a full replacement. the media was last replaced in 2008 and there is no PM I could find to replace the media on any periodicity. I reviewed the OMM and there was no information. Recommend backgrounding WO 01162454 and adding to the T-20 or earlier to eleviate the impact to the evaporator ponds. <I> **** Actions Taken **** reviewed OMM and PWC-FU-1 PMID for PM frequency and last time conducted. | 02-00-PWC-FU-1
396676 | CR | 20190710 |  | 4 | WOA-V-23 leaking by seat at GT 5 gpm. | N | N |  | N | YES | <D> **** Detailed Description **** While investigating WR 29150165 (evap pond high flowrate), WOA-V-23 was found to be passing GT 5 gpm. Position indicator is near the SHUT position, however these valves are known to accumulate debris in the seat and cause leakby. <I> **** Actions Taken **** Closed WOA-V-63 to stop the leakby, wrote C-WOA-V-63-001 for config control. <N> **** Equipment Description **** RW 487 | 02-00-WOA-V-23
396677 | CR | 20190710 | CAQ | D | Short lived isotopes on PRM effluent particulate filter | Y | Y |  | N | NO | <D> **** Detailed Description **** This CR is for trending purposes and does not affect plant operations. After returning to power from R24, short lived radioactive isotopes Tc-99m and Na-24 were observed in the particulate sample for the reactor building effluent during the weekly 16.11.6 surveillance on 7/09/19. This was observed prior to R24, and tracked in CR 00392316 and 00391996. Work during R24 was performed to stop the leakage suspected to be the source of these isotopes. It is not yet known if the source of these isotopes is the same as the source prior to R24, and the emission rate of Tc-99m and Na-24 is significantly lower than it was prior to R24. The effluent emission rate does not challenge ODCM limits. <I> **** Actions Taken **** Compared isotope emission rate to limits, contacted supervisor and engineering, wrote CR. <N> This AR-CR is being addressed under AR-CR 392316. Per SWP -CAP-01, assignment 02 under resolving AR-CR 392316 has been created to address the issue documented in this AR-CR. Appropriate cross references have been added.
396679 | CR | 20190710 |  | 4 | Unusual Main Turbine Vibrations Observed |  |  |  | N | YES | <D> **** Detailed Description **** Unusual vibrations were observed on the Main Turbine bearings. No significant changes to backpressure or lube oil temperature were observed to help explain. See attached EDMS pictures of the recorder. Note that normally all of the vibration trends are straight, not the odd back and forth with some other bearings doing equal but opposite changes. The last photo also includes values for maximum/minimum/current vibrations along the bottom. | 02-00-MS-DT-1C
396680 | CR | 20190710 |  | 3 | FLEX-FE-8 Offsite | N | Y |  | N | YES | <D> **** Detailed Description **** Received report from FLEX program owner that FLEX-FE-8 would be offsite. CR written to track its return per LCS 1.11.1.A . <I> **** Actions Taken **** Wrote sheet L19-FLEX-FE-8-001 to track N+1 equipment being removed. <N> **** Equipment Description **** FLEX-FE-8
396684 | CR | 20190711 | CAQ | D | R24 Drywell Coatings Walkdown - Areas of Rust | Y | Y |  | N | NO | <D> **** Detailed Description **** During the R24 Drywell Coatings Walkdown several areas of general rust were identified (rust grade 0 approximately 100% surface rusted per ASTM D610-08) at what appeared to be bolting hardware, removed coating for inspection, mechanical damage, weld prep surfaces and weld joints that were not subsequently coated after welding. The rust is a general surface rust that does not affect the function of the supports and does not impact the Coatings margin. SWP -SPS-03 requires repair of rust that is showing through coating. In these cases, the coating is tightly adhered, has been removed, or the component was never coated, so there is no impact to the coating program limits and no requirement for repair. This CR is written for trending purposes only. (See General Notes for list of locations) <I> **** Actions Taken **** Identified locations are being tracked, trended and monitored in the Unqualified Coatings log located on the Engineering Collaboration website. Work Order generated to perform coating when most efficient. <N> **** Equipment Description **** Drywell 1. 3â€ pipe near the floor exhibits an 8 inÂ² area of rusting (rust grade 0 approximately 100% surface rusted per ASTM D610-08) due to mechanical damage. (See R24 DW Report Item 5 Photo #5) 2. A pipe support bracket in the overhead exhibits rusting (rust grade 0 approximately 100% surface rusted per ASTM D610-08) at the weld joints and bottom of support bracket. (See R24 DW Report Item 11 Photo #11) 3. An overhead attachment bracket exhibits rusting (rust grade 0 approximately 100% surface rusted per ASTM D610-08) at the weld joints and grinded/prepared areas. (See R24 DW Report Item 12 Photo #12) 4. A pipe flange and piping exhibit pinpoint rusting along approximately 8â€ of the pipe and the entire flange area. (See R24 DW Report Item 13 Photo #13) 5. A support bracket welded to the outboard wall exhibits rusting (rust grade 0 approximately 100% surface rusted per ASTM D610-08) at the weld joint and prepared area. (See R24 DW Report Item 14 Photo #14) 6. A valve body, flange and bolting hardware exhibit rusting (rust grade 0 approximately 100% surface rusted per ASTM D610-08. (See R24 DW Report Item 15 Photo #15) 7. An 8â€ pipe weld joint exhibits bare substrate with light flash rusting. It appears that this area was intentionally removed to allow for welding examination. (See R24 DW Report Item 16 Photo #16) 8. RCC piping flanges exhibit rust (rust grade 0 approximately 100% surface rusted per ASTM D610-08) on all the bolting hardware. (See R24 DW Report Item 18 Photo #18) 9. a snubber bracket welded to outboard wall exhibits rusting (rust grade 0 approximately 100% surface rusted per ASTM D610-08) at the weld joints. (See R24 DW Report Item 19 Photo #19 10. Horizontal and vertical support brace exhibits isolated areas of pinpoint rusting and general rusting along the edges of the horizontal support (identified during R23 Inspection). No apparent changes were observed during this inspection. (See R24 DW Report Item 23 Photo #23) 11. An electrical conduit support exhibits rusting (rust grade 0 approximately 100% surface rusted per ASTM D610-08) at the weld joint. (See R24 DW Report Item 27 Photo #27) 12. 8â€ pipe running vertically along the outboard wall exhibits rusting (rust grade 0 approximately 100% surface rusted per ASTM D610-08) at an upper weld joint (runs approximately 12â€ length of the pipe) and lower weld joint (runs approximately 2â€™ length of the pipe to include the elbow and penetration into the outboard wall). (See R24 DW Report Item 30 Photo #30) 13. horizontal support brace exhibits an area of mechanical damage with bare substrate at the top of the horizontal brace. (See R24 DW Report Item 31 Photo #31) 14. At elevation 570â€™ azimuth 225Â° an old support brace that has been torch cut exhibits rusting (rust grade 0 approximately 100% surface rusted per ASTM D610-08) at the torch cut heat effected area. (See R24 DW Report Item 32 Photo #32) <S> Work Order needs to be generated to perform coating when most efficient.
396685 | CR | 20190711 | CAQ | D | R24 Wetwell Coatings Walkdown - Areas of Rust | Y | Y |  | N | NO | <D> **** Detailed Description **** During the R24 Wetwell Coatings Walkdown several areas of general rust were identified (rust grade 0 approximately 100% surface rusted per ASTM D610-08) at what incudes the outboard wall, valves, support brackets and steel plating. The rust is a general surface rust that does not affect the function of the supports and does not impact the Coatings margin .SWP-SPS-03 requires repair of rust that is showing through coating. In these cases, the coating is tightly adhered, has been removed, or the component was never coated, so there is no impact to the coating program limits and no requirement for repair. This CR is written for trending purposes only. (See General Notes for list of locations) <I> **** Actions Taken **** Identified locations are being tracked, trended and monitored in the Unqualified Coatings log located on the Engineering Collaboration website. Work Order generated to perform coating when most efficient. <N> **** Equipment Description **** Wetwell 1. The Wetwell inorganic zinc coated outboard wall exhibits isolated areas/patches of rust (rust grade 0 approximately 100% surface rusted per ASTM D610-08), pinpoint rusting and mechanical damage that exhibit minor to heavy rust. (See R24 WW Report Item 1 Photo #1) 2. A valve and support bracket exhibit general rusting (rust grade 0 approximately 100% surface rusted per ASTM D610 -08). (See R24 WW Report Item 7 Photo #7) 3. A 10â€ pipe on the outboard wall exhibits general rusting (rust grade 0 approximately 100% surface rusted per ASTM D610-08) at all of the welded joints and the entire gusset supports. (See R24 WW Report Item 10 Photo #10) 4. All downcomers and overhead steel plating exhibit general rusting (rust grade 0 approximately 100% surface rusted per ASTM D610-08) where the downcomers penetrate through the drywell floor. A white residue was also identified leaching from around the joint areas. Could possibly be calcium leaching from the concrete drywell floor, due to the high humidity of the Wetwell. One (1) area at azimuth 225? exhibited a calcium stalactite. (See R24 WW Report Item 11 Photo #11 <S> Work Order needs to be generated to perform coating when most efficient
396686 | CR | 20190711 | CAQ | D | R24 Wetwell Coatings Walkdown - Cracked Epoxy Coating | Y | Y |  | N | NO | <D> **** Detailed Description **** During the R24 Wetwell Coatings Walkdown, at elevation 480â€™ around azimuth 52 degrees, a Wetwell support column exhibits cracked epoxy coating. The epoxy is tightly adhered so there is no impact to the coating program limits and no requirement for repair. This CR is written for trending purposes only. <I> **** Actions Taken **** Identified locations are being tracked, trended and monitored in the Unqualified Coatings log located on the Engineering Collaboration website. Work Order generated to perform coating when most efficient. <N> **** Equipment Description **** Wetwell 1. A Wetwell support column exhibits cracked epoxy coating with possible staining from the uncoated and rusted bearing pad. Moisture is being mixed with the rust from the bearing pad and running down onto the column. The epoxy coating appears to be tightly adhered. (See R24 WW Report Item 6 Photo #6) <S> Work Order needs to be generated to perform coating when most efficient.
396689 | CR | 20190711 |  | 4 | Aux Boiler Corrion Inhibitor below Action level | N | N |  | N | YES | <D> **** Detailed Description **** The last Aux Boiler sampled had 2 ppm of corrosion inhibitor and the action level is LE 30 ppm. A corrosion inhibitor chemical add is required. The Boiler will need to run for a little over an hour for proper mixing of chemicals and a post add sample. Operations will need to run the boiler for chemistry to do the add. <I> **** Actions Taken **** Notified MCR, Chemistry Supervision and Chemistry system specialist. Generated WR. <N> **** Equipment Description **** Aux Boiler room TG 441' | 02-00-AS-BLR-1
396690 | CR | 20190711 |  | 3 | Compressor Jacket Water has tritium in it | N | N |  | N | I DONT KNOW | <C> MRT Change request: CR 396690 Severity moved from 4/Trend Repair to Severity 3 assigned to AR-CHEM. <D> **** Detailed Description **** The CJW was sampled on 7-10-19 twice and tritium was found in the jacket water both times. This is deemed a clean system so the only way to remove the tritium is to bleed and feed the system. FIN has done this in the past and chemistry will have to do a corrosion inhibitor add once the system has been sampled again for tritium and deemed clean. The CJW samples are sent off site for some of the analysis required by SWP-CHE-02 and as it is contaminated these analysis cannot be completed. This is a violation of SWP-CHE-02. <N> **** Equipment Description **** TG 441' CAS system See EDMS for Evaluation of Tritium in CJW and cross references to AR-CR 299219 and AR-EVAL 302641. At the request of the Chemistry Operations Supervisor, AR -EVAL 396864 was initiated and cross referenced to re -evaluate that the prior evaluation to ensure it is still valid. No further action required under this CR.
396691 | CR | 20190711 |  | 3 | R24 LL- Fuel movement outage planning |  |  |  | N | NO | <D> **** Detailed Description **** During planning of the fuel movement windows during the outage, there should be a hold point inserted where the fuel movement (before or after any maintenance windows) cannot be moved up past a certain time after scram. Moving fuel movement up in the schedule can invalidate the decay heat assumptions built into the spent fuel pool decay heat calculation. A hold point (in days/hours after scram) should be based on the decay heat calculation that Reactor Engineering provides. During initial outage planning stages, the previous outageâ€™s decay heat calculation can be used as an approximation. <I> **** Actions Taken **** Initiated CR
396692 | CR | 20190711 |  | 4 | Outage design change not turned over to OPS in Passport |  |  |  | N | NO | <D> **** Detailed Description **** EC 17560 installed drain valves COND-V-173C and COND-V-174C between COND-V-119C and COND-V-120C to help facilitate system draining. The design change was installed, all WO tasks completed or cancelled, Top Tier Drawing updated, procedures updated. However, OPS signature for return to service was not obtained. <I> **** Actions Taken **** Completed filling of attributes section, emailed OPS for signature, wrote CR.
396694 | CR | 20190711 |  | 4 | RCC-FI-3 glass was found loose | N | N |  | N | YES | <D> **** Detailed Description **** While working on RCC coupon replacement 02113090-01/02 it was noticed that after disassembling the unions as required by procedure that the glass on the FI-3 was loose and leaking. <I> **** Actions Taken **** Initiated CR and WR <N> **** Equipment Description **** RCC-FI-3
396695 | CR | 20190711 |  | 3 | DRAWING FILING TABLE - BROKEN |  |  |  | N | NO | <D> **** Detailed Description **** MULTIPLE DRAWERS IN FILING TABLE ARE SLIGHLTY OPEN AND DO NOT CLOSE COMPLETELY DUE TO THE DRAWERS BEING JAMMED. DRAWERS SEEM TO BE SOMEWHAT MISALIGNED AS WELL, PREVENTING THE DRAWERS FROM NOT BEING FULLY FUNCTIONAL. <I> **** Actions Taken **** ISSUE REPORTED TO RIM LEAD AND SUPERVISION AS WELL AS WORK CONTROL PERSONNEL. WORK REQUEST WAS CREATED ALONG WITH CR. <N> **** Equipment Description **** DRAWING FILING TABLE LOCATED IN YAKIMA BLDG 27 IN WORK CONTROL. FAR RIGHT, BACK WALL NEAR WINDOW.
396696 | CR | 20190711 |  | 3 | R24 LL- Create instruction for EOC ACUMEN data dumps |  |  |  | N | NO | <D> **** Detailed Description **** Create an EOC instruction or procedure that spells out which files to get to support 3DMonicore/Acumen data dumps. Current procedure 9.3.39 is not detailed/accurate enough to identify where/how to get all the files. This document should also ensure that the EOC exposures for individual fuel bundles are obtained for the subsequent Special Nuclear Material inventory. Assign to Reactor Engineering. <I> **** Actions Taken **** Initiated CR
396697 | CR | 20190711 |  | 3 | R24 LL- TSP-CRD-C101 changes |  |  |  | N | NO | <D> **** Detailed Description **** TSP-CRD-C101 changes: 1. The Section for resetting AST database stops well short of the description needed to analyze the data and then reset the cycle for a new refueling outage. More details to match requested software steps is warranted. Lesson learned is that the database needs to be deleted, and one should NOT use the â€œreset refuel outage dateâ€ function as this does NOT reset the database for the new fuel cycle. 2. Allow mode 1 scram times below LPSP with RWM bypassed. Current procedure requires remaining above LPSP. <I> **** Actions Taken **** Initiated CR
396698 | CR | 20190711 |  | 3 | R24 LL- Detaliled walkthrough of RxEng related outage tasks |  |  |  | N | NO | <D> **** Detailed Description **** A more detailed walkthrough of the expected order of execution and required coordination between NCTLs, CRDM/CRB, and LPRM work should be performed to ensure both Dayshift and Nightshift individuals are knowledgeable on the tasks. Consider making a recurring pre-outage AR assignment. Assign to Reactor Engineering <I> **** Actions Taken **** Initiated CR
396699 | CR | 20190711 |  | 3 | R24 LL- Combine WO Task for CRDMs and CRB shuffles |  |  |  | N | NO | <D> **** Detailed Description **** A single WO task for both Control Rod Drive Mech and Control Rod Blade shuffles during the outage should be created. The procedure (PPM 6.5.9) is combined now so the work orders should be combined. The WOT should also contain specific guidance for contingency of completing CRDM, CRB, and restoration to be completed in any order as needed for coordination with other activities. <I> **** Actions Taken **** Initiated CR.
396700 | CR | 20190711 |  | 3 | R24 LL- Schedule outage fuel inspection analysis time |  |  |  | N | NO | <D> **** Detailed Description **** Schedule and plan for data analysis support of any fuel inspections to ensure the station is not waiting for those results to make decisions during the outage. Assign to Reactor Engineering. <I> **** Actions Taken **** Initiated CR.
396701 | CR | 20190711 |  | 3 | R24 LL- Combine fuel movement procedures |  |  |  | N | NO | <D> **** Detailed Description **** SOP-REFUEL-OPS, OI-40, PPM 6.3.2, and PPM 6.3.28 contain guidance on fuel movement. The fuel movement instructions should be combined into one procedure since it's difficult for Operations and Engineering to find guidance for different situations. <I> **** Actions Taken **** Initiated CT
396702 | CR | 20190711 |  | 3 | R24 LL- PPM 6.5.9 modification |  |  |  | N | NO | <D> **** Detailed Description **** PPM 6.5.9 needs to add a column for CRDM completion table (Attachment 7.1) to separate out installation of PIP connectors, as this activity is done AFTER all CRDMs are replaced and torqued. A separate one line item task can be used to identify this action/activity. <I> **** Actions Taken **** Initiated CR
396703 | CR | 20190711 |  | 3 | R24 LL- post LPRM restoration IV curve timing. |  |  |  | N | NO | <D> **** Detailed Description **** LPRM restoration WO should not require Reactor Engineer to perform an I-V curve to return newly replaced detectors from bypass. This action should be done when there is a neutron flux present just prior to first TIP run at 60%. <I> **** Actions Taken **** Initiated CR.
396704 | CR | 20190711 | CAQ | C | 4.601.A4 6-6 RCIC oil flt DP high alarm | Y | N |  | N | YES | <D> **** Detailed Description **** while running RCIC - received high oil filter dp alarm - setpoint 6 psid - indicating 20 psid. Swapped filters and indication remains at 20 psid. | 02-00-RCIC-DPS-14
396705 | CR | 20190711 |  | 4 | (QA) Emergency Lighting Charger Fault | N | N |  | Y | YES | <C> MRT Change request: CR 396705 moved from CAQ Severity D/Trend Repair to NON-CAQ Severity 4/Trend Repair. <D> **** Detailed Description **** A Quality Auditor identified E-BU-SWA6/3 (Rx 468 SW Stairwell) stairwell emergency backup lighting panel indicates charger fault (3 red blinks). Backup Unit is not Appendix R. <I> **** Actions Taken **** Informed Shift Manager. <N> Non-essential lighting. FPSI 19-0158. | 02-00-E-BU-SWA6/3
396706 | CR | 20190711 |  | 3 | R24 LL- PPM 9.3.28 modifications |  |  |  | N | NO | <D> **** Detailed Description **** PPM 9.3.28: 1. Allow core top limits to be set +1000 by I&C prior to prohibiting drywell and TIP room entry. 2. The adjustment screws that are used for defining the core top and bottom limits on the TIP digit cards are small and could be easily lost. There should be some spares somewhere easily accessible (i.e. in the control room). These screws need to have the same or similar electrical conductive properties as the current screws. Procedure 9.3.28 should be changed to state where these replacement screws are kept. 3. Consider making the criteria for TIP limit adjustment +/- 2 inches. <I> **** Actions Taken **** Initiated CR.
396707 | CR | 20190711 |  | 3 | Inadequate config task for TM-EC-17264 |  |  |  | N | NO | <D> **** Detailed Description **** MS-RV-1B locked in alarm has been corrected and the AR -EVAL-392486 did not include ISP-M-M201 as part of the Config task. There is a potential for not performing LCS step to confirm MS-RV-1B position indication at H13/P601. <I> **** Actions Taken **** I&C Tech noted the discrepancy in CR-396514 (This is a good catch). ISP-MS-M201 is being revised, but a procedure hold should be placed on WO 02137743 to ensure it is not performed prior to issuance of the revision.
396708 | CR | 20190711 |  | 3 | R24 LL- SNE control room reqs in different procedures |  |  |  | N | NO | <D> **** Detailed Description **** The definition of when to have a SNE in the control room is slightly different in PPM 3.1.2 vs PPM 9.3.12. <I> **** Actions Taken **** Initiated CR.
396709 | CR | 20190711 |  | 3 | R24 LL- LEFM bypassing at low power |  |  |  | N | NO | <D> **** Detailed Description **** The need for bypassing the LEFM at low power (and unbypassing at high power) needs to be proceduralized. Possible procedures are 9.3.12, 3.1.2. and 3.2.1. <I> **** Actions Taken **** Initiated CR.
396710 | CR | 20190711 |  | 3 | R24 LL- Core verification lighting |  |  |  | N | NO | <D> **** Detailed Description **** For core verification, a side light is necessary to read the fuel bundle serial numbers. This may need to be added to PPM 6.3.5. Working with the refuel floor personnel is necessary to set up the lighting. <I> **** Actions Taken **** Initiated CR.
396711 | CR | 20190711 |  | 3 | Add enhancement to PPM 1.10.11 |  |  |  | N | NO | <D> **** Detailed Description **** Add an enhancement to PPM 1.10.11 step 5.6.1.c to contact the vender once a deviation has been identified for Part 21 evaluations. <I> **** Actions Taken **** Licensing management notified. Recommend 3/AR-LIC
396712 | CR | 20190711 |  | 3 | R24 LL- PPM 9.3.9 modification |  |  |  | N | NO | <D> **** Detailed Description **** PPM 9.3.9 should be modified to state that the shutdown pullsheet should be entered before the Low Power Setpoint even in the event of coastdown. Assign to Reactor Engineering. <I> **** Actions Taken **** Initiated CR.
396714 | CR | 20190711 | CAQ | D | C204 Human Performance Error |  |  |  | N | NO | <D> **** Detailed Description **** At 1024 an individual form Org. Code 72510 did not verify that door C204 was secured after entering the Vital Island. These actions do not align with SWP-SEC-03 subsection 4.7 "Personnel Use of Vital Area Doors" <I> **** Actions Taken **** A sweep of the area determined that there was no unauthorized access granted. The individual processing through the door was escorted out of the vital area and offsite. A statement was taken with their supervisor offsite. SEL and CR were written and Security Supervision was notified.
396715 | CR | 20190711 |  | 4 | D-MS-ST-4A/5A-001 - Danger Tag Valves checked shut | N | N |  | N | YES | <D> **** Detailed Description **** This CR is to document that the following danger tagged valves were checked. MS-V-110A was manually seated to stop leakage into the clearance boundary. Checked shut the following valves with Shift Manager approval. MS-V-110A - nudged closed MS-V-169A - nudged closed MS-V-161A - closed 1/16th turn MS-V-162A - closed 1/16th turn MS-V-170A - closed 1/16th turn
396716 | CR | 20190711 | CAQ | D | annual testing of E-B0-PBX test equipment (Alber) | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Per WO#02127030-01, electricians set up load bank and test equipment to peform annual testing on PBX battery. The test requires a load of 114 amps for 600 minutes. Once the overall voltage drops below 42.0 volts or a single cell drops below 1.0 VPC, then the test software will abort the test. At approximately 9.5 hours into the test, the software detected a loss of voltage on cell 9 and 10 of string 1. Electricians paused the test and measured voltage with a DMM on the affected cells. They verified the cells still had 1.8 VPC and resumed the test. It should be noted that the setup for the test occured on a different shift and problems were encountered with cable assembly on cells 9 and 10. A brand new cable assembly was obtained and installed prior to starting the test. All cells appeared normal and the test was started. it is suspected that test equipment may be failing. <I> **** Actions Taken **** Notified Supervisor, Notified Engineer and PSRO. Write a CR for trending <N> **** Equipment Description **** E-B0-PBX
396717 | CR | 20190711 |  | 4 | R24LL - JITT for Engineering administrative processes |  |  |  | N | NO | <D> **** Detailed Description **** Engineering personnel can benefit from JITT for administrative processes such as TIRPS, OCC-03, etc. This lesson learned CR is to add JITT prior to R25 for administrative processes for Engineering personnel. <I> **** Actions Taken **** Engineering 4.0 critique completed that identified this R24 lessons learned. <N> TREQ 19-0097 was generated.
396718 | CR | 20190711 |  | 3 | R24LL - Engineering develop condenser walk down timeline. |  |  |  | N | NO | <D> **** Detailed Description **** The EOC could have benefited from a condenser walkdown timeline during R24. Recommend developing a condenser walkdown timeline for R25 which consists of who will perform what walkdowns and by when. <I> **** Actions Taken **** Engineering 4.0 critique completed that identified this R24 lessons learned.
396719 | CR | 20190711 |  | 3 | R24LL - Engineering EOC roles and responsibilities |  |  |  | N | NO | <D> **** Detailed Description **** The EOC could have benefited from defined roles and responsibilities for the fourth EOC chair. Roles and resposibilities were clearly defined for the system engineering, design engineering and technical services engineering chairs. Action is to define the roles and responsibilities of the fourth chair in the EOC. <I> **** Actions Taken **** Engineering 4.0 critique completed that identified this R24 lessons learned.
396720 | CR | 20190711 |  | 3 | R24LL - Add applicable individuals to the EOC/OCC email list |  |  |  | N | NO | <D> **** Detailed Description **** Engineering has an EOC/OCC email list that should contain all engineering supervisors and managers. This list does not include acting individuals who may be assigned to one of the EOC chairs during an outage. The action or lesson learned is to include all individuals who will be assigned to sit in one of the four EOC chairs to the engineering EOC/OCC email group. This action should be complete just prior to R25. <I> **** Actions Taken **** Engineering 4.0 critique completed that identified this R24 lessons learned.
396722 | CR | 20190711 |  | 3 | R24LL - Desktop guide for Syntempo and Data Glance |  |  |  | N | NO | <D> **** Detailed Description **** Engineering experienced a lack of proficiency in Syntempo and Data Glance. Developement of a desktop guide would be beneficial for those individual who are not proficient. Please develop a desktop guide for Syntempo and Data Glance for individuals to use while they build proficiency. <I> **** Actions Taken **** Engineering 4.0 critique completed that identified this R24 lessons learned.
396723 | CR | 20190711 |  | 3 | R24LL - Benchmark how other plants perform VT-2 inspections |  |  |  | N | NO | <D> **** Detailed Description **** Benchmark how other plants perform VT-2 inspections to determine a more efficient method to performing the inspections. Columibia should also qualify more individuals to be able to perform VT-2 inspections. The benchmark should include how many individuals are qualified, what department they are assigned to and how they schedule individuals when performing the inspections. Currently CGS utilizes Engineers, do other stations use equipment operators, insulators, etc.? <I> **** Actions Taken **** Engineering 4.0 critique completed that identified this R24 lessons learned.
396724 | CR | 20190711 |  | 3 | R24LL - Standing delegation for supervisors in EOC |  |  |  | N | NO | <D> **** Detailed Description **** Engineering supervisors could have benefited from a standing delegation when supporting the EOC during R24. Several instances were identified where CRs could not be closed until the respective supervisor came back to the plant during scheduled days off. Engineering should develop a standing delegation for engineering supervisors in the EOC to have the authority to close AR assignments and corrective actions. <I> **** Actions Taken **** Engineering 4.0 critique completed that identified this R24 lessons learned.
396725 | CR | 20190711 |  | 4 | DLR 00034351 potentially exposed to X-ray during Travel |  |  |  | N | NO | <D> **** Detailed Description **** DLR 0034351 was potentially exposed to Airport X-ray during travel. The DLR was in a briefcase and was stopped as it entered the X-ray machine at the airport but it is unsure if exposure to x-ray occurred or not. No entry into the RCA with the DLR has occurred in this reporting period started on 07-01-19. <I> **** Actions Taken **** 1. Notified Supervisor and Manager at the morning D-15 upon return to the Site 2. HP Staff Advisor notifed of potential X-ray exposure to DLR 3. Employee DLR was replaced
396726 | CR | 20190711 |  | 4 | 16.3.8 RW BLDG EXH FLOW RATE-CFT | N | Y |  | N | NO | <D> **** Detailed Description **** While craft out performing Work Order 02115461-01 16.3.8 RW BLDG EXH FLOW RATE-CFT, step 7.3.8, it was discovered that the computer point MVL110 was unavailable. Craft stopped and expanded the team by contacting Operations and their supervisor. Suspected that the computer point is out due to D-WEA-SR-25-001 C/O hanging. <I> **** Actions Taken **** Informed Electrical Supervision and Operations. Coordinated with the Shift Manager to close out the surveillance. <N> **** Equipment Description **** Computer point MVL110
396727 | CR | 20190711 |  | 4 | HV-V-27C S3 steam leak, packing or pressure seal | N | N |  | N | YES | <D> **** Detailed Description **** HV-V-27C has an estimated S3 steam leak as observed from leakage to floor on camera TG 01. Likely the pressure seal again, but could be packing. Looks the same as pre-R24 (WR 29139774). <I> **** Actions Taken **** Updated FLM map <N> **** Equipment Description **** TG 501 A5/12.7 | 02-00-HV-V-27C
396729 | CR | 20190711 |  | 3 | CBD-FT-1 change in programming not evaluated | N | Y |  | N | YES | <D> **** Detailed Description **** This is a documentation issue. During setup of CBD-FT-1 replacement in 2011(WO 02000891-02), it was identified that some elements of the CBD-FT-1 programming had been changed, and setup per the IMDS required changes. No CR was initiated for this issue, the IMDS was not updated, and no technical documentation could be located for acceptance of the change in programming. The issue was rediscovered in 2019 when replacement of CBD-FT-1 occurred under WR 29146384. CR 00391564 was initiated to updated the IMDS and CR 00391774 was initiated to update the OMM; however, no formal evaluation of the change in programming was performed. CBD-FT-1 appears to be performing as intended since the recent replacement. | 02-00-CBD-FT-1
396730 | CR | 20190711 | CAQ | D | WEA-FN-53A motor abnormally hot | Y | N |  | N | YES | <D> **** Detailed Description **** WEA-FN-53A (Div 1 Battery Rm Exhaust fan) motor was abnormally hot to the touch. This motor is usually only warm to the touch and feels very comparable to WEA-FN-53B. Div 1 battery room temp is trending normally. There does not appear to be any immediate danger of motor failure. WEA-FN-53A motor was 140F and WEA-FN-53B motor was 118F, per Infared gun. This AR/WR generated for trending purposes, mostly. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RW 525 | 02-00-WEA-FN-53A
396731 | CR | 20190711 |  | 4 | HV-V-31A S5 packing leak | N | N |  | N | YES | <D> **** Detailed Description **** HV-V-31A has an S5 packing leak, as viewed from camera TG 04. View is obstructed by ladder rung, so there's a possibility the leak is from another source. <I> **** Actions Taken **** Updated FLM map. <N> **** Equipment Description **** TG 501 | 02-00-HV-V-31A
396732 | CR | 20190711 |  | 4 | Unidentified leak from TG 471 overhead at G/6. | N | N |  | N | YES | <D> **** Detailed Description **** Unidentified leak (water dripping) from TG 471 overhead ventilation duct at G/6. There are heater vent lines in this area of the overhead that have had through wall leaks in the past. <I> **** Actions Taken **** Updated FLM map <N> **** Equipment Description **** TG 471 heater bay G/6
396733 | CR | 20190711 |  | 4 | EC-16405 mark-up for ECP-DG1/INSP-B101 incomplete |  |  |  | N | NO | <D> **** Detailed Description **** The ECP-DG1/INSP-B101 markup that was provided after EC -16405 implementation did not provide a Precaution and Limitations and Notes prior to the revised steps to provide operator awareness of operability clarification of switch positions. <I> **** Actions Taken **** Consulted Operations, added to ECP-DG1/INSP-B101 which is currently in routing. Recommend trending CR.
396734 | CR | 20190711 | CAQ | D | accumulator trouble alarm 54-35 | Y | N |  | N | YES | <C> CR reopened to cross reference additional WP 02146548, marked completion required box, then taken back to complete <D> **** Detailed Description **** received accumulator trouble alarm 54-35 due to low N2 pressure.. <I> **** Actions Taken **** OPS 2 cleared alarm. Repressurized the accumulator | 02-00-CRD-TK-125/5435
396735 | CR | 20190711 | CAQ | D | Multiple Fire/Trouble alarms all at once FCP-2 | N | Y |  | N | YES | <D> **** Detailed Description **** Board FCP-2 had fire and trouble alarms for tiles 4-1 through 4-5 and 5-1 through 5-5 come in all at once. They cleared immediately. Possible power supply anomaly. All tiles from 2 rows alarming indicates that a common component is likely the fault. No obvious problems with the components inside FCP-2. <I> **** Actions Taken **** Alarming locations were walked down by watchstanders and verified abnormal conditions did not exist. FCP-2 was investigated with no obvious culprits. <N> **** Equipment Description **** MCR FCP-2 | 02-00-FP-CP-FCP2
396736 | CR | 20190711 | CAQ | D | WMA-EHC-53A Stripped Cover Fastener Holes | Y | N |  | N | YES | <D> **** Detailed Description **** While performing WO# 02136724, one of the two new replacement cover fasteners couldn't achieve the desired torque due to the hole threads were stripped out. Also 4 of the existing cover fasteners couldn't achieve the desired torque because of stripped hole threads. <I> **** Actions Taken **** Informed Supervisor, wrote CR to document, attached a marked up picture to WO# 02136724-01 that identified which holes were bad. Noted the condition in the WO. <N> **** Equipment Description **** RW525 J4/10.5 | 02-00-WMA-EHC-53A
396737 | CR | 20190711 |  | 4 | EC-11288 had insufficient config task for PPM 16.11.1 & MWO |  |  |  | N | NO | <D> **** Detailed Description **** CR-396614, Revision required to PPM 16.1.11 and MWO was written as the MWO and PPM 16.11.1 were not updated for the new temp/humidity sensors installed per EC-11288. <I> **** Actions Taken **** Recommend trending.
396738 | CR | 20190711 |  | 4 | S5 steam leaks from BS-MANWAY-6/2 and BS-MANWAY-4/3 | N | N |  | N | YES | <D> **** Detailed Description **** Leaks have developed again at BS-MANWAY-6/2 and BS-MANWAY -4/3. Puddles are forming on the floor under each in the same location as pre-R24 (WR 29143740 and 29147385). Likely S5 leaks. <I> **** Actions Taken **** Updated FLM map <N> **** Equipment Description **** TG 490 heater bay | 02-00-BS-MANWAY-4/3,02-00-BS-MANWAY-6/2
396739 | CR | 20190711 |  | 3 | ANI Suggestion: Gap Analysis of record retention durations | N | N |  | N | NO | <D> **** Detailed Description **** Energy Northwest will perform a gap analysis of their records schedules against ANI Bulletin 15-01 for record retention durations. <I> **** Actions Taken **** CR written A gap analysis to be performed. <N> ANI identified a potential gap between ANI 15-01 Bulletin v. our records retention schedules.
396740 | CR | 20190711 |  | 4 | Control Panel fuse labels don't match drawings | N | N |  | N | NO | <D> **** Detailed Description **** WEA-RMS-CP25/TEST craft identified that the fuse labels in Control Panel WEA-CP-25 don't match the drawings and Standard fuse naming convention. Labels at the fuses and on cables attached to fuses need to be relabeled to match the drawings and Fuse database THIS may require determing and reterming wires to relabel them as well as loss of power to fuse loads. While working WO 02129877-01 IMPLEMENT DESIGN CHANGE FOR <I> **** Actions Taken **** notified supervisor. Initiated this CR <N> **** Equipment Description **** WEA-CP-25 (W 487' Q2/16.0)
396741 | CR | 20190711 |  | 3 | SOP-HVAC/RW-START enhancment | N | N |  | N | NO | <D> **** Detailed Description **** SOP-HVAC/RW-START (Section 5.2, WEA-SR-25 Startup) requires enhancement/clarifications. See attached EDMS for proposed changes (See pages 9-11. Changes in RED). <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** SOP-HVAC/RW-START
396742 | CR | 20190711 |  | 3 | Grease supplied in COND-M-P/4 does not match purchase order | N | N |  | N | YES | <D> **** Detailed Description **** The purchase order for the new motor for COND-P-4 specified Mobil EP grease. The motor came with EM grease. The two are not compatable. Per the component engineer, the EM grease is a better motor grease and is stocked on site. <I> **** Actions Taken **** Called swing shift maintenance supervisor to inform him of the error and to not add EP grease. A plate on the motor states to use EM grease. | 02-00-COND-M-P/4
396743 | CR | 20190711 |  | 3 | FP-P-110 run LT 30 minutes | N | Y |  | N | NO | <D> **** Detailed Description **** FP-P-110 was not run for its required 30 minutes during the monthly surveillance done under WO 02136816. The operator transcribed the start time incorrectly which led them to believe it was started 10 minutes earlier than it was. The inadequate run time was caught during the review of the surveillance. This required FP-P-110 to be run again to meet the 30 minute required run time per PPM 15.1.4. <I> **** Actions Taken **** Discussed with crew management and operator. Reperforming PPM 15.1.4 to met 30 minute run time. <N> FP-P-110 surveillance 15.1.4 was completed SAT.
396744 | CR | 20190711 | CAQ | D | Accumulator Trouble CRD-HCU-4259 | Y | N |  | N | YES | <D> **** Detailed Description **** MCR received Accumulator Trouble on CRD-HCU-4259. The issue was low N2 pressure and was corrected without issue per SOP-CRD-HCU. | 02-00-CRD-HCU-4259
396745 | CR | 20190712 | CAQ | D | N2 Leak on CRD HCU 42-59 Near P6 | Y | N |  | N | YES | <C> CR reopened to cross reference additional ARs 397047, 397130 and WP 02146549, marked completion required box, then taken back to complete <D> **** Detailed Description **** There is a nitrogen leak from the connection between the block and the P6 pipe nipple. The HCU bled down to the alarm setpoint 8 days after its last recharge. <I> **** Actions Taken **** Repressurized HCU Informed MCR | 02-00-CRD-HCU-4259
396746 | CR | 20190712 | CAQ | D | LPRM 32-49B failed upscale | Y | N |  | N | YES | <D> **** Detailed Description **** On 7/11/19 at 23:33 the control room received P603-A8 drop 2-5 "LPRM UPSCALE" for LPRM 32-49B reading steady at 130.0%. Control room staff verified the failed reading, entered ABN-LPRM and bypassed the LPRM with HV-OFF. <I> **** Actions Taken **** Informed CRS and took actions per ABN-LPRM | 02-00-LPRM-DET-32/49B
396747 | CR | 20190712 |  | 4 | Flocculator did not trip on High Turbidity condition | N | Y |  | N | YES | <D> **** Detailed Description **** Observed Flocculator running with outlet turbidity at 0.3 NTU (as seen on PWC-TBIT-2). This did not match with outlet turbidity at PWC-XR-1 (Yokogawa) which read 0.004 NTU. The Yokogawa feeds the Flocculator trip so this input needs to be fixed. Flocculator was shutdown using SOP -FLOCCULATOR-SHUTDOWN, step 5.1.1. Flocculator level was unusually high and bubbles were seen emerging from the charcoal bed after stopped (stopped after approximately 5 minutes). High Turbidity Shutdown switch was verified in ON. <I> **** Actions Taken **** Shutdown Flocculator with SOP-FLOCCULATOR-SHUTDOWN, step 5 .1.1. Notified Chemistry of high turbidity condition. Verified High Turbidity Shutdown switch was in ON. | 02-00-PWC-XR-1
396748 | CR | 20190712 | CAQ | D | CIA-V-104A Leaking | Y | N |  | N | YES | <D> **** Detailed Description **** CIA-V-104A, the isolation for backup bottle CIA-TK-20A, has a nitrogen leak from the bonnet. The leak, while unquantifiable in nature, is minor enough that a fully charged bottle will probably last a week or more before needing to be replaced. CIA-TK-20A is being left in service due to CIA-TK-3A being isolated for excessive leakby. <I> **** Actions Taken **** Informed MCR | 02-00-CIA-V-104A
396749 | CR | 20190712 |  | 3 | PPM 15.1.4 enhancement | N | N |  | N | NO | <D> **** Detailed Description **** PPM 15.1.4, step 7.4, requires to verify FP-P-110 is at ambient condition. This step is also a $ step which means that the step must be completed SAT for the surveillance to pass. Verifying that a component is at an ambient condition should not be a prerequisite to a component meeting its surveillance test requirements. Verifying that a component is at ambient condition should be used as a means to ensure that unacceptable pre-conditioning is not taking place. By comparison, PPM 15.1.3, Step 7.4, verifies FP-P-1 is at ambient conditions but is not a $ step. Recommend removing the $ reference to step 7.4 in PPM 15.1.4
396750 | CR | 20190712 |  | 3 | Main Generator hydrogen dew point 11 degree Celsius | N | N |  | N | YES | <D> **** Detailed Description **** The Main Generator gas dryer was placed in service approximately 3 weeks after the main generator was synced to the grid due to clearance orders in place to repair leaks discovered during the air test in R 24. Hydrogen dew point indicated positive 11 degrees Celsius when Main Generator gas dryer was placed in service. Normal operation Dew point is between negative 70 and negative 80 degree Celsius. Hydrogen compressor was started to lower dew point. There is a note in SOP-H2/CO2-OPS that Generator gas dew point should be LT +7 degree Celsius during normal operation. Another note state The dryer may be isolated for up to 5 days. Recommend evaluating if having the main generator gas dryer out of service for 3 weeks had any unforeseen consequences for the main generator. <I> **** Actions Taken **** Discussed this with the CRS and SM | 02-00-H2-DY-1
396752 | CR | 20190712 | CAQ | D | SFS-STORM-003 Displays YELLOW | Y | Y |  | N | YES | <D> **** Detailed Description **** During performance of OSP-SFS-D101, SFS-STORM-003 was found to display YELLOW. This condition has been long standing. The previous WR written to identify/correct this issue have been CLOSED/COMPLETED by crediting the completion of ICP-SFS-A301. This has not satisfactorily addressed the YELLOW condition. (Or OSP-SFS-D101 needs to be changed to address when a WR truly needs to be generated.) This WR written per OSP-SFS-D101. <I> **** Actions Taken **** Informed MCR generated new WR. <N> **** Equipment Description **** TG 471W | 02-00-SFS-STORM-003
396753 | CR | 20190712 | CAQ | D | SFS-STORM-029 Displays YELLOW | Y | Y |  | N | YES | <D> **** Detailed Description **** During performance of OSP-SFS-D101, SFS-STORM-029 was found to display YELLOW. This condition has been long standing. The previous WR written to identify/correct this issue have been CLOSED/COMPLETED by crediting the completion of ICP-SFS-A301. This has not satisfactorily addressed the YELLOW condition. (Or OSP-SFS-D101 needs to be changed to address when a WR truly needs to be generated.) This WR written per OSP-SFS-D101. <I> **** Actions Taken **** Informed MCR. Generated new WR <N> **** Equipment Description **** TG471W | 02-00-SFS-STORM-029
396754 | CR | 20190712 |  | 3 | WEA-FN-1C current imbalance | N | N |  | N | YES | <D> **** Detailed Description **** While taking current readings in support of WO 02115461 for WEA flow rate CFT, it was noted that on WEA-FN-1C, the amperage taken on C phase was approx. 33% higher than A & B phases. This fan appears to operate with no issues, and this CR is being generated primarily for trending. <I> **** Actions Taken **** Notified MCR and generated CR <N> **** Equipment Description **** RW 487 (J5/16) | 02-00-WEA-FN-1C
396755 | CR | 20190712 |  | 3 | Skype For Business system outage. |  |  |  | N | NO | <D> **** Detailed Description **** Skype For business system was unavailable to users from approximately 9:20pm Thursday July 13th through 9:30am Friday July 12th. During scheduled system maintenance the redundant skype servers not being working on services failed. This impacted the ability for any users to log into skype to use the instant message or meeting functions. <I> **** Actions Taken **** Attempted recovery Thursday evening using known recovery strategies identified in ISDI-MAINT-87 failed. Supervisor and IS Duty officer notified of the issue. A Support Case was opened with the vendor. Contact was made with the vendor Friday morning and the issues was resolved. All Skype services became available at approximately 9:30am Friday 7/12.
396756 | CR | 20190712 | CAQ | D | WMA-FL-52A filter is at end of roll | N | N |  | N | YES | <C> MRT Change request: CR 396756 Severity moved from NON-CAQ Severity 4 to CAQ D/Trend Repair. <D> **** Detailed Description **** WMA-FL-52A filter end of roll alarm came in for Board P in the MCR. Local indication shows End of Roll. <I> **** Actions Taken **** Filter was advanced locally and the end of roll alarm remains in. <N> **** Equipment Description **** RW 525' Div 1 Hvac room | 02-00-WMA-FL-52A
396757 | CR | 20190712 |  | 4 | RRC-TR-ASD/A/1 pressure is above max spec. | N | N |  | N | YES | <D> **** Detailed Description **** RRC-TR-ASD/A/1 pressure is reading 4.25 psig. Max spec. per the OPS-4 logs is 4.0 psig. Please restore pressure to normal operating band. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** ASD | 02-00-RRC-TR-ASD/A/1
396758 | CR | 20190712 |  | 4 | Steam leak in the vincinity of HV-V-31A on MSR 1A. | N | N |  | N | YES | <C> DUPLICATE OF AR 396731 <D> **** Detailed Description **** There is approximately a foot long plume of steam pointing down towards the floor in the vicinity of HV-V-31A on MSR 1A. Cannot get exact location because of a ladder rung blocking the camera (can be viewed on 501' TG #4 camera). <I> **** Actions Taken **** Initiated CR <N> **** Equipment Description **** Vicinity of HV-V-31A on MSR 1A | 02-00-HV-V-31A
396759 | CR | 20190712 | CAQ | D | FP-V-169 packing leak. | N | Y |  | N | YES | <D> **** Detailed Description **** FP-V-169 packing is leaking at a rate of about 20 drops per second when open. This leakage is following the performance of FP-P-110 monthly run per 15.1.4. Please adjust packing. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** Flocculator bldg. | 02-00-FP-V-169
396762 | CR | 20190713 | CAQ | D | CMS-SR-20 fan will not start. | Y | N |  | N | YES | <D> **** Detailed Description **** CMS-SR-20 fan failed around 2320 07-12-19. Attempts to start CMS-FN-20 were unsuccessful. The sample rack and RM -2000 have power . Please investigate why the pump for CMS-SR-20 will not start. | 02-00-CMS-FN-20
396763 | CR | 20190713 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm at 07:20 on 7/13/19. Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E -TR-S A: 240KV B: 240KV C: 240KV. E-TR-B A: 119KV B: 119KV C: 118KV. The following sensor was tripped and is reset: J7 - 500KV Neutral Ground Overcurrent. BPA Dittmer reports the cause was a momentary relay actuation on the ASHE-SLATT 500KV line involving a single pole. Line automatically reclosed with no equipment damage noted. The 115KV and 230KV systems were not affected. 500KV voltage at ASHE is 539KV. <I> **** Actions Taken **** Submitted CR to document occurrence. Notified the CRS and Shift Manager.
396764 | CR | 20190713 |  | 3 | Calculation Form 18645 R9 does not meet ENW expectations |  |  |  | N | NO | <D> **** Detailed Description **** Calculation cover page form 18645 R9 is not user friendly. The columns do not align, there are extra lines, the title block (header) doesn't transfer from page to page. This revision has cost additional time to make a quality product.
396765 | CR | 20190713 | CAQ | D | FP-B0-1B battery swelling | N | Y |  | N | YES | <C> CR reopened to cross reference additional WP 02146648, marked completion required box, then taken back to complete <D> **** Detailed Description **** The positive terminal post is being pushed up. The top of the case is showing a slight bulge <I> **** Actions Taken **** Informed CRS, supervisor, and fire protection engineer <N> **** Equipment Description **** Circ Water Pump House | 02-00-FP-B0-1B
396766 | CR | 20190713 |  | 3 | PPM 10.25.132 MOV Diagnostic Procedure |  |  |  | N | NO | <D> **** Detailed Description **** PPM 10.25.132 MOV Diagnostic Procedure does not contain wording regarding identification of parasitic loads in diagnostic traces. This is a requirement specifically for EPRI PPM valves. This CR is administrative and does not impact or affect any plant components. <N> Revision request uploaded to the procedure database. Link located in the EDMS of this AR.
396767 | CR | 20190713 |  | 3 | Private Aides to Navigation River buoy floating down river | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The Benton County River patrol found one of the PATON river buoys floating down river. Benton County Sheriff notified the Shift Manager. The missing buoy is the submerged concrete structure furthest North on the river. <I> **** Actions Taken **** E&RP supervision notified. USCG Notified per 33 CFR 66.01-50, Protection of Private Aids to Navigation. OI-34 notifications complete. <N> Environmental Services (J LePage) inspected the Energy Northwest PATONs at about 5:30 pm on Monday 7/15/19 and found all three EN green-can PATONS in the Columbia river at their assigned locations. The buoy recovered by Benton County Sheriff was a white foam buoy, tentatively claimed by the City of Pasco. E&RP contacted the US Coast Guard (Tim Westcott, via phone call and email) to withdraw the missing buoy notification. No further actions required.
396768 | CR | 20190713 |  | 4 | T-4 sump pillows need replacement. | N | N |  | N | YES | <D> **** Detailed Description **** T-4 sump pillows are very dirty and appear to be 1/2 submerged. Identified while performing WO#02136835-01 <I> **** Actions Taken **** Notified supervisor and annotated on WO. <N> **** Equipment Description **** NW condenser bay.
396769 | CR | 20190713 |  | 4 | OG Analyzer room TG 441 needs to be relamped. |  |  |  | N | YES | <D> **** Detailed Description **** OG Analyzer room lights are burned out on the east side of the room ( B side ), making it impossible to obtain OPS 3 logs for the B analyzer using the installed camera. Please relamp. Note: this is a high rad area. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 441SW
396772 | CR | 20190714 |  | 3 | MS-ST-6A could not be completed. | N | N |  | N | YES | <D> **** Detailed Description **** Working MS-ST-6A 02093410-01, encountered water, to steam leakby , causing strainer flange to be retightened to stop the steam. after retorque of the bolts, the temperature of the piping was at 390 degrees. also MS-ST-5A 02084402-01 temperatures were elevated . did not want to go forward with work. MS-ST-4A 02084403-01 Was completed with aprox 9 gallons of hot water drained and still dribbling while strainer replacement was completed. | 02-00-MS-ST-6A
396773 | CR | 20190714 |  | 4 | WCH-V-256 leaking approx 20 drops/min | N | N |  | N | YES | <D> **** Detailed Description **** WCH-V-256 leaking approx 20 drops/min This is the drain valve from the WCH chill water expansion tank (WCH-TK-51) <I> **** Actions Taken **** Installed tygon to drain Informed Laborers Informed MCR | 02-00-WCH-V-256
396774 | CR | 20190714 |  | 4 | Water leak along the shaft of Flocculator paddle wheel | N | N |  | N | YES | <D> **** Detailed Description **** Leakage has significantly increased from the flocculator paddle wheel shaft. See video for leakage. Shaft/seal needs maintenance. <I> **** Actions Taken **** Notified CRS | 02-00-PWC-FU-1
396775 | CR | 20190714 | CAQ | D | LPRM Detector 08/49A Failed upscale | Y | N |  | N | YES | <D> **** Detailed Description **** LPRM Detector 08/49A failed downscale. CR for trending. Attached ABN-LPRM procedure, EDNA plot and MON run following bypass of detector. <I> **** Actions Taken **** Bypassed detector with HV off. Uploaded ABN-LPRM, EDNA Trace and MON Run to EDMS. Correction to the text of the CR: LPRM 08-49A failed upscale, not downscale. | 02-00-LPRM-DET-08/49A
396776 | CR | 20190714 |  | 4 | Charger fault on Flocculator bldg emergency lighting unit | N | N |  | N | YES | <D> **** Detailed Description **** Emergency lighting unit in the flocculaor building service alert light blinking three times, indicating a charger fault. See attached video. <I> **** Actions Taken **** Notified CRS <N> **** Equipment Description **** Flocculator Building
396777 | CR | 20190714 |  | 4 | Scaffold blocking fire equipment | N | N |  | N | NO | <D> **** Detailed Description **** Scaffold blocking fire equipment. When scaffold is installed around RHR 'B' floor plugs on RX 471 West side, it completely blocks access to the smoke removal trunks required for use with REA-FN-16 . Recommend evaluate moving trunk storage locker <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** REA-FN-16 smoke removal trunk cabinet RX 471 West. No fire fighting capabilities are impacted by this condition.
396778 | CR | 20190714 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm at 15:24 on 7/14/19. Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 239KV B: 240KV C: 240KV; E-TR-B A: 120KV B: 119KV C: 119KV. The following sensors were tripped and are reset: J7- 500KV Neutral Ground, J15 - 230KV Undervoltage. BPA reports the following: The cause was a trip with automatic closure on the Vantage - Hanford #1 500 KV line. (There is an active range fire in the area). Relaying involved a single pole with automatic re -closure. There is no known equipment damage at this time / no emergent line outage required. The 115 KV and 230 KV systems were unaffected. Grid frequency is stable and 500 KV system voltage at Ashe substation is 537KV. BPA also reports that line crews have been dispatched to the area (estimated location is 7.9 miles from Vantage substation) <I> **** Actions Taken **** Submitted CR to document the occurrence. Notified the CRS and Shift Manager.
396779 | CR | 20190714 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm. The a | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. The alarm was due to the J7 sensor [500KV neutral ground overcurrent] J12 [SM8 Undervoltage] and J15 [230KV Undervoltage]. The J07, J12 and J15 sensors have been reset. E-TR-S and E-TR-B voltages are 239/239/238 kV and 120/119/119 kV respectively. BPA Munro reports that the #1 Vantage -Hanford 500KV line tripped open and had to be closed. There was not a need for an emergent outage and a RAS was initiated. All plant controllers and equipment exhibited normal operation. <I> **** Actions Taken **** Informed CRS/SM
396780 | CR | 20190714 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm. The a |  |  |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. The alarm was due to the J12 [SM8 Undervoltage] and J15 [230KV Undervoltage]. The J12 and J15 sensors have been reset. E-TR-S and E-TR-B voltages are 239/239/238 kV and 120/119/119 kV respectively. BPA Munro reports that the #1 Vantage -Hanford 500KV line tripped open and had to be closed. There was not a need for an emergent outage and a RAS was initiated. All plant controllers and equipment exhibited normal operation. <I> **** Actions Taken **** Informed CRS/SM
396781 | CR | 20190714 |  | 4 | Slop barrel in RFT B room found overflowing. | N | N |  | N | YES | <D> **** Detailed Description **** Found the slop barrel in RFT B room overflowing. HP was informed and laborers cleaned it up and indicated that the barrel filled much quicker then was previously noted. <I> **** Actions Taken **** Initiated this CR <N> **** Equipment Description **** North side of RFT B room. | 02-00-RFW-DT-1B
396782 | CR | 20190715 |  | 4 | Door C-511 lock Not working as designed | N | N |  | N | YES | <D> **** Detailed Description **** Radwaste Door C-511 locking mechanism is not working. <I> **** Actions Taken **** Contacted Operations and generated CR/WR. | 02-00-W-DOOR-C511
396788 | CR | 20190715 |  | 4 | FD-P-12 has no indication locally or at the breaker. | N | N |  | N | YES | <D> **** Detailed Description **** Took the CS for FD-P-12 (T-1 sump ) to run and the white light at BD-RAD-41 went out. Investigated the breaker at MC 2P (3D) and found both lights out. Replaced bulbs and depressed overload reset with no change in status.Suspect fuses cleared. <I> **** Actions Taken **** Returned FD-P-12 CS to auto and informed supervisor. <N> **** Equipment Description **** TG 441 E. | 02-00-FD-P-12
396789 | CR | 20190715 |  | 4 | HIRD issues engineering and human resources department |  |  |  | N | NO | <C> This issue will be resolved by the Employee Concerns Program (ECP). No additional actions are necessary in the Corrective Action Program. If actual deficient conditions are identified during ECP investigation, additional CR's will be written. <D> documenting previous HIRD incident by senior management see edms <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
396790 | CR | 20190715 |  | 4 | HIRD induced employee discipline |  |  |  | N | NO | <C> This issue will be resolved by the Employee Concerns Program (ECP). No additional actions are necessary in the Corrective Action Program. If actual deficient conditions are identified during ECP investigation, additional CR's will be written. <D> **** Detailed Description **** see edms
396791 | CR | 20190715 |  | 4 | management directed Clearance order violation, etc |  |  |  | N | NO | <C> This issue will be resolved by the Employee Concerns Program (ECP). No additional actions are necessary in the Corrective Action Program. If actual deficient conditions are identified during ECP investigation, additional CR's will be written. <D> **** Detailed Description **** management directed Clearance order violation, management lack of qualifications, upward accountability, other issues see edms
396792 | CR | 20190715 |  | 4 | Budget prioritization issues |  |  |  | N | NO | <C> This issue will be resolved by the Employee Concerns Program (ECP). No additional actions are necessary in the Corrective Action Program. If actual deficient conditions are identified during ECP investigation, additional CR's will be written. <D> see edms <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
396793 | CR | 20190715 |  | 4 | Engineering ratings meeting |  |  |  | N | NO | <C> This issue will be resolved by the Employee Concerns Program (ECP). No additional actions are necessary in the Corrective Action Program. If actual deficient conditions are identified during ECP investigation, additional CR's will be written. <D> **** Detailed Description **** see edms
396794 | CR | 20190715 |  | 4 | fatigue rules for engineers |  |  |  | N | NO | <C> This issue will be resolved by the Employee Concerns Program (ECP). No additional actions are necessary in the Corrective Action Program. If actual deficient conditions are identified during ECP investigation, additional CR's will be written. <D> **** Detailed Description **** see edms
396795 | CR | 20190715 |  | 4 | ERO issues, field teams |  |  |  | N | NO | <C> This issue will be resolved by the Employee Concerns Program (ECP). No additional actions are necessary in the Corrective Action Program. If actual deficient conditions are identified during ECP investigation, additional CR's will be written. <D> **** Detailed Description **** see edms
396796 | CR | 20190715 |  | 4 | closing CAQ s to the maintenance process |  |  |  | N | NO | <C> This issue will be resolved by the Employee Concerns Program (ECP). No additional actions are necessary in the Corrective Action Program. If actual deficient conditions are identified during ECP investigation, additional CR's will be written. <D> **** Detailed Description **** see edms
396798 | CR | 20190715 | CAQ | D | FP-V-76 seat leakage | N | N |  | N | YES | <D> **** Detailed Description **** FP-V-76 exhibited seat leakage when attempting to isolate FP-AO-SGT/66 for maintenance. This required expansion of the clearance boundaries. Repair or replace FP-V-76. <I> **** Actions Taken **** Shift Manager and Work Week manager were informed. Clearance boundaries were expanded for planned maintenance. . Further investigation revealed that FP-V-SGT/61 was the cause of the system in-leakage, not FP-V-76. WR 29150490 was updated. . | 02-00-FP-V-76
396800 | CR | 20190715 |  | 3 | PCR: PPM 1.3.79 Section 4.3 |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate PPM 1.3.79 Section 4.3 for usefulness of the Monthly Reactivity Management Event Review Subcommittee. Note states that an email is an acceptable means in lieu of a meeting. Reference AR-235787. <I> **** Actions Taken **** Submitted AR.
396806 | CR | 20190715 |  | 4 | DLR ran through xray machine |  |  |  | N | NO | <D> **** Detailed Description **** DLR was ran through Xray machine. Lanyard was broken so individual clipped badge onto his shirt, placed broken lanyard inside his personal bag which still had DLR attached. <I> **** Actions Taken **** Contacted supervision and HP. <N> Williams Plant Services.
396807 | CR | 20190715 | CAQ | C | Standard found out of tolerance | N | N |  | N | NO | <C> CR 396807 re-opened and re-assigned to AR-CALSERV at the request of Calibration Services. <D> **** Detailed Description **** Calcode #0063401 Heise Model ST-2H was found OOT and adjusted. No Plant impact. Used for atmosheric pressure only. Not a calibrated paramenter. NOD# 20-02 <N> No plant impact as stated in the AR. No actions required by EFIN.
396811 | CR | 20190715 |  | 4 | TRS BPD C â€“ Recommend Coarse Adjustment in R25 | N | N |  | N | YES | <D> **** Detailed Description **** Note: Values obtained during this PM are acceptable per the BPA SPC Engineer and all three phases of the TRS Bushing Potential Devices are fully functional. This CR is to drive changes to facilitate future adjustments if needed. During the performance of WO 02119238 ETRSBPDABCE702: BPA CALIBRATE BUSHING POTENTIAL DEVICES, E-TR-BPDS/C (C-Phase of the Bushing Potential Device for the Startup Transformer) had acceptable values for Line-To-Line and Line-TO-Ground however it could have been adjusted to get closure to target values. Medium and fine adjustments were already maxed out. A change to the coarse adjustment is required to make any further changes. A coarse adjustment requires a 230 kV line outage and high-side grounded to make the changes. Recommend performing a coarse adjustment in R25 and to perform the TRS BPD calibration PM for the PMT (PMRQ 18826-01). <I> **** Actions Taken **** Contacted System Engineer and Supervision. <N> This device does not impact operability of E-TR-S. The bushing potential devices are used for metering purposes to determine how much power is being used from the electrical grid (or supplied to the electrical grid when a diesel generator is running). The adjustments available do not impact the 230 kV system or the ability of E-TR-S to supply required loads in an accident condition. | 02-00-E-TR-BPDS/C
396812 | CR | 20190715 |  | 3 | Main Turbine bearing 7 vibration exceeded 7 mils | N | N |  | N | YES | <D> **** Detailed Description **** On Saturday morning, 7/13/2019, steady state vibrations on main turbine bearing 7 reached 7 mils. The trend is still slowly rising. This threshold triggered the next action point in ODMI 395842. <I> **** Actions Taken **** Increased monitoring of bearing 7 vibrations to hourly. These are captured in the CRO1 temporary logs. Notified management via the weekend production phone call. A plan is needed for a downpower to perform a balance shot on the main turbine. | 02-00-MS-DT-1C
396813 | CR | 20190715 |  | 4 | OG-RF-20B Oil Level High | N | N |  | N | YES | <D> **** Detailed Description **** Level was observed at approximately 75% up the sight glass when on rounds. Logs state to write a CR if level is GT 50% up sight glass. Please lower level. <I> **** Actions Taken **** Notified SSS | 02-00-OG-RF-20B
396814 | CR | 20190715 |  | 3 | Impact7a statements not showing correctly in eWP |  |  |  | N | NO | <D> **** Detailed Description **** One of the OPS crews has identified thata some impact7a sheets arent showing up in eWP. Two examples I have found are 02092185- impact is blank in eWP and filled out in portal. 02117301 the eWP version is an old version and the portal-j version is updated. <I> **** Actions Taken **** contacted eWP help line. Advised the affected crew to look in portal <N> The PM Package was built in DataGlance on 03/02/18. FYI - PM Packages are built in Asset Suite 2 years prior to the due date and will be built in DataGlance once the package goes to Approved or Ready. During the 2 years after the package was created, Planning is completed. So when the package is ready for Walkdown/Working in DataGlance, a package validation needs to be performed in DataGlance to bring in any new, updated, new revisions work instructions or documents. In the case of WO 02092185, a validate was not performed on the package prior to the CR being written on 07/15/19, a validation was not performed until 07/16/19 which updated the Impact7a instruction as well as bringing over new instructions and updating documents.
396816 | CR | 20190715 |  | 4 | OG-RF-20A D/P Low | N | N |  | N | YES | <D> **** Detailed Description **** Refrigeration unit "A" compressor oil pressure (GY-PI-20A3) minus "A" compressor suction pressure (GY-PI-20A1) was 22 psid while taking rounds. Band is 30-75 psid. <I> **** Actions Taken **** Notified SSS | 02-00-OG-RF-20A
396817 | CR | 20190715 |  | 3 | R24LL - CRs closed to trend without actions taken |  |  |  | N | NO | <D> **** Detailed Description **** Currently there are 440 R24LL CRs, 192 of which were closed to Trend. A review revealed that about 45 of them should have been assigned to a department to take action or evaluate as a lessons learned for continuous improvement to our processes. CRG closed these CRs to trend because 1) no single department took ownership, therefore 2) an assumption was made by CRG that the outage critique process would identify any specific actions needed later and the CR could be trended. This assumption was inaccurate. The CRs will need to be reopened and actions developed to address the conditions documented. Assign this CR as a 3/AR-OTMG. <I> **** Actions Taken **** Discussed with CAP supervisor, PSO CIC, CRG Chair, and Outage Manager. Outage Management will work with CAP to reopen the CRs and create actions where needed.
396819 | CR | 20190715 |  | 4 | OG Glycol Temp. Low OOS | N | N |  | N | YES | <D> **** Detailed Description **** On rounds glycol temperature was 32F as read on GY-TIC-17. Band is 32.5-35.5F. <I> **** Actions Taken **** Notified SSS | 02-00-GY-TIC-17
396822 | CR | 20190715 |  | 3 | R25 procedure change SOP-ELEC-DIV1-TEMPPOWER |  |  |  | N | NO | <D> **** Detailed Description **** Change two sections in SOP-ELEC-DIV1-TEMPPOWER for TP installation in any Mode ref AR-EVAL 396821. Update prerequisites and make editorial changes. Uploaded in EDMS <I> **** Actions Taken **** Wrote CR
396823 | CR | 20190715 |  |  | Emergency Notification CRASH to Benton County did not work |  |  |  | N | YES | <D> During test of the Emergency Notification CRASH Syatem, the line to Benton County did not make contact. Benton County was contacted on the commerical line to ensure communication link was maintained. <I> Telecom notified, looking into problem <N> none
396825 | CR | 20190715 |  | 4 | Mechanical rep for 0810 C/O Mtg late & not prepared |  |  |  | N | NO | <D> **** Detailed Description **** At the 0810 Carrover Meeting, there was no representative from the Mechanical shop. The WWM had to go the shop to find someone to attend. THis delayed the meeting by about 5 minutes. A representative was finally sent, but he was not prepared for the meeting. He did write down actions that he needed to follow up on to provide us the information that we needed. <I> **** Actions Taken **** I followed up with the Acting Mechnical Manager, who stated that he had forgotten to send someone to the meeting as he had to attend EP Training. Coaching was provided and accepted.
396826 | CR | 20190715 |  | 4 | PCSC Committee Quorum Not Met |  |  |  | N | NO | <D> **** Detailed Description **** 7/15/19 PCSC Committee meeting quorum was not met. Chemistry representation was absent with no communications. <I> **** Actions Taken **** initiate CR for trending
396827 | CR | 20190715 |  | 3 | R24 LL: Week after the Outage should not contain WO tasks |  |  |  | N | NO | <D> **** Detailed Description **** The week directly after the Outage should not contain any work except for items that will go late in that week. A lot of effort was spent on organizing the June 17 WW, the first daily work week after the R24 Outage. When the outage went longer than expected, a lot of WOs had to be quickly re-scheduled with some WOs having to complete within the week. This led to an error-likely situation. It would be better to not schedule anything within the week. We can always pull work forward and there are usually many tasks left over from the outage that need to be addresseed in a timely manner to help FIN out. This would keep all of the craft gainfully employed, while minimizing our risk level with re-scheduling things at the last minute to accommodate the changing outage schedule. <I> **** Actions Taken **** Discussed this issue with Plant Management. Providing this recommendation.
396829 | CR | 20190715 |  | 3 | R24 LL: Planning needs a formal plan to not fall behind |  |  |  | N | NO | <D> **** Detailed Description **** During the R24 Outage, Planning fell behind their milestones for preparing work packages to be worked in weeks after the outage. Planning should develop a plan for future outages to prevent this from occuring again. QA documented an example of this in CR 396152. <I> **** Actions Taken **** Discussed this issue with Plant Management.
396832 | CR | 20190715 |  | 4 | Sludge and corrosion products found in TSW-HX-6B | N | N |  | N | YES | <D> **** Detailed Description **** During performing clean and inspect PM of TSW-HX-6B performed under WO 02111651, lot of corrosion products and sludge were found blocking some of the HX tubes. About 7 tubes on the Inlet/Outlet side and 8 on the Reversing side were blocked by those materials. The temperature trending data donâ€™t show performance issue with the heat exchanger when it was in service. The heat exchanger tubes are going to be cleaned. This is for trending only. <N> **** Equipment Description **** T441 The tubes are cleaned as part of WO 02111651 instructions and no further actions are needed. | 02-00-TSW-HX-6B
396834 | CR | 20190715 | CAQ | D | Emergency Notification CRASH to Benton County did not work | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During test of the Emergency Notification CRASH System, the line to Benton did not make contact. <I> **** Actions Taken **** Benton County was contacted on the commerical line to verify Notification Function was maintained. CGS Telecom was notified and commenced investigation. . The phone swith port used for CRASH was found inoperable and required to be reset. Broke fix and tested good with Bendon County.
396835 | CR | 20190715 | CAQ | C | B.5.b trailer inventory deficiencies, WO #02139440 | N | Y |  | N | YES | <D> **** Detailed Description **** See EDMS Docs for description. <I> **** Actions Taken **** 1. Replaced copy of SOP-FP-TRUCK-OPS with current revision. 2. Relocked and RESEALED (with red tamper seals) the left gang box IAW work order instructions. 3. Notified shift management of deficiencies. <N> **** Equipment Description **** Building 600
396837 | CR | 20190715 |  | 3 | As found wiring for FP Zone 1 not per drawing | N | N |  | N | NO | <D> **** Detailed Description **** During detector changes for Fire Protection zone 1, per WO# 02126624-01, Craft noted that the as found wires spliced between detectors 1-6 and 1-7 (for detectors 1-6a and 1-6b) did not match the detail shown on drawing 217-00,84,23. The drawing shows the following detectors connected in series; 1-6, 1-6a, 1-6b, 1-7. However, based on the wire labeling, the detectors were connected as follows; 1-6, 1-6b, 1-6a, 1-7. The circuit is currently out of service for rework of the detectors and this configuration would not have affected operation of the detectors - drawing configuration only. <I> **** Actions Taken **** Notified Engineering and wrote CR. Suggest wiring the detectors as the drawing shows, once detector replacement is complete.
396838 | CR | 20190715 |  | 3 | Degraded channel heads on TSW-HX-6B | N | N |  | N | YES | <D> **** Detailed Description **** During performing clean and inspect PM of TSW-HX-6B performed under WO 02111651, the inlet/outlet and reversing channel heads were found to be degraded along the edge of the sealing surfaces. One location on the inlet/outlet head that shows a lost material (about 1/8â€ deep). The gasket is still capable of sealing so thereâ€™s no need to repair during this maintenance window. Recommend action to HX engineer to evaluate the need to add replacing both heads to the next maintenance window or to repair (weld-up then machining) the existing head while installed. | 02-00-TSW-HX-6B
396839 | CR | 20190715 |  | 4 | XD 6 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** XD 6 failed its 1600 test and needs maintenance. notify security prior to work. <I> **** Actions Taken **** failed test, notified supervision, CR/WR generated <N> **** Equipment Description **** Located in the PAAP | 02-00-SEC-XD-6
396840 | CR | 20190715 |  | 4 | foriegn material found in starter contactor | N | N |  | N | YES | <D> **** Detailed Description **** During performance of 10.25.187E in work order 02094182-01 a piece of wood was found in the contactor internals of COND-42-1D2B. <I> **** Actions Taken **** Removed foriegn material, informed supervisor, initiated CR. | 02-00-COND-42-1D2B
396841 | CR | 20190715 |  | 4 | DEH fluid â€“ OEM recommended limits exceeded (x2) | N | N |  | N | YES | <D> **** Detailed Description **** Lab results for a DEH fluid sample taken on 02July2019 returned two values that exceeded a DEH fluid OEM recommended limit. Both were related to high particulate count for the given size range. Particle count for a 100ml sample should be: 5-10 Micron - LT 9700 10-25 Micron â€“ LT 2680 The sample for these particle sizes returned counts of 14632 and 3876 particles, respectively. These values do not exceed the Main Turbine OEM limits. Section 4.4.3.8 and the following [Table 4-24] provide Turbine OEM particle count recommendations. For a Siemens/Westinghouse unit such as CGS the limits for 5-10 micron particles is 24,000 and a count of 5,360 for the 10-25 micron sized particles. [See document in EDMS.] Trend information: This is the first occurrence this cycle. Continue to monitor, write CRs on filters with high dP and replace. <I> **** Actions Taken **** Reviewed turbine OEM limits Informed supervisor | 02-00-DEH-TK-2
396842 | CR | 20190715 |  | 4 | PC SYS STAT TROUBLE Alarm | N | N |  | N | NO | <D> **** Detailed Description **** At 1647 a PC SYS SAT TROUBLE alarm came in on the HSSF-CHEM pannel. <I> **** Actions Taken **** Per procedure CI-14.4 the CRS was notified and this CR was written <N> **** Equipment Description **** HSSF-CHEM pannel
396843 | CR | 20190715 |  | 3 | Security Comp DMP file exports not transferring to corp net | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Data diode failed and prevented transfer of DMP files to corp network <I> **** Actions Taken **** Restarted diode, ran manual exports, Comp Eng working on configuring scheduled exports
396844 | CR | 20190715 |  | 4 | WOA-FL-1 not advancing properly. | N | N |  | N | YES | <D> **** Detailed Description **** WOA-FL-1 is bunched up in the guide screen. Please adjust. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** RW 487 | 02-00-WOA-FL-1
396845 | CR | 20190715 |  | 3 | Model Work Order needs revised |  |  |  | N | NO | <D> **** Detailed Description **** While performing quarterly vibration monitoring on WMA fans electricians noted in the work steps with an annotation *1 that there is no vibration route for the following EPNs (WMA-FN-54B or WEA-FN-53B). The work step has a checklist, where the craft mark with a "check" when data has been obtained on the applicable EPN. Only certain WMA/WEA fans have route data for both the FAN and the Assciated Motor. There may be a variety of reasons why data is not collected on the two previously mentioned fans, but they should probably be removed from the Work Step checklist. Or, a means to collect data to an active route should be created. <I> **** Actions Taken **** Notified Supervisor and Generated CR. e-mail with CR reference sent to vibration engineer. <N> **** Equipment Description **** various WMA-FN-54B WEA-FN-53B Work performed WO#02115748
396846 | CR | 20190715 | CAQ | D | 0205956905 PMT for FDR-V-7 Air operator leaks | Y | N |  | N | YES | <C> CR reopened to cross reference additional WR 02059569-05/09 marked completion required box, then taken back to complete <D> **** Detailed Description **** 0205956905 PMT for FDR-V-7 Air operator leaks when valve is stroked close. Top cap leaks when valve is closed and doesnâ€™t leak when valve is open. Top cap gasket needs to be replaced. PMT Not satisfactory <I> **** Actions Taken **** Contacted supervisor, CRS and wrote CR. Need to Hang local clearance replace gasket and perform PMT. | 02-00-FDR-AO-7
396847 | CR | 20190716 | CAQ | D | MCR received Accumulator Trouble on CRD-HCU-4259. | Y | N |  | N | YES | <D> Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-4259. Dispatched OPS-2 to investigate. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-4259 low pressure. OPS2 re-pressurized per SOP-CRD-HCU. Alarm is now clear. <I> Wrote this AR from trending. Xref WO for P6 connector. | 02-00-CRD-HCU-4259
396848 | CR | 20190716 |  | 4 | Recieve 4.840.A5 AIR COMP A CO MONITOR HI LEVEL | N | N |  | N | YES | <D> **** Detailed Description **** Recieve 4.840.A5 AIR COMP A CO MONITOR HI LEVEL after CAS-C-1B. CAS-MON-1A and CAS-MON-1C both peaked over 130 and CAS-MON-1B peaked about 45 (did not bring in an alarm). WR 29150279 had just been completed a short time before. AR 225916 suggests that oil saturated fitlers may be a potential cause. <I> **** Actions Taken **** Delayed removing SA-C-1 from service until CO levels had returned to a more reasonable level. | 02-00-CAS-MON-1A
396849 | CR | 20190716 |  | 4 | CAS-MON-1B not alarming above 10 ppm | N | N |  | N | YES | <D> **** Detailed Description **** During elevated CO condition, CAS-MON-1B did not go into alarmed state with indicated levels up to 45 ppm. See AR 00396848 for further information. <I> **** Actions Taken **** N/A | 02-00-CAS-MON-1B
396853 | CR | 20190716 |  | 4 | E-AY-TR/M3 is in alarm | N | N |  | N | YES | <D> **** Detailed Description **** Over the last couple of days the Kelman for E-TR-M3 has been in alarm for CO2. The purpose of this CR is to document the condition and to drive a change in the alarm setting and take a manual DGA sample for the transformer oil. The gas in alarm in CO2 and this has been rising as the transformer has been operating and it has no impact on operation of the transformer since it is not an impact to the TDC. <I> Generated CR and updated Kelman DGA settings to clear the alarm and set a new monitoring threshold . The CO2 level observed is still within IEEE C57 .104-2008 limits for CO2. | 02-00-E-AY-TR/M3
396856 | CR | 20190716 |  | 3 | R24 LL: DELAYED SHIPMENT OF CRDM'S FOR REBUILD |  |  |  | N | NO | <D> **** Detailed Description **** This is a lessons learned CR only - no impact on plant equipment. Off-site shipment of 20 CRDMs removed in R24 for rebuild was delayed 14 days for completion of rad shipping characterization. This was not unexpected due to the known iron excursion/crud burst encountered in the previous operating cycle. The wait time for completion of the characterization resulted in the 8 CRDM shipping containers remaining in the reactor bldg truck bay for 14 days, impacting other outage activities. <I> **** Actions Taken **** Recommend this be assigned to AR-RXMAINT to develop a CRDM shipping storage plan for future outages to prevent impacts to the reactor bldg truck bay.
396860 | CR | 20190716 |  | 4 | FP-V-SGT/46, 56, 66 maintenance lessons learned |  |  |  | N | NO | <D> **** Detailed Description **** Work scheduled on FP-V-SGT/46, 56, and 66 were scheduled in the 7/15 workweek under WOs 02073780, 02142137, and 02073777 respectively. These valves were previously scheduled and cut from scope during a previous work week due to parts issues and clearance boundary issues. During the current work week the activities are scheuled to overlap. The clearances used for this work rely on opening either FP-V-SGT/46, 56, or 66 to drain and depressurize the volume. All three of the solenoids for these valves share a common power supply that is deenergized by the clearances. If any one of the clearances is hanging, it prevents draining and depressurizing the remaining volumes. These valves must be either worked in series with no clearance overlap, or all clearances must be hung at the same time. <I> **** Actions Taken **** Wrote this CR to drive incorporation of these lessons learned for the next pm occurence.
396861 | CR | 20190716 |  | 4 | TEA-FN-52 HEPA dP Exceeds Limits | N | Y |  | N | YES | <D> **** Detailed Description **** During quarterly fume hood air flow checks per CI-11.13 it was observed that TEA-FN-52 HEPA filter dPIS-53 was offscale high. <I> **** Actions Taken **** CR/WR initiated. Recommend replacing HEPA filter to restore dP to acceptable range. <N> **** Equipment Description **** Chemistry SR-3 Fume Hood TB 441' | 02-00-TEA-FN-52
396863 | CR | 20190716 |  | 4 | RWCU-V-436A failed to indicate open | N | N |  | N | YES | <D> **** Detailed Description **** During RWCU-TK-104A Recirculation, RWCU-V-436A failed to indicate open. Expected to see green light to extinguish and red light come on, but instead the green light went out and the red light did not come on for either indication on G11-P001-3 in RWCR. With CRS permission, attempted to continue with procedure but RWCU-P-28 failed to start. This is likely due to RWCU-V-436A failing to indicate open. This issue prevents us from recirculating and transferring spent resin from RWCU-TK-104A. RWCU-TK-104A is currently full of resin. <I> **** Actions Taken **** Checked with known good light bulbs and still no indication. Informed CRS. Performed RWCU-TK-104B recirculation with no issue using RWCU-P-28. | 02-00-RWCU-V-436A
396868 | CR | 20190716 | CAQ | C | Pager not receiving ERO notifications | N | Y |  | N | NO | <C> This CR and assignment has been conservatively determined to be CAQ. <D> **** Detailed Description **** My pager is not receiving ERO messages. I did receive notification through the cell phone during ERO drill on July 16, but no such information from pager . Pager # 0012. <I> **** Actions Taken **** None.
396869 | CR | 20190716 |  | 3 | CPR-LIS-97A IMDS has typo |  |  |  | N | NO | <D> **** Detailed Description **** During performance of CPR-LIS-97A bench calibration, 02134914-02, it was noticed that the IMDS contains a typo. While checking the inidation calibration the value of 3 VDC has an indication value of 50%. While checking the switch trip points the low switch has a set point of 3 VDC and an indicator value of 95%. The value for the indicator should be 50%. 3 VDC is 50% of a 1-5 VDC scale. <I> **** Actions Taken **** Notified supervisor, wrote CR to get IMDS fixed.
396870 | CR | 20190716 |  | 4 | MS-VMP-1 status change | N | N |  | N | YES | <D> **** Detailed Description **** MS-VMP-1 status change, currently shows BVMS lights #3 and #4 lit in RED. Turbine vibration CR's previously written this cycle include #396679 and #396812 <I> **** Actions Taken **** Notified MCR/ CRS | 02-00-MS-VMP-1
396872 | CR | 20190716 |  | 4 | Need to validate sampling labs for transformer DGA samples | N | N |  | N | YES | <D> **** Detailed Description **** During R24 oil samples were taken for the main transformers by BPA and the results were being reviewed and it appears the samples are showing lower values than the SD Myers reports. The samples taken by BPA were taken when the transformers were light loaded (i.e. backfeed) or prior to transformer soak and typically other samples are taken when the transformers are loaded. The purpose of this CR is to document the the descrepencies between the SD Myers and BPA lab and to obtain samples using both and compare the results. This condition does not affect the operation of the main transformer and it is just to document the descrepencies in the results. | 02-00-E-TR-M1,02-00-E-TR-M2,02-00-E-TR-M3
396873 | CR | 20190716 |  | 3 | ME-02-02-25 has more than 5 CMRs in modiifed status |  |  |  | N | NO | <D> **** Detailed Description **** CR initiated per procedure for more than five (5) CMR's in modified status on Calculation ME-02-02-25.
396876 | CR | 20190716 |  | 3 | ABN-TSG-010 and ABN-TSG-011 need revisions |  |  |  | N | NO | <D> **** Detailed Description **** ABN-TSG-010 and ABN-TSG-011 provide guidance for using B5b or FLEX equipment for water makeup to the RPV and the Spent Fuel Pool. Part of the lineup requires use of a flange connection with s Storz adapter connected to either RHR -SYS-A, B, or C. The table in both of these procedures states that the storage location is building 600 hose trailer. These connectors were all relocated into the reactor building and are now stored in cabinets in the NE and SW stairwells. Revise these two procedures to match the storage location specified in the table in step 7.7.1 of ABN-FSG-002. See EDMS for markups. <I> **** Actions Taken **** Wrote this CR.
396878 | CR | 20190716 |  | 3 | Discrepancy between PPM 1.20.10 and required PMs |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.20.10 does not reflect the proper maintenance schedule for E-DP-S1/7 and associated DC system components. Currently it is aligned to R27,R31, R35 per the procedure. It should be aligned to R25 in order to satisfy critical PM requirements since it a PM performed every 8 years and it was last performed in 2013. This also applies to panels supplied by S1/7 as outlined in PPM 1.20.10 (E -DP-S1/1B, E-DP-S1/2C, E-DP-S1/2B). <N> Editied at initiator's request to add the correct procedure (1.20.10). No actions to change bus outage alignment. As scoping for R 25 continues a list of PM's needing to align with the procedure will have SMS-AR's generated to align with the LROP procedure 1.20.10.
396880 | CR | 20190716 |  | 3 | (R24LL) Ops outage Lesson learned |  |  |  | N | NO | <D> **** Detailed Description **** Below is comment from One note to document R24LL Due to the new Arc Flash boundaries requirements of ISPM -20, it is necessary to evacuate the entirety of the TB 471W for the vast majority of breaker racking. This evacuation can take ~ 45min to an hour (as people process through the portal monitors, wrap up in-progress testing that cannot be paused, place work in a safe condition, etc.).Pausing all of this work for a ten minute breaker rack usually results in work delays of GT 30min, as workers exit the TB entirely and may not return until after a break. ISPM-20 allows for reduced boundary distances if there is a "physical barrier" to protect workers from a potential arc flash event. Erecting a temporary wall, for outages (similar to what's used for the RX 501), would be a great way to eliminate the Arc flash hazard from adjacent workers and eliminate the need to restrict access to the 471 Heater Bay and/or stop ongoing work. - <I> **** Actions Taken **** Copied information from one note Ops list CR should be assigned as a 3 and remain open to be reviewed by outage critique
396881 | CR | 20190716 |  | 3 | (R24LL) Ops outage Lesson learned to date |  |  |  | N | NO | <D> **** Detailed Description **** Recommend outage planning evaluate Operations Department work breakdown structure related to performance of SOPs and surveillances. Having multiple tasks to perform a single SOP or surveillance results in an unnecessary number of WOTs which then need to be individually chased down and updated. While theoretically the smaller WBS should provide a clearer picture of progress on a job, at a certain point, a point of diminishing returns is reached as people spend more time trying to keep computer tracking systems up to date than performing the work. Additionally, each authorization for a portion of the surveillances creates an ESOMS log entry resulting in multiple log entries for the same surveillance. For example, see multiple log entries for ESP-MSIV-B301 made on 6/1 for individual work tasks all associated with the 01 task. The Shift Manager and others are spending valuable time aggregating those entries under the 01 task so that when the work is complete, there is one stop shopping to verify it is actually complete. This is an unnecessary and waste of valuable time that could be spent focused on the problems at hand. Recommend simply sign in the 01 task and aggregate all subtasks under the 01 entry which allows one-stop shopping for reviewing completed surveillances to credit the surveillance rather than having to search each entry to confirm it was a partial. <I> **** Actions Taken **** Initiated from the one note and should remain open for outage review
396883 | CR | 20190716 |  | 4 | EN MAIL MIS-DELIVERED TO ANOTHER BUSINESS |  |  |  | N | NO | <D> **** Detailed Description **** OUR MAILROOM ATTENDANT WENT ON OUR DAILY MAILRUN AND WHEN THEY GOT TO THE COUNTER AT THE POST OFFICE OUR MAILROOM ATTENDANT WAS TOLD THAT THE POST OFFICE CLERKS HAD GIVEN OUR MAIL BIN TO ANOTHER BUSINESS IN ERROR, BUT THEY WERE SURE WE WOULD GET IT TOMORROW AS THE OTHER BUSINESS HAS BROUGHT BACK MAIL THAT WASN'T THEIRS BEFORE. <I> **** Actions Taken **** NOTIFIED SUPERVISION. GENERATING CR FOR TRENDING PURPOSES.
396884 | CR | 20190716 |  | 4 | (R24LL) Ops outage Lesson learned to date |  |  |  | N | NO | <D> **** Detailed Description **** DAD surveillance reports supporting 1.3.40 and 3.1.1 are not pulling accurate data for completion and late dates. In some cases, a frequency change occurred and that is being credited as a completed surveillance. Need to ensure that when a frequency change occurs, the date input to document the change matches the last full surveillance credit work order date.In some cases completion dates are simply incorrect. Having to maintain the checklists using multiple sources (D080, eWP, and Ops Log) to get accurate dates. Need to make sure DAD reports are set up to run correctly and new surveillances that now exist as a result of a frequency change are input to the DAD report generator. The DAD report could be a huge time saving tool, but only if we know it's working properly. <I> **** Actions Taken **** Issued for R24 LL - remain open for trending This issue will be corrected under AR-CR 394090.
396885 | CR | 20190716 |  | 3 | ERO Drill - Core Thermal Engineer Tech Memo Missing label |  |  |  | N | NO | <D> **** Detailed Description **** TM-2117 contains Figure 4.1.1-3 on page 127 which shows the maximum core uncovery time limit (y-axis) based on time after reactor shutdown (x-axis). The time after reactor shutdown is labeled in hours. The maximum core uncovery time limit has no axis unit label, but should be labeled in units of minutes. This is an error likely situation and the figure should be updated to include a y-axis unit label. <I> **** Actions Taken **** Noted on after action report in ERO drill and critiqued.
396886 | CR | 20190716 |  | 4 | Voicemail system not responsive | N | N |  | N | NO | <D> **** Detailed Description **** As of 11:25 pm 7-15-2019 the Voicemail system lost connection to the licensing server. This resulted in the system to go out of compliance and stop taking calls. <I> **** Actions Taken **** Once the issue was identified , a resync of the connection to the licensing server was established and server reboots were executed to bring system back online.
396887 | CR | 20190716 |  | 3 | New COND-M-P/4 failed pre install testing. | N | N |  | N | NO | <D> **** Detailed Description **** While testing the new COND-M-P/4 per PPM 10.25.9 the megger test criteria is required to be 5000 M ohms and the highest reading was 402 M ohms. <I> **** Actions Taken **** Informed engineering for resolution and wrote the CR to document the failure. <N> **** Equipment Description **** New replacement motor for COND-M-P/4. This equipment is not currently installed in the plant. Engineering needs to take ownership of this CR so a path forward can be identified Efin Eigneer has been notified and is already taking action, this idvidual is expecting an assignment for this issue.. Auhtor recomends a servity level 3 Non CAQ to Engineering.
396890 | CR | 20190716 |  | 3 | R24LL Crane Operator Rescue Plans |  |  |  | N | NO | <D> **** Detailed Description **** Crane Operator rescue plans need to be in place pre outage for MT-CRANE on the turbine and refuel floors. These plans should be complete with fall protection plans, etc. Staged on the floors and ready to go. <I> **** Actions Taken **** Documented in a CR and notified Reactor Maintenance. Recommend assign to Reactor Maintenance.
396891 | CR | 20190716 |  | 3 | R24LL Drywell Cooling |  |  |  | N | NO | <D> **** Detailed Description **** The Drywell was NOT scheduled to lose cooling in R24, it did at least 5 days where temperatures were negatively impacting the stay times, putting stress on workers and in some cases limiting work to 30 minute dives. This puts our workers at risk and at the same time limits production in the drywell. Suggest getting engineering support to evaluate implementing a containment cooling strategy for R25. Prairie Island does it, why canâ€™t we? <I> **** Actions Taken **** Documented in a CR. Notified Reactor Maintenance. Suggest assigning CR to Reactor Maintenance.
396892 | CR | 20190716 |  | 3 | R24LL Waterboxes lighting and platform access |  |  |  | N | NO | <D> **** Detailed Description **** Intermediate waterboxes A-B-C needs scaffolders to build a platform for access to the first rung of the fixed ladder. Reportedly from the crew performing work (Conco) the first rung is between 3 to 4 ft. off the bottom of the waterbox. Second, lighting in the waterboxes needs to either be lithium ion battery powered rechargeable or specifically designed for work in an area with water and setup in A, B, and C. During R24 it was reported that lighting was only present in A waterbox and all other work was done with headlamps. <I> **** Actions Taken **** Notified Reactor Maintenance, documented in this CR. Recommend assignment of CR to Reactor Maintenance.
396895 | CR | 20190716 |  | 2 | Wrong component worked during maintenance. | N | N |  | N | NO | <C> MRT Change request: CR 396895 moved from Severity 1 to Severity 2; level 2 clearance order event. <D> **** Detailed Description **** During the PMT of FDR-AO-7 (WO 02059569), The PMT failed (CR 396846). After investigation of why the PMT failed, it was determined that the maintenance performed was on the wrong valve operator. The craft isolated the system per the local clearance and performed the work per the work instructions. The work plan had a location of R419 M9/3.5 in FDR-SUMP-R3, when the deck plates were removed the valve was at the location described, but no EPN was observed in the sump. This was the correct make and model actuator and the only actuator in the sump,so the craft proceeded with performing their zero energy check by cracking the fitting to the actuator, after the pressure was bleed off, the gasket was changed on the actuator.After review of the isometric drawings during the investigation it was determined that the valve worked on was FDR-AO-608 and not FDR-AO-7. These valves are the same isolation <I> **** Actions Taken **** Performed investigation to gather facts. took statements from the personnel involved WR 29150503 was written to change the gasket on the correct valve (FDR-AO-7). <N> **** Equipment Description **** work was on FDR-AO-608 and should have been FDR-AO-7 This is not an equipment issue, it is Human performance
396896 | CR | 20190716 |  | 3 | R24LL TG 471 Heater Bay Lighting | N | N |  | N | NO | <D> **** Detailed Description **** TG 471 Heater bay and TG 501 FW Heater areas need permanent lighting relamped or preferrably replaced with LED lighting. Att a minimum a work task needs to be in place to run stringers/ temp lighting in the heater bay and TG 501 FW heater areas. The procurement and use of battery powered jobsite/ area LED lights (similar to those used in the drywell in R24) should also be part of the solution. <I> **** Actions Taken **** Documented in this CR. Notified Reactor Maintenance. The majority of the work in the heater bay is valve work and recommend assignment to Reactor Maintenance.
396897 | CR | 20190716 |  | 3 | R24LL Siemens Rotor Blade Removal Task |  |  |  | N | NO | <D> **** Detailed Description **** Siemens rotor blade removal is a noisy activity that (per OE from R23/24) lasts approximately two days to complete. Consider noise attenuating buffers around the task OR isolate to an area away from the RP desk, dress out area, heavily foot trafficked area. Also post areas ahead of time â€“ TG 501 and TG 471 around the heater bay posted in R24. Noise levels reached anywhere from 108 dB (4 ft from the source); 103 dB outside of their danger tape on the NW side of the rotor, 97 dB S. of the shield wall; 87 dB N. of the shield wall; 93 dB on the W. side of LP-C FME area; 86 dB TG 471 heater bay area. <I> **** Actions Taken **** Documented in this CR. Notified Reactor Maintenance. Suggest assignment to Reactor Maintenance.
396898 | CR | 20190716 |  | 3 | ME000070 Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** One student failed written exam for Basic Rigging initial. Per TDI-02, plan to remediate student and administer 2nd exam on 7-18-19. <I> **** Actions Taken **** CR written, emailed applicable supervisors
396899 | CR | 20190716 |  | 3 | R24LL Turbine Project Wood Cribbing |  |  |  | N | NO | <D> **** Detailed Description **** Wood oak cribbing for our Turbine projects is old, dried out/ cracked, and heavy. The large oak pieces of cribbing used during various stages in the turbine work are upwards of 150 lbs. As a better/ best practice these should be replaced with modern light weight composite cribbing. Other stations such as Diablo Canyon, South Texas, etc. are using the composite cribbing. The cost of one back injury would greatly exceed the cost of replacing the cribbing. Example: https://ameintl.net/products/15260/ <I> **** Actions Taken **** Documented in this CR. Notified Reactor Maintenance. Suggest assignment to Reactor Maintenance.
396900 | CR | 20190716 |  | 3 | R24 LL RM Needs Experienced Safety Professionals |  |  |  | N | NO | <D> **** Detailed Description **** Reactor Maintenance needs to consider staffing experienced safety professional(s) for outages â€“ one on days and one on nights. The turbine team employed one safety professional for R24. However that one safety person was only on days and was restricted to just the turbine floor. Turbine floor coordinators are heavily reliant on the safety representative to handle all confined space, fall protection, posting signage/ barriers, etc. Additional safety oversight on other RM projects would be proactive in reducing injuries. <I> **** Actions Taken **** Documented in this CR. Notified Reactor Maintenance. Suggest assignment to Reactor Maintenance.
396901 | CR | 20190716 |  | 3 | R24 LL Siemens contract their own Safety Professionals |  |  |  | N | NO | <D> **** Detailed Description **** If awarded the R25 contract for turbine work. EN needs to require Siemens by contract to employ their own safety representative(s) (reviewed and accepted by EN contracts team/ Reactor Maintenance/ industrial safety) for R25. <I> **** Actions Taken **** Documented in CR. Notified Reactor Maintenance. Recommend assignment to Reactor Maintenance.
396902 | CR | 20190716 |  | 4 | HEAT TRACE MEGGER RESULTS | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** megger test results for four year pm on HT-HTP-FP/23 19F dit not meet criteria per ppm 10.25.213 7.1.4 D, and E <I> **** Actions Taken **** reported to electrical supervisor, supervision reporting to engineering department <N> **** Equipment Description **** HT-HTP-FP/23 transformer yard HT-HTP-FP/23
396903 | CR | 20190716 | CAQ | D | R24 LL Customer Notification Report Issue resolution |  |  |  | N | NO | <D> **** Detailed Description **** This CR is for tracking purposes only. Customer Notification Report CNR-CGS-19-001 was issued to document miscellaneous debris from unknown sources discovered during IVVI inspections in R24 in the vessel annulus and the Dryer/Separator Pit ) DSP (See EDMS). These items were removed during the final clean-up and Foreign Object Search And Retrieval (FOSAR) activities which are performed prior to vessel close out under work order task 0210960519. Debris in the DSP was removed by vacuuming as documented in the R606â€™ log (see entry on 6/2/19 @1700). This CR is initiated to tie the CNR report to the cleaning activities that resolved them. As an R24 LL, process changes have been implemented to ensure CRs are initiated in response to CNRs in a timely fashion. <I> **** Actions Taken **** Discussed the issue with the FME Program Coordinator and Rx Maintenance. All debris reported in the CNR has been removed, no foreign material issues exist. Process updates have been made to ensure future CNRs are captured as CRs, in a timely fashion. Recommend Cat D since all necessary actions have been taken.
396904 | CR | 20190716 |  | 3 | Increasing difficulty evaluating habitability with SDS |  |  |  | N | NO | <D> **** Detailed Description **** Several years ago OSHA revised the MSDS and went to a new format called Global Harmonized System (GHS) Safety Data Sheet (SDS). The revision to the SDS format allowed the companies responsible to produce the SDS to limit the information provided in Section 3 â€“ Composition/Information on Ingredients. Many of the new or revised SDS received limit the information on ingredients to a statement that the material contains no hazardous materials as listed under OSHAâ€™s definition of hazardous. The limited or lack of ingredient information is making it more difficult to provide an accurate or adequate Control Room Habitability evaluation as prescribed under NRC Guidance 1.78. Individual ingredients and concentration are needed to perform the habitability evaluation. The result is that the chemical cannot be allowed onsite limiting use for or on plant equipment. <I> **** Actions Taken **** This condition was communicated to Chemistry Supervision and Licensing for determination of a path forward. The condition reported in this CR does not currently affect the operation, control or compliance status of the station.
396906 | CR | 20190716 |  | 3 | unable to implement TM EC 17858 as written |  |  |  | N | YES | <D> **** Detailed Description **** TG-MON-DE2 meter reads in 0.1 increments and can only be read accuratley to 2 significant digits after the decimal point. The EC changes the Danger Long setting on TG-MON-DE2 from .645 to .635. However the indicator can only be read accurately as 0.7, 0.65. 0.6, 0.55, etc. See attached photos. . This temp mod needs to be revisited and reevaulated as to wether it is really needed. <I> **** Actions Taken **** Notified System Eng and wrote CR. | 02-00-TG-MON-DE2
396907 | CR | 20190716 |  | 4 | TG-MON-DE2 Danger long and short setpoints are reversed | N | N |  | N | YES | <D> **** Detailed Description **** Danger long and Danger short setpoints on TG- MON-DE2 are reversed. Both go to same annunciator 4.820.B2, 8-1 so it does not affect the function. This has been incorrect since at least 6/7/2003 (See WO 01038773) See attached pictures and observe the direction of the toggle switch.. Recommend action to correct during next Calibration (R25) <I> **** Actions Taken **** Wrote CR <N> The issue with 396907 is simply a swap in how the setpoints are displayed. The setpoints and alarms, etc. are correct. Theyâ€™ll work, theyâ€™re just switched. There is no evaluation to make, just fix. | 02-00-TG-MON-DE2
396909 | CR | 20190716 | CAQ | D | CRASH to Benton county intermittant durring drill | N | Y |  | N | YES | <D> **** Detailed Description **** Benton County did not receive a CRASH call during the EP drill. This problem occurred the day prior and required the phone switch port be reset. CR 396834. The port was reset again and Benton County was restored within minutes and then failed again after approximately an hour. This time the phone port switch did not indicate a problem and when tested operated as required. <I> **** Actions Taken **** Benton County management was contacted to discuss how we could manipulate the circuit in order to duplicate the problem. A diagnostic trace was also run on the phone switch but it did not indicate the problem. The CRASH to all other locations remained operable throughout the drill and Fax and alternate phone lines remained operable. Recommend CAQ-C. <N> **** Equipment Description **** TEC, Frontier and Benton county
396910 | CR | 20190716 |  | 4 | SCW-P-2 abnormal noise/ rubbing sound | N | N |  | N | YES | <D> **** Detailed Description **** SCW-P-2 abnormal noise/ rubbing sound from motor <I> **** Actions Taken **** Informed MCR/ CRS Requested maintenance take vibration readings and check pump temperatures. | 02-00-SCW-P-2
396911 | CR | 20190716 | CAQ | C | Alert declaration missed in July Drill |  |  |  | N | NO | <D> **** Detailed Description **** July Alert declaration not made within required time. Drill Inject was required as per drill manual which resulted in a missed DEP opportunity. Notifications were complete and timely. <I> **** Actions Taken **** Critiqued with center.
396912 | CR | 20190716 | CAQ | D | SEC-IDS-15 requires maintenance | N | N |  | N | YES | <D> **** Detailed Description **** SEC-IDS-15 is not functioning as designed. Request maintenance to investigate. <I> **** Actions Taken **** CR/WR Generated; Compensatory measures initiated | 02-00-SEC-IDS-E/S/14/15
396914 | CR | 20190716 | CAQ | D | Leak on HCU 14-19 accumulator lower connection | Y | N |  | N | YES | <D> **** Detailed Description **** While recharging HCU 14-19 to clear low N2 pressure alarm, a leak was found on threaded connection closest to the bottom of the accumulator while snoop checking the HCU. Connection needs to be resealed. <I> **** Actions Taken **** Notified CRS | 02-00-CRD-HCU-1419
396915 | CR | 20190716 |  | 3 | Procedure requirements not followed for WAP installations | N | N |  | N | NO | <D> **** Detailed Description **** Temporary Wireless Access Points (WAPs) were installed in the power block per SWP-IS-02 under AR 357654 prior to the R23 outage. As required on Form 27140, an AR EVAL to accomodate the 10 CFR 50.59/72.48 review to document exceeding the 90 day limit is not documented or cross referenced to the parent AR. It is also not documented if the review by Fire Protection for combustible loading impacts was performed per SWP-IS-02, step 2.3.3. It is also not clear if step 6.4 is being followed consistently as actions are not completed or exist to document Security Review, Fire Protection Review, PGM Review and Quarterly walk down verification. <I> **** Actions Taken **** Initiated CR. Contacted SM.
396916 | CR | 20190716 |  | 3 | ChemLab WAP Installation not per process | N | N |  | N | NO | <D> **** Detailed Description **** The Wireless Access Points (WAPs) installed under AR 378650 in the Chem Lab were installed on 5/30/2018. Similar to issues identified in CR396915, requirements of SWP-IS-02 may not have been followed. It is not documented if an AR -EVAL for the 50.59/72.48 review was performed, if Fire Protection review was performed, or if Plant General Manager approval for installation beyond one refueling cycle was obtained. Also note that the Justification Form 27140 in the AR EDMS identifies this as a permanent installation with estimated removal by 3/27/2043. <I> **** Actions Taken **** Initiated CR. Contact SM.
396917 | CR | 20190716 | CAQ | D | 125 VDC Battery B1-7 ground alarm in and clear | Y | N |  | N | YES | <D> **** Detailed Description **** 125 VDC Battery B1-7 ground alarm in and clear, at the time no equipment was being started or stopped. The CR should be closed to trend <I> **** Actions Taken **** Followed ARP to reset the alarm, discussed with CRS | 02-00-E-B1-7
396918 | CR | 20190717 |  | 4 | WOA-FN-9 fan bearing making noise - needs replaced | N | N |  | N | YES | <D> **** Detailed Description **** The fan bearing on WOA-FN-9 is starting to make noise. Repair as necessary | 02-00-WOA-FN-9
396921 | CR | 20190717 |  | 3 | Software not performing auto updates as expected |  |  |  | N | NO | <D> **** Detailed Description **** It was identified that the software (Solarwinds) USB blocking feature on a corporate work station was no longer working as expected. This was brought to the attention of cyber by a user. Cyber security performed an investigation and determined that cause was the software being upgraded to a new version that did not perform as expected. To correct the issue the old agents of Solarwinds had to be uninstalled and new version deployed to the effected computers. Solarwinds is now working as expected. This was an HU error by an individual making the upgrade outside of the procedure process. <I> **** Actions Taken **** Notified CIO and IS Leadership Machines effected have been corrected Individual with HU error has been coached
396922 | CR | 20190717 |  | 3 | RFW-FCV-10B Insulation Dose Rate Issues during R24 |  |  |  | N | NO | <D> **** Detailed Description **** During R24, dose rates up to 2.1 rem/hr were identified on the insulation associated with RFW-FCV-10B. These dose rates were not consistent with previous radiological conditions earlier in R24 or in previous outages. An evaluation should be performed to determine the cause of this change. <I> **** Actions Taken **** HPT notified Rad Ops Supervision - CR generated to perform evaluation.
396926 | CR | 20190717 |  | 3 | Potential Trend: Complacent Work behaviors |  |  |  | N | NO | <C> reopened at the request of S. Stewart to add more information <D> **** Detailed Description **** During data analysis for the 2nd Qtr 2019 station performance summary, it was recognized that there is a potential / emergent trend in complacent work behaviors. <I> **** Actions Taken **** Reports were shared with the Maintenance Specialist and a plan to validate the potential trend was discussed. Notified Performance Improvement Manager and HU Program Manager, initiated condition report. Recommend 3 / MNTPROG
396934 | CR | 20190717 |  | 3 | Form 26048 procedure revision required | N | Y |  | N | NO | <D> **** Detailed Description **** Form 26048 Energy Northwest Public Address Emergency Message For Localized Evacuation directs evacuees to assemble in the Operations Support Center (or other area specified). This is a legacy location was when the OSC was in the GSB lunch room. PPM 13.5.1 Local, Protected Area or Site Evacuation references that the normal assembly area is the onsite Yakima Building Conference Room. Revise Form 26048 to have evacuees assemble in the Yakima Building Conference Room vice the Operations Support Center. <I> **** Actions Taken **** Initiated this CR. Informed Emergency Planning. <N> Form 26048 has been revised, to revision 11 dated 8/7/2019
396937 | CR | 20190717 |  | 3 | Need clear path & owner to return PASS system to service | Y | N |  | N | YES | <D> **** Detailed Description **** Currently, the PASS system (Post-Accident Sampling System) has been out of service for over a year. We were unable to complete 2 SVs associated with the system in the 7/8 WW as a result. They had to be Cancel Requested instead. It is not clear who owns the system and what needs to be done to return it to service. I recommend that an owner be assigned to the system, have them determine a plan going forward, and have clear actions to take with a timeline for returning the system to service. <I> **** Actions Taken **** Cancel Requested the SVs that were not completed (see Cross References for the specific SVs). Held a meeting with Chemistry, Operations, Work Control, and Engineering to see what could be done. The meeting resulted in the same recommendation that I am providing in this CR. <N> **** Equipment Description **** PASS Sample Rack, Radwaste Building 487' PASS system currently tracked Inop. Reference T17-C-PSR -PCIV-001-001. | 02-00-PSR-V-003/A,02-00-PSR-V-003/B,02-00-RHR-V-747
396939 | CR | 20190717 | CAQ | D | CRD-HCU-5435 Low pressure. | Y | N |  | N | YES | <C> CR reopened to cross reference additional WP 02146548, marked completion required box, then taken back to complete <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-54-35. It appears this is the fourth low pressure alarm in the last four weeks for this HCU. <I> **** Actions Taken **** Ops2 repressurized per SOP-CRD-HCU. | 02-00-CRD-HCU-5435
396940 | CR | 20190717 | CAQ | D | RCIC-V-206 and RCIC-V-38 have packing leakage | Y | N |  | N | YES | <D> **** Detailed Description **** While investigating water on the floor it was noted that both RCIC-V-206 and RCIC-V-38 have packing leakage. <I> **** Actions Taken **** notified hp and MCR. <N> Discussed with Ops 2 and verified that packing leakage is characterized as minor steam leak from valve packing. | 02-00-RCIC-V-206,02-00-RCIC-V-38
396941 | CR | 20190717 |  | 3 | DW-DWS-4 is isolated with supply valve Cation tagged shut. | N | N |  | N | YES | <C> MRT Change request: CR 396941 moved from 4/Trend Repair to 3/OPSST Review Safety Concern. <D> **** Detailed Description **** OPS flushes safety showers to ensure that the water will be clean. DW-DWS-4 is listed in portal J as a decon shower. If this is the case why are we flushing it? Its stainlkess steel piping and its demin water. If it was really a safety shower we would fix it instead of leaving it caution tagged out for over 6 months. Please evaluate if this needs to be flushed with safety and eye wash showers if it does then please place a "safety" priority on its repair. <I> **** Actions Taken **** wrote CR for evaluation if its a safety shower we should continue flushing it and fix it ASAP, if its a DECONN shower we shouldnt be flushing it and we can fix it or deactivate it, but we shouldnt have to flush it. <N> Since this decon shower serves the RW 437' it should remain on the weekly shower test work order. WO 02137391 is coded 4C, minor safety issue, which is correct for DW-DWS-4. No further actions required. | 02-00-DW-DWS-4
396942 | CR | 20190717 | CAQ | D | RHR-PIS-22B pointer slipping | Y | Y |  | N | YES | <D> **** Detailed Description **** During the performance of ISP-RHR-M901 WO 02137015-01 the indicator for RHR-PIS-22B was found slipping on the shaft and was unable to be calibrated. <I> **** Actions Taken **** Restored RHR-PIS-22B to service and backed out of the surveillance per the CRS direction | 02-00-RHR-PIS-22B
396945 | CR | 20190717 |  | 3 | 02115780-02 (mosel for) needs work instructions changed to |  |  |  | N | NO | <D> **** Detailed Description **** 02115780-02 (mosel for) needs work instructions changed to match OSP-RHR/IST-Q704. Motor current signature is no longer performed per SV. OSP-RHR/IST-Q704/WO needs to include PMID23100-01 with check valve testing for easier ref and need to add 10.2.13 for lubercute.
396946 | CR | 20190717 |  | 3 | SOP-HVAC/RB-OPS revision | N | N |  | N | NO | <D> **** Detailed Description **** SOP-HVAC/RB-OPS section 5.2 is to enter/exit the RB HVAC enclosure. This section directs calling secondary containment inoperable in anticipation of exceeding -0.25 inches d/p. This step was put in place when TS required d/p to be LT -0.25 inches at all times. Amendment 250 to TS revised the surveillance requirements allowing d/p to be GT -0.25 inches under known conditions. Based on this TS change, SOP-HVAC/RB-OPS should be revised to eliminate the step to declare secondary containment inoperable. <I> **** Actions Taken **** Initiated CR.
396947 | CR | 20190717 |  | 4 | FDR-AO-576B (FDR-V-608), air not present as expected. | N | N |  | N | YES | <D> **** Detailed Description **** During the zero energy check of FDR-AO-576B prior to intended maintenance, it was reported that no air was present when the instrument tubing was loosened from both the open and closed sides of the air operator. This discovery is contradictive to actual configuration and could be a potential equipment issue associated with this component. The Instrument rack regulator was walked down and verified to be reading 75 psig and the local regulator was reading 45 psig. The intent of this CR is to document the potential equipment issue and to ensure operation of the valve. See WR#29150526 for operational PMT. Both the valve and air operator were also verified not to have EPN tags hanging. <I> **** Actions Taken **** EPN Lables requested with delivery to FIN EO for installation. | 02-00-FDR-AO-576B,02-00-FDR-V-608
396948 | CR | 20190717 |  | 3 | FDR-V-608 configuration discrepancy | N | N |  | N | YES | <D> **** Detailed Description **** Configuration of the trip valve/accumulator set-up did not match drawing M619-317A rev5. The configuration matches M619-317A rev1. In this case, rev1 is correct for the field but incorrect per the rev 5 drawing. . A simular issue was identified for EDR-V-319 by CR 300014. assignment 02 of that CR was to field verify epn's listed on DWG's M619-317 and M619-317A for current configuration, this walkdown missed that FDR-V-608 had the same issue as EDR-V-139 FDR-V 608 is configured like detail C in Revision 5 of the drawing . M619-317A drawing needs updating <I> **** Actions Taken **** Wrote CR | 02-00-FDR-V-608
396952 | CR | 20190717 |  | 4 | Degraded Secondary Containment Under Spare Transformer | N | N |  | N | YES | <D> **** Detailed Description **** During the Dry Season Stormwater Inspection, degraded secondary containment was noted under the spare main transformer located in the gravel lot southeast of the warehouse complex. The containment has been blown back on top of itself and would not contain transformer oil if it were to leak from the transformer. This is a repeat finding and was noted in August of last year as a NEIL insurance concern. See pictures in EDMS docs. Request secondary containment be evaluated for replacement/repair. <I> **** Actions Taken **** Spoke with Facilities and Fire Protection Engineer regarding the state of the containment and previous actions. Informed Environmental and Regulatory Programs. <N> **** Equipment Description **** Spare main transformer in gravel lot south of warehouse complex
396955 | CR | 20190717 |  | 4 | Excessive Demin water makeup | N | N |  | N | YES | <D> **** Detailed Description **** An excessive amount of demin water has been used in the last two days. Recent problem with the Turbine air wash system dump valves. This system needs to be checked again. <I> **** Actions Taken **** Notified PSRO <N> **** Equipment Description **** Demin water trailer
396956 | CR | 20190717 |  | 3 | REA-V-1 and REA-V-2 seal inspection PM's |  |  |  | N | YES | <D> REA-V-1 & REA-V-2 seal inspections are performed on a biannual biases (2yr PM). This is the second time I personally have performed this PM and find it extremely difficult to clearly see a significant portion of the seal. These are 72â€ butterfly valves that fail closed. Inspection is performed by using a 10â€™ long piece of metal with a mirror taped to it so you can inspect the opposite side of the valve seal using a flashlight while the ventilation is running. Both of these PM's should be performed during the outage when ventilation is secured and significantly reduces the chances of a safety incident and will allow an appropriate inspection to be performed. <I> REA-V-1 is located up a ladder on RX 572' floor elevation, ,REA-V-2 is located inside the reactor building exhaust stack which has to have scaffold built inside the stack in order to reach the valve for the inspection. If this was performed during the outage the both valves could be inspected from accessing the hatch just upstream of REA-V-1 and the valves could be gagged so both inspections could be performed without having to build scaffold. Cause sometimes the scaffold is not built to acess REA-V-2. <N> REA-V-1 is located up a ladder on RX 572' floor elevation REA-V-2 is located inside the reactor building exhaust stack. CR at INPROG. Approved CR, moved to SRO for OPS Review. | 02-00-REA-V-1,02-00-REA-V-2
396957 | CR | 20190717 |  | 4 | Disconnect FD-42-2D2D will not close | N | N |  | N | YES | <D> **** Detailed Description **** Disconnect FD-42-2D2D failed to close during performance of D-FDR-P-18B-003. Recommend lubrication. <I> **** Actions Taken **** Notfied MCR and wrote CR | 02-00-FD-42-2D2D
396958 | CR | 20190717 |  | 4 | Washington EOC dedicated fax inoperable | N | Y |  | N | YES | <D> **** Detailed Description **** During the monthly fax check, the Washington EOC dedicated fax was found inoperable. Contacted the state and put in a ticket with them to fix the fax. <I> **** Actions Taken **** Notified EP and the SCC Recommend closing to WR. <N> **** Equipment Description **** Washington State EOC
396959 | CR | 20190717 |  | 4 | TSW-V-750A Chem sample point low flow | N | N |  | N | YES | <D> **** Detailed Description **** Low flow through TSW-V-750A chemistry sample point for TSW. Approximately 300 ml/min through TSW-SP-69. Inadequate purge rate may result in non-representative samples or excessive purge time. Recommend blowing down sample line with pressurized gas to purge fouling. Last performed 2017. Recommend periodic flushing of the line work order with 1 year periodicity be created. <I> **** Actions Taken **** supervisor, specialist, control room operator informed | 02-00-TSW-V-750A
396960 | CR | 20190717 |  | 4 | RCIC-P-4 DISCHARGE SCUPPER IS LEAKING ON THE FLOOR | N | N |  | N | YES | <D> **** Detailed Description **** RCIC-P-4 DISCHARGE SCUPPER IS LEAKING ON THE FLOOR. wHILE TRYING TO DETERMINE WHERE THE WATER ON THE RCIC PUMP ROOM FLOOR WAS COMING FROM, RCIC-P-4 TURNED ON AND GAVE US THE ANSWER. THE PUMP DISCHARGES INTO A BOX//ENCLOSURE THAT RUNS TO THE DRAIN. WATER WAS LEAKING FROM THE BOX IN SEVERAL PLACES AND SPILLING ONTO THE FLOOR. <I> **** Actions Taken **** WROTE cr/WR, pump is working and performing its function, just a small amount of water is going onto the floor. this has been a previous problem. | 02-00-RCIC-P-4
396961 | CR | 20190717 |  | 3 | Inefficient use of station resources: LCS SR frequencies |  |  |  | N | NO | <D> **** Detailed Description **** The current Licensee Controlled Specifications (LCS) Surveillance Requirement (SR) frequencies cause an inefficient use of station resources. For example the frequency of SR 1.3.4.6.1, perform Channel Functional Test (CFT) of the Reactor Coolant System (RCS) Interface Valves Leakage Pressure Monitors, is 31 days. Similarly constructed instruments covered by Technical Specifications (TS) SRs have frequencies of 92 days; for example TS SR 3.3.5.2 perform CFT. Additionally there does not appear to be a process to extend LCS SR frequencies. <N> STI AR 392335 is extending TS SR 3.3.5.1.2 frequency to 184 days.
396962 | CR | 20190717 |  | 3 | High Risk Plan for AR-V-1 perm. repair not approved by T-3 |  |  |  | N | NO | <D> **** Detailed Description **** High risk challenge meeting held on 7/3/19, however, approval signatures were not gained for the HRP for WO 02125129-01 by the end of T-3 as required per WCI-4.
396963 | CR | 20190717 |  | 4 | T2 Dirty | N | N |  | N | YES | <D> **** Detailed Description **** Turbine sump T2 is full of oily grime. Recommend cleaning out the sump prior to pumping to radwaste for processing. <I> **** Actions Taken **** Notified MCR and submitted CR <N> **** Equipment Description **** Turbine sump T2
396964 | CR | 20190717 | CAQ | D | ARM-RIS-33 erratic indication and alarm | N | Y |  | N | YES | <D> **** Detailed Description **** ARM-RIS-33 erratic indication and alarm. Red trip 2 lamp illuminated. Green operate lamp off. Amber trip1 lamp off. All lamps verified good. The green lamp can be reset occasionally as well as the red trip 2 lamp. see edms for unit / recorder pic <I> **** Actions Taken **** sent this AR to EP for review | 02-00-ARM-RIS-33
396965 | CR | 20190717 | CAQ | D | Suppression Pool Level Low alarm 4.601.A12 2-3 | Y | N |  | N | NO | <C> MRT Change request: CR 396965 Severity moved from NON-CAQ Severity 4 to CAQ D/Trend. <D> **** Detailed Description **** Suppression pool level low alarm recieved, Suppression pool level was -0.75". Pool level was trended with EDNA point X369. The cause of the slowly lowering trend was determined to be due to a siphon effect through the RCIC system. RCIC-P-2 was run for an additional 10 minutes per SOP -RCIC-STBY. This CR was written for trending purposes. <I> **** Actions Taken **** Discussed with CRS/SM, Performed SOP-RCIC-STBY, Restored Suppression Pool level per SOP-FPC-SPC
396966 | CR | 20190718 |  | 4 | DO-F-5 high differential psi while transferring fuel | N | N |  | N | YES | <D> **** Detailed Description **** While transferring fuel, 4.800.C2 10-3 Fuel Oil Polish Building Trouble alarm came in due to DO-F-5 high d/p reading 26 psid and steady. Filter needs to be changed. <I> **** Actions Taken **** Notified CRS | 02-00-DO-F-5
396973 | CR | 20190718 |  | 3 | SWP-CM-02 Enhancement Recommendations |  |  |  | N | NO | <D> **** Detailed Description **** CWP-CM-02 does not make it clear, that a Temporary Modification should/shall be considered when we have exhausted all troubleshooting and repair options under the WR/WO process and we have no options but to bypass the function or SSC in order to get the right work conditions, scope, parts, ect.. Recommend a procedural enhancement to make it clear. Attachment 9.1 of SWP-CM-02 decision box on whether to do a TM, Design Change or a TASM needs to be updated to reflect that a TASM can be implemented beyond 90 days if a 50.59 AD/SCREEN is performed. So the decision box does not match the allowed requirements on page 14-15. Also, you can have functions of a system bypassed with the main SSC working so the logic on attachment 9.1 does not reflect a realistic logic that can benefit the station. <I> **** Actions Taken **** Notified Supervisor
396974 | CR | 20190718 |  | 4 | Emergent Trend: |  |  |  | N | NO | <D> Over the past three months there have been several instances where gaps in implementing and adherence to the clearance order process occurred. These gaps represent degraded barriers that are in place to protect plant equipment and the safety of our personnel. <I> Discussed issue with Operations Specialist and Performance Improvement Manager. Cross referenced condition reports for review. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review. CR initiated in error, is a duplicate of CR 397010, which is now cross referenced and this CR should be closed to trend.
396975 | CR | 20190718 |  | 3 | Debris and trash in security razor wire |  |  |  | N | YES | <D> **** Detailed Description **** During a protected area and isolation zone walk down an unacceptable amount of trash and debris was observed in the security razor wire as well as inside the isolation zones. This is unacceptable in efforts to maintain equipment reliability and taking pride in our work space. Appropriate notifications will be made to mitigate the situation. <I> **** Actions Taken **** CR iniatied and security supervision notified. <N> **** Equipment Description **** Security protected area and isolation zones Security Equipment coordinator removed the trash and debris from securiy razor wire while utilizing proper PPE. No further action necessary.
396980 | CR | 20190718 |  | 3 | Contractor continued to perform work w/o contract |  |  |  | N | NO | <D> **** Detailed Description **** Contractor continued to perform work with out a valid contract. Contractor did not invoice for the work until nearly 1 year later to realize however accruals were made. Continued work began on 6/28/18, contract expired 6/30/19. Work continued in all of July. The contract expired 6/30/18 and was closed out by SCS. Project team accrued for the expenses, however did not receive the invoice until 6/25/19. <I> **** Actions Taken **** Contractor was called/left message to discuss invoice and that payment can not be made until he has filed his intent/affidavti of wages paid (Public Works Requirement). Contracts notified project team of invoice issue. Contracts to issue a new contract to satisfy the statutory requirements. Once Contractor has satisfied the requirements, payment oof invoice will be made. This CR is for trending purposes, assign to AR-ESD. No further actions required.
396981 | CR | 20190718 |  | 3 | R24 Plant Ignition Source Permits not effectively closed |  |  |  | N | NO | <D> **** Detailed Description **** A total of five expired R24 Plant Ignition Source permits are still open in the plant logging system. Review of the referenced work orders within the permits indicate the work is complete. . It is the responsibility of the work group to ensure permits are promptly closed upon completion of work and fire hazards have been removed, mitigated, or fire protection defense in depth restored at the station. Ensuring an up-to-date permit database allows fire protection to appropriately assess the fire risk to the station. . Numerous attempts have been made to contact the responsible work groups with little effect. . Recommend assigning actions to shops to review Plant Ignition Source Permit log and close open permits as necessary. . Open R24 PISP Permits as of 7-18-19 18-0077, 18-0112, 18-0124, 19-0065, 19-0082 . This is not an equipment related issue. <I> **** Actions Taken **** Tried contacting applicable workgroups multiple times. Initiated CR. <N> Williams Plant Services for 4 of five items. Mech shop for one item.
396983 | CR | 20190718 |  | 3 | R24LL: SOP-GEN-AIRTEST enhancements |  |  |  | N | NO | <D> **** Detailed Description **** The following enhancements should be condisered for SOP -GEN-AIRTEST: Add a precaution and limitation to ensure the Stator Cooling water system and hydrogen coolers are NOT placed in service during the air test Step 5.1.2 should be revised to direct isolation of the hydrogen dryer skid, the hydrogen blower, condition monitor and purity meter rather than leaving it as an option. Step 5.3.5 should be revised to provide a range of different leak rates. Less than 500 SCFD is excellent, no actions required. 500 SCFD to 1200 SCFD is acceptable, A CR should be initiated to document exceeding OEM recommended values but no additional action required. Greater than 1200 SCFD discuss with operations and determine if an ODMI should be prepared. <I> **** Actions Taken **** Discussed with supervisor, initiated CR for recommended changes.
396985 | CR | 20190718 |  | 3 | Isophase bus testing enhancements |  |  |  | N | NO | <D> **** Detailed Description **** PMID 19471 directs inspection and testing of the Isolated Phase Bus. The existing guidance directs performing megger and HIPOT testing per phase on different sections of the bus which results in 6 different HIPOT tests. The model work instructions should be changed to allow testing the entire bus with one test. Individual phase testing and sectional testing only needs to be performed if the test results for the entire bus are unacceptable. This change can save significant time and coordination during refueling outages. <I> **** Actions Taken **** Discussed with Delta Unibus (EOM) and supervisor. Initiated CR to change the model work instructions.
396987 | CR | 20190718 |  | 4 | OG-RF-20A did not start as expected | N | N |  | N | YES | <D> **** Detailed Description **** As the selected primary machine, OG-RF-20A did not start when glycol temperature increased. Currently OG-RF-20B and OF-RF-20C are running. | 02-00-OG-RF-20A
396989 | CR | 20190718 |  | 3 | Generator paralleling enhancement |  |  |  | N | NO | <D> **** Detailed Description **** CGS procedures governing the paralleling of generators direct operators to place and hold the breaker control switch in the close position until the breaker closes. The practice of holding the breaker control switch in the close position means that if the breaker does not close immediately that the synchronizing monitor is the only thing preventing an out of phase parallel. The synchronizing monitor is a reliable instrument and that has regular preventive maintenance and calibration. Paralleling a generator out of phase has the potential to cause significant generator or breaker damage. <I> **** Actions Taken **** The best practice would be to place the breaker control switch in the close position and release the switch if the breaker does not close. The operator would then readjust generator parameters if necessary and attempt breaker closure again only when the synchro scope indicates the correct conditions. Paralleling in this manner means that both the operator and the synchronizing monitor are preventing an out of phase parallel. Informal industry benchmarking shows that while CGS is not the only plant that relies solely on the synchronizing monitor, we are outliers.
396993 | CR | 20190718 |  | 4 | RWCU Demin Hold Pumps Starting too early | N | N |  | N | YES | <D> **** Detailed Description **** Both RWCU Demineralizer hold pumps (RWCU-P-3A and RWCU-P -3B) are starting at approx. 110 gpm flow through each demineralizer which is prohibiting consistent operation of RWCU demineralizers in accordance with the desired flows of approximately 105 â€“ 110 gpm stated in the ODMI for CR 391959. Current flows are 110 gpm for RWCU-DM-1A and 120 gpm for RWCU-DM-1B. Both hold pumps should start at 100 gpm flow through the respective demin. Recommend performing loop cals on the flow transmitters associated with RWCU-P-3A and RWCU-P-3B to allow consistent operation of RWCU demineralizers in accordance with the ODMI. | 02-00-RWCU-P-3A,02-00-RWCU-P-3B
396997 | CR | 20190718 |  | 3 | WO 02022933 01 Needs Enhancement |  |  |  | N | YES | <D> **** Detailed Description **** Steps 4.3.6 and 4.3.7 direct an operator to close DW-V-284 and 285 with the lazy caveat to â€œotherwise N/A this step if not performed.â€ The prerequisite for this work order is that the system has been placed in service. If the system is in service, the valves should be open. While any competent operator will know to N/A those steps, the verbiage is conducive to improper positioning in a situation where the operator is inexperienced and perceiving time pressure. It is my personal opinion that the steps should be omitted entirely, but at a minimum the steps should be formatted as an IF/THEN statement, explicitly directing the operator to close the valves only if they were found in a closed position. Keywords: PWC-V-68 Backflow Preventer 246-290 <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** WO 02022933 Task 01
396998 | CR | 20190718 |  | 4 | HTP-FP-23 CKT 19F Low Temp |  |  |  | N | YES | <D> **** Detailed Description **** The low temp bulb is flashing for circuit 19F on HTP-FP-23. Ambient air temperature is 73Â°F. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** T441 HTP-FP-23, CKT 19F work is in progress per WO 02094185. Feedback provided to Ops 3. | 02-00-HT-HTP-FP/23
397000 | CR | 20190718 |  | 4 | Low Flow CAS-FG-3C | N | N |  | N | YES | <D> **** Detailed Description **** CAS-FG-3C, the oil return flow, has shown very limited flow for the past week. Per the operating logs, "if flow is sluggish at full load, initiate a Work Request to clean return line strainers". <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** T441 | 02-00-CAS-FG-3C
397001 | CR | 20190718 |  | 4 | After Hours Revision to OSP-RHR/IST-Q704 Not Filed |  |  |  | N | NO | <D> **** Detailed Description **** On 7/17/19 an After Hours revision to OSP-RHR/IST-Q704 (Major Rev 041) was issued and two copies sent to the main control room. One copy was used in the completion of ongoing OSP-RHR/IST-Q704, but the other copy was not filed in the Main Control Room surveillance binder IAW SWP-PRO -02. The CRS had custody of the copy but became distracted and did not file it before the end of shift. The next morning it was discovered that rev 040 was still in the surveillance binder. SWP-PRO-02 states that After Hours Procedure Revisions may be implemented by any individual. This individual (or designee) then has the responsibility to ensure the process is completed. <I> **** Actions Taken **** OSP-RHR/IST-Q704 Major Rev 041 was filed correctly on 7/18/19 . CRS was informed they had not completed the filing process. CRS informed their immediate supervisor via email, and the on-duty Shift Manager who provided coaching. Records and Information Management informed. Initiated this CR.
397005 | CR | 20190718 |  | 4 | 15.2.14 FP Zone 1 | N | N |  | N | YES | <D> **** Detailed Description **** The Detectors FP-PHED-1/5, 1/6, and 1/7 on page 22 of 78 15.2.14 Maj rev 12/ minor rev. N/a are being removed/moved/changed out under EC 16607. W.O. 02126624-01 is currently being worked to implement this. Unable to test these heads. Fire System Impairment 18-0219 open. These detector heads will be tested through the performance of the new 15.2.14 once the EC is implemented under W.O. 02126624-18. <I> **** Actions Taken **** Informed Electrical Supervision and Fire Protection (Roy Burson) <N> **** Equipment Description **** Aux Boiler Room T441 | 02-00-FP-PHED-1/5,02-00-FP-PHED-1/6,02-00-FP-PHED-1/7
397010 | CR | 20190718 |  | 2 | Gaps in behaviors to clearance order process |  |  |  | N | NO | <C> MRT Change request: CR 397010 Severity moved from 3 to Severity 2. <D> **** Detailed Description **** Over the past three months there have been several occurrences where gaps in adherence to the clearance order process occurred. These gaps represent behavior shortfalls related to verification/validation and use of triggers. <I> **** Actions Taken **** Discussed issue with the Operations Manager and the Performance Improvement Program Manager, cross referenced condition reports for inclusion in evaluation to be conducted of event documented by CR 396895.
397011 | CR | 20190718 | CAQ | D | Door D-112 Mis-Aligned hinge pin | N | N |  | N | YES | <D> **** Detailed Description **** This CR is to request a WR on door D-112. During an NRC inspection, door D-112 was observed to have a middle hinge pin slightly out of alignment, working its way out of the hinge. . WR to ensure hinge pin is put back into place in the hinge. . The position of the hinge pin in door D-112 would not affect the ability of the door to perform its design function credited in Barrier Functions List FPF 1.6-1 and PPM 1.3.57. . Door D-112 is a credited non-essential fire door and flood (1.09) door. <I> **** Actions Taken **** Initiated CR. This is a non-essential Fire Door. The barrier function of the door is not impacted by the missing middle hinge so no barrier impairment is required. <N> **** Equipment Description **** D -441- - -R0/3.8 - | 02-00-D-DOOR-D112
397012 | CR | 20190718 |  | 3 | Temporary modification for TO-P-BLP |  |  |  | N | YES | <D> **** Detailed Description **** Suggest bypassing TO-PS-TG to allow TO-P-BLP to auto start less than 600 rpms. Currently with the main turbine turning gear switch in the off position there is no power to close TO-PS-TG which is required for TO-P-BLP to auto start. Right now during a plant scram manual operator action is required to start the bearing lift pump less than 600 rpms in order to prevent damaging turbine bearings due to no oil. This pressure switch is put into the circuit to insure that there is oil pressure to the bearing lift pump although it is not required to start the pump in RUN. This was suggested by an INPO evaluator. <I> **** Actions Taken **** Wrote CR | 02-00-TO-P-BLP
397014 | CR | 20190718 |  | 3 | NRC - Questions and Observations - Doors |  |  |  | N | NO | <D> **** Detailed Description **** During an NRC inspection, a question was asked as to why we have very specific criterion established in PPM 15.3.17, Fire door operability check (a more thorough inspection), while PPM 15.1.2 Fire Door Operability Surveillance (a less intrusive inspection) does not provide guidance in step 7.2 on when to issue a CR related to deficient door gap. . Recommend updating PPM 15.1.2 step 7.2 with additional guidance on what would warrant corrective action during performance of PPM 15.1.2 . . This is administrative in nature, not an equipment issue. <I> **** Actions Taken **** Initiated a CR. <N> see EDMS for closure
397016 | CR | 20190718 |  | 3 | NRC-Questions and Observations - Pre-Fire Plans |  |  |  | N | NO | <D> **** Detailed Description **** During an NRC walk down of pre-fire plans, it was observed that both service water pump house drawings utilize the exact same drawing. . Update pre-fire plan service water pump house drawing to identify the correct building with applicable fire protection features. . Assign to AR-TEFP . This issue is administrative in nature, this is not an equipment issue. <I> **** Actions Taken **** Initiated CR.
397018 | CR | 20190718 |  | 3 | Add Heat Trace panel breakers to SOP-ELEC-AC-LU or similar. |  |  |  | N | NO | <D> **** Detailed Description **** Add Heat Trace panel breakers from the following panels to SOP-ELEC-AC-LU or similar procedure. HT-HTP-PTM/1, HT-HTP-PTM/2AA, HT-HTP-PTM/2BA, HT-HTP -PTM/28, HT-HTP-PTM/29, HT-HTP-PTM/30, HT-HTP-PTM/31, HT -HTP-PTM/32, HT-HTP-PTM/4. Restoration positions are currently not available. <I> **** Actions Taken **** Wrote CR.
397022 | CR | 20190718 |  | 3 | Evaluate the need to secure SA-DY-1 with SA-C-1. |  |  |  | N | NO | <D> **** Detailed Description **** There is a note in SOP-CAS-START after step 5.7.12 that states the dryer is designed to be run continuously and should not be cycled with the air compressor. This statement can also be found in the OMM. This conflicts with SOP-CAS-SHUTDOWN step 5.3.6 which tells use to secure the dryer if the compressor will be shutdown for greater than 2 hours. This step is what leads us into securing the dryer every time we do 1000 hour maintenance on the compressor. Recommend evaluating the need to secure the dryer when we secure the compressor and updating the procedure and future clearances as appropriate.
397023 | CR | 20190718 |  | 4 | Universal waste storage area out of compliance |  |  |  | N | NO | <D> **** Detailed Description **** There are multiple universal waste storage issues in the General Services Building (GSB) machine shop universal waste storage area. There are four open-top cardboard boxes full of burned out bulbs that need to be secured in a container with a lid and labeled in accordance with GBP -ENV-17. Additionally, an unknown broken bulb was found in a cardboard drum that needs to carefully removed for disposal by E&RP. Other bulbs obstruct the broken bulb and shards. A vacuum may be required to remove the waste. This is a repeat finding for the area and corrective actions need to be taken to return the area to compliance. <I> **** Actions Taken **** Informed E&RP supervisor and wrote this CR. Attempted to remove broken bulb but stopped due to potential hazards from the broken glass. <N> **** Equipment Description **** Universal Waste storage area in the GSB machine shop
397024 | CR | 20190718 |  | 4 | MT-CRA-6B drips oil onto SWPH B floor | N | N |  | N | YES | <D> **** Detailed Description **** MT-CRA-6B in SWPH B has small oil leaks (drips) accumulating on the floor under the parked location. Oil has been wiped up but pads could not be left to catch additional oil due to SWPH HVAC running which would blow pads out of position. Oil leakage from this crane is a reoccurring issue. (ref. AR 348095). The oil is leaking only onto the SWPH B floor (e.g., is not onto any equipment). This is not active leakage, no drop per minute rate was observed, but the leakage does accumulate over several hours. <I> **** Actions Taken **** Informed supervision, wrote AR | 02-00-MT-CRA-6B
397025 | CR | 20190718 |  | 4 | Backflow preventer PWC-V-162 failed test | N | N |  | N | YES | <D> **** Detailed Description **** PWC-V-162 relief valve failed test. The relief valve should have opened above 2 psid, and it opened at 1.5 psid. Relief valve needs to be replaced <I> **** Actions Taken **** notified supervisor, generated CR and WR <N> **** Equipment Description **** RW 487' R2/15.2 Southwest side of WOA-HV-1 | 02-00-PWC-V-162
397026 | CR | 20190718 |  | 3 | History Briefs generated by EWP contain generic titles |  |  |  | N | NO | <D> **** Detailed Description **** History Briefs automatically generated by EWP provide a generic title, making it difficult to quickly assess the relevance of work associated with an EPN when reviewing completed work in the D075 panel. Request that in the future the title of automatically generated History Briefs contain the associated Work Order Task title to improve efficiency when reviewing completed work. <N> The DataGlance software is working as designed. This was a software customization that was requested as part of EN initial implementation. This CR is requesting that a future software implementation would include the Task title on the history brief to help improve efficiencies. This request has been added to the list of future DataGlance enhancements in FY21.
397027 | CR | 20190718 |  | 4 | TOA-FN-1A and 1B back-draft dampers need repaired | N | N |  | N | YES | <D> **** Detailed Description **** The discharge damper (shown as a backdraft damper on M546 -2) on TOA-FN-1A has one of the damper position arms that has fallen off. The same damper on TOA-FN-1B is periodically making banging noises, and may require adjusted. Please investigate and repair as necessary. see edms screen for pictures of both dampers. <I> **** Actions Taken **** informed Shift Support Supervisor | 02-00-TOA-FN-1A,02-00-TOA-FN-1B
397028 | CR | 20190719 |  | 4 | SA-MON-1 Out of Tolerance | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02115783-01, SA-MON-1 as found data was out of tolerance high. <I> **** Actions Taken **** Informed supervisor, completed calibration per work instructions. Wrote CR to document. All as left data in tolerance.
397029 | CR | 20190719 | CAQ | D | PPC-COMP-8715 issues | Y | N |  | N | YES | <D> **** Detailed Description **** PPC-COMP-8715 has error lamp on PPC-COMP-8715 xfer to VMS failed - reset by STA PPC-TCG-1 has fault lamp illuminated <I> **** Actions Taken **** entered ABN-COMPUTER stopped and restarted 8715 xfer to VMS and indications are returning to normal ERDS was maintained available during this failure. | 02-00-PPC-COMP-8715
397030 | CR | 20190719 |  | 4 | Small Leak through ceiling in RB 548 to RB 522 | N | N |  | N | YES | <D> HP identified very small amount of contaminated water (4 to 10K) on floor of RB 522 coming from above. Upon investigation found water drops coming from ceiling through the concrete. Leakage is one drop every few minutes and did not quantify exactly. Water is falling from RB 522 K2/3.6. No signs of any water on the ground above in accessible areas of 548. Area above leakage also includes RWCU HX Room but no entry was made. <I> Notified SSS and HP of source on RB 522. <N> RB522 K2/3.6 Ceiling - Marked by Contaminated Area tape Investigated RWCU HX room via cameras and found standing water on the floor. Appears to be come from SR-49, but source could not be exactly identified due to installed lead shielding. Catch installed and tygon routed to bucket.
397034 | CR | 20190719 |  | 3 | TMOD EC 16170 projected to remain installed until ~10/2022 |  |  |  | N | YES | <D> **** Detailed Description **** Until recently, removal/restoration of TMOD EC 16170 R0 (TEMP MOD FOR WCH-TS-51B/4) had been anticipated to occur during the Spring of 2020 (WO 02098378 / WO 02113780, Tracking AS 358980-02). Now it appears that restoration of this TMOD may not occur until ~10/21/2022 (reference PMID-RQ 13023-02). See the e-mails attached to the EDMS of this AR CR 397034. Additionally, TMOD EC 16170 R0 currently does not have an Expires On date set in Portal J. This date should have been set to two years from the EC approval date before advancing the TMOD EC to APPROVED in Portal J. TMOD EC 16170 was advanced to APPROVED on 12/15/2016 - if the Expires On date had been set per the existing guidance, this TMOD EC would be EXPIRED status since 12/15/2018. . All issues documented in this AR CR for this TMOD EC are administrative in nature. Recommend/suggest resolution by AR-EFIN. | 02-00-WCH-CR-51B,02-00-WCH-TS-51B/4
397035 | CR | 20190719 | CAQ | D | MS-RV-5B ADS test signal lights losing indication | Y | N |  | N | YES | <D> **** Detailed Description **** MS-RV-5B ADS test signal lights for channel B and D on panel H13-P631 are losing indication. This has occurred multiple times in the past 2 weeks that the lights bulbs for channel B and D were discovered extinguished. These light bulbs have been changed multiple times. The most recent instance the light bulbs were removed from the socket and warmed up for approximately 20 minutes with body heat then re-inserted into the socket and the lights turned back on. Recommend investigating and repairing the cause of the light bulbs to extinguish for MS-RV-5B ADS test signals channel B and D on P631, the current light bulbs have been installed for approximately 1 week. <I> **** Actions Taken **** Warmed up light bulbs and verified they re-illuminated discussed this issue with other operators and determined it has happened frequently since R24 with multiple operating crews and operators. <N> **** Equipment Description **** Main Control Room on h13-P631 upper portion Bulb illumination problems are not isolated to MS-RV-5B, other ADS valves have periodic bulb illumination problems. Circuit should be evaluated for adequacy of bulb design application.
397036 | CR | 20190719 |  | 3 | TMOD EC 17889 R0 INSTALLD status but possibly restoration IP |  |  |  | N | YES | <D> **** Detailed Description **** In Portal J, TMOD EC 17889 R0 (TEMP MOD TO BYPASS HWC ISOLATION RELAY) to jumper out HSSF-RLY-P2/2 is INSTALLD status and its 460-R TMOD OPS milestone has not been signed. AWAIT/C WO 02146628 recently (~7/18/19) replaced and PMT'd HSSF-RLY-P2/2 (tasks 01 and 06). However, TMOD EC 17889 R0 restoration WO 02146591 (tasks 02 and 03) remain yet to be advanced to WORKING. It appears that restoration of this TMOD EC is in-progress but its 460-R TMOD OPS milestone has not been signed. This is an administrative issue. <N> TMOD EC 17889 is installed (02146591-01 completed). TMOD EC 17889 is not in the process of being removed (02146591 -02 approved). No further actions are necessary. | 02-00-HSSF-RLY-P2/2
397037 | CR | 20190719 | CAQ | D | CRD-HCU-0627 low pressure | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-0627 <I> **** Actions Taken **** OPS2 re-pressurized per SOP-CRD-HCU | 02-00-CRD-HCU-0627
397038 | CR | 20190719 |  | 3 | Operations Training Management failed to follow TDI-09 |  |  |  | N | NO | <D> **** Detailed Description **** Operations Training Management failed to follow the guidance of TDI-09 which states â€œUpon entry into the ILC, all watchstation qualification certifications for the candidates should be removed (EO, RO, STA, IA).â€ At least one RO candidate for ILC-24 was identified with current EO qualifications. Recommend Operations Training evaluate for further instances of procedural non-compliance. <N> Operations Training is working with Operations Scheduler to ensure all remaining qualifications for ILC-24 students are removed IAW TDI-09.
397039 | CR | 20190719 |  | 4 | MT-CRA-1 oil leak | N | N |  | N | YES | <D> **** Detailed Description **** MT-CRA-1 oil leak was previously documented under CR 368240, WR 29136938. CR was of course closed and then the WR cancelled. MT-CRA-1 appears to be leaking oil. as evidenced by the string of oil absorbants under it. Please investigate a repair and or a catch to eleiminate the slip hazard as there is not a pad under every pool of oil. listed as rework since i had to write it up again. <I> **** Actions Taken **** redocumented the problem | 02-00-MT-CRA-1
397040 | CR | 20190719 |  | 4 | shaft ground brushes misalignment is worse CR 396162 | N | N |  | N | YES | <D> **** Detailed Description **** shaft ground brushes misalignment is worse. CR 396162 was previously written to note the problem it has a due date of 8/22/19 with its wR at H/app please compare the two sets of pictures and plan action accordingly. s <I> **** Actions Taken **** wrote CR <N> **** Equipment Description **** Main Generator shaft ground brushes
397041 | CR | 20190719 |  | 3 | Failed FC paths on AIX Server118 | N | N |  | N | YES | <D> **** Detailed Description **** Failed Fiber Channel paths on FC0 adapter on SERVER118 indicate a failed adapter port, SFP, or cable. Additonal troubleshooting will be needed to determine exact cause of path failures. No data has been loss occured as there are redundant ports on the FC adapter in the server. The data is still flowing over the 4 paths on FC1. <I> **** Actions Taken **** Initial troubleshooting. Creation of the CR. More troubleshooting to be done. Recommend NCAQ-3. <N> **** Equipment Description **** Corp Server Equipment. Non plant-impacting <S> Replaced Switch SFP in port 3 of FC-A switch in Kootenai Datacenter and this resolved the issue. SERVER118 is now showing all FC paths enabled on both FC ports. This CR can be closed as resolved... NCAQ-4.
397042 | CR | 20190719 |  | 4 | COND Booster Pump TI's Inconsistent | N | N |  | N | YES | <D> **** Detailed Description **** The condensate booster pump oil temperature gauges are indicating inconsistently. Many of the bearing return oil temperatures are actually indicating as lower than the cooler outlet temperature, most notably the pump inboard bearing return line for the C booster pump, which shows oil dropping by 30Âº. A hand check revealed that oil piping temperatures are as expected, so pump/motor integrity is not in question. <I> **** Actions Taken **** Informed MCR Checked Temps Manually <N> **** Equipment Description **** T441 | 02-00-COND-P-2A,02-00-COND-P-2B,02-00-COND-P-2C
397043 | CR | 20190719 |  | 4 | Ops Shift Manning Less Than 5 EOs due to Illness |  |  |  | N | NO | <D> **** Detailed Description **** On 7/19/19 the day shift EO manning was reduced to 4 EOs after the start of shift due to a sudden illness. Safe shutdown operator responsibilities were maintained as well as FB and FB leader. Another EO was called out. There was an approximate 90 minute period of time with reduced staffing before the called out EO arrived and assumed the shift.
397044 | CR | 20190719 |  | 4 | XD 3 out of service, needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** XD 3 out of service, went into home screen, notify security prior to work. <I> **** Actions Taken **** XD 3 went into home screen, placed out of service, notified supervision, CR/WR generated <N> **** Equipment Description **** Inside the search area | 02-00-SEC-XD-3
397045 | CR | 20190720 |  | 4 | XD 6 failed midnight test, maintenance needed | N | N |  | N | YES | <D> **** Detailed Description **** XD 6 failed its midnight test, no alarm, contact security prior to work. <I> **** Actions Taken **** failed test, placed out of service, notified supervision, CR/WR generated <N> **** Equipment Description **** Search area (PAAP) | 02-00-SEC-XD-6
397046 | CR | 20190720 |  | 3 | Excessive TOCs in T-2 | N | N |  | Y | YES | <D> **** Detailed Description **** Writing this CR to evaluate oil leakage from our CAS compressors . WR 29149414 started and ran all CAS compressors and CAS-C-1A had excessive TOCs of 210 PPM from the blowdown line. T-2 has excessive TOCs and is currently caution tagged and being pumped into barrels daily. Looking at past CRs the CAS compressors are often re-filled with oil. Recommend contacting the vendor to determine if our CAS compressors have exessive or normal oil consumption and normal oil discharge at the blowdown line . Recommend contacting the vendor of the compressor oil Sullair 24TK to determine if there is a better way of filtering the T-2 sump. I donâ€™t know if the the pillows are an efficient way of removing that specific type of oil (silicon based oil that does not emulsify). <I> **** Actions Taken **** hanging a caution tag on CAS-C-1A <N> Sampled T2 sump TOC=34.5 PPM on 8/3/19 | 02-00-CAS-C-1A
397047 | CR | 20190720 | CAQ | D | Low Pressure Alarm HCU 42-59 | Y | N |  | N | YES | <C> CR reopened to cross reference additional AR 397130 and WP 02146549, marked completion required box, then taken back to complete <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-4259. Dispatched OPS-2 to investigate. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-4259 low pressure. OPS2 re-pressurized per SOP-CRD-HCU. <I> **** Actions Taken **** Initiated CR for Trending. <N> **** Equipment Description **** RB522 | 02-00-CRD-HCU-4259
397048 | CR | 20190720 |  | 4 | MET Bravo Outputs to MCR are Frozen | N | Y |  | N | YES | <D> **** Detailed Description **** All of the outputs from MET B locked up yesterday at 14:03. Request Maintenance repair as required. | 02-00-MET-WMON-1B,02-00-MET-WMON-2B
397049 | CR | 20190720 |  | 4 | CW-CT-2C level is high (Distribution Deck Water Level) | N | N |  | N | YES | <D> **** Detailed Description **** while performing rounds it was noted that CW-CT-2C level is high. <I> **** Actions Taken **** Initiate a AR/WR, inform the CRS. | 02-00-CW-CT-2C
397050 | CR | 20190720 |  | 3 | Increased losses to RCC Surge tank level. | N | N |  | N | YES | <D> **** Detailed Description **** On July 11th at 2230 the rate of losses from RCC surge tank changed drastically from approximately 1â€ per week to 8â€ per week. EDNA shows a level drop from to 26 inches to 17 inches in a weeks time. This is a significant change from the previous 2 weeks and an EDNA trend from January 1st to April 15th shows very little losses historically over that time frame. <I> **** Actions Taken **** CR written. SM informed. Trend noted on EDNA. <N> **** Equipment Description **** Rx Bldg 548' | 02-00-RCC-TK-1
397051 | CR | 20190720 |  | 4 | Bad Thermostat | N | N |  | N | YES | <D> **** Detailed Description **** during performance of WO 02117003-01 found thermostat HT-TS-CL-SKID-1/3. Thermostat was full of sludge and was extremly corroded. Terminals are extremly corroded. Thermostat needs to be replaced. Left tagged out under local clearance. <I> **** Actions Taken **** COnnacted SM WROTE CR and WR | 02-00-HT-TS-CL-SKID-1/3
397052 | CR | 20190720 |  | 4 | DEH-TI-42 is reading OOS Low, possible Calibration Issue. | N | N |  | N | YES | <D> **** Detailed Description **** DEH-TI-42 is reading 102Â°F. Minimum is 105Â°F. This reads the Temp of the DEH Fluid Resevoir. The other specs, (pressures and D/Ps), do not appear high enough to believe this low of a temp. The Main Conrol room has the Resevoir temperature from DEH-TE-4. It reads 112Â°F. Temperature taken later with a Thermal Imager shows 109Â°F. DEH-TI-42 needs calibration or replacement. Here is CR/WR/WO numbers from a simular problem on this guage 381418, 29143232, 02116773. | 02-00-DEH-TI-42
397053 | CR | 20190720 | CAQ | D | CCH-PI-3B, was low during start of CCH-CR-1B. Added H2O | Y | Y |  | N | YES | <D> **** Detailed Description **** Per Page 15 of OSP-CCH/IST-M702, step 7.1.41e, This is a Trend Only CR for Adding water Per Step 7.1.41c. | 02-00-CCH-CR-1B
397054 | CR | 20190720 | CAQ | D | Received SLC tank high level alarm | Y | Y |  | N | YES | <D> **** Detailed Description **** Received SLC Tank Level High/Low alarm, H13-P603.A8.5-8. SLC-LS-600 and Computer point X077 indicate SLC level is greater than 5050 gallons. Ops 2 was dispatched to investigate local indication. Local indication reads 5000 gallons and steady. Demin Water makeup to SLC tank was verified closed and sealed. Bubbler flow rate is normal. Recommend performance of ISP-SLC-X301, Standby Liquid Control Tank Level â€“ CC. <I> **** Actions Taken **** Notified CRS and OPS 2. Verified local indication. Initated CR and WR <N> **** Equipment Description **** RB 548 | 02-00-SLC-LI-601,02-00-SLC-LS-600
397055 | CR | 20190720 |  |  | 3 of 4 ASD Glycol systems have low resistivity |  |  |  | N | YES | <D> Glycol Resistivity is low in ASD 1A/1, 1A/2, and 1B/1 channels as indicated on GY-CI-10A1, 10A2, and 10B1 . The low spec is 5 MOhms and these are all below that spec. <I> Informed MCR. Wrote CR/WR. <N> CR Canceled at the request of OPS Supervisor, this is duplicate of CR 397056. | 02-00-GY-CI-10A1,02-00-GY-CI-10A2,02-00-GY-CI-10B1
397056 | CR | 20190720 |  | 4 | 3 of 4 ASD Glycol systems have low resistivity | N | N |  | N | YES | <D> **** Detailed Description **** Glycol Resistivity is low in ASD 1A/1, 1A/2, and 1B/1 as indicated on GY-CI-10A1, 10A2, 10B1. The low spec is 5 MOhms and these are all below that spec. Portal J crashed while writing AR #397055, therefore a new AR is being created. <I> **** Actions Taken **** Informed MCR. Wrote CR/WR. | 02-00-GY-CI-10A1,02-00-GY-CI-10A2,02-00-GY-CI-10B1
397057 | CR | 20190721 | CAQ | D | W-DOOR-C204 not functioning as designed | N | N |  | N | YES | <D> **** Detailed Description **** While performing PPM 15.1.2 it was observed that W-DOOR -C204 will not close and latch when released from approximately 1/3 open as the procedure requires. The door needed to be held open approximately 80 degrees in order for it to close and latch when released. Security has also received several door alarms on this door in the past week. <I> **** Actions Taken **** Notified CRS and wrote CR. <N> This is a non-essential fire door. BI 19-0304 opened and hung in the plant. | 02-00-W-DOOR-C204
397058 | CR | 20190721 | CAQ | D | R-DOOR-R207 screw broken off | Y | N |  | N | YES | <D> **** Detailed Description **** While performing PPM 15.1.2 it was observed that the upper screw is broken off inside of the door latch plate. The fire door passed all requirements for the survellance. The lower screw on the door latch plate was able to hold the door latch plate in place. <I> **** Actions Taken **** Notified CRS and wrote CR. | 02-00-R-DOOR-R207
397059 | CR | 20190721 | CAQ | D | Wire for camera CAM-PTZ-383 through fire door | N | Y |  | N | YES | <D> **** Detailed Description **** While performing 15.1.2 it was observed that a camera wire for CAM-PTZ-383 was laid under and going through fire door R-DOOR-R508. The wire was wrapped with white tape 12 inches in length on both sides of the door. The camera and wire were both removed so that there is no longer a need for a barrier impairment. <I> **** Actions Taken **** Informed CRS and wrote CR <R> REP/REGE assignments cancelled with Compliance Supervisor concurrence. | 02-00-R-DOOR-R508
397060 | CR | 20190721 | CAQ | D | CRD-HCU-1419 low nitrogen pressure | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-1419. Dispatched OPS-2 to investigate. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-1419 was due to low nitrogen pressure. OPS2 re-pressurized per SOP-CRD-HCU and the alarm is now clear. A nitrogen leak has been previously identified and a Work Order is in planning (see cross references). This AR/CR submitted for trending. <I> **** Actions Taken **** Submitted AR/CR to document the occurrence. Notified the Control Room Supervisor and Shift Manager. | 02-00-CRD-HCU-1419
397061 | CR | 20190721 |  | 4 | HP-EQ-C015122 Cemistry IPM-8 OOS due to Low Gas Pressure | N | N |  | N | YES | <D> **** Detailed Description **** The IPM-8 (HP-EQ-C015122) removed itself from service due to low P-10 gas pressure. The mylar detectors are visibly not taut. There appears to be sufficient P-10 gas on both banks, but the center gage on the ACCU-TROL Manifold Control unit appears to have zero pressure on the center gage. <I> **** Actions Taken **** Discussed with chemistry personnel. Initiated this AR/CR. | 02-00-HP-EQ-C015122
397062 | CR | 20190721 |  | 4 | SEC-XD-5 Inop | N | N |  | N | YES | <D> **** Detailed Description **** SEC-XD-5 is inoperable due to compressor warning. <I> **** Actions Taken **** SEC-CD-5 placed out of service, electrical maintenance and security managemnt notified, and CR/WR generated. <N> **** Equipment Description **** PAAP | 02-00-SEC-XD-5
397063 | CR | 20190721 | CAQ | D | SFS-STORM-025 indiicates Yellow | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of OSP-SFS-D101, SFS-STORM-025 was found to display YELLOW. This condition has been long standing (ref. WR# 29144180 and 29147889). The previous WRs written to identify/correct this issue have been CLOSED/COMPLETED by crediting the completion of ICP-SFS-A301. This has not satisfactorily addressed the YELLOW condition. (Or OSP -SFS-D101 needs to be changed to address when a WR truly needs to be generated.) This WR written per OSP-SFS-D101. <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** TG 471W | 02-00-SFS-STORM-025
397064 | CR | 20190721 | CAQ | D | B5B-P-1 (Fire Truck) fuel level 3/4. | N | Y |  | N | YES | <C> CR reopened to cross reference additional WO 02140763, marked completion required box, then taken back to complete <D> **** Detailed Description **** Found on Sunday logs Fire Truck (both fuel tanks) at 3/4F. Logs specify for it to be Full. Do not have manpower to allow driving it to fuel station today. <I> **** Actions Taken **** Notifited CRS, initiated AR. | 02-00-B5B-P-1
397065 | CR | 20190721 |  | 4 | Oscillograph Started Alarm 15:54 7/21/19 | N | N |  | N | NO | <D> **** Detailed Description **** MCR received an Oscillograph Started alarm (H13-P800.C4.4 -3). Ops 3 reports the J7 Sensor â€“ 500KV Neutral Ground Overcurrent alarm was tripped and was able to be reset. No abnormalities were found with plant equipment (Vacuum Breakers, Controllers, Inverters). TR-S and TR-B voltages were 239/236/239 and 118/118/118 KV respectively. BPA Dittmer reports that the Watorma-Knight and LoMo-Hanford 500KV lines both tripped and locked out; they believe this was due to wild fires in the area. BPA reports there is no indication of damage, that the RAS did not initiate and there was no significant frequency deviation.
397066 | CR | 20190721 |  | 3 | CRO1 Tours not properly synchronizing |  |  |  | N | YES | <D> **** Detailed Description **** On 7-21-19 the CRO1 (At the Controls Reactor Operator) watchstation tablet failed to download information from Esoms to the tablet. The logs taken will upload to the system properly, but the synch fails with the following message: "Requesting Reading Details was unsuccessful. Please try to Synch again." This persisted after attempting a Soft-reset on the tablet, Restarting the desktop computer, and attempting to download the tours on a spare tablet. This appeared to start coincident with a grid hit and oscillograph start (15:53). <I> **** Actions Taken **** Informed Control room supervision, contacted IS department <N> **** Equipment Description **** Main Control Room This issue is still being tracked under the xrefd CR. We applied the vendor fix to resolve this issue, however, further work may need done to upgrade to next version. This work will be performed under the original CR that is xrefd. Closing this CR.
397067 | CR | 20190721 | CAQ | C | RHR-P-3 oil appears dirty | Y | N |  | N | YES | <C> AR/CR was still open so I added WO 02128633 and a check mark to the Completion required box on the WR and left action open. <D> **** Detailed Description **** While performing operator rounds it was observed that the oil in the oil sightglass for RHR-P-3 appeared a dark brown color and was not translucent like other oil sighglasses in the plant. The pump was running at the time and was not making any abnormal noises. Consider testing oil for wear or degredation or just changing the oil. <I> **** Actions Taken **** Notified CRS and wrote CRS. | 02-00-RHR-P-3
397068 | CR | 20190721 |  | 4 | HP-EQ-42808 fan belt is cracked | N | N |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was observed that the fan belt on HP-EQ-42808 is cracked and needs replaced. <I> **** Actions Taken **** Wrote CR and notified CRS | 02-00-HP-EQ-42808
397069 | CR | 20190721 |  | 4 | REA-FU-2B green power on light socket broken | N | Y |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was observed that the green power on (LT-1) light socket for REA-FU-2B was not illuminated. A new bulb was obtained and upon insertion of the bulb the light socket could be twisted 360 degrees. The light socket for the bulb is one in which the operator would insert the light bulb, press in, and twist the bulb to the right a little. The bulb could be turned 360 degrees within the light socket after insertion into the socket. <I> **** Actions Taken **** Wrote CR and infomed CRS | 02-00-REA-FU-2B
397070 | CR | 20190722 |  | 3 | RWCU-V-34 body to bonnet gasket leak | N | N |  | N | YES | <C> MRT Change request: CR 397070 Severity moved from 4/Trend Repair to Severity 3 assigned to AR-MNTPROG. The rework cordinator has entered this issue into the rework program. no further actions is required under this AR. <D> **** Detailed Description **** RWCU-V-34 body to bonnet gasket leak approx 14 drops/ min. <I> **** Actions Taken **** Notified MCR Laborers installed catch funnel, routed to floor drain | 02-00-RWCU-V-34
397071 | CR | 20190722 |  | 4 | SAS video WS needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** SAS video worksation is not functioning as desigend. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Security notification made, CR/WR initiated <N> **** Equipment Description **** SAS video WS 1 located in the control room
397073 | CR | 20190722 |  | 4 | Nalco Leak on CF-P-41 Discharge Line | N | N |  | N | YES | <D> **** Detailed Description **** Nalco leak on CF-P-41 Discharge line between CF-FG-41 and CF-PCV-41 at CF-FG-41 fitting. <I> **** Actions Taken **** Notified CRS | 02-00-CF-FG-41
397075 | CR | 20190722 |  | 4 | Gen fld gnd brush seat fail during testing | N | N |  | N | YES | <D> **** Detailed Description **** during gen field ground test received 4.800.C4 drop 10-3 brush seat failure alarm. CR directed from WOT 02116003 <N> continuous alarm during test. | 02-00-E-GEN-1
397085 | CR | 20190722 |  | 3 | TRB Outage Increased Scope: OPDS CVTs/CTs Diagnostics |  |  |  | N | NO | <D> **** Detailed Description **** With respect to the October week of the 14th 2019 TRB outage window, scope was added to the Backup transformer diagnostic PM to also do the diagnostics on all of the Open Phase Detection System (OPDS) CVTs and CTs. This newly added scope exceeds available resources to be performed in the same LCO limited hours online outage window as the Backup transformer diagnostic and other pre-existing TRB outage PMs. . The added scope for OPDS CVTs/CTs testing is separate from TRB scope and should be moved to its own PM to be scheduled for a separate online window or a refueling outage. Also consider increasing the frequency from four years for CTs and decrease scope of CVTs (see below). Reference: WO 02112838 E-TR-B: TRANSFORMER DIAGNOSTIC TESTING & PMRQ 00005853-02. 1. OPDS-CT-B1/A, B1/B & B1/C are oil filled IOSK 123 CTs (CVI DWG 1265-01,06) 2. OPDS-CVT-B1/A, B1/B & B1/C are oil filled type TEMP 123 CVTs (CVI DWG 1265-01,09) Per BPA Preventative Maintenance Guides 115 kV associated oil-filled CTs diagnostics are performed on an 84 month periodicity. OPDS-CT- B1/A, B1/B & B1/C show installation on 4/28/2017. Consider frequency change to 84 months versus being combined into the TRB diagnostics PM which is every 4 years. . Per BPA Preventative Maintenance Guides CVTs are monitored by measuring their secondary voltages every 6 months. Diagnostics are triggered based and are driven by the results of the secondary voltage results. Consider changing scope to measuring secondary voltages and remove diagnostics/make condition based. <I> **** Actions Taken **** Notified Supervision, System Engineer and Unit Coordinators. Included BPA Instrument Transformer Preventaive Maintenance Guide in the EDMS. <N> **** Equipment Description **** TRB Diagnostics PM
397086 | CR | 20190722 |  | 3 | Procedure revision not properly implemented |  |  |  | N | NO | <D> **** Detailed Description **** CR 344974 was written to augment the protection scheme for DG1 and DG2 in PPM 1.3.83 by adding posting locations for D-DOOR-D110 (room D102) and D-DOOR-D111 (D-101). These rooms contain DO-P-1A and DO-P-1B which are required for DG1 and DG2 operability. The procedure revision referenced that they were in the DG1 and DG2 rooms. <I> **** Actions Taken **** Informed SM, PSRO, and Ops procedure group supervisor.
397087 | CR | 20190722 | CAQ | C | Performance of Source Check Caused Entry Into ODCM Action | N | Y |  | N | NO | <D> **** Detailed Description **** A shift technician was performing the daily source checks for the post treatment offgas radiaiotn monitors. In this he started the check of both in parallel rather than series causing both monitors to be Inop for approximately one minute. <I> **** Actions Taken **** The CRS and supervision was informed. Recommend updating the CSP-INST-D201 reference use procedure to have a caution step warning of the issue with source checking both monitors at once. Provided immediate coaching to the shift tech and to all other technicians in the interim.
397091 | CR | 20190722 |  | 3 | Look at process for ensuring changes made to PMIDâ€™s or proc |  |  |  | N | NO | <D> **** Detailed Description **** Look at process for ensuring changes made to PMIDâ€™s or procedures include the effect they make on the corresponding PMID or procedure are also changed. An example is OSP-SLC/IST-Q701 and PMID 17131-01, 02, 03. See cross references for details
397093 | CR | 20190722 | CAQ | C | HPCS-V-1 incorrect grease applied to stem | Y | N |  | N | YES | <D> **** Detailed Description **** During the full PM on HPCS-MO-1, the grease on the stem was found to be MOV Long Life (cream color) instead of Mobile 28 (bright red). The last time the grease was inspected was 2015 (R22) during an actuator refurbishment and stem replacement (via WO 02048837). To fix this condition requires the stem nut to be removed and thoroughly cleaned (PMT is a diagnostic test). <I> **** Actions Taken **** Discussed with OCC & shift manager After CR was initiated, MOV engineering performed a walkdown with electricians and concluded the grease was Mobile 28 and was deteriorated. The stem was thoroughly cleaned and new Mobile 28 was installed. Related information to OCC and Shift manager CR states the stem was replaced, in reality the stem nut was replaced (see applicable WO). Degraded grease can impact margin via the coefficient of friction (COF) between the actuator stem nut and the valve stem. It also impacts the rate of loading (ROL). ROL is a load sensitive behavior attribute to the effects of load (magnitude and rate of change) on lubricated surfaces. The COF and ROL is determined by ENW's testing which is identified in Technical Memorandum TM-2088 "Design Stem Factors and Margins for Stem Factor Degradation and Rate of Loading Effects." ME-02-02-25 uses a conservative COF of 0.20 and 15% for Rate of Loading. HPCS-V-1 was last tested on 5/29/2015. The as-left close margin = 20.5% and opening = 150.5%. MES-10 states any margin greater than 10% is considered high margin. There is additional margin that can be shown via the following: Design Close COF = 0.20, Actual Close COF = 0.107 Design Open COF = 0.20, Actual Open COF = 0.096 Design Close Packing = 2,500 lbs, Actual Packing = 1,417 lbs Design Open Packing = 2,500 lbs, Actual Packing = 1,513 lbs ME-02-02-25 accounts for an additional 5% stem factor degradation. Additionally, a degraded stem lubrication can result in additional stem nut wear. During R22 actuator refurbishment, the stem nut was replaced. As-left diagnostic testing shows the new stem has significant amount of margin in thread wear: Design Closing zero Plateau = 0.351, actual = 0.107 Design Opening Zero Plateau = 0.351, actual = 0.278 Based on the values above there is significant amount of stem thread engagement (margin). With the degraded stem factor, there is sufficient margin for HPCS-V-1 to perform its design functions as required. There are no additional requirements or actions needed. The degraded stem lubrication was cleaned off the stem and new lubrication was applied to the stem per PM WO (PPM 10.25.4). <R> Cancelled the REP/REGE assignments with Licensing Manager concurrence. | 02-00-HPCS-MO-1,02-00-HPCS-V-1
397097 | CR | 20190722 |  | 4 | Planning: WD hold put on 02117006-01 PM with A01 freq, |  |  |  | N | NO | <D> **** Detailed Description **** Planning: WD hold put on 02117006-01 PM with A01 freq,, PM active checked so PM should come out in the READY status. Walkddown is not required for this task. <N> ***General Notes*** per the planning guide, all work orders require a walk down code to be added so the craft can review the work order. it is the supevisors responcibility to apply a graded approach to walk downs.
397102 | CR | 20190722 |  | 4 | WM Indicators did not run on Monday July 22. |  |  |  | N | NO | <D> **** Detailed Description **** An investigation revealed that the process was correctly started, but was hung-up on a refresh of an Oracle view. The database logs indicated that this view had issues (i.e. generated errors) since the rebuild of the PASS-PROD database the previous Thursday, yet it continued to function correctly the next three nights, thus giving no indication of a problem. On the fourth night (early Monday morning) it failed and prevented process completion. <I> **** Actions Taken **** The problem view was recreated and the WM Indicator processes were rerun. All views used by WM Indicators have been independently tested and verified.
397107 | CR | 20190722 | CAQ | D | WO: 02137015-01 ISP-RHR-M901 RHR-PS-22B OOT | N | Y |  | N | YES | <D> **** Detailed Description **** During the performance of this procedure it was discovered that RHR-PIS-22B was found out of tollerance. The pressure switch was adjusted back into Admin Limits. CR Written for trending purposes. <I> **** Actions Taken **** CR written for tracking purposes. <N> **** Equipment Description **** 501 RX P021. | 02-00-RHR-PIS-22B
397108 | CR | 20190722 |  | 4 | CST FLOOR SEALS NOT INSTALLED CORRECTLY | N | N |  | N | NO | <D> **** Detailed Description **** WHILE WORKING WO 02033659-01 CST BERM FLOOR SEAL FITTINGS NOT INSTALLED CORRECTLY; CRAFT & ENGINEERING IDENTIFIED TWO FLOOR SEALS THAT WERE NOT INSTALLED CORRECTLY PER MANUFACTURER DESIGN. THE SEALS & FITTINGS WERE NOT INSTALLED PER DESIGN BECAUSE OF AN INTERFERANCE IN THE SLEEVE NOT ALLOWING PROPER INSTALLATION OF PRESSURE RINGS & GROMMETS. <I> **** Actions Taken **** - INITIATED THIS CR - WILL PROVIDE PLANNING & WILLIAMS WITH ALTERNATE SOLUTIONS FOR SEAL <N> Williams Plant Services. Work is currently in-progress (WORKING). Williams contacted Engineering to field verify the installation of the pressure clamps. The 4" pressure clamp can be installed as directed. The two, 2" pressure clamps cannot. One of the two will require a revision to the package with Engineering direction to be installed different then the design. The second 2" pressure clamp will need to either be left as is or reconfigured differently.
397109 | CR | 20190722 |  | 3 | Increase in work scope for FP Zone 1 - WO# 02126624 | N | N |  | N | NO | <D> **** Detailed Description **** WO# 02126624 directs moving and/or replacing existing Fire Protection detectors in Zone 1 (per Parent EC 16607). This work is still in progress. While reviewing recently completed work in the Zone, project personnel determined that detectors 1-5, 1-6 & 1-7 (existing DS-2 photoelectrics) were re-installed, rather than replaced (with OP-121 photoelectric type detectors). This action matches the direction given in the work order instructions. This appears to be due to unclear information in the EC. The EC narrative in Table 2, Detector Action Table, indicates â€œrelocateâ€ detector versus â€œmove & replaceâ€. The verbiage implies bagging and reusing existing detector base and head. Whereas, drawing 217-84,23 wiring detail shows the terminations points for new detector bases. Since the work is still in progress (FSIP still open), there is no impact to the station â€“ this is a work scope issue. <I> **** Actions Taken **** The work order has been revised to replace the listed detectors. Wrote CR. Notified Fire Protection Engineer. CR issued to Design Engineering to update EC via FCR.
397110 | CR | 20190722 |  | 3 | Incorrect Nomenclature on PRM-RR-4 | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02130071-01, procedure 16.1.11, step 7.1.4, it was discovered that where the Yokogawa Recorder PRM-RR-4 should say "STACK MONITOR IN TEST" it says "STARTUP" <I> **** Actions Taken **** Discussed with CRS and Supervisor to do an editorial per telecom. Continued with surveillance. When writing CR, discovered that this also affects procedure 16.1.12, step 7.1.2. Recommend that PRM-RR-4 gets changed to "STACK MONITOR IN TEST" to match procedures . Nomenclature changed within WR 29150618. <N> **** Equipment Description **** 501RW MCR
397113 | CR | 20190722 |  | 3 | PPM 1.3.74 Repair return process is not effective |  |  |  | N | NO | <D> **** Detailed Description **** Multiple times the repair return process has not led to the proper implementation or repairs that are needed for plant equipment. Suggest making a separate task or work order to follow through with the process and get the proper input and guidance for who makes the determination of what to do with the equipment when removed from the plant, at this time the planner makes the determination of the repair process. We have multiple things on site that never got a decision made that are worth a large sum of money, or may be the only spare piece that we own. <I> **** Actions Taken **** Notified my supervisor and initiated this condition report.
397123 | CR | 20190722 |  | 3 | Yakima Building 441' Men's Bathroom Rejuvenation |  |  |  | N | NO | <D> **** Detailed Description **** Pleaseâ€¦pleaseâ€¦PLEASE remodel the menâ€™s room on the 441â€™ elevation of the Yakima Building as it is beyond disgusting, unsanitary and has been for years. This is due in most part to urine-saturated grout around and below the two urinals. The poor Janitors assigned to the Yakima Building do their best; however, its plain and simple, you cannot clean the uncleanable. The nauseating stench of urine remains immediately after having been cleaned. The Â½-inch grout directly below the urinals is a terrible design to start with and from what I have been told, this tile was installed almost 20 years ago. This remodel could literally consist of tile and urinal replacement only. The stalls, toilets and sinks are all in good shape and seem to function well. Please replace all the tile in the menâ€™s room with updated materials that resist urine saturation, are easy to clean and will help to maintain sanitary conditions that personnel in the Yakima Building deserve along with auto flushing urinals. My previous CR for this request some years ago resulted in the steam cleaning of the tile. This was a very short and temporary solution to an issue that in my opinion is quite simple to resolve. This is the most frequently used restroom on site as it facilitates RP, Laborers, Security, Operations and various craft personnel 24/7. It is also a restroom at an operating Nuclear Power Plant, not some back alley dive bar in Tijuana. I actually felt embarrassed that our contractors for the outage had to use such an unsanitary restroom. The pictures uploaded into EDMS were taken only a few hours after the bathroom was cleaned. Workers in the Yakima building and most certainly the janitorial staff would be elated with a rejuvenated menâ€™s room. The womenâ€™s restroom was completely updated a couple years ago and this renovation to the menâ€™s room would be considerable less intrusive and costly. <I> **** Actions Taken **** Uploaded pictures into EDMS <N> **** Equipment Description **** Yakima 441' Men's Room
397124 | CR | 20190722 | CAQ | D | HPCS-M-P/1 'C' phase heater cable megger low | Y | N |  | N | YES | <D> **** Detailed Description **** Megger readings for 'C' Phase heater cable, after determ of both ends does not meet exceptance criteria. (W.O. # 02131311) <I> **** Actions Taken **** Informed Electrical Supervision, OCC, Engineering <N> This CR appears to identify the wrong component. Per teh WO, the â€œCâ€ phase conductor for HPCS-H-GEN, the space heater for HPCS-GEN-1C was tested and meggered at 48.2 Mohm. There is no mention of HPCS-M-P/1 in the WO. | 02-00-HPCS-H-GEN
397125 | CR | 20190722 |  | 4 | Calibration Dimensional Lab affected air conditioning |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Following the scheduled power outage in the Kootenai building the Dimensional Lab had temperature issues identified upon entry into the lab area. <I> **** Actions Taken **** Supervison notified promptly and then monotored temperature as it appeared initially that the temperature was taking time to stabliize. However, after a few hours the temperature was not getting back to normal so I had the lead technician contact facilities to assist in coming over to assess the situation. Due to height they will come back tomorrow adn further assess and make recommendations on repairs needed. Currently this lab is down and will not be able to operate any calibrations. Another location is being lookrary use.
397126 | CR | 20190723 | CAQ | C | Primary Containment O2 levels are rising | Y | N |  | N | YES | <C> MRT Change request: CR 397126 Severity moved from D/Trend Repair to Severity C assigned to AR-ICMAINT. <D> **** Detailed Description **** Primary containment oxygen levels started increasing at approximately 1430 on 7/22/19. Between that time and midnight on 7/23, O2 levels rose approximately 0.23%. ISP-CMS/PRM-M402 was started on day shift on 7/22 per WO 02137291. This surveillance contains steps to replace particulate filters on CMS-SR-21. This has been the source of leaks causing this indication in the past. <I> **** Actions Taken **** Wrote this CR. Uploaded edna trend to EDMS. | 02-00-CMS-SR-21
397127 | CR | 20190723 |  | 4 | Unexpected system response durning RWCU A BW; cycle frozen | N | N |  | N | YES | <D> **** Detailed Description **** While performing a backwash of RWCU-DM-1A per SOP-RWCU -DEMIN, the automated backwash sequence stopped advacing after step 5.3.7 (q). The red CLEANING CYCLE light is still illuminated and the amber SHUTDOWN light never illuminated. The backwash cycle is currently frozen. Valve linup was verified. System was functioning normally before incident. | 02-00-RWCU-DM-1A
397130 | CR | 20190723 | CAQ | D | Low Pressure Alarm Received HCU 42-59 | Y | N |  | N | YES | <C> CR reopened to cross reference additional WP 02146549, marked completion required box, then taken back to complete <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-4259. Dispatched OPS-2 to investigate. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-4259 low pressure. OPS2 re-pressurized per SOP-CRD-HCU. This HCU last had a low pressure alarm on 7/20/19. <I> **** Actions Taken **** Notified CRS. Initiated CR and WR. <N> **** Equipment Description **** RB522 | 02-00-CRD-HCU-4259
397131 | CR | 20190723 |  | 4 | Report Only - Wasp Sting |  |  |  | N | NO | <D> **** Detailed Description **** On 07/22/2019 at the end of the day, an employee got stung by a wasp walking to his car while leaving the site. No first-aid administered. <I> **** Actions Taken **** Notified Site Support Contractor Manager and Facilities to eradicate Wasp nest that is outside of building 11 (Southwest corner) .
397138 | CR | 20190723 | CAQ | C | (IST) RHR-RV-30 replacement frequency | Y | N |  | N | NO | <D> **** Detailed Description **** RHR-RV-30 failed IST as-found testing under WO 02129666-02 on 5/27/19 (CR 394338). A replacement valve was installed under the same work order as originally scheduled. In lieu of testing, the IST Program and ASME OM Code allow thermal relief valves to be replaced at a frequency of 10 years, unless performance data indicate more frequent replacements are necessary. The original CR did not address the impact of the failed test on future replacement frequency. Recommend AR-SECOMP to evaluate. <I> **** Actions Taken **** Wrote CR. . RHR-RV-30 was last replaced under WO 01179299 on 5/10/11, and the as-found test of the removed RV also failed, see CR 240213.
397142 | CR | 20190723 |  | 4 | Oscillograph start | N | N |  | N | NO | <D> **** Detailed Description **** Oscillograph start at 1013 am due to Trip of Lomo powerhouse 500k line caused by relay testing with no reclose. No equipment damage or need for an emergent outage. No remedial action scheme initiated. Our indications showed a neutral 500k ground oscillograph start that reset. <I> **** Actions Taken **** RWCR cleared the oscillograph start after noting it was on 500k ground neutral. Dittmer was called for information
397148 | CR | 20190723 |  | 4 | Chronic 1.5 MWe deficiency due to CW system cleanliness | N | N |  | N | YES | <D> **** Detailed Description **** CW system cleaning is being scheduled for R-25 (PMID 25515). Since the last cleaning in 2012, the system has seen a drop in CW flow from 580 kgpm to 565 kgpm. This drop in flow is worth 1.5 MWe. This issue should resolve when the system is cleared of debris and sediment and tunnel lining repairs are made. This CR is written for trending and tracking purposes only. <I> **** Actions Taken **** Initiated CR. Discussed with CW system engineer. No additional actions needed at this time. <N> **** Equipment Description **** CW System
397149 | CR | 20190723 | CAQ | C | Wrong PMIDs referenced in TSW Specs |  |  |  | N | NO | <D> **** Detailed Description **** AED SPC 350 listed PMIDs 18573, 18572, 18571, and 18570 for cleaning and inspecting the main generator hydrogen coolers (TSW-HX-7A/B/C/D). These PMIDs were retired to a new PMID 23366 that has the required PMS for the heaters. Recommend action to Mechanical Design group to update the specs. accordingly. <I> **** Actions Taken **** Initiated this CR
397150 | CR | 20190723 | CAQ | C | sight glasses not replaced per work order parts not availabe | Y | N |  | N | YES | <C> CR Re-opened to change Request from MRT. MRT Change request: CR 397150 Severity 3 moved from NON-CAQ Severity C CAQ (AR-MNTPLAN). <D> **** Detailed Description **** W.O.# 02066849-01 HPCS-M-P/1 Repair Oil Leak Sight Glass Upper and Lower has steps for replacing both the upper and lower sight glasses. The replacement sight glasses in the Material Request associated with the work order were incorrect. Vendor contacted and GE part number identified as M80A660086P002 for the correct sight glass replacements. There are no replacement sight glass on site currently. Research of documentation shows that only the upper sight glass needs to be replaced. Recommend ordering replacement part(s) and rescheduling the replacement of the upper sight glass. <I> **** Actions Taken **** Contacted Electrical Supervision, OCC, and Procurement. Generated this condition report and associated work request. | 02-00-HPCS-M-P/1
397152 | CR | 20190723 |  | 3 | Lessons Learned from Power Outage |  |  |  | N | NO | <C> reopened at the request of R. Hatten <D> **** Detailed Description **** CR to track progress on issues resulting from power outage. recommend assign to AR-CALSERV. <I> **** Actions Taken **** Initiated CR to track issues resulting from power outage.
397160 | CR | 20190723 |  | 3 | EC-11288 had insufficient PPM reviews & PRM-RR-4 validation |  |  |  | N | NO | <D> **** Detailed Description **** CR-397110 documents discrepancy between PPMs 16.1.11, 16.1.12 and PRM-RR-4 Programmed Message 1. The recommendations and the error identified are incorrect. The approved PRM-RR-4 IMDS (Rev 000) was not reviewed when permission was given to do an Editorial per Telecon on 16.1.11. Message 1 is INSTRUMENT IN TEST that is used for consistency throughout the instruments associated with Yokogawas. 16.1.11 has been revised 3 times and 16.1.12 has been revised once since EC-11288 installation in 2017. <I> **** Actions Taken **** PRM-RR-4 Message 1 requires correction as do PPMs 16.1.11 and 16.1.12 to match approved engineering document.
397161 | CR | 20190723 | CAQ | C | Incorrect fuse installed during PM. | Y | Y |  | N | YES | <D> **** Detailed Description **** Work order 02117111-01 is a test and inspect PM for SW-42 -4A6D, an ATM3 fuse was installed for the control power when it should have been a FNQ-R-3 fuse. <I> **** Actions Taken **** Wrote WR# 29150633 to replace the fuse. <N> ***General Notes*** planner didnâ€™t order the fuses like they should, which prompted the supervisor to order the parts. The supervisor doesnâ€™t normally order fuses for this component and he ordered the wrong fuse. The work order package did say to verify that the fuse installed is the same as the one that is removed. This did not occur. This issue was caught after the PMT, which is what should have happened. Coaching of all involved individuals has occured. | 02-00-SW-42-4A6D
397162 | CR | 20190723 | CAQ | D | Received Oscillograph Started alarms | N | N |  | N | NO | <D> **** Detailed Description **** Startup and Backup voltages are as follows: E-TR-S A: 240 B: 238 C: 240 E-TR-B A: 120 B: 119 C: 119 The following sensor was tripped and reset: J15 BPA reports the following: Cause was many Lightning strikes in the area away from CGS. And multiply lines involved. No damage reported as of yet and all have reclosed. They said currently our area has not been involved. The 230kv was involved Time of the events were 2037 and 2045 with multi alarms each time. No RAS was initiated with gird frequency normal
397163 | CR | 20190723 | CAQ | D | Received Oscillograph Started TR-S and TR-B trouble alarms | N | N |  | N | NO | <D> **** Detailed Description **** Plant controllers and equipment response was normal. Reference AR 397162 Startup and Backup voltages are as follows: E-TR-S A: 240 B: 238 C: 240 E-TR-B A: 120 B: 119 C: 119 The following sensor was tripped and reset: J15 only. BPA reports the following: Cause was many Lightning strikes in the area away closer to CGS No damage reported as of yet and all have reclosed. They said they will keep us updated in there is and involvement of power supply to CGS. The 230kv was involved Time of the events was 2234. No RAS was initiated with gird frequency normal
397164 | CR | 20190723 | CAQ | D | Received TG BLDG 441' FSP2 trouble drop 15-3 | N | N |  | N | YES | <D> **** Detailed Description **** Received TG BLDG 441' FSP2 trouble drop 15-3. Dispatched OPS3 to investigate. OPS 3 reported a ground fault is in. Alarm is locked in and re-flashed periodically. | 02-00-FP-CP-FSP2
397165 | CR | 20190724 | CAQ | D | OSP-SW-M103 DG SW flow outside of the recomended flow range | Y | N |  | N | YES | <D> **** Detailed Description **** OSP-SW-M103 DG SW flow outside of the recomended flow range but ok. Note (5) says to write a CR if flow is outside the reccommended range. The recommended range is 940 to 1000 gpm. Actual flow was 1055 gpm. Note one states "the iupper flow values are quidelines and not operation limits". So this CR is being written per note 5 of appendix 9.1 of OSP-SW-M103. <I> **** Actions Taken **** Discussed with CRS and wrote CR. <N> DG SW flow outside the recommended range. High flow is not a deficiency as noted by the SM and ops chose not toadjust the flow in band. I recommend closing the AR just to trend the occurance. No maintenance required. | 02-00-SW-FIS-9
397166 | CR | 20190724 |  | 4 | Right OG calibration bottle is < 300# needs changed. | N | N |  | N | YES | <D> **** Detailed Description **** Right OG calibration bottle is < 300# needs changed. OPS 3 logs states "Log N2 pressure from RIGHT bottle. Initiate a Work Request to change the OG Analyzer N2 calibration gas bottle if bottle pressure is LT 300 psig.". pressure is less than 300 please change out the bottle <I> **** Actions Taken **** wrote CR as directed by a form. <N> **** Equipment Description **** T441
397167 | CR | 20190724 | CAQ | C | Overload block for HPCS-42-4A2D failed overload testing. | Y | Y |  | N | YES | <D> **** Detailed Description **** 02116991-01 is the ESP-MOVTOL-B301 to test the overloads of the contactor. The first test failed and the block did not open in 80 seconds against a criteria of 22-80 seconds. The second test failed at 118 seconds with the same criteria. The third test passed at 33.12 seconds. It seems to the testers that the heaters audibly opened but the overload block did not open the circuit and the aux contact remained closed. <I> **** Actions Taken **** Informed the OCC and Engineering for resolution. | 02-00-HPCS-42-4A2D
397168 | CR | 20190724 |  | 4 | Received Oscillograph Started and IN-2A/2B trouble alarm | N | N |  | N | NO | <D> **** Detailed Description **** Plant controllers and equipment response was normal. The Inverter noted no issues when OPS2 responded Startup and Backup voltages are as follows: E-TR-S A: 240 B: 238 C: 239 E-TR-B A: 120 B: 119 C: 119 The following sensor was tripped and reset: J7 only. BPA reports the following: The cause may have been from the DC link to California tripping off and back on. No damage reported. The 500kv was involved Time of the events was 0045. No RAS was initiated with gird frequency normal.
397169 | CR | 20190724 | CAQ | D | FP-CP-FSP2 ground fault alarm recieved clears when door shut | N | N |  | N | YES | <D> **** Detailed Description **** FP-CP-FSP2 ground fault alarm recieved clears when door shut. Responded to FP-CP-FSP2 alarm and found a ground faul alarm. Alarm would not reset. when the panel door was shut the alarm cleared, when the door was opened the alarm returned. Left the panel door shut and alarm clear. <I> **** Actions Taken **** informed the MCR. wrote this cr. | 02-00-FP-CP-FSP2
397170 | CR | 20190724 |  | 4 | Old steam tunnel camera equipment hasn't been removed | N | N |  | N | YES | <D> **** Detailed Description **** Old steam tunnel camera equipment hasnt been removed. Please see attached picture and also please note how it is accumulationg more extension cords than it ever used. Please arrange for removal and disposal as neccesary. <I> **** Actions Taken **** wrote CR. <N> **** Equipment Description **** old steam tunnel camera equipment t 501 east side
397171 | CR | 20190724 |  | 4 | PSR-O2H2A-SR48/1 shows high Dissolved Oxygen for RX H2O | N | N |  | N | YES | <D> **** Detailed Description **** PSR-O2H2A-SR48/1 recorder shows High Dissolved Oxygen 199.5 ppb for SP-8 (Reactor Water). Meter fluctuates between 0.0 and 0.19 ppm and flashes "CHECK THE PROBE". <I> **** Actions Taken **** Verified proper valve line-up for PSR-SR-48 per PPM 12.5.44. Pulled Grab Sample of SP-8 to verify Dissolved Oxygen < 5 ppb. Wrote WR for PSR-O2H2A-SR48/1. <N> **** Equipment Description **** RW 487' Chem Lab. | 02-00-PSR-O2H2A-SR48/1
397176 | CR | 20190724 | CAQ | C | MT&E Found out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0066421 Mitutoyo Caliper- model 505675 was found OOT & rejected. Used during cal cycle.occurrence WO 02059041-07. EFIN is evaluate. <N> DEF# 7071A- attached EDMS Eval from EFIN
397177 | CR | 20190724 |  | 4 | MT&E found out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0059421 Mitutoyo Micrometer - model 103-260 found OOT & adjusted within specs. Not used during Calibration cycle. No plant impact No Action Required. <N> DEF# 7070A
397179 | CR | 20190724 | CAQ | D | Expanded scope for cable replacement for DG3 space heater | Y | N |  | N | NO | <D> **** Detailed Description **** During performance of cable replacement for DG3 space heater cables per WO 02131311, craft identified that penetration seal foam was installed inside the conduit. Further evaluation identified these were flood barriers. Planning created new tasks to remove and replace foam and fire protection created the associated barrier impairment. CR written to document the unexpected foam barrier not identified during planning and preparation and the resulting expansion in work scope/duration as a lessons learned for cable replacement activities.
397180 | CR | 20190724 | CAQ | C | RECORDS SUBMITTED WITHOUT A SIGNED TRANSMITTAL |  |  |  | N | NO | <D> **** Detailed Description **** A STACK OF QAR RECORDS WAS SENT TO RECORDS CONTROL WITHOUT A SIGNED TRANSMITTAL BY ELECTRICAL MAINTENANCE. PLEASE REFER TO SWP-REC-02 SECTION 4.3.2 FOR THE SUBMITTAL PROCESS. <I> **** Actions Taken **** NOTIFIED SUPERVISION. SENDING RECORDS BACK TO ELECTRICAL MAINTENANCE FOR CORRECTION AND RE-SUBMITTAL.
397181 | CR | 20190724 | CAQ | C | Replacement part for HPCS-M-P/1 drain LOU issue | Y | N |  | N | NO | <D> **** Detailed Description **** Replacement part for HPCS-M-P/1 lower oil reservoir drain plug did meet the limitations on use for the current installed motor. It had been approved for the previously installed motor. The replacement part was not an identical replacement and required a substitution evaluation. This was not identified until work was in progress per WO 02066849. This has resulted in a delay to completion of this work activity. Engineering will complete the evaluation prior to installation of the plug on the HPCS -M-P/1. Not an equipment issue. CR written to document potential lessons learned for safety system window preparation.
397184 | CR | 20190724 |  | 4 | Degraded grout seal on electrical manhole ES-14 | N | N |  | N | YES | <D> **** Detailed Description **** Electrical manhole ES-14 has degraded grout seal on two sides. Request maintenance support to replace grout seal between concrete and steel entrance. Unknown if there is water penetration at this time. <I> **** Actions Taken **** CR/WR generated <N> **** Equipment Description **** ES-14 manhole, South east corner of PA along fence line.
397185 | CR | 20190724 |  | 4 | Employee experienced discomfort |  |  |  | N | NO | <D> **** Detailed Description **** While at an offsite team building activity employee experienced discomfort after participating in the activity. Employee reported that this discomfort comes from a personal medical condition. <I> **** Actions Taken **** Employee reported to management the discomfort and management followed up with employee to get details about the situation. Notified Management HR, Safety, Occupation Health, Performance Improvement Supervisor, ESD management and ESD GM.
397186 | CR | 20190724 |  | 3 | GBP-HR-43, Work Attire needs clarification |  |  |  | N | NO | <D> **** Detailed Description **** GBP-HR-43 Paragraph 2.3.2 states â€œTights and leggings must be worn with dresses, skirts, city shorts or tops that extend beyond the waist.â€ Recommend revising this section and clarifying the intent. As written, it sounds as if leggings AND tights are required if you wear a shirt that extends beyond your waist.
397187 | CR | 20190724 | CAQ | C | HPCS-42-4A3C alarm overload heater block screw wont tighten | Y | N |  | N | YES | <D> **** Detailed Description **** HPCS-42-4A3C - starter for HPCS-MO-15 has a stripped screw hole for the B phase 4th overload heater - alarm function. While restoring from starter pm under work order 02118276 -01, it was discovered that the B phase alarm function overload heater lead screw will not torque down. The terminal screw hole is stripped out. Engineering is evaluating alternate options for repair which will be performed under the existing work order 02118276-01. Recommend Engineering evaluate the current torquing methods listed on 10.2.10 attachment 9.6 to ensure listed torque values are not excessive for this application. <I> **** Actions Taken **** Notified SM and Engineering. Generated CR <N> **** Equipment Description **** 4A MC in DG3 room | 02-00-HPCS-42-4A3C
397189 | CR | 20190724 |  | 3 | (QA) Organizational Change Omission |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Operations Organizational Change (Dated 12/12/17), for removal of SCBA requirements for Shift Support Supervisor, failed to identify and track the alternative of required of respiratory protection training. As SCBA requirements are currently in Shift Support Supervisor Qualification Duty Area (TSO1) there is no violation of requirements. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Operations/TS Programs Audit, AU-OP-TS-19. Informed Quality and Operations, recommend assignment to Operations.
397190 | CR | 20190724 |  | 3 | (QA) Four INOP Equipment Sheets Should Be Closed |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Four active inoperable (INOP) equipment sheets should be closed since the equipment has either been repaired or returned to service. Out of the approximately 32 open inop sheets reviewed 4 can be closed. Inaccurate inoperable equipment sheets is a configuration control issue that could prevent testing or maintenance on equipment, or unnecessary escalation in action statements. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Operations/TS Programs Audit, AU-OP-TS-19. Informed Quality and Operations, recommend assignment to Operations. <N> All four LCOTR sheets were closed following feedback from the QA organization. The learning was communicated to all SRO's via email to ensure that sheets are closed as appropriate, and if necessary to open new sheets if an issue recurs.
397192 | CR | 20190724 |  | 3 | (QA) 3 LARs Did Not Follow Processes in SWP-LIC-03 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Multiple Impact Review Forms and Implementation Plans, required by SWP-LIC-03 "Licensing Document Change Process" for three different License Amendment Requests (LARs) were missing or incomplete. Documents that were present were found to be missing approvals and many failed to identify and list affected procedures. These procedure use and adherence issues have the potential to miss one or more of those actions, but there no consequences identified in these cases. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Operations/TS Programs Audit, AU-OP-TS-19. Informed Quality, Regulatory Affairs, and Operations, recommend assignment to Regulatory Affairs <N> This CR is being closed to assignment 1 in CR 397198. Which will revise SWP-LIC-03 and FORM 24341. D. Johnson Assignment added to XREF AR to folllow completion. Approved closure via supervisor approval.
397193 | CR | 20190724 |  | 3 | (QA) Superseded TSP-MSRV/IST-R701 Incomplete PPM Updates |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Surveillance TSP-MSRV/IST-R701 was superseded, however one License Basis Document and six procedures were not revised and continue to reference the surveillance. Use of procedures with incorrect references to superseded surveillance procedures risk missed surveillances and delays in implementation. A review identified no missed surveillance requirements. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Operations/TS Programs Audit, AU-OP-TS-19. Informed Quality and Operations, recommend assignment to Operations.
397194 | CR | 20190724 | CAQ | D | Position 2 on SW-TI-2B/2F is reading incorrectly. | Y | Y |  | N | YES | <D> **** Detailed Description **** Position 2 on SW-TI-2B/2F in SWPH B for SW B pond temperature is reading incorrectly at -175.2 *F when it should be reading approximately 65*F . This is an H101 reading for logs. <I> **** Actions Taken **** Initiated this CR <N> **** Equipment Description **** Position 2 on SW-TI-2B/2F in SWPH B. | 02-00-SW-TI-2B
397195 | CR | 20190724 | CAQ | C | (QA) LBIE Screening Form Refers to Outdated Step in FLEX-01 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Licensing Basis Impact Evaluation (LBIE) form (electronic and manual) refers to an outdated step in FLEX-01 "FLEX Program". The result is difficulty in complying with the administrative guidance on this LBIE Screening Form using a nonexistent step in FLEX-01. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Operations/TS Programs Audit, AU-OP-TS-19. Informed Quality, Regulatory Affairs and Operations, recommend assignment to Regulatory Affairs
397196 | CR | 20190724 | CAQ | C | (QA) License Basis Document Not Revised |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) LDCN-17-009 eliminated 2 year surveillance testing of Safety Relief Valves (SRV) via TSP-MSRV/IST-R701; however License Basis Document (LBD) IST-4 was not revised to allow the change. The LDCN retired the 2 year surveillance in the Preventive Maintenance Program, and the associated surveillance procedure was subsequently superseded. A review identified no missed surveillance requirements. The failure to ensure a license basis document is current could lead to a loss of regulatory margin. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Operations/TS Programs Audit, AU-OP-TS-19. Informed Quality, Technical Services Engineering, Regulatory Affairs, and Operations, recommend assignment to Technical Services Engineering
397198 | CR | 20190724 | CAQ | C | (QA) 7 of 20 LDCNs Did Not Follow Steps in SWP-LIC-03 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Seven of twenty Licensing Document Change Notices (LDCNs) reviewed did not follow a step within SWP-LIC-03 "Licensing Document Change Process". This is a procedure use and adherence issue with no known actual consequences. Potential consequences include regulatory exposure with not following the approved LDCN process as described in SWP-LIC-03. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Operations/TS Programs Audit, AU-OP-TS-19. Informed Quality Regulatory Affairs, and Operations, recommend assignment to Regulatory Affairs
397199 | CR | 20190724 | CAQ | C | (QA) LBID Did Not Follow Steps in SWP-LIC-02 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) One of twenty-five Licensing Basis Impact Determinations (LBIDs) reviewed did not follow steps in SWP-LIC-02 "Licensing Basis Impact Determinations" and the USA 50.59 Resource Manual. This is a procedure use and adherence issue with no known actual consequences. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Operations/TS Programs Audit, AU-OP-TS-19. Informed Quality Regulatory Affairs, and Operations, recommend assignment to Regulatory Affairs
397200 | CR | 20190724 |  | 3 | (QA) Power Block Housekeeping Not Up To Standards |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Quality identified housekeeping issues throughout the power block. Work in progress signs are not being maintained current and several reference the same (WO 01158000). Additionally, equipment was found not in approved storage locations, such as a fire extinguisher (stored upright inside white iron) and grounding straps. Substandard power block housekeeping could degrade regulatory margin as the NRC previously expressed concerns for the length of time work in progress signs are staged in the power block (AR-CR 222238). See EDMS for detailed description and photos. <I> **** Actions Taken **** This was identified as a Deficiency during the Operations/TS Programs Audit, AU-OP-TS-19. Informed Quality, Maintenance and Operations, recommend assignment to Maintenance
397202 | CR | 20190724 |  | 3 | (QA) Operators Not Enforcing Housekeeping Standards |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Quality identified several housekeeping issues while on tour with Equipment Operators. Operators are inconsistently identifying and reporting housekeeping issues, and in one case a CR was not initiated on an equipment deficiency. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Operations/TS Programs Audit, AU-OP-TS-19. Informed Quality and Operations, recommend assignment to Operations.
397204 | CR | 20190724 |  | 3 | (QA) RPI-5.0 is Not Aligned with 2 Site-Wide Procedures |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) RPI-5.0 "Preparation and Submittal of Regulatory Correspondence" still contains outdated information that no longer aligns with SWP-IRP-02 â€œCorporate Nuclear Safety Review Boardâ€ (CNSRB) and SWP-LIC-03 "Licensing Document Change Process." The result is the inability to comply with the administrative guidance stated in RPI-5.0 for approvals of certain regulatory correspondence. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Operations/TS Programs Audit, AU-OP-TS-19. Informed Quality, Regulatory Affairs, and Operations, recommend assignment to Regulatory Affairs
397205 | CR | 20190724 |  | 3 | (QA) SWP-RXE-01 References Deleted Procedure |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) SWP-RXE-01, Reactivity Management Program, Attachment 8.2 lists PPM 1.4.1, Plant Modifications, as a cross reference to implement step 4.5.4a however, PPM 1.4.1 had been canceled. PPM 1.4.1 was a legacy administrative controls process used for Plant Modifications prior to Passport when BDCs were being issued to modify the power block. The current administrative process used for Plant Modification and Configuration Control is SWP-DES-01. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Operations/TS Programs Audit, AU-OP-TS-19. Informed Quality, Reactor/Fuels Engineering, and Operations, recommend assignment to Reactor/Fuels Engineering
397209 | CR | 20190724 |  | 3 | No WiFi in RW507 |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** While working a Stack Monitor surveillance, it was decided to use one of the cordless WiFi Cisco phones on the RW507 because the area is covered with miscellaneous materials, making it difficult to run phone cord to the phone outlet. The WiFi has no service. <I> **** Actions Taken **** Used LAN phone plugged into phone outlet. Discussed with Supervision about have the area cleaned up as this also limits travel path to PRM-SR-1 to bring in tools and test equipment.
397210 | CR | 20190724 |  | 4 | Dead bats found around buildings 26 and 64 |  |  |  | N | NO | <D> **** Detailed Description **** Two dead bats in separate locations over about a 2 hour period were discovered near building exterior doors on 23Jul2019. The first dead bat was on the ground a few feet away from the Roosevelt room (exterior) door at the east end of Bld 64 (Willamette) and appears to have been removed. The second dead bat is just inches away from the alternate exit closest to the stairway on the north side of Bld 26 (Deschutes) and was still there as of noon today. There was no visible signs for the batsâ€™ deaths. If multiple bats are dying on the site it should be investigated. Recommend any newly found deceased bats be tested for rabies [may require collaboration with BFHD]. There is a news article dated 19July2019 that a 21 yr old in BC, Canada died of rabies after exposure to a bat. <I> **** Actions Taken **** Told OCC Health about the first one found. Told supervisor and coworkers in D15. Informed Facilities IAW guidance provided in GBP-ENV-20.
397211 | CR | 20190724 |  | 3 | ALARA Suggestion, Frametome Coatings |  |  |  | N | NO | <D> **** Detailed Description **** Framatome has a new line of products, QuarTec coatings, that have been recently used in nuclear power stations. It is said to have the ability to minimize radiological contaminants from adhering to components. This could have the potential to greatly reduce dose, especially on the refuel floor during outages. <I> **** Actions Taken **** Recommend research of the product and any other like products for use at our station. Sources: NUCLEARSTREET .COM and World Nuclear News.
397215 | CR | 20190724 |  | 4 | MS-LIS-24A EPN label is broken | N | N |  | N | NO | <D> **** Detailed Description **** The EPN label for MS-LIS-24A is broken in half, needs a new label made and replaced. <I> **** Actions Taken **** Filled out label request form and initiated WR to remove old label per the label request form. <N> **** Equipment Description **** MS-LIS-24A
397222 | CR | 20190724 |  | 4 | Printer Ink low on 3 ASD printer | N | N |  | N | YES | <D> **** Detailed Description **** During walkdwon it was noticed that printout from ASD printer is not readable for B2 and A2 drives.The printouts are not readable from B2 drives. Recommend replacing toner cartridge on printer. <I> **** Actions Taken **** Notified supervisor and shift manager. | 02-00-RRC-XR-1A2,02-00-RRC-XR-1B2
397223 | CR | 20190724 | CAQ | C | 3HPCS-0393: FOAM INSULATION AND CABLE REMOVAL | Y | N |  | N | YES | <D> **** Detailed Description **** While removing foam insulation and existing cable from the 2â€ conduit (3HPCS-0393) water was discovered in approximately 50â€™ of the conduit. In addition to the water there was also 55 foot Â¼â€ rope that was discovered inside the conduit along with other small debris. Reference WO 02131311-02. Pictures will be uploaded to EDMS. <I> **** Actions Taken **** Noitfied the OCC and initiated CR. Rope and cable have been removed. <N> **** Equipment Description **** HPCS-GEN-1C SPACE HEATER. 3HPCS-0393 Assign to AR-PPROG
397224 | CR | 20190724 |  | 3 | (QA) Declining Maintenance Performance |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Quality Services has determined that efforts taken to date to improve human performance behaviors as described in the Area Requiring Management Attention (ARMA) issued on April 10, 2019 (AR-CR 392031) have not been effective. This has resulted in several human performance errors prior to, during and subsequent to the R-24 refueling outage, with the most recent event involving working on equipment not protected by a clearance order. Quality is concerned that performance will not improve until Maintenance personnel internalize these events, own their performance, and change behaviors and attitudes. See EDMS for additional details. <I> **** Actions Taken **** Discussed issue with Quality Management and the Maintenance Manager
397225 | CR | 20190724 |  | 4 | ASD Glycol systems have low resistivity | N | N |  | N | YES | <D> **** Detailed Description **** During walk down it was noticed that glycol resistivity on GY-CI-10B2 is 4.761 Mohms cm which is below specs. Recommend replacing filters for all drives. Refer AR 00397056 for low resistivity on all 3 drives. <I> **** Actions Taken **** Informed supervisor and shift manager. | 02-00-GY-CI-10B2
397227 | CR | 20190724 |  | 3 | (NRC) Resident questioned potential PPM 1.3.83 change |  |  |  | N | NO | <D> **** Detailed Description **** The NRC resident questioned whether LPCS-V-5 should be added to the the list of items protected when the LPCS system is protected.
397228 | CR | 20190724 |  | 3 | (NRC) Resident questioned RB 522' Man-lift storage |  |  |  | N | NO | <D> **** Detailed Description **** The NRC resident questioned whether the RB 522' steam tunnel plug area was an approved storage location for a Man-lift. There is currently a Man-lift stored on these floor plugs.
397229 | CR | 20190724 | CAQ | D | ARM-RIS-1 spurious alarms | N | Y |  | N | YES | <D> **** Detailed Description **** Refueling Floor Rad High alarm recieved and cleared several times from 1945 to 2030. see attached EDNA trace. The alarm setpoint for ARM-RIS-1 is 300 mR/hr, HP reports the dose rates on the Refueling floor are ranging from 0 to 4 mR/hr and stable. This CR can be closed to trend <I> **** Actions Taken **** Contacted HP, discussed with Shift Supervision | 02-00-ARM-RIS-1
397230 | CR | 20190724 |  | 4 | DW-DWS-4 , safety shower has been inoperative since 5/2/2018 | N | N |  | N | YES | <D> **** Detailed Description **** DW-DWS-4 was found to run continuously on 5/2/2018 WR 29142326 was written repairs were performed and the Caution tag was cleared on 12/26/2018. The shower still leaked and was now isolated and tagged with a new clearance. I wrote cr 396941 and wr 29150532 to get these elevated and the CR is "AR COMPLETE NO ASSIGNMENTS" and the WR is "CANCEL to WO 02137391", which is at plan 12/27/2018. Please note we have a portable shower and eye wash can located there so compensatory measures have been taken. The point of the cr was that an emergency shower might have a higher priority to be fixed than six months to over a year. Discussed with supervision who directed this CR. <I> **** Actions Taken **** wrote CR . See cross referenced AR's. This issue goes back at least to 2010. There is a history of the shower control valve leaking by, CR/WR is written, WR replaces valve or internals, states problem is fixed, then it repeats. Obviously there is a problem that requires more than simply replacing parts, likely a rerouting of the piping or vacuum breaker or air gap install. | 02-00-DW-DWS-4
397232 | CR | 20190725 |  | 4 | Facilities Lighting in need of repair and/or adjustment |  |  |  | N | NO | <D> **** Detailed Description **** Exterior wall sconces on Building 17 (Wenatchee) are continually flickering / pulsing at night. Two lights on the west side of the building and one light on the east side of the building have been observed on multiple nights. The condition started following the partial loss of facilities power / loss of a phase during R24 (6/13/19). <I> **** Actions Taken **** Generated CR. Notified Facilities. <N> **** Equipment Description **** Building 17 (Wenatchee) Facilities Lighting (Exterior)
397233 | CR | 20190725 |  | 4 | Flocculator high headloss | N | N |  | N | YES | <D> **** Detailed Description **** Flocculator headloss was discovered out of spec high at 10 in hg. PWC-AV-2 would lift and headloss would drop to 2 in hg. This process would repeat every 20-30 seconds. High headloss lamp on PWC-CP-1 was not illuminated. Effluent turbidity was 0.063 NTU. <I> **** Actions Taken **** Informed CR. Backwashed flocculator. Wrote CR. | 02-00-PWC-AV-2
397234 | CR | 20190725 | CAQ | D | RWCU-FCV-33 and RWCU-P-1A ASME Non-Conformances | N | Y |  | N | YES | <D> **** Detailed Description **** AR 282022, â€˜NRC has questioned the RWCU Quality Group reclassificationâ€™, identified a generic issue with the RWCU system for which a large portion of the system (essentially everything downstream of RWCU-V-4) and large number of components (41 total) were replaced as non-ASME components following an unauthorized reclassification of the system from ASMEIII-3 to B31.1. In 2013, the plant documentation was restored to show the system was ASMEIII -3, but the physical plant was not restored back to the original ASMEIII-3 design. A functionally assessment was written to track the non-conformances and provide justification for continued functionality of these components since the system as a whole was impacted by the large number of non-conformances. A plan was developed to obtain NRC permission to reclassify the RW portion of the system back to B31.1. That modification has been completed (see EC 15262) and the large number of RW components are now conforming to the plant design for the RW portions of the system. RWCU-P-1B was replaced in 2017. The remaining two items that have not been restored are RWCU-FCV-33 and RWCU-P-1A. RWCU -FCV-33 has an open modification to restore it back to ASMEIII-3 (see AS 297874-07). The modification of RWCU -FCV-33 is being tracked through the normal modification process. RWCU-P-1A will be run until it fails due to the very high dose associated with its replacement and the low safety significance of the non-conformance. These two open non-conformances no longer warrant tracking through a Functionality Assessment since the majority of the system has been restored to a conforming condition with the completion of EC 15262. The correction of these two remaining non-conformances will be made through the corrective action process, commensurate with their safety significance. This CR will track these open non-conformances and the associated Work Orders. | 02-00-RWCU-FCV-33,02-00-RWCU-P-1A
397235 | CR | 20190725 |  | 4 | Nalco Leak on CF-P-41A Discharge Line | N | N |  | N | YES | <D> **** Detailed Description **** The leak originally reported in CR 00397073 resulted in a puddle of Nalco several feet in diameter in the area around CF-P-41A <I> **** Actions Taken **** Informed CRS / Chemistry. Placed absorbant pads around leak. Placed Danger tape around area. Secured pump. CR contacted enviromental per ABN-HAZMAT. <N> GBP-ENV-18 section 4.5 states: "Spills of nonvolatile materials contained on impervious surfaces (e.g.,concrete, asphalt) are not spills to the environment. The assessment of threat to the environment includes consideration of such factors as material released, quantity, location, and time to complete cleanup." This is not a spill to the environment due to being confined to the concrete floor of the circ water pumo house. | 02-00-CF-P-41A
397236 | CR | 20190725 |  | 4 | Oscillograph start | N | N |  | N | NO | <D> **** Detailed Description **** Oscillograph start at 0330 am due to Trip of the Rocky Creek 500k line caused by relay testing with reclose. No equipment damage or need for an emergent outage. No remedial action scheme initiated. Our indications showed a neutral 500k ground oscillograph start that reset. <I> **** Actions Taken **** OPS2 cleared the oscillograph start after noting it was on 500k ground neutral. Dittmer was called for information
397237 | CR | 20190725 |  | 3 | CWPH Emergency Spill Response Kit opened. | N | N |  | N | NO | <D> **** Detailed Description **** The spill kit in the CWPH was opened and several absorbant pads were used to contain Nalco spill. See AR 00397235 <I> **** Actions Taken **** Wrote CR
397238 | CR | 20190725 |  | 4 | Oscillograph Start | N | N |  | N | NO | <D> **** Detailed Description **** Oscillograph start at 1013 am due to Trip of Lomo Ashe 500k line cause unknown. Line was tested and reclosed No equipment damage or need for an emergent outage.Our indications showed a neutral 500k ground oscillograph start that reset <I> **** Actions Taken **** OPS2 cleared the oscillograph start after noting it was on 500k ground neutral. Dittmer was called for information
397243 | CR | 20190725 |  | 4 | Peak oil temp off scale high | N | N |  | N | YES | <D> **** Detailed Description **** N1 transformer peak oil temperature found off scale high. Suspected gauge issue. <I> **** Actions Taken **** Informed MCR, initiated CR This was the high indicator pointer only. The actual temerature was indicating normally and in band. <N> **** Equipment Description **** Transformer Yard N1 transformer | 02-00-E-TIS-TR/N1
397244 | CR | 20190725 |  | 4 | PWC-V-512 leaks by when shut. | N | N |  | N | YES | <D> **** Detailed Description **** PWC-V-512 leaks by about a pencil stream of water when shut. Initial leak by was about 2 gpm when first shut.It appears that all WR/WO's previously written for this valve are closed, but there is an actioned WR for an AR evaluation to replace the valve with a different model. <I> **** Actions Taken **** Attempted to flush the seat 2X and applied slight additional torque. Leak rate decreased from about 2 gpm to a pencil stream. <N> **** Equipment Description **** Spray Pond "B" south. | 02-00-PWC-V-512
397250 | CR | 20190725 |  | 3 | Need elevated fall arrest system in RW437 truck bay |  |  |  | N | NO | <D> **** Detailed Description **** When working in RW437 truck bay on tailers, shipping casks etc. there is no place to tie off when the crane in use. We should look at installing an elevated fall arrest system similar to what is in the NUPAC cage. <I> **** Actions Taken **** Informed supervision, wrote CR . AR type EVAL needed? Will any of the existing generic fall protection anchorage details provided by AED MIS D-FALL-PROTECT-146 suffice or is a new detail needed? <N> **** Equipment Description **** RW437 truck bay
397252 | CR | 20190725 |  | 4 | Broken thermostat in GSB 441 lunchroom | N | N |  | N | NO | <D> **** Detailed Description **** Some working areas in the GSB building 441 level are being maintained in in the high 50 degree (F) range. This is due to a broken thermostat in the lunchroom. The thermostat is located behind the icemaker and close to the window. This location tends to vary in temperature as the ice machine compressor cycles and also warms up significantly since it is direct sunlight for part of the day. <I> **** Actions Taken **** CR created <N> **** Equipment Description **** GSB 441 lunchroom
397253 | CR | 20190725 |  | 4 | FPC-FIC-15B indicates flow with FPC-DM-1B isolated. | N | N |  | N | YES | <D> **** Detailed Description **** FPC-FIC-15B indicates 450 gpm and FPC-DPR-13 indicates 6.3 psid with FPC-DM-1B off line and isolated. AR# 354036 addresses the D/P issue but does not address the indicated flow on the controller. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** RWCR | 02-00-FPC-FIC-15B
397254 | CR | 20190725 | CAQ | D | ISFSI cask 37 delta temperatue indication out of allowable | Y | N |  | N | YES | <D> **** Detailed Description **** Indicated differential in 130.8 with an allowable of 129 degrees. Prior day reading was 110.6. Suspect erronious reading. OSP-SFS-D101 has a note thats says the printout that shows this data is note used to determine operability and is for trending and monitoring. Suspect that one of the Temperature elements may be failing and giving a false reading. Determine is this value correct or incorrect and any actions needed. <I> **** Actions Taken **** Wrote this CR. generted WR against MPC | 02-00-SFS-MPC-037
397255 | CR | 20190725 |  | 3 | QA Missed opportunity |  |  |  | Y | NO | <D> **** Detailed Description **** A review of AR-CRs written in response to observations made by the NRC during plant walk downs determined that Qualityâ€™s current processes miss opportunities to identify issues that do not demonstrate excellence. Examples include AR-CR 392057 and 392650. Quality should evaluate these missed opportunities for potential process improvements. <I> **** Actions Taken **** This issued was discussed with the Quality leadership team at the July Missed Opportunity Review Board. Recommend Non-CAQ Severity 3 assignment to AR-QUALITY. <N> **** Equipment Description **** N/A
397258 | CR | 20190725 | CAQ | C | GEH Safety Communication SC 19-02 - MCPR | Y | N |  | N | NO | <D> **** Detailed Description **** GEH issued Safety Communication SC 19-02, dated July 24, 2019, that documents an error in one of the GEH methodologies related to Fuel Cycle Reload calculations regarding Safety Limit Minimum Critical Power Ratio (SLMCPR TS 2.1.1.2) and Operating Limit Minimum Critical Power Ratio (OLMCPR - TS 3.2.2) that could be non-conservative. GEH also identifies that this has been evaluated for the current operating cycle (CY25) SL MCPR and OLMCPR for CGS and that those values remain adequate, so there is no challenge to current plant operations and that no further actions are needed to address this issue for the current operating cycle . However, this error has been in existence for quite some time, so the Past Operability of Cycle 24 and Cycle 23 Operations will need to be reviewed. The document is considered propietary by GEH so it is not attached to EDMS. <I> **** Actions Taken **** Initiated CR so that documentation of Past Operability can be tracked.
397259 | CR | 20190725 |  | 3 | Quorum not met - Cross Discipline Review Team |  |  |  | N | NO | <D> **** Detailed Description **** The Cross Discipine Review Team meeting schduled for 7/25/19 at 0900 did not meet the required qourum due to a missing member from the Maintenance department (per SWP-CHE-07). It was confirmed that the individual was on site and just missed the meeting. <I> **** Actions Taken **** Notified department and initiated CR or trending purposes
397261 | CR | 20190725 |  | 3 | MAP NEEDS UPDATED IN 15.2.14 |  |  |  | N | NO | <D> **** Detailed Description **** ATTACHMENT 9.9 IN 15.2.14 FOR ZONE 1 NEEDS UPDATED HEAD LOCATIONS <I> **** Actions Taken **** NOTIFIED SUPERVISION AND CREATED CR <N> **** Equipment Description **** T441 B-H/4-7.5 ZONE 1 HEADS 1/5, 1/5A, 1/5B, 1/6, 1/7, 1/7A , 1/17
397262 | CR | 20190725 |  | 3 | Dropped object at MET tower. |  |  |  | N | NO | <C> AR reopened as per MRT to assign to MECSHOP. <D> **** Detailed Description **** While performing work on the MET tower ladder rungs per WO 02137606-01 a water bottle fell from an individualâ€™s tool pouch and struck another individual in the shoulder. The bottle was tied off using a rag tied to the handle and to the individuals harness. The bottle became dislodged during work activities and fell striking the shoulder of the individual working ~30ft below. Work was stopped and Supervision notified. The struck individual reported the incident and stated that he was fine. The individual was sent to Occupational Health for review. <I> **** Actions Taken **** Classified as a report only at this time CR generated for documentation.
397264 | CR | 20190725 |  | 4 | High risk challenge meeting did not pass. |  |  |  | N | NO | <D> **** Detailed Description **** The high risk challenge meeting held 7/24/19 for the balance shot on MS-DT-1C (W/O 02145898) did not pass. CR written for trending purposes. The meeting has been rescheduled to incorporate feedback into the plan.
397265 | CR | 20190725 |  | 4 | PWC-SEW-14, Scald valve leaking | N | N |  | N | YES | <D> **** Detailed Description **** The scald protection bleed valve was found to be leaking by and constantly dripping. <I> **** Actions Taken **** Generated work request to replace scald valve. | 02-00-PWC-SEW-14
397270 | CR | 20190725 |  | 3 | Request a Quick Card for MG gas dryer trouble alarm response |  |  |  | N | NO | <D> **** Detailed Description **** Request a Quick Card for MG gas dryer trouble alarm response, 4.800.C4 drop 4-4 currently found on pages 34 and 35 of the ARP. This QC to be stationed locally at the tool box ( preferably in a folder on the outside ) near the H2 skid. This would reduce the number of pre-stagged copies which result in a housekeeping iissue and possible use of unverified revs. <I> **** Actions Taken **** Notified supervisor.
397272 | CR | 20190725 |  | 3 | Evaluate resource loading of EP related work items |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate EP related surveillances to determine if the item should be worked around the clock or lesser schedule ie 7x10, 4x10, etc. This evaluation should take resources and overtime costs into considerations. . Assign to Work Control . Reference 02130071 PPM 16.1.11 <I> **** Actions Taken **** Discussed a morning 0615 meeting. Example is that PRM-SR-1 WO 02130071 was intentionally scheduled to take GT 7 days (PAM TS 1.3.3.1 spec is 7 days). No work on backshift or weekends - this duration of scheduling is not consistent with the requirements of PPM 13.14.11 for category A1/A2 equipment.
397275 | CR | 20190725 |  | 4 | NLOI Student Exam failure Administered 07/25/2019 |  |  |  | N | NO | <D> **** Detailed Description **** A NLOI Candidate failed GFE Thermodynamics exam given on 07/25/2019. Remediation will be conducted in accordance with TDI-02 and TDI-10. No qualification removal was required. AR is for tracking purposes only. <I> **** Actions Taken **** Informed Operations Training management and Operations Management.
397276 | CR | 20190725 | CAQ | D | (FP) Fire door found blocked open | N | N |  | N | NO | <D> **** Detailed Description **** T-129 was found blocked open by a steel wedge. <I> **** Actions Taken **** Fire Marshal removed wedge from door and veriifed the mag holder was working properly. CR created.. CR for trend only This is a non-essential fire door. <N> PIC uploaded to EDMS
397277 | CR | 20190725 |  | 4 | (FP) Double female adapter found on standpipe |  |  |  | N | NO | <D> **** Detailed Description **** During fire briogade drill, response was delayed do to a double female adapter being left on the end of the standpipe. FP-V-HS/TGB31 is the valve associated with the piece of equipment left on standpipe <I> **** Actions Taken **** Fire Marshal removed adapter and returned the item to the fire brigade turn out station. Created CR and uploaded picture of adapter and standpipe valve to EDMS
397278 | CR | 20190725 |  | 3 | Trend in licensing change document quality |  |  |  | N | NO | <D> **** Detailed Description **** The following CRs have been generated over the past couple years that identify a number of minor document quality related issues with license document change notices (LDCNs ) and license amendment requests (e.g., forms not compiled correctly, boxes not being checked, POC numbers not being included, copies of LDCNs not loaded into EDMS properly, etc.). A comprehensive evaluation of procedures and practices should be completed to ensure that the right level of rigor is being applied in the preparation and processing of these documents to ensure compliance with the applicable change processes. (Reference CRs 369345, 369346, 369389, 373489, 377563, 385937, 385943, 386989, 397192, 00397198, 397199) <I> **** Actions Taken **** Documented a thumbs down for D15. Communicated concern to Licensing staff. Instituted staff review of procedural requirements at department staff meetings.
397279 | CR | 20190725 | CAQ | D | HPCS-V-23 no light indication. | Y | N |  | N | YES | <D> **** Detailed Description **** Closed in HPCS-42-4A3D. Valve position lights did not come on. Light bulbs were replaced and thermao overloads were reset withouot success. | 02-00-HPCS-42-4A3D
397280 | CR | 20190725 |  | 4 | Chemistry dose budget exceeded for June 2019 |  |  |  | N | NO | <D> **** Detailed Description **** The Chemistry dose budget was exceeded for the online portion of June 2019. The dose estimate was 47 mR with a goal of 42 mR. The Chemistry department received 71 mR in the 11 day period following R24. The extra dose can be attributed to required sampling during plant startup. This work activity was not accounted for in the develpment of the online dose budget.
397281 | CR | 20190725 | CAQ | D | Security IDS 18/19 Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** Security IDS zones 18/19 are not functioning as designed. Contact Security at extension 2185 for further details. <I> **** Actions Taken **** Comensatory measures posted, Security Supervision notified, and CR/WR generated for Electrical Support. | 02-00-SEC-IDS-EVAL/18/19
397283 | CR | 20190725 |  | 3 | (ERO Drill) Drill Objective E.1 Demonstrated with Issue |  |  |  | N | NO | <D> **** Detailed Description **** During the July 16, 2019, Team B ERO Drill, a drill objective, E.1, Demonstrate the ability to notify off-site response organizations (ORO) consistent with the classification scheme including verification of messages in a timely manner was demonstrated with Issue. The notifications for the General Emergency classification were being made and one agency, Benton County, was not on the Crash call due to line issues at the County facility, (resolved under CR 396909). The information on the initial crash call was accurate. An attempt to utilize the dial -up line to Benton County was also unsuccessful. Contact was made promptly to Benton County via the commercial line where information was provided to an authorized County Official. A fax with the proper information was also sent and receipts indicate that fax transmission was completed at approximately 1110 to Benton County (10 minutes after the GE declaration in the drill). Communication with Benton County Emergency Management indicate they received the fax with the accurate information for the GE and PARs. While the verbal back-up notification was timely it failed to meet accuracy expectations, in that the verbal statement of the correct PARs listed on the faxed classification notification form was not clearly communicated. This issue was critiqued and discussed with the EOF Manager. Assign to EP for development of appropriate lessons learned. <I> **** Actions Taken **** Critiqued issue. Discussed with the EOF Manager.
397288 | CR | 20190725 |  | 3 | Replacement RRC-VD-R673 stiil hard to read | N | N |  | N | YES | <D> **** Detailed Description **** RRC-VD-R673 replaced again. The new display is an improvement over the previous dispaly but, it is still hard to read. It is only a slight emprovement over the previous display . the display installed was the best of the 5 that were in the warehouse. Discussed with the Shift manager and the operationg crew and Operations felt that they need a better solution. Generated this CR to challange engineering to find a better solution A different model panel PC is needed. Solution will likely need a design change. <I> **** Actions Taken **** Wrote CR | 02-00-RRC-VD-R673
397292 | CR | 20190725 |  | 4 | Received Steam dump valves not full closed alarm. | N | N |  | N | YES | <D> **** Detailed Description **** Received Steam dump valves not full closed alarm 4.840.A2 9-6. Control room operator noticed that BS-DV-2A2 indicates full open, and no other valves have repositioned. Reactor power, pressure, level are normal and stable for 100% power. Reactor feed water inlet temperature is 420.6 F and is normal for 100% power. <I> **** Actions Taken **** Initiated a temporary log to monitor dump valves while alarm is locked in. | 02-00-BS-DV-2A2
397294 | CR | 20190725 |  | 3 | (NRC Identified) Fire Tour RW 437 Areas Not Clear |  |  |  | N | NO | <D> **** Detailed Description **** The Fire tour is required to tour is required to tour RW437N area (RW 437 Behind Shield wall and Offgas Dryer rooms C130 and C131) hourly. These areas are not entered due to high radiation conditions (Area RC-1). PPM 1.3.76 has a note on attachment 9.3, Note 1 that states "The hourly fire tour can be limited to those Aaccessible portions of the fire areas. Entry into High Rad or Contaminated areas is not required...For Fire Area RC-1, this includes only RW 437' room C106 (northern portion). This is not clear in PPM 1.3.85 nor is it clear the fire tours. <I> **** Actions Taken **** Recommend revising PPM 1.3.85 to include the same note as PPM 1.3.76. PSRO conducted a brief with thefire tour to clarify why the hgih radiation areas are not required to be entered. . Note 1 on page 58 of PPM 1.3.76 states "The hourly fire tour can be limited to those 'accessible' portions of the fire areas. Entry into High Rad or Contaminated areas is not required. The fire tour route can be limited to only those portions that contain post-fire safe shutdown circuits... For Fire Area RC-1, this includes only RW 437' room C106 (northern portion)." This information should be included in PPM 1.3.85. Also, we should NOT include the inaccessible areas that are not required to be toured on the fire tour.
397295 | CR | 20190725 |  | 4 | TR-N1 Trouble Alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received XFMR TR-N1 Trouble, H13-P800.C4.1-6. Entered ABN -TRANSFORMER. Alarm was due to oil temperature high at 80Â°C. OPS4 initiated cooling spray on TR-N1 per ABN -TRANSFORMER due to high temperature. Gas sample is required. <I> **** Actions Taken **** Informed CRS and Shift Manager. Entered ABN-TRANSFORMER. Initiated cooling spray on TR-N1. <N> **** Equipment Description **** Transformer Yard | 02-00-E-TR-N1
397296 | CR | 20190725 | CAQ | D | DLO-42-7AA4B starter hummed and didnt start till 3rd try | Y | Y |  | N | YES | <D> **** Detailed Description **** While performing OSP-ELEC-W102The switch for the AC and DC pumps is taken to DC to start the DC to verify the DC bus is energized. It is then returned to auto at which time the AC pump should start. When the switch was returned to AUTO a a loud buzzing was heard (disconnect is behind the opeerator). the switch was returned to DC. A second attempt was tried at which time the Low pressure alarm was recieved. The Switch was returned to DC, lo pressure alarm was cleared and teh pump was verified running. Supervision was brought in and after a thopuirough discussion it was attempted again. This time the disconnect hummed and then the contactor closed in and a red running indication was observed. Local indication of DLO-P-11A1 showed no abnormalities in starting. Believe the contactor was binding or not picking up completely. Contactor coils were part of a replacement documented in WR 29137547 and changed <I> **** Actions Taken **** out in WO 02116394. Pleaseinspect and repair as necessary. | 02-00-DLO-42-7AA4B
397297 | CR | 20190725 |  | 4 | Unable to prepare temp lift 2019-0080 |  |  |  | N | NO | <D> **** Detailed Description **** Operating crew was unable to perform temp lift 2019-0080, not enough on-shift RO's were qualified to gen a new temp lift <I> **** Actions Taken **** discussed with shift supervision
397298 | CR | 20190726 |  | 4 | PPC is Not Functioning | N | N |  | N | YES | <D> **** Detailed Description **** PPC is non-functional. Attempts by the STA to restore per SOP-COMPUTER-OPS were unsuccessful. TDAS is primary, PPC is backup. This is not reportable. <I> **** Actions Taken **** Notified CRS, Shift Manager and System Engineer. System engineer was aware and stated PPC has not been functioning correctly for a few weeks and he is working with the vendor. <N> **** Equipment Description **** Main Control Room | 02-00-PPC-CPU-WS1
397299 | CR | 20190726 |  | 4 | ASD 1B/2 resistivity low. | N | N |  | N | YES | <D> **** Detailed Description **** Found ASD 1B/2 resistivty low. All other ASDs are also low. <I> **** Actions Taken **** Informed SSS, initiated AR. | 02-00-RRC-42-4CR/ASDB2
397300 | CR | 20190726 | CAQ | D | oscillograph start alarm | N | N |  | N | NO | <D> **** Detailed Description **** Plant controllers and equipment response was normal. J7, J11, J12, J15, J16 sensors tripped and were reset. Startup and Backup voltages are as follows: E-TR-S A: 239 B: 236 C: 239 E-TR-B A: 120 B: 119 C: 118 BPA reports the following: The cause was Lower Monumental - Ashe 500 KV line tripping off and back on. No damage reported. The 500kv was involved. Time of the events was 0143. No RAS was initiated with gird frequency normal. . Also received H2 WTR CHEM TROUBLE concurrently, documented with a different CR. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR.
397301 | CR | 20190726 |  | 4 | Alarm on HSSF-CAB-CHEM | N | N |  | N | NO | <D> **** Detailed Description **** Received a PC SYS-STAT TROUBLE alarm on HSSF-CAB-CHEM in the 487' RW Chemistry Lab. This alarm was in conjunction with OSCILLO-GRAPH-START alarm that was received in the MCR. <I> **** Actions Taken **** Informed the CRS and wrote a CR.
397302 | CR | 20190726 |  | 4 | Hydrogen water chemistry isolated | N | N |  | N | YES | <D> **** Detailed Description **** At 0143 a grid disturbance coincided with a Hydrogen Water Chemistry Trouble alarm. While Operators were investigating, YV-V-170 was found closed. <I> **** Actions Taken **** Operators are shutting down Hydrogen Water Chemistry per ABN-HWC | 02-00-HSSF-V-YV170
397304 | CR | 20190726 | CAQ | D | RW 487 elevation siesmic green light is lit. | N | Y |  | N | YES | <D> **** Detailed Description **** Long instructions for Seismic monitoring in 3.1.10 logs directs initiating a CR. Investigate the cause of this trouble LED and take approipiate corrective action. <I> **** Actions Taken **** Wrote this CR. Reset alarm Pushed the LED test/reset button to test the LEDs. All LEDs illuminated and then extinguished. | 02-00-SEIS-SMA-2B
397305 | CR | 20190726 |  | 3 | SOP-HWC-START error likely step |  |  |  | N | NO | <D> **** Detailed Description **** SOP-HWC-START step 5.2.17 step a and step b should be separate steps such as 5.2.17 and 5.2.18. With the current format, all of step 5.2.17 was inadvertently marked NA resulting in a delay in recovery of HWC. Step 5.2.17.b appeared to be associated with the nitrogen block statement on 5.2.17.a. Chaning the format will remove this error likely situation. The change request was added to the procedure AR 342416 (2 year procedure review).
397306 | CR | 20190726 | CAQ | D | CRD-HCU-1419 Accumulator Trouble | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-1419 Accumulator Trouble was due to low N2 pressure and was corrected by Ops 2. | 02-00-CRD-HCU-1419
397307 | CR | 20190726 | CAQ | D | CRD-HCU-4259 Accumulator Trouble | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-4259 Accumulator Trouble was due to low N2 pressure and was corrected by Ops 2. | 02-00-CRD-HCU-4259
397308 | CR | 20190726 |  | 3 | Procedure enhancement CSP-ISOTOPIC-M101 | N | N |  | N | NO | <D> **** Detailed Description **** Step 8.2.6 of CSP-ISOTOPIC-M101 directs the user to "Verify OG-RIS-612 indicates approximately the same...". The step does not tell the user what to do if the indication is not the same (e.g. 0 mrem/hr because offgas flow was isolated to the sample line). Investigate lineup if indication is not similar. <I> **** Actions Taken **** discussed improvement with chemistry specialist
397309 | CR | 20190727 |  | 4 | RRC-TR-ASD/B/2 Pressure Above High Spec | N | N |  | N | YES | <D> **** Detailed Description **** RRC-TR-ASD/B/2 pressure is reading 4.25 PSIG. Max spec per OPS-4 logs is 4.0 PSIG. Please restore pressure to normal operating band. <I> **** Actions Taken **** Informed supervision, wrote AR | 02-00-RRC-TR-ASD/B/2
397310 | CR | 20190727 |  | 3 | eSOMS operator rounds data are not syncing with ipads | N | N |  | N | NO | <D> **** Detailed Description **** There have been several instances over the past week where the operator rounds data in the eSOMS data base has not synced with the ipads used to collect the data from the field. This presents a challenge to the operators as there is neither a trend available for comparison of the data collected nor instructions for temporary logs. This challenges the crew with meeting the completion time for the OSP-INST-H101 surveillance. This also requires CRO1 to spend more time on hourly PPM 3.1.10 logs which adds an unnecessary distraction from the primary function of monitoring reactor power, pressure and level. <I> **** Actions Taken **** IS has been responsive to trouble calls but the source of the problem is in the eSOMS software and requires vendor support to correct. I recommend elevating the importance of this issue with the vendor to expedite a solution as this places additional strain on the operating crew.
397315 | CR | 20190727 |  | 3 | CW-P-2 found off | N | N |  | N | NO | <D> **** Detailed Description **** CW-P-2 was found off during the performance of the shiftly chemistry logs. This is contrary to normal practice; it should be run continuously to maintain a consistant flow through the coupon station. <I> **** Actions Taken **** specialist informed <N> Needs WR. WR 29150736 initiated and cross referenced.
397316 | CR | 20190727 |  | 3 | Evaluate HWC shutdown on grid hits | N | N |  | N | NO | <D> **** Detailed Description **** CR's 397301 and 397300 document a grid hit and the loss of HWC. This has previously occure and this system needs to be evaluated for a more robust power source to prevent reoccurance. <I> **** Actions Taken **** discussed with shift manager not an immediate equipment issue
397317 | CR | 20190727 | CAQ | D | FPC-TI-8 Reading low. | N | Y |  | N | YES | <D> **** Detailed Description **** FPC-TI-8 is reading approximately 89 while FPC-TI-7 is reading 101. These temperature indicators usually are within about 2 degrees of each other. Review of the computer point for FPC-TI-8 shows a reading of 100 which is consistent with FPC-TI-7 reading. <I> **** Actions Taken **** Informed CRS. Hung deficiency tag in control room | 02-00-FPC-TI-8
397318 | CR | 20190727 |  | 3 | ASD filter replacement priority | N | N |  | N | NO | <D> **** Detailed Description **** During the last seven days four AR's and associated work requests were generated for low resistivity on the ASD units. This requires ASD filters to be replaced. No action was taken to complete this or raise awareness of the rising priority until the weekend. Because this issue came up on a weekend, additional resources were called out the correct qualification/proficency causing over time expenses. <I> **** Actions Taken **** Discussed with shift manager and plant supervision on 0800 weekend production call. additional resources called out. .Action: assign to operations, maintenance and work control. This CR is not an equipment issues but a potential process issue requiring resolution.
397319 | CR | 20190727 | CAQ | D | FLEX-CAB-4 Unsat | N | Y |  | N | YES | <C> Duplicate of CR 397336 <D> **** Detailed Description **** There are several issues with FLEX-CAB-4 as identified while performing OSP-FLEX-A106. These have been previously documented in CRs. See attached document. There are several issues with FLEX-CAB-4 as identified while performing OSP-FLEX-A106. See attached document. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** R471
397320 | CR | 20190727 | CAQ | D | Received Oscillograph Started, H13-P800.C4.4-3, alarm | N | N |  | N | NO | <D> Received Oscillograph Started, H13-P800.C4.4-3, alarm. Plant controllers and equipment response was normal. Reference AR Startup and Backup voltages are as follows: E-TR-S A: 239KV B: 238KV C: 241KV E-TR-B A: 120KV B: 120KV C: 119KV The following sensors were tripped and are reset: + J12 - SM-8 Undervoltage J15 â€“ 230KV Undervoltage BPA reports the following: Cause was a trip and lock out of the Paul â€“ Raver #1 500KV line. Investingations are still on-going. Time of event 15:40. BPA Dittmer reports 500KV system voltage at ASHE is 540KV. RAS initiated, but no reactive switching was involved. <I> Informed CRS. Took actions per ARP <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
397321 | CR | 20190727 | CAQ | D | Wetwell O2 concentration slowly trending up | Y | N |  | N | YES | <D> **** Detailed Description **** Wetwell O2 concentration is slowly trending up. O2 concentration was 1.11% on 7/26/19 @ 1812. O2 concentration is 1.15% on 7/27/19 @ 1630. CMS-SR-13 is aligned to the wetwell and is the likely source of the O2 rising trend. <N> EDNA Pt X456 | 02-00-CMS-SR-13
397322 | CR | 20190727 |  | 4 | MG Exciter Condensation | N | N |  | N | YES | <D> **** Detailed Description **** OPS3 noted increased condensation in the MG exciter dog house on the TSW lines of the cooler. TSW temperatures have fluctuated with ambient temperature changes between 68-72F, which is above the condensation concern of SOP -TSW-OPS P&L 4.12. The dog house gasket is broken, see cross-referenced CR/WRs, resulting in an air leak. This leak may be introducing additional humidity, which is condensing onto the heat exchanger tubes. Recommend determining the cause of the additional condensation and correcting. <I> **** Actions Taken **** Notified CRS/SM. | 02-00-E-EXC-1
397323 | CR | 20190727 |  | 4 | E-BU-R501/2 has a charger fault | N | N |  | N | YES | <D> **** Detailed Description **** Found E-BU-R501/2 with a charger fault (3 blink). <I> **** Actions Taken **** Initiated AR, Informed SSS. | 02-00-E-BU-R501/2
397324 | CR | 20190727 |  | 3 | T2 has Hi TOC's and there is no game plan for remedy? | N | N |  | N | YES | <C> AR reopened as per MRT to 3/CHEM <D> **** Detailed Description **** FDR-SUMP-T2 was Identified as a source of high TOC's after exhausting a large portion of yellow drums. the Discharge of T-1's (broken pump)temp sump pump was changed to FDR -SUMP T7 which drastically cut down the amount of water that goes into T2. Currently a small amopunt of water is being pumped out of T2 tio either clear the Hi-Hi alarm or just to lower level. This is being cut by a large amoiunt of Good water so the tanks will pass. T2 has been a source of TOC's due to the amount of oil leaking out of the CAS compressors and since its a synthetic oil it neither sinks or floats. Options include findintg a differant outlet for t2 water. treating t2 water in place with some type of TOC treatment (they exist). Send it to the CST knowing we arent going to fix the troblem. Long term fix woulkd be to replace the CAS Compressors which was scheduled three outages ago. <I> **** Actions Taken **** Seeking resolution for T2 high TOC's | 02-00-FD-SUMP-T2
397325 | CR | 20190727 |  | 4 | SHaft ground brush appears to be riding on metal part of bru | N | N |  | N | YES | <D> **** Detailed Description **** SHaft ground brush appears to be riding on metal part of brushe backing. Previously identified on CR 396162 and when it got worse on 397040. please see attached pictures. <I> **** Actions Taken **** wrote a third cr. <N> **** Equipment Description **** t501
397326 | CR | 20190728 | CAQ | D | E-IR-81 Oil Accumulation Below RPS-PS-5A | Y | N |  | N | YES | <D> **** Detailed Description **** Oil is slowly accumulating on the union below RPS-PS-5A as well as in the bottom of the cabinet inside E-IR-81. This is a very slow buildup of oil, pictures are attached. It does not appear to affect the operation of the components. <I> **** Actions Taken **** Informed CRS, wrote CR/WR <N> **** Equipment Description **** TB 471 East | 02-00-E-IR-81,02-00-RPS-PS-5A
397327 | CR | 20190728 |  | 4 | COND-V-117B Gearbox Leaking Oil Onto Ground | N | N |  | N | YES | <D> **** Detailed Description **** COND-V-117B gearbox leaking oil onto the ground creating a slipping hazard. Recommend installing a catch beneath the valve to prevent oil accumulation on the ground. Pictures attached. <I> **** Actions Taken **** Informed supervision, wrote CR/WR <N> **** Equipment Description **** TB 441 West | 02-00-COND-V-117B
397328 | CR | 20190728 | CAQ | D | CRD-HCU-2203 Accumulator Trouble Alarm | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-2203 Accumulator Trouble Alarm due to high water level. Alarm was cleared by Ops 2. | 02-00-CRD-HCU-2203
397333 | CR | 20190728 |  | 3 | 12.5.35A procedure enhancement | N | N |  | N | NO | <D> **** Detailed Description **** During the performance of RFOs related to setting up the PRM temporary sample cart on the 606' for PRM-CAB-2 several possibilities for improvement were noted. 1. The procedure has no guidance for taking a noble gas sample on the 606'. 2 The procedure has no guidance for taking a tritium sample on the 606'. 3. Attachment 9.2 has total flow listed instead of bypass flow. 4 Attachment 9.2 has the unit for Rx bldg dP as negative inches of water. - this is normally the case but it could be positive so the units should be just inches of water. <I> **** Actions Taken **** specialist informed
397334 | CR | 20190728 |  | 4 | E-TR-6/62 has pressure LT 0 (-.2psig) | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-6/62 pressure is -.2psig and needs nitrogen added. Nitrogen was previously added 6/21/19 under WR 29149473. This is an unacceptably short time between needing a nitrogen charge and should be investigated. <I> **** Actions Taken **** Wrote this WR/CR and notified the MCR. | 02-00-E-TR-6/62
397336 | CR | 20190728 | CAQ | C | OSP-FLEX-A106 discrepancies and questions | N | Y |  | N | NO | <D> **** Detailed Description **** During performance of OSP-FLEX-A106, certain questions and discrepancies were noted. Please see attached document for detailed description. CR was generated to get clarification. <I> **** Actions Taken **** Notified SM and generating CR <N> **** Equipment Description **** FLEX BLDG 82 EQUIPMENT
397338 | CR | 20190728 | CAQ | D | FLEX Fuel Volumes | N | Y |  | N | NO | <D> **** Detailed Description **** There is no method to verify FLEX-CAB-2/TKF1, FLEX-CAB -2/TKF2, FLEX-CAB-1/TKF1, and FLEX-CAB-1/TKF2 volumes as required by OSP-FLEX-A106. These are 30 gallon capacity storage drums with no indication of current fuel volume. OSP-FLEX-A106 requires all 4 tanks to be verified GT 25 gallons. Recommend determining a method to verify the capacity of these tanks and adding it to OSP-FLEX-A106. <I> **** Actions Taken **** Notified MCR and wrote CR. <N> Obtianed Gas tank levels greater than 25 gallons by removal of fill plugs on the tanks.Meets the requirements in section 9.8.1 and 9.8.2
397339 | CR | 20190729 | CAQ | C | OSP-FLEX-A106 inventory missing 3 wrenches | N | Y |  | N | YES | <D> **** Detailed Description **** OSP-FLEX-A106 inventory step 9.3.3 storage space 2H4 is missing 3 wrenches 3/4 X 7/8 open end combination wrenches. Of note there are 6 wrenches of the same size in storage space 2H6 that requires there to be 6. <I> **** Actions Taken **** CRS Informed and this CR was written as directed by the OSP. <N> **** Equipment Description **** FLEX-TRLR-2 bldg 600
397340 | CR | 20190729 |  | 4 | CF-P-42B is low on Oil | N | N |  | N | YES | <D> **** Detailed Description **** While Check oil level on the pump the oil level only left a small tic of oil o the stick please add oil to the pump. recommend fill all the pumps at the same time to ensurem they are topped off. <I> **** Actions Taken **** wrote Wr/CR | 02-00-CF-P-42B
397341 | CR | 20190729 |  | 4 | TMU-F-2 Black sleeve for the blow down came out | N | N |  | N | YES | <D> **** Detailed Description **** TMU-F-2 Black sleeve for the blow down came out. Filter was not on service. Attempted to put it back in but when tested the filter leaked air. please replace or repair asnecessary. It was the second filter, on top of the twi that lool like they are in parallel, On the print its listed as a D/P indicator. filter is currently offline. <I> **** Actions Taken **** wrote CR/WR | 02-00-TMU-F-2
397342 | CR | 20190729 | CAQ | D | IDS 22 23 Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** CAS received a constant malfunction alarm on IDS 22 23. A walkdown of the area was conducted and there was nothing found that could be causing the zone to alarm. <I> **** Actions Taken **** Posted compensatory measures. CR/WR was generated. | 02-00-SEC-IDS-EVAL/22/23
397343 | CR | 20190729 | CAQ | D | SP-1 conductivity element >10% from grab sample | N | Y |  | N | YES | <D> **** Detailed Description **** SP-1, reactor water, conductivity element was determined to be off by >10% (but <20%) from grab sample results during the performance of the weekly instrument cross-check. This does not inop the equipment, however, it is not a desireable condition and recalibration should be performed. <I> **** Actions Taken **** control room informed, supervisor/specialist notified | 02-00-S-CE-1
397350 | CR | 20190729 |  | 3 | Standard out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Calcode 0067084 Heise Model HQS-1 Sensor 0-25 IN/H20 was found OOT and adjusted. No usage during calibration cycle. NOD# 20-03 was issued. Please assign to CALSERV
397352 | CR | 20190729 |  | 3 | PM Batch Job failing | N | N |  | N | NO | <D> **** Detailed Description **** The PM batch job is failing to generate Current Occurances due to program abend. Future Generated PMs is not running due to the failure <I> **** Actions Taken **** Current Occurances are being generated on line when requested and Running Futures PM Batch Job seperately. . Investigating reason for current occurance program is. abending <N> Upon investigation, it was found that the AAA program is finding an error with the Facility code and forcing to program to abend. . Closing CR to "AR00398526 - PM Batch Program Fix" to correct the finding.
397353 | CR | 20190729 |  | 3 | 4.800.C3 procedure enhancement | N | N |  | N | NO | <D> **** Detailed Description **** Annunciator response procedure 4.800.C3 drop 10-6 provides guidance for hydrogen leakage at IBD/EXCITER. This section of the procedure should provide guidance for OPS to open the exciter doghouse to vent the area for low levels (below the lower explosive limit) of confirmed H2 leakage to prevent hydrogen from building up in the enclosure. The following guidance should be added to the procedure between steps 8 and 9: H2 monitor TG-H2IS-1 indicates elevated hydrogen concentration >20% LEL but <50% LEL in the exciter doghouse., Frequency = When alarm is received (P800.C3 Drop 10-6) . Action: . Operations: Open the doghouse doors on the exciter to ensure ventilation is adequate to prevent explosive atmosphere. Disable the exciter ground detector by pulling fuses <I> **** Actions Taken **** Discussed with OPS, initiated CR to process procedure change
397354 | CR | 20190729 | CAQ | C | M&TE Suspended/ Lost | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0068181 Heise Sensor- model HQS-2 30psig was last c/o 5/15/19 WO #02111590. Can't locate- Out of Calibration. EFIN will need to evaluate 7 usages for Plant Impact. DEF #7072A written. <I> **** Actions Taken **** EFIN Needs Evaluate 7 usages. <N> Re-opened to add Defiency report to EDMS per request form Tool Crib Attendant.
397357 | CR | 20190729 |  | 4 | ALARA suggestion | N | N |  | N | NO | <D> **** Detailed Description **** Operations has noted that in delivering green bag trash to RW 437 for disposal they need to pass through dose fields of 5-15 mrem/hour. The suggestion is to deliver green bag trash to 467 RW and then move it to 437 in batches when several bags accumulate. <I> **** Actions Taken **** This is a good suggestion and is being implemented. The Operations dose champion has been contacted to let the operators know.
397365 | CR | 20190729 | CAQ | C | FLEX-VEH-4 & FLEX-P-1 have low fuel oil levels | N | Y |  | N | YES | <D> **** Detailed Description **** Per OSP-FLEX-A106 step 9.8.2, FLEX-P-1 (High Head Godwin Pump) should be full and it's 3/4. FLEX-VEH-4 (Flatbed Truck) should be full and it's 7/8. Both are located in Bldg. 82. <I> **** Actions Taken **** Wrote this CR/WR and Contacted SSS. | 02-CM-FLEX-P-1
397369 | CR | 20190729 | CAQ | D | LCS 1.3.3.1.C.1 not completed within 7 days | N | Y |  | N | NO | <D> **** Detailed Description **** PPM 16.1.11 rendered PRM-RE-11, PRM-RE-12 and PRM-RE-13 of the Reactor Building Stack Monitor Non-Functional per WO 02130071. The surveillance was not completed within 7 days exceeding the action time of LCS 1.3.3.1.C.1 to restore the system to Operable status therefore requiring entry to LCS 1.3.3.1.E which requires that a CR be written immediately. This CR fulfills the action of LCS 1.3.3.1 .E.1. This CR needs to address why the SSC was not restored to functional status within the completion time and provide a plan for restoring the SSC to functional status. If not previously documented the CR should also provide an accurate and concise description of the initial cause(s) for the non-functionality, the required compensatory measure not met, an initial functionality assessment, and corrective actions taken and planned for restoring the SSC to functional status. <N> See LCS Basis 1.3.3.1.E.1 for more guidance on what this CR should address. LCS BASES REQUIRED INFORMATION: 1) The stack monitor was not restored within the required completion time because of a surveillance scheduling error. 2) The plan for restoration is to perform the surveillance and restore functuionality on 7/30/19. 3) The cause of the non-functionality was a shortfall in the work control/scheduling process. There was no equipment failure that resulted in the non -functionality. 4) Corrective actions taken/planned: The surveillance will be performed om 7/30/19 to meet functionality requirement.
397370 | CR | 20190729 |  | 3 | R25 LL PO.6 Scoping Spreadsheet Issues | N | N |  | N | NO | <D> **** Detailed Description **** A new PO.6 scoping tool is being used for R25 scoping. The new Excel spreadsheet has many improvements from previous outage scoping spreadsheets, but has had multiple issues when implemented. There have been multiple instances of the PO.6 tool having error messages or not allowing individuals to update the review section. These issues were exacerbated by having only a single individual capable of fixing bugs etc. for this spreadsheet. When that person was out of town, whole days of engineering reviews were lost due to an error in the spreadsheet. This has delayed engineering reviews, which have a stringent due date. The new tool has a lot of benefits, but should have been tested longer before directing engineering to use it for the PO.6 review. Also, there needs to be more than one individual capable of fixing issues with the spreadsheet to prevent delays in engineering reviews or rework.
397372 | CR | 20190729 | CAQ | D | Sec-IDS-5 6 not functioning as designed. | N | N |  | N | YES | <D> **** Detailed Description **** CAS received a Malfunction on SEC-IDS-5 6. The zones are not functioning as designed. Request electrical maintenance to investigate. <I> **** Actions Taken **** CR/WR Generated; Compensatory Measures initiated | 02-00-SEC-IDS-E/S/5/6
397378 | CR | 20190729 | CAQ | C | FSAR typo in Section F.2.4.1 | N | Y |  | N | NO | <D> **** Detailed Description **** FSAR Section F.2.4.1 lists the total dynamic head to be 289 feet for FP-P-2A, FP-P-2B and FP-P-1. CVI DWG 29-00,15 and other documentation lists the total dynamic head to be 298 feet. It is apparent the FSAR section is discrepant and should be updated. See EDMS for further details. <I> **** Actions Taken **** Notified Supervisor Notified Fire Protection Engineering
397380 | CR | 20190729 |  | 4 | WOA-MC-3 found not functioning | N | N |  | N | YES | <D> **** Detailed Description **** While performing 02110768-01 WOA-MC-3 was found broken and not responding <I> **** Actions Taken **** Notified supervision and wrote this CR <N> **** Equipment Description **** Rad waste 487 | 02-00-WOA-MC-3
397381 | CR | 20190729 |  | 4 | light fixture in RW 501' cable chase not working | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** WO#02118825-01 was written to replace cable chase room lighting with LED fixtures. However, The EC for incandescent fixtures within the RW 525 and RW 501 cable chase rooms has not been approved yet, and therefore the work instructions were written to just relamp the fixtures with incandescent bulbs, to alleviate the safety concern. one fixture at RW 501 K9/9.5 still does not work even after relamping. <I> **** Actions Taken **** Write CR and WR <N> **** Equipment Description **** general lighting in RW 501 K9/9.5
397382 | CR | 20190729 | CAQ | C | REA-FU-2A and REA-FU-2B lamp colors donâ€™t agree with drawing | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** REA-FU-2A and REA-FU-2B heat detection waterspray control box lights, LT-1 is green and LT-2 is red. PPM 15.2.29, 4 .RBHV.A and 4.RBHV.B concur with the field conditions. However, EWD-80E-045, EWD-80E-046 and CVI DWG 18-00,1,2, do not concur. They show that LT-1 is red and LT-2 is green. Both EWDâ€™s are Top Tier drawings and the CVI is not a Top Tier drawing. This discrepancy is too complex to simply go change the lenses to match the drawings as procedures are involved which show the opposite of the drawings. Please investigate and correct this issue and make all documents and the field agree. Please see EDMS for examples of this problem. <I> **** Actions Taken **** Wrote this AR/CR. <N> **** Equipment Description **** Rx 572
397383 | CR | 20190729 | CAQ | C | No open WR to correct degraded SRM-B condition | Y | Y |  | N | YES | <D> **** Detailed Description **** CR 393993 identified that the SRM-B drive-end flexible shaft coupling was loose and could not be fully engaged to the drive shaft. WO 02043326-12 to replace the flexible drive shaft (and correct this degraded condition) was added to R24 scope (OSCR 394077), deferred (OSCR 394252), and then subsequently canceled. WO 02043326 was a PM WO to which corrective work scope was added. At the end of the day only the PM scope got completed and the corrective work was canceled without any subsequent actions taken (e.g. initiate a new WR, or CR if appropriate). This may be a process gap. This CR is to document the apparent process gap and ensure a new WR is initiated to address the condition. <I> **** Actions Taken **** Discussed with supervisor | 02-00-SRM-DRVE-DET/1B,02-00-SRM-MM-1B
397387 | CR | 20190729 | CAQ | D | IDS 15 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** IDS 15 is not functioning as designed and requires maintenance. Contact 2185 for more details <I> **** Actions Taken **** Security Supervision notified. Compensatory measures posted. CR/WR initiated. | 02-00-SEC-IDS-E/S/14/15
397388 | CR | 20190729 | CAQ | C | Spare APRM NIC CPU card battery dead, memory lost | N | N |  | N | YES | <D> **** Detailed Description **** The backup battery on the spare APRM NUMAC Interface Computer (NIC) CPU card was found dead during performance of WO 02101747 (PM REPLACE BACKUP BATTERY ON NUMAC NIC CPU CARD). Testing of the spare CPU board after battery replacement found that it had lost all its programming and will require re-installation per CVI OMM 1133-00,67 (NIC SOFTWARE INSTALLATION MANUAL). As is, the CPU card is not a viable spare for APRM-COMP-NIC. This affects spare equipment only, no impact to the APRM system. PM strategy/frequency also may need to be reassessed. Recommend assignment to system engineering. <I> **** Actions Taken **** Discussed with I&C, supervisor, vendor <N> **** Equipment Description **** CID 23372 NUMAC INTERFACE COMPUTER CPU CARD FOR PRNM | 02-00-APRM-COMP-NIC
397389 | CR | 20190729 |  | 4 | CW-PHITS-1 has a FAIL/S4 LED lit | N | Y |  | N | YES | <D> **** Detailed Description **** CW-PHITS-1 Yokogawa display has a fail message at the top right of the screen and the FAIL/S4 LED is lit under 'CONTACTS'. CW PH has dropped by 0.4 units PH over 2 hours. CW-PHITS-1 has been placed in manual control. <I> **** Actions Taken **** Notified CRS and initiated CR/WR. CW-PHITS-1 is not in manual. CW-PHITS-1 is in Auto with PH lowering slowly. <N> **** Equipment Description **** CWPH | 02-00-CW-PHITS-1
397390 | CR | 20190729 |  | 4 | CW-PHITS-1 diverges from Grab Sample | N | Y |  | N | YES | <D> **** Detailed Description **** Grab sample indicates pH of 8.47 and computer point F141 reads 7.48 pH on Circ Water | 02-00-CW-PHITS-1
397391 | CR | 20190730 |  | 4 | TMU-V-107 Missing Bushing Nut Prevents Valve From Operating | N | N |  | N | YES | <D> **** Detailed Description **** TMU-V-107 is missing the bushing nut and is preventing the valve from operating. As the handwheel is turned, the bushing threads down the stem of the valve, backing itself away from the yoke and pushes the handwheel off the top of the valve while the stem has no actual movement. Replacement of the bushing nut is required in order to open the valve for clearance D-TMU-V-104-001. <N> **** Equipment Description **** Located in Flocculator building | 02-00-TMU-V-107
397392 | CR | 20190730 |  | 3 | 12.5.8 Gaseous Effluent Discharge Sampling proc. enhancement | N | N |  | N | NO | <D> **** Detailed Description **** The instructions contained in 12.5.8 direct you not to decay correct for the time during which the sample was taken, however, the counting software asks for the sample start and stop to use in volume determination. Sections 7.1, 7.2, 7.3, 74 and 7.8 all should be updated to remove the step related to not decay correcting during sample collection. e.g. 7.3.12.d. <I> **** Actions Taken **** specialist informed
397393 | CR | 20190730 |  | 4 | 6 Pieces of M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** 6 Pieces of M&TE Passed Closeout Calibrations and have NOT been used. All have been Suspended until R25. 5 Industrial Scientific Gas Monitors- model Ventis MX4. Calcode #0067242 DEF #7073A written. Calcode #0067243. DEF #7074A written. Calcode #0067367. DEF #7075A written. Calcode #0068296. DEF #7076A written. Calcode #0068298. DEF #7077A written. Clemco Carbon Monoxide Alarm- model CMS-2 Calcode #0068519. DEF #7078A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only
397394 | CR | 20190730 |  | 3 | Enhancement to ABN-RHR-SDC-LOSS | N | N |  | N | NO | <D> **** Detailed Description **** The CAUTION prior to step 4.1.5 needs to be modified as it is not necessarily true anymore with the changes to TS 3.3.5.2 and the new water inventory control spec. Step 4.1.5 should also be evaluated for enhancement as well as this appears to follow the old guidance for the SDC level 3 isolation logic requirements. Recommend 4.1.5.a.1 to read "Verify RHR-V-8 is operable or 3.4.1 requirements are met". Recommend 4.1.5.b.1 to read "Verify RHR-V-9 is operable or 3.4.1 requirements are met". <I> **** Actions Taken **** CR submitted.
397398 | CR | 20190730 | CAQ | D | CRD-HCU-4259 Rod Accumulator Trouble Low Pressure | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-4259 Rod Accumulator Trouble alarmed on low pressure. Ops 2 corrected condition per SOP-CRD-HCU. | 02-00-CRD-HCU-4259
397400 | CR | 20190730 |  | 4 | 5 Pieces of M&TE Suspmneded Until R25 | N | N |  | N | NO | <D> **** Detailed Description **** 5 Heise Pressure Calibrators- model PTE-1XT Passed Closeout Calibrations and have NOT been used. Suspended until R25. Calcode #0068154. DEF #7079A written. Calcode #0068155. DEF #7080A written. Calcdoe #0068156. DEF #7081A written. Calcode #0068159. DEF #7082A written. Calcode #0068201. DEF #7083A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only
397402 | CR | 20190730 | CAQ | C | PM WO 02135151 status changed without performing the work | Y | N |  | N | YES | <D> **** Detailed Description **** WO 02135151 (starter coil replacement) for HPCS-42-4A2D asset suit status indicates FINISHED yet the work scope was not performed. <I> **** Actions Taken **** initiated CR <N> This work order was scheduled during the HPCS window with the wrong part reserved. There were none of the correct size coils on hand. When planning was challenged with the intent of the work order, he responded that if the coil was bad elect. were to scavange a coil from a starter in the warehouse â€“ task 06. This has been the approach to the obsolete ITE buckets but not this type GE bucket. According to ENG., this should NOT have been the intent but to obtain the correct coil and replace. We tried to validate with Becker but the ENG did not respond until just recently. craft supervisor returned the work order to ready status and ensure it gets scheduled when due in 2023. It should not have been scheduled this early. | 02-00-HPCS-42-4A2D
397403 | CR | 20190730 |  | 4 | M&TE Rejected | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0059132 Quest Technologies Heat Stress Monitor- model Questemp 10 Passed Closeout Calibration and has NOT been used. Rejected- Broken Beyond Repair. DEF #7084A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only
397404 | CR | 20190730 |  | 3 | D-EDR-V-150A -001 C/O enhancement for future tagouts | N | N |  | N | NO | <D> **** Detailed Description **** D-EDR-V-150A -001 placed Control Switch for EDR-V-139/141 in the recycle position which closes EDR-V-139 and opens EDR-V-141. Closing EDR-V-139 gives worker protection for the EDR-V-150A internal rebuild job. However, opening EDR-V-141 without further isolation of EDR-DM-29 creates a drainpath to EDR-TK-2 or 5 which probably caused drying out of EDR-DM-29 resin, possibly resulting in premature exhaustion of the resin. The control switch has a CLOSED position which would have shut both valves, protecting workers and not draining the deep bed. Suggest increased sensitivity of this condition in future radwaste tagouts that interface with deep beds. <I> **** Actions Taken **** Notified Supervision and wrote this CR.
397406 | CR | 20190730 |  | 3 | ROA-TS-2: Parts will not mount like for like, new modle TS | N | N |  | N | YES | <D> **** Detailed Description **** WO: 02127707-01. Replacement part does not match currently installed part. Mounting configuration will not work. new TS has mounting feet that protrude from the face of TS. Unlike the old TS, which is mounted flush "Face to Face" with a mounting plate, making replacement impossible Reference pictures in the 01 task and the 02 task. New Like for Like part is needed, or mounting plate needs modification. <I> **** Actions Taken **** Supervision notfied, WO taken to returned. . AR Type EVAL needed? <N> **** Equipment Description **** 572 RX | 02-00-ROA-TS-2
397410 | CR | 20190730 | CAQ | D | No change in leakrate after torquing FP-F-6A & 6B. | N | Y |  | N | YES | <D> **** Detailed Description **** FP-V-6A & 6B were torqued to 225 ft-lbs in an attempt to stop leakage per clearance D-FP-V-5 -001. FP-V-6A had no movement and FP-V-6B handwheel moved about 0.5." TSW-V -228 was also checked shut and got approximately 1/16 of a turn but no change in leakbye. | 02-00-FP-V-6A,02-00-FP-V-6B,02-00-TSW-V-228
397411 | CR | 20190730 |  | 4 | WOA-FN-3 breaker fuses potentially tripped - No Indication | N | N |  | N | YES | <D> **** Detailed Description **** WOA-FN-3 breaker had no indication and tested with new bulbs. Fan locally was rotating slowly in reverse. Breaker cycled with thermal overload reset and no change to indication. Fuses are likely blown. <I> **** Actions Taken **** Breaker cycled and reset with CRS permission. No change. | 02-00-WOA-42-7E2C
397412 | CR | 20190730 |  | 3 | SOP-HVAC/RB-OPS Enhancement | N | N |  | N | NO | <D> **** Detailed Description **** SOP-HVAC/RB-OPS, Section 5.2, for entering the RB HVAC enclosure, directs declaring secondary containment inoperable due to the potential to exceed -.25â€ WG while the enclosure door is open. TSSR 3.6.4.1.1 has been revised to provide a note that TSSR 3.6.4.1.1 is not required to be met for 4 hrs if analysis demonstrates that a SGT subsystem is capable of establishing the required secondary containment vacuum. References to operations with the potential for draining the vessel should also be removed. Recommend revising the SOP to remove references to declaring secondary containment Inoperable for RB HVAC enclosure entry/exits and add information relative to assessing secondary containment operability per TSSR 3.6.4.1.1 and OSP-INST-H101, Att 9.9. Proposed draft attached to EDMS.
397413 | CR | 20190730 |  | 4 | P602.A5 4-7 RWCU pump A trouble alarm | N | N |  | N | YES | <D> **** Detailed Description **** MCR received P602.A5 4-7 on 7/30 at approximately 0830. OPS2 reported the alarm was due to CRD purge flow low (CRD-FS-2A alarm setpoint 1.5gpm) with installed ultrasonic flow element reading 2.2-2.8 gpm and CRD-DPI-7 (RWCU purge filters differential pressure) reading 28 psid. The ARP has an action to swap RWCU purge filters at 30 psid. The alarm cleared with no operator actions taken approximately 30 min later. CR initiated for trending. <I> **** Actions Taken **** Informed CRS, dispatched OPS2 to investigate, initiated AR/CR | 02-00-CRD-FS-2A
397414 | CR | 20190730 |  | 3 | TMU Pump House Camera Request | N | N |  | N | NO | <D> **** Detailed Description **** Request IS install a remotely controlled camera in the TMU pump house to allow remote viewing. this would support fire alarm response and personnel safety for workers in the pumphouse working alone (e.g. Ops 4 on rounds). <N> **** Equipment Description **** TMU Pumphouse
397415 | CR | 20190730 |  | 3 | TMU pumps failed to start (R24) |  |  |  | N | YES | <D> **** Detailed Description **** During R24 the TMU pump pre-lubricating water flow permissive could not be satisfied for TMU-P-1A, TMU-P-1B, or TMU-P-1C, when attempting to place the TMU pumps in service. This condition was documented in CR 393597, but the cause has not yet been determined. Recommend further investigation to determine the cause and appropriate maintenance to prevent recurrence. <N> The TMU system supports the in-scope MRule function of providing makeup to the Service Water ponds following a design basis tornado. The inability to place a TMU pump in service challenges the reliability of the in-scope function of the TMU system. | 02-00-PWC-P-5,02-00-TMU-FIS-5A,02-00-TMU-FIS-5B,02-00-TMU-FIS-5C
397416 | CR | 20190730 |  |  | (IST) Clarification needed in OSP-SW/IST-Q703 |  |  |  | N | NO | <D> **** Detailed Description **** Revisions to OSP-SW/IST-Q703 per TIRP 378527 in 2018 included the installation of a Heise gauge each quarter to minimize instrumentation inaccuracies and to allow trending of any deltas between the gauge reading and SW-PI-40. Following a yearâ€™s worth of data, it is recommended to permanently implement the Heise gauge installation for each quarterly test. With the installation of this gauge, the 2 year CPT can be credited to the quarterly test. The procedure needs to be revised to provide these clarifications. Assign to AR-PPROG.
397417 | CR | 20190730 |  | 3 | Standard out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Calcode 0064458 Thunder Scientific Model 1200 Humidity Generator was found OOT and adjusted. The OOT parameter was not used during the cal cycle. NOD 20-04 issued. Please assign to CALSERV
397420 | CR | 20190730 |  | 3 | E520-3 & EWD-48E-005 typographical errors | N | N |  | N | NO | <D> **** Detailed Description **** AED E520-3 has a typographical error; TG-SV-TGY at D-7 should actually be TG-SV-TGV. EWD48E-005 has a typographical error; TO-BS-BL at E-9 should actually be TO-PS-BL.
397423 | CR | 20190730 |  | 3 | OSP-SW/IST-Q703 Procedure Enhancement | N | N |  | N | NO | <D> **** Detailed Description **** The 2 yr CPT has been performed quarterly as directed by engineering to utilize the heise gage used in the CPT to support the normal quarterly IST test. This is to ensure a more accurate reading of pump discharge pressure. In discussion with the IST engineer it is desired to continue this and a change to the surveillance would be prudent to utilize the heise gage quarterly. Discussed an action for the IST engineer who will draft a revision to the procedure.
397425 | CR | 20190730 |  | 4 | 12 Pieces of M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** 12 Heise/ Ashcroft Sensors models HQS-2 30 or 60psig have Passed Closeout Calibrations and have been Suspended until R25 . See EDMS for list of Calcodes & DEF #'s. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
397426 | CR | 20190730 | CAQ | C | Intermittent TMU Pump House Fire alarm | N | N |  | N | YES | <D> **** Detailed Description **** At approximately 0905 on 7/30, received FCP-1 drop 8-2 TMU Pump house Fire alarm in and clear. Once cleared this alarm came in and cleared again about 5-10 min later. Verified MCR indications of TMU parameters were normal and stable. OPS4 was dispatched to investigate and reported no indications of smoke or fire. These alarms were concurrent with the performance of PPM 15.2.2. <I> **** Actions Taken **** Informed CRS and SCC, dispatched OPS4 | 02-00-FP-CP-LCP1
397427 | CR | 20190730 |  | 4 | Oracle DR DB server122 failed hard disk | N | N |  | N | YES | <D> **** Detailed Description **** Oracle DR Database server SERVER122 has a failed internal disk (hdisk1). The internal disks are mirrored so no data has been lost and no systems have been affected. <I> **** Actions Taken **** Contacted IBM for replacment under current maintenance contract. The failed disk has been evacuated and is ready to be replaced by IBM on 7/30/19. <N> **** Equipment Description **** Corporate Computer equipment . No EPN <S> Call placed to IBM and replacement drive installed by IBM Field Engineer. Verified the data was mirrored to the new drive and no errors present. Recommend NCAQ-4.
397430 | CR | 20190730 |  | 4 | M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0068674 Hytorc Hyd. Torque Wrench- model ICE-3 Passed Closeout Calibration and now Suspended until R25. DEF #7097A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
397434 | CR | 20190730 |  | 3 | RWCU SOP Enhancement to prevent pump damage | N | N |  | N | NO | <D> **** Detailed Description **** The RWCU pump motors are sensitive to heat damage caused by process fluid entering the motor. The CRD purge system and an external HX with RCC cooling water are used to keep hot process water from damaging the motor. The motor assembly is very expensive (GT $700K). On 1/12/2017 a leak from the fill and vent piping on the RWCU-P-1B motor was discovered (See AR 360121). In response the pump was stopped and CRD purge isolated. The pump was not isolated from the process fluid. As a result, hot water flowed through the motor and out the leak, permanently damaging the RWCU-P-1B motor (see AR 361003). The motor had to be replaced at large cost and dose (GT 750 mRem). The operating procedures should be updated to address this situation so the pump can be isolated prior to securing the pump and securing CRD purge. This can prevent expensive damage to the motor in the future if a leak is to occur again at the RWCU pump. Recommend assignment to Ops Procedures. Engineering to provide recommended wording to update the procedures.
397437 | CR | 20190730 | CAQ | C | Voltage Below Admin Leve on E-PP-7AF | Y | N |  | N | YES | <C> CR reopened to add completion required check mark to referenced WO 02147724 per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** During performance of OSP-ELEC-W102 per WO 02137381 the voltage on E-PP-7AF was 118.9 volts, below the admin limit of 119.0 volts. The measured 118.9 volts is above the minimum allowable voltage of 114.0. CR to evaluate and trend. | 02-00-E-PP-7AF
397439 | CR | 20190730 |  | 3 | Inadequate planning of Engineering Change | N | N |  | N | NO | <D> **** Detailed Description **** On 07/30/19, OPSPROC was notified that EC 17007 for AR-V-1 would be field implemented the following day. No assignment had been created for affected Operations procedures to be revised. Once notified, an assignment was created for OPSPROC to revise the affected procedures with a due date of 08/05/19. This is only 3 business days later. This is in conflict with SWP-PRO-02, section 5.3 which states that the standard turnaround time for procedure revision processing is nine business days. This does not include drafting, review, and approval of revisions. SWP-DES-01, step 2.3 states that implementation includes integration of changes to affect plant procedures. This is another example of inadequate planning and execution of an engineering change via the Standard Design Process. <I> **** Actions Taken **** Affected procedures will be revised and coordination with Document Control will be required to expedite implementation. Other instances: CR 394512, CR 394833, CR 396617
397440 | CR | 20190730 |  | 4 | Replacement of WMA-TE/TT-53B | Y | N |  | N | NO | <D> **** Detailed Description **** WMA-TE-53B was found installed inside ducting, zip tied to a section of copper tubing that spans the width of the duct. The copper tube is swageloked to bulk head connections that are located on adjacent sides of the duct. Access to the inside of the air handler duct is required for replacement of WMA-TE-53B which expands scope significantly to this maintenance task. <I> **** Actions Taken **** Stopped, contacted supervision, operations, restored original WMA-TE-53B, and sent WO to planning for revisions.
397441 | CR | 20190730 |  | 4 | Erratic and unreliable Circ water PH indication | N | Y |  | N | YES | <D> **** Detailed Description **** At 1311 on 7/30 the control room received CIRC WATER B/D NPDES PH LIMIT HIGH on the Alarm typer. No accompanying CW Chemistry trouble was received. Computer point F141 and local instrument readings were reading unreliably from 9.5 up to 14.0 in step changes. Chemistry reported grab samples at a pH of 8.46. While the grab sample is within band, the instrument readings are outside our NPDES limits. Also a high pH is an input to SAT-P-1A(B) to initiate to lower CW pH, erroneously in this case. Recommend calibration/repair of CW-PHITS-1 at earliest opportunity. <I> **** Actions Taken **** Informed CRS and SSS. | 02-00-CW-PHITS-1
397443 | CR | 20190730 |  | 4 | Both RWCU Purge filters need to be replaced CRD-F-7A/B | N | N |  | N | YES | <D> **** Detailed Description **** Swapped to CRD-F-7A while responding to RWCU Pump A Trouble but it was found at 25 psid. CRD-F-7B is at 28 psid and needs to be changed out. Current configuration is CRD-F-7A in service with CRD-F-7B isolated per SOP-CRD-FILTERS, sect 5.6. This CR/WR is for the changeout of CRD-F-7B as there is already a current active CR/WR for CRD-F-7A (393685, 29148799) that is H/APPR status since 5/18/2019. <I> **** Actions Taken **** Notified CRS and generated CR/WR | 02-00-CRD-F-7B
397444 | CR | 20190730 |  | 4 | HT-HTP-FP/6/1 Power On Lights Not Functioning | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO# 02117003-01 the â€˜Power Onâ€ lights for 50F and 51F were found not working and may need new lamp sockets due to replacement lamps not working when installed. Further investigation needed. Heat trace still fuctions as designed. <I> **** Actions Taken **** Notified supervision and CR | 02-00-HT-HTP-FP/6/1
397445 | CR | 20190730 |  | 4 | RWCU Pump A Trouble Locked In - Low Flow | N | N |  | N | YES | <D> **** Detailed Description **** During response to RWCU-P-1A trouble alarm in control room, discovered low flow light. Ultrasonic flowmeter indicated 2.2 - 2.7 gallons per minute. Adjusted CRD-FCV-512A up to 3 gallons per minute per ARP 4.602.A5 and alarm cleared (large deadband). Upon restoring to normal flow, the alarm was set off again at 2.8 gallons per minute. Flow was restored to 2.3 to 2.8 gallons per minute with alarm locked in. <I> **** Actions Taken **** Attempted to clear alarm with actions from ARP 4.602.A5, step 3. Alarm clears at about 3 gallons per minute, but realarms at about 2.8 gallons per minute. | 02-00-CRD-FCV-512A
397446 | CR | 20190730 |  | 4 | SO-P-SOBP coupling is in poor condition | N | N |  | N | YES | <D> **** Detailed Description **** While replacing the motor WO# 0212882401 It was found that the coupling is in very poor condition and could be some of the cause of the abnormal niose. The whole coupling should be replaced not just the rubber spider. the coupling is a lovejoy L-190, motor bore is 1 7/8" and the pump bore 1 1/4". <I> **** Actions Taken **** Contacted supervisor and planner. currently the coupling is removed for the motor solo run. | 02-00-SO-P-SOBP
397447 | CR | 20190730 | CAQ | C | (QA) Maintenance Work Process GAP â€“ PV in Work Requests | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) Quality Services identified a gap in the work management process that reveals a vulnerability to missing required inspection activities. Work Request 29150633, containing less than adequate information and direction, was used to correct an error from WOT 02117111-01 where an incorrect fuse was installed in Safety Related Starter SW -42-4A6D. Work Request 29150633 did not clearly contain Peer Verification (PV) Hold Points for parts and installation, PV sign-offs or Limitations on Use (LOU) for the replacement fuse. WOT 02117111-01 contained clearly identified LOUs, PV Hold Points and PV sign-offs. Entering the Work Request process instead of revising the original WOT or creating a new WOT to correct the deficient condition potentially misses required inspections. Factual Basis: â€¢ WOT 02117111-01, (SW-V-29) SW-42-4A6D TEST AND INSPECT STARTER (SR), contains PV Hold Points and sign-offs for parts and installation for the fuse replacement. â€¢ CR 397161 identifies that an incorrect ATM3 fuse (CID 70005075) was installed per WOT 02117111-01, when a FNQ-R-3 fuse (CID 7642) should have been installed. â€¢ Work Request 29150633 was developed and performed to replace the incorrect fuse and has PV next to the line for the fuse replacement, but does not indicate if there is a PV Hold Point or if a Peer Verifier should initial for acceptability for the fuse replacement. The completed work request (see EDMS) did not have an initial next to the PV. â€¢ SWP-INS-01, Quality Control Inspection and Peer Verification, Section 3.8 states: â€œWork Order Task steps subject to Peer Verification should have double sign-off blocks, one for the Task performer and one for the Peer Verifier. The Peer Verifier shall not be the one who performed or directly supervised the activity being inspected. {R-6.2}â€. â€¢ QAP-ASU-07, Peer Verification Program Planning, specifies acceptable planning methods for PV steps as it relates to WOTs and WOT instructions. Attachment 8.6 provides specific examples and details for writing PV Hold Points within WOT instructions and the PV Hold Point Index and PV Hold Point Summary within the Portal J M108 panel of the WOT. A work request does not contain typical WOT Instructions and does not have an M108 panels. â€¢ QAP-ASU-07, Attachment 8.5, states that fuse replacement in QC-1 components is exempt from QC or PV inspection. Insight: â€¢ Quality Control convened a meeting with Maintenance and Work Control on July 8, 2019 to discuss using peer verification in work requests. It was agreed in this meeting, that until a decision is reached and applicable procedures are revised addressing inspections within work requests, that PV would not be performed using work requests. The Component Group Manager stated that this information was discussed with the maintenance supervisors. <I> **** Actions Taken **** This issue is considered a Deficiency identified during continuous monitoring activities. Quality recommends assignment to Maintenance. <N> **** Equipment Description **** N/A
397449 | CR | 20190730 | CAQ | C | 6/20/2019 nights CR02 FDR-FQ-38 apparently logged in error | Y | N |  | N | NO | <D> **** Detailed Description **** The number logged in eSOMS for FDR-FQ-38, floor drain radioactive flow totalizer, on 6/20/2019 nightshift appears to be incorrect. This number is used to calculate flow for OSP-INST-H101 to satisfy technical specification surveillance requirement 3.4.5.1 on a 12 hour frequency. EDNA trend data from that time period shows no change in indicated flow from FDR-FT-38. Using the logged data from FDR-FQ-38 before and after the suspected logging error there was no change floor drain flow and therefore no reason to believe technical specification flow requirements were violated. This issue was identified when the NRC questioned consolidated entry data.
397450 | CR | 20190730 |  | 4 | ENW individual reported he had numbness on forearm and wrist | N | N |  | N | NO | <D> **** Detailed Description **** While working at the cubicle, individual feeling discomfort on left elbow in forearm and wrist. Individual report Occupational Health for evaluation. <I> **** Actions Taken **** Individual evaluate by Occupational Health and released to work. Industrial Safety notified. Employee and Supervisor Evaluation of Incident Form fill out.
397451 | CR | 20190730 | CAQ | C | NRC Resident provided feedback/coaching to employee | N | N |  | N | NO | <D> **** Detailed Description **** On the afternoon of 7/30 an ENW employee processing through the PAAP search train announced that the NRC Resident Inspector was getting ready to come through the area. The NRC Resident was in proximity to hear this statement, and immediately provided coaching to the employee. Additional coaching was provided to the employee by ENW management. <I> **** Actions Taken **** Coaching provided. Appropriate Management notified. Follow up communication was conducted with NRC Resident to relay additional coaching had been provided to employee. CR generated. <N> Coaching was provided on the spot to the individual. Individual went to all security squad briefings and briefed the situation and provided lessons learned. D15 thumbs down write up was provided for station distribution. At this time no further actions are being conducted. . During the time of event NRC resident was not conducting any formal inspection activities.
397453 | CR | 20190730 |  | 4 | SA-PCV-10 gland follower nut found loose | N | N |  | N | YES | <D> **** Detailed Description **** WHile performing a nearby drain valve, I noticed the gland nut was loose on one side of the follower on SA-PCV-10. <I> **** Actions Taken **** notified supervision and wrote this CR | 02-00-SA-PCV-10
397454 | CR | 20190730 |  | 4 | Labels falling off on MCR Board GG2 |  |  |  | N | YES | <D> **** Detailed Description **** Multiple labels are falling off on MCR board H13-P833 and are being held up by scotch tape. Please repair with a better adhesive. <I> **** Actions Taken **** CR/WR <N> **** Equipment Description **** MCR Board H13-P833, G2
397455 | CR | 20190730 |  | 3 | Leader & Organizational Performance Potential Adverse Trend |  |  |  | N | NO | <D> **** Detailed Description **** There have been some recent examples where leaders may not be consistently demonstrating, through their own actions and behaviors, industry leading performance related to Set Direction essential outcome as described in an industry best practice publication associated with leadership and teamwork effectiveness and included in the Excellence Model handbook. These examples include an emergent R24 failure of COND-P-4 motor requiring replacement (reference AR 394756) where motor replacement has been met with numerous challenges resulting in 6 completion date commitment changes in the last 3 to 4 weeks. Examples also included are AR 397262 and AR 397264. These two ARs were screened as severity level 4, close to trend, with no further action required. Each of these potentially involve opportunities missed for leaders to demonstrate more passion for determination of organizational and/or programmatic causes. <I> **** Actions Taken **** Discussed during management CR review on 7/30/2019 and agreed to initiate this CR for potential further analysis of these examples for O&P causes or other opportunities to learn and take appropriate action.
397456 | CR | 20190730 | CAQ | D | Rod Accumulator Trouble Alarm for CRD-HCU-5819 | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-5819 was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear. Trending only. | 02-00-CRD-HCU-5819
397457 | CR | 20190730 | CAQ | D | CRD-HCU-58-19 High Water Level alarm received | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-58-19. After investigation, Rod Accumulator Trouble Alarm P603-A7 drop 6-7 was for CRD-HCU-58-19 high water level. <I> **** Actions Taken **** Wrote CR OPS 2 Cleared alarm | 02-00-CRD-HCU-5819
397461 | CR | 20190731 | CAQ | D | CRD-HCU-26-51 High Water Level alarm received | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-26-51. After investigation, Rod Accumulator Trouble Alarm P603-A7 drop 6-7 was for CRD-HCU-26-51 high water level. <I> **** Actions Taken **** Wrote CR OPS 2 cleared alarm | 02-00-CRD-HCU-2651
397462 | CR | 20190731 |  | 4 | 16 Pieces of M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** 16 Torque Wrenches were NOT used during Calibration cycles and have been Suspended until R25. See EDMS for list of Calcodes, models and DEF #'s associated with each one. No Action Required. <I> **** Actions Taken **** None Trending purposes only
397465 | CR | 20190731 |  | 4 | 10 Pieces of M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** 10 Pieces of M&TE were NOT used during Calibration cycles and have been Suspended until R25. See EDMS for list of Calcodes, descriptions, models and associated DEF #'s for each. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
397475 | CR | 20190731 |  | 3 | A new section is needed in SOP-CRD-HCU. |  |  |  | N | NO | <D> **** Detailed Description **** Currently, SOP-CRD-HCU section 5.7 is the section primarily used for isolating an HCU for maintenance. When the plant is online and only the scram accumulator is being replaced a gag device is being used to gag closed CRD-V-126/XXXX as a second boundary to CRD-V-101/XXXX per AR 389736. Performing steps 5.7.19 through 5.7.23 are unnecessary and needlessly challenge the gag on CRD-V-126/XXXX. Recommend creating a new section for isolating CRD-HCUâ€™s for the purpose of only replacing scram accumulators that would remove steps 5.7.3 through 5.7.4, 5.7.9, 5.7.19 through 5.7.23 and steps 5.7.33 through 5.7.36. Please see marked up copy in EDMS. This would be a new section not a change to section 5.7. <I> **** Actions Taken **** Discussed with procedure group SRO.
397478 | CR | 20190731 |  | 4 | Output from TG-MON-VB4 cannot be detected | N | N |  | N | YES | <D> **** Detailed Description **** During Main Turbine shaft vibration data acquisition, TG -MON-VB4 output signal could not be recorded with the rest of the other bearingsâ€™ data. TG-MON-VB4 is the module on the Bentley Nevada 7200 that indicates vibration levels for Bearing 4 in the Main Control Room (MCR). The module display is reading normally and consistent with eDNA data at around 4 to 4.3 mils. The loss of output signal inhibits data acquisition for Bearing 4, but does not impact data collection for the other bearings. The purpose of the current data collection effort is to calculate balance requirements for Bearing 7 and Bearing 8. The necessary data required for a balance move at these locations is being acquired and is not affected by the condition. The deficiency appears to be isolated to the output from the three jacks on the front of the module (Rel, Abs, and Sies), which are not used by Operations. This condition does not impact Operations ability to read vibration levels, see panel alarms, or follow monitoring or ARP requirements. The module is obsolete, but will need to be replaced or refurbished. <I> **** Actions Taken **** Checked ground, swapped cables, swapped connectors, swapped jack locations. Informed supervisor (acting) and manager. <N> **** Equipment Description **** Bentley Nevada panel, MCR | 02-00-TG-MON-VB4
397480 | CR | 20190731 |  | 4 | fire alarm trip at Building 35 | N | Y |  | N | NO | <D> **** Detailed Description **** During testing on the HVAC system in building 35(training center) inadvertent trip of the fire alarm occurred. The alarm system was not disabled as required for the testing. The testing was expected to complete in 1 day, but carried into the second day. All alarms were restored after the first day of work; notifications were not made on the next day to re-disable the alarm system. Ineffective communications between the 3 groups involved led to starting the test without disabling the alarm first. <I> **** Actions Taken **** Verified alarms were from the testing and not from actual fire. Alarms were reset in Building 35. <N> **** Equipment Description **** fire panel in building 35
397482 | CR | 20190731 |  | 4 | MT&E found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0066212 HEISE Model CM300 GAUGE, PRESSURE 300 PSIG was found out of tolernance and adjusted. Not used during Calibration cycle. DEF #7124A written. No Plant Impact. No Action Required.
397483 | CR | 20190731 |  | 4 | SP-4 In-Line Recorder GT 10% Difference | N | N |  | N | YES | <D> **** Detailed Description **** SP-4 in-line conductivity recorder disagrees with grab sample by 12%. Recorder still in service. <I> **** Actions Taken **** Initiated CR, Specialist informed <N> **** Equipment Description **** 441' TG Chemistry Sample Room | 02-00-S-CR-1
397484 | CR | 20190731 |  | 3 | No Spare CRD Pump Preventative Maintenance Performed |  |  |  | N | NO | <D> **** Detailed Description **** Spare Control Rod Drive (CRD) pump CATID 58166983 was refurbished and placed in warehouse storage on 03-01-12 via PO 335505. PMID 26709 was completed on 04-17-19 to PM the pump which is scheduled for November 2019. The CRD pump is scheduled for replacement in October 2019. No PM's have been performed on the pump since it delivered in 2012. Long Term Storage requirements via the OEM have not been followed. The OEM is no longer in business. Other manufacturers of like pumps, the refurbishment vendor, component Engineer and other SME's recommend the bearings be replaced, the O-rings checked, shaft sag checked, mechanical seal inspected and gaskets replaced before installation. <I> **** Actions Taken **** 1. Notified Component Pump Engineer 2. Obtained several independent analysis and recommendation at recent Pump User Group meeting with the EN Pump Component Engineer. 3. Verified the pump had not been PM'd with the Maintenance PM Coordinator 4. Requested a quote from the refurbishment vendor to inspect and restore the pump to a condition where the confidence to operate in the plant for 12 years is not at risk due to 7 years in storage without a PM being performed. 5. Notified Supervisor 6. Notified Asset Management of potential additional cost of the CRD Pump Replacement Project. <N> ***General Notes*** Extent of condition conducted under CR# 390209.
397485 | CR | 20190731 | CAQ | C | PPC-CPU-VMS/WS found with cpu halt error | N | N |  | N | YES | <D> **** Detailed Description **** On 7/30/2019, a Main Control Room operator inquired why he was unable to view the PPC screens in Reflection. The program would open but failed to connect to or show any data from PPC. TDAS worked fine. Investigating the PPC console, PPC-CPU-VMS/WS showed an error screen, apparently occurring pre-boot or during boot. See EDMS for photos. Recommend cat D to Computer Engineering to power cycle workstation or evaluate replacing parts, if applicable. <I> **** Actions Taken **** Took screenshots, wrote CR. | 02-00-PPC-CPU-VMS/WS
397489 | CR | 20190731 | CAQ | C | MCCB failed testing | Y | N |  | N | YES | <D> **** Detailed Description **** When the HPCS-42-4A3D molded case circuit breaker was tested, it tripped below the acceptable range on one phase. A new breaker was issued, tested, and installed. The failure was not documented with a condition report. | 02-00-HPCS-42-4A3D
397493 | CR | 20190731 |  | 4 | EDR-V-150A as found condition | N | N |  | N | YES | <D> **** Detailed Description **** During W.O 02114501 we performed investigations to verify if this valve was sticking in the seat. This valve operates satisfactory and does not need rebuilt. Note to planning and engineering for the future....do not plan a work order for valve repair. We found the stem seal on the air actuator had a minor leak which was repaired. This valve shares a common air supply with the 150B valve. Both of these need the modification under AR 200902 done to them. If the concern of this work order repeats itself in the future, the EC needs to be implemented. <I> **** Actions Taken **** notified supervisor <N> EC MALT 4322 is CLOSED. AR Eval has been written to satisfy this issue. (Ref AR# 397551) | 02-00-EDR-AO-150A,02-00-EDR-AO-150B,02-00-EDR-V-150A,02-00-EDR-V-150B
397497 | CR | 20190731 |  | 4 | pump house A has lights that are burned out. | N | N |  | N | YES | <D> **** Detailed Description **** pump house A has various lights that are burned out. <I> **** Actions Taken **** write CR <N> **** Equipment Description **** pump house A Verified 4 of 8 overhead light fixtures are out. These are all from E-LP-3DC.
397500 | CR | 20190731 | CAQ | D | failed HEPA testing for OFMA-HF-1C and 3 | N | Y |  | N | YES | <D> **** Detailed Description **** Testing of the OFMA HEPA systems in building 35 resulted in failed results. OFMA-HF-1C (WO 02138368) Failed test OFMA-HF-3 (WO 02146090) Failed Test OFMA-HF-1H (WO 02138369) Passed testing These filters all will require replacement, as some of the filters have dates of 1987 on them. New Work packages need to be planned and parts ordered to <I> **** Actions Taken **** Contacted EP and notified as this is EP equipment | 02-00-OFMA-HF-1C,02-00-OFMA-HF-1H,02-00-OFMA-HF-3
397501 | CR | 20190731 |  | 4 | Failed NWT cross check due to instrument bias |  |  |  | N | NO | <D> **** Detailed Description **** The reported value for chlorides and sulfates for NWT set 128 was biased low due to the instrument being biased low. The concensus known value was higher by 16% which is outside of the 15% that is with in 3 sigma. The instrument was re-calibrated and the samples were re-run. The new analysis provided acceptable values of +/- 5%. This CR is written as a trending CR for documentation purposes as the issue was not due to Chemistry technician error. <I> **** Actions Taken **** Notified Chemistry Supervision and re-ran samples
397502 | CR | 20190731 |  | 4 | SAT-PCV-1 making abnormal noises. | N | N |  | N | YES | <D> **** Detailed Description **** SAT-PCV-1 is making abnormal noises each time the SAT pump strokes. <I> **** Actions Taken **** Notified CR, wrote CR. | 02-00-SAT-PCV-1
397503 | CR | 20190731 | CAQ | C | CMS-SR-20 failure to start after maintenance | Y | N |  | N | YES | <D> **** Detailed Description **** Startup was attempted on CMS-SR-20 (SOP-CN-OPS section 5.5) after a particulate detector replacement. On Step 5.5.14, when the SELECT key was pressed to start the sample pump, the PUMP ON light illuminated and the PUMP OFF light extinguished, however no flow was observed on CMS-FIS-1 (CMS-FE-1 indication), and the pump indication lights swapped with the PUMP OFF light illuminated and the PUMP ON light extinguished after approximately 30 seconds. Per the procedure, flow must exceed 1 SCFM within 30 seconds after the sample pump is started or it will trip. After stopping at step 5.5.14, CMS-SR-20 was shutdown per section 5.7 by direction of the CRS for PCSC. <I> **** Actions Taken **** Notified CRS/SSS | 02-00-CMS-SR-20
397504 | CR | 20190731 |  | 3 | Expired staged equipment, SWPH B |  |  |  | N | NO | <D> **** Detailed Description **** There is a pile of scaffold equipment with a staged equipment sign that expired June 28th inside the SWPH 'B' delay fence. The referenced WO is 02111471-10. Please remove this equipment. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> Willaims Plant Services. Scaffold materials have been removed and stored in an approved location. AR can be closed.
397505 | CR | 20190731 |  | 4 | SW Pond Level Gauges need cleaning | Y | N |  | N | NO | <D> **** Detailed Description **** The gauges used to indicate SW pond levels are very dirty and crusted, making them very hard to read. Please clean these gauges. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** Level gauges (tapes) in each SW pond.
397506 | CR | 20190731 |  | 4 | R25 Outage Indicators not working to support open milestones |  |  |  | N | NO | <D> **** Detailed Description **** It was discovered while opening PO.27 for R25 (outage walk downs being completed) that the Pre-Outage performance indicators are not functioning. These PIâ€™s are required to be updated and running per PPM 1.20.1 as criteria for opening the milestone. The recent revision made to pull these milestones earlier into the cycle created or compounded this problem as scope is not established yet. Currently affected open milestones affected are planning complete, Clearance orders prepared, and Walk downs complete. <I> **** Actions Taken **** Brainstormed solutions with the outage manager, outage lead scheduler, and outage supervisor, but require IS to support the fix. The outage group has written ITSR 397481 to address this. Recommend outage group take this CR and champion the resolution.
397507 | CR | 20190731 | CAQ | D | E-PP-7AF VAC A phase found lower than administrative limit | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02147724 marked completion required box, then taken back to complete <D> **** Detailed Description **** E-PP-7AF VAC on A phase found lower than administrative limit detailed in OSP-ELEC-W102 attachment 9.3 . Breaker E-PP-7AF voltage was as found is currently 118.94 VAC the administrative limit is 119.0 VAC and a Min low voltage of 114.0. Craft used a couple of Flukes and found the readings to be accurate. The only anomaly found was the VAC started at 119.15 right when you place the meter on the A phase then would start to stabilize at 118.94 VAC (see attached photo for MAX reading found ). <I> **** Actions Taken **** Contacted CRS and SM wrote CR . Documented data in WO 02137558-01 <N> This CR is the same issue as identified in AR 397437. Assignment to referenece this CR has been created under AR 397437 | 02-00-E-PP-7AF
397508 | CR | 20190731 | CAQ | C | PRM-SR-1 NGD-11 out of tolerance | N | Y |  | N | YES | <D> **** Detailed Description **** During the performance of ppm 16.1.11 step 7.35.19 the as found count rate value was out of tolerance. Adjusted HV value and re-performed count rate test. Raised high voltage value to 453VDC. The as left count rate is in tolerance. <I> **** Actions Taken **** Notified Supervision and Engineering adjusted HVPS to achieve acceptable activity. NDG-11 HVPS as left value is 453VDC. PRM-CCU-1 (PU-02 AA1) NGD-11â€™s IMDS HVPS value needs to be updated to reflect the new HV set point. <N> **** Equipment Description **** PRM-SR-1 <R> REP/REGE assignments cancelled with Compliance Supervisor concurrence. | 02-00-PRM-SR-1
397509 | CR | 20190731 | CAQ | C | Annulus ave temperature exceeded 150F on OSP-INST-H101 | Y | Y |  | N | NO | <D> **** Detailed Description **** Annulus ave temperature exceeded 150F on OSP-INST-H101. On 8/1/19 night shift OSP-INST-H101 the calculated annulus ave temperature reached 150.2F exceeding the RFO 1.7.1 limit of 150F. Entered RFO 1.7.1 and increased blowdown flow to lower RCC temperature and took actions associated with RFO. <I> **** Actions Taken **** Wrote CR and took RFO actions
397510 | CR | 20190801 |  | 4 | RCC-POI-4A only indicates 90% open with RCC-V-4A full open. | N | N |  | N | YES | <D> RCC-POI-4A only indicates 90% open with RCC-V-4A full open.Local indication for RCC-V-4A is Open. RCC-POI-4A indication was also eratic while opening. <I> Informed CRS/SM | 02-00-RCC-POI-4A
397511 | CR | 20190801 |  | 4 | Anti-Slip Ladder Rung Covers need Attention on RW 437' | N | N |  | N | NO | <D> **** Detailed Description **** The Anti-Slip Ladder Rung Covers on RW 437' Processing Tank Ladders need replaced. They are not in good condition and have electrical tape trying to hold them together. Some Anti-Slip Rung Covers are missing. (EDR-TK-5,EDR-TK -4A ,EDR-TK-4B & FDR-TK-9) <I> **** Actions Taken **** -Notified Supervision -Initiated CR & WR. <N> **** Equipment Description **** EDR-TK-5 (and other Processing Tanks on RW 437') HP Supervision walked down the safety concern identified in the CR. As an interim action, caution signs were placed in the area to warn workers of the potential hazard until the ladder rung covers can be replaced.
397512 | CR | 20190801 |  | 4 | IPM-8 @ HP PAP taken OOS | N | N |  | N | NO | <D> **** Detailed Description **** IPM-8 (HP-EQ-32777) at the HP PAP was taking its self Out of Service regularly and performing contamination checks while in alarm mode. Took IPM-8 out of service so it's not continuously doing these checks and causing unwanted noise at the PAP. <I> **** Actions Taken **** Notified Supervision Initiated CR/WR <N> **** Equipment Description **** HP PAP
397540 | CR | 20190801 |  | 4 | PWC-P-102 outer bearing is unusually warm. | N | N |  | N | YES | <D> **** Detailed Description **** The outer bearing on PWC-P-102 is unusually warm, estimated to be about 20-30 degrees warmer then the inboard bearing. <I> **** Actions Taken **** Initiated this CR. <N> **** Equipment Description **** Inside building 40 which is next to Flocculator building. | 02-00-PWC-P-102
397541 | CR | 20190801 | CAQ | C | EC 8458 missed updating drawing M607-1 |  |  |  | N | NO | <D> **** Detailed Description **** EC 8458 "Reroute feedwater heater drains and air removal piping" changed the piping configuration upstream of AR-V-1 to the LP condensor on drawing M511 but failed to update drawing M607-1. Drawing M607-1 shows a portion of this piping and needs to be revised to agree with drawing M511. Assign to AR-DESDFTM <I> **** Actions Taken **** Informed my Supervision
397543 | CR | 20190801 | CAQ | C | Received Recirc B System Vibration high alarm | N | N |  | N | YES | <C> AR was still open so I added WR 29150824 to the cross reference panel and checked the Completion required box. <D> **** Detailed Description **** Received Recirc B System Vibration high alarm, vibration panel indicates the point in alarm is RRC-VBI-P1B/XE reading +46 mils. Temperatures on RRC-TRS-601 for RRC-P-1B are stable not rising. OPS 2 attempted to reset the alarm, the alarm cleared but came back in shortly after. <I> **** Actions Taken **** Notified CRS and initated CR and WR <N> **** Equipment Description **** RB 522 | 02-00-RRC-P-1B,02-00-RRC-VBI-P1B/XE
397546 | CR | 20190801 |  | 3 | Repeat Universal Waste Storage Issues | N | N |  | N | NO | <D> **** Detailed Description **** Weekly inspection of the Universal Waste storage area located in the GSB machine shop identified two deficiencies with storage of universal waste lamps. Waste was stored in an open container without a secured lid and without a label. This condition is not meeting state and federal requirements to store universal waste. This is a repeat issue of CRâ€™s 392588, 397023, 391322, and 392403. <I> **** Actions Taken **** Wrote CR.
397547 | CR | 20190801 |  | 3 | Universal Waste Lamps Exceed Accumulation Time Limit | N | N |  | N | NO | <D> **** Detailed Description **** Weekly inspection of the Universal Waste storage area located next to the tool crib on RW 467â€™ identified two deficiencies with storage and accumulating universal waste. One container had a universal waste label with an accumulation date of 7/25/18. This exceeds the one year storage limit for universal waste. Another container of universal waste lamps was found without a proper universal waste label or accumulation date. This condition is not meeting requirements found in GBP-ENV-17 Section 4.3.12, State and federal requirements. <I> **** Actions Taken **** Wrote CR.
397549 | CR | 20190801 |  | 4 | Safety Shower 437â€™ RW OOS | N | N |  | N | YES | <D> **** Detailed Description **** The safety shower located at 437â€™ RW (DW-DWS-4) has been out of services for too long. This is the only shower located in the area and provides valuable protection for employees if they should come into contact with a hazardous chemical or radioactive waste. This shower has been inoperative since 5/2/2018 (CR 397230) and needs to be fixed. <I> **** Actions Taken **** Discussed issue with VP / General Counsel and wrote this CR. <N> Per Safety - there is a comp measure in place with a temporary shower there. | 02-00-DW-DWS-4
397552 | CR | 20190801 | CAQ | C | PWC Outlet Turbidity Meter did not record to chart recorder | N | Y |  | N | YES | <D> **** Detailed Description **** Potable water outlet turbidimeter, PWC-TBIT-2, did not record to PWC-XR-1 from 7/2/19 to 7/16/19. It is a regulatory requirement (DOH) to record the outlet turbidity every 4 hours while the flocculator is making water. The turbidimeter itself was working correctly and the local reading was correct. However, the value was not transmitted to the data recorder. I&C fixed the issue on 7/16/19. This has been a recurring issue for several months and happens each time the power is lost to the flocculator. This needs to be prevented from happening again as it is a regulatory requirement. <I> **** Actions Taken **** Notified E&RP and requested notification be made to the WADOH. The missing data will also be reported in the monthly potable water report to the WADOH. Please assign an action to operations to add the recorded outlet turbidity reading on PWC-XR-1 to the shiftly rounds in addition to the local reading on the turbidimeter on PWC -TBIT-2. <R> REP/REGE assignments cancelled with Compliance Supervisor concurrence. | 02-00-PWC-TBIT-2,02-00-PWC-XR-1
397553 | CR | 20190801 |  | 3 | Partial performance EC 17007 | N | N |  | N | NO | <D> **** Detailed Description **** EC 17007 was implemented up to the point of performing the cosmetic steps of removing the swith/indicating lights and installing a metal plate based on a discussion of risk with Operations, Electrical Maintenance, Engineering, and the Work Week Manager. Recommend creating a task to perform the removal of the RMS for AR-V-1 and installing the metal plate when the risk of impacting condenser vacuum and the exposure to energized conductors is reduced. Mechanical Gag installed per TMOD 16670 remains in place. AR-SPV-1/1 and 1/2 are both removed. Wires associated with RMS AR-V-1 are Spared per the PWTI in the EC. <I> **** Actions Taken **** Discussed with Operations, Electrical Maintenance, Engineering, and the Work Week Manager. . EC 17007 has been partially implemented - final implementation (i.e., of the non-completed implementation steps per WOT 02125129-01) will occur via the WO associated with WR 29150796. TMOD EC 16670 is being restored by this partial implementation of permanent modification EC 17007. <N> **** Equipment Description **** at Main Controlroom panel E-CP-H13/P820. . Follow on work will be completed under WR 29150796. See closure notes in assignment 01.
397554 | CR | 20190801 |  | 4 | 8-120B cask leak check not performed as scheduled | N | N |  | N | NO | <D> **** Detailed Description **** A vendor was scheduled to arrive on-site and perform a leak check on the 8-120B cask on 07/31/19 in support of shipment 19-88 RWCU HIC 19-012-HP. The equipment the vendor needed to perform the leak check was misplaced in transit therefore postponing the leak check and subsequent shipping date. <I> **** Actions Taken **** Arrangements have been made to receive another set of equipment and the leak check is currently scheduled to be completed on 08/01/19. No further action required.
397555 | CR | 20190801 |  | 3 | gasket material that is leak prone should not be used |  |  |  | N | NO | <D> **** Detailed Description **** There is current OE that nylon impregnated rubber gasket material is prone to leak. Engineering did an evaluation to use other gasket material that are not prone to leak. Work orders are still being planned using the nylon impregnated rubber. There are many workers at the station that are unaware that nylon impregnated rubber should not be used. Many of the planners are unaware of this and keep planning packages using it. Maintenance currently has an IMPO AFI for leaks. There needs to be a better communicated change for this. The Nylon impregnated rubber such as CAT # 26196 should be searched in work orders and removed. Should consider removing it from the WRHS. <I> **** Actions Taken **** Contacted supervisor and fluid leak coordinator
397557 | CR | 20190801 | CAQ | C | lost term block screw 0212512901 | N | N |  | N | NO | <D> **** Detailed Description **** during a "demo" wire removal job in the control room, one term block screw was dropped and lost at the bottom of the cabinet. Craft had a catch basin in place along with the proper tool (holding screw driver). however the screw bounced away after slipping out of the tool. QC and the NRC were present at this job and craft promptly reported this to the CRS. It is electrical crafts evaluation that this lost screw has no threat. Craft spent time serching for screw but with all the congestion screw was lost. <I> **** Actions Taken **** reported to CR reported to supervision <N> **** Equipment Description **** E-CP-H13/P820
397559 | CR | 20190801 |  | 3 | ALARA Suggestion, Move Controls for RW 437' Liner Trolley | N | N |  | N | YES | <D> **** Detailed Description **** The power controls for the RW 437' liner trolley, PWR-HOI -1, places the operator in unessesary dose fields. Dose rates at the controls can range from 5 mrem/hr up to 120 mrem/hr depending on the type of liner being moved. Some shielding has been placed at the hand rails to the trolley pit, but due to weight load restrictions on the false floor back by the controller, a shield rack in the area is not a viable option. Besides moving the controls it would also benefit the operator to have a light indicator as to the far East or West location of the trolley so a visual verification is not needed. One other hazard of having the controls located where they are is that if there was a malfunction of the crane and the liner was unable to continue being moved into a shielded cask, depending on the stopped location, the operator could be forced to exit the area in close proximity to the unshielded liner. <I> **** Actions Taken **** Discussed with the Rad Waste HP Technicians, RMC Laborers and HP Management that a CR would be generated to capture this concern. | 02-00-PWR-HOI-1
397561 | CR | 20190801 |  | 3 | PPM 11.2.6.1 may need revision | N | N |  | N | NO | <D> **** Detailed Description **** PPM 11.2.6.1 Issuance & Retrieval of Personnel Dosimetry may need revision. A TREQ (19-0083) was written recently on providing HP technicians training on issuing DLRâ€™s. Feedback is the procedure is not easy to follow. Please look into revising the procedure for clearer guidance if this warrants. Suggest to have snips of Asset Suite panels excluding any confidential personal information to show the flow along with the written guidance. Please see TREQ or myself for more information on the specifics. <I> **** Actions Taken **** TREQ 19-0083 previously written. Performing Needs Analysis and Performance Analysis. Discussed with Rad Support. SME created job aid with Asset Suite snips. Wrote this CR.
397566 | CR | 20190801 |  | 3 | PPM 3.2.1 Editorial Change | N | N |  | N | NO | <D> **** Detailed Description **** PPM 3.2.1, Normal Plant Shutdown, Step 5.6.32 directs setting DEH setpoint to EXACTLY 45psig to achieve RPV pressure of LT 48 psig. In reality, the DEH setpoint required to achieve RPV pressure of 48psig varies depending on decay heat, lenght of shutdown, and other factors. Recommend changing PPM 3.2.1 step 5.6.32.b to read "approximately 45psig". This provides flexibility to go beyond 45psig if necessary. Recommend assignment to operations procedures group for adjustment.
397567 | CR | 20190801 |  | 4 | Reactor Iodine Dose Equivalent elevated trend | Y | N |  | N | NO | <D> **** Detailed Description **** The reactor sample for Iodine Dose Equivalent collected on 7/30/19 indicates an increasing trend over the last 3 samples. The most recent value is 2.8E-6 uCi/g which is up from a low value of 5.8E-7 uCi/g on 7/9/19. The Tech Spec limit is 2.0E-1 uCi/g. An increasing trend is one indication of degrading nuclear fuel health. Review of the other fuel health indicators did not show any negative trends. The offgas pretreatment monitor trend is steady and flat. The offgas isotopic analysis performed on 8/1/19 does not indicate any change from previous values. I recommend Category D/Trend. <I> **** Actions Taken **** Reviewed analytical parameters to verify correct results. Observed radiation monitor trends and reviewed the offgas isotopic results to determine if there is any indication of fuel leakage. Discussed with Fuels Engineering. Informed Chemistry supervision/management.
397570 | CR | 20190801 |  | 3 | (QA) Yellow catch containment used outside of the RCA | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) A yellow catch containment is in use outside of the RCA in the Flocculator building. During a Quality Auditor walkdown of the Flocculator building, a yellow catch containment (witches hat) was observed in use to collect and direct leakage from the Flocculator paddle wheel shaft. Use of yellow plastic products such as bags and containments are normally limited to use inside the RCA for contamination control, in accordance with GEN-RPP-04 Entry Into, Conduct In, and Exit from Radiologically Controlled Areas. Using yellow containment devices outside of the RCA can result in radioactive contamination outside of the RCA if the device was previously used. Refer to attached pictures in EDMS. Insight: Standard practice, as managed by the RMC Laborers, is to use green catch containments outside of the RCA to signify non-radiological contents. The Laborers maintain a store of catch containments, both yellow and green, in the Unitech supply trailer. The process is designed for a worker to request a catch containment from the Laborers who provide either yellow or green based upon the intended use location. Recommend assignment to RP. <I> **** Actions Taken **** Discussed this issue with the RMC laborer supervisor. Informed the Operations Shift Support Supervisor to replace the yellow catch containment with a green one. Initiated this CR.
397574 | CR | 20190801 |  | 4 | MS-V-736 has a 10dpm leak | N | N |  | N | YES | <D> **** Detailed Description **** Looking at camera TG/22, there is a 10dpm leak from MS-V -736 that dripping onto MS-V-737 and quickly evaporating. <I> **** Actions Taken **** Notified fluid leak manager. Leak appears to be from packing. <N> **** Equipment Description **** T -474- - -A8/6.4 - | 02-00-MS-V-736
397577 | CR | 20190801 |  | 3 | RFW-HX-6A and RFW-HX-6B indicated dP high | N | N |  | N | YES | <D> **** Detailed Description **** RFW-HX-6A and RFW-HX-6B differential pressures as indicated on RFW-DPI-3A(B) are above the maximum value of 19 psid specified in the CRO3 operating rounds. RFW-DPI-3A indicates 20.5 psid and RFW-DPI-3B indicates 20 psid. The RFW-HX-6A high d/P was previously documented by CR374477. WO 02135053 was performed to calibrate both RFW-DPT-3A and RFW-DPT-3B and finished on 8/1/19. Following calibration RFW-DPI-3A indication remained at the previous value of 20.5 psid. RFW-DPI-3B went from 18.5 psid (in spec) to 20 psid. This CR written to document the new out of spec reading. <I> **** Actions Taken **** Submitted CR and WR. Notified the Shift Manager. | 02-00-RFW-DPI-3A,02-00-RFW-DPI-3B
397578 | CR | 20190801 | CAQ | D | Low Pressure Alarm Received HCU 26-55 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-2655. Dispatched OPS-2 to investigate. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-2655 low pressure. OPS2 re-pressurized per SOP-CRD-HCU. <I> **** Actions Taken **** Notified CRS. OPS2 re-pressurized HCU <N> **** Equipment Description **** RB 522 | 02-00-CRD-HCU-2655
397579 | CR | 20190801 |  | 4 | NRC - LOCATE SOP-WARMWEATHER-OPS |  |  |  | N | NO | <D> **** Detailed Description **** NRC resident requests a copy of completed SOP-WARMWEATHER -OPS procedure. The crew checked the open procedures binder and the normal storage locations but were unable to locate it. <I> **** Actions Taken **** Notified shift manager <N> The procedure was found tonight and will be presented to the NRC for review. This procedure can remain open for extended period of time. The procedure can be in the MCR or with the operators performing the work.
397580 | CR | 20190801 |  | 4 | Plugged nozzles in TOA-HV-1A. | N | N |  | N | YES | <D> **** Detailed Description **** Approximately a third of the airwash spray nozzles in TOA-HV-1A are plugged. Most of the plugged nozzles are in the top half of the unit. <I> **** Actions Taken **** Initiated this CR. <N> **** Equipment Description **** 501' TB east side. | 02-00-TOA-HV-1A
397581 | CR | 20190801 |  | 4 | Thermostat for PSRO office broken | N | N |  | N | YES | <D> **** Detailed Description **** TIC-59, the thermostat for the PSRO/SSS office on the first floor of the GSB is broken. The thermostat is physically located behind the ice machine in the lunch room where it is subjected to hot compressor discharge from the ice machine. Even though it is subjected to this warm discharge, it is currently contolling temperature in the office at approximately 84F and cannot be adjusted due to it being broken. Request thermostat be replaced, preferably in a location that makes more sense. In the interim, recommend reinstallation of a temporary air conditioner in the PSRO/SSS office. <I> **** Actions Taken **** Notified SM. <N> **** Equipment Description **** TIC-59, located behind ice machine in GSB lunch room.
397582 | CR | 20190801 |  | 4 | GSB chill water temperature is high. | N | N |  | N | YES | <D> **** Detailed Description **** Per Ops 3 logs, GSB chill water temperature is supposed to be 40-60 degrres Fahrenheit but was found at 67 degrees. Ambient temp the day it was found was about 98 degrees but it still may need to be evaluated. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** 420' GSB NW corner. | 02-00-SCH-TI-3
397583 | CR | 20190801 |  | 4 | Plugge nozzles in TOA-HV-2B. | N | N |  | N | YES | <D> **** Detailed Description **** Over half of the bottom airwash spray nozzles in TOA-HV-2B are plugged. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** 501' TB west side. | 02-00-TOA-HV-2B
397584 | CR | 20190801 |  | 3 | Inconsistent with OI-41 application of CR COMM levels |  |  |  | N | NO | <D> **** Detailed Description **** This is general feedback for the assignment of CR COMM priorities in work order planning. There have been frequent cases when tasks that should have been CR COMM 2 or 3â€”such as scaffolding tasks or Clearance Order Hang or Lift tasksâ€”have been assigned CR COMM 1. Other SROs have anecdotally confirmed they have come across such cases and simply authorized the tasks to get through the EWP process. Conversely, there have been some cases when work that should have been classed as CR COMM 1 has not been. One example is WO 02146549. The HC and LC tasks (which were subsequently canceled) and the PMT task were classified as CR COMM 1 when CR COMM 3 would be appropriate. Performance of the -01 task, however, was classified CR COMM 3 when this is the task that renders an HCU Inoperable and requires entry into LCO 3.1.5. This should have been marked CR COMM 1 in accordance with OI-41.
397585 | CR | 20190801 |  | 4 | Steam Tunnel camera does not work. | N | N |  | N | YES | <D> **** Detailed Description **** The Steam Tunnel camera used for camera tours for Ops 3 rounds does not appear to be working. Unable to perform Steam Tunnel camera tour. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** Steam Tunnel camera
397586 | CR | 20190802 | CAQ | D | 0212208006 PMT WMA-AH-53B Sealant has 1/8â€™ hole leak | Y | Y |  | N | YES | <D> **** Detailed Description **** Sealant needs to be reapplied to stop leak. Suggest to apply when ventilation is off or get approval to make red rubber gasket for WMA-TT-53B probe than apply sealant on top. It is apparent that sealant blow out due to not having enough cure time to keep the seal from blowing out due to ventilation pressure. <I> **** Actions Taken **** write CR contact CRS and supervisor <N> **** Equipment Description **** WMA-AH-53B at probe penatration for WMA-TT-53B | 02-00-WMA-TT-53B
397587 | CR | 20190802 |  | 4 | Fitting for filter on E-TR-N2 for spray broken | N | N |  | N | YES | <D> **** Detailed Description **** The fitting that houses the filter for the transformer spray for E-TR-N2 was found leaking when lined up per SOP -WARMWEATHER-OPS. Attached a photo. <N> **** Equipment Description **** Connected to the spray line for E-TR-N2
397588 | CR | 20190802 |  | 3 | Procedure enhancement SOP-WARMWEATHER-OPS |  |  |  | N | NO | <D> **** Detailed Description **** Include an additional attachment of a one line diagram of the temporary cooling water systems for the ASD link reactors and normal transformers to assist with hand over hand walkdown to verify the system is properly installed. <I> **** Actions Taken **** Notified SM.
397606 | CR | 20190802 | CAQ | D | Found fire door W-DOOR-C214 not fully closed | N | Y |  | N | YES | <D> **** Detailed Description **** While on a walkdown of W467', it was observed in passing that fire door W-DOOR-C214 was not fully closed. See the photos attached to the EDMS of this AR CR 397606. The subject fire door was immediately closed and latched (SAT). Noted exitsing Barrier Impairments 18-0446 (WR 29145141 / AR CR 385752) and 19-0294 (WR 29150076 / AR CR 395991). Until repaired, users of this fire door need to make sure they manually pull the door into the fully closed and latched position. <I> **** Actions Taken **** As stated in the AR CR Detailed Description. The fire door was returned to the fully closed and latched position. | 02-00-W-DOOR-C214
397607 | CR | 20190802 |  | 4 | PP 60 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** PP 60 needs maintenance. The outer cover of the box needs to be attached using a different method. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Security notification made, CR/WR generated <N> **** Equipment Description **** PP 60 441 GSB in HP office
397608 | CR | 20190802 | CAQ | D | E-TR-7A/2 degraded | Y | N |  | N | YES | <D> **** Detailed Description **** On 8/1/19, measurements were taken under WR 29150791 on E -TR-7A/2 which supplies 240 VAC to loads on E-PP-7AF. The supply side of on Phase to Ground measurements are as follows: A-G: 123.79 VAC and B-G is 124.21 VAC. On the load side, at E-PP-7AF, A-G: 118.83 VAC and B-G: 118.55 VAC. Upon discussions with Systems Engineer, he feels the transformer is degraded and requires replacement at next FO/R25 opportunity. Additional Troubleshooting can be considered but at Risk. email sent on 8/2/19 attached to edms. Parts are shown in BOM. Recommend inspection and staging of parts. <I> **** Actions Taken **** Notified Engineering Leadership and SM <N> This is being crossed referenced to CR 397437. | 02-00-E-TR-7A/2
397609 | CR | 20190802 |  | 3 | NRC Walkdown identified housekeeping and WIP issues | N | N |  | N | NO | <D> **** Detailed Description **** The NRC resident walked down the reactor building and identified the following issues. The WIP signs should be corrected for work in progress, and items should be removed for work that is finished. 522 â€“ SW corner â€“ scaffold table with no WIP 572 â€“ SE corner â€“ WIP 02110908 due in July, Owner I&C Craft/Maint. Supervisor. WO completion date is 8/12/19 with I&C Craft/Maint. Supervisor as owner. Update sign for date and owner. 572 â€“ by SGT â€“ WIP 02115569-79 - due 8/1/19, Owner Supervisor â€“ Williams Plant Services. WO is at finished. Remove cart. 548 â€“ NW Corner â€“ WIP 02073390 due in May, Owner I&C Craft/Maint. Supervisor. WO is at finished. Remove cart. 548 â€“ Cart with illegible WIP. 471 â€“ SE corner â€“ Scaffold Cart, no WIP sign. <I> **** Actions Taken **** Emailed owners that could be identified to update and/or remove their inprogress work. <N> Williams Plant Services owns WO 02115569-79. All other items are shop owners. Removed names from CR per SWP-CAP-01 Issues with WO-02115569-79 have been corrected.
397610 | CR | 20190802 |  | 4 | NRC â€“ E-BU-R422/6 Unit Failure | N | N |  | N | YES | <D> **** Detailed Description **** While performing walk-through the NRC resident identified E-BU-R422/6 Charging Status light is flashing red. Per PPM 10.25.156 this is indicative of unit failure. The service alert voltage light is also solid red, which is an indication of low battery capacity. <I> **** Actions Taken **** Shift Manager informed. CR initiated. This likely means the batteries for the unit need to be replaced. <N> **** Equipment Description **** HPCS pump room south wall, 10 feet up. FPSI 19-0171, Non-Essential lighting. | 02-00-E-BU-R422/6
397611 | CR | 20190802 |  | 4 | NRC â€“ E-BU-SWA5/3 Charger Fault | N | N |  | N | YES | <D> **** Detailed Description **** While performing walk-through the NRC resident identified E-BU-SWA5/3 Charger Fault light glowing red. Upon SSS walk-through, the light did not appear to be illuminated and the Operating Status light was green (normal). This unit could still be degraded and should be investigated further. This unit is located in RB North East Stairwell below 471â€™ elevation. <I> **** Actions Taken **** Shift Manager informed. CR initiated to request more in -depth investigation. <N> **** Equipment Description **** RB Northeast stairwell landing below 471 elevation FPSI 19-0172. Non-Essential Lighting. | 02-00-E-BU-SWA5/3
397612 | CR | 20190802 | CAQ | D | Rod Accumulator Trouble Alarm for CRD-HCU-1419. | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-1419 was low pressure. OPS2 re-pressurized per SOP -CRD-HCU. trend only | 02-00-CRD-HCU-1419
397613 | CR | 20190802 |  | 4 | E-BU-SWA5/2 has a battery fault | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-SWA5/2 has a battery fault light blinking <I> **** Actions Taken **** CRS/SM informed. FPSI 19-0172 opened and portable lantern staged. <N> Non-essential lighting. FPSI 19-0173. | 02-00-E-BU-SWA5/2
397614 | CR | 20190802 | CAQ | D | Received alarm 4.851.S2 Rx Bldg Stack General Trouble. | N | Y |  | N | YES | <D> **** Detailed Description **** Received alarm 4.851.S2 Rx Bldg Stack General Trouble. The source of the alarm as indicated on PRM-RIS-1 event screen is ID # 56007 C/S test for PAP1 SDG-04-fail. Alarm is dated Aug 02 2019 0457:25. | 02-00-PRM-RIS-1
397620 | CR | 20190803 | CAQ | C | Loss of TDAS. | Y | Y |  | N | YES | <D> **** Detailed Description **** Power light on TDAS-COMP-8715 is out. Lost data on TDAS computers. PPC is previously unavailable. <I> **** Actions Taken **** Entered ABN-COMPUTER. | 02-00-TDAS-COMP-8715
397621 | CR | 20190803 |  | 3 | WO 02109631 missing task for mechanics |  |  |  | N | NO | <D> **** Detailed Description **** WO 02109631 for recovery from cold weather ops and entry into warm weather ops has no separate task for mechanics to install supplemental cooling to the condensate booster pump motors per step 6.2.7 of SOP-WARMWEATHER-OPS <I> **** Actions Taken **** Informed the MCR and generated a WR to have the mechanics preform section 6.2.7 of SOP-WARMWERATHER-OPS. <N> **** Equipment Description **** SOP-WARMWEATHER-OPS
397622 | CR | 20190803 | CAQ | D | HCU 26-55 P6 connector has small N2 leak | Y | N |  | N | YES | <D> **** Detailed Description **** The P6 threaded fitting on the cartridge valve, CRD-V-111/2655, has a small N2 leak that needs repaired. This evententually leaks enough N2 for the accumulator to cause an alarm in the main control room. | 02-00-CRD-HCU-2655
397623 | CR | 20190803 |  | 4 | RECIRC B SYSTEM VIBRATION HIGH (H13-P602-A6 drop 2-8) is in |  |  |  | N | YES | <D> **** Detailed Description **** RECIRC B SYSTEM VIBRATION HIGH (H13-P602-A6 drop 2-8) is in alarm due to RRC-VBI-P1B/XE (Pump Thrust) spiking to 47 mils. This is the Alert level alarm on channel A. Channel B does not work. <I> **** Actions Taken **** Monitoring via remote camera <N> This CR is being trended to CR 397543 | 02-00-RRC-VMP-1
397624 | CR | 20190803 |  | 4 | Rad Waste control room issues and t-2 barrel concern | N | N |  | N | YES | <D> **** Detailed Description **** This CR is to document several current issues with rad waste processing equipment and recommend cleaning T-2. 1. T2 sump Hi Hi alarm currently in. OPS3 has temp log to check t-2 level, Laborers are pumping the sump to barrels due to HIGH TOCs. Chemistry check TOC 8/3/19 are 34.5 PPM vs. the limit of 200 PPB. Currently we are pumping this to barrels which is disposal of mixed waste, recommend on cleaning T-2 to see if it lowers TOCs to a value radwaste can process. 2. T1 sump blown fuses, pumping into T7 sump. AR 396788, WR 29150489 3. T4 sump blown fuses on P15A, P15B is available. AR 396124, WR 29150170 4. T7 sump, pumps will occasionally stay running. Cautions tags on P18A and P18B. P18B in PTL, seems to help to keep auctioneering ckt from cycling. . AR 396202 WR 29150225. | 02-00-FD-SUMP-T2
397625 | CR | 20190803 | CAQ | C | Unable to reset/restore MONCR2 following TDAS blown fuse | Y | N |  | N | YES | <D> Following the blown fuse on TDAS during the restoration, we were unable to restore the PPC-CPU-3DM computer. The TDAS-CPU-3DM computer is working, so there is still input for the 3D MONCORE system. <I> Verified 3D MONCORE functioning normally using MONCR1 from TDAS-CPU-3DM. Performed TSP-THERM-C101 to verify no thermal limits were exceeded. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review. | 02-00-PPC-CPU-3DM
397626 | CR | 20190803 |  | 3 | ALARA Cast Not Transmitting Data | N | N |  | N | NO | <D> **** Detailed Description **** In the past week ALARA Cast has been having issues with transmitting certain Electroinic Dosimeters or AMPs that have been placed in the field to monitor dose rates throughout the plant. Multiple EDs have been lost and tonight all but 1 device has been lost. This system is used as a compensatory measure when the plant ARMs are out of service. Currently RIS-33 is the only plant installed ARM that is out and has a transmitting device in place as a comp measure to monitor dose rates in that area. The ED that was in place to monitor dose rates at RIS-33 was lost. CRS said that HP would need to do hourly tours of the area to minitor dose rates for the lost Comp measure. Dose rates at RIS-33 were checked by HP and found to be 0.1 mrem/hr. The only ARM that is working and transmitting was moved to RIS-33 to fulfill the needed comp measure. <I> **** Actions Taken **** Notified CRS, Notified HP Supervision, Notified IS, Checked Dose Rates at RIS-33, Install only functioning transmitting ARM at RIS-33 location. Initiated this CR
397635 | CR | 20190804 |  | 4 | Security CCTV's | N | N |  | N | YES | <D> **** Detailed Description **** Security requesting electrical support for CCTV scheduled upkeep. Please contact security @ 2185 <I> **** Actions Taken **** CR/WR generated | 02-00-SEC-CCTV-XXXXXXXX
397636 | CR | 20190804 |  | 3 | SCW tank pressure below operating band | N | N |  | N | YES | <D> **** Detailed Description **** SCW H2 pressure was low at 0.8 psig, operating band is 2 to 5.5 psig. Previous CR 395989, WR 29150073 had same issue with low pressure and was corrected on 7/31 per WR and closed. Based on eSOMS OPS3 logs, SCW pressure was SAT for 2 shifts and subsequently back to below operating band following closure of WR. This new AR/WR is for trending and possibly addressing issue of SCW pressure leak. Potential issue could be SCW-RV-454 not maintaining adequate pressure (or a leak in the system). I reviewed eSOMS trend on SCW H2 Vent meter and noted usage for past 7 days at 110 to 120, and for comparison I reviewed a 7 day trend in March 2019 trending about 120 to 130 range. I raised H2 pressure in SCW per SOP-SCW-OPS step 5.15.2 to 4 psig at 1050 on 8/4. I snooped the fittings on SCW-RV-454, SAT results. I will update OPS3 turnover sheet to continue monitoring SCW pressure. <I> **** Actions Taken **** MCR staff informed. Raised pressure per SOP-SCW-OPS. CR/WR written. | 02-00-SCW-PI-457,02-00-SCW-RV-454
397637 | CR | 20190804 | CAQ | D | SST high level alarms frequently | N | N |  | N | YES | <C> CR reopened to cross reference additional WR 29146166, marked completion required box, then taken back to complete <D> **** Detailed Description **** Continuing to receive SST A and B high level alarms frequently. Appears the switch that closes the make up valve needs calibrated (closing sooner / lower level would prevent alarms) After receipt of the FPC A panel high level alarm the make up valve is often noted to be intermediate and the FPC panel B high level alarm comes in. FPC-LIS-2A and or 2B control COND-SPV-42 to control SST level. This has been an issue for almost a year at this point and no action has been taken yet. <N> Skimmer Suge Tank (SST) | 02-00-FPC-LIS-2A,02-00-FPC-LIS-2B
397638 | CR | 20190804 |  | 4 | FDR-RMS-V/166 control switch getting harder to operate | N | N |  | N | YES | <D> **** Detailed Description **** The control switch for FDR-V-166 is getting harder to operate and should be replaced at the earliest convience. This valve is used all the time to process fdr water through the filter. | 02-00-FDR-RMS-V/166
397639 | CR | 20190804 |  | 3 | OOS log reading for DG fuel oil not corrected |  |  |  | N | NO | <D> **** Detailed Description **** The out of spec log reading for total volume of DG fuel available was not identified as being correctable after the caution tag was lifted from DO-V-64 on 07/31/2019. Several Operations Crews missed the oppertunity to identify the low fuel oil level and correct the issue <I> **** Actions Taken **** Informed the Shift Mananger Fuel oil transferred on day shift 8/4. <N> Email sent to all crew managers and supervisors to emphasize that the behaviors demonstrated resulted in poor turnover between crews. While this did not result in a TS low oil level issue, we were unnecessarily below 3.1.10 oil levels after the fuel in FO-TK-1 was acceptable for transfer.
397640 | CR | 20190805 | CAQ | C | WW/DW Vacuum breaker (1CD) Failed surveillance | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of OSP-CVB/IST-M701 on 8/5/19, the Rear Disc on CVB-V-1CD failed to indicate fully open. With CRS permission multiple attempts to open the valve were taken, and new light bulbs were installed, but the "Fully Open" light did not illuminate. <I> **** Actions Taken **** Informed CRS/SM <N> T19-CVB-V-1QR-001. | 02-00-CVB-V-1CD
397641 | CR | 20190805 | CAQ | C | WW/DW Vacuum Breaker (1QR) failed to open | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of OSP-CVB/IST-M701 on 8/5/19, CVB -V-1QR Rear disc failed to open. When the control switch was taken to open, the valve continued to indicate closed. With CRS permission, multiple attempts of variing length were performed, with no change. <I> **** Actions Taken **** Informed CRS/SM <N> T19-CVB-V-1QR-001 | 02-00-CVB-V-1QR
397642 | CR | 20190805 |  | 4 | Security Communication Center UPS Power | N | N |  | N | YES | <D> **** Detailed Description **** UPS Power for Security Communication Center equipment requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security supervision notified. Restored power to essential equipement. Performed walk downs of affected areas. Initiate CR/WR. <N> **** Equipment Description **** SCC UPS Power supply located in the Security Communication Center Does this item have an EPN or an associated EPN?
397645 | CR | 20190805 |  | 4 | MCR small CT printer failed | N | N |  | N | YES | <D> **** Detailed Description **** MCR small CT printer indicates ribbon out and media out with both components stocked in machine. Previously this has been a sensor issue. Small CTs will be written by hand as this unit does not function. <N> **** Equipment Description **** MCR zebra zt510 small ct printer
397647 | CR | 20190805 |  | 2 | Safety First - Station Focus Area - Progress Unacceptable |  |  |  | N | NO | <C> CR Changed from sev 3 to sev 2 and Owed to Group changed from AR-PERFIMP to AR-MMGR by MRT <D> **** Detailed Description **** The Safety First Station Focus Area progress to date is unacceptable. There have been 3 recordable injuries, 1 lost time accident and 3 level 2 clearance order errors in 2019 (see X-REF and EDMS for injury log). . Need an aggregate review of the injuries and first aid events to look for common themes. Ops is already doing an aggregate review of the recent level 2 clearance order errors (see X-REF). . Need new action plan developed to improve Safety performance on site.
397648 | CR | 20190805 |  | 4 | Chemistry dose budget exceeded for July 2019 |  |  |  | N | NO | <D> **** Detailed Description **** The Chemistry dose budget was exceeded for July 2019. The does estimate was 161 mR with a goal of 145 mR. The Chemistry department received 180 mR. The extra dose can be attributed to higher dose rates in the hot sample sink following R24 and the extra sampling required due to loss of HWC twice during the month of July.
397649 | CR | 20190805 |  | 4 | 10 Pieces of M&TE Suspended until R25 |  |  |  | N | NO | <D> **** Detailed Description **** 10 Pieces of M&TE were NOT used during Calibration cycles and have been Suspended until R25. See EDMS for Calcodes, Descriptions, Models and associated DEF numbers. No Action Required. <I> **** Actions Taken **** None Trending purposes only
397650 | CR | 20190805 |  | 4 | COND-V-260A,B,C,E & F need MWO update. |  |  |  | N | NO | <D> **** Detailed Description **** The Model Work Orders for EPN's COND-V-260A,B,C,E and F need to be revised to include (qty 2) CID 27608 (2" CGI gasket) on the MR and the associated Limits on Use incorporated into the work instructions. This revision should also include any work orders generated from the MWO's that have not yet been worked. <I> **** Actions Taken **** wrote this CR <N> All model WOs have been updated by planning to include CGI gaskets, and Limitations on Use have been added to the instructions. Additionally, future PM WOs 02131976 and 02130565 have been updated.
397653 | CR | 20190805 | CAQ | C | TDAS computer power loss (PPC OOS) | Y | Y |  | N | YES | <D> **** Detailed Description **** lost TDAS computer inputs and noted TDAS computer power lamp off. Suspect cleared fuse. | 02-00-TDAS-COMP-8715
397655 | CR | 20190805 |  | 3 | 10.25.85 needs editorial change |  |  |  | N | NO | <D> **** Detailed Description **** On Attachment 9.2 the EPN CVB-RMS-V/1ST/FRONT (CVB-RMS -V/1AB/REAR) needs to be removed on step 1.0, 4.0 and 7.0 <I> **** Actions Taken **** Informed procedure writer and initiated CR <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
397661 | CR | 20190805 |  | 3 | PPM 12.1.1 enhancement to save dose |  |  |  | N | NO | <D> **** Detailed Description **** Attachment 15.2 has conductivity cell calibration cross checks at a frequency of following calibration and weekly when in instrument is in service. Review of the Power Plant Analytical Chemistry Guidelines stats that a frequency of following calibration and monthly is all that is required. if 12.1.1 is changed to reflect this requirement it would save a considerable amount of dose for the chemistry shift technicians every month. <I> **** Actions Taken **** Informed Chemistry Specialists and wrote CR to document need for procedure enhancement.
397662 | CR | 20190805 |  | 3 | Missing quorum member at PCSC/Risk Committee meeting |  |  |  | N | NO | <D> **** Detailed Description **** Missing Maintenance department craft quorum member at PCSC/Risk Committee meeting. Only one Maint craft from any shop is required for meeting (PPM 1.3.81). Adaquate notice was delivered to shops/supervisors. <I> **** Actions Taken **** CR initiated.
397666 | CR | 20190805 | CAQ | C | TDAS and PPC computers blowing fuses | Y | Y |  | N | YES | <D> **** Detailed Description **** TDAS-COMP-8715 and PPC-COMP-8715 have recently blown fuses The vendor manual calls for 250V 15A slow blow fuses. the Currently installed fuses are 125V 15A fast blow fuses. <I> **** Actions Taken **** discussed with vendor who agreed that we should put the slow blow fuses in, he also recommended that we remove the unused SBC2 cards which draw ~15amps and their associated hard drives. See 00397653 for same issue and IOD. | 02-00-PPC-COMP-8715,02-00-TDAS-COMP-8715
397667 | CR | 20190805 |  | 3 | Enhancement to WO 02116602, DSA-AR-1A press switch cal |  |  |  | N | YES | <D> **** Detailed Description **** Enhancement to WO 02116602 DSA-AR-1A pressure switches calibration. This is to ensure a more conservative approach to maintain compressors in service. First; enhance step 4.2. Add, â€œ Record position of DSA-RMS -C1A/S46 (circle one) Lead 1A1 or Lead 1A2â€ then correct current step to place switch in Lead 1A2 position, ie change Lead 1A1 to Lead 1A2. I would suggest making current step 4.2 into 4.2.a so sequencing is maintained. Second, enhance step 4.28 which currently reads â€œREQUEST Operations place DSA-RMS-C1A/S46 in the Lead position as desired at E-CP-DG/RP1â€. Change to â€œRequest Operations place DSA-RMS-C1A/S46 to position recorded in step 4.2 or as desired at E-CP-DG/RP1â€ Please evaluate for correctness, availability and conservatism. <I> **** Actions Taken **** Informed I&C techs at job site <N> **** Equipment Description **** WO 02116602
397669 | CR | 20190805 |  | 4 | Turbine side seal oil LOOS | N | N |  | N | YES | <D> **** Detailed Description **** Turbine side seal oil and H2 D/p occasionally LOOS. Calculated reading <I> **** Actions Taken **** Informed MCR. Initiated CR | 02-00-SO-PI-201
397670 | CR | 20190805 |  | 4 | Cenerator Condition Monitor | N | N |  | N | YES | <D> **** Detailed Description **** Generator Condition Monitor Chart Paper needs to be replaced. <I> **** Actions Taken **** Initiated CR. Informed MCR | 02-00-TG-ID-1
397671 | CR | 20190805 |  | 4 | Operations Dose budget exceeded for July 2019 |  |  |  | N | NO | <D> **** Detailed Description **** Operations department dose budget for July 2019 was exceeded. Dose estimate was 225 mrem and the department received 272 mrem. Contributors were inspection of RWCU-DM-1B due to emergent issue, oil cleanup of Reactor Feed Turbines, clearance order activities for D-EDR-V-42 -001 and D-EDR-V-150A-001, and multiple HCU trouble alarm responses. <I> **** Actions Taken **** Submitted CR per GEN-RPP-16.
397672 | CR | 20190805 | CAQ | D | DSA-PS-1A, 5A, 6A found OOT | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During DSA-AR-1A pressure switch calibrations, DSA-PS-1A, 5A, and 6A were found OOT. Calibrated per 10.24.28 to within IMDS tolerances. <I> **** Actions Taken **** Contacted supervision, operations, calibrated per 10.24.28 <N> **** Equipment Description **** DG 1
397673 | CR | 20190805 |  | 3 | oil leak on spared transformer | N | N |  | N | YES | <D> **** Detailed Description **** there is an approx 20 dpm oil leak on the northern-most spare tranformer in the NW corner of the switch yard by the BRE. the leak is on a 4" pipe elbow/bolted flange on the SW corner of the transformer. it is leaking onto the rocks and has formed approx 30 ft2 discolored area in the rocks due to wind drift. <I> **** Actions Taken **** informed MCR informed E&RP placed pig mats under active drip point to prevent further ground contact <N> **** Equipment Description **** northern most spare transformer-nw corner of transformer ya rd E&RP contacted and confirmed with GPB-ENV-18 that the estimated quantitiy of oil leaked to the ground is not reportable. Containment established. As of 8/6/2019 (8am), E&RP is still gathering information to estimate the amount of oil that spilled and to assess reportability to regulatory agencies. E&RP has finished evaluating the spill and has estimated spill volume is less than 5 gallons. This spill is not reportable to offsite agencies
397674 | CR | 20190805 | CAQ | D | 4.800.C4 OSCILLOGRAPH STARTED. | N | N |  | N | NO | <D> **** Detailed Description **** Startup and Backup voltages are as follows: E-TR-S A: 239 B: 238 C: 241 E-TR-B A: 120 B: 119 C: 119 The following sensors were tripped and are reset: J15. BPA reports the following: a. Cause was 230KV fault at McNary b. Relaying involved is unknown. c. N/A d. Line did not auto reclose. e. Unknown if emergent outage needed. f. 230kv involved g. No h. N/A i. 1723 k. No RAS
397675 | CR | 20190805 | CAQ | D | LEFM has a minor alert - still in check plus | N | Y |  | N | YES | <D> **** Detailed Description **** LEFM status shows a minor alert but is still in check plus mode (no LCS 1.3.9 entry). Meter 2 state for plane A and B show an unknown status while Meter 1 shows a normal check plus status. Investigate and repair/ <I> **** Actions Taken **** CR and WR. | 02-00-RFW-CPU-CPU2,02-00-RFW-FT-XMT2A
397676 | CR | 20190805 | CAQ | C | DW Annulus Temp Exceeded 150F Alert Limit | Y | Y |  | N | NO | <D> **** Detailed Description **** DW annulus temperature was calculated to be 150.2F, exceeding 150F Alert limit of LCS 1.7.1. CR required for condition A.2. <I> **** Actions Taken **** RO 1 has a 4 hour temp log for calculate annulus temp, new alert limit is 155F. <N> This is separate event from CR 397509.
397677 | CR | 20190805 |  | 4 | RB SW Elevator Fan Not Running | N | N |  | N | YES | <D> **** Detailed Description **** The fan for the RB SW Elevator is not running. Elevator cabin conditions are humid at best, bording on downright floridian. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** Reactor Building SW Elevator
397678 | CR | 20190805 | CAQ | D | Received 4.603.A7 Rod Accumulator Trouble for HCU 2655. | Y | N |  | N | YES | <D> **** Detailed Description **** Received 4.603.A7 Rod Accumulator Trouble for HCU 2655. Alarm due to accumulator low N2 pressure. Recharged. <I> **** Actions Taken **** Recharged Accumulator. Alarm cleared. | 02-00-CRD-HCU-2655
397679 | CR | 20190806 | CAQ | D | IDS 09 needs maintenance | N | Y |  | N | YES | <D> **** Detailed Description **** IDS 09 is not functioning as designed. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Comp in place, security notification made, CR/WR generated | 02-00-SEC-IDS-E/S/9/10
397680 | CR | 20190806 |  | 4 | CAS sink needs maintenance |  |  |  | N | YES | <D> **** Detailed Description **** The sink in CAS needs maintenance. It appears to be clogged. <I> **** Actions Taken **** CR/WR generated <N> **** Equipment Description **** Sink in CAS bathroom
397681 | CR | 20190806 |  | 4 | COND-V-242B has no open indication | N | N |  | N | YES | <D> **** Detailed Description **** During performance of SOP-CFD-DRAIN for COND-DM-1B maintenance, the open indication light for COND-V-242B on COND-CP-DM/1 did not illuminate. Bulb was checked and valve position was locally verified. Could be an issue with the socket or limit switches on the valve. Closed light did go out. <I> **** Actions Taken **** Verified local position of valve. | 02-00-COND-V-242B
397682 | CR | 20190806 |  | 4 | XD6 Needs Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** XD6 Needs Maintenance <I> **** Actions Taken **** Tagged out of service, CR/WR, Security Supervision Notified | 02-00-SEC-XD-6
397685 | CR | 20190806 |  | 3 | LL from recent evacuation of Kootenai Building |  |  |  | N | NO | <D> **** Detailed Description **** When the Kootenai was evacuated on 07/31/19, emergency zone coordinators fulfilled their responsibilities to sweep the building and monitor entrances. The Facility Emergency Director (FED) and backup were not present. Some FEDs and zone coordinators listed with Emergency Preparedness as filling the positions were out-of-date. Process enhancements for tracking position responsibilities should be explored. Communication gaps also occurred and at one point the crowd attempted to reenter the building prior to an official announcement from an FED or Fire Marshall that it was safe to do so. Finally, a â€œhot washâ€ or debrief did not occur following the event. <I> **** Actions Taken **** Provided feedback to EP. Initiated CR.
397686 | CR | 20190806 | CAQ | C | MT&E Found out of Tolerance | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0059896 Hipotronics AC HIPOT Tester- model 60HVT-A found OOT & adjusted within specs. EFIN to evaluate 8 usages. DEF #7135A written and will be attached EDMS when complete.
397690 | CR | 20190806 |  | 3 | Seal Oil procedure enhancements |  |  |  | N | NO | <D> **** Detailed Description **** Seal Oil procedures SOP-SO-OPS and SOP-SO-START should be revised to provide an acceptable and consistent band for air side seal oil operation. All procedures should recommend adjusting seal oil differential pressure to 11 - 15 psid. This band allows for daily variations in differential pressure as generator pressure changes and also allows for the difference between both ends of the generator. The operator rounds should also be updated with the same values to minimize concern with out of spec readings and unnecessary adjustments to the system. <I> **** Actions Taken **** Discussed with FIN and OPS, initiated CR to update procedures.
397697 | CR | 20190806 |  | 4 | 2 Pieces M&TE Suspended/ Lost |  |  |  | N | NO | <D> **** Detailed Description **** 2 Pieces of M&TE Can't be located and are Suspended as lost. Both were checked out by I/C for LLRT work for R25. No Activity in Poral J for any usage. Calcode #0068337 Heise Gauge CM200psig. DEF #7136A written. Calcode #0065557 Ashcroft Sensor- model HQS-2 30inhgvac. DEF #7137A written No Action Required. <I> **** Actions Taken **** None Trending purposes
397698 | CR | 20190806 |  | 4 | PSR-IX-3 is Showing Elevated Dose Rates |  |  |  | N | YES | <D> **** Detailed Description **** During a trending dose review of PSR-IX-2 under PM WO 02116627 Noted dose rates on PSR-SR-3 have increased significnatly from 8 mrem/hr contact and 2 mrem/hr at 30cms to 80 mrem/hr contact and 10 mrem/hr. Recommend the IX Column be changed out. Last WO to change the IX Column was WO 02130034 <I> **** Actions Taken **** Informed supervisor | 02-00-PSR-IX-3
397701 | CR | 20190806 |  | 4 | DBAI 2019 (NRC Identified) House Keeping Mini Lamps |  |  |  | N | NO | <D> **** Detailed Description **** NRC inspector identified a box of miniature lamp bulbs were stored on one of the supports behind E-PNL-IN/2. These lamps should not be stored here. This is a house keeping issue. <I> **** Actions Taken **** Removed the box and initiated CR
397702 | CR | 20190806 |  | 4 | DBAI 2019 (NRC Identified) house keeping strings on conduit |  |  |  | N | NO | <D> **** Detailed Description **** NRC inspector identified yellow string on conduit above E -PP-8A. This is a house keeping issue. String should be removed.
397703 | CR | 20190806 | CAQ | C | Firmware update for Seismic System |  |  |  | N | YES | <D> **** Detailed Description **** Communication was received from the manufacturer of the newly installed Seismic system recommending a firmware update for the MR2002-SM24-K Seismic Strong Motion Recorders. . An issue with the time stamp on the products MR2002-SM24-K with the firmware version up to V2.0.5 was detected. (Columbia has firmware version V2.05.) The problem will occur when the date will change from the 31.12.2019 to 01.01.2020 with the year being not properly incremented. The date will be set at 01.01.2000 instead of 01.01.2020. This DOES NOT affect the Design Function of the equipment to detect an earthquake and activate the relays in case of alarm threshold exceedance. . A new firmware is available to correct the issue. Additional questions were sent to the manufacturer and we are awaiting their response before initiating an AR-EVAL. See EDMS for the manufacturerâ€™s communication. <I> **** Actions Taken **** Discussed with Design Engineering and Supervisor | 02-00-SEIS-SMA-1A,02-00-SEIS-SMA-1B,02-00-SEIS-SMA-1C,02-00-SEIS-SMA-2A,02-00-SEIS-SMA-2B,02-00-SEIS-SMA-3
397704 | CR | 20190806 |  | 3 | PPM 16.11.6 needs enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Step 7.2.4 States to Notify the MCR before manipulating PRM-SR-2 valves. This step and the note above it would be more benficial as the first step in Section 7.2 <I> **** Actions Taken **** Informed Chemistry Specialist. Wrote CR
397705 | CR | 20190806 |  | 3 | DBAI 2019- PPM 10.2.53 step 7.4.3 q (last bullet) has a typo |  |  |  | N | NO | <C> CR Re-opened to update title to DBAI 2019. Completed. <D> **** Detailed Description **** The last bullet of PPM 10.2.53 step 7.4.3 q has a typographical error that should be corrected. "QC-1 equipment excluding equipment bases (per p. above)." should be corrected to read "QC-1 equipment excluding equipment bases (per r. below)." See the mark-up of PPM 10.2.53 revision 46 page 19 or 35 attached to the EDMS of this AR CR 397705. Suggest resolution assignment to Maintenance Procedures. . This PPM 10.2.53 typo was noted in passing while investigating 2019 DBAI Communication Form #034. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
397706 | CR | 20190806 |  | 4 | SCH-CR-51 system 1 compressor tripped off. | N | N |  | N | YES | <D> **** Detailed Description **** SCH-CR-51 system 1 compressor was found off, having tripped on high current. Both oil sightglasses were full, so need to remove some oil prior to restarting for investigation. <N> **** Equipment Description **** SB basement | 02-00-SCH-CR-51
397707 | CR | 20190806 |  | 3 | Procedure enhancement for PPM 16.1.11 Stack Monitor CC/RC |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of PPM 16.1.11 it was discovered that there are multiple places where enhancements to the procedure would help clarify the work instructions. This is a new surveillance that is infrequently performed. <I> **** Actions Taken **** Stopped and expanded the team when unsure or if clarification was needed. Initiated a CR/WR to ensure the procedure gets enhanced. <N> **** Equipment Description **** PRM-SR-1 RW 507'
397710 | CR | 20190806 |  | 4 | 12 Pieces of M&TE Suspended until R25 |  |  |  | N | NO | <D> **** Detailed Description **** 12 Crimpers that were NOT used during Calibration cycles have been Suspended until R25. See list for Calcodes, Descriptions, Models and associated DEF #'s. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
397711 | CR | 20190806 |  | 4 | M2 Cooler Group 2 Conduit Support needs re-installed. | N | N |  | N | YES | <D> **** Detailed Description **** During a walkdown of Transformers with E&RP, conduit support hardware was found located on the concrete pad of M2 near cooler group 2. See the EDMS for pictures. It appears to be left over from investigation activities of the loss of M2 cooler group 2 pump 2. Recommend the re -installation of the conduit support. - Also located one bolt on the M2 transformer pad near cooler group 4. Looked around and above and did not identify a location missing a bolt or if it was left over from R24. Recommend another review of the area for any missing bolts. <I> **** Actions Taken **** Contacted System Engineer. FIN and Supervision. | 02-00-E-TR-M2
397716 | CR | 20190806 |  | 4 | Degraded conduit on CP-TB-ANODES/DW3 | N | N |  | N | NO | <D> **** Detailed Description **** While performing work under WO 0213-0048-01, concrete pad replacement, it was discovered that the conduits that run up through the pad into the Anode Panel are very degraded. One of the conduits has a large hole rusted through it, another conduit was broken and the rest are very rusted, see photos in EDMS. <I> **** Actions Taken **** Contacted supervisor, WWM and planner to resolve. Initiated CR.
397717 | CR | 20190806 |  | 3 | DBAI 2019 Enhancemen needed to ABN-CONT-VENT |  |  |  | N | NO | <D> **** Detailed Description **** ABN-CONT-VENT directs venting the WW/DW during a loss of AC and DC power. Step 4.1.3.g directs closing SGT-V-2A and step 4.1.3.h directs closing SGT-V-2B to lineup the system for venting, however both of these steps should be conditional to allow the use of just 1 train. Performing both steps prior to venting is not required and would delay venting efforts. Step 4.2.4.g and 4.2.4.h have the same issue when venting the DW. Pages 6, 7, 9, and 10 have been highlighted with the proposed changes. See EDMS for proposed document. <I> **** Actions Taken **** CR initiated
397718 | CR | 20190806 |  | 4 | S-DOOR-S103 fire door is missing screws on kick-plate | N | N |  | N | YES | <D> **** Detailed Description **** S-DOOR-S103 fire door kick-plate is missing some screws; replace screws as necessary ore with rivits if that is acceptable for a fire rated door. Screws are always missing on this door possibly due to it is used quite frequently. | 02-00-S-DOOR-S103
397720 | CR | 20190806 | CAQ | D | D-105 Door Lock Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** After taking Diesel #1 logs, I placed my badge gainst the badge reader in order to exit the room, the door popped open due to the differential pressure between the corridor and the Diesel Room however I did not hear a beep, i did not get a green/red light from the card reader and the blue light was not flashing. I proceeded to close the door and re-badge and everything seemed to work fine after that. <I> **** Actions Taken **** CR/WR generated Supervision Notified Security Notified This issue does not impact the barier function of the door but is a security lock issue. <N> **** Equipment Description **** Door D-105 (entrance and exit to DG1 from RCA)
397721 | CR | 20190806 |  | 3 | Stop Work Initiated, RW 437' Resin Process Area |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** While attempting to lift a high dose rate resin liner, located behind the shielded rad waste processing area. The remote grapple did not fully engage the lifting ring correctly and became stuck. <I> **** Actions Taken **** The team recognized the need to stop work. Two Craft Supervisors were in the field observing the work. The hoist for the crane connected to the grapple was verified to have its power shut down and locked. The area was down posted from a Locked High Radiation Area and the Radiation Protection Manager was notifed. See photo in EDMS.
397722 | CR | 20190806 |  | 3 | Portacount As-Found calibration out of Tolerance | N | N |  | N | NO | <D> **** Detailed Description **** The Portacount model 8030, serial number 8030123705, asset number 65943, was recently calibrated. The Calibration Report was received, but the as-found instrument readings were out of tolerance. See attachment in EDMS Docs. The instrument was reading 19% - 30% higher than the test standard, and this instrument was in use from 1/24/19 to 5/9/19. <I> **** Actions Taken **** Discussed with RP supervision. A review of the fit test results obtained from the above mentioned instrument for the on shift personnel for the next 2 days, showed that no results were within 30% of the pass limit.
397724 | CR | 20190806 | CAQ | C | High drywell temperature | Y | Y |  | N | NO | <D> **** Detailed Description **** DW annulus temperature was calculated to be 150F, exceeding 150F Alert limit of LCS 1.7.1. CR required for condition A.2. Actions Taken RO 1 has a 4 hour temp log for calculate annulus temp, new alert limit is 155F. This is separate event from 8/5/19 <N> The issue of average DW annulus exceeding 150F is a continuing issue that began on 07/31/19 (00397509), and subsequently on 08/05/19 (00397676). This CR and all subsequent CR's for this summer should be trended to either 397509 or 397676. --MJ Holle 08/07/19
397725 | CR | 20190806 |  | 4 | CR 397611 has incorrect EPN | N | N |  | N | NO | <D> **** Detailed Description **** The NRC identified that CR 397611 had identified the incorrect EPN. The EPN should have been E-BU-SWA5/5. <N> WR and FSPI? AR CR 397611 WR 29150817 indicates EPN E-BU-SWA5/3 and indicates that FPSI 19-0172 was for EPN E-BU-SWA5/3.
397727 | CR | 20190806 |  | 4 | TG-ID-1 out of paper | N | N |  | N | YES | <D> **** Detailed Description **** TG-ID-1 out of paper, needs new paper roll <I> **** Actions Taken **** Informed MCR | 02-00-TG-ID-1
397728 | CR | 20190806 |  | 4 | COND-AO-207B needs to be replaced or repaired | N | N |  | N | YES | <D> **** Detailed Description **** During stroke test of new valve COND-V-207B craft found that the Air operator isnâ€™t working as designed and has significant blow. This air operator leak â€œblowbyâ€ is why the valve isnâ€™t closing correctly and allowing valve isolation leakby. Supervisor tried to order a replacement AO CAT ID 13301 (See MR 323930) currently a like for like replacement isnâ€™t available in the warehouse. <I> **** Actions Taken **** Contacted SM and WWM wrote CR | 02-00-COND-AO-207B
397729 | CR | 20190807 |  | 4 | DG1 room lighting needs replaced | N | N |  | N | NO | <D> **** Detailed Description **** DG1 room lighting needs replaced. More than half the fluorescent lamps are burnt out/ missing/ not working <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** DG1 room lighting
397730 | CR | 20190807 |  | 4 | DG-1 jacking tool missing locking pin | N | N |  | N | YES | <D> **** Detailed Description **** While placing the jacking tool on DG-1, the air motor separated from the jacking tool gear mechanism. These two pieces are held together by a sliding bolt that is secured with a locking pin (as observed on DG-2 jacking tool). The pin is missing allowing the sliding bolt to move and decouple the air motor from the gear mechanism if held at certain angles. The bolt was slid back into place and we were able to bar over the diesel, but a pin is needed to prevent separation. Please replace the locking pin. <I> **** Actions Taken **** Notified CRS <N> **** Equipment Description **** DG-1 Jacking tool in DG-1 metal chest by day tank room
397736 | CR | 20190807 |  | 3 | SDOCA Perimeter Road Needs Maintenance | N | N |  | N | NO | <D> **** Detailed Description **** SDOCA Perimeter Road Needs Maintenance X2141 for details <I> **** Actions Taken **** CR/WR Generated, Security Supervision Notified, Security Equipment Coordinator Notified <N> Facility has graded the identified areas and additional gravel has been compacted, no additional actions necessary.
397737 | CR | 20190807 |  | 4 | Oscillograph Started alarm | N | N |  | N | NO | <D> **** Detailed Description **** The Oscillograph Started alarm was due to the J7 sensor [500KV Neutral Ground]. The J7 sensor has been reset. E -TR-S and E-TR-B voltages as indicated on H13-P800 are 240/238/241 kV and 119/118/118 kV respectively. BPA Dittmer reports the 500 KV Grand Coulee Hanford 1 relayed off and back on. No RAS initiated. All plant controllers and equipment exhibited normal operation.
397738 | CR | 20190807 |  | 4 | 10 Pieces of M&TE Suspended until R25 |  |  |  | N | NO | <D> **** Detailed Description **** 10 Pieces of M&TE were NOT used during Calibration cycles and have been Suspended until R25. See list for Calcodes, Descriptions, Models and assocated DEF #'s. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
397739 | CR | 20190807 |  | 4 | Water found in ES-15 during maintenance activities | N | N |  | N | YES | <D> **** Detailed Description **** Water was found during maintenance activities in manhole ES-15. Approx. 6-10 inches total. Request support to remove water and verify operability of components inside. <I> **** Actions Taken **** CR/WR generated | 02-00-SEC-TAS-ES15T
397740 | CR | 20190807 | CAQ | C | 2019 DBAI no splice in cable 2MISC-0304 | Y | N |  | N | NO | <D> **** Detailed Description **** WORK ORDER 02050251-15 REWORKED CABLE 2MISC-0304 FROM THE CABLE SPREDING ROOM TO E-PP-8AA. IT WAS PLANNED TO INSTALL A CLASS 1E SPLICE IN A CONDULET AND LABEL THE CONDULET "SP-W069". WHEN THE RACEWAY WAS REWORKED BETWEEN THE CABLE TRAY AND THE PANEL, THE EXISTING CABLE WAS LONG ENOUGH AND DID NOT REQUIRE A SPLICE. THE WORK ORDER WAS REVISED AND THE DOCUMENTATION WAS NOT. THIS IS A DOCUMENTATION ISSUE ONLY. <I> **** Actions Taken **** INITIATED THIS CR AND NOTIFIED DESIGN ENGINEERING OF THE CONFIGURATION IMPACT TO EDISON(CARPS) AND EWD-46E-248, E763-2, <N> **** Equipment Description **** SP-W069 WAS ANTICAPATED TO BE NEAR TRAY NODE 7908 IN THE CA BLE SPREADING ROOM.
397749 | CR | 20190807 |  | 4 | RWP 30004328 is G.E. 5.000 p-Rem and exceeds est. by 50% |  |  |  | N | NO | <D> **** Detailed Description **** RWP 30004328 has total dose estimate of 4.962 p-Rem and actual dose expenditure of 8.903 p-Rem, for a dose variance of 79.4%. This RWP was created for a multitude of jobs in the High Radiaition Areas of the Steam Tunnel, Rx 501' Valve Rooms, and Drywell Controlled Area. There are 35 diffferent Work Orders and 52 ALARA Tasks on this RWP. There is no job on this RWP that is G.E. 5.000 p-Rem and exceeds est. by 50%. <I> **** Actions Taken **** Documented Post Job Review, documented CR and notified Supervisor.
397750 | CR | 20190807 |  | 3 | MET Bravo Outputs to MCR are Frozen | N | Y |  | N | YES | <D> **** Detailed Description **** All of the outputs from MET B locked up on 8/5/2019 at ~12.10 PM . Request server be reset by computer engieering. Last done 7/24/19. <I> **** Actions Taken **** Informed CRS. Initiated This CR | 02-00-MET-WMON-1B
397755 | CR | 20190807 | CAQ | C | DBAI 2019 (NRC Identified) Documentation issue with Vol 18 |  |  |  | N | NO | <D> **** Detailed Description **** PPM 18.1.34 was performed for PMT following RHR-P-2A maintenance following EC 14635. Step 7.11.8 supports documentation of pump suction pressure on attachment 9.1. Step 7.11.22 supports documentation of discharge pressure per the histrogram, however there is no pounded step to calculate and verify differential pressure meets SR 3.5.1.4 requirements. All the data exists within the surveillance to validate that differential pressure in fact met the requirements of SR 3.5.1.4. This CR is written to document the administrative issue. There is no operability concern with RHR-P-2A. OSP-RHR/IST-Q702 was verfiied to have the step to verify differential pressure (step 7.2.80) per SR 3.5.1.4. Completed 18.1.34 uploaded into EDMS. <I> **** Actions Taken **** CR written and MCR notified.
397761 | CR | 20190807 |  | 4 | Inaccurate Reading from Digital Meter on CL-TK-4 | N | N |  | N | NO | <D> CL-LI-4 (Level indicator for CL-TK-4 â€“ The sodium bromide/hydrobromic acid/biosperse tank) is inaccurate. This reading needs to be accurate so that OPS can identify whether or not there is space to accept incoming chemical deliveries. Issue was previously documented in CR 392264. <I> Notified supervisor, notified chemistry, wrote this CR to document the issue. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
397763 | CR | 20190807 |  | 3 | Condensate Demineralizer tag-out enhancements | N | N |  | N | NO | <D> **** Detailed Description **** While performing work in the 8/5/19 work week on multiple valves, Operations was contacted to manipulate a drain valve (COND-V-1079B) that was not on the clearance order in order to drain a section of the piping that would allow COND-V-231B to be replaced. While attempting to remove COND-V-260B excessive draining was noted and Operations was contacted to close COND-V-214B. Upon closing COND-V-214B leakage stopped and COND-V-260B was then able to be removed. Work on these valves was being performed under C/OS D-COND-DM-1B-001. Having COND-V-1079B and COND-V-214B as part of the tag out in the appropriate positions would have saved time during this â€˜Bâ€™ demineralizer outage. This enhancement could be applied to other demineralizer outages in the future for the PM valve replacements. <I> **** Actions Taken **** Notified Operations during Demin outage. Discussed with shop Manager.
397764 | CR | 20190807 |  | 3 | PPMs 10.27.30A, B not per IMDS | Y | N |  | N | NO | <D> **** Detailed Description **** PPMs 10.27.30A and 10.27.30B have not been revised to be in alignment with DSA-PCV-1A, 1B, 2A, 2B IMDS's (revised on 7-11-18). The IMDS were revised per AR-EVAL-378382 but the assignment to change the procedures was closed on 7-5-18 and migrated to the Sharepoint database. 10.27.30A is scheduled to be performed on 10-8-19 in the DG1 window. 10.27.30B was performed on 5-10-19 per WO-02106823. <I> **** Actions Taken **** Recommend assignment to MAINTPROG to reopen AR-EVAL -378382-03.
397765 | CR | 20190807 |  | 3 | AR-EVAL-378382-03 markup perpetual do-loop | N | N |  | N | NO | <D> **** Detailed Description **** Per I&C, the markup for Assignment 03 that updates PPMs 10.27.30A and 30B to eliminate steps related to dynamic monitoring is not workable. This is preventing the required engineering changes to the DSA-PCV-1A, 1B, 2A, 2B setpoints from being issued. The procedures have a perpetual do-loop built-in as the issue concerning static vs dynamic monitoring has never been resolved. <I> **** Actions Taken **** PPM 10.27.30A is needed on 10-8-19.
397766 | CR | 20190807 |  | 3 | SOP-CFD-FILL procedure enhancement. | N | N |  | N | NO | <D> **** Detailed Description **** Need to change steps 5.2.9, 5.3.9, 5.4.9, 5.5.9, 5.6.9 and step 5.7.9 of SOP-CFD-FILL to eleminate the reference to WO 01159580-35. Please replace with a statement to the effect " per WO instructions provided to I&C ". This is needed to eliminate confussion between the I&C tech. instructions and the OPS procedure. <I> **** Actions Taken **** CR per CRS request.
397767 | CR | 20190807 |  | 4 | Two GFES candidates failed Rx Theory Phase GFE exam | N | N |  | N | NO | <D> **** Detailed Description **** An ILC-24 and NLOI candidate each failed the Rx Theory exam given on 8/7/2019. Remediation will be conducted in accordance with TDI-02 and TDIs-09 and 10 respectively. No qualifications are impacted. AR is for tracking purposes only. <I> **** Actions Taken **** Informed Ops and Training management. Held informal performance review. Reviewed exam for common weak areas. Documented informal performance review in ILC and NLOI One Note.
397768 | CR | 20190807 |  | 3 | DG1 room housekeeping (NRC Identified) | N | N |  | N | NO | <D> **** Detailed Description **** The vacuum cleaner staged in the DG1 room had the tape covering the suction hose come loose. This resulted in a small pile of rust and debris on the floor. The area has been cleaned and the hose re-taped.
397769 | CR | 20190807 |  | 4 | HWC P500 Device Trouble (Alarm drop 1-1) | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing battery replacements for HSSF/HWC Fanuc PLC's under WO# 0213 1977 01. HWC p500 panel alarm drop 1-1 (Device Trouble)activated while battery was removed for exchange. ARP for drop 1-1 states to write WR and CR for investigation. Appears status bit for low battery has control logic tied to alarm drop and needs to be cleared in PLC fault table. <I> **** Actions Taken **** Informed I/C Supervision and MCR staff. Wrote CR/WR to document condition <N> **** Equipment Description **** HWC p500 Fanuc PLC
397770 | CR | 20190807 |  | 4 | RW control room Portal Monitor may have a failing detector. | N | N |  | N | YES | <D> **** Detailed Description **** While performing routine calibration of ARGOS HP-EQ-42820, a detector was found to be questionable. The difference between the previous vs current efficiencies of Detector 25b was found to be at the 20%. Above which would be unacceptable. While this is procedurally acceptable, it may be an indication that the detector is failing. The detector may need to be replaced prior to next scheduled calibration. <I> **** Actions Taken **** Discussed issue with HP Supervision. | 02-00-HP-EQ-42820
397771 | CR | 20190807 |  | 3 | R24LL - New Hire Checklist for Outage Temps | N | N |  | N | NO | <D> **** Detailed Description **** During the R24 station critique, supervisors revealed that the shops spent a great deal of time completing the standard New Hire Checklist while on boarding outage temps for R24, which ended up being burdensome while also trying to bring them up to speed on their outage job in short period of time. The purpose of this LL CR is to explore improving this process going forward specifically for outage temps (e.g., eliminate the requirement, shorten the form). Recommend assignment Severity 3 / AR-HR as owner of the process. <I> **** Actions Taken **** Discussed w/HR Mgr, set up a mtg w/stakeholders to discuss issue <N> reopened per request of owner. A revised new hire checklist has been reviewed by insterested parties and approved. Updated checklist has received all approvals and is set for release on 10/29/19. Action complete.
397772 | CR | 20190807 |  | 4 | DRA-EUH-11 Power light not lit - NRC identified | N | N |  | N | YES | <D> **** Detailed Description **** DRA-EUH-11 was found to have its, red, power available light not illuminated. This issue was identified by the NRC resident. The Power light has been relamped and is working properly. <I> **** Actions Taken **** Informed MCR of bulb replacement. <N> **** Equipment Description **** DRA-EUH-11, control box. DG1 storage tank room | 02-00-DRA-EUH-11
397774 | CR | 20190807 |  | 3 | Non functioning eye wash stations. | N | N |  | N | YES | <C> MRT Change: CR 397774 Severity moved from 4/Trend Repair to Severity 3 assigned to AR-PERFIMP. <D> **** Detailed Description **** DW-DWS-4 and PWC-SEW-9 are isolated due to leaking by preventing the testing of those eye wash stations. Between the 2 valves, 10 CRs have been written in the last 5 years for the valves. Recommend fixing the valves once and for all. In the meantime, work instructions for WO #02137854 require temporary eye washes be stationed next to the broken ones. | 02-00-DW-DWS-4,02-00-PWC-SEW-9
397775 | CR | 20190807 |  | 4 | Off site power outage caused ENOC to lose power | N | N |  | N | NO | <C> Facility code changed from 02 to 06 by MRT <D> **** Detailed Description **** Power outage to the APEL, MPF, and CDC buildings on August 7th, 2019, from approximately 1pm to 3pm. Outage caused by a failed connector in a City of Richland Transformer. <I> **** Actions Taken **** Contacted City of Richland to determine cause. Coordinated with building tenants and made proper chain of command notifications. Contacted Fire department who responded to CDC for fire panel alarm. Facilities and Fire Department personel reset fire panel. Coordinated with Facilities to make sure back up generators were working and emergency systems functional. Once power came back on, made proper notifications to tenants, and managment. Facilities performed additional walkdowns to make sure all building systems came back on and were functional. No further issues identified.
397776 | CR | 20190807 |  | 4 | Received GENERTOR BUS DUCT TEMPERATURE HIGH alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received GENERTOR BUS DUCT TEMPERATURE HIGH alarm ( 4.800 .C4 1-2 ). Dispatched OPS3, and OPS 4 to investigate. TSW line up was verified and IBD temperatures as follows. IBD-TI-F1- 92 F, setpoint is 160F IBD-TI-F3 â€“ 140 F, setpoint is 200F IBD-TI-F5 â€“ 80C , setpoint is 93C IBD-TI-F7 â€“ 90F , setpoint is 160F IBD-TI-F9 â€“ 132F, setpoint is 200F IBD-TI-F11 â€“ 86 C, setpoint is 93C. CW Blow down is currently secured. Suspect that this alarm will clear shortly after blowdown is re-established. IBD -FN-1B is running. <I> **** Actions Taken **** Currently investigating. | 02-00-IBD-FN-1B
397777 | CR | 20190807 |  | 4 | DBAI 2019 Scaffold Tag retagging may lose Engineering approv | N | N |  | N | YES | <D> **** Detailed Description **** During a field walkdown associated with the in-progress 2019 DBAI, three PPM 10.2.53 Scaffold Tags in the Diesel Generator Building were identified that had anomalous Engineering approval documented in the field. It appears that the anomalies noted were the result of past re-tagging efforts. All anomalies noted have been corrected in the field. 1) Scaffold Tag 1669 - Did not document an Engineering approval for this DG2 maintenance platform access ladder (i.e., like that which had been documented for the other 7 EDG maintenance platform access ladders). 2) Scaffold Tag 1668 - Indicated Engineer approval for this DG2 maintenance platform access ladder but did not indicate the Engineer's name. 3) Scaffold Tag 1676 - Did not indicate Engineer approval for this Safway scaffold stair in the DG1 exhaust silencer room on the Scaffold Tag. This scaffold stair was Engineer approved via WOT 01169549-01, AR SELF 187115, and AR EVAL 187114. <N> Title change request from Engineering to identify this as DBAI. | 02-00-D-BLDG-MISC
397778 | CR | 20190807 | CAQ | C | DBAI 2019 CIA System Analysis Legacy Issue | Y | N |  | N | NO | <D> **** Detailed Description **** ME-02-92-29 determined that 1 CIA nitrogen bottle in Division 1 and 2 CIA nitrogen bottles in Division 2 could be valved out of service at any time and still maintain system operability requirements. However, the analysis did not consider ADS valve actuations as an input, only system leakage. When 1 bank actuation is considered in a division, the conclusion of the analysis will change to 1 CIA nitrogen bottle can be valved out in each division, not 2 valves in Division 2. This analysis does not establish operability of the normally designed, normally maintained CIA nitrogen bottle racks. The analysis was for an off-normal condition. This is a legacy analysis issue.
397779 | CR | 20190807 |  | 3 | CR Key Box, Keys 246 not present. | N | N |  | N | NO | <D> **** Detailed Description **** 1.3.23 New rev 63 dated 7/6/19 added 2 keys on slot 246. The keys for slot 246 are not present in the lock box in the control room. The keys are for WEA-CP-25 flow and fan input test switch. (WEA-RMS-CP25/TEST)
397780 | CR | 20190808 | CAQ | C | PPC is out of service | N | N |  | N | YES | <C> CR reopened to cross reference additional WR 29148640, marked completion required box, then taken back to complete <D> **** Detailed Description **** PPC is out of service with red status on multiple TDAS remote and PPC MUX inputs. <I> **** Actions Taken **** Contacted engineering backshift coordinator and IS. Shifted from PPC as primary to TDAS as primary per SOP -COMPUTER-OPS. | 02-00-PPC-COMP-8715
397781 | CR | 20190808 | CAQ | D | Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02146548, marked completion required box, then taken back to complete <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-5435.Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-5435 was due to low Nitrogen pressure. OPS2 re-pressurized per SOP-CRD-HCU and the alarm is clear. <I> **** Actions Taken **** informed crs/sm | 02-00-CRD-HCU-5435
397782 | CR | 20190808 |  | 3 | ABN-COMPUTER revision needed | N | N |  | N | NO | <D> **** Detailed Description **** ABN-COMPUTER currently does not have a step to transfer from PPC to TDAS in the event of a failure of PPC while it is primary. A step similar to 4.14 should be added to allow/direct this action. <I> **** Actions Taken **** initiated CR
397783 | CR | 20190808 |  | 4 | A/C unit Out Of Service at the checkpoint | N | N |  | N | YES | <D> **** Detailed Description **** A/C failed at the checkpoint, Placed a portable A/C unit in its place. <I> **** Actions Taken **** A/C unit failed, supervision notified, CR/WR generated <N> **** Equipment Description **** Checkpoint main building
397784 | CR | 20190808 | CAQ | D | HPCS room temp high out of spec. | Y | Y |  | N | YES | <C> MRT Change: CR 397784 moved from NON-CAQ Severity 4/Trend Repair To CAQ Severity D/Trend Repair. <D> **** Detailed Description **** HPCS roome temp near the DG read 96 F with a high log spec of 95 F. <I> **** Actions Taken **** Informed CRS. <N> **** Equipment Description **** HPCS Room Temp
397785 | CR | 20190808 |  | 4 | DO-F-5 Hi DP for polisher. | N | N |  | N | YES | <D> **** Detailed Description **** DO-F-5 high DP alarm was recieved while transferring FO from DO-TK-1A to FO-TK-1 for DG testing. DP on DO-DPIS-5 read 20# during transfer. <I> **** Actions Taken **** Stopped transfer, recieved CRS permission to finish transfer. | 02-00-DO-F-5
397792 | CR | 20190808 |  | 4 | MT&E Found Out of Tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0066896 AEMC Dual Current Probe- model MN185 Passed Calibration but now Rejected- unable to repair. DEF #7160A written. No Plant Impact. No Action Required.
397793 | CR | 20190808 | CAQ | C | MT&E Found Out of Tolerance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0066908 Honeywell Pressure Transducer- model FPG 100psi found OOT & adjusted within specs. DEF #7162A written. EFIN to Evaluate the 3 usages.
397794 | CR | 20190808 | CAQ | C | MT&E Found Out of Tolerance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0067140 Megger Dig. Low Resistance Ohmmeter- model DLRO 10 found OOT & Needs Repair. DEF #7163A written for EFIN to Evaluate the 5 usages.
397796 | CR | 20190808 |  | 4 | Screen will not turn on for RFW-TR-1 in MCR. | N | N |  | N | YES | <D> **** Detailed Description **** Durnig operator round it was observed that the screen for RFW-TR-1 was not illuminated as it normally was. Attempts to awaken the screen by depressing the DISP/ENTER and arrow buttons failed. The green light on the lower left is still illumunated. WR 29140000 suggests that the alarm functions provided by this recoreder should still function. PPI PPM 4.840.A1 page 73 gives a list of the computer points that are associated with this recoreder so if the alarm does function the points can be checked. This would take time to determine the alarming point as that there are 22 points with 12 listed as having alarm functions. Recomend investigating and correcting to allow for monitoring of Reactor feed pump temperatures. <I> **** Actions Taken **** Wrote this CR. Informed CRS. Added 2 previous instances of failed screens to Xref tab. | 02-00-RFW-TR-1
397801 | CR | 20190808 |  | 4 | SCW-FQI-2 abnormal trend | N | N |  | N | YES | <D> **** Detailed Description **** SCW-FQI-2 (H2 Vent totalizer) is trending abnormally when compared to pre R24 trends. SCW-FQI-2 has trended ~ 100 SCF per day, over the last 2 days. Pre R24, SCW-FQ-2 would consistently trend ~ 150 SCF per day, or more. This reduced trend and the reduced SCW-TK-1 pressure, identified under WR# 29150828, may share a common cause. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TG 501W | 02-00-SCW-FQI-2
397804 | CR | 20190808 | CAQ | D | Rod Accumulator Trouble Alarm on CRD-HCU-2655 | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02147787, marked completion required box, then taken back to complete <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-2655 was low pressure. OPS2 re-pressurized per SOP -CRD-HCU. | 02-00-CRD-HCU-2655
397805 | CR | 20190808 |  | 4 | Recieved 4.FCP.2 drop 16-5 ASD FIRE ALARM | N | N |  | N | YES | <D> **** Detailed Description **** Recieved 4.FCP.2 drop 16-5 ASD FIRE. Operators reported 4 minutes after fire alarm that there was no fire present. After determining that there was no fire FP-V-428 was closed. FP-P-2A auto started with the annunciation of this alarm. Investigation suggests that FP-ID-85/3 is the culprit as that its alarm light was illuminated. With this decector acuated the alarm could not be reset at FSP-13. VRMA-AC-1 and VRMA-AC-2 were verified to be operating. Invetigate and correct this deficiency to return fire protection to the ASD building. This has an alarm locked in on FCP-2 in the MCR. Evaluate for inclusion to the OPS aggregate list. <I> **** Actions Taken **** Wrote this CR. Followed ARP. | 02-00-FP-ID-85/3
397807 | CR | 20190808 |  | 4 | Columbia's Environmental PI for Hazardous Waste Red for July |  |  |  | N | NO | <D> **** Detailed Description **** Columbiaâ€™s Environmental Performance Indicator (PI) for hazardous waste turned red in July. Columbia exceeded the hazardous waste monthly limit by 38.8 pounds. The cause of the indicator turning red was due to an increase of excess and expired chemicals disposed of in July (some of this waste was from R-24). This doesnâ€™t jeopardize Columbiaâ€™s current medium quality generator status and this PI is anticipated to turn back to green in August. <I> **** Actions Taken **** Discussed with department manager and developed a plan to prevent reoccurrence of this issue.
397808 | CR | 20190808 | CAQ | D | Received Rod Accumulator Trouble Alarm for CRD-HCU-0231 | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02146633, marked completion required box, then taken back to complete <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-0231 was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear. | 02-00-CRD-HCU-0231
397809 | CR | 20190808 | CAQ | D | Recieved Accumulator Trouble Alarm for CRD-HCU-2655 | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02147787, marked completion required box, then taken back to complete <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-2655 was low pressure. OPS2 re-pressurized per SOP -CRD-HCU. Later in the shift WO 02147787 repaired the P6 connector for theis HCU. <N> unintended duplicate of AR 397804 | 02-00-CRD-HCU-2655
397810 | CR | 20190808 | CAQ | D | Evaluated Suppliers List approved 17025:2017 suppliers |  |  |  | Y | NO | <D> **** Detailed Description **** Problem Statement: The Evaluated Supplier List (ESL) showed suppliers accredited to ISO 17025:2017 as approved for use. This is not aligned with the station quality assurance program. The Operational Quality Assurance Program Description specifies that only the 2005 version of the standard is acceptable. <I> **** Actions Taken **** Set the list of identified suppliers to inactive and communicated with Supply Chain Services and the Calibration Lab the suppliers are no longer approved for use.
397811 | CR | 20190808 |  | 4 | MT-ELEV-3 (TB East Elevator) is stuck on TB 471E | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-3, the Turbine Building East Elevator, is stuck on the TB 471 Elevation. All Doors were verified to be closed properly. Power was cycled to the elevator in an attempt to reset the logic. The Elevator remains stuck on the TB 471. <I> **** Actions Taken **** Informed MCR. Placed Elevator out of service barrier in place. <N> **** Equipment Description **** TB East side Elevator. | 02-00-MT-ELEV-3
397812 | CR | 20190808 |  | 4 | Parking bay angle configuration |  |  |  | N | NO | <D> **** Detailed Description **** With recent increase in cars incidences in Deschutes building parking lot, consideration should be given to parking bay angle configuration. Parking bays angled at 45 to 60 degrees would increase safety and are more efficient. 90 degree angled parking bays by Deschutes and Willamette building are difficult to park in, and pull out off, especially when parked next to a large truck or SUV. The Benefits of Angled Parking bay/Spaces â€¢ Increased Safety. Safer because (1) it forces a one-way flow of traffic, and (2) it can be easier to get into and out of spots. â€¢ Maneuverable Spots. Getting in and out of slanted spots is much easier than trying to pull out of a straight parking space. â€¢ Traffic Flow. â€¢ Less Space. angled parking requires less space. According to Professor Percy, the shift to 45-degree bays results in a 23% space saving, so on a typical 500 bay parking lot youâ€™d add an extra 119 parking spaces. Reference information is available in the AR EDMS. <N> Notes from Facilities Principal Engineer, Craig Witte: I do not believe one way parking access is safer. It restricts flexibility and forces people to access parking in only one direction. Using the Deschutes parking lot as an example. Here, in order to provide for efficient vehicle and parking flow every other driving lane will need to be one direction or the other. Since the Deschutes parking lot is laid out in an east west direction and there are 4 driving lanes, this means that any vehicle leaving the site access road will only be able to access the Deschutes parking lot with two of those 4 driving lanes. At peak hours this may result in vehicles bunching up on those drive lanes which are east bound. A similar issue will develop at the end of the working day where every vehicle is forced to always go in one direction and every vehicle can only turn on to the access road in two locations. Finally, the two lanes which would be west bound cannot connect to the access road. This is necessary to prevent an unsuspecting driver from heading the wrong way down one of these access roads as they leave the access road and enter the parking lot. Regarding the additional efficiency of angled parking. There is less efficiency. The optimal universally usable parking stall is generally accepted to be 9â€™ wide by 20â€™ long. As the parking stall is rotated off the vehicle access driving lane then, per parking design convention, the driving lane can be reduced in width if vehicle travel is restricted to only one direction. With a 45 degree rotated stall the vehicle access lane can be 12â€™ wide. With a 60 degree rotation the vehicle access lane can be 15â€™ wide. Considering the space of a 9â€™x20â€™ stalls symmetrical on both sides of the appropriate width access lane. A 45 degree parking configuration will then occupy 355 SF per stall. This includes the width of the vehicle access lane, a 60 degree configuration occupies 315 SF per stall (with access lane width) and a stall 90 degrees (perpendicular) to the drive lane will occupy 290 SF per stall (including access lane). Thus, in my opinion, angle one way parking is neither more safe nor is it more efficient. I do not believe it is a good idea to change to angled parking.
397813 | CR | 20190808 |  | 3 | 2019 DBAI: Wording for Ref 2.9 of PPM 10.2.53 R46 clarified |  |  |  | N | NO | <D> **** Detailed Description **** This is an administrative issue only. Reference 2.9 of PPM 10.2.53 "Scaffolding" Rev 46 says "AR-245159, remove seismic scaffolding information from PPM 10.2.53 and place in new PPM 10.2.222." This wording needs clarified because it seems to say that PPM 10.2.222 " Seismic Storage Requirements For Transient Equipment" will have information about seismic restraint of scaffold, which it does not. PPM 10.2.222 is for Transient Equipment and PPM 10.2.53 is for scaffold. Suggest that Reference 2.9 of PPM 10.2.53 says something like: "AR-245159, removes Seismic Storage Requirements For Transient Equipment from PPM 10.2.53 and places it in new PPM 10.2.222." <I> **** Actions Taken **** Wrote this CR.
397814 | CR | 20190808 |  | 4 | Both lights out RW 525 stairwell | N | N |  | N | YES | <D> **** Detailed Description **** Both the permanent lights in the RW Building 525 stairwell are out. <N> **** Equipment Description **** RW 525 stairwell
397816 | CR | 20190808 |  | 4 | Eyewash Station # 35 is OOS | N | N |  | N | YES | <D> **** Detailed Description **** The eyewash station (#35) next to Bldg. 118 is out of service. The pressure gage on the device reads 0 psi. This station needs to be recharged. <I> **** Actions Taken **** Wrote CR and generated WR. <N> **** Equipment Description **** EYEWASH STATION #35
397817 | CR | 20190808 |  | 4 | Critical PM Could not be completed | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02116595-01 RFW-DT-1A Lube Pedestal and Linkage, it was determined that accessing the zerk fitting to lubricate was unsafe. Climbing on hot the (160-250 degree) equipment, insulation, and piping is unacceptable. A walkdown was performed to determine if scaffold could be installed to alleviate this condition and the determination was that the scaffold builders would be exposed to the same hazards. Additionally this is a high radiation area. This PM and the RFW-DT-1B needs to be recoded to outage when all of these safety, risk, and dose factors would be considered low. <I> **** Actions Taken **** Initiated AR CR, work request to complete missing steps; contacted the Systems Engineering Manager per SWP-PRO-01for approval to N/A steps and determined the PM work order could be taken to finished, notified MCR and WWM. Additionally SMS-AR initiated to defer and recode PMID 9994-01 and 9995-01 to outage. Discussed with System engineer who indicated no initial impact. | 02-00-RFW-DT-1A,02-00-RFW-DT-1B
397820 | CR | 20190808 | CAQ | C | Cal Lab accepted OSD&D w/ incorrect calibration certificate |  |  |  | N | NO | <D> **** Detailed Description **** routine calibration; the Instrument for OSD&D 15503 was sent 12/21/2018 and the Instrument for OSD&D 15412 was sent 11/20/2018. Review of the vendorâ€™s accreditation prior to sending the assets out and review of the Calibration Certification when the items were returned did not identify the incorrect certification year. Technical work performed meets or exceeds the requirements of ISO/IEC 17025:2005 and 2017 versions and standards accepted fully meet the manufacturerâ€™s specifications and do not affect operability of any standards or plant M&TE. Keysight was active on Evaluated Supplier List (ESL) with no restrictions. PO for Keysight did not specify year for standard (ISO/IEC 17025) SPC 494 requirements were met as there is no requirement for year to be specified on certificate. Recommend assign to AR-CALSERV Category C <I> **** Actions Taken **** Created CR and notified supervisor, verified validity of all calibrations performed with equipment and determined no impact on operability of M&TE. Requested Keysight be placed Inactive on ESL until OQAPD can be revised. See EDMS for additional documentation. <N> All assinments that supported the investigation and corrected the deficiencies have been completed. Condition Evaluations are no longer required per CAP. All actions associated with AR are complete.
397821 | CR | 20190808 |  | 4 | Doors not meet criteria per 15.3.17 | N | N |  | N | YES | <D> **** Detailed Description **** Working 15.3.17 02117321-01 DOOR T-202 Rip in Metal , and Gap over 1/4" T-121,and T-102 Gaps over 1/4" | 02-00-T-DOOR-T102,02-00-T-DOOR-T121,02-00-T-DOOR-T202
397822 | CR | 20190808 |  | 3 | Iodine Dose Equivalent remains elevated | Y | N |  | N | NO | <D> **** Detailed Description **** The reactor sample for Iodine Dose Equivalent collected on 8/6/19 continues to indicate an increasing trend. The most recent value is 4.89E-6 uCi/g. The Tech Spec limit is 2.0E-1 uCi/g. Review of the other fuel health indicators did not show any negative trends. The offgas pretreatment monitor trend is steady and flat. The offgas isotopic analysis performed on 8/8/19 does not indicate any change from previous values. Fuels Engineering has contacted the fuel vendor, GNF to review the data. They do not believe it is an issue with the fuel cladding based on the lack of any change in offgas isotopes. Recommend Category D/Trend <I> **** Actions Taken **** Submitted an industry question the BWRVIP mitigation committee members to solicit input on the current trend and plant conditions.
397823 | CR | 20190808 | CAQ | D | Degraded Insulation Found on PRM-SR-2 | N | Y |  | N | YES | <D> **** Detailed Description **** While performing a walk down in support of the Radioactive Gaseous and Liquid Effluent Treatment Focused Self -Assessment, insulation was found to be degraded. The insulation on HT-TIS-PRM/C1 was found to be separating and needs to be repaired. See picture in EDMS <I> **** Actions Taken **** CR written <N> **** Equipment Description **** PRM-SR-2 HT-TIS-PRM/C1
397824 | CR | 20190808 |  | 4 | AED D-DGGRATINGEXT-206 update needed |  |  |  | N | YES | <D> **** Detailed Description **** The AED drawing for the permanent aluminum grating extensions on the west and east sides of DG-ENG-1A1, DG-ENG-1A2, DG-ENG-1B1, and DG-ENG-1B2 (AED MIS D-DGGRATINGEXT-206) needs to be updated. For the drawing to accurately reflect the existing field configuration for these extensions, a note should be added to the drawing indicating the aluminum grating may be coped (e.g., notched or trimmed) to accomodate existing field interferences (e.g., small bore DO piping/supports and DLO tubing/supports). Recommend resolution asignment to Mechanical Drafting. <I> No update for this drawing is needed - see existing NOTE 1 on the drawing "GRATING MAY BE CUT OR NOTCHED TO CLEAR INTERFERENCES." Recommend closeure with no action. | 02-00-DG-ENG-1A1,02-00-DG-ENG-1A2,02-00-DG-ENG-1B1,02-00-DG-ENG-1B2
397825 | CR | 20190808 |  | 3 | AR-SA 376387 identified errors in PPM ISP-TEA/PRM-X301 | N | Y |  | N | NO | <D> **** Detailed Description **** Focused Self-Assessment 71124.06 Radioactive Gaseous and Liquid Effluent Treatment identified two areas in PPM ISP-TEA/PRM-X301 that require correction. Section 7.4.19 references Table 7.4b when it should reference Table 7.4a. Section 7.6.9, Table 7.6a lists the maximum limit for TEA-RIS-13 Channel 2 Background Reading as 0. 0E0 to 1.8 1E-2. Calculation No. NE-02-09-12 lists the maximum allowed background range as 1.91E-02. <I> **** Actions Taken **** Informed SA Lead and documented in CR.
397826 | CR | 20190808 | CAQ | D | while performing WO 02134365-01 sample rack 13 found OOT | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** during the first auto o2 calibration found O2 OOT cal gas 6.00% analizer indicated 5.79% tolerance of Â±.2% <I> **** Actions Taken **** Perfomed a 2nd auto cal and O2 passed notified supervisor
397827 | CR | 20190808 |  | 4 | MD-V-89A appears to be closed | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WR 29150924 to stroke BS-V-39A, there was no temperature change noted via BS-TT-RV26A eDNA CIM data. This indicates MD-V-89A may be closed. This valve was replaced with the piping spool during R24. No as left valve position was specified in the WO and as found was "closed" so the valve is likely still closed. WR being generated to verify valve position and open valve if necessary. Scaffold is in place for access. <I> **** Actions Taken **** Spoke to FIN SRO. FIN SRO discussed with mechanics. <N> **** Equipment Description **** T -471- - -F5/4.6 -OVER A EVAP DRTK 485 | 02-00-MD-V-89A
397828 | CR | 20190808 | CAQ | D | 2019 DBAI - Clearance between DO lines and grating | Y | N |  | N | YES | <D> east-west clearance of approximately 11/16" and a minimum existing north-south clearance of zero inches to the south for one of the two DO lines. However, the field clearance is sufficient to preclude any design basis analysis AED CAL DO-2710-3. Horizontal SSE seismic loads and movements for these DO lines are even smaller than During the 2019 DBAI, an NRC inspector identified a **** Detailed Description **** clearance concern existing between a coped/notched area in the aluminum grating extension on the west side of DG1 DG-ENG-1A1 and two small bore DO lines. The concern was that the relatively flexible small bore DO lines might be damaged during a design basis seismic event because of their potential seismic motion (pipe movement) resulting in impacts with the relatively rigid nearby aluminum grating. The subject aluminum grating extension is depicted by AED D-DGGRATINGEXT-206 and the subject DO piping is depicted by CVI 317-00,1193,1 and CVI 317-00,318,1. Design Engineering investigated the concern and the existing clearances between the DO lines and the aluminum grating (greater than 2-1/4" east-west and greater than or equal to 1" north-south) are sufficient to preclude any potentially unevaluated pipe interaction with the nearby aluminum grating. This field investigation conclusion was confirmed via subsequent review of pipe stress analysis AED CAL DO-2526-3 - horizontal SSE seismic movements of the small bore DO piping will be small based upon the very small horizontal SSE loads calculated for the DO piping configuration of the DO piping is relatively stiff and the Design Engineering completed field walkdown of the similar potential for any significant north-south impact load from piping supports on either side of the grating. piping interaction with the grating under SSE conditions does not exist. Additionally, the existing east-west aluminum grating and DO lines on the west side of DG2 DG-ENG-1B1. Reference the same AED drawing for the grating and isometrics CVI 317-00,333,1 and CVI 317-00,337,1 for the DO lines). The investigation identified an existing seismic interaction between the DO piping and grating. These conclusions were confirmed via review of pipe stress those for the similar configuration adjacent to DG1. Therefore, there is no concern with the continued operation, function, or qualification of the EDG engines, aluminum grating, or any of the small bore DO piping associated with this condition. However, it would be appropriate to increase the size of the cope/notch in the aluminum grating on the west side of DG-ENG-1B1 to provide additional clearance for the DO lines to their south. <I> **** Actions Taken **** A complete extent of condition walkdown in the DG1 and DG2 areas was conducted by Design Engineering. Similar potential interaction between the aluminum grating and small bore DO piping west of DG-ENG-1A2 and west of DG-ENG-1B2 is precluded by pipe support U-bolts (or pipe support U-bolts and axial lugs) for the DO piping existing near the grating locations. No similar conditions were found on the east side of DG-ENG-1A1 or DG-ENG-1B1. On the east side of DG-ENG-1A2 and DG-ENG-1B2, there are copes/notches in the grating for tubing associated with DLO-V-710A2 and DLO-V-710B2 but the tubing is well supported immediately on either side of the grating which precludes the potential for any design basis seismic interactions between the tubing and grating. Notified Operations. Sent e-mail to the Shift Manager with the unjumbled AR CR text (attached to the AR CR EDMS). Photos attached to the AR CR EDMS of the grating/DO piping proximity configuration existing west of DG-ENG-1A1 and existing west of DG-ENG-1B1. | 02-00-DG-ENG-1A1,02-00-DG-ENG-1B1
397829 | CR | 20190808 |  | 4 | Lighting - 2 bulbs out 501' control room corridor | N | N |  | N | YES | <D> **** Detailed Description **** 2 bulbs, 1 fixture, are out on the east end of the 501' control room corridor. <I> **** Actions Taken **** CRS informed <N> **** Equipment Description **** fluorescent bulbs in fixture east end of 501' corridor
397830 | CR | 20190808 | CAQ | D | exhaust flow rate disparity between PDIS and WEA-SR-25 | N | Y |  | N | YES | <C> CR reopened to cross reference AR 00376942 and additional WR 29141192, marked completion required box, then taken back to complete <D> **** Detailed Description **** The PDIS data points ENW.CGS.L110 and X366 radwaste exhaust flow rate have are mismatched with the exhaust flow indicated on the WEA-SR-25 by approximately 10 - 15 %. This difference could cause a number of issues including sample flow on the WEA-SR-25 to be indicated isokenetic when it is not and introducing error in our offsite dose calculations. Currently we are using the higher value so we would be erring on the side of caution. Suggest determination of which value is correct and an IC correction be made to adjust the incorrect data point. <I> **** Actions Taken **** Specialist informed | 02-00-WEA-SR-25
397831 | CR | 20190808 |  | 3 | The CR Wizard jumbled the order of the lines for CR 397828 | N | N |  | N | NO | <D> **** Detailed Description **** When AR CR 397828 was initiated using the CR Wizard, the order of the lines for the Detail Description was jumbled (i.e., apparently randomized). This has happened before. The correct order of the line entries for the CR was maintained in the associated WR (i.e., WR 29150944). <N> Moving this out to allow for more time for the business analyst to review. ------------------------------------------------------------ We have seen this issue before (CRâ€™s AR185834, AR196281, 256739). It only happens on CR's with long descriptions. The issue is with the way the customer uses the scroll bars when adding text. Since only 3 lines of description text are displayed at a time, the customer needs to scroll down to enter more lines of text. There are 2 scroll functions, the single down-arrow which scrolls on the same page and the double down-arrow which scrolls to the next page. Using those scroll arrows incorrectly (using the double arrow instead of the single arrow) can cause the gen-args to be created improperly. The gen-arg is a field in the table which keeps the description in order as entered by the customer. The CR wizard application in AssetSuite is part of the AssetSuite upgrade project to be implemented in the summer of 2020. With the Assetsuite Upgrade now windows based technology, this issue should go away since the scrolling function is now windows based where multiple lines of the description are viewable at one time.
397832 | CR | 20190808 |  | 4 | CAS-MIS-10 not indicating temperature | N | N |  | N | YES | <D> **** Detailed Description **** On OPS-3 rounds, CAS-MIS-10 was reading, "UnderRnge DP/C" Sensor may be failing/failed. Please investigate <I> **** Actions Taken **** Notified CRS <N> **** Equipment Description **** Aux Boiler room. West wall, behind IR-28 | 02-00-CAS-MIS-10
397833 | CR | 20190808 |  | 4 | Wobbling belts on SRA-FN-51 | N | N |  | N | YES | <D> **** Detailed Description **** SRA-FN-51 has wobbling belts, with one significantly worse than the others. See attached video. Belt/sheave maintenance recommended. <I> **** Actions Taken **** Notified CRS <N> **** Equipment Description **** Service Building 456' | 02-00-SRA-FN-51
397834 | CR | 20190809 |  | 4 | CF-P-41A/B failed to prime | N | N |  | N | YES | <D> **** Detailed Description **** During performance of SOP-CW-CHEM-MAINT Section 5.17 following maintenance, CF-P-41A and B failed to prime. Both pumps were ran for GT 30 min with no discharge flow or pressure. CF-P-41B showed approx 30 psig discharge pressure and had little flow for a few seconds but was unsustainable. <I> **** Actions Taken **** Informed Supervision. . See multiple cross-referenced CR's. This has been an operator burden since January 2018 and still has not been resolved. This issue has been on and off the PCL as a result. We need to raise the priority to permanently fix this. | 02-00-CF-P-41A,02-00-CF-P-41B
397835 | CR | 20190809 | CAQ | D | CVB-V-1CD failed PMT | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of OSP-CVB/IST-M701 for PMT of CVB-V-1CD the full open light did not illuminate <I> **** Actions Taken **** restored from PMT surveillance and initiated CR <N> **** Equipment Description **** CVB-V-1CD | 02-00-CVB-V-1CD
397836 | CR | 20190809 | CAQ | D | T121 dog latch | N | N |  | N | YES | <D> **** Detailed Description **** T121 dog latch not functioning as designed. <I> **** Actions Taken **** Generated CR work request. <N> **** Equipment Description **** T121, Northwest Quadrant, North Wall Turbine Building.
397837 | CR | 20190809 | CAQ | D | SEC CCTV 13 & 13 T | N | N |  | N | YES | <D> **** Detailed Description **** SEC CCTV 13 & 13 T not functioning as designed. <I> **** Actions Taken **** Generated CR/WR | 02-00-SEC-CCTV-13,02-00-SEC-CCTV-13T
397838 | CR | 20190809 |  | 4 | Security PAAP door 12 | N | N |  | N | YES | <D> **** Detailed Description **** PAAP door 12 is not functioning as designed. Please contact Security at extension 2185 for further details. <I> **** Actions Taken **** Security Supervision notified. CR/WR generated for Electrical support. | 02-00-AAP-DOOR-AAP12
397839 | CR | 20190809 |  | 4 | CAS Bathroom Sink | N | N |  | N | NO | <D> **** Detailed Description **** The bathroom sink in the Central Alarm Station Bldg. 62 is draining slow. Request Facilities support to address the issue. <I> **** Actions Taken **** Security Supervision notified. CR/WR generated for Facilities support. <N> **** Equipment Description **** Building 62- CAS bathroom
397841 | CR | 20190809 |  | 3 | TDAS remote 8 input failed | N | N |  | N | YES | <D> **** Detailed Description **** Received TDAS remote 8-P801B alarm casuing red TDAS status. No ERDS inputs are impacted by this condition. <I> **** Actions Taken **** Disabled annunciator in TDAS to clear red condition. . TDAS-MUX-8 is located in panel H13-P801. This MUX has the white "POWER ON" light illuminated, however, it is cold to the touch, indicating it is not powered up. Prior history shows failure of the 5 VDC and 15 VDC power supplies has caused a similar condition in the past. | 02-00-TDAS-COMP-8715
397842 | CR | 20190809 |  | 4 | TO-TK-2 filter basket appears to be clogged | N | N |  | N | YES | <D> **** Detailed Description **** Oil was found leaking from strainer basket housing and pooling under TO-TK-2. Basket change likely needed. <I> **** Actions Taken **** notified CRS <N> **** Equipment Description **** TO-TK-2 room | 02-00-TO-TK-2
397843 | CR | 20190809 |  | 4 | Door T-129 will not close | N | N |  | N | YES | <D> **** Detailed Description **** Working 15.3.17 T-DOOR-T-129 auto closing door will not close , air flow thru main corridor not allowing door to fully close and latch | 02-00-T-DOOR-T129
397844 | CR | 20190809 |  | 4 | SAM-12 Handle/Latch Deficiency | N | N |  | N | NO | <D> **** Detailed Description **** The door on the SAM-12, located at the Alternate Access, doesn't always latch shut. When the door is shut & latched, the individual using the SAM-12 can open the SAM-12 without lifting up on the handle/latch. (HP-EQ-42812)- This has been a reoccuring problem with different Small Article Monitors. Historical CR's are #'s: 00320247,00354842,00362439,00369540 & 00389702. SAM-12 is still functional and will be left in service, it just needs worked on by FIN. <I> **** Actions Taken **** -Initiated CR & WR -Notified Supervision <N> **** Equipment Description **** HP AAP (HP-EQ-42812)
397846 | CR | 20190809 |  | 4 | Lighting out on 525' radwaste stairwell | N | N |  | N | YES | <D> **** Detailed Description **** 2 bulbs removed from fixture on 525' radwaste in the stairwell and 1 bulb removed, one out on 530' radwaste stairwell. Area is not well illuminated. <I> **** Actions Taken **** CRS informed <N> **** Equipment Description **** Lighting 525' RW bldg stairwell
397848 | CR | 20190809 |  | 4 | RWCR Small Article Monitor Needs Attention | N | N |  | N | NO | <D> **** Detailed Description **** The SAM (Small Article Monitor) @ the Radwaste Control Room has a display monitor that will start flashing (4 to 5 times) and chiming following a count. Whether it displays "Clean" or "ALARM" it will start flashing and chiming which isn't normal. The SAM still passes functional checks and is functional, it will be left in service. Possible short in wiring (electrical). (HP-EQ-42713) <I> **** Actions Taken **** -Initiated CR & WR. -Notified Supervision. <N> **** Equipment Description **** RWCR SAM (HP-EQ-42713)
397849 | CR | 20190809 |  | 3 | E-TR-M3 (Main 3 Transformer) Gas Anlayzer is in ALARM | N | N |  | N | YES | <D> **** Detailed Description **** The red ALARM light is lit on the E-TR-M3 gas analyzer. Please investigate/repair. Note: E-TR-M3 has an open ODMI that references monitoring the DGA samples for gas trending. A 2B45S key is required for xfmer yard access. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** Xfmr yard 2B45S key required for access. | 02-00-E-TR-M3
397851 | CR | 20190809 |  | 4 | Chemical spill cleanup is needed at the CW pump house |  |  |  | N | NO | <D> **** Detailed Description **** There is residual chemical on the floor around the CF-P -41A/B and 42A/B. The pump area is still isolated by a danger barrier but the leakage was stopped. The system was repaired per WR 29150606. The area requires routine access so the chemical on the floor needs to be cleaned up and the danger barrier removed. <N> **** Equipment Description **** CW pump house floor near CF-P-41A/B and 42A/B
397852 | CR | 20190809 |  | 4 | Rx Building Stack General Trouble | N | Y |  | N | YES | <D> **** Detailed Description **** At 10:43 MCR received a Rx Building Stack General Trouble alarm, which cleared less than a minute later. The Event Logs Detail screen said that â€œNGD-12 AC Not Valid Valueâ€ was the cause. | 02-00-PRM-SR-1
397853 | CR | 20190809 |  | 3 | Cart not secured in vicinity of PP-7AZ | N | N |  | N | NO | <D> **** Detailed Description **** Observed work cart not secured within close proximity of PP-7AZ in the MCR (see photos attached EDMS). The cartâ€™s floor mounted retainer bracket had broken free and the cart was able to freely roll around despite the cartâ€™s wheel chocks being engaged. Additionally, excessive loose test equipment was piled on and around both carts despite the availability of equipment lockers for storage. A set of used old coveralls was found draped around with a label saying â€œ12 cal/cm2â€ on breast pocket along with an electrical safety faceshield. Recommend the wheels/chocks of both carts be evaluated for replacement, since one cart rolled freely. The broken floor mounted retainer bracket was fixed by Ops after discovery, though only plastic Panduits were used. <I> **** Actions Taken **** Re-mounted the broken off retainer bracket
397854 | CR | 20190809 |  | 3 | ABN-CR-EVAC Procedure Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Per ABN-CR-EVAC attachment 7.7, the Safe Shutdown EO is required to don an ARC flash suit with hood and high voltage rated gloves, pull twelve sets of fuse blocks and open six 4160V breakers, all within ten minutes of the reactor scram. This is a challenging time limit. Recommend adding an additional Subsequent Operator Action in step 4.1.1 for the RO to trip all Booster and Condensate pumps
397855 | CR | 20190809 |  | 4 | TMU-V-1 (Surge Arrestor) Opens Early | N | N |  | N | YES | <D> **** Detailed Description **** The TMU Surge Arrestor valve has been observed to be open with TMU header pressure indicating 90 psig on TMU-PI-1. TMU-V-1 is not supposed to Open until 104 psig. Per the first note in the ARP 4.824.M.9-6, TMU-V-1 opens mechanically (via a relief valve) when pressure is GT 104 psig. Logic diagrams associated with TMU-V-1 support that TMU-RV-10 causes the Surge Arrestor to open on high pressure. Suspect that TMU-RV-10 is lifting prematurely, causing the Surge Arrestor to also open prematurely. | 02-00-TMU-RV-10
397856 | CR | 20190809 | CAQ | D | Received Rod Accumulator Trouble Alarm for CRD-HCU-1419 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-1419. Dispatched OPS-2 to investigate. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-1419 was due to low nitrogen pressure. OPS2 re-pressurized per SOP-CRD-HCU and the alarm is now clear. A nitrogen leak has been previously identified and a Work Order is in planning (see cross references). This AR/CR submitted for trending. | 02-00-CRD-HCU-1419
397857 | CR | 20190809 |  | 4 | TSW-V-750A Chem sample point NO flow | N | N |  | N | YES | <D> **** Detailed Description **** update to previous AR 396959. The flow has continued to degrade to the point where with the valve fully open there is no flow. The alternate sample point, radiation monitor, causes alarms in the control room and could be a distraction. <I> **** Actions Taken **** CRS and supervisor informed <N> Could try cycling the manual root valve (TSW-V-750). | 02-00-TSW-V-750A
397858 | CR | 20190809 | CAQ | C | CMS-PI-10 has inappropriate units | Y | N |  | N | YES | <D> **** Detailed Description **** CMS-PI-10 does not read out in the appropriate units. ABN-CONT-VENT relies on local indication of Containment Pressure, via CMS-PI-10. The emergency venting is to begin when Containment pressure reaches 2 PSIG. Unfortunately, CMS-PI-10 units read out in inches of H2O. CMS-PI-10 upper range ends at +10 inches of H2O. 2 PSIG correlates to ~55 inches of Water, making CMS-PI-10 useless for obtaining an accurate value of Containment pressure. Please replace CMS-PI-10 with an appropriately scaled gauge, with the proper units. See EDMS for IMDS, M drawing, and ABN-CONT -VENT. <I> **** Actions Taken **** Informed MCR <N> If changing the unist on CMS-PI-10 is desired, an AR type EVAL is required for evaluation. | 02-00-CMS-PI-10
397859 | CR | 20190809 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 239 B: 237 C: 240 E-TR-B A: 120 B: 119 C: 118 The following sensors were tripped and are reset: J-7 500KVN BPA reports the following: a. Cause was multiple lightning strikes in the area causing multiple lines to trip and automatically reclose. BPA reports no damaged equipment. Grid voltage has remained at 540KV and stable. 230/115 kv grid has not been involved. RAS was not initiated. <I> **** Actions Taken **** Reset alarm per ARP, contacted Dittmer dispatch
397860 | CR | 20190810 | CAQ | D | Unexpected MCR annunciator P840-A5 8.2 | Y | N |  | N | YES | <D> **** Detailed Description **** Upon start of SW-P-1A, alarm P840-A5 8.2 "Spray Pond A Temperature High" alarm locked in. The alarm high setpoint is 72F. Pond A temperature on SW-TI-1A and SW-TI-1C remained at 70F. Per the ARP, local pond temperatures from SW-TI-2A were averaged to 70.75F (72/73/69/69 on each channel). <I> **** Actions Taken **** Discussed with CRS and other control room operators. | 02-00-SW-TS-1A
397862 | CR | 20190810 |  | 3 | PDIS-MON-GDS1 locked up on grey screen | N | N |  | N | YES | <D> **** Detailed Description **** PDIS-MON-GDS1 locked up the screen is currently grey with the loading symbol swirling. The screen is not responding to operator commands. <I> **** Actions Taken **** Wrote CR Informed CRS (after 10 min the screen returned to normal. Still recommend investigating to determine cause.) <N> GDS restored itself to service about 10 minutes later. Currently functioning, however the "Reactivity" button is yellow, with no apparent cause. | 02-00-PDIS-MON-GDS1
397863 | CR | 20190810 |  | 4 | Computer Point X441 Erratic | N | N |  | N | YES | <D> **** Detailed Description **** The X441 computer point for drywell pressure low range division 1 has become erratic. See attached EDMS for trend with division 2 point (X361). This point impacts GDS but not ERDS. Recommend calibration. <I> **** Actions Taken **** Notified CRS and submitted CR. | 02-00-TDAS-MUX-13
397864 | CR | 20190810 |  |  | TDAS-MUX-8 Failure |  |  |  | N | YES | <D> **** Detailed Description **** On the PPC | 02-00-TDAS-MUX-8
397866 | CR | 20190810 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 240 B: 237 C: 241 E-TR-B A: 120 B: 120 C: 119 The following sensors were tripped and are reset: J7 500KV N BPA reports the following: The cause was momentary single pole relay of 500KV Shultz-Raver #3, no damaged equipment, the line reclosed, no damage, no RAS initiated, and no change in grid frequency. <I> **** Actions Taken **** Recommend trending
397867 | CR | 20190810 | CAQ | D | DW Annulus Exceeds 150F | Y | Y |  | N | NO | <D> **** Detailed Description **** This CR satisfies RFO 1.7.1 action A.2. Sacrificial Shield Wall Lower/Mid Annulus average temperature exceeds 150F. Per note 19 of Table 1.7.1-1.10.d LCS 1.7.1 is not met. Reference CR 397509 and 397676 for previous entries. <I> **** Actions Taken **** Notified CRS and entered RFO 1.7.1 required compensatory measures. <N> Cross referenced CR 397509 was initiated for the same reason as this CR. Assignment 03 in 397509 is evaluating the potential effect of the high DW Annulus temp on equipment in the area. This CR can be closed to CR 397509.
397868 | CR | 20190810 |  | 4 | Received Oscillograph Started alarm. at 1753. | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. The alarm was due to the J7 sensor [500kV Neutral Ground Overcurrent]. The J7 sensor has been reset. E-TR-S and E -TR-B voltages are 240/238/240 kV and 121/120/119 kV respectively. BPA Dittmer reports a momentary disruption at Wautoma/Rock Creek 500KV line and automatically reclosed. There was no initiation of the Remedial Action Scheme [RAS]. All plant controllers and equipment exhibited normal operation.
397869 | CR | 20190810 | CAQ | D | Received Oscillograph Started alarm at 2030. | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. The alarm was due to the J15 sensor [230KV undervoltage]. The J15 sensor has been reset. E-TR-S and E-TR-B voltages are 240/239/240 kV and 120/120/119 kV respectively. BPA Munro reports that the Potholes - Sand Dunes 230 KV line relayed off and on due to a momentary lightning fault. Did not affect power to CGS from either 230 kV or 115 kV power supplies. No damage or RAS in place. All plant controllers and equipment exhibited normal operation.
397871 | CR | 20190810 |  | 4 | CR small CT printer does not work | N | N |  | N | YES | <D> **** Detailed Description **** small CT printer in MCR has ribbon out fault when full of ribbon. Fault will not stay reset. <N> **** Equipment Description **** MCR small CT printer
397872 | CR | 20190811 |  | 4 | Received the "OSCILLOGRAPH STARTED" alarm at 0231 | N | N |  | N | NO | <D> **** Detailed Description **** Received the "OSCILLOGRAPH STARTED" alarm due to 500KV neutral OC (J7) which has been reset. BPA reports that the Lower Monumental-Hanford line relayed off and then back on. Plant Inverters, Hotwell and Feedwater heater controllers and Containment Vacuum Breakers exhibited normal operations. The 115 Kv and 230 Kv portions of the grid were not affected. TR-S and TR-B voltages are 240/238/240 kV and 120/120/118 kV
397873 | CR | 20190811 |  | 4 | Received the "OSCILLOGRAPH STARTED" alarm at 0340 | N | N |  | N | NO | <D> **** Detailed Description **** Received the "OSCILLOGRAPH STARTED" alarm due to 500KV neutral OC (J7) which has been reset. BPA reports that the Lower Monumental-Hanford line relayed off and then back on. Plant Inverters, Hotwell and Feedwater heater controllers and Containment Vacuum Breakers exhibited normal operations. The 115 Kv and 230 Kv portions of the grid were not affected. TR-S and TR-B voltages are 240/239/240 kV and 121/120/119 kV.
397877 | CR | 20190811 | CAQ | C | LD-TE-3E at its alarm setpoint | Y | Y |  | N | YES | <D> **** Detailed Description **** On 8/6/2019 LD-TRS-608 point 12 alarmed at 125 degrees. ARP actions followed, CRO temporary log established. LD -TE-3E continues to read about 125 degrees (RWCU HX pipe area) all other RWCU rooms have steady temperatures. CR generated for trending and also to request and evaluation of elevated temperatures in the RWCU HX room. | 02-00-LD-TE-3E
397878 | CR | 20190811 | CAQ | D | Received the "OSCILLOGRAPH STARTED" alarm at 0530 | N | N |  | N | NO | <D> **** Detailed Description **** Received the "OSCILLOGRAPH STARTED" alarm due to 500KV neutral OC (J7), SM-8 undervoltage (J12), and 230KV Undervoltage (J15) and main generator negative sequence which have been reset. BPA reports that the multiple 500KV lines relayed off and then back on. Plant Inverters, Hotwell and Feedwater heater controllers and Containment Vacuum Breakers exhibited normal operations. The 115 Kv and 230 Kv portions of the grid were not affected. TR-S and TR-B voltages are 240/239/240 kV and 121/120/119 kV. <I> **** Actions Taken **** Wrote Cr Informed CRS
397879 | CR | 20190811 |  | 4 | RWCU-V-34 Gasket Leakage has Increased Significantly | N | N |  | N | YES | <D> **** Detailed Description **** CR 397070 written on 7/22/19 identified ~14 drops per minute leaking from the body to bonnet flange of RWCU-V-34. WR 29150604 was updated 8/9/19 stating the leak has increased significantly to approximately 0.5 gallons per minute. Investigation today showed the leak has continued to get worse and is now about 1 gallon per minute. Most of the leak is contained by the installed catch and Tygon tube however some water is now splashing outside of the catch and depositing onto the floor. <I> **** Actions Taken **** CRS/SM Informed. Ops2, IA and HP were dispatched to RWCU -V-4. Dose rates near the valve are ~2 mrem/hr. Water on the floor does not appear to be spreading fast. Current puddle surface area is about 4 square feet. Indications of severe degradation of the flange gasket. . This leak was OSCR'ed in to and worked in R24 under WOT 02109737-01 and 0205068801. The valve was disassembled, repaired, and reassembled with a new body to bonnet gasket with fasteners torqued to 320 ft-lbs. Additionally the wedge was pulled, a new wedge was machined, blue checked and installed. The valve was repacked on reassembly. Now two months after the work was done the leakage is worse than before. Also, RWCU-FCV-33 is leaking by in order for any pressure to be felt on RWCU-V-34. This valve was worked under WO 02119802 in April 2019 and leak checked in May 2019. Very disappointing that both of these valves require rework so soon. <N> **** Equipment Description **** RB 471' outside southwest elevator | 02-00-RWCU-V-34
397880 | CR | 20190811 |  | 4 | Water leaking on/around E-MC-5B | N | N |  | N | YES | <D> **** Detailed Description **** While hanging a clearance it was noted that a mall puddme had formed on the back east corner of E-MC-5B. Source of the water is belived to be from a seam under the galvanized tin sheeting between the Service building and the Mechanical shop. <I> **** Actions Taken **** Informed the infield supervisor and wrote this CR | 02-00-E-MC-5B
397881 | CR | 20190811 |  | 3 | DBAI 2019 NRC Question on RHR-P-2A MOD impact to DG1 | Y | N |  | N | NO | <C> RISK: Medium. CAUSE: Uncertain. Severity B - Investigation Template. .... MRT Change: CR 397881 Moved to AR- OPSMGT. <D> **** Detailed Description **** Background â€“ RHR-P-2A motor and pump were replaced per EC 14635 under WO 02033672 in December 2018. RHR-P-2A post modification testing and operability testing were performed by PPM 18.1.34 per WO 02033672-55. EC 14635 documents an evaluation of the impact to DG1 due to the modification. Specifically: 1) CMR 14751 against calculation E/I-02-91-03 shows that during LOOP and LOOP with LOCA conditions the steady state load is below the DG1 rating of 4400kW and 2) CMR 15837 against calculation E/I-02-16-02 verifies the load acceptance function of DG1, the starting function against the onsite emergency AC power source, and the effect of load rejection on DG1. The NRCâ€™s contention is that post modification testing was completed SAT, however they are challenging the use of analysis for operability of DG-1 and they feel that integrated testing of DG-1 should have been performed during R24 to complete operability testing following the modification. The surveillance frequency of integrated testing was extended to 4 years in April 2019 and so Division 1 integrated testing was not performed in R24 and therefore the NRC believes we are not in compliance with SR 3.0.1. Division 1 integrated testing will occur in R25. <I> **** Actions Taken **** SM, licensing notified. <N> CR Bring Back - Operations to gather more information, and to get other teams involved for final determination. Rescreen on 8/27/2019 OFM agreed to level 3 per attribute notes. HUIT assignment changed to ASGN . CR reopened to edit priority.
397882 | CR | 20190811 | CAQ | D | Rain leaking through roof into DG3 | Y | N |  | N | YES | <D> **** Detailed Description **** Rain is leaking through the roof access hatch onto the floor near the south end of HPCS-GEN-DG3 forming a 3 foot puddle. <I> **** Actions Taken **** Informed SSS | 02-00-HPCS-GEN-DG3
397883 | CR | 20190811 |  | 4 | DSA-DY-1A Desiccant film creating a slip hazard | N | N |  | N | YES | <D> **** Detailed Description **** The water/film desiccant byproduct which is blown down into a scupper from DSA-DY-1A is misting back out and spreading over the cable tray above causing it to rust. The film has also settled on the surrounding floor and white iron creating a slip hazard. Attempts to wipe it up just smeared it around. The right cleaner needs to be used to break up the film. The cable tray and wiring needs to be evaluated for deterioration. <I> **** Actions Taken **** Informed SSS | 02-00-DSA-DY-1A
397884 | CR | 20190812 | CAQ | D | FP-V-62 leaks by seat | N | N |  | N | YES | <D> **** Detailed Description **** during system isolation FP-V-62 was shut but pressure returned to the system when FP-V-SGT/26 was allowed to shut. Pressure returned slowly indicating FP-V-62 was leaking by. <I> **** Actions Taken **** stopped all work | 02-00-FP-V-62
397888 | CR | 20190812 |  | 4 | Flocculator Effluent Pump Found Tripped | N | N |  | N | YES | <D> **** Detailed Description **** Motor Controller for PWC-P-120 was found tripped <I> **** Actions Taken **** Initiated CR and informed MCR | 02-00-PWC-42-FP1B
397889 | CR | 20190812 |  | 4 | WBCM Detector Damage Not Reported to Radiological Operations | N | N |  | N | NO | <D> **** Detailed Description **** The ARGOS 5AB model whole body contamination monitor (WBCM) was found with a damaged detector. The detector, metal screen, and mylar cover were punctured. The puncture was then covered with a piece of red duct tape with the writing "screen ripped - SHARP." Neither the puncturing of the detector nor the application of the tape covering were reported to radiological operations. The WBCM removed itself from service as expected. <I> **** Actions Taken **** I&C replaced the damaged detector. The unit was response checked and placed back into service. The damaged detector was ultimately relocated to the radiological operations office for further assessment.
397890 | CR | 20190812 |  | 3 | HWC Alarm | N | N |  | N | NO | <C> MRT Change: CR 397890 Severity moved from 4/Trend Repair to Severity 3 assigned to AR-EFIN. <D> Received a PC SYS-STAT Trouble alarm on HSSF-CAB-CHEM in the 487' chemistry lab. This is in conjunction with an unplanned isolation of YV-170. <I> Informed the CRS and wrote a CR per CI-14.4.
397891 | CR | 20190812 |  | 3 | CI-1.6 Managing Chemistry Department Quals requires revision |  |  |  | N | NO | <D> **** Detailed Description **** CI-1.6 requires a revision. Review procedure for applicable revisions. At a minimum, Attachment 6.1 needs to be revised to be in alignment with the chemistry technician qualification directory (5.1). <I> **** Actions Taken **** Initiated condition report. Informed chemistry and training supervision.
397895 | CR | 20190812 |  | 4 | MT&E Found Out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0053525 Tektronix Oâ€™Scope- model 3032B found OOT & needs adjustment. Not used during Calibration cycle. DEF #7164A written. No Plant Impact. No Action Required.
397897 | CR | 20190812 |  | 4 | 10 Pieces of M&TE Suspended until R25 |  |  |  | N | NO | <D> **** Detailed Description **** 10 Pieces of M&TE have Passed Calibration and have NOT been used during Calibration cycles. No Plant Impact. Suspended until R25. See list for Calcodes, Descriptions, Models & associated DEF #'s for each. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
397898 | CR | 20190812 |  | 4 | CL-TK-11 small leak at fill pipe fitting | N | N |  | N | YES | <D> **** Detailed Description **** The 2" fill pipe at CL-TK-11 (one of three new tanks added for the De-Halogenation system at CWPH) has a small leak at the elbow fitting at the bottom of the tank. (see attached pictures). The threaded connection appears to have leaked residual from when the pipe was used for filling the tank. Chemical is FOAMTROL AF1090, Chemical Permit# 1758 (anti-foaming solution) NOTE: attached pictures taken after recent rain - other than drop below fitting and connection moist, no active leak (drops per minute) can be seen. <I> **** Actions Taken **** Wrote CR <N> E&RP walked down the elbow fitting on CL-TK-11 and noted a puddle below the fitting. The puddle is completely contained on the conrete and does not pose a threat to the enviornment at this time. It is not reportable to outside agencies. | 02-00-CL-TK-11
397899 | CR | 20190812 |  | 3 | 2019 DBAI - Calculation CE-02-87-29 Requires Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** PPM 10.2.53 provides requirements for erection of scaffolding to preclude adverse interactions with plant components especially during a design seismic event. The analyses documented in CE-02-87-29 provides the bases for these requirements of PPM 10.2.53 for restrained scaffolds. During DBAI, a NRC inspector inquired about the basis for the minimum 2â€ clear distance specified in PPM 10.2.53 and the analysis in CE-02-87-29 which validated this dimension. While the appropriate SMEs could provide the link between the analysis in CE-02-87-29 and the requirement in PPM 10.2.53, this relationship between the two documents would not be as easily identified by less knowledgeable personnel. Expectation for any calculation is that the results should be self-evident to an informed observer/reader of the analysis. Therefore, CE-02-87-29 requires revision to clearly document the basis for the 2" clear distance called out in PPM 10.2.53. This is a documentation issue only. Scaffolds installed per PPM 10.2.53 are still seismically qualified for all areas of the plant. <I> **** Actions Taken **** 1) Discussed with other SMEs 2) Initiated this CR for calculation revision 3) Provided response to NRC
397902 | CR | 20190812 |  | 3 | PPM 10.4.1 needs enhanced |  |  |  | N | NO | <D> **** Detailed Description **** Precaution and limitation 4.9 states the only qualified operators are to operate/inspect/test cranes. This limits the electrical craft from performing this procedure. And places unnessesary restrictions on electrical support task. <I> **** Actions Taken **** contacted supervision and shift manager. obtained permission to n/a P&L 4.9 for electrical support task. wrote cr <N> **** Equipment Description **** MT-HOI-40 ***General Notes*** An assignment has been made under the Maintenance procedure revision data base. No further actions is needed for the Procedure revision. A link to the data base has been added to the EDMS of this AR.
397903 | CR | 20190812 |  | 3 | ABN-BACKPRESSURE Procedure Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** ABN-BACKPRESSURE should contain a step to secure hydrogen water chemistry (HWC) at CRS discretion; similar to SOP -AR-OPS step 5.5.1 and 5.6.1. Securing HWC limits the inflow of non-condensable gases into the main condenser allowing the operating crew more time to deal the issue causing high backpressure; similarly securing HWC during SJAE shifts directed by SOP-AR-OPS.
397905 | CR | 20190812 |  | 4 | MCR floor tile in lifting up | N | N |  | N | YES | <D> **** Detailed Description **** MCR carpeted floor tile in front of H13-800-C4 is lifting up causing a potential trip hazard. The floor tile was duct taped down to prevent someone from tripping on the tile. Recommend repairing floor tile. <I> **** Actions Taken **** Wrote CR Informed CRS/SM <N> **** Equipment Description **** MCR carpeted floor tile in front of H13-800-C4
397906 | CR | 20190812 |  | 4 | AS-PI-1C found out of tolerance | N | N |  | N | YES | <D> **** Detailed Description **** AS-PI-1C was found out of tolerance high and low throughout it cardinals points and also exhibited too much hysteresis which made it impossible to calibrate to within specifications. <I> **** Actions Taken **** notified supervision and ops | 02-00-AS-PI-1C
397909 | CR | 20190812 |  | 4 | H2 Water Chemistry Alarm (PC SYS STAT TROUBLE) | N | N |  | N | YES | <D> **** Detailed Description **** Recieved the following alarms from HSSF-CAB-CHEM/LAB: PCP TROUBLE ALARM (PC SYS-STAT TROUBLE) which is a high priority alarm, VAPORIZOR A OUTLET PRES. STATUS INCICATI (HS PAH408-STAT HIGH) which is n abnormal priority and PUMP B OUTLET PRES. ALRM HIGH STATUS (HS PAH418-STAT HIGH) which is an abnormal priority. All alarms state the a Tele Tank message was sent to the vendor. <I> **** Actions Taken **** Chemistry supervision informed. MCR/CRS informed. CR written per HSSF-CAB-CHEM/LAB (CI-14.4). | 02-00-HSSF-CP-P1
397910 | CR | 20190812 |  | 4 | Received H2 WTR CHEM TROUBLE, H13-P840.A3.7-6, alarm. | N | N |  | N | YES | <D> **** Detailed Description **** Received H2 WTR CHEM TROUBLE, H13-P840.A3.7-6, alarm, due to SUPPLY FACILITY TROUBLE. OPS3 reports that the H2 WTR CHEM TROUBLE, H13-P840.A3.7-6, alarm is due to SUPPLY FACILITY TROUBLE, and that the HMI shows PC SYS -STAT TROUBLE, HS PAH408-STAT HIGH, and HS PAH418 -STAT HIGH. HSSF-V-YV170 indicates OPEN. Dispatched an extra EO to HSSF to respond per 4.500.2-7. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR's. | 02-00-HSSF-P-1A,02-00-HSSF-P-1B
397911 | CR | 20190812 | CAQ | D | FP Pipe 10â€FP(2)-1 Requires Replacement | N | Y |  | N | YES | <D> **** Detailed Description **** Review of PMID 00022694, FP-V-33, PIPING UT EXAM, indicates loss of pipe wall thickness probably due to flow accelerated corrosion during 18 month PPM 15.4.8 pump flow tests and general corrosion. The nominal wall thickness for schedule 40 10 inch pipe is 0.365. The latest data indicates the pipe wall thickness is 0.135 which is trending downward. Action level to replace this pipe is 0.200. . 10â€FP(2)-1 FP pipe needs to be replaced immediately downstream of FP-V-33. This pipe transitions through the floor into the Circulating Water Basin, from FP-V-33 and is open to the atmosphere of the basin. . This does not affect functionality of the circulating water fire pumps (FP-P-1, FP-P-2B, FP-P-2A) because the 10â€F P(2)-1 FP pipe is only utilized in the PPM 15.4.8 (18 month) test configuration/lineup. . Recommend replacement during R25 when CW Basin is drained. Reference M515-1, 215-00,1268, and PMID 22694. <I> **** Actions Taken **** Contacted Shift Manager, Initiated CR. <N> **** Equipment Description **** P -450- - -X3/4.9 - | 02-00-FP-V-33
397912 | CR | 20190812 | CAQ | C | Effluent monitor set point calculations not updated with ODC | N | Y |  | N | NO | <D> **** Detailed Description **** This does not impact plant operations or the ability to declare an emergency classification. During focused self -assessment 376387, the ODCM alarm set point calculations for the WEA and TEA noble gas monitors were found to be using outdated information. These calculations should be updated to reflect the values currently in the ODCM. See below for additional details. Table 3-3 in the ODCM was revised in amendment 51, Dec 2013, and again via Amendment 55, Aug 2016. The dispersion coefficients, X/Q, for radioactive gases and particulates leaving the REA, WEA, and TEA systems were updated based on new meteorological data. During F-SA 376387, it was found that the set point calculations for the alarm levels on the WEA and TEA noble gas monitors DO NOT reflect these updated X/Q values. The set point calculations cite Table 3-3 in the ODCM, , but the values of X/Q in these calculations are from an ODCM revision prior to amendment 51 (Dec 2013). The current X/Q values are significantly different from the historical values used in the set point calculations for WEA and TEA, however; the values used are consistent with making an accurate EAL determination. The set point calculation for REA has been updated to reflect the current X/Q values in ODCM table 3-3. The changes to the X/Q values for WEA and TEA in this amendment would have changed the calculated set points for the noble gas monitors in WEA by a factor of 2x, and TEA by a factor of 50x. The emergency action limit (EAL) for an unusual event (UE), is defined in NE-02-09-12 as being 2x the ODCM HI ALARM. If the TEA set point were increased by a factor of 50x, then the threshold for a UE in the TEA system would have been greater than the EAL threshold for an Alert due to the different methodology in determining these EALs: the UE is defined as 2x the ODCM HI ALARM or as determined by PPM 16.14.1, while the other EALs are determined using RASCAL. CR 00312036 was written to evaluate the impact of changing the ODCM table 3-3 values, particularly the impact on the EALs. This CR eventually resulted in a change to procedure PPM 16.14.1, the Gaseous Monitor Setpoint Determination procedure. This change, 16.14.1 Rev 5, added step 5.6 to â€œverify setpoint(s) are compatible with calculation NE-02-09-12 and Emergency Preparedness EALs.â€ The procedural change would require documenting reasons for any discrepancies between the calculated set point, the implemented set point, and the UE EAL as already determined. After the procedural change was implemented and CR 00312036 was closed, the set point calculations for TEA and WEA were never updated. <I> **** Actions Taken **** Notified Reactor Engineering, Emergency Preparedness, Licensing, Chemistry Management and the Shift Manager. The calculations for WEA (NE-02-08-08) and TEA (NE-02-08-09) should be updated via PPM 16.14.1 to reflect the changes to X/Q in ODCM table 3-3 and/or the considerations made as required by PPM 16.14.1 on the impact to the EALs. Recommend assigning to AR-RXENG to update NE-02-08-08 and NE-02-08-09.
397913 | CR | 20190812 |  | 3 | R25 SOP-ELEC-PP7AA-MAINT procedure change. |  |  |  | N | NO | <D> **** Detailed Description **** Multiple editorials and changes, PRM EC 11288 changed power supplies, RPIS rod position changed power supplies. Uploaded mark-up in EDMS. <I> **** Actions Taken **** Wrote CR
397916 | CR | 20190812 |  | 4 | Appliance found plugged into an extension cord. |  |  |  | N | NO | <D> **** Detailed Description **** While performing a walk down of bld. 32 a portable air conditioning unit was found running while plugged into an extension cord. This goes against ISPM-6, Electrical Tools, Appliances and Extension Cord Use. This unit should have been plugged directly into a receptacle. <I> **** Actions Taken **** Unplugged extension cord and found a new recepticle that the unit could be plugged directly into. Initiated CR. <N> Williams Plant Services.
397917 | CR | 20190812 |  | 4 | Lighting poor in DG1 engine room | N | N |  | N | YES | <D> **** Detailed Description **** There are many fixtures in DG1 engine room that are completely out, causing the room to be dimly illuminated. Please replace burned out lamps to return room lighting to normal for safety. <I> **** Actions Taken **** Notified SMgt, wrote CR. Non-essential lighting <N> **** Equipment Description **** DG1 engine room lamp fixtures.
397918 | CR | 20190812 |  | 4 | Scaffold no longer needed; please disassemble. |  |  |  | N | NO | <D> **** Detailed Description **** There is a scaffold erected in RW 525 chiller room for AOA-V-51A maintenance. The scaffold was erected with a date of 3/19/19, and it appears maintenance is done. Please remove this scaffold for easier access to exhaust fans. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 525 by CR toilet exhaust fan.
397921 | CR | 20190812 |  | 3 | Noble Gas Detector HVPS Setting too high |  |  |  | N | YES | <D> **** Detailed Description **** Two noble gas detectors for the Containment Drywell Rad Monitor purchased under PO 341993 (part number 03602341 -001) had HVPS Settings that were too high. Serial numbers 10003 and 10004 had HVPS settings provided on the GA Transfer Calibration of 1925 VDC and 1940 VDC, respectively. According to the manual, the max operating voltage is 1880 VDC. Both detectors will need to be returned to GA for repair. <I> **** Actions Taken **** Talked to vendor on path forward Equipment not installed in plant. | 02-00-CMS-RE-12/3A,02-00-CMS-RE-12/3B,02-00-CMS-SR-20,02-00-CMS-SR-21
397922 | CR | 20190812 |  | 4 | bee stung employee in hand |  |  |  | N | NO | <D> **** Detailed Description **** At approximately 1020 an EN employee walking from the ENOC maintenance shop along the lay down yard fence was stung on the pinky finger of the right hand. <I> **** Actions Taken **** EN employee notified supervisor, employee elected self administered first aid, Supervisor notified department manager of incident and this CR was generated.
397923 | CR | 20190812 |  | 4 | Main Turbine Bearing 4 increase in vibration amplitude | N | N |  | N | YES | <D> **** Detailed Description **** Vibration on Bearing 4 (LPA, West end) has displayed an upward trend in amplitude. The peak to peak levels were in the range of 4 mils, but has since trended up to approximately 5 mils. There was a possible initiating event in the afternoon of 25July2019 when a few bearings showed a small abrupt downward shift; however, the upward trend was not apparent until about the first weekend of August2019 when a potential second initiating event the afternoon of 02Aug2019 revealed the trace broke out of its normal range. See image in EDMS. Vibration amplitude data for Bearing 4 was not able to be obtained during the last vibration data collection efforts due to a failed output on TG-MON-VB4 as documented in CR AR 397478. This CR is for early warning of the trend and no action is needed at this time [ARP and OCC-03 actions are at 7 mils, NEIL reporting begins at 6 mils]. <I> **** Actions Taken **** reviewed additional data, informed supervisor and manager <N> **** Equipment Description **** Brg 4 located on LPA, West end | 02-00-MS-DT-1A
397924 | CR | 20190812 | CAQ | D | Unexpected Alarm - Rod Drive Control System Inoperable | Y | Y |  | N | YES | <D> **** Detailed Description **** Alarm 4.603.A7-2.8 "Rod Drive Control System Inoperable" came in. No rods drifted and ABN-ROD was not entered. See EDMS for a picture of the Fault Location Map/Analyzer. RDCS was able to be reset per the ARP. A System Error was indicated on the Rod Worth Minimizer. The RWM was initialized per the SOP and the system returned to normal. <I> **** Actions Taken **** EDiscussed with CRS. Reset and restored the system per the ARP. | 02-00-CRD-DMM-1
397925 | CR | 20190812 |  | 3 | CRO1 tablet synchronization failure |  |  |  | N | NO | <D> **** Detailed Description **** received multiple synchronization failure alarms on the CRO1 tablet. Data appears to be transferred to the computer even though failure notification appears on tablet. this is a frequent unresolved repeat issue - ~ 1/2 of the time when uploading logs. <N> This issue is documented under the cross referenced CR 396151. Recommend NCAQ 4, closed to the original CR. 397925 and 398698 are the same issue as was previously documented in 397310. An eval assignment has been created on 398698 to fully evaluate all CRs in the XCREF to assess what actions are needed to correct the issue. This CR has ITBOA- SUPV approval to close with notes and XREF the CR that is adressing the issues identified under on CR. No further actions under this CR.
397926 | CR | 20190812 |  | 4 | Caution Tag printer in the main control room doesn't work |  |  |  | N | NO | <D> **** Detailed Description **** The Caution Tag printer in the main control room doesn't work. When the machine goes through the self-calibration cycle, it ends with an "Out of Media" message. The printer is loaded correctly per the manual, and this appears to be a sensor issue according to the Troubleshooting section. <I> **** Actions Taken **** As noted above <N> **** Equipment Description **** Caution tag printer in the Main Control Room
397927 | CR | 20190813 |  | 4 | Main Transformer TR-M3 Trouble alarm | N | N |  | N | YES | <D> **** Detailed Description **** Alarm 4.800.C4-3.1 Main Transformer TR-M3 Trouble alarm came in. OPS4 was dispatched, locally Cooler Group 2 Failure alarm was in. The Fan 5 contactor was cycled and the alarm reset. <I> **** Actions Taken **** Per the ARP and ABN-TRANSFORMER Outside temperature 64.2F. | 02-00-E-RMS-M3/43/2
397928 | CR | 20190813 |  | 4 | OPS 4 truck has headlight out |  |  |  | N | YES | <D> **** Detailed Description **** The operations (OPS 4) pickup has a RF headlight out. <I> **** Actions Taken **** Informed SSS <N> **** Equipment Description **** O441 Parking Lot
397929 | CR | 20190813 |  | 4 | SEC-XR-02 | N | N |  | N | YES | <D> **** Detailed Description **** SEC-XR-02 not functioning as intended. Please call 2185 for details. <I> **** Actions Taken **** SEC-XR-02 was taken out of service and CR/WR was generated. <N> **** Equipment Description **** PAAP | 02-00-SEC-XR-2
397930 | CR | 20190813 |  | 3 | Contaminated Tools in the Main Tool Crib |  |  |  | N | NO | <D> **** Detailed Description **** Discovered loose contamination above limits on tools in the MAin Tool Crib RW 467' during routine weekly M&TE transfer prep survey for both fixed contaminated and non -contaminated tools. <I> **** Actions Taken **** Controlled the tools by bagging and tagging in RAM bags for future decontamination. Informed Lead HP Tech. Performed EOC followup survey of all areas where these tools are stored. Submitted VSDS survey. Modified Weekly M&TE transfer inventory lists in the appropriate containers. Informed Main Tool Crib attendant.
397934 | CR | 20190813 |  | 3 | PPM 16.11.2 requires a procedure enhancement. |  |  |  | N | NO | <D> **** Detailed Description **** PPM 16.11.2 requires a procedure enhancement. In step 7.10.3, the step that the technician would evaluate the monitor reading is supposed to be identified as step "b." The way that it currently reads, it is part of step "a," but should be its own stand-alone step. Previous procedure steps that are similar in nature are formatted in the manner that I am recommending. <I> **** Actions Taken **** Informed procedure sponsor and submitted condition report.
397937 | CR | 20190813 |  | 4 | Monthly Chemical Storage area inspection discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** The monthly inspection of Mechanical Maintenance chemical storage areas discovered the following discrepancies: Chemicals found outside of flammable liquid storage cabinet in Bldg 194. North Light burned out in Bldg 116. <I> **** Actions Taken **** Notified appropriate personnel to resolve. All discrepancies resolved, no further action required.
397938 | CR | 20190813 | CAQ | C | Analysis basis LCO 3.4.4 Safety/Relief Valves (SRVs) | Y | N |  | N | NO | <D> **** Detailed Description **** This CR identifies a legacy, analysis issue for LCO 3.4.4 Safety/Relief Valves (SRVs) - < 25% RTP. The analysis of record for LCO 3.4.4 (NE-02-94-66) has not been validated for changes to the core and fuel design, cycle length and Measurement Uncertainty Re-capture (MUR) power uprate. . There is reasonable assurance of operability based on engineering judgement. An update to the analysis of record to address the CR will return acceptable results based on the following: . NE-02-94-66 (Sheet 23) documents large margin to the ASME Code limit (1375 psig reactor vessel pressure) and the dome pressure safety limit (1325 psig) of SL 2.1.2 Reactor Coolant System Pressure SL. . The limiting transient for rated power and 25 %RTP is MSIV closure with direct scram failure (i.e., valve position switch failure). NE-02-94-66 documents that the limiting transient at 25 %RTP with four required-operable SRVs is less severe than the rated power transient with 12 required-operable SRVs (per LCO 3.4.3 Safety/Relief Valves (SRVs) - ? 25% RTP). The rated power transient analysis for the current operating cycle demonstrates margin to the ASME Code limit and dome pressure safety limit. . The rated power transient is analyzed for each cycle as documented in the Supplemental Reload Licensing Report (CVI 981-01,5). . Therefore, there is reasonable assurance that LCO 3.4.4 ensures that four required-operable SRVs will protect the ASME Code limit and the dome pressure safety limit. . Past Operability is not a concern because greater than four SRVs have met the surveillance requirements of the LCO currently and for the preceding three years. The analysis of record documents that the limiting transient for rated power bounds the transient at 25 %RTP. The limiting transient at rated power is updated for each cycle as documented in the Supplemental Reload Licensing Report. Therefore, the CR does not represent an unanalyzed condition. <I> **** Actions Taken **** Recommend assignment to AR-RXFUEL to update/replace NE-02 -94-66. Extent of condition review, Bases references to NE-02-94 -66, is documented in CR(s) on the cross-references panel. . Note that NE-02-94-66 is NOT referenced in TS 3.4.3, Safety/Relief Valves (SRVs) - Greater than or Equal to 25% RTP.
397939 | CR | 20190813 | CAQ | C | EOC Bases references to NE-02-94-66 | N | N |  | N | NO | <D> **** Detailed Description **** CR 00397938 identified that calculation NE-02-94-66, for MSIV closure with direct scram failure, was not maintained current. Bases B 3.4.4 Safety/Relief Valves (SRVs) - < 25% RTP references NE-02-94-66. An extent of condition review evaluates other Bases and license basis documents, which reference NE-02-94-66. . B 3.3.1.1 Reactor Protection System (RPS) Instrumentation references NE-02-94-66, for Function 3. Reactor Vessel Steam Dome Pressure â€“ High, but states, â€œNo specific safety analysis takes direct credit for this Function.â€ CGS introduced a specific safety analysis in support of Facility Operating License No. NPF-21, Amendment 90 (GI2 -90-074). Bases for Function 3 of B 3.3.1.1 should be updated to reflect this change. B 3.3.1.1 Function 5. Main Steam Isolation Valve â€“ Closure should be updated to reference Function 3 as well as Function 2.c. Average Power Range Monitor Neutron Flux - High Function, consistent with Amendment 90. . B 3.4.4 Safety/Relief Valves (SRVs) - < 25% RTP APPLICABLE SAFETY ANALYSES description should be updated to reflect Amendment 90, which credits RPS Function 3. Reactor Vessel Steam Dome Pressure â€“ High at 25 %RTP. <I> **** Actions Taken **** Recommend assignment to AR-RXFUEL to update Bases to reflect license amendment 90 and CR 00397938.
397940 | CR | 20190813 | CAQ | D | Received 4.603.A7 Rod Accumulator Trouble for HCU 5435 | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02146548, marked completion required box, then taken back to complete <D> **** Detailed Description **** Received 4.603.A7 Rod Accumulator Trouble for HCU 5435. Alarm due to accumulator low N2 pressure. Recharged. <I> **** Actions Taken **** Wrote Cr Informed CRS | 02-00-CRD-HCU-5435
397942 | CR | 20190813 |  | 3 | ESOMS issue SPC logs not calculating RO1 logs correctly |  |  |  | N | NO | <D> **** Detailed Description **** SPC quarterly and yearly logs not calculating correctly for RO1 daily logs and must be manually recalculated every day for the logs to correctly calculate. Even then it appears that the yearly SPC hours are counting down and not adding to the year to date logs. Recommend investigating and correcting the issue <I> **** Actions Taken **** Wrote CR Informed CRS <N> ITBOA Supervisor approved extending this CR as an inquiry into the calculation, the error could probably be with the SUMLASTX function utilized in the expression.
397944 | CR | 20190813 |  | 4 | Correct PPM 15.4.5, Penetration Seal Installation |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing PPM 15.4.5, Penetration Seal Installation and Maintenance, it was discovered that numerous items need to be corrected. The items that require correction are on page 2 where the revisions are listed. The pages and the sections do not match the actual pages. These items will need to be corrected soon, as this Procedure is referred to on a regular basis by WPS Insulators. See EDMS for the attachment of the corrections needed. <I> **** Actions Taken **** Williams Insulators reviewed Procedure for corrections needed. <N> ***General Notes*** No further actions are required under this AR. An assignment has been created within the Maint. Procedure Revision Data base. A link has been added to the EDMS of this AR.
397945 | CR | 20190813 |  | 4 | Wrong oil ordered for DG-4 annual maintenance | N | Y |  | N | YES | <D> **** Detailed Description **** During the performance WO 02115248-01 E-GEN-DG4, ANNUAL MAINTENANCE it was discovered that the incorrect oil Mobil Delvac 1300 Super 15W-40 (Cat ID 16368) was ordered in lieu of Mobil Delvac 1 ESP 5W-40 per AR 384755 which currently there is no Cat ID. And no oil on site. <I> **** Actions Taken **** Notified MCR, WWM, mechanical component manager, planning, and contacted supply chain to pursue oil required. <N> ***General Notes*** Per Planning, SMS-AR, 384755 was created to revise the Model and Generated work order with the new oil. there are no further actions to take. All actions are being conducted within the proper processes. | 02-00-E-GEN-DG4
397949 | CR | 20190813 |  | 3 | E-DG-4 LCS 1.11.1 Late Entry | N | N |  | N | NO | <D> **** Detailed Description **** The LCS RFO 1.11.1 was not entered when DG-4 was tagged under L-DG4-ANNUAL-PM-001. This was identified the following shift and RFO 1.11.1.A was entered with a 90 day completion time. Standard practice is to declare equipment inoperable and/or non-functional when a clearance is hung on the equipment. <I> **** Actions Taken **** Entered LCS RFO 1.11.1.A and opened LCS sheet T19-E-GEN -DG4-001 for tracking. Notified SM. <N> Performance monitoring in place through shift manager.
397950 | CR | 20190813 |  | 3 | SCWE concern on initiating CRs |  |  |  | N | NO | <D> **** Detailed Description **** Overheard conversation in hallway that a manager had with their subordinate. The manager previously had a discussion with another manager that the employee had initiated a nuisance CR without going to their management first and getting the problem solved. The employee was not a team player by not allowing management to solve problems before initiating a CR. The manager then asked the employee their side of the story. The employee stated that they did bring it up multiple times in the past and nothing was done to resolve the safety and operability issues. The manager then told the employee not to initiate anymore CRs until they brought the issue to them first.
397951 | CR | 20190813 | CAQ | D | SLC Pentaborate Concentration reduced Chem Add needed | Y | N |  | N | YES | <D> **** Detailed Description **** The SLC pentaborate concentration has been slowing declining over the last year. The current sample was 13.66 %weight and the resample with increased sparge was 13.88% weight. The increased sparge obviously helped with mixing to increase the concentration but the steady decline is still evident. The concentration 4/2018 was 14.56% weight and it has been reducing ever since then. It is not clear where the boron is going. The scuppers were checked for leakage and there was no evidence of an on going leak. WO#02136898 was planned for a SLC add when it was first suspected of lowering concentration but it appeared to stabiliized for a while. It is evident that the lowering concentration is continuing at this point so if this work order is still usable it would be good to plan it into the schedule. <N> **** Equipment Description **** RX 548' | 02-00-SLC-TK-1
397952 | CR | 20190813 |  | 3 | Recommended change to ABN-RPS |  |  |  | N | NO | <D> **** Detailed Description **** Recommend changing ABN-RPS immediate action to IMMEDIATELY STOP all maintenance and surveillance testing, to a subsequent action to make a plant announcement to this effect. The immediate action does not add any value and in fact distracts operators from responding to the lost RPS bus. Making this a subsequent action would allow the CRS to prioritize the response to the transient more effectively. The subsequent action would insure that it is not dropped. <I> **** Actions Taken **** Wrote CR Discussed with AOM
397953 | CR | 20190813 |  | 3 | Recommended change to ABN-RWM |  |  |  | N | NO | <D> **** Detailed Description **** Recommend deleting ABN-RWM immediate action to THEN STOP all rod movement, except manual scram, AND COMPLY with Technical Specifications 3.3.2.1. This doesnâ€™t add any value and should be removed. The GIVE 2 process and normal annunciator response would tell you to stop rod movement and enter the tech specs. Also you should always be evaluating tech specs and enter anytime you no longer comply. If it is desired to keep these steps in the procedure they can be moved to a subsequent action. <I> **** Actions Taken **** Wrote CR Discussed with AOM
397954 | CR | 20190813 |  | 3 | Recommended change to ABN-Turbine |  |  |  | N | NO | <D> **** Detailed Description **** Recommend deleting the current immediate action of IF Reactor power is GT 25%, THEN VERIFY the Reactor has scrammed. Refer to PPM 3.3.1. IF Reactor power is LT 25%, THEN VERIFY the Bypass valves open. This is just verifying that an automatic action that should have occurred did occur. The setpoints are slightly different since the turbine trips at 29.5% power. Bases for this step tell you about instrument conservatism and that the plant may scram on high pressure due to the bypass valves only able to pass 25% steam. If this were to occur the likelihood of an operator being able to stop the automatic scram from occurring is minimal. The automatic high pressure scram would come in faster than an operator could react. If the plant was above 29.5% power and didnâ€™t scram on a turbine trip then PPM 1.3.1. would tell you that this should be just an automatic action that should have occurred but didnâ€™t occur. The second portion of this immediate action to verify the bypass valves open if reactor power is less than 25% is also covered in PPM 1.3.1 as an automatic action that should have occurred but didnâ€™t. <I> **** Actions Taken **** Wrote CR Discussed with AOM
397955 | CR | 20190813 |  | 3 | PPM 12.5.8 needs enhancement |  |  |  | N | NO | <D> **** Detailed Description **** In PPM 12.5.8, caution statements appear just prior to Step 7.3.6 (pg 12) and Step 7.4.6 (pg 14) giving guidance for maintaining minimim gas flowrate while conducting grab sampling of the containment atmosphere for SR-21, and SR -20, respectively. The note just prior to Step 7.3.6 identifies CMS-SR21-FE-1 as the indicator to verify flow, and the note prior to Step 7.4.6 identifies CMS-SR20-FE-1as the indicator to verify flow. A thorough walkdown of both sample rack rooms failed to identify any indicators with these EPN indentifiers. The sample racks are not original equipment. Propose to change the caution note prior to Step 7.3.6 to identify CMS-RIT-12B as the indicator to reference for SR-21, and the note prior to Step 7.4.6 to identify CMS-RIT-12A as the indicator to reference for SR -20. Note should include guidance to refer to the flow indication on the Current Activity screen for each of these
397956 | CR | 20190813 | CAQ | C | Activity Performed Without Required Qualification |  |  |  | N | NO | <D> **** Detailed Description **** Following maintenance to SAM-9 HP-EQ-42998 on 5/24/2019, the unit calibration was performed by an individual who did not carry the HPBJ qualification group for calibrating SAM-9, SAM-11, or BM-285 monitors. The monitor was used during R24 to check items entering the clean break area only. It was not used to free release items from the radiologically controlled area. The monitor is currently removed from service for at-power operations. The individual is qualified in qual group HPBS for calibrating SAM-12 models, which requires use of the same skills and knowledge. The calibration paperwork was reviewed by an individual qualified in qual group HPBJ and the as-left values met the calibration criteria. <I> **** Actions Taken **** Verified cal paperwork and qual groups. Discussed with HP management.
397957 | CR | 20190813 |  | 4 | (NRC Identified) Large insect nest at SWPH B |  |  |  | N | NO | <D> **** Detailed Description **** There is a large insect nest above the personnel access door into SWPH B. This was identified as a concern by the NRC. <I> **** Actions Taken **** Informed supervision. Wrote CR
397958 | CR | 20190813 |  | 3 | Supplies needed to complete WO 02138367-01 |  |  |  | N | NO | <D> **** Detailed Description **** In working to complete WO 02138367-01 it states to replace the old rubber shoe covers with new rubber shoe covers. However, there are no replacement rubber shoe covers to complete this WO. Plant laborers looked in Bldg 13 and the Unitech trailer where the supplies are located and none could be located. To complete this WO, 20 pairs of rubber shoe covers in size extra-large need to be ordered to be placed in the OSC cabinet. <I> **** Actions Taken **** Supervision was informed of the delta and they will be placing an order with Unitech to complete this delta. <N> Supplies have been received and restocked. No further action required per HP Supervision.
397959 | CR | 20190813 | CAQ | D | CR to track repair of defective equipment |  |  |  | N | NO | <D> **** Detailed Description **** Per 10.25.85 att.9.4 it is required to initiate a Work Request to track the defective equipment repair. The jumper number is #7, and it is logged into the TMR index log with WR 29150834 <I> **** Actions Taken **** Initiated CR/WR <N> **** Equipment Description **** 501RW
397963 | CR | 20190813 | CAQ | C | 2019 DBAI - PPM 10.2.53 Scaffold Log discrepancies |  |  |  | N | NO | <C> MRT Change: CR 397963 Severity 3 moved to Priority CAQ Severity C. <D> **** Detailed Description **** Apparent discrepancies exist between the AED D-SCAFFOLD-455 (Permanent Scaffold Schedule) drawing and the PPM 10.2.53 Scaffold Log. 1) Permanent Scaffold Tags 167, 1520, 1529, 1606, 1734, and 2920 per AED D-SCAFFOLD-455 do not exist in the Permanent portion of the PPM 10.2.53 Scaffold Log. Tag 1606 and Tag 2920 are listed in the Removed portion of the PPM 10.2.53 Scaffold Log. 2) Tag 2905 exists in the Permanent portion of the PPM 10.2.53 Scaffold Log but exists on AED D-SCAFFOLD-455 as Tag 553. 3) Permanent Scaffold Tags 1912 and 3298 per AED D-SCAFFOLD-455 exist in the Long-Term portion of the PPM 10.2.53 Scaffold Log rather than the Permanent portion of the PPM 10.2.53 Scaffold Log. 4) Tags 1676, 11381, and 16037 exist in the Permanent portion of the PPM 10.2.53 Scaffold Log but do not exist on AED D-SCAFFOLD-455. <I> **** Actions Taken **** This is an administrative configuration control issue only. Scaffold installations are per PPM 10.2.53 which provides direction ensuring they are within the bounds of the LBID review and generic bounding supporting analysis referenced in the procedure or receive the required Engineering inspection/review/approval (e.g., to provide the additional LBID review or analysis if required). This AR CR is not documenting any field configuration problem that might bring into question the continued functionality, operation, or qualification of any plant SSCs or any scaffolding installations in the plant. <N> These apparent discrepancies were identified while reviewing documentation associated with provision of an Engineering response to an NRC Inspector question for the 2019 DBAI.
397965 | CR | 20190813 |  | 4 | E-TR-M3 TRANSFIX GAS ANALYZER Caution Light Lit | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-M3 TRANSFIX GAS ANALYZER caution light is lit consistantly. <I> **** Actions Taken **** Wrote CR. | 02-00-E-AY-TR/M3
397973 | CR | 20190813 |  | 3 | PPM 10.2.13 Specifies incorrect oil for E-GEN-DG4 |  |  |  | N | NO | <D> **** Detailed Description **** PPM 10.2.13 â€œApproved Lubricantsâ€ Major revision 073 currently lists Mobil Delvac 1300 Super 15W-40 (MSDS REF -1603) as the approved lubricant for the diesel engine crankcase for E-GEN-DG4. Per AR 384755 and work instructions WO 02115248; Mobil Delvac 1 ESP 5W-40 is the correct lubricant to be used (same MSDS REF-1603). <I> **** Actions Taken **** Initiated CR to revise PPM 10.2.13
397976 | CR | 20190813 |  | 4 | SQL Server host ran out of resources during maintenance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The physical Cisco UCS blades dedicated to SQL Server ran out of resources (RAM/CPU) during Cisco UCS firmware maintenance, which affected some applications including Security Center (cameras), SecretServer, and ChangeGear. <I> **** Actions Taken **** Manually migrated virtual servers to free up resources. Re -synchronized databases and failed SQL AlwaysOn clusters back to primary data center. Recommend NON-CAQ 4.
397978 | CR | 20190813 |  | 3 | DW-DWS-4 doesn't shutoff after actuation | N | Y |  | N | YES | <D> **** Detailed Description **** Maintenace replaced shower valve and opened isolation valve. Pulled chain to activate water, upon releasing the chain the shower valve did not return to the closed position and continued to leak. Shut isolation and shower stopped leaking. Reopened isolation and the valve held closed. Removed shower head and hooked up a calibrated gauge to see what the pressure is on the line, gauge read a steady 118 psi. Manufacturer recommends no higher than 80 psi on the shower valve. Could be why the old shower valve would not shut after opening. <I> **** Actions Taken **** Caution Tag generated to Isolate DW-DWS-4 until issue is resolved. <N> **** Equipment Description **** RW 437 | 02-00-DW-DWS-4
397979 | CR | 20190813 | CAQ | D | CWPH in-line pH meter malfunctioning | N | Y |  | N | YES | <C> CR reopened to cross reference additional WR 29151283 marked completion required box, then taken back to complete <D> **** Detailed Description **** The CW in-line pH meter began to respond erratically at 1500 8/13/19. It spiked to 9.6, from 8.2, then precipitously dropped back down to 8.4 followed by another spike to 8.8 and finally it drifted down to 6.4 over the next 2.5 hours then it returned to approximately correct reading 8. This meter is used to control blowdown to the river and is used to maintain compliance with our NPDES permit. No violations of the permit occured but were it not for the keen observation of the shift personnel an out of specification condition WOULD have occured. Recommend immediate thorough investigation into this repeat incident. <I> **** Actions Taken **** CRS informed; ops adjusted to manual control of acid injection. Chemistry performed grab sampling to verify actual pH condition and advise ops. Entered into action statement A19-PHITS-002 4 hr CW grab sampling for pH. Chemistry supervision informed. | 02-00-CW-PHITS-1
397980 | CR | 20190813 | CAQ | C | SLC-TK-1 High Level alarm locked in | Y | Y |  | N | YES | <D> **** Detailed Description **** SLC-TK-1 has a locked in high level alarm following sparge. Computer trending shows the level made a step change. The detector/equipment likely needs to be rodded out. | 02-00-SLC-TK-1
397984 | CR | 20190814 | CAQ | D | NRC - Small amount of oil on each end of RCIC pump | Y | N |  | N | YES | <D> **** Detailed Description **** NRC walkdown found a small amount of oil on each end of pump. <I> **** Actions Taken **** Crew walkdown found a small leak on RFT-RO-3B of maybe a couple drops a day. No concern of inoperability. | 02-00-RCIC-P-1,02-00-RFT-RO-3B
397985 | CR | 20190814 |  | 4 | HMI alarm PC SYS-STAT LPMP TMR | N | N |  | N | YES | <D> **** Detailed Description **** HMI alarm PC SYS-STAT LPMP TMR received. Lead pump 30 minute elapsed timer. <I> **** Actions Taken **** CRS, OPS4 notified | 02-00-HSSF-CAB-CHEM/LAB
397987 | CR | 20190814 |  | 3 | procedure enhancement for SOP-CAS |  |  |  | N | NO | <D> **** Detailed Description **** Recommend replacing CAS Compressor Start steps from SOP -CAS-OPS (5.1.4-5.1.6) with the Start steps from SOP-CAS -START (5.5.3-5.5.5) to direct OPS to verify oil levels on Shifting of CAS compressors. <I> **** Actions Taken **** Informed OPS Procedures group <N> **** Equipment Description **** Procedure enhancement
397988 | CR | 20190814 |  | 4 | Laboratory Sink Leak | N | N |  | N | NO | <D> **** Detailed Description **** Water was observed overflowing a catchment and pooling under the sink in cabinets 59-60 of the Chemistry Lab on RW 487'. The leaking fitting shows signs of wear and corrosion. <I> **** Actions Taken **** Water mopped up. Catchment container emptied and replaced. <N> **** Equipment Description **** Chemistry Lab RW 487', west sink over cabinets 59-60
397989 | CR | 20190814 |  | 4 | Mt-hoi-40 main line switch still broken | N | N |  | N | YES | <D> **** Detailed Description **** upon inspection of the mt-hoi-40 per Wo # 02127047 craft identified that the main line switch has not been fixed. There was a previous CR #00383954 / WR #29144348 written during the last inspection. with no resolution of the problem. the handle still rotates 360 degrees when turned to the off or on position. creating a safety hazard in the event there is a problem during hoist operation. if the operator needed to turn the main line switch off during an event. the only option to de energize the hoist would be to unplug at the metric weld rec on the south wall. This creates more confusion if there was something unexpected to happen during normal operation. there currently no deficiency tag hung on the eqiupment. <I> **** Actions Taken **** notified supervisor and generated CR <N> **** Equipment Description **** MT-HOI-40
397990 | CR | 20190814 |  | 4 | M&TE did not auto transfer/load in EWP when scanned. |  |  |  | N | NO | <D> **** Detailed Description **** M&TE 45136 barcode was scanned with the tablet, however once on the completion review tab of the WOT for 02116599 -01 the M&TE did not show. <I> **** Actions Taken **** Added M&TE 45136 manually to M&TE field in EWP prior to task completion. Generated CR for documentation/trend.
397991 | CR | 20190814 |  | 3 | Internal Email flow delayed several hours |  |  |  | N | NO | <D> **** Detailed Description **** IS Duty officer was notified that email was not flowing. Users where sending emails to each other and noticed the other person was not receiving the email. This started around 9pm, IS duty officer was contacted around 2am. <I> **** Actions Taken **** IS Analyst was contacted, he looked at the exchange servers saw the emails stuck in the exchange server queue on 1 of the 4 exchange servers. After looking at the logs it was discovered the certificate for the smtp transport service was not showing registered. IS Analyst registered the certificate and the email was released from the queue. All email services have been restored at this time. Other errors where noted in the log so the IS Analyst put that 1 exchange server in maintenance mode. IS Analyst contacted the vendor to open a support case as this issue appeared to be related to a recent vendor software update. The issues with this server will be identified and resolved with the vendor without user impact. An IS change gear ticket has been created to track the technical details. Not Related to 10 CFR 73.54 . Recommend NCAQ-3 with follow-up actions to fully restore the system.
397994 | CR | 20190814 |  | 3 | SOP-HVAC/CR-START procedure change request |  |  |  | N | NO | <D> **** Detailed Description **** ABN-HVAC directs closure of E-DISC-PP7AF/9 and E-DISC -PP8AF/9 to provide power to division 1 or division 2 quad receptacles to power temporary cooling fans. The fans are removed per SOP-HVAC/CR-START, however the disconnects are not placed back in the Off position. Revise SOP-HVAC/CR -START to reposition the disconnects back in the Off position. <I> **** Actions Taken **** Discussed change with Ops procedure group and Operations staff. Initiated this CR.
397998 | CR | 20190814 |  | 3 | TSW-SR-34 Sample Rack Flushing Proceedure Edit |  |  |  | N | NO | <D> **** Detailed Description **** Step 6.3.11 needs edited in TSW-SR-34 Sample Rack Flushing. The proceedure references Attachement 5.15 of PPM 12.2.2 for valve line up verification. The correct attachement in PPM 12.2.2 for TSW-SR-34 is 5.14. <I> **** Actions Taken **** CR written. <N> PPM 12.13.40 TSW-SR-34 Sample Rack Flushing
397999 | CR | 20190814 |  | 4 | I&C Over Dose for July 2019 |  |  |  | N | NO | <D> **** Detailed Description **** I&C went over the estimate for July 2019. Dose estimate for teh month was 230 mrem, actual dose for the month was 299 mrem. Directly contributing to the dose overage for the month was emergnet work for trip of FWH 1C. The investigation and repair accounted for 118 mrem. The dose is completely responsible for I&C exceeding dose goal by 69 mrem. <I> **** Actions Taken **** Wrote Cr
398001 | CR | 20190814 |  | 4 | MT&E Found out of tolerance | N | N |  | N | NO | <D> Calcode #35316 Mitutoyo Dial Indicator- model 2780 found OOT & Rejected- Not Economical to Repair. Not used during Calibration cycle. DEF #7175A written. No Plant Impact. No Action Required.
398002 | CR | 20190814 | CAQ | D | Met tower delta T differences between CHA & B | N | Y |  | N | YES | <D> **** Detailed Description **** Met tower delta T differences between A & B (approximatly 0.5 deg F) this cause a different stability class that we use for classification. Need to investigate and correct the issue. CR#392049 was COMP-NA <I> **** Actions Taken **** CRS informed | 02-00-MET-TR-1
398005 | CR | 20190814 |  | 4 | Railcar track cover plate warped - trip hazard |  |  |  | N | NO | <D> **** Detailed Description **** A railcar track cover plate outside of R106 door for Reactor Building truck bay is warped and creates a trip hazard. Plate is located approximately half-way between delay fence adjacent to railcar track and the double gate just outside R106. <I> **** Actions Taken **** Reactor Major Maintenance Supervisor was informed. An orange safety cone has been placed over the warped end. Plate has been marked with a large "X" for identification. <N> **** Equipment Description **** Outside R106 door to Reactor Building Truckbay
398006 | CR | 20190814 |  | 3 | Post Maintenance Test Step Not Completed as Specified in PM | N | N |  | N | NO | <C> An assignment needs created. Why didn't they follow procedure? <D> **** Detailed Description **** A post maintenance test step in a Radio Paging system PM was not completed as specified in the Information Use procedure used in the WO. The procedure calls for the SCC to run a pager test to verify functionality. However, the technician used an alternate, equivalent method to verify functionality. The alternate method is not specified in the procedure. Upon notification, the supervisor requested the SCC to perform the specified pager test, which was successful. WO 02116656 <I> **** Actions Taken **** Notified supervision. Performed test as specified. Provided coaching to technician regarding procedure use and adherence. Reviewed and discussed SWP-PRO-01 concerning procedure adherence with the team. Took a thumbs down. Recommend NCAQ 4. ITMGMT
398007 | CR | 20190814 |  | 4 | 16 Pieces of M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** 16 Proto Torque Wrenches have passed Closeout Calibrations and are Now Suspended until R25. Not used since Calibrated. No Plant Impact. See list for Calcodes, Descriptions, models and associated DEF #'s. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
398009 | CR | 20190814 |  | 4 | The secondary siren repeater did not operate during test | N | N |  | N | YES | <D> **** Detailed Description **** During the weekly SCC test of the siren activation systems the secondary repeater was found inoperable. The primary repeater tested fully functional and would activate the sirens in an event. <I> **** Actions Taken **** Dispatched techs to repair the secondary repeater. The switch that transfers between the primary and secondary repeats had some sort of glitch and started working properly after being reset. The system was fully tested with no problems found. Recommend NCAQ 4 ITMGMT <N> **** Equipment Description **** CCCF
398010 | CR | 20190814 |  | 3 | CID29606 â€“ received wrong gasket type | N | N |  | N | NO | <D> **** Detailed Description **** While performing WO 02116959 (Annual Aux Boiler maintenance) it was discovered that CID 29606 (Blue Max manway gasket) that was issued is the wrong material. Went to warehouse and found the remaining three in stock are of the correct material. Also, the min/max for this CID is set at 3 and the Aux Boiler requires 4 every time this PM is done. See EDMS for pictures. The incorrect gasket is of a graphite material and the correct gasket has a Teflon wrap on it and is white with the words â€˜Blue Maxâ€™ printed on it. <I> **** Actions Taken **** Notified manager.
398011 | CR | 20190814 |  | 4 | Grapple #1 Failure to Function | N | N |  | N | NO | <D> **** Detailed Description **** On Tuesday, 8/13/2019 during the performance of the pre-use checks on grapple #1, a loud pop was heard while extending the grapple. To better determine the source of the loud popping noise, the grapple was returned to its storage cradle for inspection. Upon further observation, it was determined the grapple was binding on one side and would not function for retrieval of liners from the NUPAC cage. The grapple vendor, Energy Solutions, was contacted for assistance and informed the station that in their experience, the grapple would need to be returned to them for inspection and subsequent repair once the cause of the binding was determined. <I> **** Actions Taken **** The grapple was removed from service and a quote was requested from the vendor. Once a quote has been received, the grapple will be prepared for transport to the vendor for inspection, repair and annual certification. <N> Cross referenced model AR 397498 tracks calibration and maintenance on the grapples.
398013 | CR | 20190814 |  | 4 | Main Turbine Bearing 4 step change in vibration indication | N | N |  | N | YES | <D> **** Detailed Description **** Vibration amplitude on Main Turbine Bearing 4 (LPA, West end) displayed a step â€“ change upward in amplitude. The peak to peak levels were in the range of 5 mils, but a step change up to 6.2-6.4 mils occurred at ~ 14:25 on 08/14/19 (as indicated on TG-XR-TSI pt. 4 and TG-MON-VB4). There were no other corresponding events (i .e. lube oil temperatures, Main Turbine backpressure and other bearing vibration levels were steady). CR 397923 was written on 8/12/19 to document rising vibration amplitude in this bearing to the ~ 5.0 mil range. <I> **** Actions Taken **** Notified the CRS and System Engineer. Submitted CR and WR to document the condition. | 02-00-MS-DT-1A
398014 | CR | 20190814 | CAQ | D | Computer Point L108 and TDAS X198 found out of tolerance. | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO 02142219-01, PPM 16.2.3, step 7.2.21, the as found data for L108 and X198 were found out of tolerance. L108 OOT tolerance was previosly documented in CR 392731/WR 29148337. WO 02143363-01 was created to calibrate L108. <I> **** Actions Taken **** Documented as found data. Obtained permission to calibrate both points per WO 02143363-01 from Supervison. All as left data within tolerance and documented in surveillance. Wrote CR to document. Informed CRS.
398015 | CR | 20190814 |  | 3 | ENG-DES-50 still refers to Plant Support Engineering |  |  |  | N | NO | <D> **** Detailed Description **** The current revision (R2) of PPI PPM ENG-DES-50 (Interface Procedure for IP-ENG-001 Standard Design Process) continues to refer to Plant Support Engineering. The Plant Support Engineering group no longer exists. ENG-DES-50 Attachment 7.1 currently indicates that the Plant Support Engineering group is responsible for monitoring the installation, removal, and duration of Temporary Modifications using Performance Indicators and reporting tools to extract Asset Suite data. Please update ENG-DES-50 as appropriate - this procedure is owned by Design Engineering. This condition is purely administrative in nature.
398016 | CR | 20190814 |  | 2 | Employee injury | N | N |  | N | NO | <D> **** Detailed Description **** On 8/12, an employee reported back discomfort and received offsite medical treatment. The injury resulted from work performed at the TMU pumphouse. The employee is required to take time off from work for recovery. <I> **** Actions Taken **** Notified Occupational Health, Industrial Safety, Human Resources, Department Manager, and Department VP. The work activity is currently suspended. A walkdown of the job site involving Department Manager, Department VP, Industrial Safety, Operations Support General Manager, Plant General Manager, and Performance Improvement Manager has been scheduled. The employeeâ€™s position description was reviewed, compared to the activity being performed, and determined to adequately capture the work requirements/conditions. Department safety stand down was completed on 8/13.
398017 | CR | 20190814 |  | 3 | ESP Cycle Training Exam Failures | N | N |  | N | NO | <D> **** Detailed Description **** Two engineers did not achieve a passing grade on the Thermodynamics examination given on 8/14/2019. Remediation will be conducted per TDI-02. No qualifications are impacted. AR is for trending purposes only. <I> **** Actions Taken **** Informed respective Supervisors. Reviewed missed questions with students. Reviewed examination test items for adequacy.
398018 | CR | 20190814 |  | 3 | PO 354938, Reset Pressure for AS-RV-1 and AS-RV-5 | N | N |  | N | NO | <D> **** Detailed Description **** This does not affect currently installed plant equipment. As a part of quality receiving for relief valves under Purchase Order 354938, it was discovered based on review of the supplied functional test report that relief valve CID 54402831 (serial # D11538-229-1) and CID 54402845 (serial # PO-342034-001-01) have reset pressures which do not meet the purchase order requirements or the relief valve setpoint data sheets which specify the reset pressure as greater than or equal to 96% of the setpoint. The 96% requirement comes from AED/CAL ME-02-90-67 which references the 1989 edition of ASME Code sect. I PG-72 which required that â€œAfter blowing down, all valves shall close at a pressure not lower than 96% of their set pressureâ€. For this reason, Purchase Order 354938 specified a setpoint of 225psig and reset of 216psig for CID 54402831 and a setpoint of 230psig and reset of 221psig for CID 54402845. After discussion with the vendor it was determined that the relief valves in question were manufactured to the current ASME sect. I code, which has completely removed the aforementioned requirement for the reset pressure to be greater than or equal to 96% of the setpoint. Because the ASME code, to which these relief valves are manufactured, no longer requires the specific reset pressure, AED/CAL ME-02-90-67 and relief valve data sheets for AS-RV-1 and AS-RV-5 should be revised to also remove the specific reset requirement. This was discussed with the System Engineer, Relief Valve Program Engineer, and Procurement Engineering, who provided concurrence of the acceptability of the relief valves as provided; the ASME code Engineer agreed that to align the calculation and datasheets with the current ASME sect. I code is acceptable. This CR is in support of WO 02109586 and 02126005, to document the acceptability of the relief valves being received on Purchase Order 354938 and to drive revision to AED/CAL ME -02-90-67 and relief valve data sheets for AS-RV-1 and AS -RV-5 to remove the reset pressure requirements no longer imposed by the current ASME sect. I code. <I> **** Actions Taken **** Discussed with System Engineer (EFIN), Relief Valve Engineer, Procurement Engineering, Supply Chain Services Procurement Specialist, Design Supervisor, ASME Engineer, Work Week Manager, and vendor. Reviewed ASME sect. I code and AED/CAL ME-02-90-67. Wrote this CR.
398020 | CR | 20190814 |  | 4 | SMA-FL-1 is at end of roll | N | N |  | N | YES | <D> **** Detailed Description **** while performing rounds it was noted that SMA-FL-1 is at end of roll. <I> **** Actions Taken **** initiate CR/WR and inform CRS. | 02-00-SMA-FL-1
398021 | CR | 20190814 |  | 3 | Bearing 4 vibration reached alarm level | N | N |  | N | YES | <D> **** Detailed Description **** Approximately 1 hour following the step change in vibration identified in CR AR 398013, the vibration on Bearing 4 began an increasing trend until vibration levels exceeded alarm level of 7 mils at around 1700 hrs. Vibration on Bearing 4 peaked around 7.2 mils then began to trend down slightly to around 6.3 mils and began to level off. Although no other bearings appeared to experience any changes when the Bearing 4 made the step change from 5 to 6.2 mils as described in CR AR 398013 at 1421 hrs; however, the trend that followed saw levels peak around 7.2 mils was mirrored by bearings 3, 5, and 6. This CR is to document reaching alarm level on Brg4. Additionally, a bearing consistently of 6 mils will require NEIL be notified. <I> **** Actions Taken **** Informed manager, discussed with MCR staff and on management call, contacted OEM for vibration support to come to site, emailed NEIL liaison <N> **** Equipment Description **** LPA, west end | 02-00-MS-DT-1A
398022 | CR | 20190815 | CAQ | C | Intended response no observed while performing ISP-RBM-S401 | Y | N |  | N | YES | <D> **** Detailed Description **** While performing ISP-RBM-S401 STEP 7.4.6 j. on RBM A output 6computerpoint indication wouldnâ€™t trip (ON). Reperformed 7.4.6 on RBM A output 6 a second time and had the same result. Stopped CFT and contacted System Engineering and decided to back out of surveillance. This CFT will need to be performed with system engineer in attendance to witness issue. Also noted that RMB A Output 5,7 and 10 Trip on when performing section 7.4.6 on output 6. Photoâ€™s of P616 and P603 in eWP during performance <I> **** Actions Taken **** Stopped contacted system Engineering, SM and CRS didnâ€™t close out ISP-RBM-S401. Uploaded paper copy of ISP-RBM-S401 in eWP WO 02122283-01 | 02-00-RBM-CHS-A
398023 | CR | 20190815 |  | 4 | ASD resistivity approaching low spec of 5 Mohm | N | N |  | N | YES | <D> **** Detailed Description **** all channels of ASD resistiviity approaching low spec. <I> **** Actions Taken **** Informed MCR, initiated AR at request due to weeken approaching. | 02-00-RRC-IMD-ASD1A/1,02-00-RRC-IMD-ASD1A/2,02-00-RRC-IMD-ASD1B/1,02-00-RRC-IMD-ASD1B/2
398024 | CR | 20190815 | CAQ | D | Primary Containment temperature above LCS 1.7.1 limit | Y | Y |  | N | YES | <D> **** Detailed Description **** The sacrificial shield annulus average temperature rose to 150.2 F exceeding the LCS 1.7.1 Alert limit of 150 F. This condition is anticipated during hot weather. This CR satisfies LCS compensatory measure 1.7.1.A.2. <I> **** Actions Taken **** CW blowdown has been maximized to promote cooling and all three RCC heat exchangers are in service. <N> **** Equipment Description **** Primary Containment sacrificial shield annulus | 02-00-C-TK-1
398032 | CR | 20190815 | CAQ | C | TEA temporary sample cart broken | N | Y |  | N | YES | <C> MRT Change: CR 398032 moved from D/Trend Repair to Severity C assigned to AR-EMERP. <D> **** Detailed Description **** During the performance of the 4 hour flow checks it was determined that the TEA temporary sample cart was damaged. Upon further inspection it was noted that the belt, belt assembly, key stock, key stock groove were auto -disassembled by the motor. The belt, key stock and key groove all appear to have some degree of damage/wear. This is not a desireable condition as this is the current means of monitoring effluent release from the turbine building. It is suggested to either get replacement parts from the 606' PRM temporary cart, replace the TEA cart with the PRM cart or to begin sampling from the turbine bldg roof sample point. <I> **** Actions Taken **** CRS, supervisor and specialist informed <N> **** Equipment Description **** TEA temporary sample cart - 525' Radwaste HVAC room
398034 | CR | 20190815 |  | 3 | PPM 10.25.166 requires enhancement / additional notes |  |  |  | N | NO | <D> **** Detailed Description **** During the torque switch replacement on SW-MO-75A, it was noted that the new SMB-000 limiter plate labeling was reversed on one of the sides (both sides are labeled). The procedure could be enhanced to ensure the correct labeled side is installed. (see attached pictures). Electricians used the following human performance tools to address the issue: Questioning Attitude and Stop When Unsure. See actions taken for additional information. <I> **** Actions Taken **** NOTE: The SMB-000 Torque Switch limiter plates are printed on both sides. The open/close labeling is different on each side of the plate. See the excerpt from Limitorque drawing (Attached). This allows the plate to be installed in the field in the orientation needed to coincide with the rotation of the valve. NOTE: The Limiter Plate was installed correctely and verified by QC. NOTE: Recommend revising PPM 10.25.166 Section 7.7.9.b to add a Caution/Note regarding the installation of the limiter plate (labeled on both sides).
398036 | CR | 20190815 |  | 4 | 14 Pieces of M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** 14 Pieces of M&TE were Not used during Calibration cycles and have been Suspended until R25. No Plant Impact. See list for Calcodes, Descriptions, Models and assocated DEF #'s. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
398037 | CR | 20190815 | CAQ | C | SW-M-P/1B oil sample for ODMI missed | Y | Y |  | N | YES | <D> **** Detailed Description **** The ODMI for SW-M-P/1B directs that weekly oil samples are taken following the Monday spray pond chemical addition. The oil sample was missed on 8/12/19. The current trend of water content in the upper bearing oil reservoir would support that the current water content is less than the first action level of the ODMI. Recent trend data is as follows: 8/5/19 - 1755 ppm water 7/29/19 - 1415 ppm water 7/22/19 - 1082 ppm water The first action point per the ODMI is 3000 ppm water. <I> **** Actions Taken **** Notified system engineering, requested support during 8/15 0615 meeting to obtain oil sample following the 8/15 scheduled run of SW-P-1B. | 02-00-SW-M-P/1B
398038 | CR | 20190815 |  | 4 | 5 Pieces of M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** 5 Pieces of M&TE have Passed Closeout Calibrations and are now Suspended until R25. Not used since Calibrated. No Plant Impact. See list for Calcodes, Descritpions, Models and associated DEF #'s. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
398039 | CR | 20190815 | CAQ | D | Second control power fuse not replaced | Y | N |  | N | YES | <C> MRT Change: CR 398039 moved from NON-CAQ Severity 4 to CAQ D/Trend Repair. <D> **** Detailed Description **** When replacing the under-rated control power transformers in the NLI starters, the control power fuses are also being replaced. In discussion with the system engineer, this is being done as a conservative measure as the fuses may have been stressed. RCIC-42-8BA9D, motor starter for RCIC-V-63, has two control power fuses in series. When the control power transformer was recently replaced, only one of the two fuses was replaced. While there is no reason to believe the fuses had been over-stressed by the original transformer, it is recommended that both fuses be replaced at the next opportunity. | 02-00-RCIC-42-8BA9D
398043 | CR | 20190815 |  | 3 | Blind corners in deschutes outside conf Rm 2-244. |  |  |  | N | NO | <D> **** Detailed Description **** With the construction of conference room 2-244 in the second floor of the deschutes building, it has created two blind spots for people walking past the area outside of the conference room in the main walk way. There have been multiple near misses of people almost running into one another when crossing the entry points into the main hallway in front of 2-244. Some individuals have taken it upon themselves to announce their presence when walking by which have helped to mitigate potential collisions, however, most individuals have not adopted this same safe behavior. Recommend that two corner mirrors be installed, one in the corner of the pillar outside the entrance to 2-244 and another on the corner of office 2 -268 to aid in people being able to see people coming from both directions to avoid any potential injuries. <I> **** Actions Taken **** notified supervisor. <N> **** Equipment Description **** Deschutes (PEC) 2-244
398046 | CR | 20190815 |  | 4 | DataGlance Sytem Down |  |  |  | N | NO | <D> **** Detailed Description **** When logging into DataGlance a connection error was displayed. <I> **** Actions Taken **** Notified Analyst that system was down. IS managment sent out a broadcast message notifying usersr that the system was down and then again when the DataGlance system was available. <N> Application error logs on the server included entries of "Cannot get a connection, pool exhausted". This is a reference to database connection, and the number of concurrent connections (the pool) that are allowed. Contacted the DBA, who noted an elevated number of open connections. The DBA then checked the Oracle SYSAUX tablespace and found that it was full. When SYSAUX is full, new database connections cannot be established (users can't log in, new jobs can't run/start). The DBA provided additional space to SYSAUX, which allowed database connections to be established. Users could then log in to the application.
398047 | CR | 20190815 |  | 3 | Poorly Written D-15 Thumbs Down on 8/15 |  |  |  | N | NO | <C> Anon CR reviewed for SCWE and moved for ops review. <D> **** ANONYMOUS CR - Detailed Description **** The thumbs down article in the D-15 for 8/15 was poorly written and left more questions than takeaways. Managers at the Operations Focus Meeting should be reviewing and providing input for D-15 commications. Several phone calls asking for clarifications on the thumbs down produced no additional information. <I> **** Actions Taken **** Discussed with supervisor, initiated CR. <N> Discussed CR with E&RP Manager. Based on injury evaluation, there is no discrete activity that is tied to the injury. Therefore the discussion on â€œwhat to do differentlyâ€ was limited for the write up.
398048 | CR | 20190815 | CAQ | C | EWD inaccuracy |  |  |  | N | NO | <D> **** Detailed Description **** EWD-51E-047 and EWD-51E-048 have a difference between the contact that picks up TG-RLY-TK2/ASOBP. EWD-51E-048 seems to be the correct configuration. <I> **** Actions Taken **** CR written. <N> **** Equipment Description **** EWD
398049 | CR | 20190815 | CAQ | C | PPM 16.2.3 TEA-FT-13 Loop Check Table | N | Y |  | N | NO | <D> **** Detailed Description **** Table 7.2b of PPM 16.2.3 doesn't allow for negative values at the 0.0 INWC input data for Computer points X198 and L108. The spec is-0 to +7425. Since the is an extremely sensitive input that bounces around quite a bit, calibration of the computer points for a "zero" reading is extremely difficult to impossible without "elevating" the zero reading which can throw off the upscale readings. <I> **** Actions Taken **** Wrote this CR and talked to engineering. The allowable values for this point need to be changed to allow for a slightly negative reading at zero input to facilitate a more accurate computer point calibration. <N> Extending AR due date to allow time for engineering review of IMDS parameters prior to amking a procedure change.
398054 | CR | 20190815 | CAQ | D | Computer Point L107 Out of Tolerance | N | Y |  | N | I DONT KNOW | <C> CR reopened to cross reference additional WO 02142220 then taken to complete. <D> **** Detailed Description **** During performance of WO# 02142219-01, step 7.7.3, the As Found data for Computer Point L107 was found Out of Tolerance. <I> **** Actions Taken **** Per step 7.7.8b, Informed Supervisor and Operations. Continued with surveillance. Wrote CR/WR to document and get L107 calibrated. <N> **** Equipment Description **** 501RW MCR
398055 | CR | 20190815 | CAQ | D | 2019 DBAI - AR CR 397828 follow-on inspection team concern | Y | N |  | N | YES | <D> **** Detailed Description **** While off-site reviewing photos attached to the EDMS of AR CR 397828, the 2019 Design Basis Assurance Inspection (DBAI) NRC inspection team questioned the appearance of one of the AR CR 397828 subject small bore DO pipe lines. The NRC inspection team questioned if one of the lines might have a crack in it. Design Engineering personnel immediately reviewed photos (the markings appeared to be scratches in the silver paint on the DO lines) and subsequently performed a field walkdown inspection. The subject small bore DO line is associated with DO-FLX-4B1 (Return to DO-TK-3B). The markings on this line identified as a possible concern were confirmed to be scratches in the paint. Concurrence for this assessment was obtained from Technical Services and System Engineering. Photos taken during the walkdown are attached to the EDMS of this AR CR 398055. <I> **** Actions Taken **** This CR is initiated to identify the NRC concern raised and Engineering resolution of that concern. Recommend TREND. <N> WR 291150944 fieldwork was completed 8/15/19 to address the AR CR 397828 clearance issue (SAT per Engineering walkdown completed 8/16/19). Nothing new or alarming with respect to this AR CR 398055 condition was revealed as a result of the increased access that now exists - as previously concluded, there is only scuffed/chipped paint on the DO piping. | 02-00-DG-ENG-1B1,02-00-DO-FLX-4B1
398057 | CR | 20190815 |  | 3 | Apparent Adverse Trend â€“ HWC system reliability | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** There have been 3 unexpected trips of HWC so far in Cycle 25. This is unacceptable performance since it impacts Operations, Chemistry, Maintenance and Engineering to restore the system. The trips also impact the BWRVIP program health and cause perturbations of reactor coolant chemistry. The Chemistry Performance Indicator will also reflect this negative trend which ultimately impacts the INPO Index and Equipment Reliability (ERI). In each trip the station successfully restarted the system in a timely manner and HWC availability is predicted to reach the industry goal of 99% prior to the end of 2019 so there is no immediate concern regarding crack mitigation of vessel internals. HWC is a Tier 3 system that does not have an assigned system engineer. Maintenance owns the work activities on HWC with support from E-FIN. Consideration should be given to making HWC a Tier 2 system due to the significant impact it can have on BWRVIP and mitigation of IGSCC. <I> **** Actions Taken **** Discussed at Cross Discipline Review Team meeting. Initiating this adverse trend CR.
398058 | CR | 20190815 | CAQ | D | DBAI19(NRC) Concerns about piping clearance on DG1, DG2, DG3 | Y | N |  | N | YES | <D> **** Detailed Description **** CR 397828 was written on 8/8/19 to address concerns with piping clearance on DGs identified by the DBAI inspection team. Additional areas for concern were identified on 8/15/19. In addition to the already identified areas near the aluminum grating, it was identified that piping comes up through steel deck plates on the floor. These deck plates have slots cut into them for the piping to come through, but the deckplates themselves are not restrained to the floor and could contact the piping. See EDMS for photos. <I> **** Actions Taken **** Walked down all three DG rooms and took photos of the areas for concern. Wrote this CR. Design Engineering reviewed the AR CR description and photos attached to the AR CR EDMS. 1) The small bore piping penetrating through notches / copes in the D441' DG1, DG2, and DG3 floor trenches removable diamond plate covers could interact with the removable diamond plate covers during a design basis seismic event. CIVES-6 (Design Requirements for NonSafety-Related Items in Seismic Category 1 Areas) section 6.4 (Acceptable Impacts) provides guidance. a) Small bore piping is considered a soft target (targets that would require a moderate amount of energy to cause damage if impacted). b) Impacts on soft targets may be considered to be acceptable if the source is moderate weight for proximity effects. The subject diamond plate trench covers are installed in sections and are therefore small and relatively lightweight. Per review of CIVES-1 RSDS SSE seismic response spectra data, the SSE horizontal seismic accelerations for rigid items on the D441' floor (such as the subject trench covers) are less than 0.4g (small). If a trench cover weighs 10 lbs, the horizontal force would be 0.4 x 10 lbs = 4 lbs under a 0.4g acceleration. This horizontal force is resisted by static and dynamic friction forces and what is left over could result in an impact force with surrounding items (e.g., the DO lines) if they are too close. CIVES-6 Table 2 establishes that the accepted coefficient of friction for sliding response of unrestrained items at Columbia is between 0.25 and 0.56. Assuming the minimum coefficient of friction, an unrestrained trench cover on the D441' floor under SSE seismic conditions could result in an est impact load of W x (0.4 - 0.25) = 0.15 x W where W is the weight of the trench cover in lbs. By inspection, the trench cover sections weigh less than 50 lbs. As such, their associated maximum estimated impact load on surrounding items would be 50 lbs x 0.15 = 7.5 lbs. Even if doubled, this is clearly an acceptable impact load for any of the small bore DO lines penetrating through the subject trench covers. As such, the AR CR 398058 subject trench covers do not represent an unacceptable QC 2 over 1 condition for the small bore DO lines penetrating through them. 2) Other photos are of small bore piping proximity to other items in DG3 (grating) and DG1 (nearby item supports). The support configs in the photos appear to preclude the possibility of potentially unacceptable interactions between the identified items. A field walkdown was conducted by Design Engineering to confirm the apparent support configuration. DG1, DG2, and DG3 engine and generator areas were all walked down. Existing items were found to be sufficiently restrained as anticipated. No instances of inadequate support configuration for proximate items were identified. Note: The aluminum grating extensions adjacent to the DG1 and DG2 engines is detailed on drawing AED MIS D-DGGRATINGEXT-206 and has seismic category 1M qualification included with AED QID 118001-01. Installation of these extensions was authorized by Engineering via AR EVAL 6815 and occured via WO 01081656 in December of 2006. <N> CR title updated to add DBAI19. Would have added DBAI 2019 if it would have fit. | 02-00-DG-ENG-1C,02-00-DG-GEN-1,02-00-DG-GEN-DG2
398063 | CR | 20190815 |  | 4 | Declared prohibited item at security roadblock |  |  |  | N | NO | <D> **** Detailed Description **** An individual who had no business here at ENW had a declared prohibited item, hand gun magazine, in his vehicle Appropriate notifications were made. <I> **** Actions Taken **** Shift manager, Benton County and security supervision notified. OI-34 notifications completed.
398065 | CR | 20190815 |  | 3 | Potential Trend: R24 Outage Radiological Performance |  |  |  | N | NO | <D> **** Detailed Description **** During the July 2019 FAS meeting, a potential trend in Outage Radiological Performance was discussed. During R-24 there were six instances where inadequate behavioral human performance by radworkers could have resulted in radiological events: 1 RAM found outside RCA, 2 total dose alarms, 1 unanticipated dose rate alarm, 1 CA exit non -compliance and 1 RWP dressout violation. This condition report is being initiated to validate the potential trend by completing a Trend Validation Worksheet per TM-01, Trending Manual. <I> **** Actions Taken **** Recommend NCAQ Severity 3 to AR-RPOPS. <N> Additionally, this CR will review 14 events where Radiological Services personnel contributed to a human performance event resulting in 1 Lost Time Injury, 1 OSHA Recordable Injury, 2 Department Clock Resets and 1 Crew Clock Reset.
398075 | CR | 20190815 |  | 3 | 02126625-02 fail to finish due to procedure issue | N | N |  | N | NO | <D> **** Detailed Description **** WOT# 02126625-02 (FP Zone 3 PMT) was started as scheduled on 8/15/19. Due to a procedure issue with PPM 15.2.14, the PMT task will not complete as scheduled. Step 7.4.2.e needs to be re-written as an "IF - THEN" step, since it only applies to FP Zone 4E; the PMT is being performed on FP Zone 3. <I> **** Actions Taken **** Discussed with Williams Supervision and OPS - stopped worked. Will continue once procedure is corrected.
398079 | CR | 20190815 |  | 3 | Need records for non-rad worker respirator fit test |  |  |  | N | NO | <D> **** Detailed Description **** A recent search of records that support the respiratory protection program was conducting following generation of AR-397722, and found that the past 2 fit test reports were not available in records for one individual. These reports are still saved on the computer used to perform fit tests, and therefore, should be retrieved and sent to records. <I> **** Actions Taken **** Communicated with RP Supervision. A records search showed that a mask fit is in records for 2017, but not for 2018 or 2019. A printed copy of the 2018 and 2019 fit test reports show that the individual had Passed, and therefore, is qualified.
398080 | CR | 20190815 |  | 4 | Increasing Potential for Potable Water Contamination at IDC | N | N |  | N | NO | <D> **** Detailed Description **** Due to the decommissioning of the Industrial Development Complex many buildings have been recently torn down which has resulted in a large number of â€œdead legsâ€ in the fire and potable water system. The potable water piping comes off the fire water system. These â€œdead legsâ€ increase the possibility of contamination of the potable water system. This is a concern as more building and water service demolition is scheduled in the near future which will continue to create more â€œdead legsâ€ in the water system, directly increasing the potential for contamination. The water system is currently tested monthly and no significant issues have been found. Recommend installing a separate potable water service from the pump house to the few buildings that are scheduled to remain and Columbiaâ€™s cross tie after demolition is complete to separate the fire water (dead-legs) from the potable water loop <I> **** Actions Taken **** This CR, Water Operator notified, Facilities Manager notified, flushing of dead-legs
398081 | CR | 20190815 |  | 4 | Individual Cycle 19-3 Written Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** Individual Cycle 19-3 Written Exam Failure conducted 8/15/19. Remediation to be conducted in accordance with TDI-08. Recommend severity level 4 with operations training or training manager concurrance since no other actions will be required. <I> **** Actions Taken **** Administrative disqualification processed.
398082 | CR | 20190815 | CAQ | D | One (1) TSC Satellite phone inoperable | N | Y |  | N | YES | <D> **** Detailed Description **** During the Satellite base phone testing, WO 02117126, it was found one (1) satellite phone line in the TSC was not operational. Note: There are thirteen (13) phones lines in the TSC that were not affected and remained fully functional. Affected Phone - TSC Maintenance Manager - Line 2 The TSC Maintenance Manager Line 1 is opperational. The TSC Maintenance Manager Line 2 is considered a backup line. <I> **** Actions Taken **** Notified supervision and EP. Initial troubleshooting was unsuccessful. <N> **** Equipment Description **** TSC and B82 | 02-00-TSC-BLDG-MISC
398083 | CR | 20190815 | CAQ | D | FP-P-110 Pump Bearings Warm | N | Y |  | N | YES | <D> **** Detailed Description **** FP-P-110 bearings were warmer to the touch than normal during 15.1.4. They may need additional lubricant. <I> **** Actions Taken **** Informed MCR. | 02-00-FP-P-110
398084 | CR | 20190815 |  | 3 | Laptop used outside intended purpose | N | N |  | N | NO | <D> **** Detailed Description **** In 8/15/19, during a PMDD self-audit, Cyber Security discovered that a yellow laptop was used outside of its intended purpose as labeled. Individuals overlooked the label designation and failed to stop work and obtain a correct laptop. Upon further investigation it was discovered that cyber security did not provide the craft with a laptop that could have been used to complete this work. SWP-CSW-15 requires the use of laptops be restricted to their intended purpose. Although the incorrect laptop was used, the correct PMDD processes were followed throughout the work order such as being checked in and out within the permitted timeframe, virus-scanned before and after use, check-in/out via a delegated custodian and Form 26900 was completed. This is not a reportable event. <I> **** Actions Taken **** Cyber validated that laptop did not have a virus. Cyber reviewed scanning logs to verify laptop was scanned before and after the use for this WO. Cyber reveiwed check-in logs to validate this is an isolated event and this laptop was only used this one time. Reccomend Cat 3 to ITMGMT
398085 | CR | 20190816 |  | 4 | Lighting RB 501' Tip Mezzanine Room | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Lightings in RB 501 tip mezzanine room needs to be replaced. <I> **** Actions Taken **** wrote this CR and WR <N> **** Equipment Description **** RB 501 tip mezzanine room
398089 | CR | 20190816 |  | 4 | Restoration of CBD-FT-10 wiring failed | N | Y |  | N | YES | <D> **** Detailed Description **** After completion of step 4.2 of WO# 02119558-26, we had no voltage at CBD-FT-10. We checked the transmitter test terminals for current, and we had 0 mA. Stopped and contacted supervisor and CRS to get permission to restore the wiring to as found terminations. They agreed. <I> **** Actions Taken **** With the lead lifted, going to the new PLC at the Dehalogenation Trailer, we had about 24 VDC at terminal TB#-13. We landed A-1-13 Black lead back on TB3-11. At that point, voltage returned and current was reasonable for the process conditions (around 4 mA). This makes it appear like we may have a ground between E-IR-17 and the new PLC at the Dehalogenation Trailer. | 02-00-CL-SKID-2
398090 | CR | 20190816 |  | 4 | RWCU Pump A trouble alarm. | N | N |  | N | YES | <D> **** Detailed Description **** RWCU Pump A trouble alarm (H13-P602-A5 tile 4-7) came in and cleared twice. RWCU-P-1A continued to run. CRD flow remained stable at 1.8 gpm and RWCU pump cavity temperature remains stable at 150F. RWCU non regenerative hx outlet temp reads 128F. <I> **** Actions Taken **** Wrote CR Informed CRS | 02-00-RWCU-P-1A
398091 | CR | 20190816 |  | 4 | CF-P-42B is low on oil. | N | N |  | N | YES | <D> **** Detailed Description **** CF-P-42B is low on oil. normal ther is oil on the dip stick but there is not when checked. oil is visible. Please add oil. pump is not running <I> **** Actions Taken **** cr wr | 02-00-CF-P-42B
398092 | CR | 20190816 | CAQ | D | Water leaking on ground needs to be evaluated (permitted) | N | N |  | N | YES | <C> MRT Change: CR 398092 Severity C moved to D/Trend Repair. <D> **** Detailed Description **** CR 397805, WR 29150923 document a actuated Deluge system in the ASD building. the isolation valve is cautuion tagged shut and the drain is open. Water is apparently leaking by and discharging on the ground outside the building. I believe this needs to be evaluated for discharge. <I> **** Actions Taken **** wtrote CR <N> On 8/19/19 E&RP walked down the 3-4 gal/min of fire water draining from the deluge system to the ground outside the ASD building. Fire water flowing to the ground is not reportable. | 02-00-FP-V-P85/00
398093 | CR | 20190816 |  | 4 | PWC-FU-1 flapper valve was observed not to seat after Backwa | N | N |  | N | YES | <D> **** Detailed Description **** PWC-FU-1 flapper valve was observed not to seat after Backwash. After backwashing the flocculoator water was oberved going over the weirs in the filter chamber, but not going over the weirs in the settling chamber. since the settling chamber feeds the trough that feeds the filter chamber the only path for water to flow was thru the open flapper valve. Valve apprently shut a few minutes later as flow out of the flocculator stopped until the settling chamber filled up and started overflowing into the trough that feeds the Filter chamber. Normal operation was observed after that. Please evaluate if repairs or tracking is needed. <I> **** Actions Taken **** wrote CR WR | 02-00-PWC-FU-1
398094 | CR | 20190817 | CAQ | D | Received 4.603.A7 Rod Accumulator Trouble for HCU 5435 | Y | N |  | N | YES | <D> **** Detailed Description **** Received 4.603.A7 Rod Accumulator Trouble for HCU 5435. Alarm due to accumulator low N2 pressure. Recharged. <I> **** Actions Taken **** Wrote Cr Informed CRS | 02-00-CRD-HCU-5435
398095 | CR | 20190817 | CAQ | D | Nitrogen leak CRD-PI-131/5435 REWORK | Y | N |  | N | YES | <D> **** Detailed Description **** There is a N2 leak from the connection of CRD-PI-131/5435 to CRD-V-111/5435. This was initially written up before R24, and repairs completed under WP 02050182, however the leak is still there, and the HCU has had to be recharged every 3-4 days since R24 at about 0.5mrem each time. Refer to AR# 378667 for EDMS picture and video; it is the same as now. Please repair this; it is costing us unnecessary dose. <I> **** Actions Taken **** Recharged HCU, informed MCR, generated AR/WR. | 02-00-CRD-HCU-5435,02-00-CRD-PI-131/5435
398096 | CR | 20190817 | CAQ | C | CRD-V-111/5435 mounted too low | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-V-111/5435 block seems to be mounted about 1" lower than on the other HCUs; it is sufficiently low that the support structure interferes slightly with valve operation. Recommend investigate and repair. <I> **** Actions Taken **** Informed MCR, generated AR/WR. | 02-00-CRD-HCU-5435,02-00-CRD-V-111/5435
398097 | CR | 20190817 |  | 3 | E-PP-5NB doesnt have a Breaker list holder. | N | N |  | N | YES | <D> **** Detailed Description **** E-PP-5NB doesnt have a Breaker list holder. all electrical panels have a holder for the "volt BKR line up sheet", attachment 7.6 of SOP-ELEC-AC-LU , but E-PP-5NB does not. Please make it like all the others and get a holder for it. <I> **** Actions Taken **** wr/CR . See SOP-ELEC-AC-LU page 215. | 02-00-E-PP-5NB
398098 | CR | 20190817 |  | 4 | Outdoor Light out, outside diesel building. | N | N |  | N | YES | <D> **** Detailed Description **** Street Light out, outside diesel building. light is mounted between the DG3 and DG1 gorilla caged doors up high. <I> **** Actions Taken **** cr/wr <N> **** Equipment Description **** outside light mounted on diesel building
398100 | CR | 20190817 |  | 4 | Received the "OSCILLOGRAPH STARTED" alarm 0503 | N | N |  | N | NO | <D> **** Detailed Description **** Received the "OSCILLOGRAPH STARTED" alarm due to 500KV neutral OC (J7), SM-8 undervoltage (J12), and 230KV Undervoltage (J15) which have been reset. BPA reports that ASHE MERRIAN 500KV lines relayed off and then back on. Plant Inverters, Hotwell and Feedwater heater controllers and Containment Vacuum Breakers exhibited normal operations. The 115 Kv and 230 Kv portions of the grid were not affected. TR-S and TR-B voltages are 238/236/238 kV and 120/121/120 kV. <I> **** Actions Taken **** Wrote CR Informed CRS
398101 | CR | 20190817 | CAQ | D | WEA-SR-25 "No Isok. Control" | N | Y |  | N | YES | <D> **** Detailed Description **** WEA-SR-25 in "No Isok. Control". <I> **** Actions Taken **** Wrote CR per CI-15.2, informed effluent specialist. <N> **** Equipment Description **** 487' RW | 02-00-WEA-SR-25
398102 | CR | 20190817 |  | 4 | The steam leak repair on MS-V-163B appears to be leaking | N | N |  | N | YES | <D> **** Detailed Description **** 29149938 installed a furmanite box around the leak off line for MS-V-163 to address a large steam leak. It is possible to see spurts of steam coming for the box on TG501 camera #4. The returned leakage can be seen on the bottom right side of the camera image. Recomend investigation and repair if possible during balance shot of main turbine during the week of Sept 16th. <I> **** Actions Taken **** Wrote this CR. generated WR. added picture attempting to show the leakage location. | 02-00-MS-V-163B
398103 | CR | 20190817 |  | 4 | STM DUMP VLVS NOT FULL CLOSED alarm | N | N |  | N | YES | <D> **** Detailed Description **** STM DUMP VLVS NOT FULL CLOSED H13-P840.A2.9-6 alarm is alarming and clearing with no change in configuration. Currently BS-DV-2A2 is open. This alarm should not clear until all dump valves are closed. Investigate and repair. | 02-00-ANN-ANN-A/A2
398104 | CR | 20190817 |  | 4 | steam tunnel camera wouldnt open | N | N |  | N | YES | <D> **** Detailed Description **** while performing the nightly camera tour the steam tunnel camera would not open. Peer check was obtained and they also were unsucessful. please evaluate and repair as necessary. <I> **** Actions Taken **** cr/wr <N> **** Equipment Description **** steam tunnel camera
398105 | CR | 20190818 |  | 4 | T-121 Dog Latch Needs Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** T-121 Dog Latch Needs Maintenance. Mounting bracket needs to be resecured to the door frame. <I> **** Actions Taken **** Security Supervision Notified, CR/WR Initiated, Security Equipment Coordinator Notified. Offiicers briefed. <N> **** Equipment Description **** Door Tango 121 frame - Turbine Bld
398106 | CR | 20190818 |  | 4 | Standing water found in the east condenser pit area | N | N |  | N | YES | <D> **** Detailed Description **** Standing water found in the east condenser pit area, ( please reference 00397324 for trying to correct bad T2 water.). No active leaks could be seen. It does appear that the drain screen is very clogged. Pictures attached. A very quick look was taken (60mr) to see if there was any active leaks and none were visible at the time, no signs of dripping water, water movemet could be seen. Possibly due to clogged screen it has been slowly draining to T2 sump? <I> **** Actions Taken **** wrote cr | 02-00-FD-SUMP-T2
398107 | CR | 20190818 |  | 4 | TMU-P-1A Oil Leak | N | N |  | N | YES | <D> **** Detailed Description **** TMU-P-1A has a small oil leak. A large buildup of dead bugs is forming in the leaked oil. <I> **** Actions Taken **** Wrote CR | 02-00-TMU-P-1A
398108 | CR | 20190818 |  | 4 | T-DOOR-T121 failed to latch when closed from 1/3 open | N | N |  | N | YES | <D> **** Detailed Description **** T-DOOR-T121 failed to latch when closed from 1/3 open per step 7.1.3 of PPM 15.1.2. <I> **** Actions Taken **** wr/cr informed the CRS | 02-00-T-DOOR-T121
398111 | CR | 20190818 | CAQ | D | TR-B Reverse Power Relay alarm | Y | N |  | N | NO | <D> **** Detailed Description **** MCR received â€œXFMR TR-B Rev Pwr Relayâ€ (H13-P800.C4.3-5) in and immediately clear. BPA Munro said they had seen no transient on the 115KV grid. No other odd indications or abnormalities were noted.
398112 | CR | 20190818 | CAQ | D | Rod Accumulator Trouble Alarm for CRD-HCU-0627 | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-0627 was low nitrogen pressure. For trending | 02-00-CRD-HCU-0627
398113 | CR | 20190818 |  | 3 | AMS-3 Could Not Be Located For Delivery To I&C | N | N |  | N | NO | <D> **** Detailed Description **** Per WO #02127050-02, AMS-3 HP-EQ-C016785 was to be delivered to I&C for calibration, however this AMS-3 is currently not in service in the plant and could not be located at any of the various locations RP stores them. It is possible HP-EQ-C016785 has been removed from service, disposed of during the recent mass exodus of unrepairable AMS-3's and it's inclusion in this work order is one of legacy in nature. If this is the case, please remove it from the AMS-3 inventory to prevent future confusion and the wasting of precious RP time searching for an AMS-3 that does not exist. <I> **** Actions Taken **** Performed seach in various locations around the plant and notified RP Supervision that the AMS-3 could not be located.
398114 | CR | 20190818 |  | 4 | MS-SPV-125B pressure regulator off-scale high | N | N |  | N | YES | <D> **** Detailed Description **** During walkdown of instrument rack 14, the pressure regulator for MS-SPV-125B was noted to be off-scale high (GT 120 psig). MS-SPV-125B supplies air to the air-to -close trap station 8 valve. AMDS for MS-AO-125B provides normal air pressure 100 -0/+3 psig, with a min-max of 70 -125 psig. MS-SPV-125B was warm indicating the solenoid is active and is maintaining valve position. Please investigate air regulator and repair. <I> **** Actions Taken **** Notified System Engineer. | 02-00-MS-SPV-125B
398118 | CR | 20190818 |  | 4 | RW elevator emergency button too easy to accidentally push | N | N |  | N | NO | <D> **** Detailed Description **** The main control room receives several false 2222 calls a week from the radwaste building elevator due to people accidentally pushing the emergency button. There should be a cover placed over the emergency button to prevent accidental bumping of the button. <I> **** Actions Taken **** wrote cr informed CRS . There are several accidental emergency calls to the control room each week due to inadvertantly bumping the call button. Sometimes the individual is unaware they are calling on the emergency line. This is a distraction to the control room staff and could prevent us from receiving a valid emergency call.
398119 | CR | 20190818 | CAQ | C | RHR-A Discharge Pressure Rise | Y | Y |  | N | YES | <D> **** Detailed Description **** RHR-Aâ€™s discharge pressure has been rising since the system was used to cool the suppression pool on 8/16/2019. Pressure has been rising fairly linearly since the pump was stopped (see EDMS). Current rate of pressure rise is about 6# per hour. <I> **** Actions Taken **** Perparing to vent RHR-A with OSP-RHR-M101. | 02-00-RHR-V-42A,02-00-RHR-V-53A
398120 | CR | 20190818 |  | 3 | Several Hundred Gallons of Sulfuric Acid in Temporary Totes | N | N |  | N | NO | <D> **** Detailed Description **** Replacement of SAT-LG-17 under WO 02126073 required draining of residual sulfuric acid from SAT-TK-2. This acid has been sitting in nine temporary tote containers by the CW pumphouse since January 2019. Unlike SAT-TK-2, the totes are not in a bermed area. They do not appear to be in a designated accumulation or chemical storage area. Some of this acid could be used for pH control in the CW basin, however, some of the totes contain sludge and tank liner material that should NOT be introduced into the basin. <I> **** Actions Taken **** Contacted Maintenance, Chemistry, E&RP and OPS Management via email. <N> E&RP is aware of the sulfuric acid totes and is working with Chemistry to get the material shipped offsite in September.
398121 | CR | 20190818 |  | 4 | DO-F-5 high DP TREND | N | N |  | N | YES | <D> **** Detailed Description **** DO-F-5 high dp as written up in ARs 396966 & 397785; during fuel oil recirc DP was observed to read 29psid, higher than previously documented; condition is worsening. <I> **** Actions Taken **** Informed MCR, generated AR. | 02-00-DO-F-5
398122 | CR | 20190818 |  | 4 | Low glycol resistivity ASD 1A/2 & 1B/1 | N | N |  | N | YES | <D> **** Detailed Description **** ASD glycol resistivities were observed to be below spec on channels 1A/2 & 1B/1, and 1A/1 was approaching min spec. Recommend change filters. <I> **** Actions Taken **** Informed MCR, generated AR/WR. | 02-00-GY-CI-10A1,02-00-GY-CI-10A2,02-00-GY-CI-10B1
398123 | CR | 20190819 |  | 3 | SA-V-23 found capped. | N | N |  | N | YES | <C> CR re-opened at the request of OPS and re-assigned to OPSST. Moved from Severity 4 to 3. <D> **** Detailed Description **** While performing RWCU BW/PC on RWCU-DM-1B found SA-V-23 capped. This was different from expected. Removed cap and performed Backwash and Precoat and recapped after completion as directed by the main control room. It is unknown if this is a recent configuration change. <I> **** Actions Taken **** Informed MCR, initaited AR. <N> SA-V-23 is shown capped on M523-3 zone F/14. SA-V-23 is depicted capped on CVI ISO 215-00,2956. . SOP-CAS-LU and SOP-RWCU-DEMIN indicate throttled? | 02-00-SA-V-23
398124 | CR | 20190819 |  | 4 | CF-V-620 intermediate indications. | N | N |  | N | YES | <D> **** Detailed Description **** While performing SOP-RWCU-Demin 5.6.26 CF-V-620 did not indicate shut but intermediate. Looked at the operator and found it ~2cm from the shut contact. By direction from CRS performed step 5.6.28 to attempt to get it to shut and indicate fully shut. Valve stopped ~2cm from contact again. With CRS permission continued on with procedure. <I> **** Actions Taken **** Informed CRS, initated AR. Attempted to get system to reperform sequence. | 02-00-CF-V-620
398125 | CR | 20190819 |  | 4 | CAS-C-1C needs oil added | N | N |  | N | YES | <D> **** Detailed Description **** While performing rounds it was noted that CAS-C-1C was at the minimum spec for oil level and some oil will need to be added soon. <I> **** Actions Taken **** Informed CRS, Wrote CR | 02-00-CAS-C-1C
398128 | CR | 20190819 |  | 4 | 17 Pieces of M&TE Suspended until R25 |  |  |  | N | NO | <D> **** Detailed Description **** 17 Pieces of M&TE have Passed Closeout Calibrations and are Now Suspended until R25. Not used since Calibrated. No Plant Impact. See list for Calcodes, Descriptions, Models and assocated DEF #'s for each. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
398137 | CR | 20190819 | CAQ | D | WMA-AD-54A/1 and 54A/2 have incorrect power supply labels | N | N |  | N | NO | <C> MRT Change: CR 398137 moved from NON-CAQ Severity 4/Trend Repair to CAQ Severity D/Trend Repair. <D> **** Detailed Description **** While researching the E-PP-7AF loads for the upcoming E -TR-7A/2 replacement I found that the WMA-AD-54A/1 and 54A/2 have incorrect power supply labels in the main control room and in the simulator. The current labels list the power supplies as E-PP-7AF. The actual power supplies are: WMA-AD-54A/1 E-PP-7AE; WMA-AD-54A/2 E-PP-7AE; WMA -AD-54B/1 E-PP-8AF; WMA-AD-54B/2 E-PP-8AF. Please replace the WMA-AD-54A/1 and 54A/2 labels with one that have the correct power supplies. <N> The correct EPNs are WMA-AD-54A1 and WMA-AD-54A2.
398138 | CR | 20190819 |  | 4 | CW-CT-1A level is high | N | N |  | N | YES | <D> **** Detailed Description **** CW-CT-1A has a high level of 13 inches. | 02-00-CW-CT-1A
398139 | CR | 20190819 |  | 3 | ISO/IEC 17025:2017 acceptance | N | N |  | N | NO | <D> **** Detailed Description **** ISO/IEC 17025 has been revised from :2005 to :2017. The NRC has recently reviewed and approved the new revision for calibration activity (ML19056A451 is attached for reference). Columbia Generating Stationâ€™s OQAPD currently references only the :2005 revision, yet several vendors on the Evaluated Suppliers List are being set to inactive because the vendors have transitioned to the :2017 revision, and CGS does not currently recognize the :2017 revision. There are currently 6 vendors that the EN Standards Laboratory cannot accept calibrations from because they have transitioned to the :2017 revision. The vendors are: Fluke (Phoenix, AZ), Keysight (El Segundo, CA), Keysight (Loveland, CO), Keysight (Roseville, CA), Interface (Scottsdale, AZ), and Vitrek (Poway, CA). There are currently 4 OSD&Ds being held up for processing, and several Standards requiring calibration that cannot be processed because of the inactive status of the vendors. These Standards are required for calibration activity for CGS. There are also several additional vendors who could be set to inactive in the coming weeks/months depending on the timeliness of the OQAPD revision. This request is being made to revise the OQAPD as soon as possible so that these vendors can be reactivated and further delays on the calibration of EN Standards can be minimized. AR-CALSERV will be the sponsor for the revision of the procedure; the CR should be assigned to Quality Services for revision of the OQAPD. <N> Confirmed with Supervisor that OQAPD revision can be tracked as an action under original AR-CR 397820 OQAPD rev 055 now allows use of either ISO/IEC 17025:2005 or ISO/IEC 17025:2017. All actions to address this issue are tracked under AR-CR 397820. Closing this CR to 397820.
398141 | CR | 20190819 | CAQ | C | MT&E found out of tolerance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #37634 Ametek Torque Screwdriver- model TC5000-12 found OOT & Rejected. Driver has a history of adjustments required. DEF #7233A written for EFIN to Evaluate All the usages.
398144 | CR | 20190819 |  | 4 | 5 Pieces of M&TE Suspended until R25 |  |  |  | N | NO | <D> **** Detailed Description **** 5 Proto Torque Wrenches have Passed Closeout Calibratitons and are now Suspended until R25. Not used since Calibrated. No Plant Impact. See list for Calcodes, Descriptions, Models and associated DEF #'s. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
398145 | CR | 20190819 |  | 4 | MS-V-115B has an S5 packing leak. | N | N |  | N | YES | <D> **** Detailed Description **** MS-V-115B has an S5 packing leak. The motor operator was replaced in R24 by WO 02137580 and repacked by 02115970. The stuffing box was discovered steam cut and is to be replaced in R25 by WO 02145002. This valve needs to be electrically backseated ASAP to prevent ruining the new motor operator. <I> **** Actions Taken **** Coordinated with HP for leak investigation. Informed OPS. <N> **** Equipment Description **** OG Preheater room | 02-00-MS-V-115B
398146 | CR | 20190819 | CAQ | C | Standard found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** For 001-10-01-006: The OOT Standard was used for (1) CGS/ENSL Standard (C019012) on 3/14/2017 (in tolerance). The Standard (C019012) was calibrated again in 12/2017 using different Standards (001-10-01-006 was not used), results were in tolerance again. NO IMPACT. Assign to AR-CALSERV.
398147 | CR | 20190819 | CAQ | C | Standard found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** For 42412: The Set was used for CGS calibrations 44 times, and for SLIC calibrations 115 times. The Standard was OOT for the 0.130â€ Block and the 0.131â€ Block. These blocks were not used to calibrate any of the 159 instruments noted on the reverse traceability reports. All Blocks used from Set 42412 that were used for other calibration activity were found to be in tolerance during the most recent calibration activity. Assign to AR-CALSERV.
398148 | CR | 20190819 |  | 3 | EC 10769 for replacement of LPCS-M-P/1 (R25) needs revised |  |  |  | N | NO | <D> **** Detailed Description **** EC 10769 for replacement of LPCS-M-P/1 in R25 needs re -evaluation/revision for PMT testing. EC 10769 specifies TSP-DG1-B502 for performance testing due to a higher locked rotor current rating on the replacement LPCS pump motor. However, this is not the correct surveillance. TSP-DG1 -B502 is the DG 110%, 24 hour and hot restart procedure. LPCS is not even required to be run during this surveillance. It is likely the procedure was intended to be TSP-DG1/LOCA-B501 which does test the DG1 response to pump starts and is typical of motor PMT testing for RHR and LPCS motor replacements. In light of AR/CR 397881 for RHR-M-P2A replacement, the PMT/operability testing for EC 10769 requirements for this pump need to be validated.. EC 10769 is currently in the process of being re-reviewed for R25 implementation as it has expired. <I> **** Actions Taken **** Not an operability issue. For R25 outage planning. This evaluation needs to be performed promptly as current proposed R25 sequence has the Div 1 LOP/LOCA testing at the start of the division to support CW/TSW out of service to support CW basin drain and inspection (similar to R20 sequence). A requirement to perform the LOCA test as a PMT could either significantly shorten the CW basin work or potentially push outage duration by holding up Div 1 operability testing.
398149 | CR | 20190819 |  | 3 | EC 10769 section 5.5 (LPCS-M-P/1 replacement) needs updated |  |  |  | N | NO | <D> **** Detailed Description **** EC 10769 section 5.5 lists tech spec requirements for LCO 3.5.2 which are no longer valid. LCO 3.5.2 no longer differentiates mode 5 relative to cavity water level due to changes in R24 for TSTF 542 Water Inventory Control. EC 10769 is currently in the process of being re-reviewed for R25 implementation as it has expired. This is a seperate issue from AR/CR 398148 but may be resolved in parallel. <I> **** Actions Taken **** Not an operability issue. This us for R25 outage planning.
398152 | CR | 20190819 | CAQ | B | Potential circuit breaker part defect | Y | N |  | N | YES | <C> RISK: Medium. CAUSE: Unknown. Severity B, Assignment has been generated on CR 391337-21 to address this. <D> **** Detailed Description **** While performing failure analysis on the breaker removed from service as SW-CB-P1B (UTC 539849), Westinghouse was unable to conclusively determine a cause for the breaker failing to actuate the cubicle MOC switches. However, they did find a manufacturing defect on one of the two slotted banana links while removing the SureClose mechanism components as requested by CGS. The slot in one link was under-tolerance, creating an area where the associated pin would bind. Westinghouse does not believe the defect to be the failure cause as their testing of another mechanism showed that the pin did not travel into the area where the binding would occur. Upon receiving the SureClose components, CGS Code Programs examined the parts and did observe wear marks on the slotted banana link that indicates the pin does travel into the area where binding would occur. To determine if any other CGS breakers may have banana links with this same under-tolerance condition, a limited number of breakers will be inspected. As the defective banana link was installed in a breaker that was manufactured in 2015, three other breakers purchased near that same time period are judged to be most likely to have the same condition and will be inspected but three breakers of the original circa 2000 purchase order will also be checked. Work requests have been initiated to perform the proposed inspections. The inspections include CRD-CB-P1B, E-CB-8/DG2, and four spare breakers. As the CRD-CB-P1B MOC switches actuate a breaker trip alarm and operate the motor space heater, it is judged there is no design function concern. And as E-CB-8/DG2 is normally closed and the identified condition would only occur during a breaker closure, it is felt there is no impact to its design function. The Westinghouse report and Code Programs analysis have been uploaded to the EDMS Docs. <N> This CR identifies extent of condition for SW-V-2B failure to open and will be resolved by CR 391337. <R> REP/REGE assignments are not needed and were cancelled with Compliance Supervisor concurrence. | 02-00-CRD-CB-P1B,02-00-E-CB-8/DG2
398154 | CR | 20190819 |  | 3 | PPC substitutable computer data points out of date | N | N |  | N | YES | <D> **** Detailed Description **** The list of substitutable process computer data points is not up to date. The list does not take into account I/O address changes implemented in the following Engineering Changes: . EC 08076 - REPLACE POWER RANGE NEUTRON MONITORING SYSTEM EC 12155 â€“ ULTRASONIC FLOWMETERS EC 13492 â€“ CYBER SECURITY DIGITAL ASSET PROTECTION SYSTEM (DAPS) EC 15092 - PDIS AND PPC MODIFICATION FOR MUR (MEASUREMENT UNCERTAINTY RECAPTURE) . The CGS Plant Process Computer (PPC) can perform its required functions. The condition only applies to the functionality of placing data points in substitution via Option 8 of the Utilities Menu for maintenance activities. No other functionality of the PPC is impacted. <I> **** Actions Taken **** Recommend assignment to AR-COMPENG to update the PPC substitutable points list to reflect the current in-service I/O list. | 02-00-PPC-CPU-VMS/WS,02-00-TDAS-CPU-VMS/WS
398155 | CR | 20190819 |  | 4 | RWCU-FCV-33 seat leakage causes high P alarm/ RWCU-V-34 leak | N | N |  | N | YES | <D> **** Detailed Description **** RWCU-FCV-33 has seat leakage. This is causing high pressure alarms downstream of RWCU-FCV-33 and body to bonnet leakage on RWCU-V-34. RWCU-V-32 has been closed to mitigate the leakage. Need to repair seat leakage on RWCU-FCV-33. Both RWCU-FCV-33 and RWCU-V-34 were repaired in the last 4 months, but leakage has returned. | 02-00-RWCU-FCV-33
398157 | CR | 20190819 | CAQ | D | MAL 9 10 |  |  |  | N | YES | <D> **** Detailed Description **** Not operating as intended <I> **** Actions Taken **** Comp measure posted. Security & Electrical managers notified | 02-00-SEC-IDS-E/S/9/10
398164 | CR | 20190819 |  | 3 | ALARA Suggestion RW 437' Resin Processing Area |  |  |  | N | NO | <D> **** Detailed Description **** The RP Department did not have a person available to operate the Pendant Crane in support of rad waste processing, so the Maintenance Department was asked if they could send someone with the proper qualification. The work was to move a high radiation resin liner from behind the shielded rad waste processing area via the remote grapple, fly it out of the area and land it down onto the trolley located in the trolley pit, which was parked to the far west. Next the grapple is delatched from the liner, and the trolley with liner is moved to the far east of the pit, the liner is then rigged and picked up by the overhead Crane. It is then flown south and lowered into a shielded cask located on a truck trailer. It would be a benefit to have visual markers for the crane operator to help align for the moves, this would utimately save time and thus dose. <I> **** Actions Taken **** This observation was discussed with the Maintenance individual that suggested markers being put in place. Next the recommendation was discussed with other rad waste workers, they had thought of the idea before but did not pursue it. When dealing with high dose rate liners, seconds saved is dose saved. See photo of Trolley Pit attached in EDMS.
398167 | CR | 20190819 |  | 3 | Suspect bad Relay Replacement part | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02114908-03, PMT for relay replacement task 01, step 4.4 it states that alarm P602 -A5.6-1 should be clear. It was not. <I> **** Actions Taken **** Informed Supervision and CRS. Obtained new replacement relay and reperformed. Same results. Expanded team. Determind that alarm should stay locked in as long as instrument is not in "Operate" mode. Obtained permission to continue with PMT. SAT. Wrote CR to document.
398168 | CR | 20190819 |  | 3 | Degraded gasket found on SHCO-P1B | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO #02139506-01 when the pump was removed we found that the gasket used had delaminated. The gasket used is an OEM part (CID # 58162391) and is a fiber impregnated black rubber style. We have station OE that this type of gasket is leak prone due to the fiber creating a leak path and should not be used in this application. See pictures in EDMS <I> **** Actions Taken **** Due to the recent station AFI of leak path sealing and the IER 18-003 Mechanical Skills * Have a thorough knowledge of different gasket materials and the appropriate gasket to be used for each application this gasket should not be used in this application and we should seek a better material for this work. Notified Engineering supervisor, my supervisor and notified the main control room. . Engineering concurs that the gasket material for this application needs to be reviewed. Request Maintenance to create an AR EVAL assignment to Engineering to perform the review of the gasket material application and if required update the CAT ID with a better suited gasket material. | 02-00-SHCO-P-1B
398169 | CR | 20190819 | CAQ | C | Elevated Residual Chlorine Measured in IDC Potable Water | N | Y |  | N | YES | <D> **** Detailed Description **** The Water Distribution Manager for the IDC potable water system measured excessive residual chlorine in the IDC potable water distribution system on 8/19/2019. A follow -up residual chlorine sample was collected from the IDC potable water storage tank and measured >8.8 mg/L. This exceeds the primary drinking water standard for chlorine of 4.0 mg/L maximum residual disinfectant level (MRDL). <I> **** Actions Taken **** Contacted IDC Supervisor, Environmental Services Supervisor, E&RP Manager, and E&RP potable water program owner. E&RP reviewed WAC 246-290 reporting requirements and provided notification to WA Department of Health by phone/email. The IDC Supervisor called the vendor for the hypochlorite feeding system and is working to flush the system and reduce the residual chlorine in the tank and distribution system. Vendor will be onsite on Wednesday. The Water Distribution Manager for IDC provided a notification to IDC potable water system users to not drink Site 1 water until further notice due to a malfunction of the drinking water chlorinating system. <N> **** Equipment Description **** IDC potable water system hypochlorite feeding system E&RP complete the required notification to the state Department of Health on 8-19-2019. See EDMS docs for a copy of the notification. . Affected facility changed to IDC "01". Completed flushing of the potable water storage tank and main pipe lines to bring chlorine level to acceptable range. A tech-rep from the vendor TMG SErvices came out on Wednesday, 8-21-19, and identified the problem as a faulty probe sensor. This problem was rectified, and the system is functioning normally.
398170 | CR | 20190819 | CAQ | C | AR-300227 PPM 10.20.1 Markup Incorrect |  |  |  | N | NO | <D> **** Detailed Description **** The markup for AR-300227-39 to revise DG procedures 10.20.1, 10.20.12, 10.20.14, 10.20.16, and 10.20.19 was written in 2016. The markup was not revised, nor was corrective action assigned to revise the markup when worked was stopped during a DG window in 2017 (see CR-372274). As there is no documentation that there is an issue with the markup, it was incorporated into the proposed 10.20.1 revision for the upcoming October DG-1 window by the contractor. Since the contractor was not brought in until T-8, the PPM 10.20.1 revision may not be ready for the diesel window due to limited resources. <I> **** Actions Taken **** Initiated CR to obtain accurate markup.
398171 | CR | 20190819 |  | 3 | Concern on initiating CRs |  |  |  | N | NO | <D> **** Detailed Description **** Was informed by department manager behind closed doors, that a CR may be initiated at any time for any reason. Concerned that the current ability to write CRs is not known throughout the department as the limitations on CR initiation was done by supervision and management in front of others.
398172 | CR | 20190819 | CAQ | D | CMS-SR-20 tripped off after 45 minutes of run time. | Y | N |  | N | YES | <D> **** Detailed Description **** CMS-SR-20 tripped off after 45 minutes of run time. Pictures of screens in EDMS. <I> **** Actions Taken **** Wrote this CR. Dispatched OPS2 to investigate. Informed supervision. <N> Operator Reports that the sample pump is running at 2 scfm and no obvious problems observed. . About 30 minutes later the Channels went back into operate. | 02-00-CMS-SR-20
398173 | CR | 20190819 |  | 3 | 2019 DBAI (NRC) - Question of PPM 10.2.53 process rigor |  |  |  | N | NO | <D> **** Detailed Description **** During a team interview with NRC Inspectors for the in-progress 2019 DBAI, an Inspector indicated that the current PPM 10.2.53 (Scaffolding) process at Columbia for scaffolds erected for greater than 90 days (i.e., long-term or permanent scaffolds) may be dated and lack the rigor currently applied by other stations. This should be investigated and PPM 10.2.53 should be updated if our long-term or permanent scaffolding process is found to be out-of-date with industry excellence. . This AR CR 398173 is not documenting any identified problem in the physical plant - only a question of process rigor that should be investigated.
398174 | CR | 20190819 |  | 3 | 2019 DBAI (NRC) - Ops involvement for scaffolding |  |  |  | N | NO | <D> **** Detailed Description **** During a team interview with NRC inspectors for the in-progress 2019 DBAI, an Inspector questioned if PPM 10.2.53 Precaution and Limitation 4.18 with respect to travel path should require Operations involvement during scaffold erection activities to verify its satisfaction. As currently written, PPM 10.2.53 P&L 4.18 states "Ensure scaffolding does not block or impede the travel path for continued operability or functionality of nearby equipment (e.g., valve handwheel or stem movement or valve operator motion during disk position changes). If there is any concern regarding nearby equipment operational motion or travel path impacts, contact engineering for evaluation." , This AR CR 398174 is not documenting any identified problem in the physical plant - only a PPM 10.2.53 process question that should be investigated.
398175 | CR | 20190819 | CAQ | D | DW Annulus Temperature GT LCS Limit | Y | Y |  | N | NO | <D> **** Detailed Description **** The sacrificial shield annulus average temperature exceeded the LCS 1.7.1 Alert limit of 150 F. This condition is anticipated during hot weather. This CR satisfies LCS compensatory measure 1.7.1.A.2. <I> **** Actions Taken **** DW cooling has been maximized
398176 | CR | 20190819 |  | 3 | 2019 DBAI (NRC) - PPM 10.2.53 Engineer qualification |  |  |  | N | NO | <D> **** Detailed Description **** During a team interview with NRC Inspectors for the in-progress 2019 DBAI, an Inspector questioned if PPM 10.2.53 (Scaffolding) should require specific qualifications (i.e., PQD Qual Group qualifications) for Engineers involved with scaffold approvals per the PPM 10.2.53 process. As currently written, the existence of specific qualifications are only indicated in PPM 10.2.53 for personel who erect, move, dismantle, or alter scaffold (P&L 4.10). Nothing is currently indicated in the procedure for Engineers except that an electrical engineer should be contacted for electrical questions (P&L 4.9, 7.2.7 a), a degreed civil or mechanical engineer is required for structural questions (7.4.4 a), and Fire Protection is needed for Fire Protection questions (e.g., P&L 4.15, 7.1.3, etc). . The Qual Group for erecting, moving, dismantling, and altering scaffolding is MEBT qualification. Engineers determining if additional LBID review is required should require LDAA or LDAB qualification. . This AR CR 398176 is not documenting any identified problem in the physical plant - only a PPM 10.2.53 process question that should be investigated.
398177 | CR | 20190819 |  | 3 | 2019 DBAI (NRC) PPM 10.2.53 does not ref D-SCAFFOLD-455 |  |  |  | N | NO | <D> **** Detailed Description **** PPM 10.2.53 (SCAFFOLDING) includes a process for evaluation and configuration control of permanent scaffolding at Columbia but does not currently include any reference to controlled drawing AED D-SCAFFOLD-455 (PERMANENT SCAFFOLD SCHEDULE). Please update the PPM 10.2.53 permanent scaffolding process to include reference to drawing AED D-SCAFFOLD-455. . This delta was discussed during a team interview with NRC Inspectors for the in-progress 2019 DBAI. <I> PPM 10.2.53 R46 AR CR 398177 mark-up prepared and attached to the AR CR EDMS.
398178 | CR | 20190819 | CAQ | C | ISP-LPCS/RHR-M901 Incorrect LCS Allowable Value | Y | Y |  | N | NO | <D> **** Detailed Description **** ISP-LPCS/RHR-M901 performs the CFT/CC of RHR-PIS-22A and LPCS-PIS-5. These instruments are LCS required functions for RCS interface valve leakage per LCS 1.3.4.6. LCS Table 1.3.4.6-1 requires RHR-PIS-22A to trip LE 475# and LPCS -PIS-5 to trip LE 442#. ISP-LPCS/RHR-M901 incorrectly identifies these allowable values as LT 495# for RHR-PIS -22A (Step 7.1.15) and LT 439.9# for LPCS-PIS-5 (Step 7.2.27). These allowable values should be the same as LCS Table 1.3.4.6-1. This is correctly implemented in ISP -RHR-M901 for division 2 instruments RHR-PIS-22B and RHR -PIS-22C. ISP-LPCS/RHR-M901 needs to be updated to reflect the requirements of LCS 1.3.4.6 Table 1.3.4.6-1. <I> **** Actions Taken **** Verified RHR-PIS-22A and LPCS-PIS-5 trip within the requirements of Table 1.3.4.6-1 during the last performance of ISP-LPCS/RHR-M901 (WO 02142223). <N> Extended AR to discuss the issue with Engineering and Licensing prior to making changes. D. Van Alyne 9/18/19
398179 | CR | 20190819 | CAQ | D | RHR-PIS-22B stop snubber required adjustment | Y | Y |  | N | YES | <D> **** Detailed Description **** During performance of ISP-RHR-M901 channel calibration under WO#02117305-01 , the stop snubber required adjustment per step 7.1.21. <I> **** Actions Taken **** Wrote this CR per step 7.1.21 and notified supervisor. | 02-00-RHR-PIS-22B
398180 | CR | 20190820 |  | 4 | COND-P-2A & 2B oil sumps level high | N | N |  | N | YES | <D> **** Detailed Description **** COND-P-2A & 2B oil sumps have level high out of spec, 3/4 against a spec of 11/16. Recommend monitor to verify no continued rise, repair if any leaks indicated. <I> **** Actions Taken **** Informed MCR, generated AR/WR. . | 02-00-COND-P-2A,02-00-COND-P-2B
398181 | CR | 20190820 |  | 4 | E-TR-M3 cooler 2 alarm | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-M3 alarmed on Cooler 2 failure or off position approx. 0345am. Alarm cleared upon reset. Written to trend. Temperatures 49W1-60, 49W2-58, 26Q-60; <I> **** Actions Taken **** Informed CRS, Reset Alarm | 02-00-E-TR-M3
398182 | CR | 20190820 |  | 4 | Main Generator Gross MWe Indications Disagree | N | N |  | N | YES | <D> **** Detailed Description **** Over the course of the shift, the STA/IA noticed a consistent difference between Main Generator Gross MWe indications. Between 0330 and 0430 TDAS displayed around 1175 MWe, DEH-MON-2 (DEH Screen) displayed around 1190 MWe and TG-TR-144 (Main Generator Monitor) displayed around 1200 MWe. The difference between these three indications appears to be consistent. Instruments may be out of calibration. <I> **** Actions Taken **** Informed CRS, Shift Manager and Computer Engineering. Initiated CR. <N> **** Equipment Description **** Main Control Room H13-P820 | 02-00-DEH-MON-2
398183 | CR | 20190820 |  | 4 | E-MC-7BB lighting very poor | N | N |  | N | YES | <D> **** Detailed Description **** The lighing for E-MC-7BB is very poor, only 2 bulbs remain out of 12. This is located in Room R611 on Rx 572. <I> **** Actions Taken **** Informed SSS | 02-00-E-MC-7BB
398184 | CR | 20190820 |  | 4 | Poor lighting in SWPH A | N | N |  | N | YES | <D> **** Detailed Description **** Three of the eight overhead lights in the SWPH A are out resulting in poor lighting conditions. <I> **** Actions Taken **** Wrote CR | 02-00-SW-BLDG-MISC/A
398185 | CR | 20190820 |  | 4 | 6 Pieces of M&TE Suspended until R25 |  |  |  | N | NO | <D> **** Detailed Description **** 6 Fluke Multimeters have Passed Closeout Calibrations and are now Suspended until R25. Not used since Calibrated. No Plant Impact. See list for Calcodes, Descriptions, models and associated DEF #'s. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
398186 | CR | 20190820 |  | 4 | 3 pieces of M&TE Suspended until R25 |  |  |  | N | NO | <D> **** Detailed Description **** 3 Pieces of M&TE were Not used during Calibration cycles and are now Suspended until R25. Calcode #45309 Mitutoyo Dial Caliper- model 505-644-50 8in. DEF #7240A written. Calcode #0063995 Proto Torque Wrench- model J6177F 250in. DEF #7241A written. Calcode #0065687 Proto Torque Wrench- model 6066C 1000in. DEF #7242A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
398206 | CR | 20190820 |  | 3 | SCW-FLT-2 is at max. allowable D/P. | N | N |  | N | YES | <D> **** Detailed Description **** SCW-FLT-2 is at 4 psid as read on SCW-PI-484 and SCW-PI -482 in the OPS 3 logs. The high spec. is GT or ET 4 psid. Although the max. spec has not been exceeded yet, recommend evaluting the need to change out filter. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG 441W | 02-00-SCW-FLT-2
398212 | CR | 20190820 |  | 3 | TSW-FG-3A/3B/3C logs and specs. need to be evaluated. | N | N |  | N | YES | <D> **** Detailed Description **** OPS-3 rounds require verification of TSW flow through TSW FG-3A/3B/3C but refer to them as bullseyes. The bullseyes have been replaced during R-24 with 0-10 gpm flow indicating gauges/meters. Also, TSW-FG-3C and TSW-FG-3B read GT 10 gpm and TSW-FG-3A reads about 6 gpm. Is there a min spec? If so the specs need to be added to the OPS3 readings as well as a change to reference flow meters and not bullseyes. <I> **** Actions Taken **** Notified supervisor. <N> Per AED MEC M508-2 and AED SPC 350, TSW-FG-3A(B,C) are associated with TSW-HX-4A(B,C) for COND-M-P/1A(B,C). Per AED SPC 350 Table 35, the vendor required TSW cooling flow rate for Condensate pump motor thrust bearing oil reservoir cooling is 4 gpm (with reference given to CVI 11B-00,2 and CVI 11B-00,6). Additionally, the accepted TSW System Lineup Test (SLT) flow rate for these loads was 4 gpm (each) +0.4/-0.2 gpm. The original equipment installed at TSW-FG-3A(B,C) were Flow Glass (FG). From this AR CR description, what is currently installed at TSW-FG-3A(B,C) are actually Flow Indicator (FI) EXCEPT that the subject flow indicators likely have no PM or IMDS for periodic calibration. If the new components at TSW-FG-3A(B,C) are going to be used as flow indicators, the station should ask if their EPNs should be changed to TSW-FI-3A(B,C). Talking liberally, a flow indicator is also a flow glass (perhaps no EPN change is necessary). Is there a similar issue for TSW-FG-1A(B,C) and TSW-FG-2 A(B,C) from the Condensate BP LO Coolers? | 02-00-TSW-FG-3A,02-00-TSW-FG-3B,02-00-TSW-FG-3C
398232 | CR | 20190820 |  | 3 | ALARA Suggestion- Raise Awareness of Travel Path Dose Rates |  |  |  | N | NO | <D> **** Detailed Description **** Workers should be identifying the lowest dose travel path to their job site prior to entering the main RCA. As an example, dose rates in the reactor building vary greatly depending on what elevation or which side of the floor you traverse. Higher dose rate areas should be avoided when there is a lower travel path that can be taken. Tenths of a millirem add up! <I> **** Actions Taken **** Discussed this concern with RP Management. Recommended the RCA TRIP tickets be revised so that travel path dose rates are also documented along with the work area dose rates.
398233 | CR | 20190820 |  | 3 | ENG-DES-50 update for step 3.7.2 needed |  |  |  | N | NO | <D> **** Detailed Description **** For Owners Acceptance Review, ENG-DES-50 step 3.7.2 currently only refers to the direction provided by one Attachment in IP-ENG-001 (happens to be the Attachment for Design Change Package). In fact, direction for this activiy exists in multiple Attachments to IP-ENG-001 (e.g., Attachments for Conceptual/Common Design Phase, Design Equivalent Change Package, Commercial Change Package, Design Change Package, and Field Change Request. Suggest that the reference to IP-ENG-001 in ENG-DES-50 step 3.7.2 should be made more generic. It should not only refer to the IP-ENG-001 direction for one change package type. See the mark-up attached to the EDMS of this AR CR. . This is a process enhancement only - no impact/effect upon the physical plant. Suggest resolution by Design Engineering.
398240 | CR | 20190820 | CAQ | C | ARM-RIS-30 downscale. Unable to reset for any period of time | N | Y |  | N | YES | <D> **** Detailed Description **** ARM-RIS-30 downscale. Unable to reset for any period of time. ARM is attachment 8.1 equipment for PPM 13.14.11 for EAL RA3.1 and category 10-007 A1. PPM 13.8.1 attachement 7.7 has compensetory measures for this equipment. Recommend fixing this EP related equipment. <I> **** Actions Taken **** Informed supervision and Initaited this CR | 02-00-ARM-RIS-30
398241 | CR | 20190820 | CAQ | D | Recieved SLC tank level high alarm in. TDAS X077 also high. | Y | Y |  | N | YES | <D> **** Detailed Description **** Recieved SLC tank level high alarm in. TDAS X077 also high. Suspect that the level indicator is fouled again. Investigate and correct. Requset a more permanant fix as that this is essentially a nuisance and is in an area that takes time and dose to fix. <I> **** Actions Taken **** Wrote this AR. | 02-00-SLC-LI-601
398242 | CR | 20190820 |  | 3 | procedure revision, OI-07 |  |  |  | N | NO | <D> **** Detailed Description **** Procedure revision to OI-07, marked up copy in EDMS folder. <N> Revision 15 of OI-07 approved for implementation on 9/19/2019. No actions required.
398243 | CR | 20190820 | CAQ | D | 2019 DBAI (NRC) truncated information inadvertently provided |  |  |  | N | NO | <D> **** Detailed Description **** Earlier in the 2019 DBAI, an NRC Inspector requested a copy of the PPM 10.2.53 Scaffold Log for Long Term and Permanent scaffolds. This information is in an MS Excel spreadsheet on the S drive (ACTIVE SCAFFOLD LOGS.xls) and its LONG TERM and PERMANENT tabs were printed to printer PDF995 intending to create a pdf of the information to provide. It was not known or discovered prior to delivery of the information to the NRC that the pdf of the information was truncated when created in this fashion. As an ultimate end result, the pdf information provided to the NRC in response to their request was inadvertently truncated. This was in no way intentional. . Subsequently, the NRC Inspector identified a discrepancy between the number of Long Term scaffolds indicated verbally during a team interview and the number indicated on the pdf of the Long Term Scaffold Log provided earlier. . Investigation promptly re-created what had occurred as described above and determined that the information from the MS Excel spread sheet had to be selected and then printed to printer PDF995 using the Print Selected setting to result in a non-truncated pdf. . DBAI Team, Licensing, and Design Engineering personnel were notified upon confirmation of the problem and briefed regarding what had occured. The correct information from the PPM 10.2.53 Scaffold Log (Long Term and Permanent tabs) was re-collected and submitted for verification (to be provided to the NRC Inspector). This AR CR was initiated to document the occurrence. <I> **** Actions Taken **** As described above.
398244 | CR | 20190820 |  | 3 | Broken key on fence north of ASD building |  |  |  | N | NO | <D> **** Detailed Description **** craft discovered broken key on fence. <I> **** Actions Taken **** report to supervision cr <N> **** Equipment Description **** ASD fence door north.
398245 | CR | 20190820 |  | 4 | M&TE Suspended/ Lost |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #39506 Mitutoyo OD Mic- model 103-260 1in Last c/o 5/26/19 WO #02085914. OD Mic missing when box and card returned. Posssibly trashed. No Activity in Portal J. No Plant Impact. Suspended/lost. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
398249 | CR | 20190820 |  | 3 | VBModule service interruption |  |  |  | N | NO | <D> **** Detailed Description **** Users received error message when trying to access VBModules (including checkpoint tab in PQD) <I> **** Actions Taken **** Solution Center notified IS team. Identified it was a server issue possibly related to app pool refresh rate. The issue was resolved but will requre further evaluation to determine cause and solution. <N> Recommend NCAQ 3 ITMGMT
398251 | CR | 20190820 |  | 4 | External network switch failure | N | N |  | N | YES | <D> **** Detailed Description **** External corporate network switch DMZ34-104C-01 failed. This caused failure of Williams Time Clock, Facilities Key Boxes, and the ERO external network drops for NRC (unused except for in an actual ERO activation). <I> **** Actions Taken **** Replaced network switch. Confirmed services working. Notified EP, Williams, facilities, and IS leads. No further action recommended. <N> **** Equipment Description **** Network switch DMZ34-104C-01.
398252 | CR | 20190820 | CAQ | D | Degraded ninety degree fitting upstream of SW FE 39 | Y | N |  | N | YES | <D> **** Detailed Description **** During a walkdown for SW FE 39, it was identified that the 90 degree fitting upstream of the flanges is degraded. The shoulder of the flange was cut unevenly and it appears that an excessive amount of material may have been removed from the fitting in the past when maintenance was performed. Reusing this fitting to perform the work, replacing the piping in WO 02139804-01 would degrade the condition further.The fitting needs to be replaced due to the as -found condition of the 90 degree fitting and due to supports and interferences, additional welds will need to be added to replace the following upstream fitting as well; there is no accessibility to perform welds near the supports. . Plan to replace piping down to the 90 degree fitting at weld 36C1 (CVI ISO 317-00,39,1) to support the replacement of SW FE 39 flanges per EC 17505. ASME plan, W.O. and weld record will need to be updated. <I> **** Actions Taken **** Intiate AR/CR and returned the packages to planning. | 02-00-SW-FE-39
398254 | CR | 20190820 |  | 4 | Lighting in the RW 437' Truck Bay |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** About 50 percent of the lights in the Rad Waste truck bay are burned out. See pictures in EDMS. <I> **** Actions Taken **** Conveyed to my Supervisor and documented condition. <N> **** Equipment Description **** RW 437' Truck Bay Lights
398255 | CR | 20190820 |  | 4 | Board Presentation Required Revision |  |  |  | N | NO | <D> **** Detailed Description **** The presentation supporting Board approvals relating to the Horn Rapids Solar Storage and Training project required revision after the slides were provided to the members. The late revision was needed to align the presentation to the corresponding resolution and action memorandum. <I> **** Actions Taken **** Presentation revised and leadership notified.
398256 | CR | 20190820 |  | 4 | E-TR-N2-SPARE needs test reperformed |  |  |  | N | YES | <D> **** Detailed Description **** While review ing the oil sample results for the transformers it was recommended by SD Myers to reperform the Karl Fischer Moisture analysis test to confirm the percent saturation of water in the oil. The purpose of this CR is to document the need for a sample to validate the test results from 7/10/19 | 02-00-E-TR-S-SPARE
398257 | CR | 20190820 | CAQ | 3 | 2019 DBAI (NRC) Calculation E/I-02-95-01 Table Naming Error |  |  |  | N | NO | <D> **** Detailed Description **** This condition report does not effect equipment or the results and conclusions of calculation E/I-02-95-01. During the 2019 DBAI NRC inspection, an inspector identified that table B was missing from Calculation E/I -02-95-01 R06 "Calculation for overcurrent protective device settings and coordination for 480volt distribution system". This issue was reviewed by Design Engineering and found to be a documentation issue, where the table was renamed in revision 04 without updating other calculation sections that still reference the old name. Recommend assigning to AR-DEI for to update calculation references for resolution.
398258 | CR | 20190820 |  | 4 | Work did not advance on tablet or dataglance (trending) |  |  |  | N | NO | <D> **** Detailed Description **** Work order 02138238 was performed and completed on iPad with work taken to working, field work complete and closure notes entered into the comments screen. However upon review the next morning work still showed at Ready in dataglance. Work did not advance past ready through the entire process in status tracking. <I> **** Actions Taken **** Contacted eWp help group to work through problem Wrote CR for trending
398260 | CR | 20190820 |  | 4 | Inaccurate documents provided to Board Relations |  |  |  | N | NO | <D> **** Detailed Description **** Inaccurate Action Memo and Draft EB Resolution related to HRSST BESS provided to PAO Board Relations prior to EB meeting. Error noticed day prior to EB meeting. Error due to worker practices/lack of verification and validation. <I> **** Actions Taken **** Corrections immediately made and revised documents provided to PAO Board Relations as soon as possible for use at the EB meeting. CR initiated for trending. Thumbs down drafted.
398262 | CR | 20190820 |  | 3 | DBAI 2019 (NRC) identified enhancement opportunity SW siphon | Y | N |  | N | NO | <D> **** Detailed Description **** One of the areas of interest for an inspector during DBAI was the Service Water siphon line. The NRC communication GO2-14-126 and License Amendment No. 233 say "The quarterly SW operability testing demonstrates that adequate flow is being produced and that the line is not impaired during operation." Currently our process does not quantify this monitoring. Suggest updating surveillance procedure to validate siphon line flow. . Note, this is not the first time the siphon line adequacy has been brought up by the NRC. <I> **** Actions Taken **** Wrote this CR. Discussed with Design Engineering Manager and DBAI Operation representative.
398263 | CR | 20190820 |  | 4 | Computer Point L087 flatlined | N | N |  | N | YES | <D> **** Detailed Description **** PPC computer point L087 has been stuck, unchanging since 1/18/18. Based on the trend (see EMDS), it appears that it may be an instrument issue or a PPC mux issue. Please investigate and repair. . This point is also used to feed calculated points T008, T009, and T010 (Condenser Vacuum LP, IP, and HP) which are impacted by this flatlined data point. All 3 points use L087 so the relationship between them is still valid, however the calculated values are shifted high. . Recommend to maintenance for investigation and repair. <I> **** Actions Taken **** Notified SM and generated CR/WR <N> L087 is the computer point for the cable spreading room barometric pressure. | 02-00-PL-PT-1
398265 | CR | 20190820 | CAQ | D | (QA) Pipe Cap Leaking on SW-V-664 & SW-V-666 | Y | N |  | Y | YES | <D> **** Detailed Description **** (QA) Pipe Caps on SW-V-664 & SW-V-666 are leaking at the threaded connections onto RRA-CC-1. Leak rates are less than 1 drop per minute. Issue was identified by QC during performance of ASME Code VT-2 Leakage Examination per WOT 02139801-03. Leakage is outside the ASME Code boundary / area of interest. . . <I> **** Actions Taken **** Notified Control Room Supervisor, Maintenance Craft Supervisor, QC Level III and Qualtiy Services Supervisor. <N> Walked down pipe caps with SW-B running and noted weeping on the pipe cap threads which did not form a drop after observing for several minutes. | 02-00-SW-V-664,02-00-SW-V-666
398266 | CR | 20190820 | CAQ | D | DOE/EOF Safety Radio inop | N | Y |  | N | YES | <D> **** Detailed Description **** While performing the EOF/Alt EOF Radio Controller Functional Test, WO 02138110, the DOE EOF Safety Radio did not function as expected and is inoperable. For safety communication purpose the Dial-up, Fax and Crash are all operational. . Also while performing the NOAA Weather Speaker volume test associated with this same Work Order there was excessive static. The antenna connection was adjusted and the static was eliminated. <I> **** Actions Taken **** EP, Control Room, and SCC have been notified. <N> **** Equipment Description **** DOE Safety Radio in the EOF
398267 | CR | 20190820 |  | 3 | Pump appears to be rotating backwards SO-P-SOBP | N | N |  | N | YES | <D> **** Detailed Description **** Performed PMT for 0205658904 PMT for SO-542-1A2C. Used rotation strobe light set to 1770 RPM and verified rotation of pump on the label on top of pump housing. Bump started pump and used strobe pump looks to be running backwards. Contacted MCR and supervisor wrote CR. Need to swap leads to correct issue. Ops verified that pressure was at 12psi prior to pump start and after pump start the pressure did not increase giving second data point that pump is not running correctly. <I> **** Actions Taken **** contacted MCR had them rehang/hang Danger clearance | 02-00-SO-P-SOBP
398268 | CR | 20190821 | CAQ | D | CRD-HCU-1419 rod accumulator trouble due to low N2 pressure. | Y | N |  | N | YES | <D> **** Detailed Description **** Rod accumulator trouble alarm on CRD-HCU-1419 due to low nitrogen pressure. Cleared alarm per SOP-CRD-HCU. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-HCU-1419
398270 | CR | 20190821 |  | 4 | Indication issue on HV-V-31A | N | N |  | N | YES | <D> **** Detailed Description **** HV-V-31A has been backseated to open per WR#29150476. Checked indication with control room and indication was/is closed. This indication does not match the action performed. We obtained a trace via the Votes Infinity data aquisition unit which shows a clear full trace with a backseat final position. Contacted ops to hang caution tag to reflect backseat on this valve. The HV-V-30A was taken to the close position which only allows steam to travel via the 31A route. <I> **** Actions Taken **** Contacted ops, engineering and supervision of valve position indication concern. | 02-00-HV-V-31A
398271 | CR | 20190821 | CAQ | D | Control Room exit door C-403 | Y | Y |  | N | YES | <D> **** Detailed Description **** The metal plate above the door knob of the Control Room exit door door C-403 stairwell side is loose. <I> **** Actions Taken **** Initiated work request 29151162 | 02-00-W-DOOR-C403
398272 | CR | 20190821 | CAQ | D | OG-AY-12B reading high | N | Y |  | N | YES | <D> **** Detailed Description **** see EDMNS for trend. Normally .1 to .2 % H2. Now reading .4%. Generally indicates an issue with the detector. Suggest cal verification to confirm. | 02-00-OG-AY-12B
398274 | CR | 20190821 |  | 4 | RB 572, 7BB room lighting is degraded. | N | N |  | N | NO | <D> **** Detailed Description **** There are 3 fixtures, each with 4 bulbs, in MCC 7BB room. Two of the three fixtures need all bulb replacements and the third requires some bulb replacement. <I> **** Actions Taken **** CR & WR written. non-essential lighting <N> **** Equipment Description **** RB 582, MCC 7BB room lighting
398275 | CR | 20190821 |  | 3 | Housekeeping in RB 572, 501 and 471. |  |  |  | N | NO | <D> **** Detailed Description **** In RB 572 hatch area is an LLRT test hose from R 24, Another LLRT test hose is in RB 501 TIP MEZZ room area. On RB471 by NE elevator, the SA air hose station on the column has an air hose attached with no Work In Progress sign. The air hose is attached with tie wraps to overhead and heads over the the 471 SE area where it is neatly coiled on the ground (NO Work in Progress sign) <I> **** Actions Taken **** CR written, Housekeeping Area Owners notified with this CR number. <N> **** Equipment Description **** Housekeeping in RB 572, 501, and 471 WR 29151200 written and cross referenced.
398276 | CR | 20190821 |  | 3 | Trend shows negative bias in samples per HPI-4.3A |  |  |  | N | NO | <D> **** Detailed Description **** There is no impact to the station at this time since all procedure acceptance criteria were met. The results of DLR blind spikes performed per HPI-4.3A in 2019 showed a large negative bias. One difference noted was that the spiked DLRs were stored in a Lead Pig, which would add to the negative bias by changing the background subtraction performed by the vendor on these spiked DLRs. A review of 3 years of data showed that there is a general negative bias, so this should be investigated to help improve performance. Recommend assigning to AR-RPSPT group.
398277 | CR | 20190821 |  | 3 | Purchase of a Third RW Resin Liner Grapple |  |  |  | N | NO | <D> **** Detailed Description **** ALARA Suggestion: Purchase of a Third RW Resin Liner Grapple would save dose by reducing the down time of grapple system in the disposal of processed resin. The Remote Grapple system has proven effective in reducing workers accumulated dose. When one or both of the grapples are not available the liners must be rigged manually. Manually rigging requires workers to enter dose rates which otherwise could be avoided. If a spare grapple was available, personnel exposure could be reduced by utilizing the spare grapple when the other grapple is being serviced. <I> **** Actions Taken **** Made Suggestion to RP supervision. Wrote CR
398280 | CR | 20190821 |  | 3 | WMA-FN-53A control switch in off at the ARSD panel |  |  |  | N | NO | <D> **** Detailed Description **** While researching the impact of the upcoming E-TR-7A/2 replacement in the simulator I noticed that WMA-FN-53A was not running when the alternate remote shutdown (ARSD) panel was activated using ABN-CR-EVAC. WMA-FN-53A is always running in the plant to provide cooling to the division 1 switchgear rooms. The ARSD panel The ARSD panel switches are typically aligned to maintain normal plant configuration so that normally running equipment stays running. In this case the WMA-FN-53A control switch is in off at the ARSD in the plant and in the simulator by surveillance procedure; OSP-INST-M101 and OSP-INST-B702. The purpose of this CR is to research and document the correct desired position of the WMA-FN-53A control switch on the ARSD and/or add a step to ABN-CR-EVAC to start WMA -FN-53A, or verifying it is running.
398281 | CR | 20190821 | CAQ | C | Typographical error in FSAR Appendix J references |  |  |  | N | NO | <D> **** Detailed Description **** During prepartion of CMR 3522 R001, an error was found in FSAR appendix J. Reference J.7-20 is called out as Letter BRWP-RO-81-288, dated July 29, 1981, â€œForty-Year Integrated Dose for Radiation Zones in the Reactor Building.â€ However, BRWP-RO-81-0288 is actually "MEETING MINUTES & ACTION ITEMS FROM ELECTRICAL & MECHANICAL MEETINGS". Further investigation of microfilm in Records by CR author confirms this. The correct number is BRWP-81-0288. . Additionally, reference J.7-21 is called out as BRWP-RO -81-181. This is the correct letter number for this document ("Forty-Year Integrated Dose for Radwaste and Turbine Buildings.â€) but should be changed from -181 to -0181 to make searching records easier. <I> **** Actions Taken **** Generated CR and notified supervision.
398282 | CR | 20190821 |  | 4 | P06 spreadsheet review/approval validation |  |  |  | N | NO | <D> **** Detailed Description **** During the Engineering review of the R25 spreadsheet data in support of the PO.6 milestone, there have been several erroneous review/approvals timestamps where no review or approval has yet been performed by the individual listed. Initiation of this CR is intended to document that while the spreadsheet indicates reviews as completed it may not be valid that the expected validation of recommended R25 scope has been performed by that individual. This is mainly a concern if we were to use this spreadsheet for in the future for questions to the individual that â€œperformedâ€ the work. <I> **** Actions Taken **** Wrote CR to only document that if post-review happens later that validation may not be correct. At this time no action is requested to be made, P06 scoping is continuing with a team reviewing the ranking.
398285 | CR | 20190821 | CAQ | C | MT&E Found out of tolerance |  |  |  | N | I DONT KNOW | <C> CR parent reopened to add document to EDMS. <D> **** Detailed Description **** Calcode #0068183 Ashcroft Sensor- model HQS-2 30psig found OOT & Rejected- Over pressurized. EFIN to Evaluate the 21 usages. DEF #7246A generated. <I> No degraded equipement identified. Recommend a CR action to efin to complete evaluation and generate a CR on the identified impacts.
398287 | CR | 20190821 |  | 4 | MT&E Found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0063823 Heise Pressure Calibrator- model PTE-1 found OOT & adjusted within specs. Not used in the OOT Range of Volts. DEF #7248A written. No Plant Impact. No Action Required.
398288 | CR | 20190821 | CAQ | C | Drawings Need to be Update |  |  |  | N | YES | <D> **** Detailed Description **** WO 02081479-01 was performed to install an NLI fused disconnect at E-MC-3D, cubicle 7B for the new Kelley Glove Box machine per REI AR 325010. WO 02081479-01 was completed on 10/31/2019 but the drawings were not updated to reflect the current configuration. Impacted drawings E503-6, E528-11A, E535-16A, E535-16D and CVI drawing 49-00, 86, 1 require immediate update. <I> **** Actions Taken **** Informed my supervisor Informed the design supervisor Informed the electrical shop manager Informed the SM . Drawing Changes are: E503-6 - the type â€œG-Sâ€ for E-DISC-3D7B changes to type â€œG -Nâ€. E528-11A - the E-DISC-3D7B switch frame rating and fuse changes from 60 and 60 to 200 and 100 respectively. E535-16A - cub 7A becomes a 12â€ space, cub 7A1 moves up one section and cub 7B becomes a 24â€ cubicle in the MC-3D front view layout. E535-16D - cub 7A becomes a 12â€ space, cub 7A1 moves up one section and cub 7B becomes a 24â€ cubicle in the MC-3D front view layout. CVI drawing 49-00,86,1 â€“ remove ref to CVI 952-00,16,1 for E-DISC-3D7B replace with switch frame rating 200 and fuse 100 amp and type G-N. <N> It should be noted that the work order is still at working status with several tasks not complete, to include removal of tags. This work was only partially implemented and then removed from the schedule with no indication of when it would be rescheduled. This leaves the station in an undesirable condition with risk of loss of Configuration Management. Recommend an action to Work Control to determine how to prevent re-occurence or ensure work started is completed in a timely manner. . Apparently and RIE under AR EVAL 325010. DOC AS 325010-03 already exists (with System Engineering). | 02-00-E-DISC-3D7B
398289 | CR | 20190821 |  | 4 | CATID 0058300025 quantity does not match Warehouse as found. |  |  |  | N | NO | <D> **** Detailed Description **** CATID 0058300025 shows two onsite for use for upcoming work orders in the 9/2 and 9/9/19 work weeks. Upon further review, Warehouse personnel and craft were not able to find the UTC that shows in Warehouse #3. Generated CR for trending. Note at T-7 when scope committment was made the basis for inclusion of work into the 9/2/19 and 9/9/19 for accumulator replacement was based on 2 accumulators being available. To supporrt the work in the 9/9/19 a spare accumulator staged on RW 507' will require refurbishment. <I> **** Actions Taken **** Generated CR.
398290 | CR | 20190821 |  | 4 | MT-CRA-9 pendant controller Cord Grip Connector | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During the annual inspection of MT-CRA-9 (WO#02134246-02), electricians noted that the Control Cable that runs between the pendant controller and the relay/contactor junction box, does not have the proper outer insulation into the cable connector at the pendant side. The inspection is performed per PPM 10.4.10 whereas "the pendant station is adequately supported so that the electrical conductors are not strained (if applicable). There appears to be proper strain relief and there does not appear to be any electrical hazzard present. <I> **** Actions Taken **** Notified Supervisor, Write CR and WR upload picture to edms. <N> **** Equipment Description **** MT-CRA-9A
398291 | CR | 20190821 |  | 4 | 14 Pieces of M&TE Suspended until R25 |  |  |  | N | NO | <D> **** Detailed Description **** 14 Pieces of M&TE have Passed Closout Calibrations and are Now Suspended until R25. Not used since Calibrated. No Plant Impact. See list for Calcodes, Descriptions, Models and associated DEF #'s. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
398292 | CR | 20190821 |  | 3 | Gross Megawatts on Plant Status uses drifting signal B059 | N | N |  | N | NO | <D> **** Detailed Description **** The Gross Megawatts value from the Plant Status page comes from a TDAS signal ENW.CGS.B059. This TDAS signal, and many others, are known to experience seasonal drift, a chronic computer/grounding issue, cause unknown. Seasonal drift causes readings to be low in the summer by >15 MWe and high in the winter by >3 MWe, as compared to the DEH signal for Gross Megawatts, T3 1230A. Low readings in the summer give the impression the plant output is degraded, and the impression in the winter than plant output is better than actual . Recommend DEH signal ENWBU.MODBUSH .T3 1230A be displayed on the Plant Status page. This signal is not subject to seasonal fluctuations and drift. See EDMS for signal comparison. <I> **** Actions Taken **** Initiated CR. Discussed with Computer Engineering. Recommend Plant Status page be modified.
398294 | CR | 20190821 | CAQ | D | replace damaged tubing on FP-V-SGT/36 | Y | N |  | N | NO | <D> **** Detailed Description **** during restoration of WO# 02103648-01, we found the tubing to be damaged between the solenoid and the actuator input. <I> **** Actions Taken **** stopped and reported to supervisor. After expanding the team, it was decided to replace the tubing in a new task 06
398295 | CR | 20190821 |  | 3 | Floor coating found chipped during inspection |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of WO 02138318-01 Essential Fire Rated Penetration Seal and Essential Fire and Flood Barrier Operability Inspection. Coatings personnel identified a small chip in the coatings not in the concrete on the RW -484-C313-Floor (HVAC Chase). <I> **** Actions Taken **** Notified supervision, prepped and repaired the coating, recorded deficiency in procedure. Discussed issue with PSRO. This chip was in the flood barrier. The degraded condition hsa been restored. There is no longer a DNC. No REGE/REP required.
398296 | CR | 20190821 |  | 3 | DBAI 2019 â€“ (NRC Identified) SFCP process improvements |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.5.20 (Surveillance Frequency Control Program Procedure) lays out the process for extending surveillance frequencies and is in alignment with NEI 04-10 guidance. The NRC identified potential gaps in the process such that there needs to be process triggers to ensure all pertinent information such as plant modifications are evaluated in the event that there is a delay between engineering evaluation and actual approval/implementation of the extension. Additionally PPM 1.5.19 (Surveillance Frequency Control Program) requires periodic monitoring of approved surveillance extensions and there also needs to be triggers in place to ensure that all pertinent information is evaluated such as plant modifications during those reviews as well. This CR is administrative in nature and should drive improvements to our SFCP processes and there is no impact to plant equipment. <I> **** Actions Taken **** CR written and MCR informed.
398297 | CR | 20190821 |  | 3 | 2019 DBAI (NRC) - Discrepancy in PPM 10.2.53 |  |  |  | N | NO | <D> **** Detailed Description **** PPM 10.2.53 Section 7.4.4b should say â€œbounded by existing calculations and 50.59â€ rather than â€œbuilt within the generic configuration bounds described in 7.4.3â€ to align with Section 7.4.4a and Section 4.3.4. That was the intent when the procedure was revised to include that wording â€œbounded by existing calculation and 50.59â€ based on Licensing input in CR 315686. The Degreed Civil Engineer is able to determine that a scaffold is bounded for minor changes. <I> **** Actions Taken **** Generated CR to correct PPM 10.2.53 Section 7.4.4b. There is no plant impact in clarifying the procedure.. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
398298 | CR | 20190821 |  | 3 | Hi-Hi level alarm probe on SERDS stopped working | N | N |  | N | NO | <D> **** Detailed Description **** When preparing to take bead resin, it was discovered the Self-Engaging Rapid Dewatering System (SERDS) liner HI-HI level alarm probe stopped working when it was pre -operational tested. The high level alarm probe was functioning properly. SERDS is not classified as installed plant equipment. <I> **** Actions Taken **** Informed supervision. Consulted with the vendor, who recommended the probe be replaced. Replacement probes (one is a spare) were ordered on 8/21/19, to be delivered, installed and tersted on 8/26/19. Recommend classify as trend. <N> The SERDS hi-hi level alarm probe was cleaned and is now functional. No further action required.
398299 | CR | 20190821 | CAQ | C | Shift Technical Advisor Initial Training GAP |  |  |  | N | NO | <D> **** Detailed Description **** The Shift Technical Advisor qualification (STAA) does not have a simulator training or evaluation required as part of initial qualification. This does not satisfy the requirements of ACAD 14-002, Guidelines for the Training and Qualification of Shift Technical Advisors. ACAD 14 -002, section 4.10.1 requires an evaluation in the simulator focusing on the STA roles and responsibilities prior to final qualification. In addition, FSAR 13.2.2.3.1.a states that the STA initial training program will normally include â€œCompletion of the SRO replacement operator training program or equivalentâ€. While the STAA qualification directory meets this requirement through SRO level examination requirements during initial and requalification training, a simulator training and examination requirement added to TDI-12, Shift Technical Advisor/Incident Advisor (STA/IA) Program would provide a more comprehensive qualification. Review of ANSI 18.1-1971 determined there are no STA specific requirements listed. This identified gap would not affect the qualifications of currently qualified STAs. <I> **** Actions Taken **** Notified Operations, Training, and Licensing Management.
398300 | CR | 20190821 |  | 3 | 2019 DBAI (NRC) No PMID-RQs for PPM 10.2.53 4.3.1 or 4.3.3 | N | N |  | N | NO | <D> During a 2019 DBAI team interview with the NRC inspection team on 8/21/19, it was noted that PMID-RQs apparently do not exist for PPM 10.2.53 Precaution and Limitation 4.3.1 periodic inspection of permanent scaffolding or for PPM 10.2.53 Precaution and Limitation 4.3.3 periodic inspection of long-term scaffolding. Periodicity for both of these inspections stated in PPM 10.2.53 are yearly or every 24 months for high radiation and inaccessible areas. These PMID-RQs need to be established to ensure these PPM 10.2.53 Precautions and Limitations are being satisfied. Additionally, PMID-RQ 24028-02 appears to exist for PPM 10.2.53 Precaution and Limitation 4.3.7 monthly walkdown of accessible scaffolds (or every twenty-four months for high radiation and inaccessible area scaffolds). However, the PMID-RQ actually appears to only address monthly inspection of accessible scaffolds. This apparent gap for PPM 10.2.53 Precaution and Limitation 4.3.7 also needs to be closed. . It appears that completion of these inspections has been happening due to the efforts of a small number of individuals (EN Scaffolders) working without PM WOs. Without PM WOs, there likely have been exceptions to the yearly or twenty-four month periodicity specified in PPM 10.2.53 and there likely have been deltas in the arena of ALARA planning.
398301 | CR | 20190821 |  | 4 | Declared handgun at the Security Checkpoint |  |  |  | N | NO | <D> **** Detailed Description **** At approximately 1400 hours a handgun was declared the security checkpoint by a visitor. The visitor was a regional salesman who did not have any points of contact from Energy Northwest. After Shift Manager, Security Supervision and Benton County were notified the individual was directed offsite. <I> **** Actions Taken **** CR generated.
398302 | CR | 20190821 |  | 4 | MT&E found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0066432 Hytorc Hydraulic Torque Wrench- model Avanti P7 found OOT & Rejected. Reliability questioned for future use. Not used during Calibration cycle. DEF #7261A written. No Plant Impact. No Action Required.
398303 | CR | 20190821 |  | 4 | RCA boundary should have a swing gate |  |  |  | N | NO | <D> **** Detailed Description **** The RCA boundary on top of the Condensate Storage Tank enclosure is posted on a chain which must be manually moved to enter the RCA area. The creates a risk that the boundary will be inadvertantly left down. GEN-RPP-04 step 3.10 states " Except ofr radiological barriers tempoarily moved during ingress and dgress (E.G. entry or exit through a swing-gate(, only RP personnel should install, remove or alter radiological postings and barriers.' <I> **** Actions Taken **** Wrote this CR and work requrest to improve the current posting situation. <N> **** Equipment Description **** RCA boundary on top of CST enclosure
398304 | CR | 20190821 |  | 4 | SAFETY Concern- Transformer Yard Pathway Markings Need Paint | N | N |  | N | NO | <D> **** Detailed Description **** Nether the East to West nor North to South pathway markings in the transformer yard are clearly marked anymore. The few rocks that do still have visible paint are dispersed. See photos in EDMS <I> **** Actions Taken **** Discussed with RP Supervision and the PSRO. <N> **** Equipment Description **** Transformer Yard
398308 | CR | 20190821 |  | 3 | Procedure Revision, SWP-FFD-01, GBP-SEC-02, SWP-FFD-04 |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate verbiage in SWP-FFD-01 for periodicity of inspections to ensure alignment with 10 CFR Part 26. Update GBP-SEC-02 to differentiate between corporate testing and nuclear testing. Evaluate periodicity of work hour reviews in SWP-FFD-04.
398310 | CR | 20190821 |  | 3 | Drawing Needs To Be Updated |  |  |  | N | NO | <D> **** Detailed Description **** Drawing EWD-46E-047 indicates that auxiliary switch normally closed contact b (terminal points 7B-7C) from circuit breaker, E-CB-TRB is used on EWD-46E-047. However, contact b (terminal point 7B-7C) cannot be located on the EWD-46E-047. This AR CR has no impact on Plant Operation. This is just a documentation issue. It is recommended that this should be assign to Electrical Design. <I> **** Actions Taken **** Inform Supervision and wrote CR.
398317 | CR | 20190821 |  | 3 | Degraded Condition of Grounding SCW Skid | N | N |  | N | NO | <D> **** Detailed Description **** Appears that the grounding lug connected to the Generator Stator Cooling Unit has possibly been bent over and back multiple times resulting in a cracked lug. <I> **** Actions Taken **** Notified PSRO, wrote CR. <N> **** Equipment Description **** 16/C 441` TG The Bonding/Grounding 2-hole lug at the base of the skid.
398318 | CR | 20190821 |  | 4 | CF-P-42A Found to be not pumping | N | N |  | N | YES | <D> **** Detailed Description **** On 8/20/19 Operation was asked by Chemistry to place CF-P -42A into service after a long period of down time. Clearance tages were pulled an the pump lined up and placed into service. Checking on the pump and inventory draw down later in the day indicated that the pump was not pumping. Operations adjusted the pumping rates from the Chemistry recommended settings of 50/50 to 95/100. Indication were that the pump was now pumping. Due to low residuals of scale control chemical, a manual feed of 100 gals was added to cover any lost addition time. <I> **** Actions Taken **** Manual feed of 100 gals to cover pumping down time and low residuals due to high blowdown rates. Continue to monitor draw down rates to ensure the pump is still pumping. <N> **** Equipment Description **** CF-P-42A
398319 | CR | 20190821 | CAQ | D | SLC-TK-1 High Level alarm locked in | Y | Y |  | N | YES | <D> **** Detailed Description **** SLC-TK-1 has a locked in high level alarm. Computer trending shows the level made a step change. The detector/equipment likely needs to be rodded out. This last occurred on 8/13 <I> **** Actions Taken **** Dispatched OPS2, informed crs <N> High level alarm cleared and level indication returned to slightly above normal with no action taken. | 02-00-SLC-LS-600
398321 | CR | 20190821 |  | 3 | ACUMEN cyber security documentation error |  |  |  | N | YES | <D> **** Detailed Description **** Global Nuclear Fuel (GNF) provided cyber security documentation for ACUMEN, which incorrectly specified a Kiwi Syslog server. The delivered system uses the Elasticsearch, Logstash and Kibana (ELK) stack for a syslog server. Cyber security evaluations approved by CSAT evaluated the Kiwi syslog server but did not consider ELK stack. This is a documentation issue only with no impact on cyber security because the ACUMEN system has not been turned over for operation and remains in testing. <I> **** Actions Taken **** Recommend assignment to AR-RXFUEL to resolve conflict between cyber security evaluations and the ACUMEN system. . Issue reviewed with CSPM, cyber security personnel, project team, design supervision and GNF. | 02-00-PPC-COMP-ACUMEN
398323 | CR | 20190821 |  | 4 | Both CF-P-41 A and CF-P-42 A are not Pumping | N | N |  | N | YES | <D> **** Detailed Description **** Based on inventory draw down from TK-41 and TK-42, both CF-P-41A and CF-P-42A are not pumping. No tank inventory change between 11:00 AM and 4:30 PM 8/21/19. <I> **** Actions Taken **** Change sheet was sent to the Operations to begin manual feed of scale inhibitor at 50 gals/shift. Shift Manager informed of the findings. <N> **** Equipment Description **** CF-P-41A and CF-P-42A
398324 | CR | 20190821 |  | 3 | DBAI 2019 (NRC) - Observation regarding LOP/LOCA STI |  |  |  | N | NO | <D> **** Detailed Description **** There is no impact to the approved surveillance frequency extension (reference AR 367211), this CR documents a NRC recommended enhancement to the existing STI technical evaluation for completeness. During a DBAI discussion with the NRC, one of the inspectors provided the following observation regarding the Surveillance Test Interval Evaluation performed under AR 367211 on LOP/LOCA testing. The NRCâ€™s observation was that the Qualitative Analysis documented focuses too narrowly on the Dieselâ€™s ability to reliably generate the required voltage and frequency at rated speed. The NRC inspector emphasized that a core functional requirement is that the Diesel Generator must be able to respond dynamically under loaded conditions, and that comprehensive verification of this functionality is only fully verified during this particular LOP/LOCA testing. Based on the NRC observation provided, recommendation is that additional engineering evaluation be conducted to ensure the qualitative analysis provided to endorse and justify this STI accounts for all functional requirements of the Diesel Generator. <I> **** Actions Taken **** Discussed this with the DBAI Engineering, Licensing, and Operations team. Notified Shift Manager, initiated this CR.
398327 | CR | 20190821 |  | 3 | 2019 DBAI (NRC) - PPM 10.2.53 corrections/enhancements |  |  |  | N | NO | <D> **** Detailed Description **** During an interview with the NRC inspection team for the 2019 DBAI regarding PPM 10.2.53 (Scaffolding) some areas for improvement of the procedure wording were identified. 1) Precaution and Limitation 4.2: Change "Future proposed ..." to "Proposed ...". This is an enhancement. 2) Precaution and Limitation 4.3.1: Change "Reviewed yearly, ..." to "Inspected yearly, ...". This is a correction. 3) Precaution and Limitation 4.3.3: Change "... reviewed periodically ..." to "... inspected ...". This is a correction. Scaffolder input was that the actions for Precaution and Limitations 4.3.1 and 4.3.3 were physical walkdown inspections, not just reviews. Inspections are what is appropriate. See the mark-up attached to the EDMS of this AR CR. During the interview, there was also a question if additional PPM 10.2.53 guidance for potential impacts upon existing lighting should be added. However, understanding from the CGS DBAI team is that this question was subsequently addressed (no additional wording for the procedure needed). <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
398328 | CR | 20190821 |  | 3 | Defective office table |  |  |  | N | NO | <D> **** Detailed Description **** Office table found to have two stripped screws connecting table top to base which caused the tabletop to tip when weight applied to it . An individual standing next to table leaned hand on corner of table and the top tippped up. Another individual sat down in chair next to table and put arm on it and tabletop also tipped. That's when it was noticed that the screws were out and the table top was only connected by 2 screws on one side. <I> **** Actions Taken **** Put a warning sign on table stating "Broken, do not lean on table". Notified department manager. <N> Facilities inspected table and rescrewed in table top to base. Table has been fixed. No more action needed.
398329 | CR | 20190821 | CAQ | D | Review of TSP-CONT-R801 identified errors in the leakage sum | Y | N |  | N | NO | <D> **** Detailed Description **** During post R24 outage review of WO 02111609-01 TSP-CONT -R801, Primary Containment Isolation Valve and Penetration Leak Test Program, administrative errors were identified in the leak rate summation table. Specifically, the combined X-17A, 17B penetration minimum pathway leakage value was recorded as 2215 sccm and should be 264.25 sccm utilizing As-left leakage values from WOT 02085916-08 for RFW-V-10A and 02085914-08 for RFW-V-10B. . The X-23 penetration As-left minimum pathway leakage was recorded as 82 sccm and should be 42 sccm per WOT 02117191-01. The aggregate of these errors is conservative reducing the total As-left minimum pathway total from 9552.4 sccm to 7542 sccm and well below the acceptance criteria of 0.6 La or 72, 922 sccm. Additionally, an error was discovered in the maximum pathway total for penetration X-23 resulting in a slight increase of 48 sccm increasing the total maximum pathway summation to 20,408.5 sccm and also well below the acceptance criteria of 0.6 La or 72, 922 sccm. <I> **** Actions Taken **** Notified Supervision, Shift Manager, Licensing <N> Changes to the leakage summation calculation, as documented in this CR, have already been included.
398330 | CR | 20190821 |  | 4 | RFP Comment due date/time Missed |  |  |  | N | NO | <D> **** Detailed Description **** Environmental Services was working on a response to a request for proposal and missed the applicable time for submitting comments. Supervisor understood the deliverable due date that comments were due but failed to validate and verify the specific time the comments were due. Recommend CR for trending. <I> **** Actions Taken **** Discussed enablers missed and learnings in morning staff meeting wth Environmental Services team.
398331 | CR | 20190822 |  | 4 | RWCU Pump A Trouble Alarm P602-A5.4-7 due to low CRD Purge | N | N |  | N | YES | <D> **** Detailed Description **** RWCU Pump A Trouble due to low CRD Purge flow (oscillating between 1.4-2.0 gpm) the setpoint is 1.5 gpm. Alarm cycles on and off. <I> **** Actions Taken **** Flushed the purge line via CRD-FCV-512A and set flow at ~2gpm. Alarm is continuing to cycle. <N> **** Equipment Description **** RB 522 RWCU Pump Area | 02-00-CRD-FS-2A
398332 | CR | 20190822 |  |  | PAAP HVAC Requires Maintenance |  |  |  | N | YES | <D> **** Detailed Description **** The temperature inside the PAAP is rising. There is a possible HVAC issue. <I> **** Actions Taken **** Initiate CR/WR. Security Supervision and Shift Manager notified. Doors opened to allow for air flow. All areas were walked down and no security systems are impacted at this time, <N> **** Equipment Description **** PAAP HVAC Unit
398333 | CR | 20190822 |  | 4 | PAAP HVAC | N | N |  | N | YES | <D> **** Detailed Description **** The temperature is rising in the PAAP. HVAC is not functioning as designed. <I> **** Actions Taken **** Initiate CR/WR. Security Supervision notified. Shift Manager notified. All areas were walked down and no security systems are impacted at this time. <N> **** Equipment Description **** PAAP HVAC Unit
398334 | CR | 20190822 |  | 4 | E-AY-TR/M2 Transformer Gas Analyzer Amber Caution Light Lit | N | N |  | N | YES | <D> **** Detailed Description **** E-AY-TR/M2 transformer gas analyzer amber caution light is illuminated. Temperatures were normal when compared with M1 and M3, Cooler Group #2 Alarm is still locked in, and normal visual inspection of transformer appeared to be normal. OPS4 logs direct CR to be written when amber caution light is illuminated. <I> **** Actions Taken **** Informed supervisor, wrote CR <N> **** Equipment Description **** Transformer yard. | 02-00-E-AY-TR/M2
398337 | CR | 20190822 |  |  | DW Annulus Temperature GT LCS Limit of 150F |  |  |  | N | YES | <C> CR Canceled at the request of author. OPS Support Staff requested this through email verification. <D> The sacrificial shield annulus average temperature exceeded the LCS 1.7.1 Alert limit of 150F on 8/21/19 at 1600 and returned to 150F at 0400 on 8/22/19 . This condition is anticipated during hot weather. This CR satisfies LCS compensatory measure 1.7.1..A.2. <I> DW cooling is maximized with CBD at 3000 gpm. <N> This is a duplicate of CR 398338 and can be canceled | 02-00-CN-TK-1
398338 | CR | 20190822 | CAQ | D | DW Annulus Temperature GT LCS Limit of 150F | Y | Y |  | N | NO | <D> **** Detailed Description **** The sacrificial shield annulus average temperature exceeded the LCS 1.7.1 Alert limit of 150F on 8/21/19 at 1600 and returned to 150F at 0400 on 8/22/19 . This condition is anticipated during hot weather. This CR satisfies LCS compensatory measure 1.7.1..A.2. <I> **** Actions Taken **** DW cooling is maximized with CBD at 3000 gpm.
398339 | CR | 20190822 | CAQ | C | CDA Assessment documents require revisions |  |  |  | N | NO | <D> **** Detailed Description **** On-going audits of Critical Digital Asset (CDA) assessments have revealed gaps that require revisions of the assessments. The gaps have been based on revisions to the process that require different forms, changes to make more consistent documentation, and changes based on industry operating experience. <I> **** Actions Taken **** The audit of all CDA assessments is on-going to identify additional gaps. Gaps identified are being corrected as identified and submitted to Cyber Security Assessment Team (CSAT) for review and approval. This is not a reportable event under 10CFR73.54 <N> CDA assessment document revisions that are needed are caused by changes in the assessment process (based on both internal and external influences) , requirements to provide more consistent responses, and add additional information to provide clarity. This item is low/medium risk as the industry inspections have identified similar issues at other stations and categorized the issue as both minor or as a NCV. CGS has not been inspected but has identified this issue based on review of operating experience.
398340 | CR | 20190822 | CAQ | C | Cyber PMs not conducted as aligned to industry |  |  |  | N | NO | <D> **** Detailed Description **** In some cases Cyber Security Preventative Maintenance (PM) activities have not been conducted per recent benchmarking. Some of the PMs not performed per industry benchmarking are updates to anti-virus definitions, select password resets, and baseline configuration reviews. <I> **** Actions Taken **** Working with Engineering to outline processes that will allow PMs to be conducted that align with industry operation experience.This is not a reportable event under 10CFR73.54 <N> Preventative Maintenance (PM) activities for Cyber Security need performed or updates of justification and frequency. The revisions that are needed are caused by changes in the industry benchmarking that was used as allowed by NEI 08-09 to create CGS Cyber PM strategy. This item is low/medium risk as the industry inspections have identified similar issues at other stations and categorized the issue as both minor or as a NCV. CGS has not been inspected but has identified this issue based on review of operating experience.
398341 | CR | 20190822 | CAQ | C | Classifications of CDAs not aligned to industry |  |  |  | N | NO | <D> **** Detailed Description **** Based on the review of industry operating experience it was identified that in some cases the classification of the Critical Digital Asset (CDA) needed to be changed from indirect to direct. <I> **** Actions Taken **** Identified those items that required an assessment revision and completed the updates. Assessments were reviewed and approved through Cyber Security Assessment Team (CSAT). The cyber team will continue to monitor industry operating experience and make changes as needed.This is not a reportable event under 10CFR73.54 <N> CDA assessment classification revisions that are needed are caused by changes in the industry benchmarking. This item is low/medium risk as the industry inspections have identified similar issues at other stations and categorized the issue as both minor or as a NCV. CGS has not been inspected but has identified this issue based on review of operating experience.
398342 | CR | 20190822 | CAQ | C | Baseline configuration documents requires revisions |  |  |  | N | NO | <D> **** Detailed Description **** On-going audits of Critical Digital Asset (CDA) baseline configuration have revealed gaps that require revisions. The gaps have been based on revisions to the process that require different information, changes to make more consistent documentation, and changes based on industry operating experience. <I> **** Actions Taken **** The audit of all CDA baseline configuration is on-going to identify additional gaps. Gaps identified are being corrected as identified and submitted to Cyber Security Assessment Team (CSAT) for review and approval. This is not a reportable event under 10CFR73.54 <N> CDA baseline document (digital master data sheets) revisions that are needed are caused by changes in the assessment process (based on both internal and external influences) , requirements to provide more consistent responses, and add additional information to provide clarity. This item is low/medium risk as the industry inspections have identified similar issues at other stations and categorized the issue as both minor or as a NCV. CGS has not been inspected but has identified this issue based on review of operating experience.
398343 | CR | 20190822 |  | 4 | 3 Pieces of M&TE Suspended until R25 |  |  |  | N | NO | <D> **** Detailed Description **** 3 Fluke Dig Multimeters- model 25 have Passed Closeout Calibrations and are now Suspended until R25. Not used since Calibrated. No Plant Impact. Calcode #C005069. DEF #7262A written. Calcode #37623. DEF #7263A written. Calcode #45137. DEF #7264A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
398344 | CR | 20190822 |  | 3 | Cyber Portable Media and Digital Device Expired Evaluations |  |  |  | N | NO | <D> **** Detailed Description **** On 8/15/2019, during an audit of Portable Media Digital Device (PMDD) evaluation forms, Cyber Security discovered that multiple forms had expired and not been renewed before their expiration date. During the investigation it was determined that the intent of the expiration date was for the PMDD that was needed temporarily but was applied to all PMDD.Â Â Â Â <I> **** Actions Taken **** Action was taken to update the forms. Also, as part of the effort to reduce cost/time, forms were updated to reflect that they will not expire unless the PMDD is needed temporarily or a re-evaluation is performed. This is identified as an impact to administrative processes only and not a reportable event for 10 CFR 73.54.
398345 | CR | 20190822 |  | 3 | Rad Ops Robotics Issues |  |  |  | N | NO | <D> **** Detailed Description **** While preparing for robot usage to investigate a steam leak on heater vent valve 31A, it was reported that the robots have not been able to be used as designed for several years. The old robot has had a broken antenna which has not be repaired for approximately 3 years. This requires the use of a fiber connection and makes operation of the robot take 2-3 times longer. The new robot has been waiting on procedure changes to account for the new control panel for nearly as long, which makes it unavailable for operation. <I> **** Actions Taken **** Notified rad ops supervision. Discussed issue with qualified individuals and developed a plan to support the investigation. <N> What is the EPN for the RP robot - HP-EQ-XXXXX?
398346 | CR | 20190822 |  | 4 | E-TR-M3 PENETRATION BOX | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-M3 Penetration Box is accumulating oil. <I> **** Actions Taken **** Initiated CR, informed CRS <N> Currently there is an open ODMI under AR 00393438 to cover this condition with the CT 303.3 termination box and how it may accumulate oil. Added all applicable cross references for this condition to XREF panel. T. Mclaen 8/22/19 | 02-00-E-TR-M3
398350 | CR | 20190822 |  | 4 | Declared Alcohol at the Security Checkpoint |  |  |  | N | NO | <D> **** Detailed Description **** Two BPA Contractors for the same job showed up to the Security Checkpoint and declared they had prohibited items in their vehicles. The BPA point of contact had shared prohibited item information with the company and the information was not passed on to the Contractors. Security Supervision, Shift Manager and Benton county were all notified. Benton County chose not to respond. The individuals were coached and denied access.
398352 | CR | 20190822 |  | 3 | Potential Trend- Training frequency changes |  |  |  | N | NO | <D> **** Detailed Description **** See EDMS for details. Recommend assignment to Training Management to evaluate each event to determine if a knowledge or skill gap contributed to an event. <I> **** Actions Taken **** Discussed with Training Management and Initiated Condition Report.
398354 | CR | 20190822 |  | 3 | Adverse trend in CW Chemical Feed pump reliability. | N | N |  | N | YES | <D> **** Detailed Description **** Since Jan 2018 there have been 38 Condition reports on CF -P-41A/B, CF-P-42A/B, CF-TK-41 and CF-TK-42. The pumps /piping has been clogging, requiring Operations to add by gravity drain and maintenance to flush piping, repair and replace pumps frequently. This is a financial and manpower burden to the station as well as affecting the ability to reliably protect main condenser components. Actions are needed to determine why pumps are clogging and not pumping (chemical reaction, contaminants in tanks, etc.) and correct the condition. List of ARs are in EDMS. <I> **** Actions Taken **** Discussed at 0615 meeting and took action to write adverse trend AR. | 02-00-CF-P-41A,02-00-CF-P-41B,02-00-CF-P-42A,02-00-CF-P-42B,02-00-CF-TK-41,02-00-CF-TK-42
398355 | CR | 20190822 |  | 4 | CW-CT-2A Level high | N | N |  | N | YES | <D> **** Detailed Description **** Water level high on deck plate of CW-CT-2A <I> **** Actions Taken **** Initiated CR | 02-00-CW-CT-2A
398357 | CR | 20190822 |  | 3 | COND-PI-A2G IMDS requires update |  |  |  | N | NO | <D> **** Detailed Description **** COND-PI-A2G location currently is listed at CM-IR-1 on IDMS. COND-IR-1 is actual field location of COND-PI-A2G. IMDS requires update to reflect actual location. <I> **** Actions Taken **** Notified supervision, wrote CR. <N> **** Equipment Description **** COND-IR-1
398359 | CR | 20190822 |  | 3 | Fire Protection buried pipe wall loss | N | Y |  | N | NO | <D> **** Detailed Description **** During buried piping inspection of 4â€ FP(211)-1 and 6â€ F P(211)-1 performed under WO 02130792, one reading on the 4â€ pipe showed a min UT measurement of 0.197â€ which is lower than 0.207â€ that represents 87.5% of t nom (0.237â€). The 0.197â€ reading indicates more than 12.5% wall loss since the time of installation, and as per ENG-SPS-07 a CR should be initiated and next inspection date calculated. As per NEI-09-14 rev.4 App.C â€“ the corrosion rate can be calculated to be 0.0013 in/yr (1.3 mils/yr). Assuming a linear corrosion rate and with t min of 0.1â€ (admin. limit based on calculated t min), the next inspection date for this pipe will be in 2075 (after 56 years). Both pipes are in good condition (see pictures and UT report in EDMS). Please assign level 3 action to buried piping engineer to update the risk ranking accordingly. <I> CR documents finding. No DNC to be addressed as rate of metal loss well within inspection periodicity and piping is functional.
398360 | CR | 20190822 | CAQ | C | Inconsistency In LCS & FSAR Closure Time for RWCU-V-4 | Y | N |  | N | NO | <D> **** Detailed Description **** LCS Table 1.6.1.3-1 lists the closure time for RWCU-V-4 as 21 seconds. FSAR Table 6.2-16 lists the closure time as 16.25 seconds. IST procedure OSP-RWCU/IST-Q701 Rev 7 hich is used to satisfy TS SR 3.6.1.3.5 for closure times uses 14 seconds as the action high level (conservative to both the LCS and FSAR values). There is an apparent inconsistency (documentation issue) between the LCS and FSAR that should be corrected. <I> **** Actions Taken **** Discussed with Engineering (E Corwin). Uploaded inconsistent documents into EDMS <N> **** Equipment Description **** RWCU-V-4
398361 | CR | 20190822 |  | 3 | Transformer Yard, NRC housekeeping/scaffolding concern |  |  |  | N | NO | <D> **** Detailed Description **** While escorting the NRC Resident during a tour of Transformer Yard, Resident had a concern with scaffolding. On the SW side by TR S, scaffolding is erected. The concern is under the erected scaffolding there are various scaffold pieces, is it appropriate to use the area under the erected scaffold as a "lay down" area (no sign posted). <I> **** Actions Taken **** SSS notified, CR written for trending & stating NRC Resident concern. <N> COMPONENT GROUP MANAGER contacted and will send someone to walk it down. OPS CR Initiator (names removed per procedure).
398362 | CR | 20190822 |  | 3 | Plumbing Design Spec 15D.2 needs to be revised |  |  |  | N | NO | <D> **** Detailed Description **** Section 3.4.1.7 Emergency Shower and Eyewash is in conflict with itself. The section calls out the use of a self -closing valve and requires that â€œâ€¦materials used for shower, emergency showers and eyewashes shall be in accordance with the manufacturerâ€™s recommendations and conform to ANSI Z358.1 (American National Standard for Emergency Eyewash and Shower Equipment).â€ However, the ANSI code does not allow for self-closing valves for showers and eye washes. In addition, sub section 3.4.1.7.1 also calls out a self -closing valve. This does not affect the operability of plant equipment. <I> **** Actions Taken **** Discussed with design/supervisor.
398363 | CR | 20190822 |  | 3 | Procedure enhancement for OSP-FPC/IST-Q701 |  |  |  | N | NO | <C> AR reopened at OPS request to make a change. <D> **** Detailed Description **** please remove the steps that declare FPC-P-1A/B inop and operable, They arent tech spec, <I> **** Actions Taken **** Wrote CR. Discussed with AOM WC
398364 | CR | 20190822 |  | 4 | DW-DWS-4 shower head does not meet min height requirement | N | N |  | N | YES | <D> **** Detailed Description **** Emergency shower DW-DWS-4 does not meet the ANSI Z358.1 minimum height requirement for the showerhead. Per the ANSI code the showerhead should be 82â€ to 96â€ above the floor. The showerhead is ~71â€ above the floor. This does not prevent the use of the shower. The shower is currently tagged out due to a leaking valve. <I> **** Actions Taken **** Informed supervisor. <N> **** Equipment Description **** W437' Room C124 | 02-00-DW-DWS-4
398367 | CR | 20190822 |  | 3 | Green USB mistakenly taken home |  |  |  | N | NO | <D> **** Detailed Description **** When the worker arrived home, he realized he had a green USB in his pocket. He immediately reported it to his supervisor and had positive control of it at all times. SWP-CSW-15 Section 6.7.1F states: LIMIT transportation of PMDD to locations that are needed to support authorized EN work (e.g., do not take portable media home). <I> **** Actions Taken **** Reported to Cyber and they destroyed the USB. <N> ITMGMT NCAQ-3
398369 | CR | 20190822 |  | 3 | 15.1.28 minor Rev. needed |  |  |  | N | NO | <D> **** Detailed Description **** During the latest revision of 15.1.28 the warehouse vehicles and forklift were given station numbers. These station numbers need to be removed because when the vehicle is unavailable we cannot meet the acceptance criteria for the procedure.
398370 | CR | 20190822 |  | 3 | Fall Protection Qualification Issue - Nine Canyon |  |  |  | N | NO | <D> **** Detailed Description **** The Nine Canyon supervisor was contacted about the lack of a SFAB â€“ Fall Protection qualification for a Wind Generation Tech in the PQD database. The individual was hired on 1/3/2017. The supervisor indicated that the individual was assigned SFAB on the Personnel Requirements Form at the time of hire and had documentation for fall protection training sent to the Training Department upon receipt. <I> **** Actions Taken **** The supervisor was asked to contact Training Support to correct the issue. <N> Email send to QMS to get the Qual added for the affected individial. No addition actions necessary.
398371 | CR | 20190822 |  | 3 | First Aid/CPR Qualification Issue â€“ Nine Canyon |  |  |  | N | NO | <D> **** Detailed Description **** The Nine Canyon supervisor was contacted and asked why he was the only person at the site qualified for FPAE â€“ First Aid/CPR/AED. He stated that all the Wind Generation Techs are trained by Energy Northwest training personnel and are qualified, but not showing up in the PQD database. <I> **** Actions Taken **** The supervisor was asked to contact Training Support to correct the issue. <N> Emailed QMS and had the Quals added. Quals are not all up to date and have been advised as voluntary. Quals will be updated after next training.
398372 | CR | 20190822 |  | 3 | PPM 10.20.1 gasket and sealant discrepancy |  |  |  | N | NO | <D> **** Detailed Description **** PPM 10.20.1 step 7.7.20 for installing new gasket on soakback pump discharge tubing flange is not consistent with EC-10188. PPMs 10.20.12, 10.20.16 and 10.20.19 are also different on gasket use and sealant (form a gasket) or lubricant. EC-1088 approves an alternate Multi-Swell gasket when experiencing unacceptable leakage at identified locations. <I> **** Actions Taken **** Recommend revising PPMs 10.20.1, 10.20.12, 10.20.16 and 10.20.19 to bring into alignment with EC-10188.
398373 | CR | 20190822 |  |  | m,zjdfsa,mjdfhg |  |  |  | N | NO | <D> **** Detailed Description **** ,sdfjhsdlfh <I> **** Actions Taken **** dfghdr
398374 | CR | 20190822 |  | 3 | PPMs 10.20.1 & 10.20.12 not updated for new pump |  |  |  | N | NO | <D> **** Detailed Description **** In 2016 PPM 10.20.19 Revision 007 step 7.9.1h.5 (page 33) lowered torque value for new circulating pump fasteners to 5 ft-lbs. The old pump fastener torque value was 15-16 ft -lbs. PPMs 10.20.1 and 10.20.12 were not revised to reflect this new torque value. <I> **** Actions Taken **** Recommend revising PPMs 10.20.1 and 10.20.12 to bring into alignment with correct torque value for new pump fasteners.
398375 | CR | 20190822 |  | 3 | Rented material marked with purple paint |  |  |  | N | NO | <D> **** Detailed Description **** Rented scaffold materials to support CST inspections arrived on site marked with purple paint. Per GEN-RPP-04, "tools or equipment marked with purple paint are considered radioactive material, as they may have fixed contamination up to 5000 dpm/probe area." There are allowances to release items from the RCA that are painted purple by vendors; however, there is no mechanism to ensure that a casual observer would identify these scaffold items as non-radioactive. Recommend that vendor-supplied or rented equipment be specified to be free of purple paint markations or cease using purple paint to denote radioactive material. <I> **** Actions Taken **** Surveyed scaffold material to verify it was free of contamination. Placed an information tag on the scaffold rack to denote that the purple paint was applied by the vendor and the materials are not radioactive. <N> A snapshot benchmark will be conducted under AR-BA 398499 on the use of purple paint for radioactive material markings. AR has been cross referenced - no further actions required under this AR-CR.
398379 | CR | 20190822 |  | 4 | E-RLY-64/85/82 As found TIME/VOLTAGE check out of tolerance | N | N |  | N | YES | <D> **** Detailed Description **** During calibration of E-RLY-64/85/82 per PPM 10.25.23 and WO#02117303-01 As found TIME/VOLTAGE check 2 was out of tolerance. As found time was 0.529 seconds with a tolerance of 0.475-0.525 seconds. All other As found tests were in tolerance. <I> **** Actions Taken **** Notified PSRO and supervisor. Adjusted relay per PPM 10.25.23. TIME/VOLTAGE check 2 As left time is 0.524 seconds. All As left testing completed Sat and in tolerance. | 02-00-E-RLY-64/85/82
398380 | CR | 20190822 | CAQ | C | TSP-DG2-B502 Rework due to Non-Functional TDAS MUX 8 |  |  |  | N | YES | <D> **** Detailed Description **** While performing TSP-DG2-B502, DG2 Load Testing, step 7.3.40 requires recording the highest voltage reached by DG-2 following load-reject test trip of E-CB-DG2/8. This data is captured from Real Time Plot which receives input from multiple TDAS points. The input from DG-2 voltage and frequency was unavailable due to TDAS MUX 8 being non -functional. The crew tripped E-CB-DG2/8 per procedure but were unable to gather the required data. This resulted in a 1 hour and 40 minute delay to have I&C replace TDAS MUX 8 and have operators re-attempt the load reject test. <I> **** Actions Taken **** CRS informed the shift manager. I&C was contacted to replace TDAS MUX 8, which was already scheduled to be performed this shift and all equipment was already staged. Restored TDAS MUX 8. Re-established test conditions and performed a second load-reject test trip of E-CB-DG2/8. Test data was captured and was satisfactory. Crew will draft a Lessons Learned to identify, communicate, and close any gaps. This CR is for trending purposes. <N> **** Equipment Description **** Main Control Room NRC - Need to analyze whether preconditioning of DG-2 met the requirements of the load reject test on the second attempt. | 02-00-TDAS-MUX-8
398381 | CR | 20190822 |  | 4 | RP robot contaminated during use |  |  |  | N | NO | <D> **** Detailed Description **** During steam leak investigations for HV-V-31A, the RP robot was run underneath the active leak, resulting in water collecting in the reel trays. Upon retrieval, the loose surface contamination surveys identified up to 2,000 ccpm. The robot was placed within two radioactive materials bags and relocated to allow for decay prior to decon efforts. Recommend this CR for trending purposes only. <I> **** Actions Taken **** Collected water was cleaned out and the robot was surveyed to assess contamination levels. The robot was bagged to prevent the spread of contamination and relocated for decay prior to decon. <N> What is the EPN of the RP robot - HP-EQ-XXXXX? Robot has been decontaminated. No further action required.
398382 | CR | 20190822 |  | 3 | Rework for evaporation pond 1B sediment removal project |  |  |  | N | NO | <D> **** Detailed Description **** After further review, the waste designation for flocculant debris in evaporation pond 1B (completed in June 2019 under AR 388501-03) was determined to be insufficient. The original waste designation was based on a book designation and did not adequately address the requirements for waste disposal. This rework results in the following: 1) preparation of a sampling plan; 2) sampling of evaporation pond 1B sediment sampling and laboratory analysis; 3) delayed start of sediment removal and return of pond to service; and 4) potential for unbudgeted disposal costs. <I> **** Actions Taken **** Discussed with E&RP Manager, F&CE Manager, and Environmental Services. <N> Cross reference to CR assignment 00388501-02 generated to track the analysis work of the sediment in 1B.
398384 | CR | 20190822 |  | 3 | Approved EC-16024 Rev 000 contains ambiguity |  |  |  | N | NO | <D> **** Detailed Description **** I&C Technician caught errors in review of proposed revisions to ISP-MS-Q908 â€“ Q911 that incorporated EC-16024 per markups provided in AR-EVAL-187781 that if implemented had the potential for placing the plant in single loop operation when monitoring ATWS/RPT test switches while performing surveillance testing due to ambiguity. EC-16024 adds test jacks at C5 and C6 contacts to monitor RRC-RMS -S112A and B that were going to be installed in 2017. See drawings EWD-3E-006, 021 to see why jacks were insufficient to provide clear indication of switch status during testing. <I> **** Actions Taken **** It was recently determined that EC-16024 will need to be revised in order to have a clear indication of switch status. This was a good catch by the I&C Tech.
398386 | CR | 20190822 |  | 4 | Washington EOC dedicated fax inoperable |  |  |  | N | NO | <D> **** Detailed Description **** During the monthly fax check, the Washington EOC dedicated fax was found inoperable. Faxes to all other offsite agencies went through. The commercial fax to Washington State is also operable as a backup. Resent CR and WR are CR 396958 and WR 29150541. Recommend closing to new WR. <I> **** Actions Taken **** Notified EP and the SCC Dispatched Tech. No problem found leaving the TEC. Escalating to phone analyst to work with service provider. Posted signs in MCR to use alternate commercial FAX line to contact / notifiy Washington State. EP notiified and committed to addressing labeling in the other emergency centers. <N> **** Equipment Description **** TEC to Washington Statte EOC
398388 | CR | 20190822 |  | 4 | Test cables for DCW testing need to be re-labeled | N | N |  | N | NO | <D> **** Detailed Description **** Test cables for DCW heat exchanger test need to be re -labled; labeling on cables degrading due to age - 2 cables needed to be swapped due to poor label during setup. <I> **** Actions Taken **** System Engineer contacted Supervision, CR initiated, PEER -PEER coaching between techniciains observed, shop will be breifed in the D15 *****Close CR to TRENDING*****
398389 | CR | 20190822 |  |  | ***CR SENT TO ECP***** |  |  |  | N | NO | <D> **** Detailed Description **** ***SENT TO ECP***** See Employee Concerns Program (ECP) for contents of CR CR initiated anonymously, reviewed for Safety Conscious Work Environment (SCWE) content. Moved and Forwarded CR to AR -ECP. <N> ***SENT TO ECP***** See Employee Concerns Program (ECP) for contents of CR CR initiated anonymously, reviewed for Safety Conscious Work Environment (SCWE) content. Moved and Forwarded CR to AR -ECP. See 2019 NSCMP emergent meeting notes
398390 | CR | 20190822 |  | 4 | HV-V-30E has S4 packing leak | N | N |  | N | YES | <D> **** Detailed Description **** HV-V-30E has an S4 packing leak. Need to backseat ASAP while there is still packing. Valve is currently OPEN. <I> **** Actions Taken **** Informed OPS and WC management. Updated FLM map. <N> **** Equipment Description **** TG 501 MSR B east end | 02-00-HV-V-30E
398391 | CR | 20190822 |  | 4 | RCIC-V-1 Strain gauge for diagnostic test |  |  |  | N | NO | <D> **** Detailed Description **** During the walkdown of RCIC-V-1 identified a special designed strain gauge would be required for performing diagnostic testing. This required expedeting fees to obtain the special designed strain gauge. <I> **** Actions Taken **** No additional actions are required. A CID was created, and a PO was issued for the special designed strain gauge. The vendor has all the information needed for the strain gauge.
398392 | CR | 20190822 |  | 3 | 2019 DBAI (NRC) - Question regarding Scaffold Tags |  |  |  | N | NO | <D> **** Detailed Description **** During the 2019 DBAI, the NRC inspection team questioned the PPM 10.2.53 (Scaffolding) process use of field Scaffold Tags for documenting Engineering inspection/approvals of scaffolds when such approval is required by the process. The Scaffold Tags are not retained when their associated scaffolds are removed from the plant. The Engineering approval provided on the back of the Scaffold Tag is generally based upon a conclusion by the degreed Civil or Mechanical Engineer that the existing supporting calculations and scaffold procedure 10 CFR 50.59 screening/evaluations are bounding for the configuration inspected/evaluated. If not bounded, then additional 50.59 review is required (and would be provided). The question is if more formalized Engineering evaluation should be provided. This question should be investigated as part of the resolution of AR CR 398173. . This AR CR is for a potential PPM 10.2.53 process improvement and is not documenting any problem with the physical plant. <N> This issue is being addressed under CR# 3981732. No further actions are required due to the actions associated with CR# 398732.
398393 | CR | 20190822 |  | 4 | Yakima Building Lunchroom Stoves/Ovens Require Replacement |  |  |  | N | NO | <D> **** Detailed Description **** Both Stoves/Ovens in the Yakima Building lunchroom require replacement due to functioning poorly and overall condition. Heating elements for stove top burners and the oven take an unusually long time to work. <I> **** Actions Taken **** Discussed concern with Facilities Manager.
398395 | CR | 20190822 |  | 4 | HV-V-31A Electrical backseat | N | N |  | N | YES | <D> **** Detailed Description **** HV-V-31A was initially electrically backseated on 8/21/19 (1 time) and the control room lights indicated the valve was still in the closed direction with no impact to the steam plume. 8/22/19 a robot and personnel performed a walkdown to verify the position of the valve and due to the steam leak could not verify the position of the valve . The electrical backseat evolution was reperformed by trying to take the valve closed and then back open and into the backseat. The closed contacts did not pickup during the close stroke. Electricans stopped and contacted MOV Engineer and supervision. The valve was then given an open signal at full voltage and then quickly reduced to the degraded voltage per the procedure. The valve was at or near the backseat during the evolution. The steam plume stopped.. It is recommended to not stroke this valve during the rest of the cycle. Additionally, the stuffing box should be furmanited at the next available time. The next refueling outage should replace the valve & operator. | 02-00-HV-MO-31A,02-00-HV-V-31A
398396 | CR | 20190822 |  | 4 | Flow past TSW-PCV-26 diluting TSW sample at dehal trailer | N | N |  | N | YES | <D> **** Detailed Description **** Chemistry identified that the TSW sample at the dehalogenation trailer has a chemical signature that is indistinct from CW. A walkdown verified that the flapper on TSW-FG-49 was lifted, indicating FP water is being supplied to the TSW pre-lube line, where the dehalogenation trailer extracts a sample for TSW. Flow past TSW-PCV-26 may be diluting TSW sample at the dehal trailer. Recommend replacement/refurbishment of TSW-PCV-26 to prevent dilution of the TSW sample line. The TSW sample line will be used to control halogen feed rates when the dehalogation skid is in operation, and a diluted sample will require adjustment by Chemistry to ensure desired halogen feed rate. This does not impact the ability of the system to dehalogenate, or to continuously blow down to the river. TSW-PCV-26 was calibrated in 2018 under WO 02118854 and the same leakage was observed 3 months later. A WO for flow through TSW-PCV-26 already exists (WO 02104851); however, priority should be increased from 5G due to increased flow (based on flapper position) and potential impact to the halogenation system. | 02-00-TSW-PCV-20
398398 | CR | 20190822 |  | 4 | Flag on E-RLY-5051/1/500SC | N | N |  | N | YES | <D> **** Detailed Description **** The left flag was found dropped on E-RLY-5051/1/500SC (for E-CB-1/500S). It reset successfully. <I> **** Actions Taken **** Informed MCR Reset Flag | 02-00-E-RLY-5051/1/500SC
398401 | CR | 20190823 | CAQ | D | Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-54-35 low pressure. OPS2 re-pressurized per SOP-CRD -HCU. Alarm is clear. <I> **** Actions Taken **** Dispatched OPS-2 to investigate. OPS2 re-pressurized per SOP-CRD-HCU | 02-00-CRD-HCU-5435
398402 | CR | 20190823 |  | 4 | DO-F-5, Fuel Oil transfer filter clogged. | N | N |  | N | YES | <D> **** Detailed Description **** During transfer of Fuel Oil from FO-TK-1 to DO-TK-1B the filter high d/p alarm came in. Max d/p was approx 25 psid, per P&L 4.8 of SOP-FO-OPS the max design is 75. Filter requires replacement/cleaned. <I> **** Actions Taken **** CR & WR written. MCR staff informed. | 02-00-DO-F-5
398403 | CR | 20190823 | CAQ | D | DG-ENG-1B1 and 1B2 Eng Lube oil level low | Y | N |  | N | YES | <D> **** Detailed Description **** while performing round during 24 hour load run it was noted that DG-ENG-1B1 and 1B2 Engine Lube oil level low out of spec. Min. spec is 3.75 inches below full mark and both the engines are currently 4.25 inches below the full mark. recommend adding oil. <I> **** Actions Taken **** Inform SSS and CRS, initiate AR/WR. | 02-00-DG-ENG-1B1,02-00-DG-ENG-1B2
398404 | CR | 20190823 |  | 3 | Asset Suite 9 Scope Definition Milestone Missed |  |  |  | N | NO | <D> **** Detailed Description **** The Asset Suite 9 project has been working to obtain a scope outline for each of the 13 Asset Suite modules, a milestone to achieve this scope outline was set for 8/15/2019. Currently 12 of the 13 modules have an approved scope outline documented. The Work Management Module had not yet been approved. Please assign this CR to ITMGMT to develop and document the recovery plan.
398405 | CR | 20190823 | CAQ | D | UNANTICIPATED DC FUEL PUMP FAILURE ALARM | Y | N |  | N | YES | <D> **** Detailed Description **** When starting DG2 for the 24 hour run, an unexpected alarm was recieved. Drop 10-2 DC FUEL PUMP FAILURE came in. Operators verified that DO-P-3B1 & DO-P-3B2 were operating at +40#. Mechanically tapped DLO-PS-5B2 which cleared the alarm. <I> **** Actions Taken **** CR/WR written Supervision Notified | 02-00-DO-PS-5B2
398406 | CR | 20190823 |  | 4 | DLO-TI-1B1 needs repair | N | N |  | N | YES | <D> LO COOLER DLO-HX-2B1 INLET TEMP (50-300 F) gauge needs repair. 2 of the 3 internal screws that hold the scale on have shaken loose. The screws are still inside the case. The needle is still tracking and the scale is still in place. Pics attached <N> CR at INPROG. Approved CR, moved to SRO for OPS Review. | 02-00-DLO-TI-1B1
398407 | CR | 20190823 |  | 4 | Computer point S025 out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** While performing a loop calibration of CBD-FT-10, computer point S025 was out of tolerance at the 0.1 INWC input point. It was reading 0 and should be 625. <I> **** Actions Taken **** Notified CRS and supervision and wrote this CR/WR per PPM 16.9.1. <N> **** Equipment Description **** MCR
398408 | CR | 20190823 |  | 3 | Enhancement TSP-DG1-B502 and TSP-DG2-B502, and DG LOGS |  |  |  | N | NO | <D> **** Detailed Description **** TSP-DG1-B502 and TSP-DG2-B502 need to be updated to reflect other DG procedures (OSP-ELEC-S701,2,3; TSP-ELEC-DG3-B502; and the monthly) â€“ currently step 7.6.4 records lube oil levels with the engine not shutdown. This is contrary to the note in SOP-DG-LUBEOIL â€œRequired lube oil is calculated with the diesel shutdown..." B502 require the performance of SOP-DG-LUBEOIL to verify minimum acceptable lube oil availability. Fixing the procedure to check oil while shutdown will prevent unnecessary work and future CRs. Also evaluate the level required for out of specification for â€œengine lube oil levelâ€ while DG is operating. Currently the Min Spec is 3.75 inches below the full mark which will increase once engine is shutdown. Recommend setting the out of specification slightly above TS tolerance. Any TS violation will be discovered during the applicable procedures # oil check step. <N> The Operating crews held a procedure use and adherence stand down covering this and other minor issues. No further action required.
398409 | CR | 20190823 |  | 4 | Both CF-P-41A & CF-P-42A not pumping | N | N |  | N | YES | <D> **** Detailed Description **** Based on inventory trending, both CF-P-41A (100/95) and CF-P-42A (50/50) are not pumping. No chnage in 24 hours for TK-42 inventory and only 30 gals drop on TK-41. Inventory should have dropped by over 100 gals. <I> **** Actions Taken **** Recommend going to manual feed at 50 gals/shift until further notice. <N> **** Equipment Description **** CF-P-41 A and CF-P-42 A
398410 | CR | 20190823 |  | 3 | Page 72 was inadvertently skipped while performing TSP-DG2-B |  |  |  | N | NO | <D> **** Detailed Description **** During the 30 minute logs. Data was taken on page 71 then continued on page 73. At the end of the data run, the data section were manually filled out on page 72. All data has been verified. <I> No impact. All data collected. <N> TSP-DG2-B502
398411 | CR | 20190823 |  | 4 | DO-LITS-15 fault light is flashing red/green | N | N |  | N | YES | <D> **** Detailed Description **** The HPCS level indicator DO-LITS-15 is has the fault light LED lit and flashes red and green. | 02-00-DO-LITS-15
398412 | CR | 20190823 | CAQ | D | North side RCIC turbine oil is above the max stby oil level | Y | N |  | N | YES | <D> **** Detailed Description **** North side RCIC turbine oil level is above the max standby oil level by less than 1/8". | 02-00-RCIC-P-1
398413 | CR | 20190824 | CAQ | D | Drywell Annulus average temp exceeded RFO 1.7.1 limit | Y | Y |  | N | NO | <D> **** Detailed Description **** Drywell Annulus average temp exceeded RFO 1.7.1 limit of LE 150F. A CR is required to comply with RFO 1.7.1.A.2. CW blowdown was off for the majority of 8/23 and was restored at 1930. Recommend securing blowdown on night shift and restoring earlier in the day during hot weather to prevent drywell heatup. <I> **** Actions Taken **** Compensatory measures per RFO 1.7.1
398417 | CR | 20190824 |  | 3 | MCR ecnf printer needs new ink cartridges | N | N |  | N | NO | <D> **** Detailed Description **** The vital powered ecnf printer in the MCR, HP OfficeJet Pro 7740, needs new ink cartridges. <I> **** Actions Taken **** Informed SM <N> **** Equipment Description **** MCR ecnf printer next to IA/STA desk
398418 | CR | 20190824 |  | 4 | FPC-DPR-13 appears off, will not turn on | N | N |  | N | YES | <D> **** Detailed Description **** FPC-DPR-13 appears off, will not turn on. Screen blank FPC demin filter D/P for both A and B filters in RWCR <I> **** Actions Taken **** Informed MCR | 02-00-FPC-DPR-13
398419 | CR | 20190824 | CAQ | D | CCH-PI-3B indicated GT 25 psig during OSP-CCH/IST-M702 | Y | Y |  | N | YES | <D> **** Detailed Description **** When starting CCH-CR-1B per OSP-CCH/IST-M702, CCH-PI-3B indicated GT 25 psig and required venting pressure off per step 7.1.45.c. This CR is written to document the condition for trending per step 7.1.45.d. <I> **** Actions Taken **** Wrote this CR and notified the System Engineer. Provided a completed copy of the surveillance to the System Engineer. | 02-00-CCH-CR-1B
398420 | CR | 20190824 |  | 4 | TO-EX-1A excessive oil leak | N | N |  | N | YES | <D> **** Detailed Description **** While performing rounds it was observed that TO-EX-1A was leaking oil excessively from a nut and screw assembly that holds on a cover plate on the exhauster. The leak is near TO-V-110. A fresh oil pad was placed under TO-EX-1A early in the shift and six hours later it was half soaked with oil. TO-EX-1A was running at the time with vapor extractor D/P (TO-DPIS-10) of 0.9 "H2O. Pictures are attached. <I> **** Actions Taken **** Informed CRS and wrote CR | 02-00-TO-EX-1A
398421 | CR | 20190824 |  | 4 | Squealing noise from WOA-FN-1B drive pulley | N | N |  | N | YES | <D> **** Detailed Description **** There is a squealing noise on the drive pulley end of WOA -FN-1B. Sounds like it needs new belts or pulley adjustment. See attached video. <I> **** Actions Taken **** Notified CRS | 02-00-WOA-FN-1B
398422 | CR | 20190824 | CAQ | D | CW-PHITS-1 erratic indication | N | Y |  | N | YES | <D> **** Detailed Description **** CW-PHITS-1 indicated pH is erratic resulting in CW-PHIC-1 adjusting the in-service SAT pumpâ€™s output in response to the erroneous pH value. This is a recurrent issue. CW -PHIC-1 was placed in Manual to prevent the controller from hunting. CW-PHR-1 indicates the erratic signal started at ~ 15:33 on 08/24/19. CW-PHR-1 recorded a low pH value of 5.87 and a high pH value of 10.45 with large step changes in value. The CW Blowdown pH monitored on ENW .CIRCH2O.DHBDPH varied between ~ 8.1 and 8.4. <I> **** Actions Taken **** Notified the CRS, SM and Chemistry. Placed CW-PHIC-1 in Manual. | 02-00-CW-PHITS-1
398423 | CR | 20190824 | CAQ | D | Visible oil on the bottom inside E-IR-81 | Y | N |  | N | YES | <D> **** Detailed Description **** Oil accumulation on the bottom of the inside of E-IR-81. <N> The oil in bottom of E-IR-81 is located under RPS-PS-5A. This condition was previously documented uner CR 397326. | 02-00-E-IR-81
398424 | CR | 20190824 |  | 4 | SAT-P-1A not functioning correctly. | N | N |  | N | YES | <D> **** Detailed Description **** Please see attached to EDMS docs. CW-PHITS-1 was place in manual on 8/24/19 in response to apparant CW-PHITS-1 failure. Review of eDNA traces appear to show that SAT-P-1A may be functioning incorrectly in adjuting the rate of injection. Suspect that the positioner for adjusting stroke is failing/gummed up. Recommend replace/repair/investigate this positioner/pump. Of note is that SAT-P-1B was documented to have an air/oil leak from its positioner on 5/10/19 with a WR still a H/APPR. When SAT-P-1B fails gravity addition will be required. <I> **** Actions Taken **** Shifted to SAT-P-1B running, placed CW-PHITS-1 in automagic. Informed supervision that the health of the CW pH system made be questionable. Continuing to trend | 02-00-SAT-P-1A
398425 | CR | 20190825 |  | 3 | Unable to Run the Dose Report | N | N |  | N | NO | <D> **** Detailed Description **** -Unable to run the Dose Report as part of the HP Lead Tech Nightly Sign-Off. Notified Troy Mcnabb & Steve Brush Via Email. This has been going on for several days. <I> **** Actions Taken **** -Initiated Condition Report. <N> Issues with the dose report have been resolved. No further action required.
398428 | CR | 20190825 |  | 3 | eSOMS OPS-2 log entry change needed | N | N |  | N | NO | <D> **** Detailed Description **** The OPS-2 log, "CRD Temp in Alarm" [184] instructions state "IF the temperature of any control rod is GE 350Â°F, then notify the CRS of the temperature and rod number (log those GE 350 Â°F shiftly in MCR log), and enter ABN-ROD. {P -159950}" The instructions should also include to log temperatures exceeding 250F in the Hot Rod log book per P&L 4.10 of SOP-CRD-HCU, which states, " MS-TR-6 CRD temperatures exceeding 250F should be documented in the CRD Hot Rod log book (RB 522) for engineering trending purposes. {P-159950} " Please update the log entry. <I> **** Actions Taken **** Notified MCR supervisors <N> **** Equipment Description **** OPS-2 eSOMS log
398429 | CR | 20190825 |  | 4 | Weekly Camera Cleaning CR/WR | N | N |  | N | YES | <D> **** Detailed Description **** The following cameras are in need of cleaning: 1/13/23/32 and the ISFSI Cameras <I> **** Actions Taken **** Initiate CR/WR <N> **** Equipment Description **** PA Cameras
398430 | CR | 20190825 |  | 4 | Recieved Offgas Glycol Low Temperature alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received GLYCOL PUMP SUCTION LOW TEMPERATURE alarm H13 -P672.A9 (2-10). GY-TRS-630 alarm setpoint is 31 deg. F and indication stabilized at ~ 29.5F. OG-RF-20C was selected as lead unit and continued to run. GY-TIC-17 indicated 32 deg. F with the 34F and 35F amber lamps illuminated and the 32F lamp extinguished (lamp test was performed). Per 4.672.A9 (2-10) the primary glycol chiller should auto stop at 32.25F and decreasing. GY-TI-18 (GY -TK-2 temperature) indicated 31 def. F. GY-P-1A was only glycol pump running and had nominal discharge pressure of 40 psig as indicated on GY-PI-19. Shifted to OG-RF-20A as the lead unit and OG-RF-20C stopped, OG-RF-20A remained off. Shifted to OG-RF-20B and it started with the same indications as OG-RF-20C. Low temperature issue previously documented by WR 29150497 and CR 396819. Recommend calibration of GY-TIC-17 and or OG-TRS-630. <I> **** Actions Taken **** Notified the CRS and Shift Manager. Submitted CR to document trend. WR 29150497 and CR 396819 previously documented this concern. | 02-00-GY-TIC-17
398431 | CR | 20190825 | CAQ | D | Recieved Accumulator trouble for CRD-HCU-5415 | Y | N |  | N | YES | <D> **** Detailed Description **** High water level. <I> **** Actions Taken **** Dispatched elite eqiupment operator to address alarm IAW ARP! | 02-00-CRD-HCU-5415
398432 | CR | 20190825 |  | 4 | ARGOS @ HP PAAP Taken Out of Service (Safety Concern) | N | N |  | N | NO | <D> **** Detailed Description **** (HP-EQ-42784) ARGOS was taken Out of Service due to the Detector Screen popping out and creating a possible cut hazard. (Safety Concern) . ARGOS was Source Checked and Passed, but the Out of Service strap was placed across monitor so no one can use it until the Safety Concern is addressed. <I> **** Actions Taken **** -Notified Supervision -Initiated CR & WR. <N> **** Equipment Description **** HP PAP (HP-EQ-42784)
398433 | CR | 20190826 |  | 4 | 21H Resin out of stock | N | N |  | N | NO | <D> **** Detailed Description **** during normal weekend ops, we ran out of 21H resin buckets preventing the processing of water without changing the procedure/precoat criteria sheets and using another available resin. recommend we count and ensure adequate buckets are available to cover backshifts/weekends and/or include an alternate precoat sheet to use another type of resin in the event we are unable to count buckets/properly prepare for a weekend <I> **** Actions Taken **** informed MCR initiated CR <N> **** Equipment Description **** 467 resin storage
398434 | CR | 20190826 | CAQ | C | M&TE Suspended/ Lost | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0068410 Megger Insulation Tester- model MIT 410/2 Can't be located and is now Suspended/ Lost. EFIN EVAL: Usage #1 & #2 Temp power. Usage #3 Trouble shoot MT-CRA-1. Usage #4 Unknown WO. Outage Timeframe. Temp Power? No Plant Impact. DEF #7244A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
398435 | CR | 20190826 | CAQ | D | TR-S Low Voltage on B phase only | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of control room logs, it was identified that the B phase on TR-S is below 235KV. TR-S A, B, and C phases respectively are 238KV, 234 KV, and 237KV. BPA Munro Control Center was contacted and their indication is 239KV with no degraded conditions identified. OSP-ELEC -W101 was performed to verify operability of Start-Up Transformer. This CR satisfies Step 7.1.12.D of OSP-ELEC -W101. <I> **** Actions Taken **** Notified CRS, contacted BPA Munro, performed offsite power alignment, initiated CR <N> **** Equipment Description **** MCR indication . There is a history of observed fluctuation on the indicated B phase voltage, and calibration of the BPD providing the voltage was required to remediate the fluctuation noted. In one instance (2017, AR-CR 366318) we did write a POD, and the key takeaway is articulated on page 3-4 that states: "Failure or loss of the E-TR-BPDS/B bushing potential device (BPD) output will affect components that provide alarm and/or indication only and will not affect the proper function of the E-TR-S transformer to transfer power from the 230kV transmission system to the CGS 4.16kV and 6.9kV distribution switchgear." . Based on our history related to the observed condition, we should be going after calibration of the corresponding BPD (EPN: E-TR-BPDS/B). | 02-00-E-TR-S
398436 | CR | 20190826 | CAQ | C | Top-Tier drawing E526-2 references incorrect fuse | N | N |  | N | NO | <D> **** Detailed Description **** Drawing zone K-12 references fuse GG-F02 powering indicating lights for BS-V-60A. All other drawings available list this fuse as GG-F03. Field walkdown verified that GG-F02 DOES NOT EXIST and GG-F03 is the correct designation. Reference the following drawings: E555-E-CP-H13/P840; E537-1VA-90; EWD-72E-041; E559-E-CP -H13/P840-2.
398438 | CR | 20190826 |  | 3 | Declining Trend in MRule Evaluation Timeliness | N | N |  | N | NO | <D> **** Detailed Description **** A declining trend is identified in performing MRule evaluations in accordance with the 28-day timeliness requirement stated in SYS-4-22, â€œMaintenance Rule Program.â€ Currently, 494 out of the 668 assigned MRule evaluations are overdue (some >100 days). Performance in this area has fallen off since R-24. Challenges to nominal MRule evaluation performance are competing priorities (e.g. PO.6 milestone) and knowledge/experience gaps. This level of performance presents opportunities for late submittal of MRule related ICES reports and late declarations of systems entering MRule a(1) status in accordance with 10 CFR 50.65. <I> **** Actions Taken **** Briefed MRule coordinator, ER Supervisor, and SYSENG Manager. Recommend assignment to AR-ER.
398441 | CR | 20190826 |  | 4 | M&TE Suspended/ Lost |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0068200 Heise Pressure Calibrator- model PTE-1/XT was C/O 4/18/19 for LLRT Mobilization WO #02110908-01. No Activity in Portal J for any usage. Can't Locate. Suspended/ Lost. DEF #7266A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
398443 | CR | 20190826 |  | 4 | 4 Pieces of M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** 4 Fluke Temp. Probes- model 80T-150U/A Passed Closeout Calibrations & are now Suspended unti R25. Not used since Calibrated. Calcode #0062637. DEF #7267A written. Calcode #0065242. DEF #7268A written. Calcode #0065634. DEF #7269A written. Calcode #0065636. DEF #7270A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
398445 | CR | 20190826 |  | 3 | Dataglance not advancing work package | N | N |  | N | NO | <D> **** Detailed Description **** 02140522-01 has been reviewed by OPS for completion but the work order is still at working status in dataglance. work order will not addvance to finished. No answer when calling the eWp help line. <I> **** Actions Taken **** Wrote CR called help line <N> Control Room Supervisor, Stephen Stead, reported that WO 02140522 is stuck at H/OPS, Ops could not advance it past this point and he tried work flowing the WO multiple times. . Richard Frasure updated Asset Suite to get the work order task to H/OPS. Then Morgan Johnson closed out all but one of the open approval route records in DataGlance. Then Morgan used the option on the Operations Closeout screen in DataGlance to release the package. Once the package was released on the DataGlance Closeout panel, all other remaining DataGlance/Asset Suite processes worked as expected.
398447 | CR | 20190826 |  | 3 | NET3 Backup storage full | N | N |  | N | YES | <D> **** Detailed Description **** Storage on net3-stod-netapp1 allocated for use by Backup Exec. is completely full. Backup Exec cleanup processes appear to not be running properly. This causes scheduled backups to not complete. . This does not impact Operations or Cyber Security. This is not a reportable condition. . Recommend to Computer Engineering as a 3. <I> **** Actions Taken **** Reviewed system status for storage and backup software. Generated CR | 02-00-NET3-COMP-EPO,02-00-NET3-SOFT-BKUPEX/SVR,02-00-NET3-STOD-NETAPP1
398448 | CR | 20190826 |  | 4 | NET3-COMP-EPO hung on logout | N | N |  | N | YES | <D> **** Detailed Description **** NET3-COMP-EPO is hung on logout for some accounts. System needs to be rebooted. The cause is a known issue, AR 376954. Functions the system performs are not affected and are performing as designed. . This does not impact Operations. This is not a reportable condition. . System needs to be rebooted per WR. <I> **** Actions Taken **** Notified SM and Generated CR/WR | 02-00-NET3-COMP-EPO
398449 | CR | 20190826 |  | 3 | Error found in AED CAL ME-02-90-46. | N | N |  | N | YES | <D> **** Detailed Description **** As part of the RWCU Project, AED CAL ME-02-90-46, Relief Valve Setpoint, Capacity and Reseat Verification, was reviewed. The existing calculation contained an error that resulted in a higher required flowrate than what is actually needed. The actual required flowrate is about half of the calculated required flowrate of 27 gpm. Both RWCU-RV-1 (Catalog ID 0000026656) and RWCU-RV-3 (Catalog ID 0000014320) have a Name Plate Flow Rate of 82 and 89 gpm, respectively. This non-conforming higher required flowrate currently in ME-02-90-46 is conservative. The Design Function of RWCU -RV-1 and RWCU-RV-3 is not affected. Corrective Actions include revising this calculation, ME -02-90-46, as part of the RWCU HX and Piping Replacement Project. <I> **** Actions Taken **** Determined that the Design Function of RWCU-RV-1 and RWCU -RV-3 is not affected and initiated this CR. | 02-00-RWCU-RV-1,02-00-RWCU-RV-3
398451 | CR | 20190826 |  | 4 | Health Physics - Missing AMP 100 probe | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During the montlhy Portable Instrument Inventory, AMP 100 (RM80) probe was discovered missing. <I> **** Actions Taken **** Notified HP Supervision Notified Calibration Lab technician Initiated CR <N> **** Equipment Description **** AMP 100 RM80
398452 | CR | 20190826 |  | 4 | Security vehicle trap gate 26B needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security gate 26B at the vehicle trap is not operating by design and needs maintenance. Gate is inoperable. <I> **** Actions Taken **** CR/WR initiated. Security supervision notified. <N> **** Equipment Description **** Security Gate 26B in the vehicle trap.
398455 | CR | 20190826 | CAQ | D | Dips in RRC-P-1B Upper Seal Pressure | Y | N |  | N | YES | <D> **** Detailed Description **** Several dips in the RRC-P-1B upper seal pressure of up to 25 psi were noted since August 19. There was no corresponding change is seal temperatures. Further investigation also discovered a number of similar dips in the seal pressure between August 6 and August 11. There was also around a five degree temperature rise upper seal chamber temperature on August 9. In all cases, the seal pressure and temperature returned to normal. This behavior is a possible indication of material passing through the seal. Since the pressure and temperature returned to normal each time, however, there is no indication of damage to the seal, and the seal is expected to continue to perform its required function. | 02-00-RRC-P-1B
398457 | CR | 20190826 |  | 4 | SHCO-P-1B pump was ran without fluid on mechanical seal | N | N |  | N | YES | <D> **** Detailed Description **** During WO #02139506 the 09 task rotation check was performed with the mechanical seal dry. This is against industry best practices. Internal OE of RWCU hold pump had the same issue due to the filling and venting process and this procedure had to be changed to not damage the mechanical seal from being run dry. <I> **** Actions Taken **** Notified the main control room and mechanical maintenance manager and supervisor, contacted engineering and initiated this condition report. <N> ***General Notes*** Planning has been contacted and various solutions to this issue have been discussed. It has been identified that Engineering and OPS were contacted about running the pump dry, and the damage that this would cause. Engineering and OPS were not concerned about this issue. The mechanics are concerned because if this issue is labeled as rework, the mechanical shop will be blamed for poor craftmanship. This work order was not a PM, so their is no model work order to revise to fix this in the future. Engineering needs to provide better field support when Craft raise issues up, an assignment has been added to the maint. Procedure Revision data base to revise PPM 10.2.54 (pump test procedure) to help correct this issue going forward. | 02-00-SHCO-P-1B
398458 | CR | 20190826 |  | 4 | PA01 and PA07 assigned to peer evaluator | N | N |  | N | NO | <D> **** Detailed Description **** Peer evaluator coming in for Operations Self-Assessment assigned both employee protected area access (PA01) and supplemental protected area access (PA07). This led to PQD viewer showing unqualified for PA01 (the correct qualification assignment for industry peer). This is an administrative issue, there was no unqualified work performed and the issue has been corrected. <I> **** Actions Taken **** qualified individual in PA01 and inactivated PA07 qualification.
398459 | CR | 20190826 |  | 3 | NICMs not addressed per SWP-CM-02 | N | N |  | N | NO | <D> **** Detailed Description **** Leaving R25 there were 20 NICMs installed in the station. SWP-CM-02 sections 5.3.1 and 5.3.2 require actions for NICMs left in place for GT 1 cycle. At present, NICMs are not treated like TMODs in that the station strives to correct and removed all installed TMODs each refueling outage. It is my opinion that SWP-CM-02 requires NICMs to be treated as TMODs and be scoped for 100% removal/correction each outage and this may not be occuring at CGS. <I> **** Actions Taken **** None required. Send to outage management.
398461 | CR | 20190826 |  | 3 | OMM 999-00,194,1 has EC 17708 at the wrong status | N | N |  | N | NO | <D> **** Detailed Description **** OMM 999-00,194,1 has EC17708 at the wrong status. EC is at approved and canot be incorperated at that status. It must be at Active, Modified or closed to incorperate. <I> **** Actions Taken **** Informed Supervision and wrote CR.
398462 | CR | 20190826 | CAQ | D | E-BU-R422/4 LPCS PMP RM 'Charging Status' (NRC Identified) | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-R422/4 LPCS PMP RM 'Charging Status' light flashing. No flash pattern, just seems to be a slow, constant on/off. <I> **** Actions Taken **** Informed MCR | 02-00-E-BU-R422/4
398463 | CR | 20190826 |  | 4 | Badge export process interrupted | N | N |  | N | YES | <D> **** Detailed Description **** On Monday 8/26/2019, it was discovered that new badge data had not been transferred to Corporate since the previous Friday. Computer Engineering investigated and discovered that one of the file server's client program for transmitting badge data had hung on a standard log file operation involving closing the current log file, which had filled, and making a new log file. Restarting this client program resolved the condition and automated badge data transfers resumed with a new log file. <I> **** Actions Taken **** Restarted program, contacted vendor support, wrote CR <N> **** Equipment Description **** CENTRAL ALARM STATION | 02-00-SEC-SERVER-L3
398464 | CR | 20190826 |  | 3 | (QA) SSAC not satisfying all procedure responsibilities | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) Quality independent technical review of Senior Site ALARA Committee (SSAC) conduct identified that the SSAC did not satisfy all of the responsibilities in GEN-RPP13, Senior Site ALARA Committee for the period August 2018 â€“ July 2019. The following exceptions to specific committee requirements were identified. 1. GEN-RPP-13, step 2.3.9 states â€œâ€¦SSAC should approve the estimated dose for the job.â€ SSAC challenge (ad hoc) meeting minutes cite both the estimated dose and the SSAC goal. Quality identified that the SSAC establishes goals but does not approve estimates, contrary to the procedure. 2. GEN-RPP-13, step 2.3.3 requires the SSAC to review outage and annual site exposure goals but does not cite a frequency requirement. Quality review identified that the SSAC did not review R-24 refueling outage exposure goals. In addition, the SSAC reviewed monthly dose goals in August, September and October 2018 but did not review monthly goals from November 2018 â€“ July 2019. The August 2018 SSAC also reviewed FY18 on-line dose performance, the July 2019 and the August 2019 SSAC reviewed current and projected dose performance. 3. GEN-RPP-13, steps 2.3.8(a) or (b) requires the SSAC to develop a station dose reduction strategy including quarterly review of status and yearly review and approval of the plan(s). Plan status was reviewed in August 2019, but approval and quarterly status reviews were not observed or documented in the preceding 12 months. 4. GEN-RPP-13, step 2.3.10 requires the SSAC to review and approve in-progress reviews, new dose estimates and corrective actions for jobs where actual or revised dose exceeds the approved dose by 25%. This review and approval did not occur for R-24 refuel floor work. <I> **** Actions Taken **** This issue is a Deficiency identified during Quality continuous monitoring activities. Recommend assignment to AR-RADPL for resolution. <N> **** Equipment Description **** N/A
398465 | CR | 20190826 | CAQ | D | FP-THD-zone 55 | N | N |  | N | YES | <D> **** Detailed Description **** while performing 15.2.23 thermal detector CFT section 7.1 step 7.1.4 panel didnt perform as expected we never recieved a trouble alarm on FCP-2 drop 3-4 as expected. <I> **** Actions Taken **** notified supervisor and system engineer wrote cr/wr <N> **** Equipment Description **** FSP-3 zone 55 SM-30 module
398466 | CR | 20190826 |  | 4 | IPM on RX 606â€™ failed Calibration due to high background cou | N | N |  | N | YES | <D> **** Detailed Description **** IPM on 606â€™, HP-EQ-42663, failed Rad Cal due to Detector #16â€™s background count not within 50% of average background count. The background count on detector 16 was high. On direct frisk of detector, no contamination was found. <I> **** Actions Taken **** Placed IPM out of service, and wrote CR. Suggest replacement of detector. | 02-00-HP-EQ-42663
398467 | CR | 20190826 |  | 3 | Request for Common Cause Eval of previous equipment events | N | N |  | N | NO | <D> **** Detailed Description **** Based on an informal review of some of the previous EQITs and discussion with the System Engineering manager I am requesting a common cause analysis be performed on recent equipment events (events since the 2018 INPO eval). This will be to confirm that insights from the evaluation have been properly incorporated into resolution of issues and if not, actions are already in place to close those gaps. <I> **** Actions Taken **** CR written, discussed with System Engineering Manager
398470 | CR | 20190826 | CAQ | C | Unusual trend in WW and DW O2 and pressures. | Y | Y |  | N | YES | <D> **** Detailed Description **** The trends of containment suggest that there is communication between the DW and WW air spaces. First the DW O2 and WW O2 concentrations are trending towards a common value. The DW is trending down and the WW is trending up. This suggests that gaseous movement is from the DW to the WW. Second there has not been a difference between WW and DW after the venting of containment. The WW was vented on 8/25/19 at ~ 22:00 with a final differential pressure between the two air spaces was ~0.2 psid. Approximately 16 hours later the WW and DW were at the same pressure and tracking together with changes in barometric pressure. Recommend investigating and correcting perceived issue. Recommend evaluating if a DW to WW vacuum breaker make be leaking by or if there is another mechanism that could be the issue. <I> **** Actions Taken **** Discussed with supervision and Peers. Generated this AR. Attached eDNA graphs to this AR. <R> REP/REGE assignments are not needed and were cancelled with Compliance Supervisor concurrence. | 02-00-C-TK-1
398471 | CR | 20190826 |  | 3 | RHR C Pump Room Cleanliness |  |  |  | N | NO | <D> **** Detailed Description **** following maintenance this week on RRA-CC-1, there is a lot of debris on the floor of the pump room indicating less than thorough rigor on the cleanup portion of the job <I> **** Actions Taken **** informed shift management informed HP/laborers and asked them to clean up some one elses' mess <N> **** Equipment Description **** RHR- C Pumproom
398472 | CR | 20190826 |  | 4 | SO-PI-235 reading high out of spec. | N | N |  | N | YES | <D> **** Detailed Description **** SO-PI-235 is reading 126 psig with a high spec. of 125 psig. Recommend adjusting SO-V-242 IAW SOP-SO-START step 5.2.26 and 5.2.8. <I> **** Actions Taken **** Notified Supervisor. <N> **** Equipment Description **** TG441 W | 02-00-SO-PI-235
398473 | CR | 20190826 | CAQ | D | HPCS-PIS-3 Pointer Required Adjustment | Y | Y |  | N | YES | <D> **** Detailed Description **** During performance of ISP-HPCS-M901, HPCS-PIS-3 pointer was found OOT per table 7.1c. Pointer was adjusted per step 7.1.31, Attachment 9.1, to within tolerance. <I> **** Actions Taken **** Informed operations, supervision, adjusted per attachment 9.1, wrote CR for trending. <N> **** Equipment Description **** RX 422 | 02-00-HPCS-PIS-3
398474 | CR | 20190826 |  | 4 | Unable to collect data due to Siemens equipment | N | N |  | N | YES | <D> **** Detailed Description **** While performing 0213213201 MAIN GEN E-GEN-1 GEN-1-1-6.2 VIBRATION MONITORING We collected all the points available. Vibe points TG-MON-VB1 Thru VB11 currently have vibe data collection instrumentation on it due to the Turbine bearing 4 high vibe issue. These points will not be able to be collected for this PM until after turbine rotor balance shot outage is completed <I> **** Actions Taken **** wrote CR, contacted supervisor | 02-00-TG-MON-VB1
398475 | CR | 20190827 |  | 4 | Sec-XR-4 | N | N |  | N | YES | <D> **** Detailed Description **** SEC-XR-4 is not working as designed. <I> **** Actions Taken **** SEC-XR-4 taken out of service, generated CR/WR | 02-00-SEC-XR-4
398476 | CR | 20190827 | CAQ | D | AMA-FN-52 CS is difficult to place in PTL. | N | Y |  | N | YES | <D> **** Detailed Description **** AMA-FN-52 Control Switch is difficult to place and keep in PTL. Please investigate and repair/replace as necessary. Multiple attempts needed to get the CS to stay in the PTL position while hanging a clearance order. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TSC | 02-00-AMA-FN-52
398477 | CR | 20190827 |  | 4 | Security BRE 37 Door handle needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security BRE 37 Door handle needs maintenance. Contact Security at extension 2185 for more information. <I> **** Actions Taken **** Security Supervision notified, CR/WR generated for support. <N> **** Equipment Description **** Security BRE 37 (South of Spray Ponds)
398483 | CR | 20190827 |  | 3 | MI-1.22 revision number shown is incorrect | N | N |  | N | NO | <D> **** Detailed Description **** Revision number on the MI was not updated for both revision 21 and revision 22. Both show as revision 20 in the EDMS documents. This is an Administrative issue only.
398488 | CR | 20190827 |  | 3 | ISP-ARM-X302 Needs Revision | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** ISP-ARM-X302 needs revised to document that I&C does the RAD Cals now instead of Chemistry. <I> **** Actions Taken **** Discussed with Supervision and Procedure Writer. Wrote CR to document.
398490 | CR | 20190827 |  | 4 | PARB quorum requirements not met | N | N |  | N | NO | <D> **** Detailed Description **** On 8/27 the PARB met to review the Operating Experience report out. GBP-ORG-02 requires a chair and four members for quorum. There were only two members and the chair. <I> **** Actions Taken **** Discussed with Plant General Manager and made decision to hold the meeting without quorum.
398491 | CR | 20190827 |  | 3 | INCORRECT LABELS | N | N |  | N | YES | <D> **** Detailed Description **** The as-found condition for detector 8-3 on zone 8 was that the cabels were labeled incorrectly but terminated correctly in the detector. <I> **** Actions Taken **** Verified correct termination by pulling wires back to the T condulet. we need to swap labels 8-SD-P5 with 8-SD-P4 and swap labels 8-SD-N5 with 8-SD-N4. This will make terminations match the labeling. <N> **** Equipment Description **** TG 471' These wires were found incorrectly labeled. They were not and not EPN labels. Electricaians, along with engineering validated correct labeling and completed the labeling of each wire. Probelm resolved without the need of this AR. | 02-00-FP-ID-8/3
398492 | CR | 20190827 | CAQ | D | TEA-SR-26 sharp decrease in sample flow following bank swap | N | Y |  | N | YES | <D> **** Detailed Description **** During performance of PPM 16.11.6, a sharp decrease in sample flow rate was observed following the swapping of sample collection banks using TEA-V-4 and TEA-V-5, which direct flow through the continuous TEA particulate/iodine sample filters. Sample flow collection for TEA remains adequate to satisfy ODCM requirements. Sample flow decreased from approximately 2.1 scfm (old filters in left side alignment) to 1.77 scfm (new filters in right side alignment). Sample collection flow is non-isokinetic. Suspected issue with TEA-V-4 or TEA-V-5 alignment or possible occlusion. There is an open work request to investigate these valves: WR 29150209. Stepwise changes have been observed previously when swapping sample collection banks from left to right, but loss of flow to this extent is unusual <I> **** Actions Taken **** Investigated filters and filter housing, contacted specialist, wrote CR | 02-00-TEA-V-4,02-00-TEA-V-5
398493 | CR | 20190827 |  | 3 | Unable to complete 12.13.40 as written | N | N |  | N | NO | <D> **** Detailed Description **** Unable to complete 12.13.40, TSW-SR-34 Sample Rack Flushing, as written. In step 6.2.1 a. the procedure directs the user to "Connect the hose to TSW-V-SR34/V16 WITH TSW-QDC-SR34/1..." a system modification was performed to replace the aforementioned quick disconnect (QDC) with a nozzle. This error was repeated for a second QDC in 6.2.3 a. The procedure should remove all references to the removed QDCs. <I> **** Actions Taken **** Evolution terminated, supervisor/specialist informed <N> What was the approved modification that authorized these configuration change? If there was no approved modification, TSW-SR-34 should be returned to its as-designed configuration. Flush of TSW-SR-34 was completed under WR 29151277 WRs 29151296 and 29151297 were initiated to restore the quick disconnects on TSW-QDC-SR34/1 and TSW-QDC-SR34/2. A revision to PPM 12.13.40 is not required.
398496 | CR | 20190827 |  | 4 | CAS Video Wall needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** The video wall in CAS needs maintenance. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Security notification made, CR/WR generated <N> **** Equipment Description **** Monitors in CAS along the north wall
398497 | CR | 20190827 |  | 3 | MT&E lost/damaged. Not critical equipment, NSR. | N | N |  | N | NO | <D> **** Detailed Description **** MT&E lost/damaged. Not critical equipment, NSR. EPNs listed for future reference <N> It is not know if the MT&E was out of tolerance at the time of the HD work. As Found data could not be obtained. The work can only be done during an outage. CR was written to provide information in the event of a problem with the HD level, it is a possibility that they were not left at the correct set point during the last outage. | 02-00-HD-LT-3A,02-00-HD-LT-3B,02-00-HD-LT-3C,02-00-HD-LT-4A,02-00-HD-LT-4C
398498 | CR | 20190827 | CAQ | C | MT&E found out of tolerance | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #33408 GENRAD Decade Resistor model 1433-G found OOT & needs adjustment. EFIN to evaluate the 5 usages. DEF #7272A written.
398500 | CR | 20190827 |  | 3 | Fittings and EPN on TSW-SR-34 do not match design drawing | N | N |  | N | YES | <D> **** Detailed Description **** The quick disconnects TSW-QDC-SR34/1 and TSW-QDC-SR34/2 have been removed from TSW-SR-34 and replaced with barbed hose fittings (no EPN tag). However, the flow diagram of TSW-SR-34, AED MEC M893-4, has not been updated to reflect the replacement of these quick disconnect valves with the barbed hose fittings. TSW-QDC-SR34/1 and TSW-QDC-SR34/2 are still indicated as being a part of TSW-SR-34 in drawing M893-4. <I> **** Actions Taken **** Viewed drawings, consulted supervisor <N> **** Equipment Description **** Turbine Building 441 What was the approved modification that altered the configuration of TSW-SR-34? If there was no approved modification, TSW-SR-34 should be returned to its as-designed configuration. This field change is also contrary to CVI DWG 1057-00,7,3 (perhaps others). | 02-00-TSW-QDC-SR34/1,02-00-TSW-QDC-SR34/2,02-00-TSW-SR-34
398502 | CR | 20190827 |  | 4 | TDAS signal X258 (DG2 KW Output) degraded | N | N |  | N | YES | <D> **** Detailed Description **** The TDAS signal for point X258 is reading less than half the expected value and is very noisy. Incorrect noisy signals impact the ability to trend DG2 performance specifically governor control while parallel to the grid. This condition has been documented 2 seperate times in the past and has not been resolved (reference CRs 341067 and 379430). This issue should be investigated and repaired to allow proper monitoring, trending and investigation of future DG2 issues. | 02-00-TDAS-MUX-8
398504 | CR | 20190827 | CAQ | C | CMS-SR-20 leak | Y | N |  | N | YES | <D> **** Detailed Description **** At CMS-F-SR20/2 the o-rings were degraded and deformed. This caused the leak check in ISP-CMS/PRM-X306 to fail. The leak was so bad you could hear it at 5psi. This would cause atmosphere to enter containment when CMS-SR-20 is in service. <I> **** Actions Taken **** Under 29151170 replaced the o-rings and leak check was sat. Recommend a PM or frequency to be changed to replace the o-rings for both 20 and 21 | 02-00-CMS-F-SR20/2,02-00-CMS-SR-20
398505 | CR | 20190827 |  | 4 | Degraded channel heads on TSW-HX-6D | N | N |  | N | YES | <D> **** Detailed Description **** During performing clean and inspect PM of TSW-HX-6D performed under WO 02111653, the inlet/outlet and reversing channel heads were found to be degraded along the edge of the sealing surfaces. The gasket is still capable of sealing so thereâ€™s no need to repair during this maintenance window. Work request is initiated to replace both heads on the heat exchanger. This work has to be done during an outage as the oil on shell side has to be isolated because thereâ€™s a potential that the bundle would be floating out. <I> **** Actions Taken **** Initiated WR and this CR <N> **** Equipment Description **** T441 | 02-00-TSW-HX-6D
398506 | CR | 20190827 | CAQ | D | ARE-CR-51, loss of 20 lbs of R-22 | N | Y |  | N | YES | <D> **** Detailed Description **** during WO 02145979, the craft was able to recover 11 lbs of R-22 from the chiller. The capacity of the chiller is 31 lbs. This AR is to document the loss of 20 lbs of R-22 Refrigerant. <I> **** Actions Taken **** Performed repairs to the TSC chiller to restore operability Wrote CR to document loss and notified enviromental/regs | 02-00-ARE-CR-51
398507 | CR | 20190827 |  | 4 | Trend, Evaluation of DLR exposure data | N | N |  | N | NO | <D> **** Detailed Description **** This CR is being written to trend dosimeter evaluations per HPI-4.30, and there is no impact to the station at this time because none of the evaluated individual doses challenged administrative dose limits. During the first half of 2019, there were 2384 personnel monitored for radiation exposure, and 34 of them required personnel exposure investigations (PEIs) per guidance of HPI-4.30. The largest evaluated delta was discovered to be a contractor that flew home each weekend and took the DLR in luggage, which would have been x-rayed at the airport. This is contrary to the direction of GEN-RPP-06 step 3.7.4 and 3.8.4 for department managers/supervisors and individuals to ensure DLR is not taken while traveling. The only PEI that resulted in a change to the dose recorded by the DLRs, was for the individual traveling with DLR.
398508 | CR | 20190827 |  | 4 | Ground Fault on U681 in Control Room | N | N |  | N | YES | <D> **** Detailed Description **** While craft was performing Halon Testing per WO # 02107667-01 a ground fault came in A-200 Panel on U679 when testing S9 on U681 and did not clear, with CRS permission placed Normal/Silence Trouble Switch on the A -200 panel on U679 to the Silence Trouble Position. <I> **** Actions Taken **** Craft stop work, notified CRS and Supervison and Fire Engineer. Initiated CR and FPSI #19-0207 <N> **** Equipment Description **** FP-ID-U679 located in the Control Room Panel A-200
398509 | CR | 20190827 |  | 3 | Sources have exceeded working life | N | N |  | N | NO | <D> **** Detailed Description **** About 200 CGS radioactive sources have exceeded their Source Working Life (SWL). SWL is a date after which sources need to be evaluated for ability to perform intended purposes and probability of leakage. These sources have all been regularly leak tested and none are leaking. In addition many sources need to have the owner updated in TES. There is no regulatory impact or reporting requirements associated with this condition report. <I> **** Actions Taken **** Actions needed are update owners, have owners report whether the source is in use, assess the sources which are being used for probability of leakage, update SWL dates and/or order replacement sources as needed on a case by case basis.
398510 | CR | 20190827 |  | 3 | PeopleSoft Payroll Register Print Failure | N | N |  | N | NO | <D> **** Detailed Description **** The PeopleSoft Payroll Register Print program failed with the message (SQR 1500) Array element out of range (300) for array 'etdarray' on line 456. <N> Analyst increased the array size in the Pay002 program to 450 on 8/27/19. No further action needed.
398513 | CR | 20190827 | CAQ | D | CBD-FI-10 erratic indication. | N | Y |  | N | YES | <D> **** Detailed Description **** CRO1 noticed that CBD-FI-10 was experiencing erratic indication. The flow was at 3000gpm with spikes down to zero GPM. At the same time the CW pH indication was also having issues. | 02-00-CBD-FR-10
398514 | CR | 20190827 |  | 3 | IER response action not implemented as intended. | N | N |  | N | NO | <D> **** Detailed Description **** During the Maint. Fundamental Self-assessment with an outside peer in association on IER 17-9, a team member identified some deficiencies associated with AR# 370721-22 & 25. The assignment owner did not meet the intent of the assignments. The individual changed only one minor portion of the procedure but excluded the intent of the assignments In assignment 22 the author states that the assignment is a duplicate of assignment 25, which isnâ€™t the case. Both assignments are requesting very different things to be changed within MI-1.8. Assignment 22 requests the following changes to MI-1.8. â€œRevise the Work Implementation section of MI-1.8 to include a definition of and responsibilities for the conduct of pre/during/post-job definitions of the various inspections and who is inspections. Including the responsible for the inspections. This will ensure the inspections are conducted in a consistent manner.â€ As where assignment 25 requests the following changes to MI-1.8, â€œ Revise the work implementation section of MI-1.8 to include the expectation for workers, supervisor, and managers to apply and to reinforce maintenance technical fundamentals in pre-job briefings, during work activities, and during pre-and post-inspections.â€ . The only duplication that are present is that both assignments are requesting a revision of MI- 1.8. The procedure was revised on the date that is specified within the closure notes within the assignments. The specified revision of the procedure (Rev 71) states that the only changes was â€œAdded the phrase â€œMaintenance Technical Fundamentalsâ€ to the definition of Precision Maintenance.â€ Which has not met the intent of assignments 22, or 25. <I> **** Actions Taken **** This was shared with Maint. Management and supervisor. The procedure needs to be revised to reflect the recommendations associated with the IER 17-9 response which is documented under AR# 370721. A task was added to the Maintenance Procedure revision data base to correct this issue. Author recommends a Non-CAQ severity level 3 to AR -MNTPROC. <N> Re-opened at the request of assignment 01 owner. This assignment is being closed to AR 00392031 because it will be completed under this AR.
398516 | CR | 20190827 | CAQ | D | CW pH has erratic indication | N | Y |  | N | YES | <D> **** Detailed Description **** CW pH has erratic indication and the controller has failed to maintain CW pH. The CW pH indicated, computer point F141, went as high as high as 12.2 pH and is now at 8.2 The local indication is that the acid pumps responded to the elevated pH and have been placed in manual operation. The de-halogenation pH indication spiked down scale and came back to 8.0 pH | 02-00-CW-PHITS-1
398517 | CR | 20190827 |  | 4 | ASD 1B/2 Coolant Resistivity < 5 MOHM | N | N |  | N | YES | <D> **** Detailed Description **** ASD 1B/2 Coolant Resistivity is indicating 4.12 MOHM on GY-CI-10B2. Log instructions are to initiate WR to change filters at 5 MOHM. <I> **** Actions Taken **** Notified Supervision. CR/WR Initiated. | 02-00-GY-CI-10B2
398518 | CR | 20190828 |  | 4 | Radwaste SW (501' to 507') Stairwell lighting going out | N | N |  | N | YES | <D> **** Detailed Description **** Lighting in the stairwell from RW 501' (MCR SW Exit) to RW 507' is going out. Access is via main control room door C411. <I> **** Actions Taken **** Informed SM non-essential lighting. <N> **** Equipment Description **** RW 501' to 507' stairwell (SW MCR Exit - Door C411).
398527 | CR | 20190828 |  | 3 | PeopleSoft Payroll General Ledger Interface failure |  |  |  | N | NO | <D> **** Detailed Description **** The PeopleSoft Payroll General Ledger Interface process failed with the message '***Error*** Earning Distribution Array limit exceeded'. <N> Analyst increased array size to 1300 in the PAYGL01 program. No further action needed.
398528 | CR | 20190828 |  | 4 | MT&E found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0063371 Heise Pressure Calibrator- model PTE-1 found OOT & adjusted within specs. Not used in the OOT Range of Volts. DEF #7273A written. No Plant Impact. No Action Required.
398529 | CR | 20190828 | CAQ | C | MT&E found out of tolerance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0068432 Tektronix AC Current Probe- model P6022 found OOT & Rejected- Broken Beyond Repair. DEF #7274A written and EFIN will Evaluate the usage.
398530 | CR | 20190828 |  | 3 | AOV Program Health is YELLOW |  |  |  | N | NO | <D> **** Detailed Description **** The Plant Health Committee voted on 8/27/19 to change the AOV program health to YELLOW. Per ENG-PRG-02, a Program Health Improvement Plan (PHIP) will need to be developed, and Program Health Report updating will increase to a 6 month frequency. Recommend assignment to SECOMP.
398531 | CR | 20190828 |  | 3 | Quarterly CORC Caution Tag Audit (WO 02141535) |  |  |  | N | NO | <D> **** Detailed Description **** Quarterly CORC Caution Clearance Audit 10CFR50.59 The Quarterly CORC Caution Tag Audit (WO 02141535) has documented the caution clearances that have been hanging for GE 30 days. There are 14 new Caution clearances added to this total since the last audit: C-E-TR-N1/2 OIL-001, C-FD-RMS-P/13 -001, C-MS-V-110A -001, C-WOA-V-63 -001, C -TOA-AW-1A -001, C-SS-V-41 -002, C-OG-TC-2A -001 (D25), C -EDR-P-18A/18B-001, C-TO-EX-4A -001, C-SS-PCV-4C -001 (D25), C-RRC-V-8BDRAIN-002, C-PWC-V-417 -001 (D24), C-TOA -V-101 -001, C-HSSF EYEWASH -001. <I> **** Actions Taken **** Wrote CR.
398532 | CR | 20190828 |  | 3 | Quarterly CORC Danger & Local Tag Audit (WO 02141533) |  |  |  | N | NO | <D> **** Detailed Description **** Quarterly CORC Danger & Local Clearance Audit 10CFR50.59 The Quarterly CORC Danger & Local Tag Audit (WO 02132644) has documented the danger & local clearances that have been hanging for GE 30 days. 12 new clearances have been added to this total since the last audit: D-CW-V-6 -001, D-CW-V-5 -001, D-COND-V-79/80 -001 (D25), L-E-CB-LP5DA/23-001, L -E-TRM3-CLRGP2-001, L-PWC-P-103 -001, L-E-TRM2-CLRGP2-001, L-E-LP-3CB -001 (L25), L-E-LP-2DB -001, L-MH-ES-7 -004, L -MT-ELEV-2 -004, L-MH-ES-7 -002, Request Technical Services/Systems Engineering Manager (or designee) to determine whether a 50.59 review is required. <I> **** Actions Taken **** Wrote CR.
398535 | CR | 20190828 | CAQ | D | M&TE Suspended/ Lost |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0068305 Mitutoyo Dial Caliper- model 505-742 6" Can't be located and is now Suspended/ Lost. DEF #7271A written. See EDMS for MOV ENG Eval. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
398542 | CR | 20190828 |  | 4 | 13 Pieces of M&TE Suspended until R25 |  |  |  | N | NO | <D> **** Detailed Description **** 13 Proto/ CDI Torque Wrenches have Passed Closeout Calibrations and are Now Suspended until R25. Not used since Calibrated. No Plant Impact. No Action Required. See EDMS for list of Calcodes, Description, Models and associated DEF #'s. <I> **** Actions Taken **** None Trending purposes only.
398544 | CR | 20190828 | CAQ | C | Implementation of 10 CFR 54.37(b) Requirements |  |  |  | N | NO | <D> **** Detailed Description **** Up until the issuance of ENG-PRO-04 on March 19, 2019 there was no method in place to direct or perform the reviews needed to determine if an FSAR update was required. Recent review of 54.37(b) has identified three (3) â€œnewly identifiedâ€ SSCs that required evaluation and be put in the scope of license renewal for aging management, thereby require updating in the next 10 CFR 50.71(e) update. They affected systems are RWCU, Feedwater and RRC. The exact issues are in EDMS <I> **** Actions Taken **** An extent of condition dating back to May 22, 2012 is currently being performed to identify any if additional changes to systems, structures, and components that would have be subject to an aging management review or evaluation of time-limited aging analyses in accordance with Â§ 54.21. Discussed with the License Renewal Project Manager and the Regulatory Affairs Licensing Supervisor References: ARCR 243524, AR 210816, and 278367
398545 | CR | 20190828 |  | 3 | PPM 12.14.11 Needs Revision |  |  |  | N | NO | <D> **** Detailed Description **** In PPM 12.14.11 section 7.5.4 the procedure calls out DCW -V-702A2 when working on DG-ENG-1B2. The rest of this section refers to the appropriate valve. <I> **** Actions Taken **** CR initiated
398546 | CR | 20190828 |  | 4 | Water Truck Vehicle â€“ Safety Issue |  |  |  | N | NO | <D> **** Detailed Description **** A 2003 International water truck was observed being driving on a roadway within the owner controlled area with a loose air receiver tank on the driverâ€™s side chassis. The tank was being held up to the chassis by an air hose. The water truck was followed and was found parked in the Facilities & Commercial Engineering parking area. It was taken out of service until repairs could be made. It appears the air receiver tank slipped out of a restraining saddle. The issue did not appear to be the result of an impact or collision. <I> **** Actions Taken **** Notified Facilities & Commercial Engineering to take the vehicle out of service until repairs could be performed. Entered the VIN into the federal database to see if recalls had been issued. Four recalls found, none concerning the air receiver tank. WA Lic 99560C, VIN 1HTWGAAR73J054082. See EDMS for the vehicleâ€™s recall notices.
398547 | CR | 20190828 |  | 4 | One 2019 GFES candidate failed the comprehensive GFE exam |  |  |  | N | NO | <D> **** Detailed Description **** One ILC-25 candidate failed the 2019 GFE comprehensive exam LO000066. <I> **** Actions Taken **** Reviewed exam weak areas with student. Developed remediation plan.
398549 | CR | 20190828 |  | 4 | SharePoint performance issue blocked upload of eWP records |  |  |  | N | NO | <D> **** Detailed Description **** A SharePoint database performance issue prevented DataGlance from uploading records to the SharePoint Records Center. The issue was resolved by rebuilding the indexes in the SharePoint Records Center content database. Recommend Non-CAQ - Severity 4 <I> **** Actions Taken **** Performed Online Index Rebuild of "WSS Content Records DG" database on the Production SharePoint SQL Server instance.
398550 | CR | 20190828 |  | 3 | Warehouse Delivery truck Racks |  |  |  | N | NO | <D> **** Detailed Description **** Delivery truck side racks are excessivliy heavy to take in and out of rack pockets for daily use. Due to the weight and binding of the racks this could add additional risk to injury. <I> **** Actions Taken **** Racks were taken to Apollo and Aluminun racks are being built built.
398551 | CR | 20190828 |  | 4 | NANTeL Learning Management System Out of Service |  |  |  | N | NO | <D> **** Detailed Description **** The NANTeL Learning Management System is out of service industry wide. NANTeL is aware and is troubleshooting the issue. The bulletin from INPO regarding this issue is attached to EDMS. There are no immeadiate impacts to qualifications. <I> **** Actions Taken **** Submitted trouble ticket to NANTeL, Notified Training Management, Evaluated impact on qualifications and drafted broadcast message.
398552 | CR | 20190828 | CAQ | C | Procurement Spec deviations not applied |  |  |  | N | NO | <D> **** Detailed Description **** It was determined that Procurement Specification Deviations (PSD) generated in 2015 to Specification 12404 were not applied to an item. The procurement of this item started in 2016 after the issuance of the PSDâ€™s but is still in the process of receiving, and item has not been accepted for issuing to the warehouse or plant. A search was conducted to ensure there is no extent of condition and it was confirmed that this issue applies only to this one item. Assign to SCS as CAQ C to correct the requirements on the CID <I> **** Actions Taken **** Discussed with Supplier Quality and SCS manager. OSDD 14657 is in progress to address the issue. CID 8740 was set to H/USER to prevent use until the CID is corrected
398553 | CR | 20190828 |  | 3 | PPM 15.2.23 Procedure Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** When craft was performing PPM 15.2.23 under WO #02105561-01 craft was unable to test thermal heads 64/3, 64/5, 64/6 & 64/8 on TR-S for the detectors are inside the "Safe Working Distance" <I> **** Actions Taken **** Craft stop work and notified supervisor. Supervisor checked history and these thermal heads was identified to be done during only when transformer is de-energized. Notified engineering of procedure enchancement and heads 64/3,64/5,64/6 & 64/8 to be tested when TR-S is de -energize. <N> **** Equipment Description **** FP-THD-64/3, 64/5, 64/6 & 64/8
398554 | CR | 20190828 |  | 3 | Approve Fluke 233's for use in plant |  |  |  | N | NO | <D> **** Detailed Description **** Through recent outage OE and information sharing with USA techs, we learned about Fluke 233â€™s. Fluke 233â€™s have a detachable display that would allow us to be up to 30 feet from the equipment we are working on. They would be very useful in turbine vibration monitoring calibrations and reducing dose in our daily maintenance. Also, they could be useful in eliminating potential FME because we would not have to string leads over a long distance. <I> **** Actions Taken **** While investigating the purchase of new Flukes, I found out we have a few in the Cal Lab. They have been being assessed for use in the plant. They have been there for quite a while. Is there a way we could accelerate the assessment process?
398555 | CR | 20190828 |  | 4 | PWC-SEW-9/PWC-SEW-11 shower valves are self-closing type. | N | N |  | N | YES | <D> **** Detailed Description **** During investigation of DW-DWS-4 it was identified that the shower shut off valves for PWC-SEW-9 and PWC-SEW-11 are self-closing type valves. The valves should be manual type ball valves with pushh/pull rods. Ref AR EVAL 398325, DW-DWS-4 and PWC-SEW-9 are isolated due to valve issues and have associated WRs (xref'ed). a WR for PWC-SEW-11 will be initiated with this CR. This issue does not affect the ability to use the showers. <I> **** Actions Taken **** Informed supervisor. <N> **** Equipment Description **** CWPH SAT Pump Room CWPH Halogenation Room | 02-00-PWC-SEW-11
398557 | CR | 20190828 |  | 4 | CF-P-41B and CF-P-42B need overhaul or replacement. | N | N |  | N | YES | <D> **** Detailed Description **** While performing WR 29150948 neither CF-P-41B or CF-P-42B would develop pressure while flushing each pump with potable water. CF-P-42B is an older style pump and needs replacement while CF-P-41B is only a few months old and needs to be rebuilt. Please write work instructions to do this. <I> **** Actions Taken **** Wrote this AR/WR and informed supervision. <N> **** Equipment Description **** CWPH <S> This is more than a broke/fix. The FIN team has been doing repair after repair with no sustainable progress towards system reliability. Request assignment to SECOMP to gain an understanding of what it takes to make the system perform as intended. | 02-00-CF-P-41B,02-00-CF-P-42B
398558 | CR | 20190828 |  | 3 | Computer shipment error |  |  |  | N | NO | <D> **** Detailed Description **** On 8/26/209 it was discovered a scheduled shipment for pickup of computer inventory was handled incorrectly. Computers staged for return to the vendor was only partially fulfilled. Additionally, the vendor collected five pallets (120) computers that were allocated for a project. 227 computers were to be returned to the vendor in totality. <I> **** Actions Taken **** A complete inventory has been recorded and communicated with Supply Chain Services. Vendor has been contacted. Actions to correct this issue are in place.
398559 | CR | 20190828 |  | 3 | Negative Trend Identified in Proc Use and Adherence |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing CRs and trending within our department, a negative trend has been identified for procedural use and adherence within Design Engineering. Most of the issues have been identified as administrative in nature. Design Engineering will perform a more in-depth snapshot self -assessment to correct the negative trend. Recommend assigning to Design Engineering. <I> **** Actions Taken **** Discussed with the Design Manager and Supervisors. Initiated CR.
398560 | CR | 20190828 | CAQ | C | Potential misalignmt between c-12394 and AR-REG 210816 AS 57 |  |  |  | Y | NO | <D> **** Detailed Description **** During a review the closure information for AR-REG 210816 Assignment 57, NRC Commitment 12934 (C-12394), and the ENW Technical Memorandum (TM-2043), Quality identified a potential misalignment with how Columbia identifies Aging Management requirements for non-safety-related in the OQAPD and TM-2043. TM-2043 is the method used to identify Augmented Quality (AQ) requirements for non-safety-related (NSR) SSCâ€™s based on Commitments to the NRC. The OQAPD does not mention any of those AQ categories and does not mention TM-2043. In addition, TM-2043 does not mention the OQAPD. The intent of this condition report is to drive alignment and make changes as necessary. Recommend Assignment to Quality for resolution. . . . This issue applies to implementation of the aging management program and does not affect the design function of any installed equipment. This CR addresses a gap in completion of a license renewal regulatory commitment. <I> **** Actions Taken **** Initiated CR <N> Cancelled and reopened at request of originator to edit description
398561 | CR | 20190828 | CAQ | D | SW A pumphouse temperature gauge stuck | N | Y |  | N | YES | <D> **** Detailed Description **** Informer I temperature gauge 45248 staged in the Service Water A pumphouse is stuck at 73.4 deg. F. Gauge failed between 2000 Aug. 26th and 2000 Aug. 27th as the last known good reading of 82 deg. F was taken around 2000 on Aug. 26th. Logs have identified 73 deg. F from that point forward (morning of Aug. 27 through evening of Aug. 28). Newly installed informer (MTE #44987) indicates about 82 deg at 2100 on Aug. 28. In comparison, B Service Water pumphouse has ranged from 72 deg. F to 84 deg. F over the same time period. <I> **** Actions Taken **** Informed SM, Tool Crib Attendent, replaced temperature gauge and returned stuck gauge to the tool crib. <N> **** Equipment Description **** Service Water A Pumphouse Temp. Gauge (North Wall)
398562 | CR | 20190828 |  | 3 | Adobe sign in pop up prevents access to documents |  |  |  | N | NO | <D> **** Detailed Description **** adobe pop up prevents access to any adobe document from corporate network. Includes documents on clearances, procedures etc. Seems like phishing for passwords so no data entered. Suggest assign to IS and eliminate pop up at corporate level. See EDMS for snip of pop ut.
398563 | CR | 20190829 | CAQ | D | Security CCTV 33/33T | N | N |  | N | YES | <D> **** Detailed Description **** Security CCTV 33 and 33T are not functioning as designed. Please contact Security Supervision at extension 2185 for further details. <I> **** Actions Taken **** Compensatory measures posted. Security Supervision notified, CR/WR generated for support. | 02-00-SEC-CCTV-33
398564 | CR | 20190829 |  | 3 | All HP Turbine drains automatic opening | N | N |  | N | YES | <D> **** Detailed Description **** Turbine drains MD-V-75 through 87 all opened due to the Delta T between the Cover and Base. This is an automatic function to preclude water from entering the main turbine <I> **** Actions Taken **** shift supervision is contacting system engineering <N> TG-TE-ZBGOV - Component point T3-1302A and T3-1202A have been trending down for 48 hours. At time 0015 on 8/29/19 delta T exceeded 75 degrees and opened main drain valves 75 through 87 started cycling open and closed. Observed HD-TK-5A level cycling coincident with drain valves cycling. Placed control switch for BS-V-39A (Trap Station 16) in Open, place a caution tag for configuration control. | 02-00-MD-V-87
398565 | CR | 20190829 | CAQ | D | Floating Debris in SW Spray Pond B | Y | N |  | N | YES | <D> **** Detailed Description **** A small peice of Plasic and a small peice of cardboard was noticed to be floating in the B SW Spray Pond. Request that the appropriate work group remove the Debris from the pond. Floating Debris does not seem to be large enough to affect the operability of SW-P-1B. <I> **** Actions Taken **** Supervision Notified CR/WR Generated <N> **** Equipment Description **** B Service Water Pond
398566 | CR | 20190829 | CAQ | D | Received ACCUM trouble alarm HCU 38-31 | Y | N |  | N | YES | <D> **** Detailed Description **** accumulator trouble due to moisture. OPS 2 drained the tank and the alarm is clear. no further action necessary - suggest trend | 02-00-CRD-TK-125/3831
398571 | CR | 20190829 | CAQ | D | ANN A3 fuse cleared (3 amp F#1) | N | Y |  | N | YES | <D> **** Detailed Description **** received annunciator alarm and found A3 annunciator panel alarms from 4-7 drop tp 6-8 drop dark when tested. Checked fuses on ANN-E/S-A/A3/FGB. Found F1 (3A) cleared. Removed associated cards for individual drops and replaced fuse per CRS. Fuse immediatly cleared on insertion. Suspect power supply failure. No visible nor olfactory evidence apparent in panel. F1 is an AGC length 250V 3A fuse. | 02-00-ANN-E/S-A/A3/FGB
398573 | CR | 20190829 |  | 3 | AR EVAL 398536 not initiated IAW DES-2-9 |  |  |  | N | NO | <D> **** Detailed Description **** AR EVAL 398536 was not initiated complettely in accordance with the DES-2-9 Attachment 8.2 process. The AR is at NOTIFY status but was sent to Owed To Group ENGMGMT rather than ARRG. Suggest resolution by Maintenance Services. . This AR EVAL 398536 was for an urgent request in support of the upcoming RCIC work window.
398574 | CR | 20190829 | CAQ | C | Documentation does not depict pipe flanges for RCIC-F-1 | Y | Y |  | N | YES | <D> **** Detailed Description **** Small bore flanged connections exist in the inlet and outlet piping for RCIC-F-1 that do not appear to be depicted on station configuration documents. No detailed isometric information appears to exist for this RCIC piping - there are CVI documents but they are more like P&IDs. Consider as-building the piping to detail the subject flanges and their flange gaskets/bolting. Information on the flange gaskets in particular is needed for the upcoming RCIC work window (AR EVAL 398536 / WO 02149597). | 02-00-RCIC-F-1
398576 | CR | 20190829 | CAQ | C | Makeup Demineralizer Trailer High UV-Chlorides Detected | N | Y |  | N | NO | <D> **** Detailed Description **** Chemistry detected higher than normal levels of ultra -violet chlorides in the makeup demineralizer trailer output. <I> **** Actions Taken **** Chemistry specialist informed, Vendor notified to swap charcoal beds.
398580 | CR | 20190829 | CAQ | C | Standard found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode 0050604 Agilent Model 3458A found out of tolerance and adjusted with specs. Issued NOD #20-07.
398584 | CR | 20190829 |  | 4 | WOA-EHC-54B needs Banana jacks added to term strip | Y | N |  | N | YES | <D> **** Detailed Description **** Annual function test requires electricians to energize this heater by installing a jumper across points C1 and C3. Space is limited and visiblitly is poor. This task would be much easier and safer if banana jack standoffs are permanenetly installed at the aforementioned points. A similar task was completed on WOA-EHC-54A last year under WO 02118824 <I> **** Actions Taken **** submitted CR for WR creation <N> **** Equipment Description **** W535 L7/11.1 | 02-00-WOA-EHC-54B
398586 | CR | 20190829 |  | 3 | Cross functional Mid-Cycle readiness review |  |  |  | N | NO | <D> **** Detailed Description **** A cross-functional team was assembled to perform an independent look at the previous yearâ€™s station performance. A self-critical look at each of the major functional areas was performed and several performance gaps were identified by the team. Recommend a non-caq assignment to the applicable department to validate the teamâ€™s findings and to develop corrective actions to close the gaps, as necessary. . Operations: Operations (OP), Operational Focus (OF), Fire Protection (FP): Performance Gap - OP.1 Operators misapply procedure steps during some plant activities in a manner that produces undesired outcomes. This has resulted in radioactive liquid spills, TS/LCS non-compliance, and undesired system response. Contributing, operations managers have not developed crew supervision to the extent necessary to mitigate these low consequence performance gaps. Current perspective Operator performance has not yet developed to the level required to prevent low level events from occurring. High and medium risk evolutions and complex coordinated tasks are recognized and mitigated as appropriate, but low risk and routine tasks are not receiving the proper rigor and attention to detail, resulting in low level issues and rework. Examples â€¢ A radiological spill occurred when operators improperly N/Aâ€™d steps in a procedure. Contributing, operators did not have sufficient oversight over an under instruction watch during precoat evolutions. â€¢ A TS surveillance was missed on plant startup due to improper use of N/A. This surveillance had to be performed during the TS grace period. â€¢ A procedure step was not followed when starting up the main turbine. Operators entered a ramp rate that was not in compliance with the main turbine startup procedure. â€¢ Following a trip of HWC, conditional steps were inappropriately marked N/A, resulting in unnecessary delay in restoring HWC to service. This was due to a lack of recognition by supervision of the proficiency level of the operators who were involved in the restoration of HWC. â€¢ LCS surveillance requirements were challenged when a pump was not run for the required time of 30 minutes. This was due to a transposition error between pages and recording of an incorrect start time. Lack of rigor and lack of attention to detail resulted in another crew repeating the surveillance on the next shift. . Performance Gap - OF.2 Workers do not mitigate the risk involved in some tasks effectively. This has resulted in damage to new fuel during receipt, an inoperable TS required offsite power source, and multiple clearance events. Current perspective Risk mitigation has not yet developed to the level required to prevent events from occurring. Workers have not demonstrated the appropriate level of rigor in when identifying risk and during clearance order implementation, resulting in rework and clearance events. Examples â€¢ During new fuel receipt activities, a fuel bundle was dropped during transit. This event occurred due to inadequate risk recognition and mitigation. â€¢ The startup transformer locked out due to low oil level. This event was preventable by planning a maintenance window to replenish the oil reservoir. Station risk was not appropriately managed. â€¢ While installing temporary power, workers did not sign on to the required clearance order. â€¢ Maintenance was performed on an incorrect component not covered by a clearance order. <I> **** Actions Taken **** Discussed with department managers.
398587 | CR | 20190829 |  |  | Initiated In Error |  |  |  | N | NO | <D> **** Detailed Description **** Investigation in progress to determine if there is an issue. Do not advance. | 02-00-PWH-RV-1,02-00-PWH-RV-4
398588 | CR | 20190829 |  | 3 | Cross functional Mid-Cycle readiness review |  |  |  | N | NO | <D> **** Detailed Description **** A cross-functional team was assembled to perform an independent look at the previous yearâ€™s station performance. A self-critical look at each of the major functional areas was performed and several performance gaps were identified by the team. Recommend assignment to the applicable department to validate the teamâ€™s findings and to develop corrective actions to close the gaps, as necessary. . Radiological Protection/Chemistry: Rad Protection (RP), Rad Safety (RS), Chemistry (CY) Performance Gap - RS.1 Station leaders and workers have not aligned to minimize dose, reduce source term, and implement controls for radioactive contamination and materials. This has resulted in CGS collective radiation exposure exceeding station goals. Current perspective Columbia Collective Radiation Exposure is current 120.283 P-Rem as of July 2019. Examples The R24 Outage Total Dose Goal (Goal <130 Rem) was exceeded with an actual value 161.474 Rem (CR 396076). Overrun factors included effective dose rates (~16% higher), added emergent work (~9 Rem) and execution issues with some planned work. . Performance Gap - CY.1 Chemistry personnel do no always communicate and advocate for prompt resolution for critical chemistry equipment issues. This can result in excessive compensatory measure being implemented and is a challenge to chemistry resources. Current perspective Chemistry personnel do no always communicate and advocate for prompt resolution for critical chemistry equipment issues. Examples Circulating Water (CW) pH Monitor: The CW pH monitor has been randomly drifting and does not indicate an accurate value. This monitor is used to control acid addition to the CW system, critical for maintaining scale and dispersant protection for the main condenser, and data collected for reporting NPDES compliance. (CR 397979) FIN team is working to restore the monitor and has on several occasions claimed success but the monitor continues to drift. Acid control is on manual and adjusted based on the 4-hour grab sample from Chemistry. Chemical Feed (CF) Pumps: During the evaluation period there have been 25 condition reports initiated for CF-P-41A/B, CF-P-42A/B, CF-TK-41 and CF-TK-42 equipment issues. The pumps/piping has been clogging, requiring Operations to add by gravity drain and maintenance to flush piping, repair and replace pumps frequently. This is a financial and manpower burden to the station as well as affecting the ability to reliably protect main condenser components (CR 398354). Actions are needed to determine why pumps are clogging and not pumping (chemical reaction, contaminants in tanks, etc.) and correct the condition. <I> **** Actions Taken **** Discussed with department manager.
398589 | CR | 20190829 |  | 3 | Cross functional Mid-Cycle readiness review |  |  |  | N | NO | <D> **** Detailed Description **** A cross-functional team was assembled to perform an independent look at the previous yearâ€™s station performance. A self-critical look at each of the major functional areas was performed and several performance gaps were identified by the team. Recommend assignment to the applicable department to validate the teamâ€™s findings and to develop corrective actions to close the gaps, as necessary. . Work Management: Online Work and Outage (WM), Project Management (PM) Performance Gap â€“ WM.1 A number of work items have failed to complete during work weeks due to the failure to adhere to the key work management milestones. These exceptions have contributed to lower weekly completion rates and in some instances "failure to complete" during safety system windows. Current perspective These behaviors contributed to work week failures to complete scheduled work. Examples ROA-TS-2 replacement where the walk down did not identify the replacement temperature switch did not fit up like the installed switch (CR# 397553). Failed HEPA test where no replacement filters available (CR# 397500). HPCS-M-P/1 oil sight glass and oil drain plug replacement ordered were not like for like (CR# 397181). . Performance Gap â€“ WM.1 Communication continues to be a challenge between work management team members. Lack of timeliness and details has led to work failing to complete as scheduled, and delays. Current perspective Examples of this were seen both during R24 between Outage Control Center turn overs and daily work between work groups. Examples HSSF work not completing as scheduled due to poor communication between the Work Week Manager, Electricians and Operations (CR# 396176). Work on FD-P-15 was delayed due to clearance order not being hung over concerns with sampling methods. This was previously discussed during the T-3 meeting but not communicated to the on shift crew. FP-V-62 maintenance was delayed 3 hours due to the failure to communicate the known issue of valve isolation leak by (CR# 397884) <I> **** Actions Taken **** Discussed with department manager.
398590 | CR | 20190829 |  | 3 | Cross functional Mid-Cycle readiness review |  |  |  | N | NO | <D> **** Detailed Description **** A cross-functional team was assembled to perform an independent look at the previous yearâ€™s station performance. A self-critical look at each of the major functional areas was performed and several performance gaps were identified by the team. Recommend a non-caq assignment to the applicable department to validate the teamâ€™s findings and to develop corrective actions to close the gaps, as necessary. . Maintenance: Maintenance (MA), Fueling Activities (FA) Performance Gap - MA.1: Some maintenance workers demonstrate shortfalls in the maintenance fundamental of performance of precision work such as the incorrect landing of electrical leads, working on wrong equipment and maintaining high standards for configuration control. Current perspective The Maintenance Manager recognizes there is an adverse trend in work planning and preparation impacting the execution of some work tasks. There is currently an effort to underway in maintenance to understand the common causes between these events and to implement effective corrective actions. Examples â€¢ Supplemental electricians landed leads on incorrect terminal points resulting in damage to the TO-P-EOP motor. â€¢ Supplemental electricians incorrectly landed leads in the bucket to RHR-V-53A resulting in a loss of power to the valve during open stroke for PMT. â€¢ Improper wiring of a new relay in an air compressor motor starter caused the post maintenance test to fail. â€¢ I/C activities and test equipment improperly landed caused an unexpected actuation of HPCS-V-15 and HPCS-V-1 during a surveillance. â€¢ Supplemental workers performed work on plant equipment without being signed onto a clearance order; multiple instances. â€¢ Mechanical activities resulted in working on the wrong valve operator outside of the clearance boundary. Key Insight Contributing factors with this degraded performance include ineffective walkdowns, task previews, and participating in prejob briefings. Supervisors are sometimes not providing critical coaching and observations to detect and correct shortfalls. . Performance Gap â€“ MA.2 and FA.1 Some maintenance workers demonstrate shortfalls in the fundamental of; maintenance activities are conducted in a manner that promotes safe and reliable plant operation while working on or near Safety Related plant equipment and systems. Workers were not managing their work with a prevention attitude. During the 2019 refueling outage personnel contributed to several events that could have had an undesirable effect on plant equipment including the nuclear fuel. This has resulted in unplanned extensions to maintenance windows to recover Foreign Material (FME) dropped or left behind during the execution of work. Current perspective The Maintenance Manager recognizes there is an adverse trend in foreign material control during the execution of maintenance work on plant systems and components. That conclusion is based on several data points listed below. Examples â€¢ Quality recognized and stated in the Maintenance Functional Area Score Card (April-June 2019) that, multiple foreign material control issues occurred with tools or equipment dropped into open systems. â€¢ ED was dropped into the cavity and onto a nuclear fuel assembly. (Recovered) â€¢ ED was dropped into the cavity bellows during a lift. (Recovered) â€¢ ME covers left off of Hydrogen piping. â€¢ Ink pen retrieved from the cavity floor prior to flood up. (Recovered) â€¢ Dropped ED onto MS-DT-1C Hood scaffold. (Recovered) â€¢ Loss of smear disks on MS-DT-1C. (Not Recovered) â€¢ Initial condenser hot well inspections found FME. (Recovered) â€¢ Initial entry into the Suppression Pool found FME. (Recovered) â€¢ Initial inspection of condenser â€œA & Bâ€ condenser bay found LED light, zip-tie and small piece of pipe. (Recovered) â€¢ Failed grip tape tool lanyard â€“ tool fell from MS-DT-1C Hood to 471â€™ floor. (Recovered) â€¢ During vacuuming activities, lock wire found on cavity floor. (Recovered) â€¢ Max air hood, orange PC glove and a red object found floating in Wetwell. (Recovered) â€¢ TIG welding wire dropped while welding LP-C. Later found in condenser. (Recovered) â€¢ Scaffold pole dropped in â€œCâ€ Waterbox inlet. (Recovered) â€¢ Nut dropped in â€œAâ€ Waterbox inlet. (Not Recovered) â€¢ Broken TIG torch Back Cap piece dropped from LP-C to â€œCâ€ condenser bay. (Recovered) â€¢ A piece of metal fell inside pipe at RFW-FCV-10B. (Recovered) â€¢ Several bags of FME removed from the Condenser Hotwell during demob. <I> **** Actions Taken **** Discussed with department manager.
398593 | CR | 20190829 |  | 3 | MSAU card replacement WOT model needs updated |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** during task preview of WOT 00211836501, the instrustions in the model need to be revised to reference the correct steps/sections in ISP-IRM-X308. all sections in the ISP are "6.x" and the WOT instructions reference sections "7.x" <I> **** Actions Taken **** Informed Supervisor and made editorials to the affected steps and created CR <N> **** Equipment Description **** MCR
398597 | CR | 20190829 | CAQ | D | CMS Particulate Filter Green Color | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02138470-01, the removed Particulate Filter had a dark green color on it. <I> **** Actions Taken **** Replaced filter per procedure instructions and turned removed one over to Chemistry. Informed Supervision and wrote CR/WR to document. <N> **** Equipment Description **** 548RX . Filter paper was changed out per W.O. 02138470-01. The green coloring is from trace amounts of copper in the liquid nitrogen. See CR 371850 for engineering eval of green coloring.
398598 | CR | 20190829 |  | 4 | Insulation Need Repair |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02138470-01, it was noted that insulation around the heat trace for CMS-FIS-2 on CMS-SR-21 is broken off and needs repair. <I> **** Actions Taken **** Informed Supervisor and wrote CR/WR to document. Continued with surveillance <N> **** Equipment Description **** 548RX
398602 | CR | 20190829 |  | 3 | Safety - Frayed Power Cord In Willamette Print Center |  |  |  | N | NO | <D> **** Detailed Description **** During training on the drill press machine in the Print Center (Willamette 105), noticed that the power cord end at the plug is frayed and split, exposing internal wiring. This is a safety issue. <I> **** Actions Taken **** Stopped training. Safely unplugged equipment. Hung a sign stating "Out of Order, Do Not Use". Notified supervision, initiated this CR <N> Work order was written and the wire has been fixed and machine is back in service. CR can be closed.
398603 | CR | 20190829 |  | 4 | Universal and Hazardous Waste Management Issues |  |  |  | N | NO | <D> **** Detailed Description **** A walk down of 467â€™ RadWaste identified issues with management of universal waste. A yellow container across from the tool crib labeled â€œbroken glassâ€ was found to have several mercury vapor bulbs inside. Some of these bulbs were found broken. Mercury vapor bulbs have to be manage as Universal Waste per GBP-ENV-17. Any broken bulbs become hazardous waste and need to be transferred to the 437â€™ RadWaste for proper management and disposal. Unbroken bulbs need to be transferred into a proper container and labeled â€œUniversal Waste Lampsâ€ with an accumulation date. This condition is not meeting Washington State requirements to manage universal and hazardous waste (WAC 173-303). <I> **** Actions Taken **** Discussed with E&RP Supervisor. <N> **** Equipment Description **** 467' RadWaste
398606 | CR | 20190829 | CAQ | C | Limits on use MDR relays |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** AR371655 addressed limits on use for CAT ID 68604340 The limits were added to a relay failure MDR type in the diesel start/stop circuits. <I> **** Actions Taken **** Procurment needs to add limits on use from CAT ID 68604340 to all MDR relays. CAT ID 68604361 and anyother MDR type relays. Engineering should identify the EPN's that these limits on use apply to.
398608 | CR | 20190829 |  | 3 | OMM 918-00,1 requires revision |  |  |  | N | YES | <D> **** Detailed Description **** This is a documentation issue only. OMM 918-00,1 was superseded when the new Halogenation Skid was installed and the majority of the CL components were removed; however, the insert for the valves that remained installed (CL-V -65A, CL-V-65B, CL-V-65C, and CL-V-85), was not transferred over to the Halogenation skid OMM 1277-00,1. Recommend returning OMM 918-00,1 to ACTIVE status and updating manual to reflect installed equipment. | 02-00-CL-V-65A,02-00-CL-V-65B,02-00-CL-V-65C,02-00-CL-V-85
398609 | CR | 20190829 |  | 4 | TSC/ BRE 31 AC needs maintenance | N | Y |  | N | YES | <D> **** Detailed Description **** The AC in the TSC is having trouble keeping the area cool The thermostat is currently reading 80 degrees and the BRE is considerably warmer. <I> **** Actions Taken **** CR/WR genertated <N> **** Equipment Description **** TSC building
398610 | CR | 20190829 | CAQ | D | OG-RIS-612 INOP Failure | N | Y |  | N | YES | <D> **** Detailed Description **** During the performance of PPM 16.4.1 for OG-RIS-612 the as found high voltage inop value was 0 VDC with a set point of 255 VDC. Attempts to adjust the HV inop set point was unsuccessful. The as left inop HV is 0 VDC. The inop lamp remains locked in while in operate and is unable to be reset due to the low voltage. <I> **** Actions Taken **** Notified CRS and Supervisor. Initiated CR and WR <N> **** Equipment Description **** OG-RIS-612 MCR | 02-00-OG-RIS-612
398611 | CR | 20190829 |  | 4 | for trending RRC-IN-ASD/1B | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Per 10.25.60 and WO# 02109481, the ASD inverter is supposed to maintain 240VAC nominal for 37 minutes, when it is loaded to 118%. The test ran for 36 minutes with new batteries that were installed today (8/29/2019). This is for trending. <I> **** Actions Taken **** Notified Supervisor, Engineer and write CR <N> **** Equipment Description **** RRC-IN--ASD/1B
398614 | CR | 20190829 |  | 4 | Recieved 4.FCP.2 drop 16-5 ASD FIRE ALARM | N | N |  | N | YES | <D> **** Detailed Description **** Recieved 4.FCP.2 drop 16-5 SYS 85 PREACTION RRC PUMP ASD BLDG Trouble and Fire Alarms. No fire pumps started and operators reported 5 minutes after fire alarm that there was no fire present. System 85 Pre-Action determined to be the cause of the alarm and supply valve (FP-V-428) is currently danger tagged closed. System reset successfully with no reflash. Work Request 29150923 tested the system ALL SAT on 8/29/19. <I> **** Actions Taken **** Initiated CR, reset fire alarm. Same issue as 00397805. <N> **** Equipment Description **** ASD Building Fire Protection System 85
398615 | CR | 20190830 |  | 3 | Procedure enhancement for GBP-CAP-01 |  |  |  | N | NO | <D> **** Detailed Description **** It is unclear within GBP-CAP-01 if closing actions to the work management process is allowed. While this method is allowed for more severe CAQ issues per SWP-CAP-01, the subject is not discussed in GBP-CAP-01. If you try closing level 3 actions using the methods in SWP-CAP-01, an error message is given. It does not appear to support reducing backlog items if level 3 actions have to remain open to support work requests/ work orders that may be years from being completed. Recommend enhancing the procedure on if this process is allowed and the means of accomplishing it. <I> **** Actions Taken **** Discussed with the acting CAP Supervisor. Initiated CR.
398616 | CR | 20190830 |  | 4 | Aluminum Plate on floor in ASD Building |  |  |  | N | NO | <D> **** Detailed Description **** A 3'x4' Aluminum Plate found on the floor in the ASD building near E-PP-ASD1/1. It is unclear if this is a housekeeping issue, has been staged for work in progress, or placed there purposefully for a safety related compensatory measure, as there is no form of signage posted. <I> **** Actions Taken **** Informed supervision. Initiated CR. <N> **** Equipment Description **** ASD Building - VR -441- - -G0/2.0 -
398624 | CR | 20190830 |  | 3 | MD-V-87 UNSAT valve internals not repaired in R24 | N | N |  | N | YES | <C> MRT Change: CR 398624 moved from CAQ Severity C to NON-CAQ Severity 3. <D> **** Detailed Description **** R24 WO 02111717 for â€œMD-V-87 CAUSING THROUGH WALL PIPING LEAKâ€ was closed without repairing the UNSAT valve internals. A note in the WO says: â€œValve was reassembled with old parts and uncorrected body erosion. OCC directed to reassemble as-is.â€ No CR was generated to document that the valve was not repaired. This CR is generated with a new WR to repair the valve during a future outage. <I> **** Actions Taken **** Generated CR and WR. <N> Condition will be resolved by WR 29151334. No further actions required under this condition report. | 02-00-MD-V-87
398625 | CR | 20190830 |  | 3 | Unable to open drawing file |  |  |  | N | NO | <D> **** Detailed Description **** Unable to open AED MIS I619-IR-8-1A. Received message pop-up "Windows can't open this type of file (.dwg)." <I> **** Actions Taken **** Initiated CR.
398626 | CR | 20190830 |  | 4 | Several false fire alarms in ASD building | N | N |  | N | YES | <D> **** Detailed Description **** At 0742 SYS 85 ASD building preaction fire alarm came in at 0748 it was confirmed that there was NO fire is the ASD building or transformers. 0756 SYS 68 deluge DEV A XFMR RRC pump/asd trouble alarm came in. It was immediately confirmed that no fire or sys actuation occurred by individuals in the ASD building. <I> **** Actions Taken **** Wrote CR Informed CRS | 02-00-FP-MDS-68/2,02-00-FP-MDS-85/2
398627 | CR | 20190830 | CAQ | D | Drywell Annulus average temp exceeded RFO 1.7.1 limit | Y | Y |  | N | NO | <D> **** Detailed Description **** Drywell Annulus average temp exceeded RFO 1.7.1 limit of LE 150F. This CR satisfies RFO 1.7.1.A.2. CW blowdown is off due to halogenation and high ambient temperatures have caused a reduction in drywell cooling. <I> **** Actions Taken **** Entered LCS 1.7.1 RFO actions
398628 | CR | 20190830 |  | 4 | SA-f-1 accumulating water | N | N |  | N | YES | <D> **** Detailed Description **** Drained approx. half a gallon water from SA-F-1 <I> **** Actions Taken **** Drained water to bucket and notified MCR <N> **** Equipment Description **** RW467 at service air compressor area | 02-00-SA-F-1
398629 | CR | 20190830 |  | 4 | TSW-HX-6B has a thru wall leak, see pictures | N | N |  | N | YES | <D> **** Detailed Description **** TSW-HX-6B has a thru wall leak, see pictures. Small puddle of water was discovered under TSW-HX-6B, inspection found a small rusty stream of water leading way from the weld area of where i believe the zinc plugs are installed. <I> **** Actions Taken **** WR/CR | 02-00-TSW-HX-6B
398630 | CR | 20190830 |  | 4 | Safety concern,numerous lights need replaced in DG-1 room | N | N |  | N | YES | <D> **** Detailed Description **** Numerous lights need replaced in DG-1 room <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** DG-1 doom
398631 | CR | 20190830 |  | 4 | E-RLY-5051/75/72/C left flag was dropped | N | N |  | N | YES | <C> MRT Change: CR 398631 moved from CAQ Severity D/Trend to NON-CAQ Severity 4/Trend. <D> **** Detailed Description **** E-RLY-5051/75/72/C left flag was dropped, contacted MCR verified no alarms and obtrained permission to reset, which it did. recommend trend only <I> **** Actions Taken **** wr/cr | 02-00-E-RLY-5051/75/72/C
398632 | CR | 20190830 |  | 3 | Initial Demonstration of Capability for Laboratory Methods |  |  |  | N | NO | <D> **** Detailed Description **** The Environmental Services Laboratory has not consistently implemented and documented Initial Demonstration of Capability (IDOC) studies for Laboratory Methods. IDOCs have been completed for newly developed methods but also need to be consistently documented for existing methods. Recommend AR/CR be assigned to AR-ENLAB. <I> **** Actions Taken **** Lab staff meeting to discuss actions needed to complete and/or document IDOCs; initiated CR.
398633 | CR | 20190830 | CAQ | C | Improve Program for Laboratory MDL Studies |  |  |  | N | NO | <D> **** Detailed Description **** The Environmental Services Laboratory is not consistently implementing requirements for ongoing re-calculation of method detection limits (MDL). Samples are analyzed in accordance with published methods and laboratory procedures. MDLs should be performed at the recommended frequency for ongoing MDL determinations per guidance of 40 CFR 136, Appendix B. Recommend AR/CR be assigned to AR-ENLAB. <I> **** Actions Taken **** Discussed MDL requirements in staff meeting and initiated CR.
398634 | CR | 20190830 | CAQ | D | WW and DW pressure equalize within 5 hrs of WW and DW vent | Y | Y |  | N | YES | <D> **** Detailed Description **** After venting DW pressure was 0.52# and WW pressure 0.41# after 5 hours WW and DW pressure had converged to 0.46#. This condition has been previously document with AR 398470. This CR is for trending purposes. <I> **** Actions Taken **** Wrote CR Informed CRS/SM | 02-00-C-TK-1
398635 | CR | 20190830 | CAQ | D | Irregular blowdown data | N | Y |  | N | YES | <D> **** Detailed Description **** Since 8/25/19 blowdown flow data has been irregular, with short periods of intermittent flow recorded, both when blowdown is isolated and during normal operation (TDAS point X473). Blowdown mV signal has also been reading lower and a little nosier than usual when blowdown is isolated (TDAS point S025MV). Plot in EDMS. This may be a calibration issue. Please investigate and repair. Note: On 8/23/19 WO 02119558-26 restored CBD-FT-10 configuration per EC 16616 (Dehal mod). | 02-00-CBD-FT-10
398636 | CR | 20190830 |  | 3 | Low resistivity on ASD-1B/2 | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** FIN has replaced filters on ASD-1B/2 on two or more occassions and the resistivty has not tracked with the other trains. Suspect a low flow may be contributing to this divergant path from other trains. Suggest swapping pumps to check if low flow is from the current motor/pump. This may help isolate where to look for the next area of investigation of possible low flow and subsequent continual lowered resistivity levels. <I> **** Actions Taken **** Contacted ops on day of filter replacement and followed up with ops on the day after replacement. Monitored trend through the EDNA trend DNA history plot.
398637 | CR | 20190830 |  | 3 | Procedure 15.2.49 steps 7.6.9 and 7.12.9 | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing wo# 02141325-01 there is a discrepancy on the number of fire leds illuminated on E-FP-CP-ISD/2 AND 4. The led fire 1 light was the only light to light up. All fire alarms actived in the control room as expected and panels reset to normal. <I> **** Actions Taken **** Informed supervisor and initiated CR. Per supervisor the surveillance is satisfactory.
398638 | CR | 20190830 |  | 4 | SAT-P-1B knocking with each stroke | N | N |  | N | YES | <D> **** Detailed Description **** A knocking sound is coming from SAT-P-1B, coincident with each pump stroke. This knocking sound is not typical for this pump and is accompanied by increased vibrations in the discharge line. Knocking may indicate insufficient torque on trunion/crank nut, or worn bearings/gears. Please investigate and repair. SAT-FI-1 indicates flow to the CW basin. Acid pump control is currently in manual. CW-PHITS -1 is showing error E5.1 so pH could not be confirmed. Local pH reading from the dehalogenation skid read 8.47 from the CW sample line. | 02-00-SAT-P-1B
398639 | CR | 20190830 | CAQ | D | Locked in trouble alarm FCP-1 drop 2-2 TG bldg 471. | N | N |  | N | YES | <D> **** Detailed Description **** Received several trouble alarms on FCP-1 drop 2-2 TG bldg 471 ELECT SWGR BAY. <I> **** Actions Taken **** alarm left locked in. | 02-00-FP-CP-FCP1
398640 | CR | 20190830 |  | 3 | TG-RLY-TR/SMT wired incorrectly | N | N |  | N | YES | <D> **** Detailed Description **** During installation of Temporary Modification EC 17964, Relay TG-RLY-TR/SMT was found wired incorrectly. There was confusion between the front and back of the GE HGA relay, therefore the following drawings do not reflect the as found condition in the plant. EWD-66E-022 E520-4 E537-1VA-41 E537-1VA-43 The leads are connected to terminal points 2 and 8 and should be connected to points 1 and 7 additionally the leads to the coil may be reversed (terminal points 5 and 6). The terminals being wired incorrectly do not impact operation of the relay. <I> **** Actions Taken **** Control Room informed OCC informed EOC informed | 02-00-TG-RLY-TR/SMT
398641 | CR | 20190830 | CAQ | D | CRD-HCU-22-59 High Water Level alarm received | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-22-59. After investigation, Rod Accumulator Trouble Alarm P603-A7 drop 6-7 was for CRD-HCU-22-59 high water level. <I> **** Actions Taken **** Dispatched OPS-2 to investigate. Removed excess water from HCU. Initiated CR <N> **** Equipment Description **** rb522 | 02-00-CRD-HCU-2259
398642 | CR | 20190830 | CAQ | D | CRD-HCU-38-55 High Water Level alarm received | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-38-55. After investigation, Rod Accumulator Trouble Alarm P603-A7 drop 6-7 was for CRD-HCU-38-55 high water level. <I> **** Actions Taken **** Dispatched OPS-2 to investigate. Removed excess water from HCU. Initiated CR <N> **** Equipment Description **** rb522 | 02-00-CRD-HCU-3855
398643 | CR | 20190831 | CAQ | D | CCH-PI-3B found GT 25 psig on rounds | Y | Y |  | N | YES | <D> **** Detailed Description **** This AR is for trending. On OPS-2 rounds, CCH-P-1B suction pressure was 33.5 psig. The required band is 20-25 psig. Pressure was lowered to 23 psig, and surge pipe make up valve (PWC-V-286B) was checked closed . CCH-P-1B suction pressure was also high on 8-24-19, reference AR 00398419. <I> **** Actions Taken **** Notified CRS | 02-00-CCH-PI-3B
398644 | CR | 20190831 | CAQ | D | Abnormal operation of CRD-V-111/2259 | Y | N |  | N | YES | <D> **** Detailed Description **** When clearing a high water level alarm on HCU 22-59, CRD -V-111/2259 abnormal operation was noticed. A bumpy, grinding sensation was felt as the valve was opened, it was not felt when closing the valve. Valve appears to have an internal issue. Please investigate. <I> **** Actions Taken **** Notified CRS | 02-00-CRD-V-111/2259
398659 | CR | 20190831 | CAQ | D | RPS-PS-5A slow leakage | Y | N |  | N | YES | <D> **** Detailed Description **** RPS-PS-5A has a very slow leak (no active leakrate can be ascertained) . A small accumulation of fluid has collected inside of its cabinet (TG 471E). The leak appears to be from a threaded connection at the base of RPS-PS-5A. This issue has been written up on several different occasions (ref. WR 29144187, 29137104), and all associated WR/WOs are at canceled status with nothing having been done to correct the issue. Please repair. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TG 471E | 02-00-RPS-PS-5A
398660 | CR | 20190831 | CAQ | C | SFS-STORM-37 high differential temperature | Y | N |  | N | YES | <D> **** Detailed Description **** While performing OSP-SFS-D101 the computer report for SFS -STORM-37 indicated an Average to Ambient temperature difference of 130.2 F. This prompted a â€œNoâ€ status for Delta T validity. This is above computer report allowable delta T of 129 F but below the SR 3.1.2.1 limit of 137 F. This condition satisfies Amendment 9, Revision 1 to Certificate of compliance No. 1014, HI-STORM 100 Cask System, Appendix A, Technical Specifications, SR 3.1.2.1. Additionally the cask was inspected for blockage. <I> **** Actions Taken **** I recommend troubleshooting the associated temperature elements to validate the indications are accurate. <N> **** Equipment Description **** ISFSI pad 3 SW corner. <R> REP/REGE assignments cancelled with compliance supervisor concurrence. | 02-00-SFS-STORM-037
398661 | CR | 20190831 |  | 4 | TOA-FL-2B roll filter will not advance | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FL-2B roll filter has bunched up at the bottom of the spool and will no longer advance properly. See EDMS for pics. There does not appear to be much filter media left at the top. Reccomend entire filter replacement. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TG 501W | 02-00-TOA-FL-2B
398662 | CR | 20190831 |  | 4 | CAS-MON-1B: WO 02118647 | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of CAS-MON-1B, the sensor was discovered to be out of calibration per IMDS tolerances. The As Found Zero Value (0+-5ppm) was 3 which was in tolerance . The span (60+-5ppm) AS Found Value was 40ppm which was 20ppm low. Values were calibrated back into IMDS tolerances. Additionally the transmitter was acting faulty upon initial calibration. Alarm values were unable to me accessed for a brief period of time. The sensor also spiked suddenly with no Cal gas applied and went into High High alarm (above 90ppm). The values quickly drifted down to zero and the transmitter and sensor worked normally after the calibration. A picture is attached to the WO showing a possible poor wire termination that might be causing these issues. CR written for tracking purposes and potential investigation. <I> **** Actions Taken **** Ops and Supervision notfied, CR and WR written. <N> **** Equipment Description **** 441 TB | 02-00-CAS-MON-1B
398663 | CR | 20190831 | CAQ | D | SFS-STORM-037 temperature monitoring is INOP | Y | N |  | N | YES | <D> **** Detailed Description **** The status indicator for SFS-STORM-037 individual cask tab remained green while the casks delta T was 130.2 degrees F. According to EC 15554 this condition should have changed the status to red (GE 129 degrees F) to alert the operator that OSP-SFS-D101 may not pass. This condition need to be investigated and corrected. There also needs to be an extent of condition performed to determine if other casks exhibit the same response. Additionally SFS-TE-CASK37/2 should be investigated as it is reading 50 to 100 degrees F higher than SFS-TE-CASK37/1, 3 and 4. <N> **** Equipment Description **** TB 471 SFS-STORM-37 RTD # 2 | 02-00-SFS-CP-ISFSI/TMS,02-00-SFS-TE-CASK37/2
398664 | CR | 20190831 |  | 3 | Procedure SWP-PRO-01 procedure enhancement | N | N |  | N | NO | <D> **** Detailed Description **** Pg 24 of SWP-PRO-01 has a commitment referenced in 4.8.2.g. The commitment is linked incorrectly and reads "{C-7. 6Error! Reference source not found.}". This makes it so that the commitment cannot be viewed and is thusly useless. <I> **** Actions Taken **** control room / procedure sponsor informed
398665 | CR | 20190901 |  | 4 | CTMA-FN-1/1 tripped off | N | N |  | N | YES | <D> **** Detailed Description **** While responding to MCR alarm 4.851.S2 drop 3-5, CTMA-FN -1/1 was found not running. The control switch is in the ON position and there is no off or on indicator lit. CTMA -DISC-6R2CL and the local disconnect on CTMA-AC-1 were verified in the ON position. The filter dirty light has been lit for this fan since at least 6/36/2018 per AR#381829 with an associated WR at actioned status. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-CTMA-FN-1/1
398694 | CR | 20190901 |  | 4 | Glycol Pump Suction Temp Low Alarm in MCR | N | N |  | N | YES | <D> **** Detailed Description **** GY-TRS-630 indicates 31F down slow. The alarm setpoint is 31F. Local indication at GY-TIC-17 indicates 33F. With OG Glycol refrigeration unit C running. This indicates that the system is running properly in auto. This temperature recorder has been drifting high and low recently. Recommend replacement and/or calibration of GY-TRS-630. <I> **** Actions Taken **** MCR supervision informed. <N> **** Equipment Description **** MCR P672. | 02-00-GY-TRS-630
398695 | CR | 20190901 |  | 4 | Housekeeping: WO 02138679-01 | N | N |  | N | NO | <D> **** Detailed Description **** CR written for llights out on the 522 reactor building. Reference pictures attached to the this WO. Also Service Pumphouse A and B. and DG 3 overhead crane lighitng. reference old CRs for lighitng issues <I> **** Actions Taken **** CR written, lighitng documented via pictures in this WO, viewable by Data Glance(522 reactor only) reference older work orders for monthly lighting issues with the other listed areas <N> **** Equipment Description **** 522 rx lighting, SW pump house A, B and DG-3 overhead crane lighting.
398696 | CR | 20190901 |  | 4 | E-TR-6/62 pressure is low out of spec | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-6/62 pressure is low out of spec. The low spec is 0 PSIG. Current pressure is -0.5 PSIG, with ambient temp ~ 95F. <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** CW Electrical building | 02-00-E-TR-6/62
398697 | CR | 20190901 | CAQ | D | CRD-HCU-1823 Rod Accumulator Trouble Alarm | Y | N |  | N | YES | <D> **** Detailed Description **** High water level. <I> **** Actions Taken **** Water drained per SOP-CRD-HCU and alarm cleared. | 02-00-CRD-HCU-1823
398698 | CR | 20190901 |  | 3 | eSoms issues are impacting equipment monitoring |  |  |  | N | NO | <D> **** Detailed Description **** See EDMS <N> Closing this CR to AR 00399247 which contains the tasks to perform the eSOMS upgrade needed to correct this condition.
398707 | CR | 20190902 |  | 3 | OPS 4 rounds enhancement (form 27156) |  |  |  | N | NO | <D> **** Detailed Description **** Please add the following verbage to the Short instructions of ALL 4 ASD Coolant Resistivity readings: "For resistivity LT 1MOHM, consider reducing the affected channel to 51 Hz and removing it from service. If resistivity is LT 0.2MOHM then immediately remove the affected channel from service." This guidance comes from the P602 ARP. Current short insturctions only inform Operators to generate a WR at 5MOHM, but do not alert us to the urgency of the situation if resistivity is allowed to degrade. See EDMS for snap shot of ARP. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** OPS 4 logs (Form 27156) governed by PPM 3.1.10
398708 | CR | 20190902 |  | 3 | PMID 24972 MODEL WO# 01162449 NEEDS MODIFIED |  |  |  | N | NO | <D> **** Detailed Description **** NEED TO UPDATE WORK INSTRUCTIONS FOR PMID 24972 RWCU-CB-1A (RWCU-42-8C3B) MANUALLY OPERATE MCCB. <I> **** Actions Taken **** MARK UP OF CURRENT WO 02106598-01 AT S :\Maintenance\Maint\Electric Shop Folders\ELECTRIC SHOP PICTURES\RWCU-42-8C3B MODEL WO 01162449
398709 | CR | 20190902 |  | 3 | Procedure Enhancement OSP-RHR-A701 |  |  |  | N | NO | <D> **** Detailed Description **** OSP-RHR-A701 is the RHR-A Drop Test, wherein the keep fill pump is turned off and system pressure degradation rate is monitored and timed. Starting Service Water just prior to conducting this Drop Test would skew the results significantly because running Service Water cools the RHR HX and tends to lower RHR system pressure. Recommend a step be added to ensure SW-P-1A has been running for at least two hours prior to commencing the Drop Test. Note that this issue also applies to RHR-B drop test.
398710 | CR | 20190902 |  | 4 | CW-FN-1 Oil Level High | N | N |  | N | YES | <D> **** Detailed Description **** CW-FN-1 on CW-CT-1A oil level was found roughly an inch above the â€œFull Oil Level When Operatingâ€ mark, and equal to the â€œAdd Oilâ€ line on the manufacturerâ€™s plate. CR written for tracking purposes. <I> **** Actions Taken **** Informed supervision, wrote CR <N> **** Equipment Description **** NE fan on CW-CT-1A | 02-00-CW-FN-1
398711 | CR | 20190902 | CAQ | C | EBUWFB 441/2 annual test | N | N |  | N | NO | <D> **** Detailed Description **** Light had a battery fault indication and lamp loss indication did not pick up when wire was lifted. however the lights did stay on when the circuit was opened for 1.5 hours and voltage read full charge. <I> **** Actions Taken **** cr supervision <N> **** Equipment Description **** EBUWFB441/2 WR#29151366 generated. No further actions required under this Cr.
398719 | CR | 20190903 |  | 3 | Procedure enhancement OSP-SW/IST-Q702 |  |  |  | N | NO | <D> **** Detailed Description **** Change step 7.2.5 of OSP-SW/IST-Q702 to DG-2 <I> **** Actions Taken **** Wrote CR
398720 | CR | 20190903 |  | 3 | Unable to access history files needed for plant concern |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Unable to access history files needed for investigating plant concern. WR# 29151329, AR 00398610, OG-RIS-612 is on the plant concerns list for the INOP lamp not clearing during the performance of 16.4.1. I wanted to look into the last performance of 16.4.1(WO# 02104918-01) and was given a screen that reads, â€œSorry, this site hasnâ€™t been shared with youâ€. I have contacted supervision and they are unable to access the information either. This makes it difficult to investigate or compare past performances when plant concerns arise. In talking with other craft, this is an ongoing problem. <I> **** Actions Taken **** Expanded team, Informed supervision, wrote CR
398722 | CR | 20190903 | CAQ | C | Procedure PPM 10.1.13 not followed. |  |  |  | N | NO | <D> CR# 397557 documents a screw that was lost within an electrical cabinet within the control room. Under this CR, an assignment was created for the supervisor to follow all of the steps required per PPM 10.1.13 section 9.7.2. (Unrecovered FM Actions) per this section a DES 2-9 evaluation is required when foreign material is not removed from a system. The DES 2-9 was never completed due to the supervisor believing that the electrical panel within the control room was not a system. This error occurred because of miss communication between Engineering and the craft supervisor. The AR assignment closure notes documents that the screw will not be retrieved, and shall be left within the electrical cabinet. The concern the FME coordinator has in a worst case scenario, the screw could rub against cables and cause a short. Engineering needs to document that this condition is allowable per a DES 2-9 evaluation. The craft supervisor did not follow through with the guidance within PPM 10.1.13 to obtain this evaluation. <I> Discussed this situation with the Maintenance programs acting supervisor, craft supervisor, reopened the assignment under CR# 397557 with CAP supervisor permission in accordance with SWP-CAP-01. Created a new assignment under CR# 397557 for the craft supervisor to create an assignment, in accordance with PPM 10.1.13 section 7.9.2, for Engineering to perform a DES 2-9 evaluation on this condition. No further actions are required under this AR. Author recommends a CAQ severity level â€œD/ Trendâ€ due to all actions being taken under CR# 397557.
398725 | CR | 20190903 |  | 4 | SO-DPI-23A Needle Sticking | N | N |  | N | YES | <D> **** Detailed Description **** The needle on SO-DPI-23A is sticking. When you mechanically agitate the pressure indicator, the value will change by half a pound and stabilize after a few seconds. If you mechincally agitate the device again, it will change by another half a pound, search a little, and quickly stabilize at a different reading. By gently tapping the side of the housing a reading could stabilize anywhere between 15.25 and 16.25 psig. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** T441 Seal Oil Skid | 02-00-SO-DPI-23A
398728 | CR | 20190903 |  | 3 | Potential Gap in Solutions Implementation |  |  |  | N | NO | <D> There is a potential performance gap in the area solutions implementation (PI.3). The station identifies recurring and long-standing issues, however; corrective action plans and suggestions for improvement to resolve cross-functional station issues have not resulted in timely and sustained improvement. See EDMS for station trend resolution tmeline graph. Recommend assignment to Performance Improvement to validate trend and determine if a recovery plan should be developed. <I> Discussed issue with Performance Improvement Manager and initiated CR.
398735 | CR | 20190903 |  | 4 | First-Aid |  |  |  | N | NO | <D> **** Detailed Description **** While working on the east end of the 471'TG hallway (Storage Area) an Electrician was routing an extension cord overhead when he bumped his leg on a 20" HVAC duct causing him to lose his balance and as he tried to catch himself his right forearm came in contact with the cage of a shop light causing an abrasion to his right forearm. The employee immediately stopped and contacted WPS safety. First Aid was administered and employee returned to work with no issues. This is a First Aid. <I> **** Actions Taken **** WPS Safety followed ISPM-1 procedure requirements while notifying Occupational Health, ENW Industrial Safety and Site Support Contractor Manager regarding the details of this First Aid. No further action is required. Williams Plant Services.
398736 | CR | 20190903 |  | 4 | Missed RWP Post Job Review |  |  |  | N | NO | <D> **** Detailed Description **** The post job for RWP 30004480 was to be completed by 6-4 -19. However, due to hte RWP not being taken to HOLD until 9-1-19, the post job was missed. . <I> **** Actions Taken **** Notified Supervisor and created AR-Self 00398734-01 to track completion of Post Job Review.
398737 | CR | 20190903 |  | 3 | Reference to 1.3.55 needs added to MI-1.22A |  |  |  | N | NO | <D> **** Detailed Description **** Reference to 1.3.55 was removed from MI-1-22A as part of Rev 09 but should be added to the parts required and references section (pages 13, 14, 24). This was originally added as part of the change management under CR 00317184 when 1.3.55 was created.
398738 | CR | 20190903 |  | 3 | 471TG Hallway East End storage area. |  |  |  | N | NO | <D> **** Detailed Description **** + Poor Housekeeping in the 471TG hallway east-end storage area is an added hazard to our jobsite location for daily tasks. On the floor level there are an abundance of rags, miscellaneous equipment and debris protruding into the already slim work path. Poor housekeeping and potential falling tools/ construction material and garbage exist at the ceiling elevation of the 498TG hallway on top of cable tray covers, pipes and the concrete ledge just below the 501TG floor. It looks as if over the years garbage, tools and construction material have somehow fallen between the floor where the separate buildings meet and accumulated on the ledge. See pictures in EDMS <I> **** Actions Taken **** The craft contacted their Supervisor and WPS Safety was notified
398739 | CR | 20190903 |  |  | Testing the CR Wizard Process. |  |  |  | N | NO | <D> **** Detailed Description **** Testing the CR Wizard Process. Using the ANON Name Originator. <I> **** Actions Taken **** Using the ANON Name Originator.
398740 | CR | 20190903 |  |  | Testing the CR Wizard process |  |  |  |  | NO | <D> **** ANONYMOUS CR - Detailed Description **** Testing the CR Wizard process using the CR Anonymously Wizard. Testing the Wizard <N> CR created and canceled by me. Testing the Wizard.
398741 | CR | 20190903 |  |  | Testing the CR Wizard Process 2 |  |  |  |  | NO | <D> **** ANONYMOUS CR - Detailed Description **** Testing the CR Wizard Process test 2, using the ANON Wizard. Test complete. <I> **** Actions Taken **** Going to cancel this one.
398742 | CR | 20190903 | CAQ | D | FP-V-423 is leaking by. | N | N |  | N | YES | <D> **** Detailed Description **** FP-V-423 is leaking back towards to depressurized section of pipe that leads outside the building to the fire department connection. This is evidenced by water dripping from the hose connection. This valve was rebuilt in 2015 under WR 29123242. Please investigate and repair. <I> **** Actions Taken **** Informed supervisor and wrote this AR/WR. <N> **** Equipment Description **** ASD building. | 02-00-FP-V-423
398744 | CR | 20190903 |  | 4 | CAS-PCV-2 and CRD-F-6 SPV partially mitigated |  |  |  | N | NO | <D> **** Detailed Description **** CAS-PCV-2 and CRD-F-6 were correctly identified as a single point vulnerability (SPV)(AR 189771). A second pressure control valve and filter were installed in R24 (WO 02116063; EC 15931). Only one set of PCVs and Filters are currently in service as set forth in procedures (SOP-CRD -LU); the redundant set are isolated. Because manual intervention is required this condition only mitigates a slow failure. This CR is being written for engineering to consider an alternative that does not require manual intervention. E.g. having both filters and PCVs in service with offset pressure control set points to minimize oscillations. <N> EC DEC 15931 R1 is implemented, turned over, returned to service, and closed. Per discussion in the modification package itself: "Based upon an industry benchmarking question, the results indicate that the majority of plants have a manual swap from one regulator and filter to the other. The design team decided that due to the already installed ability to alarm on high or low pressure downstream of CRD-F-6, the manual swap would be the best way to proceed at Columbia." To make the configuration change suggested in this AR CR 398744, a new AR type EVAL is required to be initiated and processed through the DES-2-9 process.
398745 | CR | 20190903 |  | 3 | Previous Rev. to OI-69 Unclear |  |  |  | N | NO | <D> **** Detailed Description **** OI-69 covers Time Critical Operator Actions (TCOA). Periodic WO 02119136 is scheduled to verify and validate the times in these TCOA's. WOT 02119136-02 includes TCOA -27 which was eliminated from OI-69 in Revision 9 (12/12/2016). Previously this TCOA was to align SW to WMA-AH-51B if a fire is in RC-3 or RC-11 fire areas. In the Revision 9 description of changes, it is stated that "Time critical operator action to align WMA-CC-51A1 to SSW in the event of a fire in RC-12 or RC-13 no longer required. (AR 352659)." AR 352659 is all about WMA-CC-51A1 and WMA-AH-51A. These Div 1 SSC's have never been assoicated with any TCOA in OI-69. WMA-CC-51A1 is normally aligned to SW. WMA-CC-51B1 is normally aligned to CCH-CR-1B. Under certain conditions it may be necessary to either start CCH-CR-1B or align WMA-CC-51B1 to SW. Request Engineering evaluate this and submit a revision to OI-69 if necessary. <I> **** Actions Taken **** Reviewed all past revisions of OI-09 to validate there has never been a TCOA for aligning SW to WMA-CC-51A1 or WMA-AH-51A. <N> A revision to the control room heat load calculation changed the required start time for CCH-CR-1B from LT 1 hour to 3.1 hours (ABN-FIRE rev 32); this placed the operator action outside the purpose of OI-69 which is all operator actions that must be performed within 1 hour.
398746 | CR | 20190903 |  | 4 | WRA-AC-51 leaking water on the floor | N | N |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was observed that WRA -AC-51 was leaking water onto the floor. The water that was leaking was entering the "Stay Clear" area of the 525' communications room. The puddle on the floor was around four square feet. The AC unit seemed to be working fine and the room temperature at the time was 69 degrees. See also, CR 375980 WR 29140771 for similar issues. Pictures attached. <I> **** Actions Taken **** Informed CRS and wrote CR - Back Shift Mechanics notified and blew out condensate drain line. The drain pan emptied and the unit is no longer leaking water on the floor. = D.Fox <N> back shift mechanics were notified and blew out the clogged drain line. the condensate pan emptied and the unit is no longer leaking on the floor. -D.Fox | 02-00-WRA-AC-51
398747 | CR | 20190903 |  | 3 | CRD venting and draining hoses and adapters needed |  |  |  | N | NO | <C> CR re-opened and reassigned to AR-OPSST, severity 3. At the request of OPS. <D> **** Detailed Description **** While performing SOP-CRD-HCU it was noticed that the normal CRD vent and drain hoses were not staged. Normally 3 yellow high pressure/temperature hoses are staged at each end of the reactor building 522 elevation in the OPS lockers. 2 yellow hoses were found in one locker without the correct adapters at each end. Writing this CR to document the need for: 4 additional hoses; 6 adapters that allow connections to the CRD HCU downstream of CRD-V-107/* ; 4 adapters on the opposite end of the hose that allows connection to the EDR drain manifold (currently the 2 yellow hoses staged have that adapter). <N> **** Equipment Description **** CRD vent and drain hose with adapters need to be purchased
398748 | CR | 20190904 | CAQ | C | 16.4.1CC/RC Procedure change needed for OG-RIS-612 | N | Y |  | N | NO | <D> **** Detailed Description **** During the performance of 16.4.1 CC/RC it was discovered that section 7.9 cannot be performed. The recent revision to merge 16.4.2 Off-Gas Pretreatment Radiation Monitor RC into 16.4.1 CC kept the mode switch in trip test with the S3 pushbutton jumper installed. With OG-RIS-612 in this configuration section 7.9 Source Loop Check will not be able to be performed. 16.4.1 will need to be changed to place mode switch into operate and remove S3 pushbutton jumper in order for OG-RIS-612 to detect the desired exposure rates. <I> **** Actions Taken **** Stopped and verified the previous revisions of 16.4.1 and 16.4.2. Notified CRS and obtained permission to place equipment into a safe configuration and back out of 16.4.1 to have the proper revision made. <N> PPM 16.4.1 rev. 9 has been implemented and uploaded to control docs. This addresses this CR.
398762 | CR | 20190904 |  | 3 | Several I&C laptops unable to update Rohos correctly |  |  |  | N | YES | <D> **** Detailed Description **** While performing, 02138894-01, the PM to change the Roho passwords on the I&C laptops several laptops were unable to be updated properly. CGS 44, 46, and 98 would not log manually or with USB key. CGS 24, 48, and 55 were able to update the password, but did not update the USB properly, only manual entry works. <I> **** Actions Taken **** Notified supervisor, wrote CR/WR to get laptops fixed. <N> **** Equipment Description **** CGS44 CGS46 CGS48 CGS24 CGS98 CGS55 Close to WR 29151382.
398766 | CR | 20190904 |  | 4 | Work delayed due to limited resources and qual'ed personnel |  |  |  | N | YES | <D> **** Detailed Description **** During performance of 02138894-01, updating I&C laptop Roho passwords work was delayed, unable to finish the work within the scheduled time due to limited resources and lack of qualified individuals. Technician was unable to access the laptop cabinet at the tool crib inside of the plant due to tool crib personnel qualified as custodians not on site. When technician contacted the I&C supervisor to assist opening the cabinet they were unable to help due to dealing with other emergent issues. The number of qualified supervisors in the shop recently reduced to two from four, but still doing the work of four. This limits the ability of supervisors to leave their office and assist technicians in the field. <I> **** Actions Taken **** Suggest increasing the number of qualified custodians to include some or all of the craft that use laptops. This would also give the ability to the technicians to lock up laptops for breaks (without having another qualified individual guard the laptops while technician is out of sight) or when on backshift with limited personnel on site. All I&C technicians are authorized to work with CDAs have the CSAI qualification. This allows us to have possession of a CDA and use it on plant equipment, but are unable to access them. <N> **** Equipment Description **** none ***General Notes*** The lack of resources has already been addressed by the I&C Shop. No further actions are required for this issue.
398770 | CR | 20190904 | CAQ | D | RX 606' Hatch | N | N |  | N | I DONT KNOW | <C> CR at INPROG. Approved CR, moved to SRO for OPS Review. <D> While performing the PM inspection on the RX 606â€™ roof hatch we Identified two of the interior door handles look to be handmade and donâ€™t appear to be O.E.M. equipment. The westernmost latch internal spring and the handle do not function as required and needs replaced. Also the westernmost hinge bracket bolts are loose and needs to be tightened. This does not affect operability and the door can be sealed as designed. I would suggest replacing two latch mechanisms and re-tightened the hinge bolts. <I> Notified Supervision, the control room and wrote this CR. <N> RX 606' roof hatch These defects do not impact the secondary containment integrity. Secondary containment remains operable.
398771 | CR | 20190904 |  | 4 | Broken cover on HD-RLY-63X2AT/1 | N | N |  | N | YES | <D> **** Detailed Description **** While replacing HD-RLY-63X2AT the relay, when it was pulled, dropped slightly touching HD-RLY-63X2AT/1 and broke the relays cover. THis does not effect the function of the HD-RLY-63X2AT/1. <I> **** Actions Taken **** Informed supervision, temporarilly taped the cover back into place, informed SM. <N> ***General Notes*** This is not an HU event. The covers have no room between the various relays and the plastic associated with the relay covers are baked in the heat of the turbine building, which causes the plastic of the covers to become brittle over time. If you look at the design of the covers you will also note that surface area of the plastic holding the fastener is not robust enough. This is a well-known issue with these relay cover models. | 02-00-HD-RLY-63X2AT/1
398775 | CR | 20190904 |  | 4 | PWC-SV-301 leak | N | N |  | N | YES | <C> This was discussed with the Facilities manager and due to this being a plant valve is not under their control. It has a work request and therefore can be changed to a 4/TR. The MFIN supervisor has been informed. <D> **** Detailed Description **** PWC-SV-301 has a substantial leak <I> **** Actions Taken **** Notified control room. Left message with FIN supervisor <N> **** Equipment Description **** PWC-SV-301 South of cooling towers
398776 | CR | 20190904 | CAQ | C | NSR RWCU valves in the Reactor Bldg. are misclassified | N | N |  | N | NO | <D> **** Detailed Description **** NSR RWCU valves in the Reactor Building are misclassified as seismic II in Asset Suite During the review and RPE certification of EC SPC 17898 for RWCU-V-44, EC SPC 17756 for RWCU-V-105 and EC SPC 17757 for RWCU-V-104 and RWCU-V-42, it was discovered that these ASME III Class 3 non-safety related valves are misclassified in the Asset Suite/ Portal J, D031 -Equipment/Component additional details. These valves were classified as Seismic 2, Safety Class NSR and Quality Group 2 (D048). These valves should have been classified as Seismic 1M, Safety Class AQ and Quality Group A per FSAR Figure 5.4 -22.1 (Drawing M523-1) Note 1.b. Seismic Category II + and FSAR Table 3.2-1 Equipment Classification Item 18 for RWCU system which states: Valves, beyond outermost containment isolation valves Reactor Bldg. Quality Group C Quality Class II Seismic Category II and Notes: 2, 4, f, g & h. Notes: g states: 1M - non-safety-related components required to be seismically supported/mounted. This was alternatively called Seismic II + which is Seismic II piping supported on hangars designed to Seismic I loads. FSAR Section 3.2.1 states: Seismic Category 1M classification denotes systems, structures or components that are designed and constructed to comply with position C.2 of Regulatory Guide 1.29. Additionally, FSAR Section 3.2.4 QUALITY ASSURANCE CLASSIFICATION states: b. Quality Class II+ (A in MEL) - Assigned to SSCs having no safety-related function but requiring quality augmentation either as a result of NRC requirements or as committed by CGS. Quality augmentation may include such requirements as environmental qualification, seismic qualification, or other quality affecting activities specifically committed. Augmented quality applies to the following categories of SSCs: 2. Structures, systems, and components that do not perform a safety-related function but must be seismically supported/mounted (seismic 2-over-1) per Regulatory Guide 1.29. AED TEC TM-2043 Augmented Quality Requirements Section 3.6 SEISMIC CATEGORY 1M states: The 1 M category applies to non-safety-related components that are required to be seismically supported/mounted to meet Regulatory Guide 1.29, Position C.2. Components in the 1M augmented quality category have the following Asset Suite/Portal-J attributes; Seismic= 1M, Safety Classification= AQ and Quality Class= A and Environmental Qualification: Not required, EQ Related = N. Please note that RWCU pumps (1A and 1B), regenerative HXs (1A, 1B & 1C) and non-regenerative HXs (2A & 2B) are classified correctly in Asset Suite/Portal-J as Seismic= 1M, Safety Classification= AQ and Quality Class= A. This condition is an administrative issue and not an equipment issue which does not affect the CGSâ€™ SSC. This condition/discrepancy only exists in Asset Suite/Portal-J and MEL and has no impact on CGSâ€™ SSC because: (a) The licensing basis and design basis documents are in agreement with each other while they are in compliance with the applicable regulatory requirements. (b) The piping system including valves body and the actuators are modeled and analyzed to Seismic Category I loading. (Reference piping calculations: 8.14.148A for RWCU-V-104, 42, 105 and 8.10.136 for RWCU-V-44, and Reference Valves with MOV stress reports: 41B-00-0145 [RWCU-V-44], 41B-00-0143 [RWCU-V-42], 41B-00-0142 [RWCU-V -104], RWCU-V-105 with no actuator modeled as rigid member). (c) The RWCU pumps and heat exchangers are correctly classified as Seismic= 1M, Safety Classification= AQ and Quality Class= A. Additionally, this condition in Asset Suite/Portal-J is not only applicable to RWCU system in the Reactor building but also other NSR systems in any of the seismic 1 area/buildings (i.e. RCC, TMU, etc.). Therefore recommend an extent of condition for other NSR systems in any of the seismic 1 area/buildings. Recommend Severity level â€œCâ€ to ELECTRICAL/I&C DESIGN & DRAFTING GROUP (AR-DESDFTE) for resolution. <I> **** Actions Taken **** (a) Corrected the new valve Data Sheets for RWCU replacement valves. (b) Asset Suite was corrected to provide the correct safety class, seismic class and Quality Group (c) Informed the Design and RWCU Hx Project supervisors. (d) Initiated this CR (e) Contacted the main control room
398777 | CR | 20190904 | CAQ | C | (QA) QC Rejection of ASME Itemâ€™s for SW-FE-39. | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) QC identified damaged material while performing acceptance of ASME parts for WOT 02139804-02. Material is not acceptable per QC Inspection Plan G-101 due to observed damage. ASME studs (CID 25123084) have flat spots that will not allow a nut to pass over them. Flange faces (CID 35186) have linear indications that extend across the sealing areas that could cause a leak path. This issue was identified during a shop activity. <I> **** Actions Taken **** Notified the ASME PLE, EN Maintenance Supervisor, QC Level III and Quality Services Supervisor. Equipment is not installed in plant. <N> See attached pictures in EDMS file.
398778 | CR | 20190904 |  | 3 | BPA CALIBRATE METERS PM Does Not Perform In-Service Testing | N | N |  | N | YES | <D> **** Detailed Description **** This CR is associated with a PM for BPA owned WATT & VAR hour revenue meters for the purpose of billing. T-2 scheduled PM work order 02118522 BPAMETERSE880: BPA CALIBRATE METERS calibrates the meters however it does not perform in-service testing of BPA revenue meters E-VARM-1, E-WHM-5 and E-WHM-VARM/6. In-service testing is done to validate function, that all current and voltage inputs are connected and that there is not excessive burden within the circuit. New BPA internal OE identified meters at other installations that did not have all of the current inputs connected. This was realized after performing in-service testing which requires a load on the associated transformer. For CGS this means rescheduling the work, revising the PM to add loading of the TRS and TRB transformers to in-service the meters. This will also affect Operations and Electric shop resources. - Note: E-VARM-1 is the BPA VAR hour meter for the TRS transformer E-WHM-5 is the BPA WATT hour meter for the TRS transformer E-WHM-VARM/6 is the BPA combination WATT & VAR hour meter for the TRB transformer. This PM calibrates BPA revenue watt & VAR meters for the purpose of accurate billing. <I> **** Actions Taken **** Discussed with BPA SPC Engineer, Supervisor and System Engineer. Contacted the T-2 work week Manager and Unit Coordinator. Coordinated a reschedule date of 10/29 & 10/30/19. . AR-SMS submitted by Hagfeldt and on cross-referenced. No further actions need for this AR <N> **** Equipment Description **** These are BPA owned WATT & VAR Meters used for billing purp oses. | 02-00-E-VARM-1,02-00-E-WHM-5,02-00-E-WHM-VARM/6
398779 | CR | 20190904 | CAQ | C | PCINT/PCISO system has been placed into MRule (a)(1) status | N | N |  | N | NO | <D> **** Detailed Description **** This AR CR is being written in accordance with SYS-4-22 as the PCINT/PCISO system has been placed into Maintenance Rule status (a)(1). This status is in reference to 10CFR50.65 (a)(1). . The MRule performance monitoring program identified that the PCINT/PCISO system had 6 Condition Monitoring Failures (CMF) which exceeded the performance criterion of < 4 FF. Reference AR assignment 00313942-85-01 for more details. . In accordance with the Columbia M-Rule guidance document, System Engineering Instruction SYS-4-22, these failures associated with the PCINT/PCISO system were evaluated and presented to the System Engineering Manager who approved changing the MRule status to (a)(1), reference AR 313942 -85-01 assignment. The appropriate Performance Improvement Plan needs to be developed outlining any Corrective Actions, Goals and Monitoring plan to return PCINT/PCISO system to satisfactory health and (a)(2) status. Refer to System Engineering Technical Instruction SYS-4-22 for detailed guidance for this evaluation. . AR CR to be assigned to AR-ER as Cat.C to create assignment for the development of a Maintenance Rule (a)(1) performance improvement plan.
398781 | CR | 20190904 |  | 4 | PWC-SV-301 has a pencil stream body to bonnet leak | N | N |  | N | YES | <D> **** Detailed Description **** a pencil stream body to bonnet leak was found on PWC-SV-301 PWC-V-514 was shut to isolate it. <I> **** Actions Taken **** Notified the MCR and wrote this CR/WR | 02-00-PWC-SV-301
398783 | CR | 20190904 |  | 4 | WOA-MC-9B failed | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WOT 0211307401 could not complete the portion of the loop cal on WO-MC-9B, the MC did not respond to any %RH change. believe its failed. WOA-MC-9C is loctated inside the duct could not get to element to function check it. therefore could not check WOA-HU-9. <I> **** Actions Taken **** Informed Supervisor, created CR/WR to replace WOA-MC-9B | 02-00-WOA-MC-9B
398786 | CR | 20190904 |  | 3 | TIRP cause evaluation form 26592 difficult to use |  |  |  | N | NO | <D> **** Detailed Description **** During OCC review for a recent station emergent issue, the technical issue resolution process (TIRP) Cause Evaluation Sheet Form # 26592 was found to be difficult to read and understand. And, the information on the form cannot be updated and re-organized to improve this communication either as the sections of the forms are locked. Recommend updating the form as it is used as a communication tool along with investigation tool. Benchmarking was performed and an example of the enhanced version is uploaded to the EDMS folder of this CR. Recommend assigning the CR to AR-EFIN.
398788 | CR | 20190904 |  | 4 | Aux Boiler leaking water while in wet layup | N | N |  | N | YES | <D> **** Detailed Description **** AS-BLR-1 is losing approximately 1 inch a shift while in wet layup. No visible water leaking from manway covers, on the floor, or out of any components. Suspected leakage either going into T-1 or internal leakage from a tube leak. <I> **** Actions Taken **** Performed visual inspection of the Aux Boiler. Performed a walkthrough of SOP-AS-SHUTDOWN for the aux boiler shutdown/wet layup sections. Informed MCR | 02-00-AS-BLR-1
398789 | CR | 20190904 |  | 4 | DSA-V-59B leaks by the seat. | N | N |  | N | YES | <D> **** Detailed Description **** DSA-V-59B was noted to leak by during tagout of DSA-DY-1B. Leakby was stopped by closing DSA-V-70B. This would also indicate that DSA-V-15B or DSA-V-16B were leaking by as well. <I> **** Actions Taken **** Expanded clearance boundary to include DSA-V-70B. <N> **** Equipment Description **** DG2 room | 02-00-DSA-V-59B
398790 | CR | 20190904 |  | 4 | SP-4 In-Line Meter/Recorder GT 10% Difference | N | N |  | N | YES | <D> SP-4 inline conductivity recorder disagrees with grab sample by 13%. SP-4 inline conductivity meter disagrees with grab sample by 15%. Meter and Recorder still in service as long as readings are withing 20%. <I> Wrote CR, Informed Supervision <N> TG 441' Chemistry Sample Room
398793 | CR | 20190904 | CAQ | D | while performing 10.27.31 found ARM-RIS-33 high alarm OOT | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** WO#02148951-03 Found ARM-RIS-33 high alarm set at 1.21 E-10 OOT desired is 1.12 E-110 upper limit of 1.18 E-10 <I> **** Actions Taken **** Adjusted to within specifications and informed CRS.
398794 | CR | 20190904 |  | 3 | PO.6 scoping tool error causes scoping concern |  |  |  | N | NO | <D> **** Detailed Description **** During Engineering PO.6 scope review, the R25 scope of the large pump and motor programs were being validated. Three issues were identified. The first was that the LPCS-P-1 replacement/refurbishment was not assigned to an engineer for review (resolved). The second was that the COND-P-1A replacement/refurbishment work order was incorrectly scoped out of R25 based on the work order being coded RP26 (resolved). Finally, the last issue is that after marking both of those work orders for R25 scope = Y, dating my review, ensuring that I flag the column to update the spreadsheet to a Y, and then uploading my review via the macroâ€™d button, my information did not show up in the spreadsheet. More concerning than the information not showing up in the spreadsheet, however, was that my review of LPCS-P-1 had been changed to R25 = N, and timestamped with another engineering supervisorâ€™s review. This CR is being generated as the tool owner was unable to be contacted for technical support, and this situation calls into question our scoping process reliability and extent of condition for these particular issues. <I> **** Actions Taken **** Attempted to contact scoping tool owner for technical assistance and understanding. Was unable to contact via telephone or pager. Discussed with Engineering PO.6 lead supervisor my concern and lack of confidence that our team is viewing the entire population of work orders needed to review for PO.6. Elevated concern to my manager. <N> Issue was that the users were not updating the time stamp when doing block changes. Updated software to update the time stamp. Problem resolved.
398795 | CR | 20190904 |  | 3 | PO.6 scoping tool issue |  |  |  | N | NO | <D> **** Detailed Description **** The PO.6 scoping tool requires that a macroâ€™d button titled â€œGet Latest Review Dataâ€ be pressed to get the most recent data provided by engineering related to recommendation for R25 scope, Work Order rank, justification, actions needed, owner, supervisor, and reviews performed. During Engineering Supervisor review of proposed PO.6 scoping, it was identified that the tool has a feature that requires that the â€œGet Latest Review Dataâ€ button be pressed twice, in succession, in order to ensure that the team was actually looking at the most up to date data. This creates an error likely situation since scoping decisions are being made and no guidance was provided that the button would not return all of the most recent data unless depressed twice in succession. <I> **** Actions Taken **** Changed our practice to depress the button twice. In process of reviewing scope to ensure that the engineering supervisors did not incorrectly scope work orders in or out. <N> Updated spreadsheet software and issues corrected. No actions required.
398796 | CR | 20190904 |  | 3 | BS-DV-2A1 indicates OPEN on H13-P832. | N | N |  | N | YES | <D> **** Detailed Description **** BS-DV-2A1 indicates OPEN on H13-P832 (it should be CLOSED). This was discovered while performing compensatory temporary log for the locked-in annunciator H13-P840.A2 9-6 -STEAM DUMP VALVES NOT FULLY CLOSED. This annunciator was already locked-in due to BS-DV-2A being failed open (AR 397292). There is no noticeable change in Reactor Feedwater inlet temperature on normally monitored instrumentation - 420.6 def. F on plant computer overview display. RFW-TI-5 indicates ~ 413 def. F - which is what it has been indicating. The LP Heater 2A shell pressure indicates normally on BS-PI-2A at 14 psia (the 2B and 2C heaters indicated 13.7 psia and 13.4 psia, respectively). HD-LIC-2A is maintaining LP Heater 2A level at the setpoint in automatic, but controller output is near 95%. <I> **** Actions Taken **** Notified the CRS and SM. Submitted CR to document the condition. . Notified AOM Crew, WWM, Eng. Backshift Coordinator. Sent Management Text. Added to PCL. | 02-00-BS-DV-2A1
398797 | CR | 20190905 |  | 4 | PC SYS-STAT Trouble Alarm HSSF-CAB-CHEM/LAB | N | N |  | N | YES | <D> **** Detailed Description **** Recieved PC SYS-STAT Trouble Alarm from the HSSF-CAB -CHEM/LAB Annunciator Computer. This is a high priority alarm with Tele Tank signal. <I> **** Actions Taken **** CR written. CRS and chemistry supervision informed. | 02-00-HSSF-CAB-CHEM/LAB
398802 | CR | 20190905 |  | 3 | R24LL: Pre-outage plan and expectations not aligned |  |  |  | N | NO | <D> **** Detailed Description **** Gap #1 identified in station R24 Critique: Pre-Outage Plan and Expectations are not aligned, challenging outage readiness. Prior to R24, scope additions, weekly resource availability, and 2-week â€œno fly zoneâ€ were not appropriately controlled and/or utilized during the R24 pre-outage window (January to Breaker Open), resulting in decreased readiness and poor outage schedule adherence. Vertical slice ineffectiveness and inadequate application of resource / qualification look-ahead tools, exacerbated this outcome. Recommend assignment as Severity 3 to AR -OTMG to develop actions.
398803 | CR | 20190905 |  | 3 | R24LL: OCC teamwork improvement needed |  |  |  | N | NO | <D> **** Detailed Description **** Gap #2 identified in station R24 Critique: Inconsistent use of OCC priorities, goals, and communication methods challenged the teamâ€™s ability to recover schedule slips. In R24, there were multiple occurrences of misaligned priorities following OCC turnover resulting in lost productivity and decreased organizational alignment. OCC dayshift and nightshift were not aligned on intermediate schedule goals and priorities nor how to appropriately communicate goals and priorities to the organization, weakening the OCCâ€™s ability to drive towards a successful outage duration. Recommend assignment as Severity 3 to AR -OTMG to develop actions.
398804 | CR | 20190905 |  | 3 | R24LL: Schedule execution improvement needed |  |  |  | N | NO | <D> **** Detailed Description **** Gap #3 identified in station R24 Critique: Ineffective response to the initial bow wave and inadequate discipline to maintaining a viable daily schedule, combined with shift inefficiencies, resulted in poor schedule adherence. In R24, the bow wave initiated within the first 96 hours from open breakers. Bow wave recognition and response was poor, leading to multiple data-date riders, schedule conflicts, and priority differences. These events were further compounded by productivity inefficiencies (mobilization to and from the field, management of breaks, and lack of FIN availability on nights). Recommend assignment as Severity 3 to AR-OTMG to develop actions.
398805 | CR | 20190905 |  | 3 | R24LL: LLRT execution improvement needed |  |  |  | N | NO | <D> **** Detailed Description **** Gap #4 identified in station R24 Critique: Unclear expectations for leadership and coordination between the execution team and LLRT Program owner, led to significant schedule delays. In R24, LLRT execution challenged entry into and exit from several key system / outage windows. Up front challenges with the Common Residual Heat Removal (0RHR) and Reactor Water Clean-Up (RWCU) testing sequences were significant impacts to the outage. Inadequate readiness was observed regarding test equipment conditions (i.e. carts and fittings), instruction / procedure guidance, and resource allocations. Recommend assignment as Severity 3 to AR-OTMG to develop actions.
398806 | CR | 20190905 |  | 3 | R24LL: MSIV/SRV/CIA outage window is not optimized |  |  |  | N | NO | <D> **** Detailed Description **** Gap #5 identified in station R24 Critique: The current MSIV/SRV/CIA window is not optimized, resulting in preventable implementation challenges and schedule delays. In R24, due to predecessor schedule adherence impacts, equipment challenges, and lack of a clear sequence of events, the MSIV, SRV, and CIA testing windows were not completed as scheduled. Notable events included having the MSIVs stroked more than required, poor adherence to the SRV reassembly sequence resulting in schedule delays, and delayed decision making stemming from the observed CIA testing conditions. Recommend assignment as Severity 3 to AR-OTMG to develop actions.
398807 | CR | 20190905 |  | 4 | Chemistry dose budget exceeded for August 2019 |  |  |  | N | NO | <D> **** Detailed Description **** The Chemistry dose budget was exceeded for August 2019. The dose estimate was 150 mR with a goal of 135 mR. The Chemistry department received 143 mR. This is within the established estimate but above the goal. The extra dose can be attributed to loss of HWC requiring extra sampling and the continuing elevated dose rates in the hot sample sink. Evaluation of sampling and cross check activities in the hot sample sink is in progress to reduce dose.
398808 | CR | 20190905 |  | 3 | PROVIDING SSN FOR BADGING PURPOSES |  |  |  | N | NO | <D> **** Detailed Description **** Information received from another licenseeâ€™s access authorization organization revealed that a regulatory agency visiting their site refused to provide necessary data in order for them to activate a PA badge assigned to the regulators. This same data is necessary in the Columbia process in order to activate badges for personnel from this agency. In order to mitigate circumstances that would arise at Columbia given the same scenario a process must be developed and tested in order to ensure this regulatory agency may be badged as requested. Currently, an alternatively approved process does not exist to accomplish this task. <I> **** Actions Taken **** Made initial notification to Reg Affairs, and technical personnel to develop a viable solution. <N> **** Equipment Description **** Integrated Enterprise Badging System NRC badge numbers have been entered into the database for testing integrity, test data utilized did not negatively affect functionality. The path forward for NRC staff who have not previously visited Columbia and do not want to provide SSN AA will utilize NRC badge number in place of SSN. Procedures will need to be updated with guidance actions have been created to revise procedures. Night order is in place with guidance until procedures have been revised.
398809 | CR | 20190905 |  | 4 | PREVENTATIVE MAINTENANCE FOR TEA FANS |  |  |  | N | YES | <D> **** Detailed Description **** DURING PERFOMANCE OF 0214 5606 INSULATION REPAIR ON TEA-FAN -1C IT WAS IDENTIFIED THAT ALL 4 TEA FANS HAVE DEGRADED INSULATION FROM EXPOSURE TO THE ELEMENTS. MOST AREAS OF DEGREDATION ARE MINOR IN NATURE LIMITED TO ONLY THE WEATHER BARRIER AND NO INSULATION NEEDS TO BE REPLACED. IF REPAIRS ARE PERFORMED BEFORE THE DAMAGE GETS WORSE IT WOULD BE A SUBSTANTIAL SAVINGS IN LABOR VERSUS INSULATION REPLACEMENT THAT WAS REQUIRED ON TEA-FN-1C. RECOMMEND SYSTEM ENGINEER WALKDOWN TO EVALUATE DAMAGE. <I> **** Actions Taken **** NOTIFIED SUPERVISION, NOTIFIED OPERATIONS, INITIATED CR <N> **** Equipment Description **** RAD WASTE ROOF 542'EL | 02-00-TEA-FN-1A,02-00-TEA-FN-1B,02-00-TEA-FN-1C,02-00-TEA-FN-1D
398810 | CR | 20190905 |  | 4 | Low Flow TSW-SP-89 | N | N |  | N | NO | <D> **** Detailed Description **** TSW system discharge chemistry sampling point TSW-SP-89 on the outer north wall of the T117 Seal Oil Room on TB 441' continues to produce extremely low flow, necessitating excessive flush and collection times. Sample point isoluted using TSW-V-750A. <I> **** Actions Taken **** CR and WO initiated. Request for sample line to be blown out to restore flow. <N> **** Equipment Description **** TB 441' north end outside T117 seal oil room.
398814 | CR | 20190905 | CAQ | C | Radiation Exposure Record missing Units |  |  |  | N | NO | <D> **** Detailed Description **** There is no impact to operating the plant since this involves Radiation Exposure Records. The general provision of 10 CFR 20 (Subpart L) concerning Records, directs each licensee to use units of all quantities on records. Our current process for in-processing utilizes FORM 848 as a written signed statement from the individual to record their current year occupational dose, but the FORM does not list the units. The form needs to specify the units of the quantities recorded, but limit the likelihood of error if units are confused while someone is in-processing. This FORM is referenced in PPM 11.2.6.1-Issuance and Retrieval of Personnel Dosimetry.
398818 | CR | 20190905 |  | 4 | Late Inter Organizational Agreements (IOAs) |  |  |  | N | NO | <C> MRT requested notes be added by initiator for clarification of cause. . Reopened for notes to be added by the initiator. <D> **** Detailed Description **** Inter Organizational Agreements for CGS Operations and Facilities Site 1 water usage not complete by beginning of FY20. This CR is for trending purposes. <I> **** Actions Taken **** IOAs drafted and routed for approvals in late August. <N> The cause of the late IOAs were due to a failure to assign job duties during staff turnover.
398820 | CR | 20190905 | CAQ | B | Radwaste liner void space not less than 15% |  |  |  | N | NO | <C> RISK: Medium. CAUSE: Clear. B Severity - Document & Correct. Causes & Corrective Actions Known and created. MRT Change: Change to CAUSE: UNCLEAR, IT Requierd RISK: Medium. CAUSE: UNCLEAR. B Severity - Investigation Template Required. <D> **** Detailed Description **** Radioactive waste shipment 19-96 containing liner 19-048-HP departed Columbia Generating Station (CGS) in the morning of 9-4-19 bound for the US Ecology Disposal Site. At about 0900, a RWTS received a call from US Ecology informing of a potential issue with the media volume listed on the manifest. The rep. from the State of WA identified that the void space was not less than 15% as required by License Condition 24. Actual void space was 15%. <I> **** Actions Taken **** 1. State and US Ecology held discussions concerning the liner and a request was submitted and granted to dispose of the liner as is. 2. The State will issue a letter to CGS concerning this issue . 3. CGS Supervision was informed of the potential issue. 4. Verfiied CGS procedural guidance is accurate and adequate when followed to preclude recurrence of this issue. 5. Discussed this issue with all RWTS personnel on site to ensure understanding of license condition 24 requirements concerning void space.
398821 | CR | 20190905 |  | 3 | Update to TPD-19 Energy Northwest Planner Training Program |  |  |  | N | NO | <D> **** Detailed Description **** Update to TPD-19 Energy Northwest Planner Training Program Description and Planning Qual Matrix required During review of recent events multiple issues were discovered. 1. PLAA and PLAB definitions do not match current needs of Maintenance Department. 2. PLAA does not reflect the need for discipline specific qualification, though individuals with the qualification may be planning instructions for specific disciplines. 3. PLAB has different limits for different work groups. Requirements should be universal or different qual groups need to be made. 4. Implementation of discipline specific planning qualifications was not fully integrated into the TPD. 5. Does not currently align with GBP-PRO-03 for procedure layout. <I> **** Actions Taken **** Documented findings in CR.
398823 | CR | 20190905 | CAQ | C | DG-1 DSA Check valve test | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of Attachement 9.3 of OSP-ELEC-M701 the pressure on DSA-PI-9 read between steps 3 and 5 rose approximately 65 psig. The limit before a CR must be generated is LT 10psig. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** DG-1 Room | 02-00-DSA-V-15A,02-00-DSA-V-16A
398824 | CR | 20190905 |  | 4 | OG-SR-4 light cover | N | N |  | N | YES | <D> **** Detailed Description **** DS-4 on OG-SR-4 is missing its light cover and needs a replacement. <I> **** Actions Taken **** Informed chemistry specialist and wrote a CR/WR. <N> **** Equipment Description **** TB 441' chemistry sample room | 02-00-OG-SR-4
398825 | CR | 20190905 | CAQ | D | test equipment needs recalibrated |  |  |  | N | NO | <D> **** Detailed Description **** During isp-cms-x310, steps were reperformed due to ektron temperature simulator drifting in the mid ranges (120 -145, 220-245, 320-345. MTE id 0064310 <I> **** Actions Taken **** Notified operations and i/c supervision. used a different ektron and reperformed steps. returned defective mte to tool crib and signage do not use
398826 | CR | 20190905 |  | 4 | No deltaT for TSW inlet/outlet to RCC-HX-1C in eDNA | N | N |  | N | YES | <D> **** Detailed Description **** While trending and monitoring RCC Heat Exchanger data on eDNA, for RCC-HX-1C there appears to be only a 0.5Â°F delta between TSW inlet temperature (L066) and TSW outlet temperature (S017). TSW flows through RCC-HX-1C (F124) are in line with all three RCC HXs in service which was validated through discussion with the shift manager. TSW deltaT for the other two RCC HXs are between 7 and 9Â°F. Either this may be indication that one or both the inlet/outlet temperatures for TSW to RCC-HX-1C are not reading correctly or that there is very little cooling being done to the TSW flowing through RCC-HX-1C if the data is correct. <I> **** Actions Taken **** Discussed with SM, supervisor, and TSW system engineer. | 02-00-RCC-HX-1C
398827 | CR | 20190905 |  | 3 | Revision to PPM 11.2.24.2 compensatory measures |  |  |  | N | NO | <D> **** Detailed Description **** There is no impact to the station since the Compensatory Measure for OG-RIS-612 is setup correctly and data is transmitting to eDNA. Step 6.1.6.a in Attachment 8.4 of 11.2.24.2 incorrectly states how the eDNA point for this compensatory measure be setup. It should actually say â€œOG-RIS-612â€, which is how it is setup currently. The procedure should be revised to align with this. Data transmission was verified in eDNA Real Time Client, and HP Techs are logging the reading. This may also require a revision to step 6.1.9.b in the same procedure for the Long ID of this eDNA point.
398829 | CR | 20190905 | CAQ | C | FP-TK-110 Low OOS. | N | Y |  | N | YES | <D> **** Detailed Description **** Task 02136345 scheduled with FP-P-2A and FP-P-110 to support fire system testing left FP-TK-110 low OOS. <I> **** Actions Taken **** Currently Filling FP-TK-110 Protection scheme genertaed for FP-P-1 and FP-P-2A. Informed CRS/SM | 02-00-FP-TK-110
398830 | CR | 20190905 |  | 4 | Cooling Tower Fan 36 Vibration Cannot Be Reset | N | N |  | N | YES | <D> **** Detailed Description **** Received alarm 4.824.M.5-1, CW Cooling Tower Fans 31 through 36 â€“ overload/vibration high. Ops 4 dispatched to check and reset vibe switches. Fans 31 through 36 are still running. Fan 36 vibration switch will not depress. Alarm is still locked in. <I> **** Actions Taken **** Dispatched OPS 4 to investigate. Initiated CR/WR <N> **** Equipment Description **** CW Cooling Tower 2C | 02-00-CW-FN-36
398831 | CR | 20190905 | CAQ | C | SW-SYS-B LCO tracking during ODMI oil samples |  |  |  | N | NO | <D> **** Detailed Description **** Since "SW-M-P/1B shows elevated water level in upper reservoir oil" ODMI was issued on 7/22/19 there have been approximately 8 oil samples taken. During these samples there is no evidence that SW-SYS-B was declared INOP as the condition evaluation done for AR 344784 suggests that it should be.
398832 | CR | 20190905 |  | 3 | Diesel Fuel Polisher building needs updated posting. |  |  |  | N | YES | <D> **** Detailed Description **** The signage and postings for the Diesel Fuel Polisher building do not reflect the current safety standards. The Diesel Polisher building is a hardhat exempt area but the signage and postings do not reflect this and should be updated and replaced. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** Building 23
398833 | CR | 20190905 |  | 3 | SOP-FP-START Needs Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** If FP-P-110 is run for more than a brief period of time without make-up results in draining FP-TK-110 to below LCS 1.10.1 specifications. This is due to the minimum flow for FP-P-110 being routed to the evaporator ponds. Ref CR 398829 and 390524. <I> **** Actions Taken **** Recommend adding a Caution to section 5.5 of SOP-FP-START: â€œExtended operation of FP-P-110 will result in lowering level of FP-TK-110 to below LCS 1.10.1 Secondary Fire Protection System water inventory limit specified in SR 1.10.1.1 due to minimum flow of FP-P-110 draining to the evaporator ponds.â€ <N> **** Equipment Description **** Secondary Fire Protection
398834 | CR | 20190906 |  | 4 | failed EBU | N | N |  | N | NO | <D> **** Detailed Description **** 02084611 07 both EBU's failed. <I> **** Actions Taken **** cr wo documentation <N> **** Equipment Description **** cw electrical bldg 2
398835 | CR | 20190906 |  | 3 | Potable water break between PWC-V-342 and PWC-V-560 |  |  |  | N | YES | <D> **** Detailed Description **** A large PWC leak was reported to the control room by Security. The leak is located East of the CAS, just outside the fence. Estimated leak rate was about 200 GPM. Leak isolation was hampered by conflicting and out-of-date drawings. Per AED MIS P541-3 and AED ARC C876D, PWC-V-342 is a "reverse acting" ball valve. Per FAC-SIT2 G20MP001, PWC-V-342 is a normally operated gate valve. Per P541-3 PWC-V-560 is a ball valve, but FAC-SIT2 G20MP001 shows it as a normal gate valve. Per P541-3 PWC-V-340 is a "reverse acting" ball valve, but according to FAC-SIT2 G20MP001 it is a normally operated gate valve. Based on a discussion with a facilities supervisor knowledgeable of the installation of these valves, PWC-V-340, -358 and-560 are normally operated gate valves, and PWC-V-342 is a "reverse acting" ball valve. As often as we support leak isolation, Site 1 cross-tie and PWC maintenance, we must have accurate drawings and valve information. <I> **** Actions Taken **** Performed leak isolation by closing PWC-V-340 and -342. Contacted Facilities on-call supervisor. | 02-00-PWC-V-340,02-00-PWC-V-342
398845 | CR | 20190906 | CAQ | D | The rubber bumper for the R-DOOR-R110 door stop is worn out | N | N |  | N | YES | <D> **** Detailed Description **** The rubber bumper for the R-DOOR-R110 door stop is worn out. Please replace the door stop bumper for R-DOOR-R110. See the photos attached to the EDMS of this AR CR 398845. <I> This does not impact the barrier function for the door. | 02-00-R-DOOR-R110
398846 | CR | 20190906 |  | 3 | PM Model WOs for CTMA-AC-1 and CTMA-AC-2 need updated |  |  |  | N | NO | <D> **** Detailed Description **** As part of job planning/prep, it was identified that a different CATID is required for CTMA-AC-1 and CTMA-AC-2 than what was ordered. <I> **** Actions Taken **** Worked with planner on task that was at Returned status for T-3 next week. Filters will be here to support the 9/30/19 implementation week. Recommend assign to planning to follow up and ensure model WOs for PMID 2975-01 and 02, as well as PMID 2974-01 and 02 are updated. Planning did go in a update the models for PMID 2975-02 and 2974-02, for the material, however additional checks for the correct documents and CVI information, as well as the various belts that are on the the PMID-RQs, 2974-01 and 2975-01 need reviewed validated prior to next occurrence model WO being generated.
398847 | CR | 20190906 |  | 3 | Enhancement needed for FP-P-110 operation |  |  |  | N | NO | <D> **** Detailed Description **** P&L 4.5 from 15.1.4 should be incorporated into SOP-FP -start. To enhance monitor FP-TK-110 level with make up being needed due to expected tank level decline within the body of the procedure (5.5.4 and 5.5.6) SOP-FP-SHUTDOWN 5.4.8 needs a bullet added to check FP-TK -110 GT 320Kgal upon s/d of pump. Add P&L that operating FP-P-110 should only be done as a last resort. FP-P-110 will drain FP-TK-110 preferentially even with another fire pump running at CW.
398848 | CR | 20190906 |  | 4 | quartz lamp on fixture #6 on TG 501 out | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WOT 02121388-01, quarts lamp on fixture #6 on Cicuit ELP-7AD-1did not energize upon re -energizing breaker. Quarts lamp needs replaced, however location is above hatch area on TG 501' in which personnel would be above shielding from West side wall. <I> **** Actions Taken **** Generated CR. Non-essential lighting. <N> **** Equipment Description **** TG 501' West side above crane hatch on ceiling
398849 | CR | 20190906 |  | 4 | CW-CT-2B water level is high | N | N |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was observed that CW -CT-2B level was at 12.5 inches. The logs require a CR for the cooling tower high level. <I> **** Actions Taken **** Wrote CR and informed CRS | 02-00-CW-CT-2B
398850 | CR | 20190906 |  | 3 | CSP-DO-C101 R15 removed signature from coversheet |  |  |  | N | NO | <D> **** Detailed Description **** CSP-DO-C101 R15 was released without the signature / review information on the coversheet that surveillances typically have. WIthout this information, the procedure could be completed and never reviewed by an SRO or final reviewer. Recommend addiing information back onto the coversheet. <I> **** Actions Taken **** Manually added the information to the existing procedure being used.
398851 | CR | 20190906 |  | 3 | Evaluate use of FP-P-110 during FPP-2.2.2 |  |  |  | N | YES | <D> **** Detailed Description **** FPP-2.2.2 precaution 3.5 and step 7.4.3 require the use of FP-P-110 to test the B600 Dry Sprinkler System. The requirement for using FP-P-110 should be evaluated and changed to use alternate fire pumps since running FP-P-110 for an extended period or high flow requirement results in pumping FP-TK-110 below LCS RFO 1.10.1 limits and renders the Auxiliary Fire Protection water source non-functional. If the use of FP-P-110 truly is required for this test, then it is recommended that the test be planned with a deliberate entrance into LCS RFO 1.10.1.A and its attendant compensatory measures and risk mitigation strategies. Ref CRs 398829 and 390524. <I> **** Actions Taken **** This CR is in response to CR 398829 | 02-00-FP-P-110,02-00-FP-TK-110
398852 | CR | 20190906 |  | 3 | adobe issue prevents CRO2 computer use |  |  |  | N | NO | <D> **** Detailed Description **** acrobat sign in pop up prevents CRO2 from being able to perform job function and wake clearances / print turnovers or any other adobe file usage. This unnecessarily encombers all RO licensed operators when at a computer with acrobat pro on it. Please correct issue.
398853 | CR | 20190906 | CAQ | D | Leak Det RWCU Rooms Temp High | Y | Y |  | N | YES | <D> **** Detailed Description **** LD-TE-3E reads 125F setpoint of 125F there is no indication of steam leakage into the area. <I> **** Actions Taken **** Temp Log created to monitor temps <N> **** Equipment Description **** P632 MCR | 02-00-LD-TE-3E
398854 | CR | 20190906 |  | 4 | Incorrect Oil Sample Labels |  |  |  | N | NO | <D> **** Detailed Description **** CGS oil samples received at the Environmental Services Laboratory lack the proper container labeling per ISPM-11 Hazard Communication Program and sample labeling in accordance with PPM 1.19.3C, Lubrication Analysis. Laboratory analysts were not able to initially determine the oil types received due to the incomplete information. See EMDS image of oil samples. <I> **** Actions Taken **** Verified WO 02127129 oil sampling tasks; reviewed testing locations in OilView to determine oil types; notified lubrication engineer; and initiated CR. <N> ***General Notes*** Coaching has been provided to the mechanical shop about adhereing to procedural standards. No further actions required. the cause for the procedural use and adherence error is that the work order package did not specify how to label the oil samples. it simply stated to label the samples in the order that they were obtained. There was no reference within the work instructions to the reference use procedure.
398855 | CR | 20190907 |  | 4 | Steam Tunnel Camera Limited Range of Motion | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The 501TG Steam Tunnel camera, accessed through the Genetec Security Desk software, displayed a very limited range of motion. It is suspected that the camera may have fallen off of its mounting location. This camera is utilized daily for operator rounds. Having access to this camera may provide significant dose savings by preventing possible steam tunnel entry. <I> **** Actions Taken **** Informed supervision, wrote CR <N> **** Equipment Description **** Steam tunnel camera accessed through Genetec Security Desk software
398858 | CR | 20190907 | CAQ | C | (NRC) HPCS Diesel Air Compressor Cables | Y | N |  | N | NO | <D> **** Detailed Description **** During a walkdown the NRC resident questioned the routing of the Lister diesel battery cables below the foundation of the Lister diesel itself. The concern is if that cabling will be effected should the room flood. Recommend engineering evaluate. <I> **** Actions Taken **** Notified SM and wrote CR for evaluation. <N> Cables from negative terminal of batteries is routed into a conduit that then passes into the floor under the compressor diesel foundation. This appears to be the cables of concern. Cables from positive terminal are not routed via the same conduit and instead are routed directly to the lister diesel above grade.
398859 | CR | 20190907 |  | 4 | Late Relief for On-Shift HP Technicians |  |  |  | N | NO | <D> **** Detailed Description **** Two individuals failed to show up by 0600 to relieve the on -shift HP Technicians the morning of 9/7/19. This required an emergent callout and a holdover of nightshift technicians. Two qualified individuals were called out and arrived at approximately 0730. The two nightshift technicians were relieved at that time. At no time was HP staffing beneath the minimum required. <I> **** Actions Taken **** Started an immediate callout and held two nightshift technicians over until relieved. Assessed fitness of the two individuals who were called out to ensure they were fit for duty. Contact was eventually made with the scheduled shift personnel, both of whom arrived on site by 0840. Both of the individuals were assessed for fitness and determined to be fit for duty.
398860 | CR | 20190907 | CAQ | D | FP-ENG-110 Coolant Too Hot | N | Y |  | N | YES | <D> **** Detailed Description **** The engine coolant for FP-P-110 is currently 205Â°F. This is abnormally hot. Normally the heaters keep it around 175 and the temperature is even lower when the engine is actually running. <I> **** Actions Taken **** Informed MCR <N> An IR thermometer was used to check temperatures. The pipe on the outlet of the hotstart heater was 222 F and the pipe returning on the left (facing) to the heater was approx. 160F. The engine jacket and intake areas were warmer than normal, but not significantly so. Oil pan temps were 90F, and the block was just over 100F. It appears the shutoff has failed on the heater and it is no longer cycling to maintain temps. | 02-00-FP-ENG-110
398861 | CR | 20190907 |  | 4 | HWC alarm | N | N |  | N | NO | <D> **** Detailed Description **** Received a HWC alarm HS PAL124-PRES STAT LOW (Hydrogen Tube Pressure Low) on HSSF-CAB-CHEM in 487' RW chemistry lab. <I> **** Actions Taken **** Notified the CRS and wrote a CR & WR as directed by CI -14.4. Chemistry supervision was also notified. <N> **** Equipment Description **** HSSF-CAB-CHEM HSSF-P-1A and HSSF-P-1B were found off. Alarms reset locally and pumps restarted. H2 storage tube pressure recovering.
398862 | CR | 20190907 | CAQ | C | ICP-RHR-Q901 out of tolerance during channel calibration | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of ICP-RHR-Q901 WO 02110159 RHR-DPIS-12A trip was out of tolerance for the calibration limits. Required is 167 - 174" as found was 160". Instrument was calibrated with trip as left reading 170" <I> **** Actions Taken **** Performed calibration within toerances Wrote CR Infromed CRS <N> RHR-DPIS-12A was calibrated back into tolerance; no further actions required. | 02-00-RHR-DPIS-12A
398863 | CR | 20190907 |  | 4 | CIA-V-19 fitting issues | N | N |  | Y | YES | <D> **** Detailed Description **** During performance of WO#02117862-01, the test connection on CIA-V-19 was found to be galled. The fitting was able to be tightened without leaks but needs to be fixed for future air sampling performances. Also discovered the 90 deg elbow going into the bottom of the air receiver is loose and leaking nitrogen. (see pics in EDMS). Recommend mechanics to tighten and/or replace fittings as needed. <I> **** Actions Taken **** Notified CRS and supervisor, took pictures, wrote this CR. | 02-00-CIA-AR-1,02-00-CIA-V-19
398864 | CR | 20190907 |  | 4 | Cumbersome obsrvation forms have too many non used comments. |  |  |  | N | NO | <D> **** Detailed Description **** RECURRING COMPLAINT: All of the pre made observation forms have too many non applicable, rarely or never used comments that make it extremly cumbersome to transfer observations to the program. Specifically, for my last observation I had to open up 4 different observations and read several comments just to find which form would have the most applicable comments. 2 of the 3 comments were put in boxes that were not even applicable. Several of the forms have redudant comments. Two of the observations have more than 60 comments to read through to select applicable comments. I highly recommend creating a form that allows the supervisor to categorize the comments themselves. Each form should provide blank boxes to create our own comment categories. I have polled several supervisors in Operations and they have the same complaints. <N> A Supervisor led team has been created to evaluate and create options for enhancing Observation cards for more flexibility.
398865 | CR | 20190907 |  | 4 | HWC alarm | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Received a HWC alarm on HSSF-CAB-CHEM (487' RW chemistry lab), PC SYS-STAT Trouble (PCP System trouble alarm). <I> **** Actions Taken **** Informed the on-shift CRS and wrote a CR per CI-14.4.
398866 | CR | 20190907 | CAQ | D | CW-PHITS-1 is reading erratic | N | Y |  | N | YES | <D> **** Detailed Description **** CW-PHITS-1 is reading erratically. This is an ongoing problem with the NPDES CW pH instrument. The equipment has been declared non-functional and compensatory measures are in place. <I> **** Actions Taken **** Troubleshoot the pH controller and correct the problem. <N> **** Equipment Description **** CWPH pH meter | 02-00-CW-PHITS-1
398867 | CR | 20190907 | CAQ | C | Received "SLC TANK LEVEL HIGH/LOW" alarm (H13-P603.A8.5-8). | Y | Y |  | N | YES | <D> **** Detailed Description **** Received "SLC TANK LEVEL HIGH/LOW" alarm (H13-P603.A8.5-8). Indicated SLC tank levels are GT 5000 gal on SLC-LI-601 and 5161 gal on Comp. pt. X077. SLC-LI-601 has been previously identified to be reading high off scale. See WR# 29151028. This alarm is coming in more frequently. Recommend I&C to rod Out SLC Bubbler. <I> **** Actions Taken **** Inform CRS/SM | 02-00-SLC-LI-601
398868 | CR | 20190907 |  | 4 | H2 Water Chemistry Trouble Alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received Pump B Cavitation Loss alarm followed by a Pump A Cavitation Loss alarm on Chemistry HWC monitoring panel. Pumps appeared to have turned off prior to reaching their normal high pressure setpoint for the H2 Supply tubes (~1500psig) they should be shutting off at 2500 psig. Refer to previous CR 398861 Possibly due to low level in H2 Tank at HSSF. Tank level appears to be just above LLA. <I> **** Actions Taken **** Alarms were reset locally and pumps restarted. <N> **** Equipment Description **** HSSF
398869 | CR | 20190908 |  | 4 | Oscillograph Started alarm 9/8/19 0215 | N | N |  | N | NO | <D> **** Detailed Description **** MCR received Oscillograph Started alarm on 9/8/19 at 0215. BPA Munro reports the Midway-Pacific line near Union Gap cycled off and auto reclosed due to lightning. BPA further reports there has been many lightning strikes in the last several hours, especially in western WA. TR-B voltages 120/119/118 KV; TR-S 240/236/239 KV.
398870 | CR | 20190908 |  | 4 | AS-BLR-1 level is trending down abnormally | N | N |  | N | YES | <D> **** Detailed Description **** AS-BLR-1 level is trending down unexpectedly and the drain down path has not been identified. See EDMS doc for detailed discription of the issue. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TG 441 | 02-00-AS-BLR-1
398872 | CR | 20190908 | CAQ | D | MET tower channel A 245â€™ temperature indication failed | N | Y |  | N | YES | <D> **** Detailed Description **** MET tower channel A 245â€™ temperature indication failed upscale. This has caused an erroneous large differential temperature between the 33â€™ and 245â€™ elevation for the A channel. MET-TE-10A the channel A 245â€™ temperature indication inputs into the Stability class displayed on the E1 screen on TDAS. Recommend repairing or replacing MET -TE-10A. This is visible on TDAS point F152 and eDNA point META64. <I> **** Actions Taken **** Informed CRS | 02-00-MET-TE-10A
398873 | CR | 20190908 | CAQ | D | Rx 606 Ultraviolet Fire alarm locked in | N | N |  | N | YES | <D> **** Detailed Description **** FP-UVD-19A alarmed and would not reset. Upper Display read 08. Lower Display read 2. <I> **** Actions Taken **** attempted to reset | 02-00-FP-UVD-19A
398874 | CR | 20190908 |  | 3 | Restock of 21H resin is required for Rad. Waste Control Room |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** We have used all of the staged 21H resin (EDR and FDR filter resin) . Please have several new pallets of 21H resin brought up to the RW 467', behind the RWCR. Approximately 2 ft3 of this resin is used on a daily basis. With this resin not being available, Operations will be forced to use 205H resin to support water processing. This results in more frequently changed out filters and faster accumulation of spent resin to be disposed of. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** 21H resin for the EDR and FDR filter units
398875 | CR | 20190908 |  | 4 | TEA-42-3A3B, (Electrical Breaker ), will not close. | N | N |  | N | YES | <D> **** Detailed Description **** Unable to close TEA-42-3A3B after lifting the clearance order on it. Most likely just needs Lubrication and/or adjustment. | 02-00-TEA-42-3A3B
398876 | CR | 20190909 |  | 4 | Received P840.A3.7-6 "H2 WTR CHEM TROUBLE" alarm | N | N |  | N | YES | <D> **** Detailed Description **** Received HWC alarm. OPS3 reports it is H2 SUPPLY FACILITY TROUBLE, chemistry HMI shows PC SYS STAT TROUBLE. <I> **** Actions Taken **** Dispatched OPS4 to perform actions per ARP | 02-00-HSSF-CP-P1
398877 | CR | 20190909 |  | 4 | Received P840.A3. 7-6 "H2 WTR CHEM TROUBLE" alarm | N | N |  | N | YES | <D> **** Detailed Description **** HT LAL150-LEV STAT LOW Hydrogen tank level low alarm. Delivery is scheduled for 9-11-19. | 02-00-HSSF-CP-P1
398878 | CR | 20190909 |  | 3 | HP-EQ-42784 (ARGOS)fails source check | N | N |  | N | NO | <D> **** Detailed Description **** ARGOS located the HP PAP failed weekly source check. Detector #10 showed no response to source after numerous attempts <I> **** Actions Taken **** Work request written <N> **** Equipment Description **** HP-EQ-42784 HP PAP
398879 | CR | 20190909 | CAQ | D | FDR-P-15B (T4 Sump pump) abnormal operation | N | N |  | N | YES | <D> **** Detailed Description **** FDR-P-15B (T4 Sump pump) was found to have abnormal discharge trend into the RW collection tank. It appeared as if the pump was losing suction, and only momentarily moving water, despite the running light being lit continuously. See attached EDMS doc for pic of yokagowa trend. (note that FDR-TK-6 influent had been shifted to EDR-TK-2 at time of picture) Also note that FDR-P-15A is not available due to suspected blown fuse. Ref. WR29150170 from 6/26/19. The investigation/repair of at least one of these pumps should be prioritized. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RW 467 for switch. TG 441 for pump | 02-00-FDR-P-15B
398881 | CR | 20190909 |  | 3 | FSAR Figure 1.2-28.2 typographical error |  |  |  | N | NO | <D> **** Detailed Description **** The acronym for RV should be "relief valve" not "relief value". <I> **** Actions Taken **** Recommend using the minor administrative change process per SWP-LIC-03 to correct.
398883 | CR | 20190909 | CAQ | D | HPCS-HZM-R615, SM-4 frequency, reads 60.3 Hz. | N | N |  | N | YES | <C> CR reopened to cross reference additional WO 02150288 then taken to complete. <D> **** Detailed Description **** HPCS-HZM-R615, the SM-4 frequency meter on H13-P601, reads 60.3 Hz when it should read 60.0 Hz. SM-4 is powered from SM-2, which in turn is powered from E-TR-N1. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. <N> SM-4 powered by TR-N1 which is at 60.0 Hz. HPCS-HZM-R615 needs to be calibrated, reference PPM 10.25.92. | 02-00-HPCS-HZM-R615
398884 | CR | 20190909 |  | 4 | Communication cannot be established with E-AY-TR/M3 | N | N |  | N | YES | <D> **** Detailed Description **** While trying to review the data from E-TR-M3 Kelman DGA communication with the unit could not be established. The error message received is â€œFailed to open a connection to the deviceâ€. The GE Kelman data is necessary to support ODMI AR 393438. A reset of the wireless connection power may correct the issue. | 02-00-E-AY-TR/M3
398887 | CR | 20190909 |  | 4 | 5 Pieces of M&TE Suspended intil R25 |  |  |  | N | NO | <D> **** Detailed Description **** 5 Pieces of M&TE Passed Closeout Calibrations and are now Suspended until R25. Not used since Cal'd. Calcode #C011876 Proto Torque Wrench- model 6066A. DEF #7288A written. Calcode #37677 Amp Crimper- model 59250-AB. DEF #7289A written. Calcode #0059165 Amp Crimper- model 59824-1. DEF #7290A written. Calcode #0059168 Amp Crimper- model 59824 -1. DEF #7291A written. Calcode #0059813 Fluke Temp. Probe- model 80T150U. DEF #7292A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
398888 | CR | 20190909 |  | 3 | (planning) PM's need updating |  |  |  | N | NO | <D> **** Detailed Description **** The following WO's needed FMR holds. Update the models for these WO's and update tasked out WO's with FMR holds: 02137307-01, 02137308-041, 02108589-01, 02138009-01. . WO 02136163-01 is suppose to come out in the READY status, remove the WD hold from the model and all tasked WO's . WO 02141034-01 should come out in the READY status, check the PM active box, remove the WD holds on the model and all tasked WO's
398889 | CR | 20190909 |  | 3 | Standard found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode 0064275 Wahl Model 700MC Thermometer, Heat Prober was found out of tolerance and adjusted. Not used at OOT set point. <N> CR re-assigned to CALSERV at thier request.
398890 | CR | 20190909 | CAQ | D | RHR-DPIS-12A Calibration Trend | Y | N |  | N | YES | <D> **** Detailed Description **** RHR-DPIS-12A has been found out of tolerance multiple times requiring adjustment during Channel Functional tests and Channel Calibrations (ICP-RHR-Q901). The As-found setpoint has not exceeded TS limits in previous calibrations, but has been consistently out of tolerance. RHR-DPIS-12A has been out of tolerance 9 times out of the last 19 ICP-RHR -Q901 performances since 2015. This Barton Switch should be replaced to ensure continued reliability. <I> Notified CRS No immediate actions required | 02-00-RHR-DPIS-12A
398891 | CR | 20190909 |  | 4 | MT&E Found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0060881 Biddle Megger- model BM11D found OOT. Not used in OHMS Range - only Volts Range. Rejected- Unable to adjust. No Longer supported by the OEM. DEF #7293A written. No Action Required.
398892 | CR | 20190909 |  | 4 | MT&E Found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065244 Fluke Temp Probe- model 80T-150UA found OOT & adjusted within specs. Not used during Calibration cycle. DEF #7294A written. No Plant Impact. No Action Required.
398893 | CR | 20190909 |  | 3 | (NRC) SW pump expansion joints question | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** NRC resident inspector questioned why there is no apparent constraint on the SW pump expansion joints to restrict motion in the direction of compression when there are tie rods with nuts that restrict motion in the direction of expansion. The inspector noted that at other sites he has visited that similar expansion joints on safety related pumps have installed sleeves or other restricting methods that limit the travel of the expansion joint in compression. No safety concern was communicated by the inspector. Request engineering and licensing discuss question and provide answer to the NRC resident inspector. <I> **** Actions Taken **** Informed system engineer and licensing to formulate a response.
398895 | CR | 20190909 | CAQ | C | Condition Review Group (CRG) did not meet quorum on 9/9/2019 |  |  |  | N | NO | <C> MRT Change: CR 398895 moved from NON-CAQ Severity 3 to CAQ C/OPSMGT. <D> **** Detailed Description **** Condition Review Group (CRG) did not meet quorum on 9/9/2019, this was verified through completed JFGâ€™s. CAP Supervisor contacted before CRG and approved deviation from SWP-CAP-06. <I> **** Actions Taken **** Member coached to finish JFG prior to them participating in their next CRG meeting. Assign to Operations. <N> An Extent of Condition was done on all meetings since SWP -CAP-06 implementation of the required JFG (5/13/2019), and found one other instance of this done by the same individual on 8/5/2019. Informed Operations Group.
398896 | CR | 20190909 |  | 4 | Forced Outage Meeting Rescheduled |  |  |  | N | NO | <D> **** Detailed Description **** Forced Outage Meeting was rescheduled due to lack of quorum members. <I> **** Actions Taken **** Meeting rescheduled to following business day.
398897 | CR | 20190909 |  |  | 83E lamp on TR-N2 |  |  |  | N | YES | <D> **** Detailed Description **** During performance of step 4.5.2 of WO# 02118154-01, the 83E Emergency Power alarm lamp did not illuminate. <I> **** Actions Taken **** Informed supervision, initiated CR | 02-00-E-TR-N2
398898 | CR | 20190909 |  | 4 | 83E Emergency Power alarm lamp on TR-N1 | N | N |  | N | YES | <D> **** Detailed Description **** During performance of step 4.5.2 of WO# 02118154-01, the 83E Emergency Power alarm lamp did not illuminate. <I> **** Actions Taken **** Informed Supervision, Initiated CR | 02-00-E-TR-N1
398899 | CR | 20190909 |  | 3 | Better alternative to EOP key installed in RWM bypass keyloc |  |  |  | N | NO | <D> **** Detailed Description **** PPM 5.5.11 was changed on 9/9/19 to permanently install the EOP key into the RWM Bypass Key lock. A better alternative would be to remove step 2.3 from PPM 5.5.11 (RWM Bypass Key â€“ Installed in RWM keylock), remove the EOP RWM Bypass Key from the plant, and permanently install PPM 1.3.23 key 27 into the RWM Bypass Keylock. This would be consistent with the SDV High Level Trip Bypass key 29 from PPM 1.3.23 being permanently installed in the switch. This switch is also operated in PPM 5.5.11. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR.
398904 | CR | 20190909 |  | 3 | Spare refurbed TMU Pump intial flow test did not meet spec | N | N |  | N | NO | <D> **** Detailed Description **** Spare TMU initial pump testing did not meet the 204' (-0% +8%) Total Dynamic Head (TDH) specification after upgrade and refurbishment. <I> **** Actions Taken **** 1. Vendor developed and implemented a recovery plan 2. The flow re-test produced a TDH of 212' meeting spec. 3. WWM notified pump delivery still supports T schedule for "parts staged". 4. Recommend assignment to Minor Mods to update EC 17117R1 with the updated TMU-P-1B vendor drawings. 5. Recommend assignment to Component Engineering to update CVI 39-00,1 & 39-00,2 drawings along with CVI 39 -00,4 OMM.
398905 | CR | 20190909 |  | 3 | OCC-03 and EC 17964 for MD Valves |  |  |  | N | NO | <D> **** Detailed Description **** OCC-03 decision for AR 398564 states Fail open the MD valves that come off the turbine casing and cross under piping while closing the MD valves that come off of high energy locations prior to entering the HP Turbine Casing. This was accomplished by TMOD EC 17964 which forced open MD-V-87 and causes all other associated valves to remain closed and prevent the automatic function. EC 17964 forces open MD-V-87 but also has a statement that says in the EC if operations determines that MD-V-87 is required to be closed the EC allows closure of MD-V-87. This has some ambiguity and requires interpretation (engineering intended this as a contingency for urgent required actions). In discussion with operations MD-V-87 has recently been closed citing the statement in the EC that allows the closure of the MD-V-87 and current plant conditions. The OCC-03 suggests that this condition would be resolved in balance shot down power that had been planned for 19 September. The condition should be reevaluated, per the implementation state of the temporary modification and the OCC-03 with current plant conditions and the deferring of the planned resolution. Review of these documents was prompted by an NRC question. OCC-03 decision for AR 398564 should be revised for current plant conditions and resolution plan, and it should be determined if TMOD EC 17964 should be restored (if no longer required) or if revision is required (to remove ambiguity). <I> **** Actions Taken **** Notified Operations, discussed with system engineering and design engineering managers. . Operations has reopened MD-V-87. Alignment with the approved OCC-03 is the current status. Shift manager will communicate to all SM/CRSs that closing V-87 should be done only if emergent condition dictate it. . Outside of this CR, the ACMP is being upgraded to an ODMI and the OCC-03 will be updated appropriately since September downpower will not occur (as written in the current OCC-03). No further action should be required for this CR from engineering. | 02-00-MD-V-87
398907 | CR | 20190909 |  | 3 | PO.15 for R25 is Yellow |  |  |  | N | NO | <D> **** Detailed Description **** Outage milestone PO15 for planning complete is Yellow due to not making expected progress on R25 outage work package planning. The sub milestone for 25% complete was missed and the 50% milestone due the middle of October is in jeopardy at this point. Action needs to be taken to get back on track for successful milestone completion. <I> **** Actions Taken **** Discussed with outage management. A recovery plan is being generated and routed for signatures. This AR is in intended to document the performance, and an action should be generated to upload the signed recovery plan.
398908 | CR | 20190909 |  | 4 | TB 441 LIGHTING ISSUES | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of the TB 441 monthly survey it was noted there are eight lighting deficiencies. The poor lighting by service air and the condensate pumps are a safety concern. <I> **** Actions Taken **** Informed supervision, wrote this CR. See EDMS for map showing locations of lighting issues. <N> **** Equipment Description **** I have a detailed map of the locations. All locations are in non-contaminated area and low dose areas.
398909 | CR | 20190909 |  | 4 | 500kv neutral ground oscillograph start | N | N |  | N | NO | <D> **** Detailed Description **** Module J7 500kv Neutral Ground Overcurrent oscillograph start. The alarm reset. Plant controllers and equipment indicate normal. No known cause. <I> **** Actions Taken **** Walkdown controllers and equipment to verify proper operation. Called Dittmer to verify grid integrity.
398910 | CR | 20190910 | CAQ | D | CRD-HCU-5819 P6 connector leak | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-5819 has a very slow leak (slow growth of a singular bubble) from it's P6 connector. The P6 connector was torqued to the max of 200 in/lbs. The leak remained. The HCU was isolated, the P6 connector was rinsed off and wiped down, neolube was applied to the treads. But the leak remained after being re-torqued to 200 in/lbs. Please replace P6 connector. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RX 522 East HCU bank | 02-00-CRD-HCU-5819
398911 | CR | 20190910 | CAQ | D | external ground wire on RCIC-MO-19 has broken strand | Y | N |  | N | NO | <D> **** Detailed Description **** while performing the external inspection of RCIC-MO-19 (WO# 02115502-01) electricians noted that the external ground wire that runs/lands on the limit switch enclosure mounting hardware has a missing strand that is about 12" short of reaching the mechanical ground lug. <I> **** Actions Taken **** notified supervision and write CR. picture will be uploaded to EDMS <N> **** Equipment Description **** RCIC-MO-19
398915 | CR | 20190910 |  | 4 | Green badge missing from contractors vehicle |  |  |  | N | NO | <D> **** Detailed Description **** Contractor with org #72600 reported his vehicle was vandalized and his green badge is missing/stolen. Contractors badge was placed on admin hold and a badge report was requested. No unauthorized activity was confirmed from when the contarctor was last on site. <I> **** Actions Taken **** Issued a replacement badge after notifing Security Sgt and Security Services Manager of the badge report results.
398916 | CR | 20190910 |  | 3 | PMIDâ€™s 6839 and 6840 01/02 PMRQ need to be retired. | N | Y |  | N | NO | <D> **** Detailed Description **** Both PMID 6839 and 6840 PMRQ 01 & 02 need to be retired and a new AR-SMS routed to create the new VESDA PMID. â€˜Assign to Fire Protection AR-TEFPâ€™. <I> **** Actions Taken **** Generated CR to document that PMID does not appear to have been generated for the VESDA project. Contacted Fire protection Engineering and the Fire Marshall.
398918 | CR | 20190910 | CAQ | C | Communicator paging failure |  |  |  | N | YES | <C> MRT Change: CR 398918 moved from NON-CAQ Severity 3 to CAQ C/ITMGMT. <D> **** Detailed Description **** The primary and backup Emergency Notification systems, Communicator, failed to send test pages during routine testing at 6pm on 9/9/19. <I> **** Actions Taken **** IS Analyst worked with Security to verify the failures. Motorola was contacted and a support ticket opened. Subsequent testing done at 6am on 9/10/19 showed the system was functioning, but errors in reporting exist. <N> **** Equipment Description **** Emergency Notification Communicator, cloud based | FW-00-SOFT-COTS-COMM NXT
398923 | CR | 20190910 | CAQ | C | RCIC-V-739 Yoke retaining nut broken | Y | N |  | N | YES | <D> **** Detailed Description **** While loosening yoke retaining nut to ultimately remove yoke to facilitate a repack of the valve, the retaining nut broke. Reference CVI DWG 250-00,739,1 item 25. <I> **** Actions Taken **** Ordered new nut (in stock) for replacement. <N> **** Equipment Description **** R -428-R015- -H3/6.5 - Broken nut was replaced. No further actions required. | 02-00-RCIC-V-739
398924 | CR | 20190910 | CAQ | C | MULTIPLE RECORDS SUBMITTED WITH INCORRECT DIC |  |  |  | N | NO | <D> **** Detailed Description **** MULTIPLE RECORDS WERE SUBMITTED TO RECORDS CONTROL WITHOUT PROPER DIC AND/OR PROPER DOCUMENTATION OF HOW/ WHAT THE DOCUMENTS WERE. <I> **** Actions Taken **** NOTIFIED LEAD/ SUPERVISOR. CR GENERATED FOR TRACKING PURPOSES AND COACHING PROVIDED TO OPERATIONS. RECORDS BEING SENT BACK FOR CORRECTIONS AND RE-SUBMITTAL.
398925 | CR | 20190910 |  | 4 | HWC Alarm | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Received a HS PAL124-PRES STAT LOW alarm on HSSF-CAB-CHEM (HWC monitor). <I> **** Actions Taken **** Per CI-14.4 informed the CRS and wrote a CR & WR. <N> **** Equipment Description **** HSSF-CAB-CHEM
398927 | CR | 20190910 | CAQ | C | FP-ENG-1 turbo charger damage | N | Y |  | N | YES | <D> **** Detailed Description **** During the performance of FP-ENG-1 maintenance the turbo charger has what appears to be contact between the compressor and the outer housing. Fire protection engineer and Cummins recommended replacement. Currently the site does not have a new turbo charger in stock (CAT ID 16573). Recommend CR to be routed to Fire Protection Engineer for resolution. See EDMS for pictures. <I> **** Actions Taken **** Initiated CR, notified MCR, and contacted fire protection engineer. Additionally contacted SCS to start the process to procure a new turbo charger. | 02-00-FP-ENG-1
398928 | CR | 20190910 |  | 3 | EV Charging Station repair not resolved timely |  |  |  | N | NO | <D> **** Detailed Description **** This CR is for trending purposes. The Southridge EV Charging Station, owned by Greenlots as part of the collaborative EVITA project (EN is administrator of this project) was reported with a problem with the L2 equipment on 8/10/19. The L2 station has been down since this time. The L3 station was reported as inoperable on 9/8/19. EN staff has been requesting resolution since the week of 8/7/19 when the initial report was received that the station was down. The part was sent by the manufacturer and received 8/27. Communication with Greenlots' installer today resulted in the notification that the L3 station is also down and has not been fixed at this time. <I> **** Actions Taken **** EN staff notified Greenlots' senior management that the charging station has not been repaired in a timely manner and that the repairs must be made immediately. The VP has advised an action item will be determined ASAP. <N> No actions needed. Station was repaired, thoroughly tested and placed back in service.
398929 | CR | 20190910 |  | 4 | HSSF Supply and Pump Operation |  |  |  | N | YES | <C> Reopened at MRT's request to xref CR 399044. <D> **** Detailed Description **** HSSF storage tank level has been reduced to abnormally low levels due to a vendor delivery of H2 that has not been provided in a timeline that supports normal operation of the HSSF-P-1A and HSSF-P-1B. Due to the lowering storage tank level the pumps appear to have been shutting down due to cavitation which has resulted in the ASME storage tubes not being pressurized to their normal recharged state. This CR is to drive an evaluation of the circumstances of the vendorâ€™s delivery timeline to support normal operations of the system and to investigate the potential cavitation and associated damage to the pumps that may have occurred. Currently the vendor delivery is anticipated on 9/11/19. | 02-00-HSSF-P-1A,02-00-HSSF-P-1B,02-00-HSSF-TK-1
398930 | CR | 20190910 | CAQ | C | 15.1.15 procedure not found in Work Control binder. |  |  |  | N | NO | <D> **** Detailed Description **** On 9/5/19 while distributing procedure 15.1.15 revision 022/002, it was discovered the previous revision and tab had been inadvertently removed from the work control volume 15 binder. This left the work control volume 15 which is a level 1 filing location without the procedure in the event it was required. <I> **** Actions Taken **** Placed a temporary seperation sheet between 15.1.14 and 15.1.15 and inserted the new revision of the procedure. Noted it on the distribution cover sheet and notified the Lead in Document Control. <N> No further actions are required. The procedure was placed in the book when found to be missing. It is possible it was removed by someone and a copy not replaced in the binder. All other locations were found to contain the procedure under the correct tab. Because the procedure was missing it could have been retrieved from Asset Suite if the need arose.
398931 | CR | 20190910 | CAQ | D | FP-P-1 Heat Exchanger fouled | N | Y |  | N | YES | <D> **** Detailed Description **** During the performance of FP-P-1 maintenance disassembly craft identified the heat exchanger and associated piping had some fouling. See EDMS for pictures. <I> **** Actions Taken **** Initiated CR, notified MCR, and contacted fire protection engineer. Cleaned and flushed heat exchanger and associated piping to satisfactory condition for reassembly. | 02-00-FP-P-1
398932 | CR | 20190910 | CAQ | C | FP-ENG-1 internal damage found. | N | Y |  | N | YES | <D> **** Detailed Description **** During disassembly of FP-ENG-1 WO# 02118127-01 the number 5 cylinder, piston and liner were found to be damaged. There is a wear pattern on the top of the piston that shows signs of inefficient burn of the cylinder. There was no cross hatching found on any of the other cylinder walls which is indicative of wear on the liners, which reduces the cylinder pressure and causes this condition we see on cylinder 5. Recommend assignment to fire protection engineer. See EDMS for pictures <I> **** Actions Taken **** Recommend rebuild of the engine per Engineering and Vendor (Cummins Northwest) Notified the work week manager the main control room and Supervision. Notified Supply Chain Services for Parts Availability | 02-00-FP-ENG-1
398935 | CR | 20190910 | CAQ | D | RCIC-MO-1 Strain Gage Epoxy had to be ordered |  |  |  | N | NO | <D> **** Detailed Description **** RCIC-MO-1 Strain Gage Epoxy had to be ordered during day of implementation. There was no Material Request in the original work order. Not caught on walkdown. Recomend having this added to the model for Diagnostic Testing on RCIC-MO-1. <I> **** Actions Taken **** Electrical Supervison informed. Ordered epoxy and worked with OCC to have it brought to Building 26. Initialed CR to document lesson learned. <N> **** Equipment Description **** Epoxy ordered to support implementation of W.O. 02116844-08 Inspect/Install Strain Gage on RCIC-MO-1.
398936 | CR | 20190910 |  | 3 | Dept of Health Drinking Water Violation Recieved |  |  |  | N | YES | <D> **** Detailed Description **** The Department of Health has issued CGS a drinking water violation due to missed continuous turbidity measurements on the finished drinking water from 7/2/19 to 7/14/19. The turbidity readings were missed because of a malfunction with the data recorder following power loss. During the period, the potable water disinfection system was operating normally. Intermittent turbidity readings were recorded by operator rounds during the period and do not indicate that high turbidity water was released into the distribution system. The DOH is requiring that drinking water customers be notified of the violation within 30 days. <I> **** Actions Taken **** E&RP was notified of the violation. E&RP is coordinating the posting of the notice. The equipment malfunction was documented and resolved under AR 397552. Additional actions to prevent recurrence are pending in that AR. Licensing is reviewing is reportability to the NRC is required. <N> Verified with licensing this is not reportable to the NRC per NUREG-1022. Violation occured as a result of a latent organizational weakness (>18 months). A department clock reset is not required. | 02-00-PWC-XR-1
398937 | CR | 20190910 |  | 3 | Elevation of valves are incorrect |  |  |  | N | NO | <D> **** Detailed Description **** During implementation of the ERO drill it was identified that the elevation of CAS-V-100/40 ,41, 42 listed in the D030 screen are incorrect. They are listed at D425. It may be 452. They are also incorrectly listed in MSIV closure (all steps, any valve).doc on ERO- technical support/MSIV -MSRV. created confusion during the drill which delayed saving the public, other than that no immediate issues. <I> **** Actions Taken **** Recommend validating elevation and correcting both issues. CR generated for documentation <N> Valve elevations have been corrected in the D030 and 31 panels in Asset Suite based on valadating against the piping isometric drawings.
398944 | CR | 20190910 |  | 3 | Lesson Learned RCIC-T-3 Spare Parts Replacement |  |  |  | N | NO | <D> **** Detailed Description **** A spare bonnet for this trap should be available for rotational replacement when performing maintenance on the trap. During the RCIC September RCIC Maintenance Outage craft encountered thread galling with the Lock Nut (Item 7 on Dwg. 042104418, CVI 215-04). This condition was noted in past maintenance on this valve dating back to 2005. Ideally it would be more effective to have a pre-assembled bonnet and replacement kit that would allow for shorter removal and replacement time by the craft and shortening the outage time periods. <I> **** Actions Taken **** Initiated this AR
398946 | CR | 20190910 | CAQ | C | SNM Source Check out/in peer checks not performed |  |  |  | N | NO | <D> **** Detailed Description **** During the annual Special Nuclear Material Inventory, it was identified that peer verification was not performed when Special Nuclear Material (SNM) radiological instrument response check sources were checked out from and checked in to the RW 487â€™ storage locker. The steps to perform a peer check for SNM checkout and check in were marked as N/A without justification five times during R24. This is contrary to PPM 11.2.14.4 â€œProcurement, Receipt, Control and Leak Testing of Radioactive Sealed Sources and Devicesâ€ and Form 361 which implement the control of SNM in accordance with the additional and specific provisions in 10 CFR 74.19(b) and 10 CFR 72.72(c). <I> **** Actions Taken **** All SNM was verified to be present and accounted for in the storage locker.
398947 | CR | 20190910 |  | 3 | RCC pH high out of spec | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** RCC pH has been trending up. It is in closed cooling water action level 2 which requires it be back in spec within 30 days. Additional samples will be taken for different analysis but the filters were just recently changed out. The filters could have introduced a contaminate. Further investigation is required. <I> **** Actions Taken **** Notified MCR, Chemistry Supervision, and chemistry system specialist.
398948 | CR | 20190910 |  | 3 | 02092420 removed from schedule at T-0 |  |  |  | N | NO | <D> **** Detailed Description **** 02092420 RRC-E/S-S01B, REPLACE ASD 24VDC PWR SUPPLY/CAPACITORS removed at T-0 due to late identification of elevated risk. When initially reviewed, it was believed that the work was medium risk witha back up power supply available. What was missed was that a coincidental loss of the back up would result in a Recirc pump trip. This meets PPM 1.3.76 criteria for High risk as a Single Point Vulnerability. Note that 1.3.76 has a list of examples for SPV that does not include ASD/RRC however the consequences meet the definition. <I> **** Actions Taken **** Task 01 reset to Approved with HRP and SRO holds applied. Reevaluation of plant impact determined this to be High Risk SPV. The work order was removed from the current schedule and sent back to UC for rescheduling.
398949 | CR | 20190910 | CAQ | D | FDR-RIS-606 Discriminator Voltage Out Of Tolerance | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of ppm 16.7.1 the as found discriminator voltage was out of tolerance at 6.39VDC with a desired voltage of 6.8VDC. <I> **** Actions Taken **** Adjusted R7 per step 7.6.5 to within tolerance and initiated a CR for trending.
398950 | CR | 20190910 |  | 3 | DES-2-9 step 4.6.3 & step 4.6.3 b requires update |  |  |  | N | NO | <D> **** Detailed Description **** DES-2-9 (Technical Evaluations) step 4.6.3 needs to be clarified and sub-step 4.6.3 b needs to be corrected. 1) DES-2-9 step 4.6.3 exists for the situation where it is determined as part of the EVAL assignment with Design Engineering Mangager or designee concurrence that a proposed permanent design/configuration change is a Commercial Change AND the intent is for an individual outside of Design Engineering to prepare the Commercial Change Package. The current wording for DES-2-9 step 4.6.3 does not make this clear. 2) DES-2-9 sub-step 4.6.3 b directs generation of a CDP, DCP, DECP, or CCP assignment. The only acceptable assignment type is a CCP for a Commercial Change. . See the mark-up for DES-2-9 R38 MnrR1 step 4.6.3 attached to the EDMS of this AR CR 398950. This is an administrative issue only. The Responsible Organization for DES-2-9 is System Engineering. Suggest resolution of this AR CR by the Procedure Sponsor.
398951 | CR | 20190910 | CAQ | D | ERO News Release app unable to send email notifications | N | Y |  | N | NO | <D> **** Detailed Description **** This morning it was discovered that the ERO News Release app lost the functionality to send New Release email notifications. <I> **** Actions Taken **** IS Analysts immediately contacted EP for detailed information, and began troubleshooting the issue. By early afternoon, the issue was resolved and validated by independent tests conducted by both IS and by EP. <N> Upon recognition of the issue with this primary news release distribution system during today's ERO drill, the JIC staff implemented the back-up distribution process of faxing news releases. This action by the JIC ERO team maintained continuity of the news release distribution function.
398952 | CR | 20190910 |  | 4 | D-RRA-CC-6--001 clearance did not have adequate lift instru |  |  |  | N | NO | <D> **** Detailed Description **** D-RRA-CC-6-001 lift instructions did not idnetify the impact of lifting clearance with RCIC-V-45 work going on. There could have been an unintended start of RRA-FN-6 <I> **** Actions Taken **** Notes were added to clearance to enusre RCIC-V-45 work was completed prior to lifting.
398953 | CR | 20190910 |  | 3 | Thermal Performance WOT schedule grade coding |  |  |  | N | NO | <D> **** Detailed Description **** For every thermal performance test worked for either the RHR or DCW HXs, the 01 task to complete the Volume 8 procedure is usually schedule grade B and expected to be taken to fieldwork complete on the end of the scheduled workday. Every time we perform this, we run into the issue that the 01 task cannot be fully completed as it is tied to completion of the entire volume 8 procedure that also includes the thermal performance analysis. This analysis generally takes at least a week to perform the calculations and receive an independent verification that the calculations are correct. While there is a separate task for engineering to analyze the data, it still does not alleviate having to work around the schedule grade B WOT for the performance of the surveillance (the 01 task). In the past, the engineer performing the surveillance has had to reach out to Ops to let them know that the 01 task is being taken to field work complete (which it is) to leave the task at H/OPS status until after the analysis is completed and verified and can then be incorporated in the work order package. While most of the time this works, there have been times where the WOT is kicked back to working status when the ops reviewer sees there is nothing in the WO package to review. In striving for excellence, this is not how this surveillance should continue to be performed. Recommend either changing the current engineering tasks to analyze data into â€œcollect thermal performance dataâ€ and make this the Grade B task while then changing the schedule code for the 01 task so that it would allow adequate time for the Volume 8 procedures to be complete (including analyses). Another option could be changing the duration of the 01 tasks to 1 or 2 weeks which would also allow for the analysis to be completed. <I> **** Actions Taken **** Discussed with supervisor
398954 | CR | 20190910 | CAQ | D | FP-ENG-1 Cylinder liner inspection deficiencies | N | Y |  | N | YES | <D> **** Detailed Description **** During disassembly of FP-ENG-1 WO# 02118127-01 it was discovered that the liner protrusion was out of specification on all cylinders. There is a discrepancy of .001 between our OMM and the Cummins current OMM that will need to be addressed as well as 15.3.9 which gives no lower specification. There was also a scoring mark on the south side of the #5 liner that has caused some degradation to the piston and rings as indicated by the carbon build up on the top of the piston. Pictures will be uploaded to the EDMS. <I> **** Actions Taken **** Recommend rebuild of the engine per Engineering and Vendor (Cummins Northwest) Notified the work week manager the main control room and Supervision. Notified Supply Chain Services for Parts Availability | 02-00-FP-ENG-1
398956 | CR | 20190910 |  | 4 | BS-DV-2A2 has failed open. | N | N |  | N | YES | <D> **** Detailed Description **** Received Steam dump valves not full closed alarm 4.840.A2 9-6. Control room operator noticed that BS-DV-2A2 indicates full open, and no other valves have repositioned. Reactor power, pressure, level are normal and stable for 100% power. Reactor feed water inlet temperature is 420.6 F and is normal for 100% power. | 02-00-BS-DV-2A2
398957 | CR | 20190910 |  | 4 | Nalco leak between CF-FG-42 and CF-PCV-42 | N | N |  | N | YES | <D> **** Detailed Description **** Nalco leak between CF-FG-42 and CF-PCV-42. See picture. <I> **** Actions Taken **** Notified CR, Secured Pump, Wrote CR. | 02-00-CF-P-42A
398958 | CR | 20190911 | CAQ | D | MS-RIS-610C screen is starting to fail | N | Y |  | N | YES | <D> **** Detailed Description **** MS-RIS-610C screen is starting to fail. Screen is still usable for taking MSL RAD levels. Please see attached video in EDMS. Trouble shoot and correct prior to total failure. <I> **** Actions Taken **** Wrote this AR. | 02-00-MS-RIS-610C
398961 | CR | 20190911 |  | 4 | Spill kit in CWPH opened. |  |  |  | N | YES | <D> **** Detailed Description **** Opened spill hit in CWPH and used 1 absorbent pad to contain Nalco leak near CF-P-42A <I> **** Actions Taken **** Wrote CR, informed SSS. <N> **** Equipment Description **** CWPH Walked down CWPH spill kit. There are still approximately 32 absorbent pads in the kit. The inventory calls for 24.
398962 | CR | 20190911 |  | 3 | PPM 3.4.1 procedure correction Attachment 9.5 |  |  |  | N | NO | <D> **** Detailed Description **** PPM 3.4.1 procedure correction Attachment 9.5 RWCU outboard isolation tables has MS-LS-300A deenergizing RPS -RLY-K39C. This should be RPS-RLY-K39A. MS-LIS-300B says it deenergizes RPS-RLY-K39D, This should be RPS-RLY-K39B. Reference DWG 02C72-05,3,13.
398969 | CR | 20190911 | CAQ | C | DEH fluid â€“fluid and turbine OEM recommended limits exceeded | Y | Y |  | N | YES | <D> **** Detailed Description **** Lab results for a DEH fluid sample taken on 03September 2019 returned three values that exceeded the DEH fluid OEM recommended limits, two of which also exceed the turbine OEM recommended limits. Each of these limits are related to high particulate count for the given size range. Particle count for a 100ml sample should be: 5-10 Micron - LT 9700,10-25 Micron â€“ LT 2680, and 25-50 Micron â€“ LT 380 The subject sample returned counts for these particle sizes of: 5-10 Micron - 26544,10-25 Micron â€“ 9164, and 25-50 Micron - 516 EPRI DEH Fluid Maintenance Guide Section 4.4.3.8 and Table 4-24 provide turbine OEM particle count recommendations. For a Siemens/Westinghouse unit such as CGS the limits are [See document in EDMS.]: 5-10 micron particle limit is 24,000 10-25 micron particle limit is 5,360 25-50 micron particle limit is 780. All other measured parameters are within normal band. Trend information: This is the second test that revealed both fluid and turbine OEM limits have been exceeded. Last cycle saw multiple occurrences. The cause was determined to be failed insulation in vicinity of DEH lines, as well as steam leaks blowing near DEH lines, such that the DEH lines were exposed to excessive heat. The condition has reemerged. The leak on the SS line near MS -V-163B may be contributing to this condition, but there may be others. A walkdown needs to be performed by the FLC to investigate where heat is reaching the DEH lines. Also, write CRs on filters with high dP and replace <I> **** Actions Taken **** Reviewed EPRI guidance informed supervisor <N> **** Equipment Description **** TG471E | 02-00-DEH-TK-2
398970 | CR | 20190911 | CAQ | D | Scheduling conflicts resulted in craft unavailable for drill |  |  |  | N | NO | <C> MRT Change: CR 398970 moved from NON-CAQ Severity 4 to CAQ D/T. . Reopened for the addtion of the following notes from the EP manager: "Craft personnel was unable to participate during the 09/10/19 ERO Drill due to the scheduled RICIC Safety System window. This issue was identified during the pre -planning for the ERO drill. The drill controllers where briefed prior to the drill that craft personnel would not be participating in certain positions. This matter was also discussed and captured during the ERO centers final critiques. A scrub of the ERO drill schedule and Work Control schedule has been conducted to ensure that this does not transpire going forward. For further information refer to ERO Drill Packet dated 09/10/19." <D> **** Detailed Description **** For the ERO drill conducted on 9/10/19, craft personnel did not participate in the drill because the resources were needed to support the RCIC system maintenance window. In the EOF, this resulted in the need for a controller to simulate the duties of HP Technicians that would have reported to the EOF.
398971 | CR | 20190911 |  | 3 | CF-V-801 mislabeled on CVI 317-00,6218 |  |  |  | N | YES | <D> **** Detailed Description **** This is a documentation issue only. On CVI 317-00,6218 the CF-TK-41 isolation valve is labeled "CF-V-804"; however, the BOM on the isometric, M507-3, and the master equipment list all indicate that this valve is "CF-V-801". Please correct document discrepancy. <N> *Correction: Drawing number is 317-00,6218,1 | 02-00-CF-V-801
398972 | CR | 20190911 |  | 3 | PMT of RCIC-V-45 delayed |  |  |  | N | NO | <D> **** Detailed Description **** Ir was discovered that when it came to PMT of RCIC-V-45 per PPM 10.25.4 a interlock prevented operation. RCIC-V-68 is closed during SOP-RCIC-S/D preventing remote operation of RCIC-V-45 <I> **** Actions Taken **** Added a Operation Support Task to WO 02111378 to operate RCIC-V-68 to allow cycling of RCIC-V-68. Committed to add task to model WO.
398973 | CR | 20190911 | CAQ | C | (QA) WOTs not Processed in Required Timeline |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Timeline requirements have not been met for processing and sending completed Work Order Tasks (WOTs) to Records as defined in Section 3.3 of MI-3.6.4, Work Package Closure. Six examples have been identified where WOTs have not been sent to Records, but are more than 90 days past Field Work Complete (FWC). Failure to process WOTs in a timely manner could result in lost Quality Records. . WOT Packages: 02112522-06, Work Completed 5/17/2019 02117191-05, Work Completed 5/27/2019 02116081-17, Work Completed 6/2/2019 02120340-30, Work Completed 6/2/2019 02129668-13, Work Completed 6/3/2019 02101714-12, Work Completed 6/4/2019 . Requirements: MI-3.6.4, Section 3.3.1b â€“ â€œReview FWC WOTs that do not require additional reviews within 14 days from status FWC.â€ MI-3.6.4, Section 3.3.2, Second Paragraph â€“ â€œManagers will ensure that CRs are generated for all work packages that have not been sent to records for processing within 60 days from status FINISH for job types that are required to be sent to permanent file.â€ . <I> **** Actions Taken **** Notified Maintenance Service Manager and Quality Services Supervisor.
398976 | CR | 20190911 |  | 4 | SCH-CR-51, not functioning to support summer operations | N | N |  | N | YES | <D> **** Detailed Description **** During the pm (WO-02119274) to check operation of SCH-CR-51 it is noted that the chiller is not capable of working to provide the needed cooling to the Yakama BLGD during the summer. <I> **** Actions Taken **** Compressor 1/Circuit 1 - does not operate at all. There are 2 compressors on the unit and #1 will not work. In order for compressor 2 to provide cooling to the offices, all the cooling was shut off to the GSB shops. These compressors were installed this year to provide the needed cooling for summer and are already failing. this unit needs complete replacement before warm weather operations is required in 2020. See statement from tech in EDMS file. | 02-00-SCH-CR-51
398977 | CR | 20190911 |  | 4 | COND-LCV-11 tubing disconnected on top of positioner | N | N |  | N | YES | <D> **** Detailed Description **** During a walkdown it was observed that COND-LCV-11 has a tubing disconnected on top of positioner. I am not certain where the disconnected end of the tubing should be attached, possibly to upper volume booster. The tubing is currently open to atmosphere and not adequately supported. See EDMS for pictures. <I> **** Actions Taken **** Notified Supervisor and Technical Services valve group | 02-00-COND-LCV-11
398979 | CR | 20190911 |  | 3 | DSA-RV-13 and 14- Unable to meet blowdown specification | N | N |  | N | NO | <D> **** Detailed Description **** While testing subject valves for upcoming installation it was determined that the reseat pressure of 0-25 PSIG below set point could not be achieved with the new valves and still maintain acceptable seat leakage. Adjusting he blowdown ring to get within 0-25 PSIG does not give the valve action the crisp pop it needs to reseat correctly and causes seat leakage. <I> **** Actions Taken **** Contacted Relief Valve Program Manager and System Engineer for resolution .
398980 | CR | 20190911 |  | 4 | Raised lip in sidewalk E. side of the Deschutes Bldg. |  |  |  | N | NO | <D> There is a trip hazard present where the asphalt and concrete meet (walkway) in front of the Deschutes Bldg. <I> Documented with photos, added to then tracking log for industrial safety issues, create a WR <N> SIdewalk East side of the Deschutes Bldg. (see photos in ED MS for additional information) CR at INPROG. Approved CR, moved to SRO for OPS Review.
398981 | CR | 20190911 | CAQ | D | As found wiring for FP Zone 7 not per drawing | N | N |  | N | YES | <D> **** Detailed Description **** During detector changes for Fire Protection Zone 8, per WO# 02126627-01, Craft noted that the 4 wires connected to detector FP-ID-7/5 were not labeled per the drawing. Three of the wires have no labeling at all and the fourth is incorrectly labeled. The circuit is currently out of service for rework of the detector and this configuration would not have affected operation of the detector. <I> **** Actions Taken **** Notified Supervision and wrote CR. Need to perform further investigation to determine which pair of wires is coming into the detector and which pair of wires is leaving, to ensure proper re-labeling, prior to installation of the new detector and base. <N> **** Equipment Description **** TG 471' WO and zone referenced in the CR description are incorrect - should zone 7 and WO# 02126626
398982 | CR | 20190911 | CAQ | C | M&TE Tools Not Properly Labeled as RAM |  |  |  | N | NO | <D> **** Detailed Description **** Two model 2000-2 Torque Wrenches sent to the PSF with M&TE were improperly labeled as per 11.2.14.9, sec. 4.4, Control and Labeling of Radioactive Material. The two pelican boxes that held the wrenches were properly labeled as RAM. <I> **** Actions Taken **** HP Technician properly labeled the wrenches and notified RP Supervision. Supervision dispatched an HP Technician to check like wrenches in the tool crib for proper labeling. <N> This AR-CR is being addressed under AR-CR 398995. Per SWP -CAP-01, an assignment under resolving AR-CR 398995 has been created to address the issue documented in this AR-CR. Appropriate cross references have been added
398983 | CR | 20190911 |  | 4 | CW-CT-1C level is high and overflowing | N | N |  | N | YES | <D> **** Detailed Description **** CW-CT-1C water level is high (15") and is flowing over the sides around the top. Recommend sweeping tower. <I> **** Actions Taken **** Informed MCR, generated AR/WR. | 02-00-CW-CT-1C
398984 | CR | 20190911 |  | 4 | PSR-O2H2A-SR48/1 reading high for O2 | N | N |  | N | YES | <D> **** Detailed Description **** PSR-O2H2A-SR48/1 is reading high for dissolved oxygen. This is the reactor coolant dissolved oxygen online monitor. Nornal readings for this instrument are ~0.1 to 0.5 ppb and the current reading is ~10 ppb. This is an indication of degradation of the oxygen probe. Recommend performing calibration of the oxygen channel for this instrument. Grab samples are being taken daily as a compensatory measure. This will impact the Chemistry dose budget until the online instrument is restored. | 02-00-PSR-O2H2A-SR48/1
398986 | CR | 20190911 |  | 3 | Missing AD on Major revision of ABN-CAS |  |  |  | N | NO | <D> **** Detailed Description **** While processing procedure it was noted that the AD was missing. Stopped and wrote CR <I> **** Actions Taken **** Informed supervision, sent procedure back to sponsor. Recommend this CR goes to operations.
398988 | CR | 20190911 |  | 3 | Legal Action Reported Late |  |  |  | N | NO | <D> **** Detailed Description **** An employee (Org code 52233) reported a legal action on the second day back to work opposed to the procedural requirement for reporting the legal action on the first scheduled day back to work following the legal action and pursuant to SWP-SEC-07, section 3.1.1. <I> **** Actions Taken **** Notified Security Services Manager, placed individualâ€™s badge on hold pursuant to the required actions, and provided instructions and coaching to the individual on Legal Action Reporting requirements.
398989 | CR | 20190911 | CAQ | C | QAR RECORDS SUBMITTED W/O REVIEWER SIGNATURE |  |  |  | N | NO | <D> **** Detailed Description **** SURVEILLENCE RECORDS WERE SUBMITTED TO RECORDS CONTROL WITHOUT APPROPRIATE SIGNATURES BEING COMPLETED. THIS IS A SURVEILLENCE RECORD AND REQUIRES AN ASSIGNED REVIEWER SIGNATURE AND DATE BEFORE BEING SENT TO RECORDS FOR PROCESSING. <I> **** Actions Taken **** NOTIFIED SUPERVISOR/LEAD. SENDING BACK TO CHEMISTRY FOR CORRECTION AND RE-SUBMITTAL. <N> QAR records were signed by the reviewer and resubmitted to document control on 09/16/19. Closure of CR was approved by the Chemistry Technical Supervisor. No further action required.
398990 | CR | 20190911 |  | 4 | DLR Ran through X-Ray at PAAP |  |  |  | N | NO | <D> **** Detailed Description **** Employee became distracted while placing items through the x-ray and unintentionally placed their badge and DLR in the tray. <I> **** Actions Taken **** Notified management and HP. Generated CR for trending purposes.
398991 | CR | 20190911 | CAQ | C | Source Leak Check Results for Ni-63 above Limit |  |  |  | N | NO | <D> **** Detailed Description **** Source smear analysis results taken on Electron Capture Detector, located in the Kootenai, are above the limits set in HSP-SSC-O801. <I> **** Actions Taken **** HP Technicians were dispatched to post area around detector, users of the detector were notified that the detector is not available at this time. The Radiation Protection Source Program Owner and the Radiation Protection Manager were informed. HP Technicians are performing a follow up survey to determine the validity of the initial survey results. Initiated AR-REG 398985 to ensure required reports are submitted. <N> The Source ID Numbers for the Ni63 are 00-006 and 15-263 Survey Number for Leak Test is 20190911-2 WO # 010790021535 / 011458171203
398992 | CR | 20190911 |  | 3 | (PLANNING) PM NEEDS UPDATE |  |  |  | N | NO | <D> **** Detailed Description **** WO#02147487-01 should come out in the READY status, check the PM active box, remove the WD holds on the model and all tasked WO's. <I> **** Actions Taken **** Talked with supervisor and initiated CR
398994 | CR | 20190911 |  | 4 | ARC Flash Reduction Safety Focus |  |  |  | N | NO | <D> **** Detailed Description **** During R24 there was an amtector mod to SL-31/3 for personnel working downstream of this breaker. The Arc Flash incident energy prior to the Mod was 269.3 Cal/cm^2 and after was 21.6 Cal/cm^2. This is a significant reduction in incident energy for station personnel safety. Unfortunately racking this same Breaker the Incident energy is still 269.3 Cal/cm^2. SL-11,21,51,52,54,62,63 all have high incident energies still. NFPA 70E does not address anything above 40 Cal/cm^2 nor does it address the blast concussion of any Arc Flash events. Being that Safety First is one of our Current station focuses a technical review from engineering needs to be performed on multiple switchgear throughout the plant for Arc Flash reduction. See AR EVAL 00398993 <I> **** Actions Taken **** Wrote CR and AR EVAL 00398993 <N> **** Equipment Description **** .
398995 | CR | 20190911 | CAQ | C | Loose Surface Radioactive Contamination Found on M&TE |  |  |  | N | NO | <D> **** Detailed Description **** While performing a smear survey of a digital B-Rad torque wrench in support of M&TE calibration activities, loose surface contamination was detected on masslin taken over approximately 1 inch square area of the tool. It seemed to be residue from tape that had been removed during the masslin survey. The survey of the tool was located in a posted RCA/RMA, room 149D in the Kootenai bldg. Exit from this area requires a hand and foot frisk followed by counting in a whole body contamination monitor. Survey #20190911-3 <I> **** Actions Taken **** The smearable contamination was controlled at all times by the HP Technician. It was completely removed from the wrench and contained for disposal as rad waste. The box that the wrench was in and the surrounding vicinity was also surveyed for loose surface contamination. The HP Technician notified RP Supervision of the findings. RP Supervision dispatched an HP Technician to survey like wrenches kept in the tool crib of the RW 467â€™ and the RX 606â€™.
398996 | CR | 20190911 |  | 4 | CMS-SR-21 insulation damaged |  |  |  | N | YES | <D> **** Detailed Description **** CMS-SR-21 insulation damaged; a piece of insulation has fallen off exposing the heat trace and system tubing, additionally, the remaining insulation is cracked and in general disrepair. See EDMS for images <I> **** Actions Taken **** supervisor, specialist and CRS informed | 02-00-CMS-SR-21
398997 | CR | 20190911 | CAQ | C | A few Tech Spec (TS) pages need to be corrected. |  |  |  | N | NO | <D> **** Detailed Description **** A few Tech Spec (TS) pages in Asset Suite, on the Licensing Electronic Database and in the books need to be corrected. TS page 3.6.1.1-9 was changed by amendment 251. Amendment 253 changed the page again, however the change from Amendment 251 was not captured during that implementation. Page 3.6.1.3-5 was changed by Amendment 251 but the complete change was not implemented into the TS. TS 3.3.1.1 -- a few pages contain revision bars in the headers that are not present in the NRC approved copy. <I> **** Actions Taken **** Wrote CR; Providing new PDF and copy to RIM for distribution. Updated the licensing tree. Recommend Charlie to Reg Affairs to conduct an extent of condition on the TS.
398999 | CR | 20190911 | CAQ | C | CMS-RIS-27B is fluctuating excessively. | N | Y |  | N | YES | <D> **** Detailed Description **** CMS-RIS-27B is fluctuating excessively, as much as a decade and degrading. | 02-00-CMS-RIS-27B
399000 | CR | 20190911 |  | 4 | Annunciator 4.826.P2 received Drop 7-4 Filter 52B/53B End of | N | N |  | N | YES | <D> **** Detailed Description **** Annunciator 4.826.P2 received Drop 7-4 Filter 52B/53B End of Roll. Confirmed that WMA-FL-53B as the End of filter media roll. Per ARP submit CR/WR to replace alarming filter. <I> **** Actions Taken **** Informed CRS/SM | 02-00-WMA-FL-53B
399001 | CR | 20190911 |  | 4 | Event marker signal not seen by RTP | N | N |  | N | YES | <D> **** Detailed Description **** The event marker signal, X128-10, is not being seen by the real time plot established for performance of OSP -RCIC/IST-Q701. The event recorder and alarm typer are both seeing and recording the signal. Removed and reassigned the data point in the RTP, but still not able to see it on the trend graph. <I> **** Actions Taken **** Notified SM. Used Alarm typer time for time of event marker trigger. <N> **** Equipment Description **** MCR | 02-00-TDAS-COMP-8715
399002 | CR | 20190912 |  |  | RCIC-LS-11 IMDS Needs Clarification |  |  |  | N | YES | <D> **** Detailed Description **** The Instrument Master Data Sheet (IMDS) for RCIC-LS-11 states that the logic affected for switch #1 is: â€œRCIC-V-5 Opens & RCIC-P-4 Startsâ€. This gives the impression that RCIC-V-5 should always open when the switch actuates. This, however, is not always the case. RCIC-V-5 will only open when the RCIC turbine is not running (RCIC-V-45 closed). When the turbine is running, RCIC-V-5 will remain closed. A note should be added to the IMDS to clarify this and prevent future confusion. NOTE: This is a documentation issue only and does not affect any essential RCIC functions. | 02-00-RCIC-LS-11
399003 | CR | 20190912 | CAQ | C | RCIC-LS-11 IMDS Requires Clarification |  |  |  | N | NO | <D> **** Detailed Description **** The Instrument Master Data Sheet (IMDS) for RCIC-LS-11 states that the logic affected for switch #1 is: â€œRCIC-V-5 Opens & RCIC-P-4 Startsâ€. This gives the impression that RCIC-V-5 should always open when the switch actuates. This, however, is not always the case. RCIC-V-5 will only open when the RCIC turbine is not running (RCIC-V-45 closed). When the turbine is running, RCIC-V-5 will remain closed. A note should be added to the IMDS (AED IMDS RCIC LS-11) to clarify this and prevent future confusion. NOTE: This is a documentation issue only and does not affect any essential RCIC functions.
399008 | CR | 20190912 |  | 4 | 13 Pieces of M&TE Suspended until R25 |  |  |  | N | NO | <D> **** Detailed Description **** 13 Pieces of M&TE Passed Closeout Calibrations and are now Suspended until R25. Not used since Calibrated. No Plant Impact. See List for Calcodes, Descriptions and Associated DEF #'s. No Action Required. <I> **** Actions Taken **** None Trending purposes only
399009 | CR | 20190912 |  | 3 | Inadequate CR Closure for Mnt Dept Clock Resets |  |  |  | N | NO | <D> **** Detailed Description **** During the EB 17-04, First Line Supervisor Training and Development Snapshot Self-Assessment inadequate closure was identified in five of the 11 Maintenance Department Clock Resets, see EDMS for details of analysis. Recommend reopening and correcting the deficiencies identified in the EDMS of the CR for completion of this self-assessment future analysis. <I> **** Actions Taken **** Contacted Maintenance CIC and Maintenance Manager.
399012 | CR | 20190912 | CAQ | D | FP-ENG-1 Degraded Piping - License Renewal | N | Y |  | N | YES | <D> **** Detailed Description **** License Renewal . Based on the inspection by a qualified VT-1 and EVT-1 NDE specialist performed on WO 02139209-01 FP-V-11 AND FP-V-13 - LICENSE RENEWAL INSPECTION, FP piping immediately upstream and downstream of FP-V-11 should be replaced. Accumulation of deposits found on the internal piping surface indicate a degrading pipe. FP analyzed the inspection results and agrees due to the condition of the piping, the piping should be replaced. Suggest replacing pipe while FP-ENG-1 is being rebuilt or the next available FP-ENG-1 work window. . Pictures attached in EDMS folder. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** CWPH | 02-00-FP-V-11
399017 | CR | 20190912 |  | 3 | Met tower building wasp nests |  |  |  | N | YES | <D> **** Detailed Description **** WAsp nests found on outside of met tower building and base of met tower by the ladder. <I> **** Actions Taken **** Notified IC supervision and initiated CR for tracking purposes. | 02-00-MET-WMON-1A
399022 | CR | 20190912 |  | 3 | DOCUMENT SENT TO DOCUMENT CONTROL INCOMPLETE |  |  |  | N | NO | <D> **** Detailed Description **** OMM 220-01,2036,14 COULD NOT BE ISSUED BECAUSE THE EC HAS NOT BEEN ACTIVATED. <I> **** Actions Taken **** CR GENERATED AND DOCUMENT RETURNED TO ORG # 54430 <N> EC 16616 has been revised and was placed into Active status. Thus, the documents can be processed. No further actions required for this AR-CR, therefore, this AR-CR is now taken to COMPLT status.
399026 | CR | 20190912 | CAQ | D | SW-FS-71A low flow alarm | Y | Y |  | N | YES | <D> **** Detailed Description **** SW-FS-71A low flow alarm is locked in, but SW-FI-71A indicates current flow is at the top of the recommended flow range of 40-45 GPM (currently indicates 45 GPM). Lowest allowable flow is 38.5 GPM. Tapped the switch to see if a response in the indicator would be indicated; there was none. Please investigate and repair <I> **** Actions Taken **** Notified SMgt, wrote CR. . Operator initially thought the as-found flow was higher, as described in the CR. When they went back they discovered the flow was actually at the low flow alarm setpoint. SW flow returned to normal per OSP-SW-C101. <N> **** Equipment Description **** RB 548 FPC HX room | 02-00-SW-FS-71A
399027 | CR | 20190912 |  | 3 | Evaluate use of seals instead of key-locks for valves in CAs |  |  |  | N | NO | <D> **** Detailed Description **** Having key-locked valves inside of contamination areas necessitates bringing a key into the CA which may get lost or contaminated. The use of seals (red, green, yellow) would alleviate the problem, as new seals could be brought in and the old seals thrown in the rad trash. An example would be the locked SW valves in the FPC HX room. <I> **** Actions Taken **** Wrote CR, notified SMgt.
399030 | CR | 20190912 | CAQ | D | MET-WMON-1B found out of tolerance | N | Y |  | N | YES | <D> **** Detailed Description **** During the performance of ICP-MET-S301 -CC under WO 02113163 01 MET-WMON-1B was found out of tolerance slightly high. <I> **** Actions Taken **** Notified CRS, supervision and writing this CR to document <N> **** Equipment Description **** 245' level wind speed at MET Tower <R> REP/REGE assignments cancelled with Compliance Supervisor concurrence. | 02-00-MET-WMON-1B
399031 | CR | 20190912 | CAQ | C | Rremove reference to â€œlockâ€ on globe valve symbols on M501 |  |  |  | N | NO | <D> **** Detailed Description **** EC 17504 removed the locked designation from top tier drawings and added Note 14 to M501. However, the globe valve symbols on M501 still contain the LO and LC designators and the phrase â€œ(shown with lock)â€. Recommend M501 be updated to remove this information as it is confusing and seems to contradict the change management issued on 5/1/19.
399032 | CR | 20190912 |  | 3 | ICP-MET-S301 needs to be enhanced |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of ICP-MET-S301 multiple points within the procedure were found to be in need of enhancement, including some editorial issues and changes in how the work should be performed. <I> **** Actions Taken **** Notified supervision and writing this CR
399034 | CR | 20190912 |  | 3 | Work order reviews not completed per MI-3.6.4, 3.3.1.b. |  |  |  | N | NO | <D> **** Detailed Description **** In the past few days, there have been several (more than 20) PM work orders completed more than 14 days after they were finished. This has had a negative impact on the PM program as the late closure has caused the due dates for these PMs to be changed so that the due date is after the late date. This is causing an administrative burden on the PM program as the due dates need to be corrected. Part of the problem is the way that Data Glance pulls the credited date. It uses the date that the work order goes to completed, rather than the date the -01 task was finished. But ultimately, if the work orders were closed in a timely manner, this would not be an issue. <I> **** Actions Taken **** Discussed with my supervisor and wrote this CR. Recommend that when WOs are being completed beyond the 14 day requirement that the credit date is manually added on the M300 panel in Asset Suite to avoid this issue. <N> Asset Suite is working as designed. With the removal of completing the WO Package in Asset Suite, the user no longer has the ability to complete packages in Asset Suite which also gave the user the ability to change the PM Credit Date. There is not a way in DataGlance to change the PM Credit Date. â€œCredit by Critical Taskâ€ will be implemented during the Asset Suite 9 upgrade. So, when the critical task is set to FINISHED, the FINISHED date will used as the PM Credit Date
399035 | CR | 20190912 |  | 4 | TOA-FL-1B came loose from top connection. | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FL-1B EOR alarm recieved. Inspection revelaed that the left filter (farthest from entrance door) roll has came out of its holder. The filter unraveled towards the ground. <I> **** Actions Taken **** Informed MCR and silenced alarm. | 02-00-TOA-FL-1B
399037 | CR | 20190912 |  | 4 | Monthly Chemical Storage area inspection discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** The monthly inspection of Mechanical Maintenance chemical storage areas discovered the following discrepancies: Expired chemicals found in W467 tool crib flammable liquid stroage cabinet. <I> **** Actions Taken **** Expired chemicals taken to W437 for disposal. No further action required.
399038 | CR | 20190912 |  | 4 | found broke wire in TB-R302 cable J wire 10 | N | N |  | N | YES | <D> **** Detailed Description **** while performing WOT 02139999-01 for voltage leakage it was discovered that cable j wire 10 was broken approximately 4 inches up inside the insulation. <I> **** Actions Taken **** notified supervision and wrote CR <N> **** Equipment Description **** 501R TB-R302 penetration box
399041 | CR | 20190912 |  | 3 | Missing Fire Brigade Radios |  |  |  | N | YES | <C> CR found at INPROG, reviewed and moved to APPROVED. <D> After performing the Fire Brigade Portable Radio annual PM, the Telecomm Technician notified his Supervisor, the Radio Analyst and Planner/Scheduler that he was unable to find some of the portable radios. <I> Coordinated with the Fire Marshall and notified of the missing radios. Seven of the radios have still not been located and will be deactivated in the Radio System to prevent unauthorized system access. Fire Drills. Kept the PM opne <N> Fire Brigade Radio Locations, Missing radio IDs 405,647,320,646,640,772,634 Created Change Gear Ticket to disable radios in the Radio System database.
399042 | CR | 20190912 |  | 3 | Further guidance needed for PPM 1.4.8 |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.4.8 lacks appropriate guidance for the full evaluation of relief valve setpoint changes within the design process. Step 7.3.1 of PPM 1.4.8 does refer to SWP -DES-01 which does not mention anything regarding Relief valve setpoint changes. Section 3.5.2.d within SWP-DES-01 provided guidance for similar changes but doesnâ€™t contain Revisions to relief valve setpoint datasheets (PPM 1.4.8) as one of the activities or modifications that do not need an initiating AR to implement the change. As a result, if PPM 1.4.8 does need an AR to implement a relief valve setpoint change, recommend evaluating and updating PPM 1.4.8 as appropriate to clarify guidance in evaluating this change. <I> **** Actions Taken **** Discussed with System and Design Eng Supervisor
399043 | CR | 20190912 |  | 3 | Annual safety inspection performed at Calibration lab |  |  |  | N | NO | <D> **** Detailed Description **** The annual unannounced safety inspection was performed for the Calibration Lab. There were 2 findings for the inspection. <I> **** Actions Taken **** A WR 29151528 has been intiated to resolve the exit door signage and fire ext. Wrote a WR for the SWL marking for the overhead hoist in the shipping and recieving bay. Notified rep for the Cal Lab. Report sent to supervisor and loaded in EDMS. <N> **** Equipment Description **** Calibration Lab shipping and recieving bay hoist needs SWL marking on the hoist per ISPM-5. ... Overhead hoist rail system load limit sign.(see attached photo in EDMS). Exit sign over the new high bay door has not been done yet. WR 2915128 The ladder in the weight room(mass lab) has been secured. Environmental Service Scientist removed metal from behind door and appropirately store the metal piece.
399044 | CR | 20190912 |  | 3 | HSSF Pumps Cavitation Events | N | N |  | N | YES | <D> **** Detailed Description **** A review of HSSF-CAB-CHEM/LAB (HMI), Human Machine Interface Alarm Log revealed multiple instances cavitation events for both HSSF-P-1A and HSSF-P-1B, from 8/1/9 to 9/10/19. The reason for the cavitation is associated with the low Hydrogen Levels during those dates; however, the programmed protection for the system is that the pumps are turned off after the second event, on the second pump, and placed in â€œfaultâ€ mode, forcing operator action to manually restart at the HSSF facility after the condition has been cleared. CR history for that timeframe, does not show a forced re-start as much as the number of events that the HSSF HMI records. Operations should avoid re-starting the pumps and work with backup Hydrogen storage if Hydrogen levels are too low (<2â€of H2O per SYS-4-37). This condition has not affected the pump performance at this time, but can have an adverse effect with continued operation of the pumps, while multiple indication of excessive cavitation. Investigation should be requested to the vendor, why the pumps are not performing their â€œdesigned function to isolate on the second cavitation eventâ€. The pumps are on the vendor side of the facility. This CR should be owned by Maintenance since they have to requisition the work from Messer (HSSF Vendor Side) or H2E inc (PLC or Programming Side) to investigate the system not working as designed. Our Maintenance side should also review the PLC logic to see if there are functions disabled or incorrect timing on the associated thermocouple inputs for HSSF-TE-407 or HSSF-TE-417. In addition, CI -14.4 requires Chemistry initiate a CR when getting these events multiple times per attachment 6.1, Note 1 on page 18 of 19. CR database did not reveal this was being done. (See attached document in EDMS for additional Information) May need vendor to clarify how these pumps are supposed to resond on Low Hydrogen conditions. <I> **** Actions Taken **** Notified Supervisor and SM <N> **** Equipment Description **** HSSF Facility | 02-00-HSSF-P-1A,02-00-HSSF-P-1B
399046 | CR | 20190912 |  | 3 | WASP/YELLOW JACKET SAFETY HINDRANCE |  |  |  | N | NO | <D> **** Detailed Description **** BADGING IN SITE 1 ACCESS GATE WASPS OR YELLOW JACKETS SWARMED THE READER. LEAVING SITE 1, WASPS OR YELLOW JACKETS SWARMED THE TOP OF THE MOVING GATE. <I> **** Actions Taken **** CR WRITTEN. <N> Work Request was written and has been actioned to a Work Order. The issue was also discussed with Faciltiies
399047 | CR | 20190912 | CAQ | D | (NRC) Loose Bolt on ARC-B DIV-B cabinet | Y | N |  | N | YES | <D> **** Detailed Description **** NRC resident identified a loose bolt on the face of the ARC-B DIV-B cabinet in the main control room <I> **** Actions Taken **** initiated CR <N> **** Equipment Description **** ARC-B DIV-B cabinet in Main Control Room
399049 | CR | 20190912 |  | 4 | PSR-DOIT-15 cross-check OOT >10%, <20% | N | N |  | N | YES | <D> **** Detailed Description **** Dissolved oxygen cross-check between sink grab sample and inline instrument for SP-15 (PSR-DOIT-15) fell between 10% and 20%. Instrument still in service, but this difference range requires CR to be written and calibration be performed. <I> **** Actions Taken **** Initiate CR, informed specialist and supervisor | 02-00-PSR-DOIT-15
399050 | CR | 20190912 |  | 3 | B5-B Trailer lock |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** A pad lock was added to the trailer of battery B5-5. ( See attached picture) Due to limited space the lock is very diffcult to lock after door is closed. The doors are closed with fire protection tamper tye wraps that need work steps to be removed and installed. WO# 02138940-01 <I> **** Actions Taken **** Called SSS and supervisor. <N> **** Equipment Description **** B5-B located in Building 600 trailer 2.
399051 | CR | 20190913 |  | 2 | COND-LCV-11 drifted open during repair of air line | N | N |  | N | YES | <D> **** Detailed Description **** During repair of the air line to COND-LCV-11 per WR 29151531, COND-LCV-11 drifted open after air to the operator was isolated. Local position indication indicates the valve drifted open approximately 3 inches. Overall CFD d/p spiked to 46 psid, and condensate booster pump suction pressure was observed to lower to approximately 47 psig. Reactor power was reduced to 96% to maintain margin on booster pump suction pressure. <I> **** Actions Taken **** With no air to the LCV, COND-V-166 was manually shut to isolate condensate from the LCV and prevent further drift of the LCV from causing a low suction pressure alarm and trip. <N> ***General Notes*** an event investigation has been conducted. The report is in draft status as of 9/13/19, when the report is finalized it will be uploaded into the EDMS of this AR . written statements and a picture of COND-LCV-11 have been uploaded into the EDMS of this AR. Preliminary investiation results have found that a lack of risk mitiation during the clearance order creation is the cause . Recomend OPS take ownership of this CR. | 02-00-COND-LCV-11
399052 | CR | 20190913 |  | 4 | No indication of flow following start of CF-P-42A | N | N |  | N | YES | <D> **** Detailed Description **** After starting CF-P-42A no indication of flow was observed at CF-FG-42. CF-PI-42 also showed no pressure change and no chemical discharge was visible from tubing into TSW Wier downsteam of CF-V-863. <I> **** Actions Taken **** Informed CR, Shutdown Pump, Wrote CR. | 02-00-CF-P-42A
399053 | CR | 20190913 |  | 4 | Lighting over CCH-CH-1B needs to be replaced. |  |  |  | N | YES | <D> **** Detailed Description **** The lighting ballast that is right above CCH-CH-1B on the RW 525' is very dim and needs to be replaced. <I> **** Actions Taken **** Initiated this CR. <N> **** Equipment Description **** Directly above CCH-CH-1B on RW 525'.
399054 | CR | 20190913 | CAQ | D | PPC-CRT-RWM display is spastic, erratic, and unusable. | Y | N |  | N | YES | <D> **** Detailed Description **** PPC-CRT-RWM display is spastic, erratic, and unusable. Please see video. Suspect that the CRT needs repaired/replaced. <I> **** Actions Taken **** Wrote this CR to drive repair. | 02-00-PPC-CRT-RWM
399055 | CR | 20190913 |  | 3 | Unable to Run the Dose Report |  |  |  | N | NO | <D> **** Detailed Description **** -Unable to run the Dose Report as part of the HP Lead Tech Nightly Sign-Off. Notified Steve Brush & Troy Mcnabb via E-mail. <I> **** Actions Taken **** Notified Brush & Mcnabb Notified Supervision via E-mail.
399057 | CR | 20190913 |  | 3 | IPM-8 replacements ahead of AR EVAL 392199 approval |  |  |  | N | NO | <D> **** Detailed Description **** A 09/11/19 Energy Northwest news article indicates the old IPM-8 monitor replacements at the HP primary access point have already been completed and that there are plans to replace the IPM-8 monitors at the HP alternate access point. The AR type EVAL associated with the activity (AR EVAL 329199 - Eval on elect. load/floor load for APP/TSC IPM replacement) has not yet been evaluated per DES-2-9 process. Existing obsolete IPM-8 monitors are being replaced with Argos-5AB monitors. This is likely a conservative change activity but the AR EVAL is not complete (appears out of process).
399058 | CR | 20190913 |  | 4 | Substantially loosened handwheel nut for COND-V-117B | N | N |  | N | YES | <D> **** Detailed Description **** While performing field walkdown for a proposed FY21 Design modification, a substantailly loosened handwheel nut for COND-V-117B (24" manual gate valve for COND-P-2B suction isolation) was observed. See the photos attached to the AR CR 399058 EDMS. Due to the obvious safety concern associated with the observed condition, the loose handwheel nut was hand tightened (immediate response) but should be formally (i.e., fully) tightened by qualified craft. Please also check and tighten as necessary the handwheel nut for COND-V-117A, COND-V-120A, COND-V-120B, COND-V-117C, and COND-V-120C. These valves are all accessible from their associated permanent platform above COND-M-P/2A, COND-M-P/2B, and COND-M-P/2C. | 02-00-COND-V-117A,02-00-COND-V-117B,02-00-COND-V-117C,02-00-COND-V-120A,02-00-COND-V-120B,02-00-COND-V-120C
399059 | CR | 20190913 |  | 3 | AED PRC 30034 not attached to Portal J Image |  |  |  | N | NO | <D> **** Detailed Description **** An electronic copy (e.g., pdf) of AED PRC 30034 (EQUIPMENT MODIFICATION SPECIFICATION FOR WALWORTH VALVE HEX HANDWHEEL ADAPTOR MODIFICATION) is not currently attached as an Image in Portal J. The current Image attachment for this document in Portal J is a Document Summary. Please obtain and replace the existing Image with an electronic copy of the subject EMS (i.e., the actual document). This is an administrative issue only.
399060 | CR | 20190913 |  | 3 | CM issues for COND-V-117A(B,C) and 120A(B,C) | N | N |  | N | YES | <D> **** Detailed Description **** Configuration management issues noted in passing for large bore manual isolation valves COND-V-117A(B,C) (24" NSR gate valves) and COND-V-120A(B,C) (20" NSR gate valves). 1) CVI DWG 43-00,76 indicates EMS 30034 (AED PRC 30034) for COND-V-11 A(B,C) but the EMS does not appear to be implemented in the field at these valves to prevent the handwheels from falling off. Please implement EMS 30034 at COND-V-117A(B,C). 2) CVI DWG 43-00,32,1 indicates EMS 30034 (AED PRC 30034) for COND-V-120A(B,C) but the EMS does not appear to be implemented in the field at these valves to prevent the handwheels from falling off. Please implement EMS 30034 at COND-V-120A(B,C). 3) CVI DWG 43-00,76 and CVI DWG 43-00,32,1 and CVI OMM 43-00,124 indicate chainwheels for COND-V-117A(B,C) and COND-V-120A(B,C) but regular handwheels are installed in the field. Please update this CVI documentation (detail drawings and O&M manual) to depict regular handwheels for COND-V-117A(B,C) and for COND-V-120A(B,C). . This is an administrative issue only - no impact upon continued function or normal operation for the subject EPNs. | 02-00-COND-V-117A,02-00-COND-V-117B,02-00-COND-V-117C
399061 | CR | 20190913 |  | 3 | STAY CLEAR brackets and chains at E-DP-S1/1C | N | N |  | N | YES | <D> **** Detailed Description **** The PPM 1.3.81 STAY CLEAR brackets and chains currently installed at T441' E-DP-S1/1C do not conform with PPM 1.3.81 Attachment 9.7 installation requirements. Specifiically, the installation lacks the desired chain sag between brackets of ~3 inches (see PPM 1.3.81 R14 pg 45 of 46). Please replace the existing plastic chain with a slightly longer plastic chain to provide ~3 inches of chain sag such that the field installation conforms with PPM 1.3.81 Attachment 9.7. There is no immediate concern for continued SSC operation or function but the condition should be corrected to conform with the procedure. <N> Stay clear chains were adjusted to meet procedural criteria. | 02-00-E-DP-S1/1C
399062 | CR | 20190913 |  | 4 | Damaged ladder holder T441' RFW B pump room | N | N |  | N | YES | <D> **** Detailed Description **** The west bracket for the typical portable ladder holder in the T441' RFW B pump room is damaged (has been bent up and to the west). See the photos attached to the EDMS of this AR CR 399062. Please repair/replace to restore conformance with the AED S679-2 detail. Def Tag 41818. | 02-00-T-BLDG-MISC
399063 | CR | 20190913 |  | 4 | Chains for MT-HOI-2A and MT-HOI-2B roped to nearby SSCs | N | N |  | N | YES | <D> **** Detailed Description **** The chains associated with RFW A pump room MT-HOI-2A and RFW B pump room MT-HOI-2B have been tied off with ropes to nearby SSCs. This is a possible cause associated with the AR CR 399062 condition in the RFW B pump room. Please correct. | 02-00-MT-HOI-2A,02-00-MT-HOI-2B
399065 | CR | 20190913 |  | 4 | Vertical rod for support COND-1383-16 | N | N |  | N | YES | <D> **** Detailed Description **** The vertical rod for NSR QC 2 SC 2 small bore deadweight pipe support COND-1383-16 (RFW A pump room on 2"COND(103)-3 piping associated with MD-TCV-3A - CVI 317-00,5058) appears to be hanging up under thermal movements of the associated piping on bolted splice plates for NSR QC 2 SC 2 large bore pipe support RFW-10 (CVI 215-08,14749) added via legacy BDC 87-0060-0A. See the photos attached to the EDMS of this AR CR 399065. Def Tag 41819. This condition should be investigated and corrected but there is no immedate impact upon continued function of the subject small bore support or any associated SSCs. <I> Also, the retaining nut appears to be missing from the load bolt for clamp at support COND-1383-16. <N> **** Equipment Description **** T441' RFW A pump room - south end of RFW-P-1A
399066 | CR | 20190913 |  | 4 | The handwheel for 16" COND-V-168 is about to fall off | N | N |  | N | YES | <D> **** Detailed Description **** The retaining bolt for the COND-V-168 handwheel has fallen out (missing). As a consequence, the handwheel for this 16" gate valve has slid down the manual operator shaft over time and is now about to fall off. This valve is not located in the overhead or a high traffic area but the handwheel is above head level. See the photos attached to the EDMS of this AR CR 399066. Please correct this condition. Also verify that EMS 30034 (AED PRC 30034) has been implemented at this valve as indicated on CVI 43-00,91 and CVI 43-00,131. If the EMS has not been implemented, it should be implemented either as part of the correction of this AR CR condition or as a follow-on activity after immidate actions for correction of this AR CR condition are taken. <I> Notified Operations (Main Control Room). | 02-00-COND-V-168
399067 | CR | 20190913 |  | 4 | Portable ladders stored at T441' 10.1 and 10.4 don't fit | N | N |  | N | YES | <D> **** Detailed Description **** The portable ladders that have been stored at T441' Ladder Storage Locations 10.1 and 10.4 do not fit the currently existing bracket arrangements and should be relocated. The ladder stored at Ladder Storage Location 10.1 is obviously much too long and needs to be relocated. The ladder stored at Ladder Storage Location 10.4 is too wide such that one bracket cannot be engaged and obviously needs to be relocated. The style of ladder currently being stored at these locations is not a common standard step ladder of extension ladder and does not fit the size of the AED S679-2 typical portable ladder storage brackets. | 02-00-T-BLDG-MISC
399068 | CR | 20190913 |  | 4 | T441' housekeeping issues | N | N |  | N | YES | <D> T441' walk through revealed the following SWP-MAI-02 housekeeping issues: 1) Maintenance adapter fittings left installed at D-15 column hose bib SA-V-99/2. 2) Maintenance adapter fittings left installed at F-16 column hose bib SA-V-99/3. 3) Extra fittings left installed downstream of DW-V-100/56. 4) Untagged telephone cord left installed from the permanent phone at B6-5 to a non-permanent phone in the T441' RV Test Shop. 5) Untagged tygon hoses left installed at TSW-V-727A and TSW-V-727B in the Aux Boiler Room. . See the photos attached to the EDMS of this AR CR 399068. . An ab-end occurred when this AR CR 399068 was initiated using the AR CR initiation wizard. As a result, the WR's for correction of the housekeeping issues identified were not automatically created and had to be created manually. Please advance this AR CR 399068 from INPROG manually. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review. | 02-00-DW-V-100/56,02-00-SA-V-99/2,02-00-SA-V-99/3,02-00-T-BLDG-MISC,02-00-TSW-V-727A,02-00-TSW-V-727B
399069 | CR | 20190913 |  | 3 | Portable ladder left outside adjacent to DG4 |  |  |  | N | YES | <D> **** Detailed Description **** A portable ladder was observed that had been left outside (exposed to the sunlight/elements) adjacent to E-GEN-DG4 on the semi trailer rather than returned to a proper storage location. Per ISPM-9 R19 MnrR3 paragraph 3.2.8 d - Users should return ladders to proper storage location when the job is completed. Per ISPM-9 R19 MnrR3 paragraph 3.2.9 e - Ladders, when not in use, should be stored where they are protected from damage that may result from collision, temperature, moisture, sunlight, etc. Taking action to move the subject ladder to the GSB Clean Tool Crib area. <I> The subject portable ladder has been relocated to the GSB Clean Tool Crib area - it is labeled 'PAINTERS'. | 02-00-E-GEN-DG4
399070 | CR | 20190913 |  | 3 | Daily Schedule Coversheet Phone List is not being updated |  |  |  | N | NO | <D> **** Detailed Description **** The coversheet on the Daily Schedule has all of the points of contact with phone numbers and pager numbers for various departments. The Shift Managers (SM), Control Room Supervisors (CRS), and the Work Week Managers (WWM) use the coversheets to know who to call when they need support for emergent conditions in the plant. This is not being updated by the various responsible departments. The result of this is that it makes it harder for a CRS, SM, or WWM to get a hold of the right people and leads to delays in response to the emergent condition. For example, in the Daily Schedule package for the weekend of September 13, the listed Engineering Backshift Coordinator, Weekend Maintenance Supervisor, and Backshift Maintenance Supervisor are not the correct people. We need to either identify dedicated personnel in departments to update this coversheet on a regular basis or determine a better way to provide this information to the people that need it. <I> **** Actions Taken **** Discussed this issue with Engineering and Maintenance Managers. Generated this CR. <N> Engineering has an oncall phone which needs to be put on coversheet. They do not list a different phone for each individual. The schedule cover sheet has been changed to reflect this number. Talked with the Maintenance Admin concerning the Maintenance oncall individual phone number. She updates each time a change is given and maintains long range. This CR can now be closed.
399071 | CR | 20190913 |  | 4 | Scaffold Fall Protection Tie-offs |  |  |  | N | NO | <D> **** Detailed Description **** While performing the initial HP survey of Scaffold #â€™s 4538/4540 & 4537, on the TB 471â€™ West, inadequate tie-offs found. Each scaffold is tagged â€œ100% tie-offâ€ required. I was able to tie-off on each platform utilizing a TieBack lanyard around white iron (which my harness was equipped with only by chance) on both scaffolds. Scaffold # 4538/4540 did have a beam strap for tie-off, however it was not accessible from the ladder. Scaffold # 4537 had no visible designated tie-off points. The ladders to access each platform do not adequately extend above the scaffold platforms. Due to the platformsâ€™ proximity to the ceiling, ladder positions and lack of sufficient tie-off points, traversing between the ladders and platforms is extremely awkward. <I> **** Actions Taken **** HP Supervisor notified of condition of scaffolds. Safety personnel were subsequently notified. In the field, showed concerns to Safety personnel. Recommended that a competent/qualified person re-evaluate the configuration of the scaffolds and potential tie-off points. If other tie -off points (ex. beam straps, self-retracting lifelines, etc.) can be placed around platforms/ladders, it will greatly increase workersâ€™ safety of accessing and working from these scaffolds. <N> **** Equipment Description **** TB 471' West
399072 | CR | 20190913 |  | 4 | CW-CT-2B level high and overflowing | N | N |  | N | YES | <D> **** Detailed Description **** CW-CT-2B level is high at 14.75" and water is flowing over the side, and there is a significant amount of algae growth visible. Recommend cleaning tower. <I> **** Actions Taken **** Informed MCR, generated AR/WR. | 02-00-CW-CT-2B
399073 | CR | 20190913 |  | 4 | Low ASD glycol resistivities | N | N |  | N | YES | <D> **** Detailed Description **** GY-CI-10A2 was observed to be less than 5Mohm, 10A1 & 10B1 are approaching minimum spec (10B2 is also below spec but under FIN investigation). Recommend changing filters as necessary. <I> **** Actions Taken **** Generated AR/WR. | 02-00-GY-CI-10A1,02-00-GY-CI-10A2,02-00-GY-CI-10B1
399074 | CR | 20190913 |  | 3 | PWC-XR-1 PT2 scale too wide | N | N |  | N | YES | <D> **** Detailed Description **** PWC-XR-1 PT2 Turbidity Outlet (Green line) is on a 0-5 NTU scale. The Flocculator trips at 0.2 NTU outlet turbidity, with a normal value of 0.065-0.09 NTU. Recommend change scale for PT2 to 0-0.5 NTU so that a useful trend can be observed on the recorder. <I> **** Actions Taken **** Generated AR/WR. <N> Created 399165. | 02-00-PWC-XR-1
399082 | CR | 20190914 |  | 4 | CP-RECT-DW2 Light Unlit | N | N |  | N | YES | <D> **** Detailed Description **** Around 2100 on 9/13 the green lamp on CP-RECT-DW2 (potable water pumphouse) was not lit. Later in shift, around 0400, the lamp was again lit. The lamp is actually a series of LEDs, so it is unlikely to an issue with the lamp itself. <I> **** Actions Taken **** Informed MCR | 02-00-CP-RECT-DW2
399083 | CR | 20190914 |  | 4 | COND-LCV-11 inst tube needs support | N | N |  | N | YES | <D> **** Detailed Description **** COND-LCV-11 instrument tube vibration causes copper tube to work harden and snap. Either replace copper tube with SS or provide support for the copper tubing. See EDMS for video previously identified on the same tube that failed 9/13/19. Refrence AR 188920. http://thecurrent/sites/NG .OPS.PGM.Maint.Images/MPL/COND/VALVES/Movie%20of%20COND -LCV-11/COND LCV 11 11 24 2008.avi - for video | 02-00-COND-LCV-11
399084 | CR | 20190914 |  | 4 | Housekeeping issue; fire extinguisher in upright position |  |  |  | N | NO | <D> **** Detailed Description **** Found a portable fire extinguisher staged for work WO 02139804, in upright position and not secured. I placed fire extinguisher in horizontal position and prevented it from rolling away. <I> **** Actions Taken **** CR for trending. Placed fire extinguisher in horizontal position and prevented movement.
399086 | CR | 20190914 |  | 4 | H2/O2 Analyzer Heat Trace Trouble Alarm came in. | N | N |  | N | YES | <D> **** Detailed Description **** The H2/O2 Analyzer Heat Trace Trouble Alarm came in for HT-TS-SR13/2. All actions of the ABN were performed. The temperature reading locally was 115F. MCR informed <N> Heat trace low temp alarm of 100F +/- 4F is input for this annunciator and per the IMDS. As found temp was 115F. | 02-00-HT-TS-SR13/2
399087 | CR | 20190914 |  | 4 | Aux Boiler AS-BLR-1 continues to lose level | N | N |  | N | YES | <D> **** Detailed Description **** WR 29151393 was completed on 9/11 and the aux boiler was put in wet layup with a nitrogen blanket. On 9/14, the level had decreased from offscale high (wet layup) to 11" on CO-LI-1. <I> **** Actions Taken **** Refilled the Aux Boiler and restored nitrogen blanket. Wrote this CR/WR and informed supervision. | 02-00-AS-BLR-1
399088 | CR | 20190915 | CAQ | D | NRC ENS phone non-functional | N | Y |  | N | YES | <D> **** Detailed Description **** NRC HOO called via a commercial line as the ENS phone was not ringing in the main control room. Verified that the ENS phone had no signal and that calls could neither be made nor received to the NRC via the ENS. NRC HOO stated that they were putting in a trouble ticket with Verizon. <N> **** Equipment Description **** NRC ENS Phone in main control room IS and EP notified.
399095 | CR | 20190915 | CAQ | D | MS-RIS-610C display failing | N | Y |  | N | YES | <D> **** Detailed Description **** MS-RIS-610C display failing. Indication has a ghosted image aligned slightly above the normal image. See EDMS for pic. | 02-00-MS-RIS-610C
399096 | CR | 20190915 |  | 4 | COND-HX-3C shell pressure deviation from A & B | N | N |  | N | YES | <D> **** Detailed Description **** COND-HX-3C shell pressure has been trending about 10 psig higher than COND-HX-3A(B) since the outage. The shell pressures on all 3 heaters have been consistant to transients, indicating that the pressure transmitter may only require calbiration. See EDMS for further details. CR initiated for trending. <I> **** Actions Taken **** Informed CRS, verified deviation via EDNA trend. | 02-00-BS-PT-3C
399097 | CR | 20190915 |  | 4 | (NRC) SWPH A Building Exterior Lighting Out | N | N |  | N | YES | <D> **** Detailed Description **** The exterior lighting on SWPH A over the normal access door and the equipment hatch are out. Lights fixtures need to be relamped. <N> **** Equipment Description **** Service Water Pump House Exterior lights above normal acces s door and equipment hatch
399098 | CR | 20190915 | CAQ | D | CIA-TK-3A Leaking Connection | Y | N |  | N | YES | <D> **** Detailed Description **** There is a leak where the flexible hose connects to CIA-PRV-3A. This connection has NeoLube pipe thread sealant (pipe dope) that will likely need to be cleaned off and reapplied. <I> **** Actions Taken **** Informed MCR | 02-00-CIA-PRV-3A
399099 | CR | 20190915 |  | 4 | (NRC) Copper tubing corrosion | N | N |  | N | YES | <D> **** Detailed Description **** Four copper 3/4â€ lines passing through Penetration D206 -5014 in Room D102 have varying degrees of surface corrosion on them. These copper lines provide a cooling supply and return from the room D206 radio equipment air conditioning units. | 02-00-COMM-AC-D206/1,02-00-COMM-AC-D206/2
399100 | CR | 20190916 |  | 4 | Cameras needing cleaning in the Protected Area |  |  |  | N | YES | <D> **** Detailed Description **** A list of cameras needing cleaning was generated by CAS and sent to supervision for a CR/WR. <I> **** Actions Taken **** CAS officer conducted a camera inspection for visibility, generated list, notified supervision, CR/WR generated. Cameras goes as follows: CCTV 01/07/08/12/21/43/45/61 <N> **** Equipment Description **** Cameras located inside Protected Area. Cameras 43/45/61 located at the ISFSI.
399101 | CR | 20190916 |  | 4 | SP-1 conductivy | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** SP-1 grab sample conductivity was GT 10% higher than the meter & recorder, but less than 20%. <I> **** Actions Taken **** Informed the CRS and chem supervision and wrote a CR. <N> **** Equipment Description **** RW 467 control room
399102 | CR | 20190916 | CAQ | D | (NRC identified) Debris and trash in SW-B pumphouse pit | Y | N |  | N | NO | <D> **** Detailed Description **** (NRC identified) There is debris and trash from maintenance activities in the SW-B pumphouse pit below the existing scaffolding. Some of this material was retrieved and disposed of, but the scaffold arrangement is such that some of the material could not be retrieved. Request scaffolders coordinate with the maintenance department or laborers to modify the scaffold to permit access for cleaning and removal of the material. <I> **** Actions Taken **** Discussed with Shift Manager. <N> **** Equipment Description **** SW-B pumphouse
399103 | CR | 20190916 |  | 4 | FPC-DM-1A Has boundry Valve leakage. | N | N |  | N | YES | <D> **** Detailed Description **** During the Precoat procedure it was noted that FPC-DM-1A rapidly repressurizes, (about 30 Seconds), after Depressurizing per SOP-FPC-DEMIN step 5.3.3. This indicates FPC-V-6A and/or FPC-FCV-15A is leaking by. (The inlet and outlet valve). This needs to be addressed in a timely fashion. FPC-DM-1B is in need of repair. If FPC-DM-1A goes down, we will have no ability to Clean the Fuel Pool or the Suppression Pool. | 02-00-FPC-DM-1A
399105 | CR | 20190916 |  | 4 | CPR-TK-92B has relay and Alarm Issues | N | N |  | N | YES | <D> **** Detailed Description **** The High level alarm will generally not actuate on CPR-TK -92B when a High Level Condition is in. Relay K440 appears to be associated with this and is behaving abnormally, (Chattering/Vibration/Changing state with no change in tank status). This is the Phase Separator tank that is currently in use, the other is Full of resin. If this fails completely we will not be able to BW/PC CFDs. | 02-00-CPR-TK-92A
399106 | CR | 20190916 |  | 4 | The Contaminated area behind RWCR has not been Cleaned yet |  |  |  | N | YES | <D> **** Detailed Description **** The C Zone behind the RWCR, next to the RWCU Precoat Tank has not been cleaned up. We were told several times that it would be cleaned up PRIOR to the Outage. It is still a C Zone. We need to access this area anytime we do a BW/PC on a RWCU Demin. It is not setup for entry/exit. This is a small area and needs to be deconned soon. <N> **** Equipment Description **** N/A Attempts to decontaminate this area during the outage were unsuccessful. Initiated WR 29151629 to get decontamination work and dose budget into the schedule.
399107 | CR | 20190916 |  | 4 | 2 Pieces of M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** 2 Pieces of M&TE Passed Calibration and are now Rejected- unable to adjust. Not used since Cal'd. Calcode #0063823 Heise Pressure Calibrator- model PTE-1. DEF #7308A written. Calcode #0066435 Hytorc Gauge 10,000psig. DEF #7309A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
399108 | CR | 20190916 | CAQ | C | Two pieces of MT&E found out of tolerance |  |  |  | Y | I DONT KNOW | <D> Calcode #0064645 RM Young RH/Temperature Probe- model 41372LF found OOT & adjusted within specs. DEF #7310A written. DEF #7310A written. Calcode #0064893 RM Young Temperature Probe- model 41342FL found OOT & adjusted within specs. DEF #7311A written. EFIN to evaluate usages. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
399112 | CR | 20190916 |  | 3 | SOP-COLDWEATHER-OPS potential procedural conflict |  |  |  | N | NO | <D> **** Detailed Description **** Step 6.1.16.f of SOP-COLDWEATHER-OPS instructs the operator to close all CW pump house ventilation dampers upon entry into cold weather operations. The caution that immediately follows, which relates to roof ventilator operation, states it is recommended to run a maximum of two (minimum of one) roof ventilators with one damper open. This caution should be evaluated and revised as necessary. <I> **** Actions Taken **** Generated the AR
399114 | CR | 20190916 |  |  | 2 IMDSs updating currernt revision |  |  |  | N | NO | <D> **** Detailed Description **** The 2 Instrument Master Data Sheets (IMDS) to be voided are the same revision as the current ones in Asset Suite <I> **** Actions Taken **** Sent documents back. RFT-PS-63TT2/1B Revision 006 and RFT -PS-63TT2/1A Revision 009 already exist in the system and I cannot duplicate revisions. Documents will need to be the next major revision up to process. Notified my supervision and created CR. <N> CR written in error. Cancel CR.
399115 | CR | 20190916 | CAQ | D | M&TE Suspended/ Lost |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0068661 Mitutoyo Dial Caliper- model 505-742 6" is Missing from the Clean Tool Crib. Box & usage card left behind. No Activity in Portal J. Suspended/ Lost. No Plant Impact. DEF #7312A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
399116 | CR | 20190916 | CAQ | C | CID 7122- Limits on Use needs to be revised. |  |  |  | N | NO | <D> **** Detailed Description **** The Limitation on use for this CID requires the re-seat of the valve to be between 0-25 PSIG. The Relief Valve Data Sheet (RVDS) for DSA-RV-13 and DSA-RV-14 were revised to allow a reseat range of 0-30 PSIG. The RVDS revision was due to inability to achieve a 0-25 PSIG re-seat of the new valves (CID 7122) and still maintain no seat leakage (ref. ARCR 398979). <I> **** Actions Taken **** Wrote CR.
399117 | CR | 20190916 |  | 3 | PPM 5.5.12 Procedure Change |  |  |  | N | NO | <D> **** Detailed Description **** PPM 5.5.12 Rev. 11 incorporated ABN-FSG-005 battery pack usage as an alternate method to Emergency Depressurizing the RPV when the normal means were not available per AR 378726. Steps 4.7.1 and 4.7.2 were incorporated which provides operator confusion on performing the section. It implies ABN-EDMG must be enter. The original intent of AR 378726 was to remove reference to ABN-EDMG. The section should start with Step 4.7.2.a with its previous warning. The Caution and Note below Step 4.7.1 can also be removed. The intent of Emergency Depressurization is to reduce RPV pressure LT 40 psig. <N> Review the rest of the section for more changes. There is no EC. Pressure indication will be in MCR.
399120 | CR | 20190916 |  | 4 | Flooding in CWPH Room B-107 and CWPH Floor | N | N |  | N | YES | <D> **** Detailed Description **** During the halogenation on Monday 9/16, the Chem Tech observed that when the sump in the vault below the CWPH Room B107 came on the water came out of the room drain resulting in the room flooding with approximately an inch of water. The water ran out underneath the door to the main CWPH area and covered an area from the rollup door to the fire pumps. Significant amount of water. <I> **** Actions Taken **** Informed the OPS4 SSS of the situation and he confirmed he would notify the Control room. CR written. <N> **** Equipment Description **** Sump Vault - CWPH Is the drain line downstream of FD-P-15 internally restricted?
399121 | CR | 20190916 |  | 4 | 2 Pieces of M&TE Suspended/ Lost |  |  |  | N | NO | <D> **** Detailed Description **** 2 Proto Torque Wrenches from the Clean Tool Crib were checked out 4/8/19 WO #02120016-10. Never Returned. Checking Portal J- Neither were recorded in packages as being used. Calcode #43554- model 6016 150ft/. DEF #7313A written. Calcode #0067700 -model 6012C 100ft. DEF #7314A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
399123 | CR | 20190916 | CAQ | D | As found time on PRA-RLY-TK1B out of tolerance | Y | N |  | N | YES | <D> **** Detailed Description **** While performing calibration on PRA-RLY-TK1B per WO#02112853-01 and 10.25.207, the as found time was out of tolerance at 1600 seconds with a tolerance of 1620 - 1980 seconds. The next three timing tests were all within tolerance at 1727,1763 and 1774 seconds with no adjustments needed. As left time average was 1755 seconds and in tolerance. <I> **** Actions Taken **** Informed supervisor and wrote CR | 02-00-PRA-RLY-TK1B
399124 | CR | 20190916 | CAQ | D | Received RDCS INOP alarm. | N | N |  | N | YES | <D> **** Detailed Description **** see EDMS for fault map. System reset and operated with no additional issues. suggest trend - nothing to fix <I> **** Actions Taken **** Reset RDCS per ARP and re initialized RWM. System returned to normal. SE emailed fault map â€“ see EDMS for pic.
399125 | CR | 20190916 |  | 4 | Main Turbine Bearing vibration weekend changes 20190916 | N | N |  | N | YES | <D> **** Detailed Description **** Small changes appear to be developing in Main Turbine bearing vibration that looked to be the beginning of a trend that started over the weekend (13Sept2019). Brg 4 (LPA East end) has seen an approximate 0.3 mil increase up to around 6.9 mils. Brg 3 (LPA West end) has experienced a corresponding increase to 3.6 mils. Brg 7 (LPC East end) and Brg 8 (LPC West end) have seen a slight decline over the same period. These changes may be the result of the bearingsâ€™ responses to improved backpressure due to lowering seasonal temperatures. This CR is being written to document trending and monitoring findings. At approximately 0930 hrs on 16Sept2019, the vibration levels lowered near pre-weekend levels, so there are no immediate actions required. Continue to monitor and evaluate developing trends. <I> **** Actions Taken **** discussed with supervisor, PGM and VP Eng <N> **** Equipment Description **** TG501 turbine deck | 02-00-MS-DT-1A,02-00-MS-DT-1C
399129 | CR | 20190916 |  | 3 | Fire Brigade Inventory Work Order Packages |  |  |  | N | NO | <D> **** Detailed Description **** There are inconsistencies that are found within the series of Fire Brigade Inventory packages that needs to be rectified. The packages are separated into six stations, which is extremely helpful to keep the areas separated. However, there are directives within the packages that are unnecessary to perform and discrepancies within the WO package and the procedure references. Regarding the procedural references in WO Package 02139153-03 (Fire Brigade Station Inventory Station 2 BLDG 62). First, the WO references PPM 15.1 on page 10, step 1.0. This should actually reference HPI-15.1 (Inspection and Storage of Respirators and Attachments) procedure. The second improper reference pertains to HPI-15.1, step 4.4.4, which states: WHEN any SCBA or cylinder that fails inspection, DOCUMENT on Attachment 2 of the SCBA Work Order Task package the deficiencies found and actions taken. This does not correspond with the WO instructions which label attachments alphabetically, not numerically. This applies to all six WO packages that govern the entire Fire Brigade Inventory. The procedure needs to be revised as such: DOCUMENT on the respective Deficiencies Found and Actions Taken attachment of the SCBA Work Order Task package. It is unnecessary to track the SCBA spare face piece numbers in the SCBA Respirator Spare Face Piece Inspections attachment. The attachment specifies that we either record the spare face piece assigned number, or record N/A if no number has been assigned to the spare face piece. There is no procedural guidance that states we must maintain a spare face piece numbering system. All of the numbers on the SCBA spare face pieces should be removed because there is no tracking system and it prevents unnecessarily recording obsolete information. The SCBA Mask Inventory attachments on page 9 of WO 02139153-03 (Fire Brigade Station Inventory Station 2 BLDG 62), page 9 of WO 02139153-02 (FIRE BRIGADE STATION INVENTORY STATION 1 TG 441), and page 9 of WO 02139153-05 (FIRE BRIGADE STATION INVENTORY TG 501 AND MCR), can all be removed from the WO package. This is a redundant step that records the total amount of masks that is already captured in the Spare Face Piece attachment in each respective WO. The Spare Face Piece not only supplies the total number of masks available, but it also provides the size information. A note could be added to the attachment that provides the minimum amount of each size masks that is necessary to be located at each station. Removing unnecessary steps and streamlining these WO packages will create a more efficient process. <I> **** Actions Taken **** Informed HP Supervision, created AR/CR.
399130 | CR | 20190916 |  | 4 | CARPET IN HP LEAD OFFICE IS A TRIPPING HAZARD | N | N |  | N | NO | <D> **** Detailed Description **** OLD CARPET IN HP LEAD OFFICE AREA IS RIPPED. THE RIPPED AREA IS LARGE ENOUGH TO SNAG SOMEONE'S FOOT YET IS ALSO SECURE ENOUGH TO NOT "GIVE" THEREFORE ABLE TO CAUSE A FALL. <I> **** Actions Taken **** TAPED OVER CARPET SEAM. GENERATED CR.
399131 | CR | 20190916 |  | 4 | ISSC Call capabilities INOP | N | N |  | N | NO | <D> **** Detailed Description **** The Cisco Unified Contact Center Server became INOP after the Corp Phone system upgrade on Friday. this caused calls going to the solution center and 2 lines in the OCC to fail when called. <I> **** Actions Taken **** Upgraded the Contact Center Server to a supported version to bring services back on line.
399132 | CR | 20190916 |  | 3 | Reactor Water Co-60 Increase | N | N |  | N | NO | <D> **** Detailed Description **** Samples on 9/10/19 and 9/12/19 indicated a two to threefold increase in Co-60 concentration in the reactor water. No evidence of a sample line upset or other cause has been identified. Latest samples show a trend down to previous values. <I> **** Actions Taken **** Informed supervision, sought potential causes, resampled, documented in CR. Recommend assign to chemistry to trend.
399135 | CR | 20190916 | CAQ | C | WMA-CC-51B1 Obstructed Tube found During Inspection | Y | N |  | N | YES | <D> **** Detailed Description **** During the borescopic inspection of the inlet and outlet headers of WMA-CC-51B1 per WO 02115806, one tube was found with a piece of debris lodged in it. The location was on the inlet header for the lower WMA-CC-51B1. All other tubes were clear of debris and appeared clean with very little fouling. Recommended that the craft perform a reverse flush to remove the debris. <I> **** Actions Taken **** Contacted the shift manager and my supervisor to inform them of this information. <N> A reverse flush was performed on WMA-CC-51B1. The inspection of the lower coil inlet after the backflush showed the 5th tube from the bottom still had the debris in it. Engineering recommended trying to dislodge the debris with a curved piece of tubing. This was effective in dislodging the debris. To ensure none of the debris was pushed farther into the tube than what we could see with the borescope, we recommended maintenance perform another backflush. Following the second backflush, both inlet and outlet headers on the lower coil were inspected with no debris blocking any of the tubes. Both headers were clean and ready to have the anodes re-installed. | 02-00-WMA-CC-51B1
399138 | CR | 20190916 |  | 3 | CVI DWGs incorrectly indicate EMS 30034 applicability |  |  |  | N | YES | <D> **** Detailed Description **** AED PRC 30034 R0 (i.e., Equipment Modification Specification (EMS) 30034 R0) page 005 has the specific listing of Walworth valve EPNs to which the EMS is appliable. See the pdf of EMS 30034 R0 pg 005 attached to the EDMS of this AR CR 399138. This EMS is not applicable to any other EPNs unless it is revised to include additional EPNs per DES-2-5. EC ADOC 10308 updated CVI DWG 43-00,20 (NOTE 1) to indicate EMS 30034 was applicable for EPNs COND-V-147A(B) but the EMS does not currently indicate it is applicable to these EPNs. NOTE 1 should be removed from CVI DWG 43-00,20. EC ADOC 10308 updated CVI DWG 43-00,32,1 (NOTE 1) to indicate EMS 30034 was applicable for EPNs COND-V-120A (B,C) but the EMS does not currently indicate it is applicable to these EPNs. NOTE 1 should be removed from CVI DWG 43-00,32,1. EC ADOC 10308 updated CVI DWG 43-00,76 to indicate EMS 30034 was applicable for EPNs COND-V-117A(B,C) but the EMS does not currently indicate it is applicable to these EPNs. CVI DWG 43-00,76 should be updated to remove the incorrect information indicating EMS 30034 is applicable to the drawing. <I> **** Actions Taken **** Recommended cancellation of WRs initiated as part of AR CR 399060 to implement EMS 30034 on COND-V-117A(B,C) and on COND-V-120A(B,C). The WRs cannot be implemented as the existing EMS is not actually applicable to these EPNs. | 02-00-COND-V-117A,02-00-COND-V-117B,02-00-COND-V-117C,02-00-COND-V-120A,02-00-COND-V-120B,02-00-COND-V-120C,02-00-COND-V-147A,02-00-COND-V-147B
399139 | CR | 20190916 |  | 3 | CVI DWG indicate handwheels but depict chainwheels |  |  |  | N | YES | <D> **** Detailed Description **** As part of AR CR 399060, it was identified that CVI DWG 43-00,76, CVI DWG 43-00,32,1 and CVI OMM 43-00,124 had discrepancies regarding handwheels or chainwheels existing for COND-V-117A(B,C) and COND-V-120A(B,C). Handwheels exist in the field for these EPNs and the drawings state there are handwheels but the drawings still depict chainwheels. Handwheels and chainwheels are physically different in appearance. What is drawn on the drawing is in conflict with what is stated on the drawing. CVI DWG 43-00,17 and CVI DWG 43-00,20 also indicate handwheels are installed at HD-V-2A(B,C,D) and at COND-V-147A(B) but chainwheels are depicted by the drawing. Likely also an issue for CVI OMM 43-00,124 and these EPNs. <I> **** Actions Taken **** This issue was discovered as part of investigation for AR CR 399060 that also lead to initiation of AR CR 399138. The additional drawings were also updated as part of EC ADOC 10308. | 02-00-COND-V-147A,02-00-COND-V-147B,02-00-HD-V-2A,02-00-HD-V-2B,02-00-HD-V-2C,02-00-HD-V-2D
399140 | CR | 20190916 | CAQ | D | TR-S B phase voltage out of spec low | Y | N |  | N | YES | <D> **** Detailed Description **** The H13-P800 volt meter for TR-S B phase has previously been written up for reading lower than A & C phases. During an Off-site power alignment check due to DG2 inoperability, it was identified that B phase was reading out of spec low at 234 KV (spec is GE 235Kv). BPA Munro reported voltage at 238KV. The MCR meter reading is not a 'pounded step,' however it is used to check for an open phase on the transformer. Recommend calibration of the instrument. <I> **** Actions Taken **** Informed CRS, completed OSP-ELEC-W101 for TS required action. | 02-00-E-VM-230KV/B
399141 | CR | 20190916 |  | 4 | CAS-F-19A Leak | N | N |  | N | YES | <D> **** Detailed Description **** There is a minor leak from CAS-F-19A. The operability of the CAS system is not in jeopardy. See attached video. <I> **** Actions Taken **** Informed MCR | 02-00-CAS-F-19A
399142 | CR | 20190916 |  | 4 | H2-PS-1 low temp flashing | N | N |  | N | YES | <D> **** Detailed Description **** The low temp light is flashing on the heat trace panel for H2-PS-1. This was noticed on rounds after exiting from warm weather ops. | 02-00-H2-PS-1
399144 | CR | 20190917 |  | 3 | CF-PI-301 IMDS does not match replacement parts | N | N |  | N | YES | <D> **** Detailed Description **** The BOM for CF-PI-301 has a 0-160 psig gage, which was ordered to be calibrated and replaced under 02112762. The IMDS for this EPN has a 0-200 psig range. Need engineering to revise IMDS or identify a suitable replacement gage for this application. <I> **** Actions Taken **** Discussed with EFIN supervisor. Initiated CR. ..... Per discussion with EFIN supervisor and after reviewing the work order instructions , the 0-160 psig gage is appropriate for the application and the IMDS will be updated following installation of the new gage. Recommend this AR goes to engineering for IMDS revision following gage installation. | 02-00-CF-PI-301
399146 | CR | 20190917 |  | 4 | This CR is to document that a craft supervisor was pulled fr |  |  |  | N | NO | <D> **** Detailed Description **** This CR is to document that a craft supervisor was pulled from training to support maintenance shop activities. The maintenance shop would be down multiple supervisors and it was determined the craft supervisor was needed to support the remaining SW window work. Plant General Managerâ€™s permission was obtained for the supervisor not to attend training. The training class was EL 000509/510 Greyboot/ Raychem. <I> **** Actions Taken **** Initiated CR to document missed training. Obtained Plant Managers permission to not attend training. <N> The class was for Electricians, the supervisor was not required to attend the class and does not need to attend the class for qualification.
399147 | CR | 20190917 | CAQ | C | Evacuation route changes needed? |  |  |  | N | NO | <D> **** Detailed Description **** Signs on Rte 4 S show that the turnoff for George Washington Way is being closed permanently on 10/1/19. Need to revise any site evacuation maps/plans to reflect any changes based on this road closure. Should also provide a sitewide communication of these changes as well. <I> **** Actions Taken **** Initiated CR, forwarded to EP manager
399148 | CR | 20190917 | CAQ | D | 2 Pieces of M&TE Suspended/ Lost |  |  |  | N | NO | <D> **** Detailed Description **** 2 Pieces of Clean M&TE were checked out 5/1/19. No job entered- Bad entry of the individual in computer. Never Returned. No Activity in Portal J. Calcode #45501 Fluke DMM- model 87. DEF #7315A written. Calcode #45503 Fluke Clamp-On Ammeter- model 80I-600. DEF #7316A written. Suspended/ Lost. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
399149 | CR | 20190917 |  | 3 | SOP-FPC-DEMIN needs update |  |  |  | N | NO | <D> **** Detailed Description **** When returning FPC-DM-1A/1B to service SOP-FPC-DEMIN (sections 5.1 and 5.2) currently only has FPV-FCV-15A/B being verified in AUTO if FPC-FIC-15A/B is verified in AUTO. If you leave FPC-FIC-15A/B in manual (which is desired sometimes) the procedure doesnâ€™t have you verify FPV-FCV-15A in AUTO (which is always desired). Reference sections 5.5.6 and 5.6.6 which address this concern. AFTER 5.1.9 add step VERIFY FPV-FCV-15A in AUTO. AFTER 5.2.8 add step VERIFY FPV-FCV-15B in AUTO.
399151 | CR | 20190917 |  | 4 | APEL Tenant Wasp Sting |  |  |  | N | NO | <D> **** Detailed Description **** On September 16th, 2019, an APEL tenant was stung by a wasp on the East side of the building. <I> **** Actions Taken **** Facilities contacted to replace full wasp traps. This CR is for trending purposes.
399155 | CR | 20190917 |  | 4 | MANS notification not performed on downpower to 95% 9/13/19 |  |  |  | N | NO | <D> **** Detailed Description **** During the downpower to 95% on 9/13/19 Operations crews did not perform a MANS notification, and rather used the WCI09 management text to notify staff of the event. Disposition to Ops Crew Manager. <I> **** Actions Taken **** Coached on expectations. Initiated CR.
399156 | CR | 20190917 | CAQ | D | screw found in bottom of SW-CNTR-P/1B during FME inspection | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of WO # 02111470-01, electricians opened the door to SW-CNTR-P/1B to measure voltage and current on SW-M/P-1B heater circuit, on the contactor. As part of the FME inspection, prior to closing the panel door, craft noticed a screw and insulating washer/bushing laying in the bottom of the panel. Craft removed the screw and took a picture to identify the potential location of where the screw likely belongs. <I> **** Actions Taken **** Notified Supervision Write CR and WR <N> **** Equipment Description **** SW-CNTR-P/1B SWPH-B . Motor heaters are required for long-term motor reliability to remove moisture. They are NOT SR and are powered from non-SR power. From the motor CCER: "Space heaters will not have an impact on the motors capability of performing safety functions. Engineetring has no operabilty concerns, but the contactor should be repaired at the earliest opportunity.
399159 | CR | 20190917 | CAQ | D | Incorrect image uploaded to EC 15791 |  |  |  | N | NO | <D> **** Detailed Description **** This is a documentation only. The Procurement Specification Deviation (PSD) performed under EC 15791for TMU pump refurbishment does not contain the correct image (EDMS) for the change described in AR 349374. The approved PSD can be found in the EDMS of AR 349374. The image for PSD 16820 appears to have been uploaded to EC 15791 in error. Please upload the approved PSD under AR 349347 to the EDMS of EC 15791 and remove PSD 16820. Note: EC 16820 contains the correct image and does not require any change. <N> The proper PSD was placed in the EDMS of EC 15791. No further action required.
399162 | CR | 20190917 | CAQ | D | FP-P-2B seal water pressure low | N | Y |  | N | YES | <D> **** Detailed Description **** FP-P-2B seal water pressure low | 02-00-FP-P-2B
399167 | CR | 20190917 |  | 4 | HSSF not communicating with vendor | N | N |  | N | YES | <D> **** Detailed Description **** Vendor called this morning and reported that our HSSF station has not communicated any hydrogen or nitrogen levels to their system in the past 2 days. Vendor phone # (908) 328-9683. <I> **** Actions Taken **** OPS 4 walked down HSSF and did not note anything abnormal, establishing a temp log if necessary | 02-00-HSSF-TK-1,02-00-HSSF-TK-2
399170 | CR | 20190917 | CAQ | C | (NRC) Fire doors D-DOOR-D104 and D-DOOR-D107 | N | Y |  | N | YES | <D> **** Detailed Description **** Fire doors D-DOOR-D104 and D-DOOR-D107 require assistance to close and may not be in compliance with NFPA 80. PPM 15.1.2, FIre Door Operability Surveillance, states "Door may not fully close due to air-imbalance; however, not a procedure failure since equipped with strobe light.". This may not be in accordance with NFPA 80 requirements for door closure. Based on the current requirements in PPM 15.1.2, both fire doors are functional. <I> Recommend adding a reference to the FSAR code deviaitons in PPM 15.1.2 reference section to help clarify the requirement. | 02-00-D-DOOR-D104,02-00-D-DOOR-D107
399177 | CR | 20190917 |  | 3 | Housekeeping T471E Backseat Cart |  |  |  | N | NO | <D> **** Detailed Description **** Two valve backseat carts staged in storage location designed for one single cart. One of the carts has been staged and is broken for over two years, necessitating using the 2nd cart for plant needs. Assign to Electrical Maintenance to remove one of the two carts to restore the area to housekeeping standards. <I> **** Actions Taken **** Notified work owner. <N> WR 29151869 written to remove one backseating cart or identify this storage location is for two.
399180 | CR | 20190917 |  | 3 | WEA-FN-25 inadequate walkdown, planning, and scope issues |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During implementation of WO 02134942-01 Replace Scroll Vacuum Pump (SHELL), work instructions were discovered to be inadequate for the scope of work (inadequate walkdown, planning). It was determined that rather than replace just the pump the entire assembly would be replaced which included the motor. The task was now planned to do a determ/reterm to remove the old and install the new assembly. (Scope) It was missed during this scope/planning revision that other electrical tasks per PPM 10.25.116 â€œTesting of AC Motors, Controls and Generatorsâ€ needed to be performed prior to installation because it was a new motor. The decision was made that the package then needed to be revised again to just replace the pump. (Scope) The true scope of this preventative maintenance (PMID 13173-05) for this piece of equipment needs to be determined and the model work order changed to reflect it. . Recommend assignment to planning/engineering to determine true scope and model work order updated. <I> **** Actions Taken **** Notified OCC WWM, Operations, planning, and initiated this CR. <N> Model work order has been updated as required.
399189 | CR | 20190917 |  | 3 | EMS 30034 implementation for RFW-V-106A(B) and RFW-V-107A(B) | N | N |  | N | YES | <D> **** Detailed Description **** Station response to AR CR 191338 (HD-V-10A Handwheel fell off when craft went to operate it) included initiattion of WRs for implementation of EMS 30034 (AED PRC 30034) on the handwheels for RFW-V-106A, RFW-V-106B, RFW-V-107A, and RFW-V-107B (SELF AS 194716-05). EMS 30034 was subsequently implemented at RFW-V-106A and RFW-V-106B via WO 01078400 which also replaced the original chainwheel at these valves with a regular handwheel and a bolt-on aftermarket chainwheel adapter. Unfortunately, EMS 30034 is not applicable to RFW-V-106A or RFW-V-106B (these EPNs are not listed on page 005 of the current R0 EMS). Additionally, CVI DWG 43-00,92 and CVI OMM 43-00,124 were not updated to reflect the chainwheel configuration change to handwheel plus chainwheel adapter. Suggest permanent accept as-is disposition for these legacy configuration changes at RFW-V-106A and RFW-V-106B. EMS 30034 is applicable to RFW-V-107A and RFW-V-107B but the EMS has not yet been implemented at either of these EPNs. WO 01171961 for RFW-V-107A was CANCELED (due to "old Work Order and project number". and WO 01171960 remains an unworked and unscheduled R00 outage Work Order. Because it is a safety issue to prevent repeat of an actual failure at Columbia for a similar valve (HD-V-10A), EMS 30034 should be implemented at RFW-V-107A and at RFW-V-107B. <I> The WO associated with WR 29151641 for RFW-V-107A should be considered for R25 (RP25). The existing R00 WO for RFW-V-107B (WO 01171960) should als be considered for R25 (change from R00 to RP25). | 02-00-RFW-V-106A,02-00-RFW-V-106B,02-00-RFW-V-107A,02-00-RFW-V-107B
399192 | CR | 20190917 |  | 4 | HP exceeded August Dose budget. |  |  |  | N | NO | <D> **** Detailed Description **** RP exceeded their dose goal in August by 42 p-mrem. HP techs accumulated a total of 43 p-mrem of approved â€˜EMERGENTâ€™ dose during the month. Three entries into the LHRA TG 501â€™ at 100% Rx power expended 39 p-mrem. This was in support of WR 29151080 (â€˜BEARING 4 PEDESTAL VIBRATION INDEPENDENT READINGSâ€™ for 6 p-mrem), WR 2915131 5(â€˜INVESTIGATE ELECTRICAL THERMOCOUPLE CONNECTIONSâ€™ for 17 p-mrem) and WR 29151164 (â€˜Indication issue on HV-V-31Aâ€™ for 16 p-mrem). An additional 4 p-mrem was expended supporting Laborers to clean or replace a High Alarm Probe in the RW 437â€™ NUPAC Cage LHRA. <I> **** Actions Taken **** Documented CR. Informed RW Shipping Supervisor and HP/CHEM CIC.
399194 | CR | 20190917 | CAQ | C | WMA-RLY-TK/FN51B, 52B mounting requirements | Y | N |  | N | YES | <D> **** Detailed Description **** While performing WO 02124615-01 craft noted that the two relays were mounting with 2 screws. They are used to see these type relays mounted with 4 screws (like the DG relays). They want to ensure this is adequite and have information in the relays PM noting that two screw are adiquit so that it is not questioned each time a PM is performed. | 02-00-WMA-RLY-TK/FN51B,02-00-WMA-RLY-TK/FN52B
399195 | CR | 20190917 |  | 3 | change title on model WOfor WO 02139113-02 |  |  |  | N | NO | <D> **** Detailed Description **** change title on model WOfor WO 02139113-02. add (Jan, Apr, Jul, Oct), so it is visible on which months the vibs are required for OSP-WMA-M702.
399196 | CR | 20190917 |  | 4 | Deficiencies/Gaps Identified within the FME program |  |  |  | N | NO | <D> **** Detailed Description **** A negative trend/ deficiencies/ gaps in FME behaviors has been identified for the past two outages. The past two outages have seen an increasing trend in FME events. The station is performing well in regards to the FME performance indicator and FME observations while the plant is online, but performance has regressed when compared to performance prior to R-22. This is due to two threats that were identified during R-23, and one threat identified during R-24. R-23 scored 27 points within the FME performance indicator. R-24 scored 32 within the FME performance indicator. This is significant considering less outage scope was conducted during R-23 in comparison to R-22. R24 scored 28 points within the FME performance indicator. Performance has regressed when compared to performance prior to R-22. This is due to two threats that were identified during R-23, and one threat identified during R-24. R-23 scored 27 points within the FME performance indicator. R-24 scored 32 within the FME performance indicator. This trend coincides with the loss of FME training during in-processing due to efficiency bulletin 16-26c which was implemented prior to R-23. <I> **** Actions Taken **** Gap analyses have been performed on FME monitor training, FME worker training, EPRI foreign material hand book, and INPO 07-008. A review of the effects of Efficiency bulletin 16-26c on the FME program has been conducted. A common cause has been conducted on all FME events that occurred during R-24. A review of all observations associated with the FME program has been conducted and trended. Corrective actions are being implemented/ or considered under AR# 398352, AR# 397422, AR# 388645, and AR# 00400921. Author recommends a Non-CAQ severity level 4 due to actions taken.
399197 | CR | 20190917 |  | 3 | FP-PS-7 has wrong alarm drop on IMDS |  |  |  | N | NO | <D> **** Detailed Description **** while performing WO# 02118461-01 FP-PS-7 calibration, it was discovered the work instruction and IMDS had the wrong alarm drop in the control room. IMDS says it is drop 18 -2, it is actually drop 11-2. I believe the panel was upgraded some time ago and our IMDS was not revised at that time. <I> **** Actions Taken **** reported it to my supervisor and wrote this CR.
399199 | CR | 20190917 | CAQ | C | Vendor Calculation given two different CVI CAL numbers. |  |  |  | N | NO | <D> **** Detailed Description **** NAI Vendor GOTHIC Calculation, NAI-1721-001 R0, was given two different CVI CAL numbers: CVI CAL 1097-00,5 R0 and also CVI CAL 1201-00,1 R0. . Additional Details: As part of the RWCU Project and the Hardened Containment Vent (HCV) Phase 2 Project, various GOTHIC calculations were reviewed and cross-referenced. It was discovered that a NAI Vendor GOTHIC Calculation (NAI-1721-001 R0, GOTHIC Analysis of CGS Radwaste Building Response) was given two different CVI CAL numbers: CVI CAL 1097-00,5 R0 and also CVI CAL 1201-00,1 R0 (both ACTIVE Status in Asset Suite). . Calculation CVI CAL 1097-00,5 R0 has not been referenced by other EN Documents (based on no documents in Documents button for this calculation in Asset Suite). . Calculation CVI CAL 1201-00,1 contains the three revisions that the vendor, Numerical Applications, Inc. (NAI), performed for this analysis. Thus, CVI CAL 1201-00,1 R0, R1, and R2 all exist correctly in Asset Suite. Further, CVI CAL 1201-00,1 has been referenced by other EN Documents (based on three documents in Documents button for this calculation in Asset Suite). . Recommend changing Status of CVI CAL 1097-00,5 R0 to Historical, Void, or Superseded, etc. . This CR is administrative in nature, all other NAI Vendor GOTHIC Calculations had unique CVI CAL numbers. <I> **** Actions Taken **** Informed Supervision, called Control Room, and developed spreadsheet which cross-referenced all the NAI Calculations to CVI CAL calculations and determined all other NAI Vendor GOTHIC Calculations had unique CVI CAL numbers. <N> The discrepancy between NAI Vendor GOTHIC Calculation, NAI -1721-001 R0 and the CVI CAL numbers described in this CR have been corrected. . Revision 1 of CVI CAL 1097-00,5 was created in order to be superceded by CVI CAL 1201-00,1 R3. CVI-CAL 1097-00,5, rev 1 was shown as superseded in Asset Suite on 10/29/19. . Revision 3 of CVI CAL 1201-00,1 was created only to indicate that it is the Superseding Document for CVI CAL 1097-00,5 R1. CVI-CAL 1201-00,1 rev 3 was issued in Asset Suite on 10/29/19. . The calculations have now been uploaded into Asset Suite as of 11-5-19. . No further actions are required. The parent AR-CR is now closed. .
399200 | CR | 20190917 |  | 4 | (Safety Issue) Several hazards identified near CF-Tanks |  |  |  | N | NO | <D> While maintenance was being performed near the CF-Tanks multiple safety issues were identified. One of the sets of stairs that access the top of the concrete pad are missing handrail and also has two studs that sreate a tripping hazard. the handrail is very inconsistent and seems to be missing in several places. Reccomend <I> Contacted the Project Manager that had the roleinstalled the skid, Generated a CR/WR <N> skid near CF-tanks ... CR at INPROG. Approved CR, moved to SRO for OPS Review.
399203 | CR | 20190917 | CAQ | D | SW-LI-1A reading one foot higher than it should be | Y | N |  | N | YES | <D> **** Detailed Description **** SW-LI-1A reading one foot higher than it should be resulting in a false spray pond â€œAâ€ level high alarm. This happened after running SW-P-1B by itself which raised level in spray pond "A". After all SW pumps were secured and level equalized the alarm remained in. | 02-00-SW-LS-1A1
399204 | CR | 20190917 |  | 3 | Documentation for COND-V-107C, 129, and 167 needs updating |  |  |  | N | YES | <D> **** Detailed Description **** AED PRC 30034 R0 (EMS 30034) is applicable to a particular set of Walworth valves with E-I-M operators only. Earlier, it was identified that the operators at COND-V-107C and COND-V-167 were not E-I-M operators (they are Crane Converto-Gear operators). Although CVI DWG 43-00,51 and CVI DWG 43-00,114 were updated to correct the identified operator change, AED PRC 30034 R0 was not updated to remove COND-V-107C or COND-V-167 from page 005 of the document. Today, it was identified that the operator currently existing at COND-V-129 is also something other than the E-I-M operator currently indicated on CVI DWG 43-00,31. Photos are attached to the EDMS of this AR CR 399204. The existing operator for COND-V-129 should be as-built for update of CVI DWG 43-00,31 (possibly also CVI OMM 43-00,124) and AED PRC 30034 R0 pg 005 should also be updated to delete applicability to EPN COND-V-129. This is an administrative issue only - there is no impact upon continued function or operation for these EPNs or their associated systems. The discrepancy for COND-V-129 appears to have been noted as part of SELF AS 194716-03 but does not appear to have been entered into CAP at that time for resolution. | 02-00-COND-V-107C,02-00-COND-V-129,02-00-COND-V-167
399205 | CR | 20190917 |  | 4 | TSW-TI-10 missing EPN tag | N | N |  | N | YES | <D> **** Detailed Description **** The EPN tag for TSW-TI-10 has fallen off. Please reattach or generate/install a new EPN label. | 02-00-TSW-TI-10
399206 | CR | 20190917 | CAQ | D | Minor collision with building 600 during training |  |  |  | N | YES | <D> **** Detailed Description **** During training with the B5B and flex equipment; a minor collision occurred between the B5B trailer and building 600. The building 600 door frame sustained minor damage. The B5B and flex equipment sustained no apparent damage. <I> **** Actions Taken **** Informed the Main Control Room and initiated a minor fact finding Completed OI-34 for minor fact finding. No damage was identified to the FLEX equipment. <N> **** Equipment Description **** Buildling 600
399208 | CR | 20190917 |  | 4 | Abnormal CW A bay level indication | N | N |  | N | YES | <D> **** Detailed Description **** eDNA point ENW.CGS.L086 has shown signs of degradation, with increasing periods of inaccurate bay level. Plot in EDMS. This appears to be an indication issue. CW bay levels and TMU flow have been relatively stable during this time. Please investigate and repair. | 02-00-CW-LT-4
399210 | CR | 20190917 | CAQ | C | Wall damaged in Bldg 600 during training exercise | N | Y |  | N | NO | <D> **** Detailed Description **** During NLO Training Cycle 19-4 a refresher on EDMG was presented, which included a hands-on training session of B5B and FLEX equipment. Part of the hands-on session provided the NLOs with an exercise where the B5B Trailer in Building 600 is maneuvered using the dump truck also stored in that building. Trainees took turns as either the driver or as a spotter to gain experience with both roles. These actions would be required under procedures such as ABN-FSG-02 and are expected to be performed by NLOs. This training was conducted by request and in accordance with SOP-FLEX-HITCH-OPS-QC. The FLEX Engineer was consulted regarding the training and permission was requested from the MCR before moving any equipment. Prior to the brief, a walk down of the equipment was conducted. The brief explained the purpose of the training and the details of the exercise including spotter duties and responsibilities. Four spotters were used while the first driver attempted to move the trailer from its storage location (one lead spotter at the front driverâ€™s side position and three additional spotters at each corner). As the trailer was being moved a ladder support bracket, protruding approximately one foot on the driverâ€™s side contacted the corner of the storage room wall near the roll-up door opening. The truck was stopped and the wall suffered only minor cosmetic damage. No FLEX Equipment was damaged and the roll-up door was untouched. No supervisor was present during execution of this training. The MCR and FLEX Engineer were informed of the incident. Pictures are located in EDMS. <I> **** Actions Taken **** Informed the MCR and Flex Engineer. Conducted stand down with trainees and generated the CR
399211 | CR | 20190917 |  | 3 | Degraded SCW-P-2 pump discharge pressure | N | N |  | N | YES | <D> **** Detailed Description **** Received P820.B3 drop 1-5 "STATOR COIL WTR STBY PUMP AUTO START", 3-6 "STATOR COIL WTR dP HIGH", and 5-4 "STATOR COIL WTR/H2 dP LOW". OPS 3 was dispatched and found both SCW pumps to be running. SCW-P-2 was the running pump and SCW-P-1 auto started. Leak check and piping inspection was performed and no leaks were reported. With both pumps running, SCW-P-2 discharge pressure was 60# and SCW-P-1 discharge pressure was 110#. SCW-P-2 was secured. SCW-P-1 remains running and all SCW alarms are cleared with system parameters being normal. <I> **** Actions Taken **** Initiated CR and WR SCW-P-1 remains running with system parameters normal Notified CRS and SM. <N> **** Equipment Description **** TB 441 West | 02-00-SCW-P-2
399212 | CR | 20190918 |  | 4 | HTP-FP-6 24F low temp flashing | N | N |  | N | YES | <D> **** Detailed Description **** Low temp light is flashing for 24 F (PWC-SEC-10). Outside conditions are in the mid 60s F. <I> **** Actions Taken **** Noted in logs. | 02-00-HT-HTP-FP/6
399213 | CR | 20190918 |  | 4 | HT-HTP-FP/6/1 power lights for 50F and 51F dont work | N | N |  | N | YES | <D> **** Detailed Description **** Lights for 50F and 51F Power On do not work. Light bulbs instantly blow. When pressing lamp check all other lights light up. <I> **** Actions Taken **** Found light bulbs missing, attempted to replace to have them instantly blow. Annotated in logs. | 02-00-HT-HTP-FP/6/1
399214 | CR | 20190918 |  | 4 | SEC-MDET-3 failed nightly testing | N | N |  | N | YES | <D> **** Detailed Description **** SEC-MDET-3 Failed its nightly operability test <I> **** Actions Taken **** Unit was removed from service; CR/WR Generated | 02-00-SEC-MDET-3
399215 | CR | 20190918 |  | 4 | CW pH meter disagrees with grab sample >0.20 pH units | N | Y |  | N | YES | <C> MRT Change: CR 399215 moved from CAQ Severity D/Trend Repair to NON-CAQ Severity 4/Trend Repair. <D> **** Detailed Description **** CW pH meter ENW.CGS.F141, circ water b/d npdes ph limit, meter which is used to automatically control acid injection to cw disagrees with grab sample results by 0.26 pH units (the meter is under-responding). This exceeds our control limit of 0.20 pH units for I C to perform a pH meter calibration. As this meter is used to perform automatic adjustments it is important to have it as accurate as possible. The meter is still functional and is responding to changes in pH; it can still perform its automatic features currently, however, the discrepancy should be addressed. <I> **** Actions Taken **** CRS/SM informed. Chem supervisor/specialist notified. | 02-00-CW-PHITS-1
399220 | CR | 20190918 |  | 4 | CAS-C-1C not maintaining system pressure above 100# | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1C was started in support of SA-C-1 maintenance. CAS pressure as read on CAS-PI-1 was initially 106#. After 40 min, CAS system pressure was at 100.5#. CAS-C-1A was started and CAS-C-1C was secured and placed in standby. CAS-C-1C needs pressure adjustment to maintain normal system operating parameters. <I> **** Actions Taken **** Notified CRS Initiated CR Started CAS-C-1A and placed CAS-C-1C in standby <N> **** Equipment Description **** tb 441 | 02-00-CAS-C-1C
399221 | CR | 20190918 |  | 4 | CAS-C-1A and 1B maintaining system pressure around 100# | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1A, 1B, and 1C have all been started since securing SA-C-1 in support of maintenance. The combination of CAS -C-1A and 1B and the combination of CAS-C-1C and 1B were struggling in maintaining CAS system pressure at just above 100#. Operators were dispatched to locally inspect the CAS compressors, the piping, and verify no air usage was in-progress. No issues were found. All CAS compressors are running to maintain system pressure above 100# with margin while SA-C-1 is danger tagged out. <I> **** Actions Taken **** Notified CRS Initiated CR and WR <N> **** Equipment Description **** tT 441 | 02-00-CAS-C-1A
399222 | CR | 20190918 |  | 3 | Bldg 54 needs repainting | N | N |  | N | NO | <D> **** Detailed Description **** Building 54 which is located at the intersection of the plant entrance road and main parking lot needs repainting. <I> **** Actions Taken **** wrote cr <N> Close to WR 29151676.
399223 | CR | 20190918 |  | 4 | M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0068369 RAD Dig. Battery Torque Wrench- model DB-RAD 1000-2 Passed Closeout Calibration and is now Suspended until R25. Not used since Cal'd. DEF #7317A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
399226 | CR | 20190918 |  | 3 | Plateau Offering 51363 had wrong start time | N | N |  | N | NO | <D> **** Detailed Description **** Plateau Offering 51363 had wrong start time. MX000379 Chemistry fundamentals had a start time of 7:30 AM. The correct start time was 7:00 AM. Two students were late to class. The D-15 was covered during most of the half hour. Training was not impacted by the students being late. Ensured other offerings had correct start time. <I> **** Actions Taken **** Ensured other offerings had correct start time. Notified Manager and initiated CR
399227 | CR | 20190918 |  | 4 | Simulator Training delayed 30 min due to hardware issue | N | N |  | N | NO | <D> **** Detailed Description **** LR002393 Simulator Scenario was delayed 30 minutes due to a hardware issue (card failure) with the simulator. Issues were resolved and plans have been implemented to ensure no training will be missed.
399228 | CR | 20190918 |  | 3 | Procedure enhancement for 12.14.11 | N | N |  | N | NO | <D> **** Detailed Description **** please change the operability statements on page 6 through 15, per the markup in edms. . A dedicated operator maintains availability, not operability <I> **** Actions Taken **** Wrote CR
399229 | CR | 20190918 |  | 4 | Emergent work on PSR-V-640 delayed due to no High Risk Plan | N | N |  | N | NO | <D> **** Detailed Description **** FIN Team planned on working Emergent WO 02147489 on 09/18/19 but the Clearance Order could not be hung as there was no ALARA Task or High Risk Plan to allow access to scaffold where PSR-V-625 is located. The dose rates at PSR-V-625 are documented as 2800 mrem/hr on Survey # 20190521-11. Entry into dose rates that are GTE 1500 mrem/hr requires a High Risk Plan and Stay Time Keeping as per PPM 11.2.2.12 and Form 26840 R14. <I> **** Actions Taken **** A High Risk Plan has been written, a request for High Risk RWP has been made, and CR documented. FIN now plans to perform this unscheduled repair next week.
399230 | CR | 20190918 |  | 3 | Asset Suite SCSI 3.6 has incorrect REV # Listed. | N | N |  | N | NO | <D> SCSI-3.6 current REV is #9. The document uploaded is the correct REV however the REV # shows as REV # 8 and it should be REV # 9. Assign as a NON CAQ 3 to SCS for action to correct administrative error to AR-SCS. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
399232 | CR | 20190918 |  | 4 | Unable to validate issued green badge | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** When attempting to validate an active badge (in CAS) for an employee, the CAS operator was automatically logged off work station# 2 by the AIM system. The CAS operator restarted the work station, and then attempted the same task on work station #1 and experienced the same result. Access Authorization restarted IEBS 1, ensured all badge tables were correct. Computer engineering and our safeguards and compliance employee both advised to take a new photo of the individual and request another validation from CAS. Once the new photo was captured, CAS was able to view the photo and validate the badge with no further issues. This same issue occured on 12/18/19 (CR#388630). <I> **** Actions Taken **** Emergency Services Mgr and Security Lt. were notified of the issue.
399234 | CR | 20190918 |  | 3 | DUPLICATE TRAINING RECORD SENT TO RECORDS CONTROL | N | N |  | N | NO | <D> **** Detailed Description **** A TRAINING RECORD WAS SUBMITTED TO RECORDS CONTROL AND WHILE RECORDS PERSONNEL WERE PROCESSING THEY RECIEVED AN ERROR THAT THE ETAR NUMBER WAS ALREADY USED. (ALREADY EXISTED IN ASSET SUITE) <I> **** Actions Taken **** NOTIFIED MY LEAD/SUPERVISION. CR WRITTEN. RECORD IS BEING SENT BACK TO OPERATIONS FOR CORRECTIONS AND RESUBMITTAL.
399236 | CR | 20190918 |  | 3 | CF-TK-41 and 42 chemical incompatible with system. | N | N |  | N | NO | <D> **** Detailed Description **** The Nalco product in CF-TK-41 and 42 is incompatible with the stainless steel in the circ water chemical feed system. This is evidenced by the many problems the plant has experienced over the last year with this system. Further evidence is a small piece of stainless tubing that had a through wall leak. When this piece was removed, the inside was black and pitted with severe wall thinning. See picture in EDMS. Also, while performing boroscope inspection of the supply piping from the tanks to the pumps per WR 29151375, etching was noticed on the walls of the piping with some blackening on the walls. See videos in EDMS. When the chemical feed pumps are rebuilt the stainless steel ball check assemblies show minor black pitting. See picture in EDMS. Testing has been performed where Nalco was placed in a stainless tube and placed in a boiling water bath for eight hours. After cooling, the tube was emptied into a clean container and the Nalco had gone from a light yellow to a dark green. Another test was performed where the Nalco was just kept inside the stainless tubing for 24 hours at room temperature and the color changed from light yellow to light green. See pictures in EDMS. About the time that the problems with the pumps began the Nalco composition was changed from a 2:1 ratio to a 3:1 ratio. Prior to this change the degree of problems with the pumps was significantly less. Please work with the vendor to identify a scale inhibitor product that is compatible with our system materials. <I> **** Actions Taken **** Informed supervision, engineering and chemistry.
399238 | CR | 20190918 | CAQ | D | SEIS-SMA-3 failed test pulse signal test | N | Y |  | N | YES | <D> **** Detailed Description **** During the performance of ISP-SEIS-M202 WO 02145195-01 SEIS-SMA-3 (MR6) free field unit failed its test pulse signal test. There is currently a warning light for MR6 illuminated on the control room panel. MR6 should still function normally with this degraded condition. <I> **** Actions Taken **** Notified Ops, Engineering and Supervison | 02-00-SEIS-SMA-3
399241 | CR | 20190918 |  | 3 | EWP would not open 0215042501 COND-LCV-11 Job on tablet | N | N |  | N | NO | <D> **** Detailed Description **** Tried to perform 0215042501 COND-LCV-11 Valve on EWP and would not open. The error â€œcheck out error 400â€ would display. Tried to validate package on tablet and desktop. The problem added total of 2hrs to the job. Could not resolve issue. The job was successfully performed on paper. <I> **** Actions Taken **** Had CRS and SM assist Contacted Supervisor to assist <N> When "check out error 400" is received and prevents a package being checked out onto a tablet it is due to Microsoft special characters, such as dashes, double quotes and single quote. This happens due to copy and pasting contents from a word document. . In order to check packages out onto a tablet, go into Asset Suite on the details panel and type over any special character and then validate in DataGlance. If unable to update, the package can be returned to planner for editing. . Also, the package can be printed and worked on paper. Once the work is completed, the hard copy can be scanned and attached to the Edit panel in DataGlance. . WO Tasks have been updated.
399245 | CR | 20190918 | CAQ | D | Front End Loader FLEX-VEH-2 is Non-functional | N | Y |  | N | YES | <D> **** Detailed Description **** While performing the FLEX Debris Removal Equipment training session the front end loader (FLEX-VEH-2) had intermittent issues. When the loader was operating in Reverse it would intermittently shift back to Neutral. This condition results in FLEX-VEH-2 being Non-functional. Error codes from the display were noted to assist in the vender assisted troubleshooting. FLEX-VEH-2 was driven to Building 183 to have scheduled Preventative Maintenance and troubleshooting performed. The vendor (John Deere) has been contacted and the problem appears to be with the shifter rocker switch based on the symptoms. Facilities mechanics will have the replacement part tonight and will begin replacement tomorrow. <I> **** Actions Taken **** Contacted my Supervisor and the Shift Manager. The excavator (FLEX-VEH-1) is currently being staged at the FLEX Debris Removal Equipment training area across from the evaporation ponds located East of the plant. With FLEX -VEH-1 Functional but unprotected and FLEX-VEH-2 Non -Functional and unprotected LCS 1.11.1 directs that we have 45 days to restore one of the credited debris removal vehicles to Functional and protected status. <N> **** Equipment Description **** FLEX-VEH- is currently in Building 183 (Automotive Shop) Normal storage location is Building 600. | 02-CM-FLEX-VEH-2
399246 | CR | 20190918 |  | 3 | Yakima Building 27 Fire Sprinkler Hanger Deficiencies Found | N | Y |  | N | YES | <D> **** Detailed Description **** Inspection of the fire sprinkler piping and hangers in the overhead above the ceiling in the Yamika 4 conference room found multiple examples of unauthorized sprinkler piping hangers AND many examples of electrical and communications wires attached or lying on fire sprinkler piping. These conditions are not allowed by NFPA 13, the Fire Sprinkler Standard. The Standard does not allow ANY non-system components to be attached to the piping or hangers. The Standard requires that sprinkler piping hanger components be Listed for the intended purpose, with few exceptions. See pictures in the EDMS section where rope and wire have been used to support sprinkler branch lines. Conduit has been attached to the fire sprinkler piping with scrap electrical wire and zip-ties. Some communication wire has been laid across the sprinkler piping. See work requests written to correct the problems. The Yakima building fire sprinkler system is a PLANT system in accordance with SWP-DES-01. The corrections for the fire sprinkler hangers must come from the Plant maintenance group. <N> **** Equipment Description **** Fire Sprinkler System Wet 12A
399248 | CR | 20190918 | CAQ | D | PPM 16.3.1 WEA-SR-25 failed leak check | N | Y |  | N | YES | <C> MRT Change: CR 399248 moved from 4/Trend Repair to CAQ D/Trend Repair. <D> **** Detailed Description **** During the performance PPM 16.3.1 WEA Low Range Noble Gas Monitor Channel 1 CC/RC step 7.2.13 failed the leak check. Per the work instructions pressure cannot drop greater than 10â€Hg within a 15min waiting period. After the 15min waiting period the pressure dropped to 0â€ Hg. <I> **** Actions Taken **** Per step 7.2.14, notified supervisor and initiated a CR and a WR to repair leaks. <N> **** Equipment Description **** WEA-SR-25 487' RW | 02-00-WEA-SR-25
399249 | CR | 20190918 | CAQ | D | Benton County EOC dialup inoperable | N | Y |  | N | NO | <C> MRT Change: CR 399249 moved from D/Trend Repair to NON-CAQ Severity 4. . After discussion with the EP manager it was decided that this CR is CAQ. <D> **** Detailed Description **** While doing the monthly test on the dialup phones, Benton County would ring no answer. Note: The county can call us on this line. All other means of communication to the county is available. <I> **** Actions Taken **** Notified EP and verified the phone circuit on the EN side is good. We have calls in to the county to fix the issue on their end. All other means of communication to the county is available. Recommend NCAQ 4. Close to WR. <N> **** Equipment Description **** Benton County EOC
399250 | CR | 20190918 |  | 3 | PPM 4.602.A5 Action Requires Update or Invesitgation |  |  |  | N | NO | <D> **** Detailed Description **** During a Licensing Requirement review of ARM-RIS-3 and 3A, a discrepancy was found on 4.602.A5 602.A5 Annunciator Panel Alarms. Under 2-1 NEW FUEL STORAGE AREA RAD HIGH, step 6 calls for Alarm classification per PPM 13.1.1; however, EAL was determined per NE-02-09-12 â€œEmergency Action Levels (EALs) Technical Basis document that ARM -RIS-3 and 3A would not provide adequate indication of radiation levels associated with decreasing water level above irradiated fuel. Therefore the rad detectors were excluded from EALs. ARM-RIS-3 and 3A are also not listed under PPM 13.1.1; therefore, a procedure update will be required for ARP 4.602.A5 602.A5 Annunciator Panel Alarm under Window 2-1 action 6. This CR is administrative in nature. Recommend CR should be assigned to AR-OPSPROC as a 3, NON-CAQ. <I> **** Actions Taken **** Notified Engineering Supervisor and SM
399251 | CR | 20190918 | CAQ | D | Received the "OSCILLOGRAPH STARTED" alarm | N | N |  | N | NO | <D> **** Detailed Description **** Received the "OSCILLOGRAPH STARTED" alarm due to 500KV neutral OC (J7), and 230KV Undervoltage (J15) which have been reset. BPA reports that VANTAGE-SCHULTZ lines relayed off and then back on. Plant Inverters, Hotwell and Feedwater heater controllers and Containment Vacuum Breakers exhibited normal operations. TR-S and TR-B voltages are 237/235/238 kV and 119/119/118 kV <I> **** Actions Taken **** Wrote this AR.
399252 | CR | 20190918 |  | 4 | EMS 30034 implementation for BS and HD system valves | N | N |  | N | YES | <D> **** Detailed Description **** Station response to AR CR 191338 (HD-V-10A Handwheel fell off when craft went to operate it) included initiattion of WRs for implementation of EMS 30034 (AED PRC 30034) on the manual operators for BS-V-3, HD-V-2A(B,C,D), HD-V-4A(B), HD-V-5A(B), HD-V-9A(B,C), and HD-V-10B (see SELF AS 194716-02). However, the Work Orders associated with these WRs were ulitmately CANCELED in 2017 due to age and percieved low priority. Because this appears to be an unaddressed EOC safety issue, this CR is initiated to obtain WRs for RP25 WOs to ensure EMS 30034 is implemented on BS-V-3 and on HD-V-10B. RP25 WOs associated with R25 EC 17515 implementation already exist for HD-V-2A(B,C,D), HD-V-4A(B), HD-V-5A(B), and HD-V-9A(B,C). | 02-00-BS-V-3,02-00-HD-V-10B
399253 | CR | 20190918 | CAQ | C | Broken Ground WIre Discovered During Potable Water Leak Exca | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During potholing to locate the broken potable water piping described in CR 398835 a broken aluminum ground wire was discovered. It appeared to be assocated with the 115kv line nearby. It appears to have been broken for quite some time. <I> **** Actions Taken **** Facilities electrcial engineer was notified and BPA foreman was informed of the discovery. They visited the location and found that it is a ground to the nearby switch platform (B-599). This switch feeds TRB transformer. The foreman installed a temporary jumper and scheduled a permanent repair to be performed the week of September 23rd by BPA linemen. <N> **** Equipment Description **** B-599 that feeds primary side of TRB
399254 | CR | 20190918 | CAQ | D | H2/O2 Analyzer heat trace trouble alarm received | Y | N |  | N | YES | <C> CR reopened to cross reference additional WR 29151592, marked completion required box, then taken back to complete <D> **** Detailed Description **** Received H2/O2 Analyzer heat trace trouble, P814.J1.3-2. Dispatched an operator to investigate. HT-H-SR13/2 was found flashing. HT-TI-30/SR13 and HT-TI-30/SR14 both indicate normal at 115degF. The ARP indicates that low temperature of LT 100degF would cause the alarm. <I> **** Actions Taken **** Initiated CR Notified CRS <N> **** Equipment Description **** heat trace for CMS-SR-13 | 02-00-CMS-SR-13
399255 | CR | 20190918 |  | 3 | Procedure enhancement 12.2.9 CW halogenation |  |  |  | N | NO | <D> **** Detailed Description **** Procedure enhancement for 12.2.9, Circulating and Plant Service Water Halogenation Surveillance: Step 8.1.1 f and Note 2 pg 11 both tell the procedure user to evaluate chlorine every 15 minutes, however, with the new dehalogenation skid this frequency is too high. Both of the previous steps should be modified to "30 min or as directed by chemistry supervision/specialist". All references to CW-PHR-1 for pH level should be replaced with the new dehalogenation skid pH meters (table on pg 19, note 1 on pg 19, att 10.1 pg 22 and 23, and step 8.2.1) The table on attachment 10.1 for CW/TSW chemical injection should either be modified or removed completely as the pumps are now operated automatically. <I> **** Actions Taken **** CRS informed. Chemistry supervisor/specialist notified via email. <N> This procedure is the current procedure and is written for use without a Dehalogenation system, and will be a backup method for Halogenation should the Dehalogenation system fail. PPM 12.2.9 also assumes the Dehalogenation sampling system is not available. A new procedure, PPM 12.2.11, is the procedure that will be used for Halogenation/Dehalogenation once the Dehalogenation system is placed in service.
399256 | CR | 20190918 |  | 4 | SEC-XD-6 is not functioning as designed | N | N |  | N | YES | <D> **** Detailed Description **** SEC-XD-6 is not functioning as designed | 02-00-SEC-XD-6
399257 | CR | 20190919 |  | 3 | E-TR-5NB found in the 'Bypass' mode | N | N |  | N | YES | <C> MRT Change: CR 399257 moved from 4/Trend Repair to Severity 3 assigned to AR-OPSST. <D> **** Detailed Description **** E-TR-5NB found in the 'Bypass' mode, while still supplying power to E-PP-5NB. <I> **** Actions Taken **** Informed MCR <N> This issue is not a misposition or PCSC issue. E-TR-5NB automatically shifted to bypass mode. WR 29151672 will return it to normal or repair as necessary. No further actions required. | 02-00-E-TR-5NB
399258 | CR | 20190919 |  | 4 | 5 Pieces of M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** 5 Fluke True RMS Multimeters- model 187 Passed Closeout Calibrations and are Now Suspended until R25. Not used since Calibrated. No Plant Impact. See list for Calcodes, Descriptions, models and associated DEF #'s. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
399261 | CR | 20190919 | CAQ | C | SWP-CAP-01 Procedure Adherence Failure |  |  |  | N | NO | <D> **** Detailed Description **** Calibration Services, Lead Metrologist-Quality Manager failed to obtain and document appropriate CR extensions in accordance with SWP-CAP-01 for (QA) generated. Cat B CR 391003 assignment-02 & -04. See EDMS for additional notes. AU-CL-19 resulted in CR00391003 for "ENSL Program Deficiency in CC/CAP Implementation" as a Cat B CR and has been extended and the appropriate approval documentation has not been captured. These assignments should have only been on a second extension; however, due to miscommunication the Lead Metrologist and the Owed to Group Manager both extended same assignements using the same approval documentation which caused the reschedules to jump from 1 to 3 within 48 hours. This oversight was identified by Qualtiy Services and not the Owed to Group. <I> **** Actions Taken **** Initiated CR. Addresses assignment -04 of CR 391003 failure to obtain correct extension approval. <N> Requested PGM approval for extension and it was granted. RCH 10/15/19 Thumbs down taken for Missed Committments effective 10/16/19. Received approval from Vice President on 10/9/19.
399263 | CR | 20190919 | CAQ | D | MCC bucket specification 15209 needs revised. |  |  |  | N | NO | <D> **** Detailed Description **** While communicating with the vendor for the spectrum buckets there is concern with the current 15209 specification for purchasing replacement MCC buckets and parts. There are currently over 40 changes to this specification in the form of PSDs that need incorporated into the specification. The current state of this specification makes it difficult for CGS to purchase parts and buckets from each vendor. As part of this process the CGS is required to provide all of the outstanding changes to the vendor so they can review all of the information. Having this many changes makes it difficult for ENW and any vendor to ensure they conform to the specification. It is recommended that this procurement specification be updated as soon as possible so that the part 21 for the spectrum buckets can be resolved in a timely manner (Reference AR-CR 395246 and 398540). This CR was prepared to document the condition of the procurement specification and to increase the priority for updating the specification. This is an administrative issue and it currently has no impact on plant systems. <N> AR 387746-01 is cross referenced and is assigned to revise spec 15209. Two assignments to revise this spec are not needed. This CR should be trended to AR 387746-01.
399265 | CR | 20190919 | CAQ | C | (QA) QA Audit Reports not Reviewed by POC |  |  |  | Y | NO | <D> **** Detailed Description **** The POC requirement to review all QA audit reports at least semiannually was not fulfilled. Factual Basis: 1) SWP-IRP-01 Revision 023 states that POC, â€œReview all audit reports and summary reports of audits at least semiannually to ensure the effectiveness of the oversight process.â€ 2) There is no POC documentation that QA Audit Reports were reviewed at POC between the time period of 11/28/18 to present. 3) This requirement was introduced in SWP-IRP-01 Revision 023 issued 11/28/18. 4) CNSRB reviewed the QA Audit Reports within this time period. 5) The following audits within this time period require POC review: AU-CA-18, AU-CSQ-18, AU-CL-19, AU-EP -19, AU-MN-19, AU-OP TS-19, and AU-SP-19. Copies of these audits are attached. Insights: POC review of QA Audit Reports provides oversite to ensure that Quality requirements are fulfilled. Recommend assignment to AR-POC. <I> **** Actions Taken **** Notified POC Chairman and Supervisor
399267 | CR | 20190919 |  | 4 | 2 Pieces of M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** 2 Proto Torque Wrenches- model 6064C 200in. Passed Closeout Calibration and are Now Suspended until R25. Not used since Calibrated. Calcode #0066442. DEF #7232A written. Calcode #0066444. DEF #7324A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
399270 | CR | 20190919 |  | 4 | Unexcused tardy to scheduled training |  |  |  | N | NO | <D> **** Detailed Description **** Unexcused tardy to scheduled training by a Maintenance Department individual. MX000380 Rx Plant Materials. Trainee arrived at work after the scheduled start time. <I> **** Actions Taken **** Initiated Condition Report and performed actions as outlined in GBP-TQS-01. <N> individual was provided the training he missed during a break . no additional actions necessary.
399299 | CR | 20190919 |  | 3 | Standard found out of tolerance | N | N |  | N | NO | <D> Calcode #0065879 Heise Model ST-2H was found OOT and adjusted. OOT paraneter not used to calibrate other instruments. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review. Documents are uploaded and the review is complete with the recommendation to change the calibration interval to 6 months being implemented. No further actions are required
399300 | CR | 20190919 | CAQ | D | Clearance C-RRC-V-8BDRAIN-002 Needed 50.59 Review |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing clearance C-RRC-V-8BDRAIN-002, It was determined that a 50.59 review should have been completed before the clearance was hung. This clearance contains three caution tags. The first was placed on RRC-RMS-V/16B and states: "Ensure RRC-V-86B and RRC-V-92 are open and routed to an EDR or FDR drain before closing this valve." The other two were placed on RRC-V -86B and RRC-V-92, and both state: "Operate valve to keep RRC-RV-15B from lifting as directed by the CRS." This clearance has been hung and remains in place if needed in the future. Since this activity does not meet the criteria for a temporary modification in support of operations or maintenance, a 50.59 review should have been conducted before the clearance was hung. <I> **** Actions Taken **** Completed AD-19-0569 and 5059SCREEN-19-0117 for this activity. Both are located in the EDMS folder for AR 00398532. <N> The subjaect caution clearance was hung in support of maintenance activities. When the maintenance was completed the plant componenets were restored to normal configuration, but the caution clearance was not removed. The operating crew will remove the caution clearance.
399302 | CR | 20190919 |  | 3 | (QA) MT-CRA-9B Annual Inspection Not Documented |  |  |  | Y | NO | <D> **** Detailed Description **** The Plant Installed Crane/Hoist Inspection Checklist (form 24642) for MT-CRA-9B does not have a current annual inspection documented. The last one recorded was on 2/11/18. Per PPM 10.4.12, Crane, Hoist, Lifting Device and Rigging Program Control rev 032-001, step 7.6.3.e 2) An annual and Preuse Inspection is required if the annual inspection has not been performed in the last 12 months. The annual inspection was performed on 2/14/19, but not documented on the form. However, there are four instances of personnel performing the pre-use inspection after the previous annual inspection expired. This shows a potential lack of sensitivity to the industrial safety implications surrounding crane use. See picture in EDMS. <I> **** Actions Taken **** Initiated CR, informed the respnsible managers.
399303 | CR | 20190919 |  | 3 | Found SCW-V-471 out of position during the calibration | N | N |  | N | YES | <D> **** Detailed Description **** Found SCW-V-471 out of position during the calibration of DPS-15 per WR#29151648. Found SCW-V-471 valve handle position at 12 :00 and repositioned to 01:00 to get it fully close. Per SOP-SCW-LU the required position of SCW -V-471 is 3/4 turn open. Initially SCW-PI-469 indicated 60# and went to 0# after SCW-V-471 position to 3/4 turn open. <I> **** Actions Taken **** SM/CRS informed. Investigate is in progress <N> This valve SCW-V-471 was found "nearly full closed" in the past (in 2012) per CR 00255805, which was added as a cross reference. | 02-00-SCW-V-471
399310 | CR | 20190919 | CAQ | C | SW-M-P/1B Upper Bearing oil temp higher than expected | Y | N |  | N | YES | <C> WR was cancelled because SENSSS took an assignment to evaluate the elevated bearing oil temperature, per email from F. Schill 10/2/2019 <D> **** Detailed Description **** While monitoring SW-M-P/1B parameters due to elevated water content in the upper motor bearing oil reservoir (CR 396335), the SW-M-P/1B upper bearing oil reservoir temperatures have seen a rise in temperature despite Spray pond temperatures, which are used to coil the upper bearing oil, going down. Current Spray Pond Temperatures are ~62Â°F while the upper bearing oil temperature is ~143Â°F. Typically, with spray pond temperatures in the low 60â€™s, upper bearing temperature trends are typically in the mid 130â€™s. SW-M-P/1B has been running for ~29 hours and upper bearing oil temperatures have been stable throughout the duration of the run. Limits from the ODMI for CR 396335 state that: â€¢ If bearing temperature is GTE to 145Â°F, then monitor upper motor thrust bearing temperature (ENW.CGS.WO90) hourly while motor is in operation and initiate WR for I&C to validate calibration of instrumentation. â€¢ If Bearing Temperature is GTE to 150Â°F and rising, then secure the motor, and initiate management bridge call. With Upper bearing oil temperature LT 145 Â°F, no further action is required per the ODMI at this time. All other indications (ie oil sample analysis, vibrations, etc.) do not show any trends that would allude to any significant degradation to the upper motor bearing at this time. With bearing temperatures stable during motor operation and below the limits set by the ODMI, this CR is being written for trending purposes only. <I> **** Actions Taken **** Discussed with Supervisor, Pump/motor Component Engineer, and Shift Manager. | 02-00-SW-M-P/1B
399312 | CR | 20190919 |  | 3 | Datglance overriding completion dates for surveillances |  |  |  | N | NO | <D> **** Detailed Description **** When the date in portal J is generated based on the actual finished date of a work order, dataglance overwrites the completion date to the day the work order is reviewed and closed. This can cause surveillances to be scheduled past the actual late date if the day of review and the day of review closure is in excess of the frequency grace of the surveillance. Example: ISP-FDR/EDR-M401 was finsihed on 9/14/19, verified actual date in portal J matched. Reviewed the surveillance and closed in dataglance on 9/19/19. Portal J completion date changed to 9/19/19 and is greyed out (cannot be changed). <I> **** Actions Taken **** Discussed with eWP supervisor and I&C component Manager wrote CR <N> Asset Suite is working as designed. With the removal of completing the WO Package in Asset Suite, the user no longer has the ability to complete packages in Asset Suite which also gave the user the ability to change the PM Credit Date. There is not a way in DataGlance to change the PM Credit Date. â€œCredit by Critical Taskâ€ will be implemented during the Asset Suite 9 upgrade. So, when the critical task is set to FINISHED, the FINISHED date will used as the PM Credit Date
399314 | CR | 20190919 |  | 3 | (Planning and Eng) PMTâ€™s using 10.25.116 need more detail |  |  |  | N | NO | <D> **** Detailed Description **** PMTâ€™s using 10.25.116 Testing of AC Motors, Controls and Generators need more detail in the WO instructions. Currently most instruction steps use the generic statement of perform PMT testing per 10.25.116 and record on the PMT-E2. There are many steps in the PMT-E2 and most do not apply. Then a step is added for the Supervisor to verify the results are acceptable. With these general statements it leaves the PMT requirement up to the Supervisor that happens to be directing that task and craft. Supervisors do not determine the PMT or acceptable criteria for PMTâ€™s. PMT and acceptance criteria should be determined prior to the scheduled work start. Also Ops cannot adequately review scope of work if it is determined the day work is being performed. The example I have is WO 02122662-04 FPC-42-8A2C1C (FPC-P -2B) TEST AND INSPECT STARTER where the disc was disassembled and reassembled. I believe the PMT for this should be when disc is in the off position there should be no voltage on the load side and voltage when in the on position. Since wires were determed the rotation should be checked to ensure wires were not rolled. This can be performed by equipment rotation checks or process indication. WO 02122662-04 old and proposed new instructions have been added to the EDMS. <N> **** Equipment Description **** .
399315 | CR | 20190919 |  | 3 | (QA) SWP-IRP-02 revision |  |  |  | Y | NO | <D> **** Detailed Description **** As part of Quality Assurance audit preparations, the QA organization identified some legacy verbiage that remains in the procedure. Specifically the procedure was change to include Subcommittee Issue instead of action item. However the review found there we several instances where the wording â€œaction itemâ€ remains in the procedure. <I> **** Actions Taken **** Aligned with QA Supervisor. SWP-IRP-02 should be revised to remove any references to action item. Assignment to CNSRB facilitator in Org Effectiveness group.
399316 | CR | 20190919 |  | 3 | Failed Radio chemistry Environmental crosscheck 1st Qtr 2018 | N | N |  | N | NO | <D> **** Detailed Description **** The value for Chromium 51 was high in comparison to the know value of the of site lab. Every other isotop passed it's cross check. The instrument was recheck and it was still higher but passing. Count room specialist will investigate. <I> **** Actions Taken **** Chemistry Supervision, MCR, Count room specialist notified
399319 | CR | 20190919 | CAQ | D | RHR-P-2B Motor Top Hat Flange Oil Seepage | Y | N |  | N | YES | <C> CR reopened to cross reference additional WO 02150901, marked completion required box, then taken back to complete <D> **** Detailed Description **** During performance of OSP-RHR/IST-Q703 a small amount of oil was discovered to be resting on top of the RHR-P-2B motor. It appeared to have leaked out of the motor top hat flange. Because of the orientation of seepage a drip rate could not be directly determined. It was wiped up upon discovery then wiped again after an hour had elapsed and the oil pads were compared. The oil was discovered after the pump had already been started and run for less than five minutes, and the amount of oil wiped off the top of the motor after an hour of run time was drastically less than what was wiped off when originally discovered. This could be slow seepage over time while not running. Attached is a picture comparing the two oil pads used to wipe up the oil. The left pad is the pad used after an hour of run time, the right pad is the initial wiping upon discovery of the oil. <I> **** Actions Taken **** Informed MCR, cleaned up oil, photographed evidence, initialted AR | 02-00-RHR-P-2B
399320 | CR | 20190919 | CAQ | D | RHR-P-2B Oil Needs Added | Y | N |  | N | YES | <D> **** Detailed Description **** After performing OSP-RHR/IST-Q703, the lower oil level of RHR-P-2B was found to be about 1/8 inch below the standby line on the sight glass. Still meets minimum tech spec limit. Request oil be added. <I> **** Actions Taken **** Informed MCR, initiated AR | 02-00-RHR-P-2B
399322 | CR | 20190919 | CAQ | D | REA-CB-FN1A open light could not be changed. | Y | N |  | N | YES | <D> **** Detailed Description **** Found open light burned out, removed 24E bulb, could not successfully install new bulb. <I> **** Actions Taken **** Informed MCR & SSS. Initiated AR. | 02-00-REA-CB-FN1A
399323 | CR | 20190919 |  | 4 | SM-8 door does not self close. | N | N |  | N | YES | <D> **** Detailed Description **** Found SM8 East door (C-214) door does not self close. Door does latch. <I> **** Actions Taken **** Informed SSS & MCR. Initated AR. | 02-00-W-DOOR-C214
399324 | CR | 20190919 | CAQ | D | Transformer 8A/2 buzzing very loudly. | Y | N |  | N | YES | <D> **** Detailed Description **** On logs found E-TR-8A/2 buzzing or humming very loudly. <I> **** Actions Taken **** Informed MCR, initiated AR. | 02-00-E-TR-8A/2
399325 | CR | 20190919 |  | 4 | Gap.1 Stator Cooling Water Pump Trouble does annuciate | N | N |  | N | YES | <D> **** Detailed Description **** During performance of SCW-DPS-15 calibration check the alarm on the GAP panel (Drop 4-1) STATOR COIL WTR PUMP TROUBLE did not annuciate when taken to less than 60 psid with the calibration instrumentation connected. Additionally, CR #399211 has an explanation including alarms present during a stator cooling water differential pressure transient in which the standby pump started and does not include this alarm. The alarm should annuciate when either SCW-DPS-16 or SCW-DPS-15 differential pressure gets less than 60 psid. | 02-00-E-CP-GACS
399326 | CR | 20190919 |  | 4 | Ladder Behind RCC-P-1C |  |  |  | N | NO | <D> **** Detailed Description **** There is a ladder behind RCC-P-1C that is standing up, wired to white iron, standing over the RCC min flow line, and doesnâ€™t have a work in progress sign staged on it. <I> **** Actions Taken **** Informed supervision, initiated AR <N> **** Equipment Description **** Behind RCC-P-1C
399327 | CR | 20190919 |  | 4 | Cable Draped Across E-IR-H22/P015 |  |  |  | N | NO | <D> **** Detailed Description **** A cable is draped across E-IR-H22/P015 with the plug end hanging on scaffolding nearby. This instrument rack is a â€œStay Clearâ€ area. There is also no work in progress sign associated with this cable. <I> **** Actions Taken **** Informed supervision, initated AR <N> **** Equipment Description **** In front of E-IR-H22/P015
399328 | CR | 20190919 | CAQ | D | MT-CRA-2 Cab indicator light is burned out. | N | Y |  | N | YES | <D> **** Detailed Description **** During performance of MMP-HOI-101 it was observed that the cab indicator light is burned out, this light is the indication for the ground guy that the crane has lost power and is functioning normally, this does not affect the operability of the crane. <I> **** Actions Taken **** Notified main control room and my supervisor. Wrote this condition report and work request. | 02-00-MT-CRA-2
399329 | CR | 20190920 |  | 4 | XD 3 | N | N |  | N | YES | <D> **** Detailed Description **** XD-3's screen has backed all the way to the home screen and will not return to service <I> **** Actions Taken **** Placed out of service. | 02-00-SEC-MON-XD3
399333 | CR | 20190920 |  | 4 | SAFETY â€“ Possible danger exiting NW corner door on building | N | N |  | N | NO | <D> **** Detailed Description **** SAFETY â€“ Danger exiting NW corner door on bld. 75 covered by alcove. Suggest placing a strobe light, visible to vehicles approaching the alcove. Light to be connected to the opening of the door. Have strobe remain on for an extended 5-10 seconds after the door is closed. It is foreseeable that this area will result in a major accident or death if not addressed. <I> **** Actions Taken **** Initiated CR and informed supervision. <N> **** Equipment Description **** Building 75 Industrial Safety walked down the area - installed signage, cones placed out into the gravel area. WR 29151726 generated, no further actions needed from CR.
399334 | CR | 20190920 | CAQ | D | Improper storage of piping in Bldg. 82. (NRC concern) | N | Y |  | N | YES | <D> **** Detailed Description **** NRC identified improperly stored pipe on the storage rack in bldg. 82. See pics for original storage and correction made. <I> **** Actions Taken **** Tie wrapped the pipe to the storage rack since only 1/2 of the pipe length was restrained by netting. See storage requirements in attached pics. <N> **** Equipment Description **** Improperly stored pipe
399335 | CR | 20190920 |  | 3 | Evaluate risk of online DEH preventive maintenance | N | N |  | N | NO | <D> **** Detailed Description **** Evaluate risk of performing any regular (non-urgent) preventive maintenance work order tasks on the DEH system online vs during outage. Reference work orders such as WO02135036 REPLACE DEH-M-P/1B and WO 02120113 DEH-V-19B, REPLACEMENT.. . Online DEH risk â€“ becomes single point vulnerability. If loss of DEH occurs then Turbine trip, Reactor Scram, loss of normal Reactor pressure control method, Reactor pressure transient. Reactor pressure maintained by opening safety relief valves and introducing heat into primary containment/wetwell. If reactor does not scram (ATWS) then containment is only rated to handle 5% reactor power via SRVâ€™s. . . Outage DEH risk - No plant impact, DEH system offline, shutdown, drained, not crucial to safe plant operation and reactor is already depressurized.
399336 | CR | 20190920 |  | 3 | Note in OSP-NSSE-W401 is inconsistent with TS Bases |  |  |  | N | NO | <D> **** Detailed Description **** The Note prior to step 7.2.24.b in OSP-NSSE-W401 states that entry into TS 3.9.4 is necessary when a PIP cable is disconnected. This verbiage was added in the latest revision. However, this Note is inconsistent with the TS Bases page 3.10.4-2 which states that, "the disconnection of the position indication probe will cause the loss of all position indication on the affected control rod. In order for LCO 3.9.4 to be met in this condition, the withdrawn control rod must have the absence of all full-in position indication channels (switch S00, the 00 readout; switch S51, overtravel-scram water applied; and switch S52, normal green light), thus maintaining the refuel position one-rod-out interlock. A channel is operable if it provides correct position indication to the refueling interlock logic." The note is also inconsistent with TS Bases for SR 3.9.4.1, which has a more in-depth discussion. Recommend review of the Note in OSP-NSSE-W401 against TS Bases for TS 3.9.4 and 3.10.4 to ensure consistent application of TS requirements. Recommend engaging the CRD system engineer and reactor engineering for historical insights. <I> **** Actions Taken **** Wrote CR.
399337 | CR | 20190920 |  | 3 | CBD-TT-10 IMDS changes. |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Existing CBD-TT-10 is a MOORE EPTCX. This is being replaced with a ACROMAG 250T. IMDS for CBD-TT-10 needs to be changed. Bench check and calibration was performed per WO# 02139984-02. See Data Glance for marked up copy of IMDS. <I> **** Actions Taken **** Generated this CR per work instructions of WO# 02139984-02.
399338 | CR | 20190920 | CAQ | D | CCH-CR-1B oil level high. | Y | Y |  | N | YES | <D> **** Detailed Description **** Oil level unsat high during run. Found after 24 hours of runtime, informed CRS and was determined to not have a qualified refrigerant mechanic available to drain. Secured chiller and pumped to normal levels per instructions. <I> **** Actions Taken **** Informed MCR. Initiated AR. | 02-00-CCH-CR-1B
399339 | CR | 20190920 |  | 4 | HT-HTP-PTM/30 Trouble light flashing | N | N |  | N | YES | <D> **** Detailed Description **** HT-HTP-PTM/30 Trouble light flashing for channel HT-H-SR13/2. When investigated, temperature was above the low temperature mark of 100 degrees. Alarm locked in. <I> **** Actions Taken **** Informed MCR, Initiated CR | 02-00-HT-H-SR13/2
399340 | CR | 20190921 | CAQ | D | NRC ENS phone line not working | N | Y |  | N | YES | <D> **** Detailed Description **** The NRC HOO notified the MCR on the shift manager line that the ENS phone was not being answered. There was no dial tone on the phone. The commercial line has been verified as available. <N> **** Equipment Description **** NRC ENS Phone line.
399341 | CR | 20190921 |  | 4 | Packing Leak HD-LCV-7B1 | N | N |  | N | YES | <D> **** Detailed Description **** During camera tour an S4 packing leak was discovered on HD-LCV-7B1. Performance should not be affected but leak should be corrected as soon as possible <I> **** Actions Taken **** Discussed with FIN and wrote CR <N> **** Equipment Description **** T -483- - -E9/7.3 - | 02-00-HD-LCV-7B1
399342 | CR | 20190921 | CAQ | D | CRD-HCU-3047 DATA FAULT while attempting to withdraw. | Y | N |  | N | YES | <C> Reopended CR and uploaded a OCC-03 document to EDM for L. Poznanski as requested, then reclosed CR. Reopened to add signed OCC-03 document per J. Fisher <D> **** Detailed Description **** While attempting to withdraw control rod 3047 from 06 to 48 per the control rod withdrawal sheet, indication on the 4 rod display changed from 06 to blank, and the DATA FAULT light on the rod select matrix apron illuminated. No panel alarms were received. Currently, the rod worth minimizer is inoperable. <I> **** Actions Taken **** Informed CRS/ SM, entered ABN-RPIS, wrote this CR and WR. | 02-00-CRD-HCU-3047
399343 | CR | 20190921 |  | 4 | MD-V-84 did not move as expected on loss of air | N | N |  | N | YES | <D> **** Detailed Description **** During the 9/21/19 downpower an attempt was made to adjust MD-V-84 to ensure the valve was seated and regain MW loss. When air to the actuator was removed, the valve did not stroke open as expected with spring force. Retreated to a low dose area and made the call to abort the current plan and restore the air to the actuator. Will have to readress this issue at the next downpower of upcoming balance shot | 02-00-MD-V-84
399344 | CR | 20190921 |  | 4 | FLM walkdown at 73% power | N | N |  | N | YES | <D> The following leaks were found at 73% power: -HD-V-3A39 S5 pipe cap leak -BS-V-40A S5 pack leak. Tightened packing, no effect -HD-V-6A7 S4 packing leak -MD-V-71 S5 packing (assumed) leak, no clear view without scaffold. 29150458 -HD-V-5B30 S3 packing leak, 29150038 -MS-V-181A cap, S2, 02146564 -Leak from manway in 471 mezzanine, above MD valve header, W5 . -Fixed packing leak from MS-V-743, WR 29150042 -Fixed packing leak from MS-V-736, WR 29150803 | 02-00-BS-V-40A,02-00-HD-V-3A39,02-00-HD-V-6A7
399345 | CR | 20190921 |  | 4 | Packing leak from BS-V-721A | N | N |  | N | YES | <D> **** Detailed Description **** Likely source of packing leak discovered during FLM walkdown is BS-V-721A. Will need scaffold to access, could positively ID using binoculars from nearby scaffold. <N> **** Equipment Description **** TG 471 heater bay | 02-00-BS-V-721A
399346 | CR | 20190921 |  | 4 | AS-BLR-1 continues to use lose level and pressure. | N | N |  | N | YES | <D> **** Detailed Description **** While Taking rounds it was found that the Aux boiler level was lowering. level should be full with the high level alarm locked in. Level was 4" and the N2 bottle was at 350# checking at 4 pm the level was 3" and the bottle was empty. recommend evaluating where the water is going suspect the BD valves (1 and 2) or back thru the feed system . <I> **** Actions Taken **** cr,wr | 02-00-AS-BLR-1
399347 | CR | 20190921 |  | 4 | BS-DV-2A2 opened spontaneously | N | N |  | N | YES | <D> **** Detailed Description **** Alarm P840-A2 9-6 Steam Dump Valves Not Fully Closed was received and locked in. BS-DV-2A2 was found full open. Power ascension was complete with the reactor at 100% with all parameters normal and stable. This appears to be a repeat of AR#395730 This CR is being written to record the valve reopening and can be closed to trend <I> **** Actions Taken **** verified plant is stable and discussed with shift supervision. | 02-00-BS-DV-2A2
399348 | CR | 20190922 |  | 4 | 500kv neutral ground oscillograph start | N | N |  | N | NO | <D> **** Detailed Description **** Module J7 500kv Neutral Ground Overcurrent oscillograph start. The alarm reset. Plant controllers and equipment indicate normal. No known cause. <I> **** Actions Taken **** Walkdown controllers and equipment to verify proper operation. Called Dittmer to verify grid integrity.
399351 | CR | 20190922 |  | 4 | Received P800.C2.8-2 "BUS SL-21 GROUND" alarm | N | N |  | N | YES | <D> **** Detailed Description **** Ground on MC-2B and MC-2R <I> **** Actions Taken **** ground reset | 02-00-E-SL-21
399352 | CR | 20190922 |  | 3 | Unacceptable Failure to Communicate High Risk Activities |  |  |  | N | NO | <D> **** Detailed Description **** Per WCI-4, Rev 48 minor rev 6, High risk work plans (HRWP) should be approved by the end of T-3. This is consistently NOT being met for non-repetitive High Risk Work. Often HRWPâ€™s are not available for the implementing operating crew until the implementation date. Additionally, support required to mitigate or manage high risk is not consistently communicated to organizations. Once HRWPâ€™s are approved, they are often not uploaded to a location where they can be reviewed until just before implementation. As an example, High Risk WOT 02043338-04, IBD-42-3B8C JUMPER INSTALLATION (IBD-FN-1A) was added to the schedule on 9/19/19 to be implemented on 9/22/19. This task requires Operations to swap from IBD-FN-1A to IBD-FN-1B to support Electricians installing a jumper in the IBD-FN-1A starter, then swapping back from IBD-FN-1B to IBD-FN-1A. This activity places us in a single point vulnerability that could result in a significant plant downpower (to ~60%) if IBD cooling were lost. There is NO OPS support task in this WO for swapping the fans, making this invisible on the OPS schedule. This WO was also NOT on the T-2 schedule. <I> **** Actions Taken **** Prepared for and successfully completed non-scheduled high risk activity. Discussed with current and next week's WWM's, AOM Work Control and AOM Crew.
399353 | CR | 20190922 |  | 4 | Weekly PA CCTV/PTZ Cleaning List | N | N |  | N | YES | <D> **** Detailed Description **** The following cameres are in need of cleaning. 1/1T, 4/4T, 7/7T, 8/8T, 9/9T, 10/10T, 13/13T, 17/17T, 32/32T, 61/61T, PTZ28, 30, 39. <I> **** Actions Taken **** Security Supervision notified. Initiate CR/WR. <N> **** Equipment Description **** PA CCTV/PTZ Cameras.
399354 | CR | 20190922 |  | 4 | E-TR-M3 Desiccant breaking down | N | N |  | N | YES | <D> **** Detailed Description **** The desiccant dryer beads are escaping the wire mesh and building up between the mesh and the glass. This is creating a gap of several inches at the top uncovering the core. The beads are still fully contained inside the dryer. <I> **** Actions Taken **** Informed SSS | 02-00-E-TR-M3
399355 | CR | 20190922 |  | 4 | E-TR-M2 Desiccant breaking down | N | N |  | N | YES | <D> **** Detailed Description **** The desiccant dryer beads are escaping the wire mesh and building up between the mesh and the glass. This is creating a gap of several inches at the top uncovering the core. The beads are still fully contained inside the dryer. <I> **** Actions Taken **** Informed SSS | 02-00-E-TR-M2
399356 | CR | 20190922 |  | 4 | E-TR-M1 Desiccant breaking down | N | N |  | N | YES | <D> **** Detailed Description **** The desiccant dryer beads are escaping the wire mesh and building up between the mesh and the glass. This is creating a gap of several inches at the top uncovering the core. The beads are still fully contained inside the dryer. <I> **** Actions Taken **** Informed SSS | 02-00-E-TR-M1
399357 | CR | 20190923 | CAQ | D | FDR-P-23 will not stay running when started | N | N |  | N | YES | <D> **** Detailed Description **** When attempting to recirculate the resin in FDR-TK-22 per SOP-RW/FDR-OPS it was discovered FDR-P-23 will not stay running after the pistol grip switch was taken to start; the switch spring returns to the center-auto position and the pump motor stops. This pump is also used to transfer resin from FDR-TK-22 to the waste cask; currently the resin level inFDR-TK-22 has 14 cubic feet remaining (seven backwashes). The resin was going to be stirred and recirculated and then allowed to settle in hopes of any suspended solids in FDR-TK-22 would be allowed to settle as opposed to being pumped back to FDR-TK-6 when decanting is performed. <I> **** Actions Taken **** informed Shift Supervisor | 02-00-FDR-P-23
399358 | CR | 20190923 |  | 4 | TSW-V-68B clogged, not allowing flow | N | N |  | N | YES | <D> **** Detailed Description **** The TSW drain for RCC-HX-1B, TSW-V-68B, is clogged and will not drain the TSW side of the heat exchanger. There are two vent paths in the isolation boundary and there is still no flow. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-TSW-V-68B
399359 | CR | 20190923 | CAQ | D | EDR system is leaking behind the RW 437 shield wall | N | N |  | N | YES | <D> **** Detailed Description **** There is evidence of a piping leak on the EDR-TK-2 system due to decreasing tank level when the tank processing pump is running. It was noted earlier in the shift that after the backwash and precoat of EDR-DM-9 and it was being returned to service there were unusual noises heard resulting from placing the EDR filter back in service. About an hour later with EDR-TK-2 in recirculation mode, the tank level was observed to be decreasing with no apparent flow path to explain this, and the W2 Sump was observed to be running longer than the normal couple of minutes. <I> **** Actions Taken **** informed shift Supervision Entered ABN-RAD-SPILL. Added to PCL. | 02-00-EDR-TK-2
399360 | CR | 20190923 |  | 4 | ARGOS AT MAIN CONTROL ROOM OOS | N | N |  | N | YES | <D> **** Detailed Description **** ARGOS IPM AT MAIN CONTROL ROOM OOS DUE TO LOW BACKGROUND COUNTS. <I> **** Actions Taken **** GENERATED CR\WR | 02-00-HP-EQ-42803
399363 | CR | 20190923 |  | 3 | (QA) Inaccurate reference to electronic folder paths |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) SWP-FFD-04 and Form Nos. 26466, 26467, and 26468 refer to inaccurate electronic folder paths as follows: â€¢ SWP-FFD-04 Section 4.1.2 provides in part â€œ[t]he following records will be MAINTAINED in hard copy at the respective department location and also stored on a network shared area (Current\ Fatigue Management Work Hour Control/Shared Documents).â€ The network shared area is referenced as an electronic folder path that is incomplete due to omission of Team Sites in such path. The present internet browser address for this network shared area is as follows: http://thecurrent/sites/10CFR/Shared %20Documents/Forms/AllItems.aspx . â€¢ Form 26466.R4 â€“ End of Shift Cycle Review states this Form is to be placed at following electronic folder path: â€œthe Current/ Fatigue Management Work Hour Control/ Shared Documents/End of Shift Cycle Review.â€ Such folder path is incomplete due to omission of Team Sites and is inaccurate as the â€œEnd of Shift Cycle Reviewâ€ folder is now titled â€œCycle Reviews.â€ The present internet browser address for the folder is as follows: http ://thecurrent/sites/10CFR/Shared %20Documents/Forms/AllItems.aspx?RootFolder=%2Fsites %2F10CFR%2FShared%20Documents%2FCycle 3D&View=%7B8342FCC9%2DF0FD%2D4D48%2DB271%2D5D854CE7A0AB%7D . %20Reviews&FolderCTID=0x012000B48A32341B87BB468E1495739239B â€¢ Form 26467.R2 â€“ Department Manager Work Hour Review states this Form is to be placed at the following electronic folder path: â€œthe Current/Team sites/Fatigue Management and Work Hours Controls/Shared Documents/End of shift cycle Review.â€ Such folder path is inaccurate as the â€œEnd of shift cycle Reviewâ€ folder is now â€œCycle Reviews.â€ The present internet browser address for the folder is as follows: http://thecurrent/sites/10CFR/Shared %20Documents/Forms/AllItems.aspx?RootFolder=%2Fsites %2F10CFR%2FShared%20Documents%2FCycle 3D&View=%7B8342FCC9%2DF0FD%2D4D48%2DB271%2D5D854CE7A0AB%7D . %20Reviews&FolderCTID=0x012000B48A32341B87BB468E1495739239B placed at the following electronic folder path: â€œtheCURRENT/Team Sites/Fatigue Management and work hour controls/ End of Shift Cycle Reviews/ PGM Reviews.â€ Such folder path is inaccurate as the â€œEnd of Shift Cycle Reviewsâ€ folder is now â€œCycle Reviews.â€ The present internet browser address for the folder is as follows: http://thecurrent/sites/10CFR/SitePages/Home.aspx ?RootFolder=%2Fsites%2F10CFR%2FShared%20Documents%2FCycle %20Reviews%2FPGM 3D&View={BDD8FE87-113D-45AB-8065-2774EBE39635} . Quality recommends that this CR be routed to Security Access Controls (AR-SECAC). <I> **** Actions Taken **** Contacted the Security Services Manager for concurrence.
399364 | CR | 20190923 |  | 3 | (QA) Regulatory Requirements Not Consistently in Procedures |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) 10CFR26 regulatory requirements are not consistently in procedures as required by SWP-PRO-03 and SWP-PRO-04. There are nine examples where incomplete regulatory guidance is available in station procedures, and three examples were specific regulatory guidance is only in department instructions. No instances were identified where a regulatory commitment was not met. Requirements: â€¢ 10 CFR 26.27 States "(c) Procedures. Each licensee and other entity shall prepare, implement, and maintain written procedures that describe the methods to be used in implementing the FFD policy and the requirements of this part. â€¢ OQAPD Appendix III section 4.2 states, â€œEach program and procedure required by plant and ISFSI Technical Specifications and other procedures that affect nuclear safety (emphasis added), and changes thereto, shall be reviewed by a minimum of two technical reviewers; i.e., the procedure sponsor and a Qualified Procedure Reviewer who are knowledgeable in the affected functional area . . .â€ â€¢ SWP-PRO-03, Procedure and Work Instruction Use and Adherence, section 2.2.1.b states, â€œENSURE procedures are consistent with commitments and regulatory requirements.â€ â€¢ SWP-PRO-04, Nuclear Procedure Program states: o Step 3.2.2, â€œISSUE an Administrative or Technical Procedure if any of the following statements apply to the activityâ€¦ The activity is required by the Operational Quality Assurance Program Description (OQAPD) to be addressed in a procedureâ€ o Step 3.2.3, â€œUSE an Instruction or Order in lieu of a Procedure provided all the following conditions are met: The Instruction or Order is not the implementing document of quality assurance program requirements or regulatory requirements â€¢ SWP-PUR-01, Procurement of Services, section 3.0 states â€œA service to supply a person(s) who is to be qualified by Energy Northwest and work to Energy Northwest procedures under Energy Northwest direction and QA programâ€. Factual Basis: â€¢ The following regulatory requirements are not currently reflected in ENW: o 10CFR.26.183(a), Qualifications - Note SWP-FFD-01, section 6.36 contains a portion of the requirements o 10CFR.26.183(b), Relationships o 10CFR.26.183(d)(1)(D)(iii) MRO may not delegate responsibilities to staff o 10CFR.26.185(h),(1) substituted specimen donor response within 5 business days o 10CFR.26.185(i)(1), Review of adulterates specimens donor response within 5 business days o 10CFR.26.185(j)(4), Foreign country medication o 10CFR.26.185(m) results scientifically insufficient â€“ Note FFDI 1.2, section 4.13.e and f provide a portion of the requirements. o 10CFR.26.187.e Continuing education o 10CFR.26.187.f, Documentation â€¢ The following regulatory requirements are only reflected in department instructions controlled by GBP-PRO-01, Non -Nuclear Procedure Program: o 10CFR.26.185(b) Reporting of initial test results prohibited - FFDI 1.2, section 4.13.1. o 10CFR.26.185(f) Review of invalid specimens - FFDI 1.2, Section 4.13.1.e and f. o 10CFR.26.185(l) Retesting Authorized - FFDI 1.2 section 4.13.e and f â€¢ A sample of 20 test results did not identify any regulatory violations and a MRO interview verified strong working knowledge of all the listed regulations. â€¢ A review of 2015 and 2017 FFD audits verified that the checklists not associated with MRO have been sampling to verify regulatory requirements are in applicable procedures. Insights: â€¢ Interviews indicate that the FFD management has an expectation that, through competencies and examination and the language of the contract, the MRO is meeting regulatory requirements and did not see a need to incorporate all regulatory detail into station procedures. â€¢ Note that general responsibilities to comply with 10CFR26 are listed in commercial grade contract for Medical Review Officer (MRO) #327300 . Quality recommends that this CR be routed to Security Access Controls (AR-SECAC). <I> **** Actions Taken **** Contacted the Security Services Manager for concurrence.
399365 | CR | 20190923 |  | 3 | (QA) No documentation for procedure enhancement evaluation |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) No documentation is evident for the procedure change evaluation for AR-SA 336642 assignment 07. The Self -Assessment utilizing NRC IP 71130.01 to determine if Energy Northwest Access Authorization Program is meeting regulatory requirements (AR-SA 336642) recommended evaluating whether Security Programs Implementing Procedure SWP-SPIP-65, Access Authorization Program, needs to be enhanced to meet requirements regarding Social Security Number verification. Contrary to AR-SA 336642-07 description, no documentation was found in either completion notes or EDMS for the evaluation. No changes were made to SWP-IPIC-65 as a result of the evaluation. Failure to document the results of an evaluation make it difficult to validate the justification for no procedure change. . Factual Basis: â€¢ Self-Assessment utilizing NRC IP 71130.01 to determine if Energy Northwest Access Authorization Program is meeting regulatory requirements identified enhancement R-5 to evaluate whether SWP-SPIP-65 Security Programs Implementing Procedures needs to be enhanced to meet requirements regarding Social Security Number verification with AR-SA Assignment Number: 336642-07 â€¢ AR-SA 336642-07 Description field directed â€œEvaluate whether SWP-SPIP-65 Security Programs Implementing Procedures needs to be enhanced to meet requirements regarding Social Security Number verification. If evaluation identifies procedure changes then create action and cross reference to this SA and or create the assignment under this SA for tracking purposes. Provide documentation through completion notes and or EDMS.â€ â€¢ SWP-ASU-02, Self-Assessment and Benchmark Processâ€™, step 4.12 requires documenting actions taken in the completion notes and uploading supporting documents in the EDMs. â€¢ No documentation is evident in either the completion notes or EDMS . Insight: â€¢ This activity is infrequently performed by the individual. Had the procedure (SWP-ASU-02) been referenced the step (4.12) requiring documenting actions taken would have been noted and adhered to. . Quality recommends that this CR be routed to Security Access Controls (AR-SECAC). . <I> **** Actions Taken **** Contacted the Security Services Manager for concurrence.
399367 | CR | 20190923 |  | 3 | (QA) SARC assignments closed in violation of procedure |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) AR-SA 336642 assignments 07 and 08 closed by employee other than Department Supervisor. The Self-Assessment utilizing NRC IP 71130.01 to determine if Energy Northwest Access Authorization Program is meeting regulatory requirements (AR-SA 336642) was conducted utilizing SWP -ASU-02, Self-Assessment and Benchmark Process. Section 4.12 and Attachment 8.4 of SWP-ASU-02 describe the requirements for closure of a SARC assignment including documentation of required Department Supervisor approval. Assignment 07 of AR-SA 336642 was completed 09/26/2017 by an employee other than (and not designated as) the Department Supervisor. Assignment 08 of AR-SA 336642 was completed 11/30/2017 without Department Supervisor approval. . Factual Basis: â€¢ SWP-ASU-02 Attachment 8.4 lists the Department Supervisor as required approval for completion of a SARC assignment. AR-SA 336642-07 and 08 were designated as SARC assignments but were completed by an employee other than a supervisor. â€¢ Delegation of Authority rosters do not indicate employee to have been delegated to act on supervisorâ€™s behalf at time of completion of AR-SA 336642-07 and 08. â€¢ SWP-ASU-02, step 4.12.1c requires the performer to â€œDOCUMENT the Department managerâ€™s/supervisorâ€™s approval of the closure in the SARC assignment.â€ â€¢ Completion notes do not include actions taken for resolution or documentation of Department Manager/Supervisor approval for closure. . Insight: â€¢ The remaining four SARC assignments had routing lists attached to the assignment. Attaching a routing list to the two affected assignments may have prevented the closure error. . Quality recommends that this CR be routed to Security Access Controls (AR-SECAC). . <I> **** Actions Taken **** Contacted the Security Services Manager for concurrence.
399368 | CR | 20190923 |  | 3 | Issue with late notification for ECs in Work Control Process |  |  |  | N | NO | <D> **** Detailed Description **** WCI-4 Online Work Control Process states in section 3.2 that all Engineering Changes are to be complete by the week of T-40. But again on section 3.3 it states ECs are to be complete by end of T-20. Both cases do not allow for late identification of a need for an EC as a result of Planning, such as identifying that a Limitation on Use (LOU) requires an EC in order to install a component. An EH hold is placed on the Work Order with no regard for the unexpected cycling this causes the design organization. In a pursuit of excellence, recommend Work Control determine how best to handle this disagreement. <I> **** Actions Taken **** Discussed with fellow Design Supervisors. Initiated CR.
399369 | CR | 20190923 |  | 3 | (QA) One Incomplete Security Organizational Change |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Organizations Change Form 26239 was incomplete contrary to SWP-ORG-01 "Organizational Changes", and two related documents still reflect the outdated position title. This is a procedure use and adherence issue with no known actual consequence; however, documents citing outdated position titles can lead to confusion regarding who is supposed to fulfill specified responsibilities. Factual Basis: â€¢ Form 26239 for Operations Support (approved 7/16/18) changes a "Position" title from "Emergency Services Support Manager" to "Security Services Manager". â€¢ An incomplete form was submitted to Human Resources with no boxes checked in section 4 for "Type of Reorganization". ("Position" is correct box based on definition in SWP -ORG-01). â€¢ Section 8A on this form listed AR-SELF 381293 to track required document updates, but this completed AR-SELF missed revisions to both PPM 1.20.1 "Refuel Outage Preparation and Milestones" and ISDI-TRAP-16 "PADS â€“ Technical Recovery Action Plan (TRAP)". â€¢ Attachment 6.1 "Pre-Outage Milestone Summary Matrix" and Attachment 6.2 "Pre-Outage Milestones" within PPM 1.20.1 both still contain outdated title "Emergency Services Support Manager" as the Owner for the PO.37 Milestone. â€¢ Attachment 7.1 in ISDI-TRAP-16 still contains outdated title "Emergency Services Support Manager" in section 7.1 "Contacts"; however, the phone extension listed remains correct. â€¢ Organizational Changes are infrequently performed activities. â€¢ One similar issue was identified by Quality during the AU-AA-FD-MRO/SAE-17 audit (AR-CR 371507) as well as one similar self- identified issue (AR-CR 370441) during the audit period. . Quality recommends that this CR be routed to Security Access Controls (AR-SECAC). . <I> **** Actions Taken **** Contacted the Security Services Manager for concurrence.
399371 | CR | 20190923 |  | 3 | Possible procedure update to SOP-HVAC/RB-OPS |  |  |  | N | NO | <D> **** Detailed Description **** Several notes in the procedure state "Reactor Building D/P CT -0.25" WC in Modes 1, 2, and 3, and during operations with a potential for draining the vessel, requires and entry into Tech Spec 3.6.4.1." The 'during operations with a potential for draining the vessel' condition has been removed from the applicability of TS 3.6.4.1.
399373 | CR | 20190923 |  | 3 | Product Quality Scoresheet needs improvement |  |  |  | N | NO | <D> **** Detailed Description **** Form 27050A Post Implementation Critique needs improvement. The improvements in design quality over the last cycle have resulted in the grading ciriteria within the form to grade an overwhelming majority of design changes as "Exceeds Expectations" even though there may have been room for improvement. Recommend Design Engineering make improvement to the form to continue our drive for excellence. <I> **** Actions Taken **** Discussed with Design Manager and team members. Initiated CR. <N> Form 26370 is HISTORY status in Portal J (since 10/30/2018). At the request of the CR Initiator, the CR Description field changed to correct FORM 27050A.
399376 | CR | 20190923 | CAQ | D | M&TE Suspended/ Lost |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #C011739 Fluke Dig. Multimeter- model 25 is Missing from the Tool Crib and is Now Suspended/ Lost. No Activity in Portal J. DEF #7325A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
399379 | CR | 20190923 |  | 4 | Black Widow in Building 12 air compressor room |  |  |  | N | NO | <D> **** Detailed Description **** During quarterly building 12 safety inspection, came across a healthy black widow in the air compressor room. This is the closet like room on the south side of the building that only houses an air compressor controlled from inside building 12. <I> **** Actions Taken **** Photos taken, the CR intiiated, and supervision informed .See EDMS for photos
399382 | CR | 20190923 |  | 4 | Building 12 Safety Inspection Discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** During this quarterâ€™s Building 12 Safety Inspection I found two discrepancies. One a garden hose attached to an exterior spigot on the north side with no ongoing work nor Work In Progress sign. Hose was dry. Then in the room accessed without keys on the north side, an ice box (Igloo style) is stored on a shelf that does not leave the required 24â€ nor 18â€ gap per Inspection form 24570. <I> **** Actions Taken **** Photos taken, initialted CR, supervision informed. See EDMS for photos.
399385 | CR | 20190923 |  | 3 | IBD fan inspections should be rescheduled due to safety | N | N |  | N | YES | <D> **** Detailed Description **** Work orders for IBD fan inspections need to be rescheduled for outage time frame. The inspection would require the fan to be stopped for an inspection of the fan blades and the belts and the motor. The fan is turning due to the flow from the adjacent fan running. There is no brake mechanism to stop the fan from turning. These have been done previously to the best of the ability while the equipment is turning which is not the best practice. <I> **** Actions Taken **** Notified my supervisor and the main control room. Recommend rescheduling due to the safety concern of rotating equipment in the confined space. <N> Used stobe light to gage speed of fan. 414 RPM Submitted SMS-AR 400664 to change from an on-line PM to an Outage PM. Did this for PMID-RQ's 7749-04 and 7750-04 for both A and B fans. | 02-00-IBD-FN-1B
399388 | CR | 20190923 |  | 3 | Work order 02117849-01 not able to be worked |  |  |  | N | NO | <D> **** Detailed Description **** The work order task instructions â€œtask permitsâ€ said no clearance required, and per IER 18-003 mechanical skills â€œknowledgeâ€ the basic design and key functions of equipment and components as they relate to maintenance, we questioned the clearance boundary. This work order will need to be returned due to the following issues. â€¢ Work order needed to be part of the high risk work plan due to single point vulnerability if it is worked on line. â€¢ This work order was planned as a minor maintenance repair with only minimal guidance and needs to be planned as a regular work order with precautions and limitations and follow the work order process. â€¢ During implementation it was found that the tear was internal to the unit which would require a clearance order and confined space evaluation. â€¢ The use of chemicals CID 37254 inside the unit was not evaluated due the flammability of the glue and the fumes being drawn into the bus ducting. This would also upgrade the confined space from non-permit required to permit required. <I> **** Actions Taken **** Notified my supervisor, main control room, initiated this CR and notified the work week manager. Returned Work Order
399391 | CR | 20190923 |  | 3 | IBD Accelerometer Replace should be rescheduled for safety | N | N |  | N | YES | <D> **** Detailed Description **** Work orders for IBD accelerometer replacement need to be rescheduled for outage time frame. The replacement would require the fan to be stopped for access to the bolts needing to be removed and accelerometers. The fan is turning due to the flow from the adjacent fan running. There is no brake mechanism to stop the fan from turning. <I> **** Actions Taken **** Electrical supervision informed. Work Week Manager Informed. <N> The PMID-RQ for this work is 23980-01. AR 399456 retired this PM and the work is no longer performed. | 02-00-IBD-FN-1B
399392 | CR | 20190923 |  | 3 | Procedure enhancement for ABN-Transformer |  |  |  | N | NO | <D> **** Detailed Description **** The note before step 7.3.7.a gives an epn that doesnt exist. See EDMS. . The note should say that E-DISC-7AA3B is Kirk Key interlocked with E-DISC-8AA3F. <I> **** Actions Taken **** Wrote CR
399393 | CR | 20190923 |  | 3 | Viscosity Standard Check Acceptable Limit Clarification |  |  |  | N | NO | <D> **** Detailed Description **** In Diesel Fuel CI-11.8 sections 5.2.10 and 5.2.11 the acceptable limit for the viscosity std. is unclear because it says "... within 2.0 +/- 0.2 (cSt)" and should just say for example, "...+/- ? (cSt) of the calibrated value...". <I> **** Actions Taken **** CR written and supervision notified.
399397 | CR | 20190923 |  | 4 | Quorum not Met at Forced Outage Meeting |  |  |  | N | NO | <D> **** Detailed Description **** Quorum was not met at Forced Outage Meeting on 9/23/19. Meeting will not be rescheduled. Next meeting is scheduled on 10/14/19. <I> **** Actions Taken **** Continued meeting to discuss items from this last weekend's downpower and future forced outage. <N> System Eng, was the group not in attendance. J. Hauger (SYSENG manager) said the FO meeting was scheduled over Core Business schedule so there was a schedule conflict.
399398 | CR | 20190923 |  | 3 | OSP-RHR/IST-Q702 not revised after EC 14635 implemented | Y | Y |  | N | NO | <D> **** Detailed Description **** OSP-RHR/IST-Q702 (RHR Loop A Operability Test) step 7.2.38 was not updated following the Implementation of EC 14635 to include the updated allowable oil leakage values. EC 14635 replaced RHR-P-2A and RHR-M-P/2A. The updated allowable oil leakage rates are 3 drops/hour for the lower reservoir and 8 drops/hour for the upper reservoir as determined in CMR 14733. . The RHR System Engineer reviewed the previous surveillance performances since the motor RHR-M-P/2A was changed and there was no oil leakage identified on each performance. . Detailed discussion EC 14635 was implemented in December 2018. Calculation ME-02-05-01 (Calculation For Determination Of Acceptable Oil Leakage Rates From Pump Motors) was updated by CMR 14733 to reflect the replacement RHR-M-P/2A. The CMR 14733 was prepared and approved in support of EC 14635. However, the procedure OSP-RHR/IST-Q702 was not updated as a part of the Return to Service activities following implementation. . Recommend that the resolution of this CR be assigned to Operations Procedures to revise OSP-RHR/IST-Q702. <I> **** Actions Taken **** Discussed this issue with RHR System Engineer and the Mechanical/Civil Design Supervisor Initiated this CR Notified the Shift Manager
399399 | CR | 20190923 | CAQ | D | WEA-RIS-14 Out Of Tolerance | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During the performance of PPM 16.3.1 it was discovered that Table 7.5b Channel 1 As-Found loop check is out of tolerance for WEA-RIT-14 CH 4 and WEA-RIS-14 CH4, These channels receive a signal from WEA-PLC-ISOL/1A, WEA-PLC -ISOL/1B and WEA-PLC-ISOL/1C. <I> **** Actions Taken **** Initiating a work request to calibrate individual current isolators for WEA-PLC-1
399400 | CR | 20190923 |  | 3 | Procedural enhancement desired for HPI-8.2 |  |  |  | N | NO | <D> **** Detailed Description **** HPI-8.2 QUANTITATIVE RESPIRATOR FIT TESTING USING PORTACOUNT PLUS SYSTEM does not address the proper response for message â€œfit factor was suspiciously highâ€. While performing a Porta-count fit test I was getting yellow message that the â€œfit factor was suspiciously highâ€. The Daily checks were completed satisfactorily. The unit was changed out with another that was in calibration was placed in service. The daily checks were performed and the particle emission from the humidifier was lowered. <I> **** Actions Taken **** To aid in the proper response to this message, I suggest procedural guidance of the following:: Adding in the set-up requirements for the humidifier the Three Bear Approach: not too much, not too little but just right. Also, if the message â€œfit factor was suspiciously highâ€ the operator should check the particle emission rate, obstructions in the test hose and possible need to change out the unit.
399401 | CR | 20190923 | CAQ | C | Roll filter for CAT ID 58403394 is not like for like |  |  |  | N | NO | <C> This CR changed from Non-CAQ 3 to CAQ C for PROCENG as per the MRT. <D> **** Detailed Description **** Roll filter for WMA-FL-52A (CAT ID 58403394) is not like for like as the currently installed roll filter. The cat id was and is the same as the previously installed filter (new MR# 351179 old MR#170422). The new filter is blue in color (old style is yellow and the color isnâ€™t an issue) and the medium isnâ€™t woven as tight nor does it have a strong outer layer compared to the old style (maybe different manufacturer). The craft stopped the install and contacted the system engineer for recommendation(s) as to if the new style of filter was acceptable to install. There is OE that if the roll filter is installed backwards the filter will become friable and will clog the fins up in the WMA coiling coils (AR-CR NUMBER 00285720) <I> **** Actions Taken **** The new style filter leads you to believe that it will come apart and clog the coils if installed. The system engineer requested the craft write a CR and have procurement engineering evaluate the new style filter. New material is not yet installed in the system. <N> **** Equipment Description **** WMA-FL-52A
399403 | CR | 20190923 |  | 3 | SD000182 Revision required |  |  |  | N | NO | <D> **** Detailed Description **** System description contains a discrepancy with the semaphore flags between the different flags. M1 thru 3 have a semaphore installed but description does not mention this. Also TR-S description says that semaphore is installed when there is not one. For TR-N2, there are 16 fans installed but description only mentions 8. <I> **** Actions Taken **** CR written. Ops Training informed.
399404 | CR | 20190923 |  | 3 | RCC conductivity High | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** RCC Conductivity is at 4.7 uS/cm and the CCW action level one criteria is above 2.0uS/cm. It is not at action level 2 but with the high trend in the pH (AR#398947) it is recommended that the deep bed demineralizer be changed out again. This is not a normal trend. The demineralizer usually lasts a year or more it was last changed out around 4/1/19. Investigation is in progress for the source of the contaminatess. In the mean time the only way to clean up the system is to change out the deminerilizer. Also recommend sampling for ATP. The demineralizer water temp was taken and it was roughly 90 degrees Fahrenheit which would not cause resin degradation. <I> **** Actions Taken **** Notified MCR, Chemistry supervision, Chemistry specialist.
399405 | CR | 20190923 |  | 3 | Reschedule of AOV continuing training. |  |  |  | N | NO | <D> **** Detailed Description **** AOV CT was scheduled for 9/24/19 as an SME led class. MM Line Manager approved SME support for this class in July when all AOV classes were scheduled (initial and continuing). However, there was poor communication between training and the line and the SME was pulled for scheduled work resulting in no support for the AOV CT on 9/24. Class had to be rescheduled to 12/4/19. Tag chair, Training manager and PGM all approved for reschedule. No qualifications are impacted by this reschedule of training. <I> **** Actions Taken **** Training rescheduled to 12/4/2019. SME included in plateau invite to course.
399406 | CR | 20190923 | CAQ | D | The SCC did not receive responses from all the pager sites | N | Y |  | N | YES | <D> **** Detailed Description **** During the SCC shift change Pager Test 2 of the 6 pages did not report as expected. This is an indication of RF interference affecting the test receiver on Rattlesnake Mt. or failing paging transmitters. Note there is overlapping pager coverage and other means to notify personnel in an event. <I> **** Actions Taken **** Notified EP, MCR, and IS. CAQ-D close to WR. <N> **** Equipment Description **** Paging sites, TEC
399407 | CR | 20190924 | CAQ | D | CSP-V-800/26 bonnet loosened when attempting to operate. | Y | N |  | N | YES | <D> **** Detailed Description **** CSP-V-800/26 bonnet loosened when attempting to operate. Valve was difficult to operate and while attempting to open the bonnet turned ~ 5 degrees of rotation. Valve disc remains closed. <I> **** Actions Taken **** stopped surveilance and contacted SM. restored this section and notified mechanics. | 02-00-CSP-V-800/26
399408 | CR | 20190924 |  | 3 | voltage unbalance on IBD-42-2R13C | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Electricians obtained voltage and current readings from IBD-42-2R13C as PMT following coil replacement WO# 02043338-03. Typically when voltages are obtained on three phase systems we calculate the imbalance between the phases. This work order does not have steps to calculate the percent unbalance relationship between phases, but there appears to be a large imbalance between A, B and C phase. A to Ground is measured at 281VAC. B to Ground is measured at 240VAC and C to Ground is measured at 317VAC. The following measurements are Phase to Phase, A-B 481VAC B-C 483VAC and C-A 483VAC. Running current seems to be balanced at approx. 31 amps on each phase as well. Average voltage is 279 and % unbalance is 27.5%. <I> **** Actions Taken **** Write CR and Notified Shift Manager. <N> **** Equipment Description **** TG 471 IBD-42-2R13C
399409 | CR | 20190924 | CAQ | C | LCS 1.3.3.1.C.1 not completed within 7 days | N | Y |  | N | YES | <D> **** Detailed Description **** WEA-SR-25 was removed from service on 9/17/19 for planned maintenance. WEA-SR-25 was not returned to service within 7 days exceeding the action time of LCS 1.3.3.1.C.1 to restore the system to Operable status therefore requiring entry to LCS 1.3.3.1.E which requires that a CR be written immediately. This CR fulfills the action of LCS 1.3.3.1.E .1. During performance of 16.3.1 WEA Low Range Noble Gas Monitor Channel 1 CC/RC failed the leak check. Work is ongoing to restore WEA-SR-25 to service and perform required PMTs to restore to Operable. <I> **** Actions Taken **** Initiated CR as required per LCS 1.3.3.1.E.1. Informed Shift Manager. <N> WEA-SR-25 was removed from service 9/17/2019 for planned pump replacement under WO 02134942 which was originally scheduled for 4 hours. The seven day LCS completion time was exceeded due to scope the growth documented in CR 399180, 399248, and 399399. WEA-SR-25 repairs are planned to be completed under WO 02134942 by 10/2/19. | 02-00-WEA-SR-25
399413 | CR | 20190924 |  | 3 | Evaluate DEH TROUBLE ARP to provide correct operator actions |  |  |  | N | YES | <D> **** Detailed Description **** The DEH TROUBLE P820-B1 2-5 will alarm for various reasons. Some of those alarms may require operator action. Example DEH trouble alarm due to HP EXT ZONE (GOV) TEMP DEV HIGH ALARM came in at 75 degrees delta on 8/29/2019. During the investigation it was noted that there exist documentation that states to consider tripping the turbine when the delta reaches 100 degrees. I have attached the paperwork noted above and an excel file with a list of DEH alarms. Request an evaluation of possible DEH Alarms that would require quick operator response to protect people and equipment. The ARP for the DEH TROUBLE directs writing a work request and notifying the system engineer. There may be cases when lowering power or tripping the turbine should be the more appropriate and timely choice. This will provide operators with clear direction to help them make the correct decisions in abnormal operating conditions. <N> The DEH TROUBLE annunciator is not intended to require quick operator response to protect people and equipment (hence write WR, inform system engineer). There is a separate DEH WARNING annunciator for this purpose. For the particular example provided, the DEH WARNING annunciator would come in at a delta of 100 degF. It would be prudent to augment the DEH WARNING response to direct the appropriate operator action. | 02-00-DEH-COMP-1
399417 | CR | 20190924 |  | 3 | WEA-PLC-ISOL/1A, 1B, and 1C each need an IMDS |  |  |  | N | YES | <D> **** Detailed Description **** WEA-PLC-ISOL/1A, 1B, and 1C each need a IMDS | 02-00-WEA-PLC-ISOL/1A,02-00-WEA-PLC-ISOL/1B,02-00-WEA-PLC-ISOL/1C
399418 | CR | 20190924 | CAQ | D | Received FPC RM COOLER FLOW LOW/TEMP HI alarm. | Y | Y |  | N | YES | <D> **** Detailed Description **** Received FPC RM COOLER FLOW LOW/ TEMP HI, H13.P812.R1.4-2, alarm shortly after starting SW-P-1A. The as found flow through RRA-CC-20 as indicated on SW-FI-71A was 32 gpm. Per OSP-SW-M101, the recommended flow range is 40-45 gpm, and the minimum operability value is 38.5 gpm. Performed OSP -SW-C101 to fully open SW-V-184A for 3 minutes, and then restore flow to the recommended flow range. As left flow as indicated on SW-FI-71A is 43 gpm. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-RRA-CC-20
399419 | CR | 20190924 |  | 3 | Work package walk down requirement for safety system windows |  |  |  | N | YES | <D> **** Detailed Description **** Currently WCI-4 requires that All departments commence walk down of packages and advance WOs to READY (status 45) by the end of T-4. For safety system windows this requirement does not leave a lot of time for issues that are discovered to be resolved (work instruction corrections, procedure changes, parts not being on site etc.) Benchmarking other stations has identified that walk downs being completed by the craft no later than T-6 has been beneficial to resolving issues early. This lead to better schedule adherence and less work being deferred or moved out of the scheduled work week. Improving the predictability and execution of the schedule and reducing the likelihood of something being over looked. <I> **** Actions Taken **** Created CR, Discussed with supervisor and Manager <N> **** Equipment Description **** N/A Per discussion with Online Work Control Manager the WCI-4 will remain as currently written. Walkdowns may be performed at earlier dates.
399422 | CR | 20190924 |  | 4 | False step change for multiple eDNA bearing temperature pts. | N | N |  | N | NO | <D> **** Detailed Description **** While investigating potential causes for higher than expected bearing temperature in the SW-M-P/1B (CR 399310), it appears that PDIS data in eDNA shows a false step change of ~6-8Â°F for SW-M-P/1B temperatures on 9/7 at ~11am similar to CR 384331 that was initiated around this same time in 2018. SW-M-P/1A motor bearing temps were looked at and a similar step change is apparent at approximately the same time. This change in temperature does not correspond to other system parameters for either motor. Other eDNA points investigated that validate this false step change are: Circ Water Thrust bearing temps, turbine oil drain temps, TSW/Cond/RHR Motor temps (div 1, 2, and 3), and Feed Turbine Thrust bearings (See EDMS). Recommend find similar cause for all these PDIS points to have a step change in data and recalibrate and/or restore data points to their correct values. <I> **** Actions Taken **** Discussed and validated trend with System Engineering and supervisor. Notified SM. <N> **** Equipment Description **** Control Room Analog input computer cabinet
399423 | CR | 20190924 | CAQ | D | WEA-PLC-ISOL1A, 1B, 1C need calibrated | N | Y |  | N | YES | <D> **** Detailed Description **** WEA-SR-25 is currently out of service 0210868901 and the Isolators need calibrated <I> **** Actions Taken **** CR 345191, CR 376416 | 02-00-WEA-PLC-ISOL/1A,02-00-WEA-PLC-ISOL/1B,02-00-WEA-PLC-ISOL/1C
399424 | CR | 20190924 |  | 4 | RCIC System Outage Lesson Learned I&C |  |  |  | N | NO | <D> **** Detailed Description **** While working on RCIC-LS-11 per W/O 02145439-01, it was discovered that a new Floating Block should be machined. The next time there is work to be perform on RCIC-LS-11, scope will be added with a task to machine a new Floating Block. <I> **** Actions Taken **** Wrote CR LL. Spoke with Supervision
399427 | CR | 20190924 |  | 4 | After Hours Document Not Issued Due to Human Performance |  |  |  | N | NO | <D> **** Detailed Description **** An after-hours procedure was written and implemented on 9/21/2019. Per SWP-PRO-02, Document Control is to issue after hours to filing locations the next buinsess day (9/23/2019). However, due to potential human performance error, the document in APW failed to obtain all signatures. This may have been due in part to routing the procedure for review and signature to another individual via the Add/Modify button. <I> **** Actions Taken **** Issue in APW was identified and correct individual was able to sign. Document Control issued the document same day signature was applied (9/24/2019). <N> Suggest this CR for Trend only. Error occured due APW issue and/or Human Performance in using the Add/Modify button in APW. Upon further investigation, cause was determined to be a glitch with APW software.
399428 | CR | 20190924 |  | 4 | EDNA point W143 not reading as expected | N | N |  | N | YES | <D> **** Detailed Description **** EDNA point W143 (RHR-P-2B MOTOR STATOR WIND TEMP POINT-5) is not reading as expected. When the RHR-B pump is running the reading from this EDNA point is much lower than the other RHR-M-P/2B stator winding temperature points (Ex. On 9/19/19: W141 = 140F, W142 = 139F, W143=110F). RHR-A and RHR-C stator winding temperatures are all trending within a few degrees of each other in EDNA. RHR-TE-504/5 feeds EDNA point W143. This is likely an indication issue since all the other RHR-B stator winding temperature elements are reading as expected when the pump is running. | 02-00-RHR-TE-504/5
399432 | CR | 20190924 |  |  | Late eSOMS entry for Maintenance | [5 empty] | <D> Maintenance craft was on scheduled PT and came into work and failed to notify supervisor or shop admin. He worked 2 hours of his shift before realizing his he did not cancel his PT and be entered back into eSOMS.
399433 | CR | 20190924 |  | 4 | Late eSOMS entry for Maintenance |  |  |  | N | NO | <D> **** Detailed Description **** Maintenance craft was on scheduled PT and came into work and failed to notify supervisor or shop admin. He worked 2 hours of his shift before realizing his he did not cancel his PT and be entered back into eSOMS. <I> **** Actions Taken **** Updated eSOMS with correct hours and notified supervisor of late entry.
399434 | CR | 20190924 | CAQ | D | WMA-TCV-52A packing leak increase | N | N |  | Y | YES | <D> **** Detailed Description **** â€¢ WMA-TCV-52A has indications of water leak, AR-CR 391439, WR 29129159 (cancelled to WR 29099638, Priority 4F, Actioned (8/16/2012). Originally identified as minor leak, leak appears to cycle with valve position from original minor leak with water pooled on packing gland but not dripping to current indicators of significant floor stains, significant rust on packing gland, and water damage to insulation. <I> **** Actions Taken **** Generated AR-CR to validate existing work priority and augment the scope to include insulation repairs. This issue was identified during a QA plant walkdown. See EDMS for associated pictures. . This leak has existed since 2013. WO 02038576 still being planned. Although WMA-TCV-52A is NSR, this is located in the Div 1 SR HVAC room. This needs to be made a priority to fix within 12 weeks. The NRC commented on it over a year ago. <N> This work is scheduled March 9th 2020. Note added to P6 â€œdonâ€™t move out of March 9th week without AOM WC concurrenceâ€ | 02-00-WMA-TCV-52A
399435 | CR | 20190924 | CAQ | C | Editorial for M526-2, E-13, CF-V-7 should be CF-V-720. |  |  |  | N | NO | <D> **** Detailed Description **** Editorial for M526-2, E-13, CF-V-7 should be CF-V-720. <I> **** Actions Taken **** ref CVI ISO 317-00,2957
399436 | CR | 20190924 |  | 4 | Water damaged wall at PWC-V-139 | N | N |  | Y | YES | <D> **** Detailed Description **** â€¢ Wall at PWC-V-139 has water damage to wall in two places (pipe wall penetration and wall below near floor), material appears similar to sheetrock (Next to Equipment Room door C-505, Communications Room), Verified Door C-505 is not a credited barrier in PPM 1.3.57, therefor no operational risk from the nearby degraded wall. WR 29134674 repaired a leak on PWC-V-139 in 2017, however no WR was generated for wall water damage. <I> **** Actions Taken **** Generated AR-CR and WR. This issue was identified during a QA plant walkdown. See EDMS for associated pictures. <N> **** Equipment Description **** Wall around PWC-V-139, near Communication Room Door C-505,
399438 | CR | 20190924 | CAQ | D | C408 Needs Maintenance | Y | Y |  | N | YES | <D> **** Detailed Description **** C408 Needs Maintenance, call security for details. <I> **** Actions Taken **** Recieve alarm/ full ops test/ notified supervision/ CR/WR generated <N> **** Equipment Description **** 501 corridor, Control Room Door | 02-00-W-DOOR-C408
399439 | CR | 20190924 | CAQ | D | (QA) QC rejection of items for DE-F-1A1, DE-F-1A2 | N | N |  | Y | YES | <D> **** Detailed Description **** (QA) QC identified an unsatisfactory condition while performing parts acceptance for work order 02119140 task 30. Cat ID 58407412 (filter) that was presented to QC shows damage to finned areas and sheet metal frame on all 18 filters. Also one of the 18 filters inspected did not have the cat ID identified on the outside of the shipping box/carton for traceability. Quality Control acceptance per G-101 states that, items will be free of any apparent physical damage, rust or corrosion and degradation. <I> **** Actions Taken **** Notified the Quality Services Supervisor, QC Level III and the Maintenance Supervisor. Material verification is for shop work activity modification of filters per EMS 30146. Materials are not plant installed components at this time. <N> E-mail was placed into the EDMS of this CR 399439 to capture the Engineering inspection / evaluation of this condition as not impacting filter functions. The filters are acceptable for use in WO 02119140 task 30. | 02-00-DE-F-1A1,02-00-DE-F-1A2
399440 | CR | 20190924 |  | 3 | PWC-V-752 & PWC-V-753 are missing from SOP-PW-LU. |  |  |  | N | NO | <D> **** Detailed Description **** No restoration position for PWC-V-752 & PWC-V-753 are listed in procedures. Clearance lift 11/12/19 per current schedule. <I> **** Actions Taken **** Wrote CR. | 02-00-PWC-V-752
399441 | CR | 20190924 |  | 4 | (QA) Deficiency Tag Not Removed |  |  |  | Y | NO | <D> **** Detailed Description **** â€¢ Deficiency Tag 40350: WMA-AH-51B small air leak, AR-CR 335240, WR 29123635 DL, 4A, Work completed under WO 02090643 but Deficiency Tag not removed IAW MI-3.6.4, Attachment 5.1. Verified no open WR against WMA-AH-51B air leakage, generated AR-CR. Maintenance verified and is removing the deficiency tag. <I> **** Actions Taken **** This issue was identified during a QA plant walkdown. <N> Per Mechanical Supervisor, tag has been removed.
399442 | CR | 20190924 | CAQ | D | CCH-CR-1A Oil Filter DP Rise | Y | Y |  | N | YES | <D> **** Detailed Description **** During monitoring and trending of CCH-CR-1A performance data, a rise in oil filter differential pressure was identified. The oil filter DP is currently trending at 15 â€“ 18 psi and has been steadily increasing at a rate of 2-3 psi per month since April 2019. The chiller has history of operating with a DP of 60 psi before a trip occurs. . The current DP trend was reviewed against chiller filter DP issues that have occurred in the past. In the past, a similar DP rise occurred on CCH-CR-1B but was not acted upon and the filter rapidly fouled during the following surveillance run. Per analysis performed under AR 314206 regarding the previous DP rise, there was a point when a critical mass of burnt oil debris developed such that the filter DP would rapidly spike during the following chiller run. . Historically, CCH-CR-1A filter DP rises have been gradual and occurred over the course of several monthly surveillance runs. However, CCH-CR-1B experienced a significant and rapid rise in filter DP not long after an overhaul had been performed. During an overhaul, the oil system is drained and accessible debris is removed. A new volume of oil is then charged into the system during restoration. The fresh oil can behave similar to solvent and collect residual debris that may have been disturbed during the overhaul. Thus, filter fouling is more likely to occur following an overhaul. . Based on the facts that the oil filter has been gradually increasing and the chiller has not recently been overhauled (last overhaul was January 2016), there is reasonable expectation that significant debris accumulation has not occurred at this point and CCH-CR-1A is fully capable of performing its function. . It is recommended that an oil filter replacement be added to the Priority Work List and that the work be performed prior to the next chiller surveillance (10/12/19). Reference WO 02093006 for previous oil filter replacements. <I> **** Actions Taken **** Discussed with supervisor and Shift Manager. | 02-00-CCH-CR-1A
399443 | CR | 20190924 | CAQ | C | (QA) Scaffold with inadequate floor protection |  |  |  | Y | NO | <D> **** Detailed Description **** â€¢ Scaffold #1713, has no rubber floor protection, just degraded duct tape to protect a credited flood barrier floor coating. All other scaffold locations inspected had a blue rubber mat between scaffold components and coated floors for protection. Maintenance indicated the scaffolders will be correcting the condition this week. o PPM 10.2.53, section 7.4.3.a. states â€œProtect floor when erecting and disassembling scaffolding as appropriate by using protective floor covering. Floor paint (coatings) may be a credited flood barrier as described in PPM 1.3.57.â€ Generated AR-CR. Care should be taken to not damage flood barrier coatings or generate a barrier impairment when extracting the duct tape from adhered floor coatings. <I> **** Actions Taken **** This issue was identified during a QA plant walkdown. See EDMS for associated pictures. <N> Per Mechanical Maintenance Supervisor scaffold condition has been corrected.
399444 | CR | 20190924 |  | 3 | Sealed Source Surveillance Applicability to Non-CGS Sources |  |  |  | N | NO | <D> **** Detailed Description **** Health Physics needs to review the requirements for performing the sealed source surveillance (HSP-SSC-O801) and how it applies to sources that fall outside of the CGS license. The surveillance is designed to meet two goals: 1) to perform sealed source testing to meet LCS 1.7.8 and 2) to perform testing of generally licensed devices per 10CFR31. In some cases, generally licensed devices that fall outside of the CGS license (such as those owned by APEL lab) should have source custodians or radiation safety officers assigned to oversee remediation, repairs, or replacement of any leaking sources. There is ambiguity in how the CGS Health Physics Organization interfaces with organizations outside of the CGS license in responding to events related to the sources. <I> **** Actions Taken **** Discussed concerns with technicians performing the sealed source surveillance.
399445 | CR | 20190924 |  | 3 | Update SD000182 and AC systems powerpoint for Buchholz relay |  |  |  | N | NO | <D> **** Detailed Description **** After the recent trip and lockout of E-TR-M1, the Buchholz relays in TR-M1/2/3 are now alarm only. This change has been made permanent since then (EC 17550). Both SD000182 and the AC distribution PowerPoint reflects the temporary change but there is still some murkiness to the wording in â€˜trip function.â€™ Now that this is permanent, the SD and powerpoint need to more clearly say the functions of each Buchholz switch position in reference to the main transformer and also for the startup transformer so as to prevent any confusion. On another note, on page 56 of the SD in â€˜9. SM-7 Undervoltageâ€™ the 3 second time delay is wording is omitted. So as it currently reads everything that is on the 3 second TD happens immediately, which is not true. <I> MAN SYS SD000182 is listed on the ADL for ACTIVE status EC DEC 17550. <N> **** Equipment Description **** SD000182 and powerpoint
399446 | CR | 20190924 |  | 4 | WO: 02106114-01 CST Temp Calibration access issues. | N | N |  | N | NO | <D> **** Detailed Description **** During field prep in performance of this work order, it was discovered that several Temperature Controller elements could not be accessed due to recent scaffolding instillation in support of other work. <I> **** Actions Taken **** Supervision notified of access issues, and work taken back to planning to get rescheduled and additional tasks added.
399447 | CR | 20190924 |  | 4 | MD-42-2C12B WO# 02090344-01 | N | N |  | N | YES | <D> **** Detailed Description **** during performance of 10.25.187E found erratic resistance readings on NC aux contacts after applying current. The open contactor also has an approximatly one second pause before changing states during the low voltage pick up test. <I> **** Actions Taken **** notified supervisor and initiated CR | 02-00-MD-42-2C12B
399448 | CR | 20190924 |  | 3 | SIEM logs not configured to design specification | N | N |  | N | NO | <D> On 9/24/19, upon review of the Cyber Security SIEM configuration settings, it was discovered that the log retention policy was not configured as per the EC design specification. Although the retention settings met regulatory requirements, it did not meet Columbia's design inputs. This is not reportable as per 10 CFR 73.54. <I> Advised CSPM and initiated CR to correct the settings as per the EC 13492. Recommend assigning to Computer Engineering to align configuration to the EC and update Build-from-Scratch documents for the affected equipment, NET3-COMP-SIEM and NET4-COMP-SIEM. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review
399449 | CR | 20190924 |  | 4 | Chemistry Lab Leaking Sink | N | N |  | N | NO | <D> **** Detailed Description **** On the Radwaste Building 487' elevation in the chemistry laboratory the sink inside fumehood WEA-FAN-2A is leaking into the cabinets below. This is a contaminated fumehood. <I> **** Actions Taken **** Cleaned up leak and placed catch basin beneath leak. <N> **** Equipment Description **** Radwaste Building 487' Chemistry Laboratory, WEA-FAN-2A
399450 | CR | 20190924 |  | 4 | Failed EBU's | N | N |  | N | YES | <D> **** Detailed Description **** Craft performing WO #02141295-01 EBUT02 (TG441,471) EMERG LT ANNUAL INSPECT had 3 ebu's fail inspection (E-BU-T471/1, E-BU-T471/9 and E-BU-C202/471/1). <I> **** Actions Taken **** Craft stop notified supervision of failed EBU's, order and receive new batteries and placed on charger, impairment and CR was written as per PPM 10.25.156. Control Room was also notified. . Issued FPSI 19-0257 | 02-00-E-BU-C202/471/1,02-00-E-BU-T471/1,02-00-E-BU-T471/9
399451 | CR | 20190924 | CAQ | C | Unapproved modification on E-PP-7AF | Y | Y |  | N | YES | <D> **** Detailed Description **** Under WR 29150798, step 3, banana jack plugs were installed on E-PP-7AF (see attached pictures). This was not authorized under the Non-Intrusive Compensatory Measure per AR-EVAL 00397548. The intent of the NICM per SWP-CM-02 was to support monitoring of E-TR-7A/2 since it was degraded prior to recent replacement. The Multimeters were supposed to be installed on the available, empty disconnects associated with the degrading phase at the time with the panel door open, but secured, IAW the NICM. After replacement of the transformer, the NICM Multimeters were removed, but E-PP-7AF panel was changed and the change was not authorized by any AR-EVAL, or any drawings. At this moment, it is not clear if there are additional wires making connections not shown on EWD-46E-240. We need a WR/WO to restore E-PP-7AF configuration. E-PP-7AF is Safety Related, Crit C, Seismic 1 and loads are Safety Related. This was discovered after a review of open WRs, CRs, WOs and walkdown performed between yesterday and today. All associated with AR-EVAL 00397548. CR is intended to identify an unapproved configuration change and have it restored via the WO process. <I> **** Actions Taken **** Called CRS, SM, also discussed with Planner, Engineering Minor Mods Supervisor, EFIN Supervisor, Electrical Systems Supervisor and Systems Engineer <N> **** Equipment Description **** RW 467 Alternate SD Panel Room | 02-00-E-PP-7AF
399452 | CR | 20190924 |  | 3 | FWHs instruments need to be calibrated/repaired. | N | N |  | N | NO | <D> **** Detailed Description **** During trending and monitoring of FWHs performance, both Terminal Temperature Difference (TTD) and Drain Cooler Approach (DCA) measurements were found incorrect and unreliable. Some examples include negative temperature readings and/or out-of-range measurements. This wonâ€™t allow proper trending and monitoring of the FWHs especially the ones that have significant tubes plugged. This issue was identified in the past and WOs (see email for list of WOs in EDMS) were put in the system 2021 days ago (almost 6 years ago) to calibrate the instruments but no actions were taken and the work kept pushed and deferred. This work has to be done because monitoring TTDs and DCAs is the only available method to assess the condition of the FWHs. Recommend calibrating, repairing or replacing all temp. & pressure instruments for all FWHs starting in R25 <I> **** Actions Taken **** Discussed this issue with both the COND system and thermal performance engineers and initiated this CR
399454 | CR | 20190924 |  | 4 | MT-ELEV-1 call buttons sticking | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-1(NorthEast Rx bldg elevator) Rx bldg 572 call up button got stuck pushed in and remained illuminated which kept the elevator at that floor while the door opened and closed repeatedly. Once I was able to get the button unstuck the elevator responded as expected. Suggest evaluating all the buttons for contact and friction issues. <I> **** Actions Taken **** Informed SSS; | 02-00-MT-ELEV-1
399455 | CR | 20190924 |  | 4 | TB EOP Box Has been moved |  |  |  | N | NO | <D> **** Detailed Description **** The TB EOP Box and its associated ladder was moved from its normal space during the outage. Please retuurn the box and ladder to their designated orange-painted floor location next to COND-P-2A. Box is currently west of this position. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 441 near COND-P-2A.
399457 | CR | 20190924 |  | 4 | Fire brigade SCBA cabinet found unsealed. |  |  |  | N | NO | <D> **** Detailed Description **** During rounds, it was noted that one of the fire brigade SCBA cabinets (containing units #5 and #6) had a broken seal. These cabinets are sealed to ensure all equipment within is there and available for immediate fire brigade use. <I> **** Actions Taken **** Notified SMgt, inventoried cabinet, and re-sealed. <N> **** Equipment Description **** TB 441 E near fire brigade turnout station.
399458 | CR | 20190924 |  | 4 | wrong revision for Update IMDS COND-DPIC-5 Per EC 17711 |  |  |  | N | NO | <D> **** Detailed Description **** The file given to Document control had the revision number of one already in asset suite. Because of this, the RMS could not upload a PDF image that did not match the new revision to be placed in asset suite. Document said revision 7 but should have said revision 8. <I> **** Actions Taken **** Notified Supervision and requestor of the mismatch. The requestor resent a corrected copy with the correct revision number and the RMS created the new revision. CR is for tending purposes only.
399459 | CR | 20190924 | CAQ | C | WR/WOs for AR CRs cancelled without accept as-is disposition |  |  |  | N | YES | <C> This CR has been reopened and assigned CAQ C/PERFIMP. <D> **** Detailed Description **** Received AAA notification that the following Work Requests (Work Orders) associated with COMP-NA AR CRs had been cancelled: 1) WR 29101409 (WO 02033584) associated with AR CR 273666. 2) WR 29101657 (WO 02038021) associated with AR CR 274333. 3) WR 29101052 (WO 02082178) associated with AR CR 272744. 4) WR 29101028 (WO 02082179) associated with AR CR 272708. . This cancellation appears to have occurred without accept as-is disposition of the associated AR CR conditions with the following justification only: "WORK NO LONGER APPLICABLE Canceled (OX) by WRSC Back Log review." . <N> The OX code on the work order means that it is "accept as is". Attempting to contact the initiator to get more clarifiction since we do not see an issue as described in the CR. Per PPM 1.3.68 page 9 section 3.9 Work Control last bullet on page describes the OX code as "not to be worked" and used after the WRSC identifies the issue to be of very low or no consequence. From 6.22 Other Maintenance (OM) description last bullet "OX â€“ deficiency that is documented and evaluated by the appropriate team members that has been determined will not be worked." gives a good definition. Page 46 ot the procedure. | 02-00-D-BLDG-MISC,02-00-FDR-RO-2,02-00-W-BLDG-MISC
399462 | CR | 20190924 |  | 4 | Security OCA Bar |  |  |  | N | NO | <D> **** Detailed Description **** The Road around the OCA Barrier is in need of maintenance. There are mulitiple areas that are in need of leveling and additional gravel. Sand has built up in areas that could lead to vehicles getting stuck. <I> **** Actions Taken **** Generated CR/WR and contacted Security Maintenance Supervisor. <N> **** Equipment Description **** Road around the SDOCA
399463 | CR | 20190925 | CAQ | A | DSA-PCV-2C Leak | Y | N |  | N | YES | <C> Risk: High, Cause: Unclear Root Cause required <D> **** Detailed Description **** DSA-PCV-2C developed a leak which caused the DG-3 DSA system to depressurize. The leak was isolated and DSA pressure was restored to one of the air start headers, while the other had to remain isolated due to the leak. <N> A similar event happened in 2017 per CR 00369316, which was added as a cross reference. Graded at CRG as High Risk Severity "A" ; cause unclear; RCE required. | 02-00-DSA-PCV-2C
399465 | CR | 20190925 |  | 4 | MT&E found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065294 AWS Torque Tester- model AWS-MTMDP-4L would not power on. Not used during Calibration cycle. Rejected. DEF #7326A written. No Plant Impact. No Action Required.
399466 | CR | 20190925 |  | 3 | Enhancements to Model WO 00DKV9 Portable instrument inventor |  |  |  | Y | NO | <D> **** Detailed Description **** WO for Portable instrument inventory step 4.3 requiring the attachment of a Repair tag to each instrument going for routine calibration is an unnecessary use of resources. These instruments are gathered and sent to the Cal lab personnel, who can easily see from the cal sticker that it is due for cal. Step 4.3 should be eliminated and replaced with a note exempting all portable instrument being sent to Cal lab specifically for routine calibration. <I> **** Actions Taken **** Presented issue to HP Supervision. Reviewed HPI-0.16 section 4.3.
399468 | CR | 20190925 |  | 3 | document from EPP not most recent revision |  |  |  | N | NO | <D> **** Detailed Description **** using EPP to bring up ISP-MS/IST-A101 the technician showed rev 4 minor rev 2. The actual approved procedure is major revision 5. <I> **** Actions Taken **** call eWp hotline wrote cr <N> In the tablet version of DataGlance, when the technician is bringing in a new procedure into the package, the ePP library needs to be refreshed prior to uploading a document. . The tablet ePP keeps the procedures in memory and needs to be refreshed to bring in all the changes since the last refresh was performed.
399470 | CR | 20190925 |  | 4 | MT&E found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #45405 Found OOT & adjusted within specs. Not used during Calibration cycle. DEF #7327A written. No Plant Impact. No Action Required.
399471 | CR | 20190925 |  | 3 | SYS-2-17 INPO/WANO indicator guidance needs updating |  |  |  | N | NO | <D> **** Detailed Description **** SYS-2-17 System Heath Reporting Procedure section 6.10 (INPO/WANO) needs to be updated to reflect the change in how INPO/WANO PIC data is presented. There is no longer an INPO White category. There is only INPO Green, Yellow, or Red. In addition, step 6.10.7 needs to be updated since this does not reflect how INPO calculates Yellow and Red colors for safety systems (High Pressure Injection, RHR, and Diesel unavailability). As an enhancement, there should also be a step discussing where to find the specific system unavailability percentages and graphs for the health reports.
399472 | CR | 20190925 |  | 4 | RWCR alarm,relay spastic event 9/24/19 @ 0730 hrs. | N | N |  | N | YES | <D> **** Detailed Description **** The following alarms: P001-A16, windows 2-2 and 2-7 P001-A19,window 2-6 started cycling sporatically with numerous relay chatter from behind board panel. Event went away after about 5 minutes. Anomaly recorded on MWR-LR-75, MWR-LR-124 and FDR-LR-36. <I> **** Actions Taken **** MCR notified. <N> **** Equipment Description **** RWCR main processing panel G11-P001-2
399473 | CR | 20190925 |  | 4 | RWCU Blowdown Press High/low locked in | N | N |  | N | YES | <D> **** Detailed Description **** P602.A5 drop 5-7 alarm has been locked in and written up previously, but the AR and associated WO have been cancelled. This AR is to track the issue status and associated repair. <I> **** Actions Taken **** Re-wrote CR to track status <N> This is a known issue with work order to address, 02149246. The current plant configuration to compensate for RWCU-V-33 leakby and RWCU-V-34 bonnet leak is to close RWCU-V32 which is causing the low pressure. This will be the case until 33 & 34 can be repaired which will probably be a refueling outage. The system engineer is sending an email to the initiator to explain. Operations Management knows the situation and has agreed with the plant configuration. | 02-00-RWCU-FCV-33
399474 | CR | 20190925 |  | 4 | Dept. P Card mistakely used for personl purchase |  |  |  | N | NO | <D> **** Detailed Description **** On a regular basis I use my personal amazon prime account to purchase items for Columba Generating Station. This has saved the company a significant amount of money on item pricing and shipping costs. But in doing so I have several payment options attached to my account. On August 22nd I purchased a personal item and by mistake charged it to the wrong credit card. The amount mistakenly charged to the dept. P card was $12.26. <I> **** Actions Taken **** A personal check in the amount of $12.26 to Energy Northwest has been mailed to P.O. Box 2 Finance was notified and document filed in audit folder. Treasury notified on pending reimbursement.
399476 | CR | 20190925 |  | 4 | Foreign materials found during RCC-HX-1B inspection | N | N |  | N | YES | <D> **** Detailed Description **** During RCC-HX-1B inspection under WO 02120672, foreign materials were found on the tubesheet and the channel heads and inside the tubes. The foreign materials are clams, cooling tower fillers and some plastic pieces. The condition of outlet channel head was worse than the inlet channel head with lot of tubercles and clam shells sticking to the shell (see EDMS). Some areas with pitting were also found on the inner surface of the channel heads as well. The channel heads replacement is tracked under CR 364288 and AR 1245, therefore, no further action is currently required. The heat exchanger tubes, tubesheets and channel heads will be cleaned as part of the PM and the foreign materials will be also retrieved. This is for trend. <I> **** Actions Taken **** Communicated the issue to the system engineer and chemistry and initiated the CR <N> **** Equipment Description **** RX448 | 02-00-RCC-HX-1B
399477 | CR | 20190925 | CAQ | D | Unsat Sealed Source Surveillance | N | N |  | N | NO | <C> CR was edited at Originators request to remove inaccurate information <D> **** Detailed Description **** During the sealed source surveillance, a leaking Ni-63 source was discovered in a generally licensed device. This represents an unsatisfactory result for the sealed source surveillance (HSP-SSC-O801). This source is a generally licensed device and its leakage is greater than 0.005 microcuries, which makes it reportable to the NRC under 10CFR31.5(c)(5). This source does not fall under LCS 1.7.8 or the reportability criteria associated with that specification. <I> **** Actions Taken **** Discussed findings with Operations personnel. Generated an AR-REG to report the leaking source to the NRC. Removed the device from service as required by 10CFR31.5(c)(5). <N> Verified with RP that this sealed source is not a Columbia Gen Station owned sealed source subject to LCS 1.7.8 requirements. (documenting unsat surveillance only, CR 398991 is tracking actions related to the leaking source) per email from K. Gillard 9/26/2019
399479 | CR | 20190925 | CAQ | C | Unapproved QL-1 Reciept Inspection Plan Used |  |  |  | Y | NO | <D> **** Detailed Description **** Receipt Inspection for PO 350224 (RIP No. 279) was not documented on an approved Receipt Inspection Plan, resulting in a deficiency in the vaulted QA record. The correct approvals had in fact been obtained from Engineering, but the inspection results were not documented on the Engineering signed/approved form. This issue was identified during the 2019 NIEP Evaluation (AU-QP-QA-19). Recommend CAQ action to Quality Services to have the RIP signed by Procurement Engineering. <I> **** Actions Taken **** Notified Quality Supervisor and Manager.
399480 | CR | 20190925 |  | 4 | HWC-H2D-409 failed to calibrate during 10.27.97. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02119905 01 (10.27.97) HWC-H2D -409 failed to calibrate within values listed in table 7.4a <I> **** Actions Taken **** Notified I/C Supervision and informed Operations. Performed 2nd calibration attempt as allowed in 10.27.97. with no success. Initial attempt value of 63 % and 2nd attempt of 74% was obtained. Expected value of 50% as directed in 10.27.97. not achieved after completion of 10.27.97. Wrote CR/WR as directed by 10.27.97 completed surveillance with all other area monitors as left values SAT. <N> **** Equipment Description **** HWC-H2D-409
399482 | CR | 20190925 |  | 3 | Training Program Committee Meetings Not Held |  |  |  | Y | NO | <D> **** Detailed Description **** Quality Department Training Program Committee is not being administered in accordance with TPD-21. For example, contrary to Section 2.3, the training committee has not been sustained, and there is no evidence of completion of qualification GN000267 or JFGs. The Quality department has however continued to conduct their annual training, i.e., most recently in August 2019. This issue was identified during the 2019 NIEP Evaluation (AU-QP-QA-19). Recommend NCAQ action to Quality to evaluate and take action to conduct the meetings or change the procedure. <I> **** Actions Taken **** Discussed with the Quality Manager. <N> This is non-accredited training.
399484 | CR | 20190925 | CAQ | D | MET tower temperature element as found out of tolerance |  |  |  | N | YES | <D> **** Detailed Description **** CAL CODE 0068493-02 as found was out of tolerance Installed in Met Tower 03-06-19 as MET-TE-10A, 245 ft level Removed from Met Tower 05-10-19 Delta Temperature with element at 33 ft level out of tolerance, LCS 1.3.7.8 applicible. Past functionality. <I> **** Actions Taken **** Per LCS 1.3.7.8 A, wrote CR. <N> This CR documents an out of cal temperature element used in the MET tower that is currently not installed and therefore does not impact current functionality. Past functionality is not assessed for LCS required SSC's unlike past operability for TS SSC's. | 02-00-MET-TE-10A
399485 | CR | 20190925 |  | 4 | Comp. pt. S025 | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Comp. pt. S025 (CBD flow indication) is out of tolerance at the lower end of its range. S025 reads 0gpm until we simulate approximately 800gpm input value at the transmitter CBD-FT-10 at which time it starts indicating within tolerance through the rest of its range. <I> **** Actions Taken **** Notified supervision and computer engineering <N> **** Equipment Description **** PPC S025mv
399486 | CR | 20190925 |  | 4 | HVAC system for security check point needs a Thermosat. | N | N |  | N | YES | <D> **** Detailed Description **** The BRE at the security check point needs a temperature controller installed on the HVAC unit. This building needs to be maintained at 72 degrees for proper operation of SEC-XD-9 and SEC-XD-10. <I> **** Actions Taken **** Informed Security and supervision. <N> **** Equipment Description **** HVAC inwall unit at security check point BRE.
399487 | CR | 20190925 | CAQ | C | Alternate vulnerability screening method not documented |  |  |  | N | NO | <D> **** Detailed Description **** *** Detailed Description *** Self-Assessment 397657 During USA peer assessment of checklist items 6 and 22 it was identified that the methods and alternate frequencies for some CDAs were not properly documented and approved. A prior decision to perform the screening using alternate methodologies was not documented. <I> **** Actions Taken **** Reviewed with department management. Does not impact plant operations. Please assign CAT 3 to AR-ITCYBER. <N> Cat C ITMGMT Causes are known as it was identified that not all basis/methods used to screen vulnerabilities have been documented and approved. Action created This item is low/medium risk as the industry inspections have identified similar issues at other stations and categorized the issue as both minor or as a NCV. CGS has not been inspected but has identified this issue based on review of operating experience. This is not reportable per 10 CFR 73.54
399488 | CR | 20190925 |  | 3 | SWP-CSW-24 needs additional guidance |  |  |  | N | NO | <D> **** Detailed Description **** *** Detailed Description *** Self-Assessment 397657 During USA peer assessment checklist items 16 and 17 it was identified that SWP-CSW-24, Cyber Security Procurement needs additional guidance in how to follow the process. The procedure needs to provide guidance about storage of approved test plans, where to store completed test plans, templates/previous samples as examples of what good looks like, and if test plans will be part of the design process. <I> **** Actions Taken **** Reviewed with department management. Does not impact plant operations. Please assign CAT 3 to AR-ITCYBER. <N> Assign Cat 3 to ITMGMT Causes are known as procedure lacks guidance for cyber test plans required from non-trusted vendors and action created to update procedure This item is low risk as the no instances have been identified in which the procedure has not been performed. This is not reportable per 10 CFR 73.54
399489 | CR | 20190925 | CAQ | C | CDA port usage not aligned to drawing |  |  |  | N | NO | <D> **** Detailed Description **** *** Detailed Description *** Self-Assessment 397657 During USA peer assessment walk down of checklist item 30 it was identified that a port did not match the design document port. <I> **** Actions Taken **** Reviewed with department management. Does not impact plant operations. Please assign CAT 3 to AR-ITCYBER. <N> Cat C ITMGMT Causes are known as it appears the wrong port was documented and actions created This item is low/medium risk as the industry inspections have identified similar issues at other stations and categorized the issue as both minor or as a NCV. CGS has not been inspected but has identified this issue based on review of operating experience. This is not reportable per 10 CFR 73.54
399490 | CR | 20190925 |  | 3 | SWP-CSW-21 revision required |  |  |  | N | NO | <D> **** Detailed Description **** *** Detailed Description *** Self-Assessment 397657 During USA peer assessment of checklist 49 it was identified that SWP-CSW-21 contained a PMID that has been retired. <I> **** Actions Taken **** Reviewed with department management. Does not impact plant operations. Please assign CAT 3 to AR-ITCYBER. <N> Assign Cat 3 to ITMGMT Causes are known and action created to review procedure and validate all PMID information is correct and up to date. This item is low risk as the no instances have occurred in which the created PMs have not been performed. However there is the potential for a PM to be missed This is not reportable per 10 CFR 73.54
399491 | CR | 20190925 |  | 3 | SWP-CSW-12 questions not embedded into CDA process |  |  |  | N | NO | <D> **** Detailed Description **** *** Detailed Description *** Self-Assessment 397657 During USA peer assessment of checklist item 76 it was identified that SWP-CSW-12 has two questions that need to be answered in order to change communications path to go to a higher classification level. These questions need to be added to the forms to ensure they are answered. There has not been an instance to date in which these questions should have been answered and were not. <I> **** Actions Taken **** Reviewed with department management. Does not impact plant operations. Please assign CAT 3 to AR-ITCYBER. <N> Assign Cat 3 to ITMGMT Causes are known as these questions were missed when updating the assessment process and action created to update assessment for m(s) to include the questions. This item is low risk as there are no instances that have occurred that would are in violation of the procedure however there is the potential for the steps to be missed This is not reportable per 10 CFR 73.54
399492 | CR | 20190925 |  | 3 | SFAQ not referenced in procedures |  |  |  | N | NO | <D> **** Detailed Description **** *** Detailed Description *** Self-Assessment 397657 During USA peer assessment of checklist section 15 it was identified that procedures did not contain references to the SFAQs as needed. <I> **** Actions Taken **** Reviewed with department management. Does not impact plant operations. Please assign CAT 3 to AR-ITCYBER. <N> Please assign Cat 3 to ITMGMT Causes are known and actions created This item is low risk as the detail from the SFAQs are outlined in the cyber procedures but it is not referenced This is not reportable per 10 CFR 73.54
399493 | CR | 20190925 |  | 3 | CBD-V-1 Packing Overtightened | N | N |  |  | YES | <C> ANON CR generated. Reviewed for Safety Conscious Work Environment (SCWE), forwarded to OPS for review. <D> **** ANONYMOUS CR - Detailed Description **** CBD-V-1 packing is comically overtightened. Either the valve needs to be replaced, or the craft responsible. | 02-00-CBD-V-1
399494 | CR | 20190925 | CAQ | D | Washington State EOC CRASH inoperable | N | Y |  | N | YES | <D> **** Detailed Description **** While the Washington State EOC was working on the dedicated fax the associated phone equipment failed disabling their CRASH. Energy Northwest telecom techs were testing with them when the equipment on the State end failed. <I> **** Actions Taken **** Notified EP. The Dial up line and Commercial line confirmed operable. The Commercial Fax was also retested to confirm it is operable. The problem is at Camp Murray. Recommend trend and closing to dedicated fax WR 29151210 to track. CAQ-D <N> **** Equipment Description **** Washington State EOC Camp Murrey
399495 | CR | 20190925 |  | 3 | AED IMDS OG-FS-3/2 needs updated or made historical |  |  |  | N | YES | <D> **** Detailed Description **** Originally, Off Gas pretreat rad sample low/high flow switch OG-FS-3/2 (T441' OG-CP-1) provided output to/for W501' main control room annunciator 4.602.A5-4.5 but this annunciator was a nuisance to plant Operations and was eliminated from the plant design via implementation of EC MPDC 5546. However, AED IMDS OG-FS-3/2 was not updated to indicate its Annunciator output to Remote Alarm Location 4.602.A5-4.5 no longer exists. AED IMDS OG-FS-3/2 needs to be updated or simply made historical. Suggest resolution by AR-DMC as this is now a Legacy issue. This was noted during document reviews associated with AR EVAL 397260 for OG-FIC-3/2 replacement. This is an administrative issue only. <N> Correction - suggest resolution by AR-DEI (not AR-DMC). Could also come back to AR-MODS for resolution. | 02-00-OG-FIC-3/2,02-00-OG-FS-3/2
399496 | CR | 20190925 |  | 3 | Security Rifle 375 |  |  |  | N | YES | <D> **** Detailed Description **** Security Rifle 375 Aimpoint Location needs to be evaluated. <I> **** Actions Taken **** Rifle taken out of service, contacted security training and generated CR for tracking. <N> **** Equipment Description **** Bldg 88 Vault
399503 | CR | 20190926 | CAQ | C | Equipment cyber classification change needed per industry OE |  |  |  | N | NO | <D> **** Detailed Description **** During review of industry OE it was identified that a piece of equipment requires a cyber security classification change. This piece of equipment is currently not part of the current cyber scope. <I> **** Actions Taken **** Discussed with Security Please assign Cat C to ITMGMT Contact Cyber Security for additional details. This is not reportable per 10 CFR 73.54 <N> The piece of equipment based on industry operating experience will need to be re-evaluated for cyber classification and additional physical controls added. This item is low/medium risk as the industry inspections have identified similar issues at other stations and categorized the issue as both minor or as a NCV. CGS has not been inspected but has identified this issue based on review of operating experience.
399504 | CR | 20190926 |  | 3 | Training slide for RP000001 disrepancy with RPT-01 |  |  |  | N | NO | <D> **** Detailed Description **** For the RP000001 requal. on slide towards the end is say the Delta Suit has a protection factor of 1. The controlled Document RPT-01 on page 46 of 50 shows the Delta Suit having a protection factor of 5,000. <I> **** Actions Taken **** Generated CR. WIll insert slide from CBT showing typo on EDMS.
399505 | CR | 20190926 |  | 3 | Internal Audit Schedule approval signature not obtained |  |  |  | Y | NO | <D> **** Detailed Description **** The 2019 - 2021 Internal Audit Schedule, Revision 0, issued May 28, 2019, did not contain the Quality Managerâ€™s approval signature as required by SWP-ASU-01, Section 3.5.2, and QSI-26, Section 3.5.7. The two preceding memorandums for Internal Audit Schedules, 2017-2019 Revision 1, and 2018-2020 Revision 2, contained the Quality Managerâ€™s approval signature. . The approval was sent via email, but approval was not documented on the memorandum with the schedule. . This issue was identified during the 2019 NIEP Evaluation (AU-QP-QA-19). Recommend NCAQ action to Quality to evaluate and take action to ensure memorandums contain Quality Manager's approval signature. <I> **** Actions Taken **** Discussed with the Quality Manager
399506 | CR | 20190926 |  | 3 | Incorrect reference to QAP-ASU-05 step |  |  |  | Y | NO | <D> **** Detailed Description **** Instructions on Form 23776 for the qualification and certification of inspection personnel, #9 contains an incorrect reference to QAP-ASU-05, paragraph 4.7.1 instead of 4.7.3. This error has affected the recertification documentation for one Level IIID receipt inspector, but does not affect his recertification. . This issue was identified during the 2019 NIEP Evaluation (AU-QP-QA-19). Recommend NCAQ action to Quality to evaluate and correct the reference. <I> **** Actions Taken **** Discussed with the Quality Manager
399507 | CR | 20190926 | CAQ | C | Documentation defined in ANSI/ASME N45.2-1978 not performed |  |  |  | Y | NO | <D> **** Detailed Description **** Documentation of the basis for determination of Level III capability requirements delineated in Table 1 of ANSI/ASME N45.2-1978 is not being performed, and is not adequately translated into implementing procedure QAP-ASU-05. . The Level IIID evaluation for certification is performed by the Quality Supervisor per QAP-ASU-05. The basis for the Supervisor performing this evaluation is described in the OQAPD, Appendix II. However, the documented evidence for the basis for the duties of the Level III performed by the CGS QC Supervisor could not be produced, and the requirement for this â€œbasis documentâ€ is not referenced in QAP-ASU-05 . This issue was identified during the 2019 NIEP Evaluation (AU-QP-QA-19). Recommend NCAQ action to Quality to evaluate and translate into implementing procedure QAP-ASU-05. . <I> **** Actions Taken **** Discussed with the Quality Manager .
399515 | CR | 20190926 |  | 4 | Inadequate Lighting in RWCU HX Room | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Inadequate lighting was noted in the RWCU Heat Exchanger room. This room has been an ongoing concern, and it creates an avoidable industrial safety risk in a radiologically significant area. <I> **** Actions Taken **** Discussed concerns at OFM with the management team. <N> **** Equipment Description **** RWCU HX Room Lighting
399517 | CR | 20190926 |  | 3 | R24LL: Revise SOP-CW-FILL prior to R25 |  |  |  | N | NO | <D> **** Detailed Description **** Remove steps 5.1.31,32,33. These steps will occur some time after refilling the CW basin and their placement in this section will prevent reestablishing CW basin chemistry in a timely manner following basin refill.
399519 | CR | 20190926 |  | 3 | Updates needed to SD000194 Uniterruptible Power Supply Sys |  |  |  | N | NO | <D> **** Detailed Description **** The references to the Learning Objectives in the system text (right margin) were inadvertently removed at revision 14. These references should be restored to maintain consistency with other system descriptions. Also the System Interrelationships in section VIII seem to be incomplete when referenced against ABN-ELEC-INV. Suggest updating the system description to provide a more complete list. Finally, the kirk key configuration on E-IN-1 has changed slightly. Figure 2 of the system description should be updated accordingly.
399520 | CR | 20190926 |  | 4 | FIN personnel pulled off of investigating PPC-CRT-RWM |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** FIN personnel pulled off of investigating PPC-CRT-RWM to support I/C Shop scheduled work. There is only two I/C FIN Techs today. This CR is for trending only
399521 | CR | 20190926 |  | 4 | Deschutes North Entrance mat not laying flat |  |  |  | N | NO | <D> Noted the corner of the floor mat inside the entrance door get turned up while an individual was entering the Deschutes building via the north entrance door next to the Willamette building. . Inspected the mat and it does not appear to be laying flat at one point. See EDMS photos. <I> Layed the mat back down. Briefed Supervisor and Industrial Safety. <N> Walked down the area - flattened out the particular mat. In speaking with the Facilities staff, some of the mats were changed out today. It wasn't apparent if this particular one was swapped out or not. However the current condition is acceptable.
399523 | CR | 20190926 |  | 4 | MULTIPLE DUPLICATE TRAINING RECORDS SENT TO RECORDS CONTROL |  |  |  | N | NO | <D> **** Detailed Description **** THREE TRAINING RECORDS WERE SENT TO RECORDS CONTROL AND WHILE RECORDS CONTROL PERSONNEL WERE PROCESSING THEY RECIEVED AN ERROR THAT THE ETAR NUMBER WAS ALREADY USED. (ALREADY EXISTED IN ASSET SUITE) <I> **** Actions Taken **** NOTIFIED MY LEAD/SUPERVISOR. CR. WRITTEN. RECORDS ARE BEING SENT BACK TO OPERATIONS TRAINING FOR CORRECTIONS AND RE-SUBMITTAL. <N> The duplicate training records were submitted on a Record Transmittal to Records Control dated 6/20/18 by an individual who no longer works at the company. Records Control received the records on 6/21/18. The duplicate records are class IDs 023511, 023488, and 822824. Records Coordinator verified that the records were retrievable from the records database, and duplicates were shredded.
399524 | CR | 20190926 | CAQ | D | WOA-V-51B EHO Spring Alignment | Y | N |  | N | YES | <D> **** Detailed Description **** This CR is for trending purposes only. An equipment operator noted that the EHO (valve actuator) spring associated with WOA-V-51B is crooked and slightly out of the â€œpocketâ€ that retains it. The system engineer walked down the actuator and confirmed this configuration as noted by the equipment operator. WOA-V-51B is the Control Room Remote Air Intake #2 (SE) Isolation Valve. It remains in the locked open position. This valve is operated by a hand crank and does not rely on the spring actuator for valve operation. Although the spring is not completely straight and out of its â€œpocketâ€, there is no immediate concern of the actuator failing or preventing manual operation of this valve. It is common for these valves to be slightly out of plumb and it will not affect the actuator operation. This valve remains operational and functional. See EDMS for picture of this condition. | 02-00-WOA-V-51B
399525 | CR | 20190926 |  | 4 | CRD-V-16A Indication of seat leakage | N | N |  | N | YES | <D> **** Detailed Description **** CRD-V-16A is warm on both sides of the check valve. The discharge temperature of CRD-P-1B can be felt along the entire pipe going to CRD-P-1A, indicating that there is reverse flow through the A CRD Pump discharge check valve CRD-V-16A into CRD-P-1A. CRD-P-1B discharge pressure is normal, indicating that the flow is not impacting the operation of CRD-P-1B yet. DP across the check valve is 1500 psid, so leakage is expected to increase over time. This requires an outage to repair, since the valve requires both pumps out of service to repair. | 02-00-CRD-V-16A
399527 | CR | 20190926 | CAQ | D | DG roof hatch seal inspection results (WO 02115845). | Y | N |  | N | YES | <D> **** Detailed Description **** The DG roof hatch seals were found to be in satisfactory condition. However, during the inspection (WO 02118545) the following discrepancies were noted. All three DG roof hatches need to be recoated. The coating on the hatches is starting to peel and chip particularly in the areas where there is embedded steel. The coating should be applied to all three hatches similar to the DG 2 hatch. The condition of the coating does not affect the capability of the roof plug to perform its design functions. There are holes in the roof membrane around the hatch for DG 1 and DG 2, DO-FA-1B (west flame arrestor), and near a roof vent/penetration in the NW corner. The roof membrane holes identified in this CR have all been previously identified. See map in EDMS. <I> **** Actions Taken **** Informed Supervisor, discussed with FIN. <N> **** Equipment Description **** DG Roof | 02-00-D-BLDG-MISC
399529 | CR | 20190926 |  | 4 | PSR-V-640 and PSR-V-641 labelled incorrectly. | N | N |  | N | YES | <D> **** Detailed Description **** While hanging D-PSR-SR-49-002 it was discovered that the labelling on PSR-V-640 and PSR-V-641 were swapped. Due to this labelling error the leaking valve, PSR-V-641, was written up as PSR-V-640 packing leak. Due to this labelling error the clearance orders for doing the repair work tagged shut the drain path by shutting PSR-V-640 which is labelled PSR-V-641. Both AED MEC M607-4 and CVI ISO 317 -00,6191 agree that the order of valves from the RWCU system to the PSR-SR-49 is RWCU-V-625, PSR-V-641 and PSR -V-640 then PSR-SR-49. The actual labelling in the field is RWCU-V-625, PSR-V-640 and PSR-V-641 then PSR-SR-49. The labels for PSR-V-640 and PSR-V-641 need to be swapped. Please see EDMS for drawings. <I> **** Actions Taken **** Informed supervision and wrote AR/WR. <N> **** Equipment Description **** Rx 548 RWCU Hx Rm | 02-00-PSR-V-640,02-00-PSR-V-641
399530 | CR | 20190926 |  | 4 | FDR-FCV-102 Slow To Respond | N | N |  | N | YES | <D> **** Detailed Description **** When starting MWR processing, the system did not reach 70gpm until FDR-FC-23 was at 70% demand (usually this happens below 50%). At 75% demand the valve was admitting about 80gpm, but after a few seconds sytem flow shot up to over 110gpm. At this time FCV-23 demand was lowered to 48% and flow returned to 80gpm. The controller was placed in automatic per SOP-RW/MWR-OPS and the system appears to be controlling flow adequately. This is not usual behavior for the system, and the health of FDR -FCV-102 is in question. This valve is important for daily radwaste processing. <I> **** Actions Taken **** Informed MCR | 02-00-FDR-FCV-102
399531 | CR | 20190926 |  | 4 | Valve EPN Tags incorrectly labeled (PSR-V-640 and PSR-V-641) | N | N |  | N | YES | <C> DUPLICATE OF 399529 <D> **** Detailed Description **** During clearance hang activity for D-PSR-49-002 FIN RO recognized that the EPN tag labeling PSR-V-640 and PSR-V -641 where labeled incorrectly (verified using print M607-4 and ISO 317-00,6191) . This issue changes the scope of the C/O boundary. The C/O was revised and a JHA added to WO â€œ02147489-02 REPLACE BONNET AND TORQUE - PSR-V-640â€ identifying single point isolation. WO 02147489-01 to identify the correct valve to be worked, (FIN RO also identified that PSR-V-641 was leaking from the packing and was identified incorrectly due to the EPN issue) <I> **** Actions Taken **** Revise C/O, WO and relabel Valves per M607-4 and ISO 317 -00,6191 | 02-00-PSR-V-640
399532 | CR | 20190926 | CAQ | D | Received FPC RM COOLER FLOW LOW/ TEMP HI alarm | Y | Y |  | N | YES | <D> **** Detailed Description **** Received FPC RM COOLER FLOW LOW/ TEMP HI, H13.P812.R1.4-2, alarm shortly after starting SW-P-1A. The as found flow through RRA-CC-20 as indicated on SW-FI-71A was 35 gpm (per 4.812.R1 4-2, the low flow alarm setpoint is LE 35 gpm). Per OSP-SW-C101, the recommended flow range is 40-45 gpm, and the minimum operability value is 38.5 gpm. Performed OSP-SW-C101 to fully open SW-V-184A for 3 minutes, and then restore flow to the recommended flow range. As left flow as indicated on SW-FI-71A is 43 gpm and the alarm is clear. This is a repeat occurrence â€“ reference WR 29151738 written on 09/24/19 for the same issue. Addressing this low flow alarm requires entry into the FPC HX room on RX 548â€™ - a high radiation contaminated area. A total of 1.7 mrem was accumulated between 2 EOâ€™s on this occurrence. <I> **** Actions Taken **** Notified the CRS and Shift Manager. Submitted CR and WR. Performed OSP-SW-C101 to flush and clear alarm. | 02-00-RRA-CC-20
399533 | CR | 20190926 | CAQ | C | Ineffective CAP Process leads to three recent events |  |  |  | N | NO | <D> **** Detailed Description **** In the past two weeks there have been three notable events with previous precursor CRs that did not alleviate the causes. The three events were: (1) COND-LCV-11 drifted open resulting in a downpower with the potential for a SCRAM, (2) Loss of an SCW pump with heightened station risk, (3) Loss of HPCS DG DSA pressure resulting in a loss of HPCS Safety Function and a Licensee Event Report. (1) CR 398977 â€œCOND-LCV-11 drifted openâ€ and CR 398977 â€œCOND-LCV-11 tubing disconnectedâ€ Precursor event CR 188920 â€œAirline disconnected at COND -LCV-11â€ and CR 189187 â€œAirline vibrates excessivelyâ€ led to WO 01167092 COND-LCV-11 INSTALL PREFORMED CHANNEL MOUNT ON AIR LINES. WO 01167092 was FINISHED on 6/10/2014 without supporting the air lines, with a note stating that â€œthe tubing runs are too long and nowhere to put a rigid support.â€ (2) CR 399211 â€œDegraded SCW-P-2 pumpâ€ and CR 399303 â€œFound SCW-V-471 out of positionâ€ Precursor event CR 255805 â€œStandby SCW pump auto startedâ€ noted SCW-V-471 was found â€œout of position nearly full closed.â€ The CR 255805 assignment for the valve being out of position was closed with â€œThe cause of SCW-V-471 being slightly open vice 3/4 turn open is indeterminate.â€ (3) CR 399463 â€œDSA-PCV-2C Leakâ€ Precursor event identified in CR 369316 â€œDSA-V-4A leaking byâ€ and CR 369318 â€œDSA-PCV-2C venting off DSA-AR-2Câ€ very similar. Both the 2017 precursor event and the 2019 event had the same thing happen â€œwhile attempting to drain only DSA-AR-1C, DSA-PCV-2C started venting DSA-AR-2C.â€ Both CRs from the precursor event (AR 369316 and 369318) were made Severity D COMP-NA. <I> **** Actions Taken **** This CR was generated in an attempt to improve the CAP process. Consider not closing most CR issues immediately to Work Requests when further evaluation may be required. This CR identifies a program issue and there is no impact on any plant equipment. <N> **** Equipment Description **** None
399534 | CR | 20190926 |  | 3 | R24LL: SOP-ENTRY-WETWELL change |  |  |  | N | NO | <D> **** Detailed Description **** Change SOP-ENTRY-WETWELL to specify Caution Tags rather than Danger Tags for wet well spray valves. See EDMS for details and justification. <I> **** Actions Taken **** initiated CR.
399535 | CR | 20190926 |  |  | Relocate In storage CID's requiring PM's | [5 empty] | <D> Supply Chain has committed to relocate the large components (Pumps, Motors, Transformers and Generators) valued over $100K and requiring in-storage PMâ€™s to one location (Building 188) to reduce the challenge of locating equipment identified for in-storage maintenance. This is to be cross referenced to the AR-390209 (QA) Elevation - Spare Equipment Preventive Maintenance and it has been added to the Supply Chain Services Excellence Plan.
399536 | CR | 20190926 |  | 3 | SYS-4-31 Should be Revised |  |  |  | N | NO | <D> **** Detailed Description **** Recommend changes to SYS-4-31, System and Equipment Performance Monitoring and Trending Program. EDMS contains a marked up version. This is an administrative procedure and does not represent a degraded or non-conforming condition. <I> **** Actions Taken **** Notifed my supervisor
399537 | CR | 20190926 |  | 4 | Degraded sealing surface on RCC-HX-1B | N | N |  | N | YES | <D> **** Detailed Description **** During performing the clean and inspect PM on RCC-HX-1B under WO 02120672, the gasket sealing surface found to be pitted and degraded. However, the new gasket is 1/8â€ thick and itâ€™s going to be used together with an RTV to seal the sealing surface. Therefore, a leak due to this problem from that area is not expected before the next inspection date (in 2023). Recommend replacing the heads in the next maintenance window (in 2023). Replacing the heads is already tracked under AR CR 364288 and AR EVAL 1245. Therefore, no further actions are needed. <N> **** Equipment Description **** RX548 | 02-00-RCC-HX-1B
399538 | CR | 20190926 |  | 3 | FY19 impl Capital projects w/o FY20 funding for Eng closeout |  |  |  | N | NO | <D> **** Detailed Description **** Some ENL charges from Design Engineering Capital groups have been made to the FY20 Minor Mods (CAP) budget (project 01302402) that were specific to other project scope and not associated with minor plant modification projects. For example, charges were made to complete administrative closeout (e.g., drafting drawing updates and Engineering project closeout) for a number of FY19 Capital projects that had been funded for FY19 but apparently not funded into FY20 because field implementation had been completed during FY19. The FY19 Capital projects should have gone back to Asset Management to obtain the needed FY20 Capital project funding for these FY20 charges. <I> **** Actions Taken **** Discussed with PHCSC, Asset Management, and Design Engineering personnel.
399540 | CR | 20190926 |  | 4 | Excessive Blowdown CAS-C-1C | N | N |  | N | YES | <D> **** Detailed Description **** Excessive blowdown from drain on CAS-C-1C. Burping out of Equipment Drain (more than normal) and onto the floor extending all the way to the air recievers. <I> **** Actions Taken **** Swapped to CAS-C-1A. | 02-00-CAS-C-1C
399541 | CR | 20190926 |  | 3 | Building 32 dust collector motor wired incorrectly | N | N |  | N | NO | <D> **** Detailed Description **** Recently a new dust collector was installed for the Insulators band saw in Building 32. The motor is a 230v motor and was wired for 480v. The motor was turned on and immediately seized up. The area was secured and the motor was tagged to not use. This is not plant equipment. <I> **** Actions Taken **** Contacted Site Support Manager <N> Williams Plant Services. The dust collector is a tool in the Insulators Shop. Based on a conversation with one of the electricians, the motor did not seize up as documented. After about three minutes of run time, the motor began to lightly smoke so the electrician shut off the power to the motor. The motor is a 230/480 volt capable motor. The electricians wired the dust collector for 480 volt as specified but did not notice the motor was wired for 230 volt and therefore did not change the conductor termination points as needed. They will make the necessary conductor location changes this morning and run the motor to determine if there is any damage. The motor was wired 230 volt from the manufacturer.
399542 | CR | 20190926 |  | 4 | SEC-MDET-11 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** The handheld metal detector SEC-MDET-11 needs maintenance. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Unit taken out of service, CR/WR generated | 02-00-SEC-MDET-11
399543 | CR | 20190926 | CAQ | D | CBD-SR-2 proprtional light did not light up. | N | Y |  | N | YES | <D> **** Detailed Description **** Swapped CBD-SR-2 from Time to Propertional with toggle switch. Time light went out the proprtional light did not light up. Power light lit and counter continued to count. <I> **** Actions Taken **** Performed manul sample and verified a sample was taken. Informed CRS. <N> 26SEP19 ~2300 - noted that proportional light is lit. | 02-00-CBD-SR-2
399544 | CR | 20190926 |  | 3 | Incorrect flags for Digital Device in Portal J |  |  |  | N | NO | <D> **** Detailed Description **** On 9/26/2019, the device, PPC-CRT-RWM, was found to not be flagged correctly in Portal J as a digital device and was found to not have been assessed to be included in the cyber security program. This is not reportable as per 10 CFR 73.54. <I> **** Actions Taken **** Digital flag has been turned on for this device. An assessment by Cyber Security to scope PPC-CRT-RWM into the cyber security program as an indirect CDA will be accomplished. This is not reportable as per 10 CFR 73.54.
399545 | CR | 20190926 |  | 4 | E-BU-DG441/6 is flashing "Charger Fault" | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-DG441/6, the emergency light located in DG3 room near the day tank door, is flashing the light sequence indicating "Charger Fault." Please investigate and repair. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** DG3 room | 02-00-E-BU-DG441/6
399546 | CR | 20190926 |  | 3 | PPM 1.5.13, Criticality definition basis [NRC identified] |  |  |  | N | NO | <D> **** Detailed Description **** During discussions on 9/24/19, the NRC resident inspector noted that Columbia does not specify the basis for the definition of component criticality. Columbia personnel explained the definition came from INPO AP-913 document. However, AP-913 is not referenced anywhere in PPM 1.5.13 or other station procedures to clarify the basis of component criticality definition(s). Recommend CR be assigned to maintenance programs to address the issue. <I> **** Actions Taken **** Discussed with Maintenance Support (procedure owner) Supervisor. Confirmed that there was no other maintenance procedure that provided further clarification on the criticality definitions. And, wrote the CR.
399547 | CR | 20190926 | CAQ | D | DG3 DSA dew point air sample failed after 10 blowdowns | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performace of 10.27.90C (02130222-06) the Dew Point sample failed. We informed Ops and they blew down the DSA system 10 times with no passing results. The last time the dew point was checked on 9/26/19 @ 1700, the reading was -15 DEG C. Minimum passing sample is -19 DEG C or lower. <I> **** Actions Taken **** Informed CRS, Supervision, created CR/WR to replace the desiccant. <N> **** Equipment Description **** 441 DG3 room
399548 | CR | 20190926 | CAQ | C | (NRC) Wait times following painting prior to running SGT |  |  |  | N | NO | <C> AR/CR Changed from a NON-CAQ 3 to a CAQ C by MRT <D> **** Detailed Description **** The NRC resident questioned why there were no wait times specified in procedures for charcoal filtration units such as SGT, CREF, and the TSC Filter unit. The procedures reference a P&L that cautions against running these units when paint fumes, chemical fumes, or smoke are present in the area, but no wait times are specified.PPM 10.2.14 provides a table in attachment 21 that specifies cure times for paints and thinners used at CGS. This may be a good starting point for establishing a wait times. Recommend engineering evaluate for the need to specify wait times in ops procedures. If it is necessary, Ops procedures governing the operation of charcoal filter units will need to be scrubbed and changed as applicable. <I> **** Actions Taken **** Wrote this CR.
399549 | CR | 20190927 |  | 4 | COND-P-1A lower oil level LOW | N | N |  | N | YES | <D> **** Detailed Description **** COND-P-1A lower oil level was found out-of-band on rounds. The band is +/- 1/8'' from midline, the level was below this. See attached photo. Oil addition needed. <I> **** Actions Taken **** Notified CRS | 02-00-COND-P-1A
399556 | CR | 20190927 |  | 4 | CL-LI-4 does not work | N | N |  | N | YES | <D> **** Detailed Description **** CL-LI-4 (Sodium Bromide bulk tank level) does not indicate the correct level in the tank (CL-TK-4). CL-LI-4 currently reads between 1770 and 1962 gallons. Local tank level is 27 inches which calculates out to 1296 gallons. <I> **** Actions Taken **** Informed Specialist and Chemistry Supervision. Inform CRS. Wrote CR. | 02-00-CL-LI-4
399557 | CR | 20190927 | CAQ | C | SOP-DG-DSA direction to open NC DSA-V-84 | Y | N |  | N | YES | <D> **** Detailed Description **** As part if its direction for isolating and depressurizing HPCS DG3 air receivers (DSA-AR-1C or DSA-AR-2C), SOP-DG-DSA section 5.1 includes direction to open DSA-V-84 (normally closed cross-tie between the 1C and 2C HPCS DG3 DSA headers downstream of DSA-PCV-2C and DSA-PCV-1C). When performed, this SOP direction will connect the two separate HPCS DSA systems and appears to be in conflict with FSAR 9.5.6 (Starting Air System). Additionally, this direction results in a configuration where one HPCS DSA air reciever volume (through one regulating PCV) is driving four DSA motors instead of only two DSA motors. Reference AED M512-1. The HPCS DSA system was sized with capacity for and tested to confirm capability of 3 starts with each separate system from separate air receivers through separate piping and control valves to a pair of air motors. Four air start motors will consume more DSA air volume than two air start motors. The start capability testing documented in calculation AED CAL ME-02-94-44 R2 for HPCS DG3 does not evaluate or document testing completed for any DSA piping configuration with DSA-V-84 in the open position. The procedural direction for isolating and depressurizing the 1C and 2C DSA air receivers (including direction to open DSA-V-84) was added to SOP-DG-DSA via major rev 5 (12/10/09). From the Procedure Revision Form package, this change was treated as administrative, made with a supporting AD only (AD-09-1584), did not receive an Engineering review, and did not discuss potential impacts upon 3 start capability for DG3. For resolution, it is suggested that the DSA-DG-DSA direction be revised to also always maintain DSA-V-84 in the CLOSED position. Resolution of this AR CR 399557 should be completed as part of the resolution of AR CR 399463. <I> Three (3) start capability for the HPCS DG3 DSA system is only for sizing of the start air system - there is no Technical Specification requirement for 3 starts. Reference TS 3.8.3 and TS B 3.8.3. DSA-V-84 is normally closed - there is no concern for system function or operation when DSA-V-84 is in its normally closed position. Spoke with the Shift Manager and NSSS System Engineering. <N> C-DSA-V-84 hung to control valve closed and to provide cross reference to this CR. <R> REP/REGE assignments cancelled, reporting is being performed under CR 399463 (cross-referenced). | 02-00-DSA-AR-1C,02-00-DSA-AR-2C,02-00-DSA-V-84
399558 | CR | 20190927 |  | 3 | Radioactive Shipping Software Issue |  |  |  | N | NO | <D> **** Detailed Description **** During the characterization process step 2.4.2 of PPM 11.2.23.2 requires verification and validation (V & V) of software output for performing characterization of radioactive material. The generated output is compared to a designated test case for each waste stream. The V & V is considered satisfactory if the comparison yields values that correspond to those generated in the test case. While characterizing container RMC-CV-00173, the V & V performed did not compare well with the test case prompting the RWTS to suspend the characterization process to determine the cause of the discrepancy. The waste stream used for this characterization is the 2018 RAM â€“ Non waste tools and equipment. <I> **** Actions Taken **** 1. Had a second V & V performed by a different RWTS on this waste stream to ensure proper data entry. Second RWTS had same results. 2. Investigated potential causes for the discrepancy. None were identified 3. Informed RP Supervision of the discrepancy. 4. Contacted software vendor, DW James, for assistance in determining cause. DW James has not been able to determine cause and has requested a copy of the data base to facilitate determination. <N> Shipments stopped until resolution of software issue. See EDMS for causes and actions.
399559 | CR | 20190927 |  | 4 | (NRC) SW Pump House B Ventilation Louver Positions | N | N |  | N | YES | <D> **** Detailed Description **** The NRC observed that the louvers on the discharge of POA -FN-2B are not all aligned and appear to be either stuck in some cases or misaligned. The louvers should be inspected during the next POA-FN-2B maintenance activity to confirm proper operation/orientation of the louvers. A waldown of the area confirmed ample air flow from the outlet of the fan and louvers, however with the louvers not all orientated in the same direction some air flow may not be directed as intended. A specific safety concern was not communicated. Pictures are attached to EDMS. | 02-00-POA-FN-2B
399560 | CR | 20190927 |  | 3 | NRC Identified BLD 88 Elevator expiration sticker | N | N |  | N | YES | <D> **** Detailed Description **** NRC Identified BLD 88 Elevator inspection sticker expires on 10-01-2019. <I> **** Actions Taken **** Shift Manager Notified, Security Supervision Notified, CR Initiated <N> **** Equipment Description **** BLD 88 Elevator
399561 | CR | 20190927 |  | 3 | PPM 12.5.39 Procedure Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** PPM 12.5.39 needs to be updated. This procedure requires a clearance order hang to reposition equipment that is controlled within the procedure. An enhancement is needed to either remove the clearance requirement or to specify a Local Clearance be written. <I> **** Actions Taken **** Wrote CR
399562 | CR | 20190927 |  | 3 | SOP-CW-CHEM-MAINT needs clarification |  |  |  | N | NO | <D> **** Detailed Description **** While trying to flush the system per section 5.11 for hanging tags and valve work. It was discovered that step 5.11.3 needs clarification for Chemistry. THere is a procedure for operating the equipment with chemicals, but nothing exist for running water through the system for flushing . Also Chemistry request clarification on step 5.11.18. No guidance is given to know when flush is complete. <N> **** Equipment Description **** SOP precedure revision
399563 | CR | 20190927 | CAQ | D | D-DOOR-D110 Not Unlocking Properly | N | Y |  | N | YES | <D> **** Detailed Description **** D-DOOR-D110 is not unlocking properly. Contact security for additional details. Functionality of this essential fire door is not impacted by this malfunction. <I> **** Actions Taken **** Notified MCR and Security. | 02-00-D-DOOR-D110
399564 | CR | 20190927 |  | 3 | Typo in LCS 1.7.2.A.2 |  |  |  | N | NO | <D> **** Detailed Description **** The "Required Compensatory Measure" for one or more CCH chillers Inoperable states "OR Verify Standby Service Water (SW) System capable of maintaining control room temperature LE 85Â°F dry blub." That SHOULD read "LE 85Â°F dry bulb." The word is spelled correctly in the bases. <I> **** Actions Taken **** Discovered during T-5 review of WO 02126661 WO ESP-SW/IST -Q701, SW-TCV-11A OPERABILITY.
399565 | CR | 20190927 | CAQ | D | Security Door D110 needs maintenance | N | Y |  | N | YES | <C> DUPLICATE OF 399563 <D> **** Detailed Description **** Security diesel door D110 is not operating by design and needs maintenance. The egress cardreader is not functioning as designed and door has been keylocked. <I> **** Actions Taken **** CR/WR initiated. Security supervision notified. Shift manager notified. Door keylocked and taken out of service. | 02-00-D-DOOR-D110
399566 | CR | 20190928 |  | 4 | Timer mis-counted during CFD BW/PC | N | N |  | N | YES | <D> **** Detailed Description **** DDuring the backwash of COND-DM-1F, step 35 is a final backwash of 30 seconds ,and is controlled by a "Final Backwash" timer on COND-CP-DM/2. This timer is currently set at 30 seconds, yet it was observed counting down from 300 seconds. This sent almost 2000 extra gallons to the radwaste system for processing. Please investigate this anomaly. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RWCR | 02-00-COND-CP-DM/2
399567 | CR | 20190928 |  | 4 | System stayed in precoat during precoat of CFD | N | N |  | N | YES | <D> **** Detailed Description **** During the precoat process for COND-DM-1F, the timer motor is taken to "off" during the precoat phase to allow time to add resin and testing. When this is complete, the timer motor switch is taken back to "run" and the "Precoat Timer" on COND-CP-DM/2 counts down from 5 minutes to continue to process. However, it was noted that the precoat timer counted down to zero and nothing happened. The Precoat Timer was lit at "0", with a down arrow in the display and a dash. Supervision was then involved, and it was decided to attempt a push of the "Cycle Control" button. Nothing happened when the button was pushed when the switch was set to "Auto" or "Manual". Then, "Additional Precoat" was pressed. This reset the "Precoat Timer" back to 5 minutes and it began counting down again. This was effective, as at the end of the countdown, the system progressed to the next cycle. Please investigate the source of this problem. <I> **** Actions Taken **** Notified SMgt, worked through solutions described above, and wrote CR. <N> **** Equipment Description **** RWCR | 02-00-COND-CP-DM/2
399568 | CR | 20190928 | CAQ | D | CRD-HCU-42-07 High Water Level alarm received | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-42-07. After investigation, Rod Accumulator Trouble Alarm P603-A7 drop 6-7 was for CRD-HCU-42-07 high water level. <I> **** Actions Taken **** Dispatched OPS-2 to investigate. Removed excess water from HCU. Initiated CR informed CRS | 02-00-CRD-HCU-4207
399569 | CR | 20190928 |  | 4 | Only 2 Control Room Operators (CRO) in the protected area |  |  |  | N | NO | <D> **** Detailed Description **** On Sept 28th from 0015 to 0044 there were only 2 CROs in the protected area. This was due to a family emergancy. <I> **** Actions Taken **** Wrote CR. . Per PPM 1.3.1 Section 4.10 note: "The shift crew composition may be one less than the minimum requirements specified for a period not to exceed 2 hours in order to accommodate unexpected absence of on-duty shift crew members, provided immediate action is taken to restore the shift crew composition to the minimum specified, using the call-in process, if necessary."
399570 | CR | 20190928 |  | 4 | 21A Camera Control Pad |  |  |  | N | YES | <D> **** Detailed Description **** The camera control pad in BRE 21A is not functioning as desinged and requires maintenance. <I> **** Actions Taken **** Security Supervision notified. Initiate CR/WR. <N> **** Equipment Description **** Offsite BRE 21A
399571 | CR | 20190928 |  | 3 | OPS4 log "Floc Outlet turbidity recorder" needs revision | N | N |  | N | YES | <D> **** Detailed Description **** OPS4 Log station 527 is stating the recorded log is out of spec when it is not. This is a new log to compare Flocculator Outlet Turbidity local vs. digital. This log computes a 20% tolerance against the local reading to establish a min & max. Since the log became effective it has highlighted the reading as being outside the 20% tolerance for the minimum spec when that is not true. The math formula or the software recognition in eSOMS needs to be updated to correct the error notice. <I> **** Actions Taken **** Informed SSS | 02-00-PWC-XR-1
399578 | CR | 20190928 |  | 4 | ASD/A Input Transformer Trouble alarm is locked in. | N | N |  | N | YES | <D> **** Detailed Description **** ASD/A Input Transformer Trouble alarm is locked in. EO reports no parameters out of tolerance locally. <I> **** Actions Taken **** Had EO investigate.Wrote this AR. Alarm cleared shortly after coming in. | 02-00-RRC-TR-ASD/A/1
399579 | CR | 20190928 | CAQ | D | RWM operate light is off, entry into ABN-RWM | Y | N |  | N | YES | <D> **** Detailed Description **** Entered ABN-RWM due to the RWM computer OPER light being off, causing "red iced cubes" on TDAS/PPC. TDAS/PPC unable to see rod positions. Four rod display is still operable. Unable to perform action 4.1 of ABN-RWM due to inability to reinitialize the RWM verbatim since the RWM display is not working to allow touch screen operation. TDAS/PPC N1 and N2 screens show ?? for all rod positions indicating the RWM is not communicating with TDAS/PPC. <I> **** Actions Taken **** Discussed with SNE and SM. Bypassed TDAS RWM alarm function to restore "green ice cubes." | 02-00-PPC-CPU-RWM
399580 | CR | 20190928 | CAQ | D | Security Manhole ES-1 | N | N |  | N | YES | <D> **** Detailed Description **** Security Manhole ES-1 is not functiong as designed. Please contact Security at 2185 for further details. <I> **** Actions Taken **** Security Supervision notified, and Compensatory measures posted. CR/WR generated for Electrical support. | 02-00-SEC-TAS-ES01T
399581 | CR | 20190928 | CAQ | C | There is a gereral rising trend in DW/WW O2 concentrations | Y | N |  | N | YES | <D> **** Detailed Description **** There is a gereral rising trend in DW/WW O2 concentrations. Due to the leakage between the drywell and wetwell it is difficult to detemine the source of inleakage. Suspect that CMS-SR-20 is leaking. The logged vacuum data has been declining since it was placed inservice and is now at 2. Previous vacuum values have been logged consistantly in the range of 6-11 between 6/30/19 and 7-30-19 (when the sample rack went out of service until 8/28) Please see graph attached to EDMS docs. Suggest investigating O2 leakage and addressing. Current concentration is about 1.8% with a limit of 3.5%. <I> **** Actions Taken **** Wrote this AR and WR. Informed supervision. | 02-00-C-TK-1
399582 | CR | 20190928 |  | 4 | CL-V-65A found internally degraded | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WO 02147469-01 it was found that the ball had severe degradation and effected efficiency, as well as the mounting flanges show slight wear and recommend replacing flanges during next maintenance opportunity. See pictures in EDMS <I> **** Actions Taken **** Notified my supervisor the main control room and initiated this condition report. | 02-00-CL-V-65A
399583 | CR | 20190928 |  | 3 | CL-V-65A CID 9230 was not like for like |  |  |  | N | NO | <D> **** Detailed Description **** During performance of WO 02147469-01 during valve replacement it was noted that the valves were not like for like, the new valve had a square body versus the old one which had an oval type body, all measurements were the same and alignment was correct. Material was checked in portal J to confirm compatibility and this valve has been used previously. Valve was installed per work instructions, recommend engineering evaluate the differences in CIDâ€™s. See EDMS for pictures. <I> **** Actions Taken **** Notified my supervisor and the main control room and initiated this condition report.
399584 | CR | 20190928 |  | 3 | Ops Dept leadership assessment conduct via SurveyMonkey |  |  |  | N | NO | <D> **** Detailed Description **** Operations Department internal leadership assessment questionairres are now being done utilizing SurveryMonkey. The survey consists of 16 questions and requires a signficant time investment to complete. However, there is no ability to save work completed using SurveryMonkey, so the survey must be completed all in one sitting. Recommend the department consider another methodology for conducting these self assessments to allow personnel to save work and complete the survey as time on shift permits and come back to previously completed work. <I> **** Actions Taken **** Discussed with SM. <N> The system automatically saves when you exit and allows you to return to surveys in progress. This has been verified by the creator of the survey. 10/17/219 - Reopened the CR based no the same resutls are still happening. Action to Ops admin to reseach
399585 | CR | 20190928 |  | 3 | Equipment on TB 441' past staging date. |  |  |  | N | YES | <D> **** Detailed Description **** Some of the equipment, a lift and tool box for example, that is staged on the TB '441 is past its staging date. Dates on staging signs should be updated if eqipment is still needed or the equipment should be put away. <I> **** Actions Taken **** Initiated CR <N> **** Equipment Description **** Located to the west of the Condensate pumps on the TB' 441.
399586 | CR | 20190928 |  | 4 | safety no hot water in bldg 17 |  |  |  | N | YES | <D> **** Detailed Description **** no hot water for washing hands or doing dishes in bldg. 17 <I> **** Actions Taken **** left a message with the weekend supervisor wrote this cr <N> **** Equipment Description **** bldg. 17
399587 | CR | 20190928 |  | 3 | Procedural enhancement TSP-THERM-C101 |  |  |  | N | NO | <D> **** Detailed Description **** Attempted to perform section 10.2 of TSP-THERM-C101. The CAUTION at the top of page 16 refers to P&L 5.5 and 5.6 for which adaptive mode to use for the manual calculation. P&l 5.6 does not exist and 5.5 has nothing to do with adaptive modes. The procedure also never addresses restarting the live data transfer process that was stopped (not by procedural step) by the NOTE below step 10.2.1. Additionally, the program would not accept the calculated MWD in step 10.2.6 as it is looking for a much larger number than the current cycle exposure. Request SNEs review and revise the procedure to include all procedurally required steps, reference the correct discussion on adaptive modes, and provide additonal direction for operators on shift. See attached email in EDMS file. <I> **** Actions Taken **** Discussed with SM and SNE.
399588 | CR | 20190928 |  | 4 | High iron in EDR-TK-4B | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of a release to CST sample of EDR -TK-4B a high rust content was noted. The content of rust was significantly higher than average and a general increase of iron has been noted in the recent past (2 months). This could indicate a high level of corrosion exists in the EDR system or in the decant water where the water was from. The in-line filter for the sample line became clogged with iron. <I> **** Actions Taken **** CRS/RWCR operator informed/consulted. Chemistry supervisor/specialist notified. Filter saved in lab. | 02-00-EDR-TK-4B
399589 | CR | 20190928 |  | 4 | PWC-P-8 found airbound | N | N |  | N | YES | <D> **** Detailed Description **** PWC-P-8 was found airbound and FRC in the potable water system was lower than expected 1.18 ppm vs. 1.30 ppm. This pump is designed to maintain FRC (free residual chlorine) in the site potable water at 1.30 ppm. It has no backup and if FRC goes low out of specification it is a state reportable violation. Recommend FIN investigate pump for damage. Recommend OPS-4 check on pump status (airbound or working normal) shiftly and notify shift chemist of status. <I> **** Actions Taken **** CRS informed. Chemistry supervisor/specialist notified. Pump primed and air bubble removed. | 02-00-PWC-P-8
399590 | CR | 20190928 |  | 4 | Lights out on 452' RW near RW elevator | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of chemistry daily logs it was noted that 2 lighting fixtures with 4 bulbs were out. Area is tenebrific but navigable. <I> **** Actions Taken **** CRS informed <N> **** Equipment Description **** Lights outside the RW elevator on the 452' RW elevation.
399591 | CR | 20190928 | CAQ | D | Rod accumulator trouble on CRD-HCU-1411 due to high water. | Y | N |  | N | YES | <D> **** Detailed Description **** Rod accumulator trouble on CRD-HCU-1411 due to high water level. <I> **** Actions Taken **** Informed CRS/ SM, cleared alarm per SOP-CRD-HCU. | 02-00-CRD-HCU-1411
399592 | CR | 20190928 |  | 4 | Water leak on TB471 | N | N |  | N | YES | <D> **** Detailed Description **** Water is leaking from the ceiling above the CAS compressors. Upon investigation a leak was discoverd on the TB471 around G-6 (between seal steam evaporator 1B and heater 6A). See camera TG/12 preset 1. <I> **** Actions Taken **** Wrote CR, Informed CRS <N> **** Equipment Description **** TB471 G-6
399593 | CR | 20190929 |  | 4 | ASD door does not shut itself. | N | N |  | N | YES | <D> **** Detailed Description **** Door does not latch shut from the 1/3 open position. Lots of positive building pressure may be contributing to this. <I> **** Actions Taken **** Informed MCR, initiated AR <N> **** Equipment Description **** ASD door A-100
399594 | CR | 20190929 |  | 4 | HWC trouble alarm due to low hydrogen pressure. | N | N |  | N | YES | <D> **** Detailed Description **** HWC trouble alarm due to low hydrogen pressure. Upon investigation no pumps were running with system pressure less than 500 psig. It is not clear why the pumps are not running or trying to start. No alarms were in at HSSF. The YV170 valve was open and HWC continues to inject to the plant. <I> **** Actions Taken **** Wrote CR Informed CRS . Confirmed with Operators that we received hydrogen on the evening of 9/27/19 which nearly filled the HSSF. <N> **** Equipment Description **** HSSF facility trouble
399595 | CR | 20190929 |  | 4 | Hydrogen Tube pressure low alarm @ HSSF | N | N |  | N | YES | <D> **** Detailed Description **** @ 0012 an HS PAL124-PRES STAT LOW alarm appeared on the HSSF-CAB-CHEM/LAB Annunciator Panel for the Hydrogen Storage Supply Facility (HSSF). this indicates Hydrogen Tube Pressure Low @ the HSSF. At the time of the alarm Tube pressure was 492 PSIG and is currently at 457 PSIG and appears to be decreasing. <I> **** Actions Taken **** Per CI-14.4 contacted Control Room and initiated Condition Report and Work Request <N> **** Equipment Description **** Hydrogen Supply @ Hydrogen Storage Supply Facility (HSSF) HSSF-CAB-CHEM/LAB located RW 487' Chem Lab. | 02-00-HSSF-CAB-CHEM/LAB
399596 | CR | 20190929 |  | 4 | Steam leak on BS-V-43B | N | N |  | N | YES | <D> **** Detailed Description **** There is a small steam leak at the packing on BS-V-43B. <I> **** Actions Taken **** Wrote CR, Informed CRS | 02-00-BS-V-43B
399600 | CR | 20190929 |  | 4 | ASD A input transformer trouble. | N | N |  | N | YES | <D> **** Detailed Description **** ASD A input transforer trouble alarm in. Transformer liquid temp. 32. Winding temp 45. Pressure 0.5#, Level ~0.5. ~40F outside temperature. <I> **** Actions Taken **** Informed MCR of Transformer readings, initiated AR <N> **** Equipment Description **** ASD input transformer | 02-00-RRC-TR-ASD/A/1
399601 | CR | 20190929 |  | 4 | Lighting ballast is out in Building 600. | N | N |  | N | YES | <D> **** Detailed Description **** The lighting ballast right above the door (NW corner) in FLEX building 600 is out and should be replaced. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** NW corner of B600 right above the door.
399602 | CR | 20190929 | CAQ | D | FLEX-GEN-DG5 low oil pressure alarm. | N | Y |  | N | YES | <D> **** Detailed Description **** FLEX-GEN-DG5 in Building 600 has a low oil pressure alarm in. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** Building 600
399603 | CR | 20190929 |  | 4 | RRC-VBI-P1B/XS/XY is showing 11.4 mils and not alarming. | N | N |  | N | YES | <D> **** Detailed Description **** RRC-VBI-P1B/XS/XY is showing 11.4 mils and not alarming. IMDS shows this should cause an alert level alarm at 11.0 +/- .3 mils. Suspect that the instrument needs calibration. Additionally all other non-failed RRC-P-1B parameters appear normal at this time. Recommend validating the indicated vibration levels. A temporary log is already in place to monitor RRC-P-1B vibrations due to RRC-VBI-P1B/XE being failed up scale. Additionally recommend implementing the bypass of the RRC-VBI-P1B/XE module to restore alarm functionality an aid in prompt monitoring of this equipment should additional alarms come in. <I> **** Actions Taken **** Informed supervision. Wrote this CR and WR. Note from System Engineer: The reading reported in the CR is the gap voltage which is -11.4 VDC. The actual vibration level is 6.0 mils which is normal for this pump and motor. | 02-00-RRC-VBI-P1B/XS/XY
399604 | CR | 20190929 |  | 4 | EDR-DM-9 tripped off line and hold pump did not start. | N | N |  | N | YES | <D> **** Detailed Description **** Entering RWCR found EDR-DM-9 tripped off line with a low flow alarm, no high D/P alarm, and the hold pump off. ( EDR-P-12). Suspect the filter may have tripped off line due to flow LT 70 gpm . (Controller set at 77%). <I> **** Actions Taken **** Started the Hold pump by depressing the filter stop button and informed supervisor. BW/PC to be performed. <N> **** Equipment Description **** RW 467 | 02-00-EDR-P-12
399605 | CR | 20190929 | CAQ | D | FLEX-GEN-DG5 low oil pressure alarm. | N | Y |  | N | YES | <C> DUPLICATE OF AR 399602 <D> **** Detailed Description **** There is a low oil pressure alarm in on FLEX-GEN-DG5 control panel. Per SOP-FLEX-GEN-DG5-START page 27, warning alarms are to be recorded and logged with the respective Suspect Parameter Number (SPN 100 for oil pressure). <I> **** Actions Taken **** Initiated CR. . It is actually a Low Coolant Temperature alarm, NOT low oil pressure. <N> **** Equipment Description **** FLEX-GEN-DG5 in building 600.
399606 | CR | 20190929 |  | 4 | WOA-EHC-5 not functioning as expected | N | N |  | N | YES | <D> **** Detailed Description **** When WOA-PS-5A was calibration checked, the 1st and 2nd stage heaters in WOA-EHC-5 didn't appear to be coming on as expected. There was also no power at WOA-PS-5A. Breaker was then checked and verified to be on. WOA-EHC-5A is required to be functional to adequately complete our loop calibration of WOA-TIC-5A. <I> **** Actions Taken **** Notified CRS and supervision | 02-00-WOA-EHC-5
399607 | CR | 20190929 |  | 4 | Fuel Pool Tell Tale Drains leaking | N | N |  | N | YES | <D> **** Detailed Description **** Fuel Pool Tell tale drains have a small puddle in the box from 20-40 drips per min. From what I could count the drips are not consistent varying from flurries of almost 1 per sec to pauses of no drips for several seconds or longer <I> **** Actions Taken **** Informed CRS <N> **** Equipment Description **** Capture box on the RB 548 west side Located at M.0/7.7
399608 | CR | 20190930 | CAQ | D | Water discovered in RW 467 "A" Valve Gallery | N | N |  | N | I DONT KNOW | <C> This CR reopened as the source of the leak was discovered and is from EDR-V-52 valve to pipe weld. This is essential radwaste and historically is CAQ. Change from non-CAQ 4 to a CAQ D. <D> **** Detailed Description **** Water discovered while posting for FPC-DEMIN-A backwash. No active leak was found. Survey of area showed no contamination spread. Unknown at this time the source of the leak. Water was mopped up with exception of small amount along the wall. Area was posted HRA CA. <I> **** Actions Taken **** Informed RWCR.
399609 | CR | 20190930 |  | 4 | EDR-V-44 not opening when EDR-P-11 running | N | N |  | N | YES | <D> **** Detailed Description **** EDR-V-44 will not open when starting EDR processing from EDR-TK-2, does open from EDR-TK-5. See attached document. <I> **** Actions Taken **** Initiated AR, informed MCR | 02-00-EDR-V-44
399613 | CR | 20190930 |  | 3 | HP001550 OJT Guide needs Revised |  |  |  | N | NO | <D> **** Detailed Description **** OJT Guide (HP001550) is in need of a Revision. HPI-12.96 needs to be added to the list of Procedures used on this Qual Card. It would also be beneficial to add a comment in the Precautions/Limitations about using the Training Region of PortalJ for this training. <I> **** Actions Taken **** Notified Supervision Initiated CR
399615 | CR | 20190930 |  | 4 | Dose rates on Rx Building East EDR Header are increasing |  |  |  | N | YES | <D> **** Detailed Description **** During the performance of Wo 02135486, HP Survey of EDR-1 Piping in Rx BLDG it is noted that dose rates on EDR East Header are increasing and planning to flush the EDR Line would be prudent. <I> **** Actions Taken **** Created WR <N> **** Equipment Description **** Rx 522 to 422 East Side | 02-00-EDR-PIPE-MISC
399621 | CR | 20190930 |  | 3 | Fire Protection |  |  |  | N | NO | <D> **** Detailed Description **** Operations would not allow us to work, work order 02139652-01. The Fire System Impairment was not ready for the work to begin. <I> **** Actions Taken **** Contacted Work Week Manager
399622 | CR | 20190930 |  | 4 | Loss of commercial power on Rattlesnake Mt. CCCF | N | N |  | N | NO | <D> **** Detailed Description **** The CCCF lost commercial power and transferred to generator power. The BPUD indicated snow and ice is most likely the problem and are working to restore power. The fuel tanks are near full and will run the gernator for at least 5 days. <I> **** Actions Taken **** Notified the SCC and Facilities. Recommend NCAQ-4 for trending.
399623 | CR | 20190930 |  | 3 | Procedure enhancement for 1.3.57 |  |  |  | N | NO | <D> **** Detailed Description **** The table at the bottom of page 57 has four fuel pool cooling components to declare inoperable that arent ever required to be operable. They should be removed from this table. There is not an LCO/RFO to enter for these components. See EDMS <I> **** Actions Taken **** Wrote CR. Discusses woth AOM WC
399624 | CR | 20190930 |  | 4 | eSOMS Application unavailable | N | N |  | N | NO | <D> eSOMS application was unavaiilable. <I> Disabled verbose logging on eSOMS web service and deleted log file. This restored normal application functionality.
399626 | CR | 20190930 | CAQ | C | EWD 11E-034 incorrectly lists RCC-V-129 instead of RCC-V-131 |  |  |  | N | NO | <D> **** Detailed Description **** TOP TIER dwg 11E-034 incorrectly lists RCC-V-129 instead of RCC-V-131 in the description/ title box in the lower right part of the drawing.
399627 | CR | 20190930 |  | 3 | Discrepancy between TOP TIER DWG and SOP on valve position |  |  |  | N | NO | <D> **** Detailed Description **** Top tier DWG M525-1 identifies valves as closed and capped while SOP-RCC-LU shows them to be only closed. The following valves are shown as closed and capped:RCC-V-603, 80A, 638, 161, 618. The isometric drawing for all except RCC-V-618 also shows they are capped. All the valves are located inside the drywell.
399628 | CR | 20190930 |  | 3 | (LL) Clearance boundary not adequate during RCC-HX-1B work |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The initial red flagged clearance was not adequate for the work; too much leak by on the isolation valves. This delayed the actual start of the work by two days. A temp list was performed and the valves were cycled and reclosed. This worked and the RCC-HX-1B work was able to be performed. . Recommend assignment to operations to evaluate when tagging out TSW the isolation valves need to be cycled (open, closed, open, closed) before they are final closed and tagged to help remove build-up and flush of the â€œstuffâ€ on the valve disk seating surfaces. <I> **** Actions Taken **** Notified WWM and initiated this lessons learned CR.
399630 | CR | 20190930 |  | 3 | ABN-GENERATOR needs revision |  |  |  | N | NO | <D> **** Detailed Description **** The Bases of ABN-GENERATOR step 4.1.9a states that a Main Turbine trip at GT 30% reactor power results in a reactor scram. The value of 30% should be changed to 29.5% to reflect the new value following the measurement uncertainty recapture power uprate. <N> Bases step 4.4.1a also requires revision.
399631 | CR | 20190930 |  | 3 | Unable to Complete WOT 02135824-02 RadCal on IPM-8 |  |  |  | N | NO | <D> **** Detailed Description **** Radiological Operations was unable to complete C-grade WOT 02135824-02 during the scheduled work week. The task is to perform a rad calibration on the IPM-8 at the Kootenai building. The predecessor activity (02135824-01) to perform the electronic calibration is D-grade and has not been completed to support start of the rad calibration. <I> **** Actions Taken **** Discussed the item as a "failed to finish" item with the work week manager. <N> The Schedule Grade Code for both tasks have been aligned to C in the Auto-Scheduler and AS6. The prerequisite task is scheduled a week in advance. The above will fix the issue identified in this CR.
399632 | CR | 20190930 |  | 3 | Scheduled work impacted due to Procedure Change |  |  |  | N | NO | <D> **** Detailed Description **** Unable to complete scheduled work as due to a Minor Revision procedure change to PPM 10.25.74 Testing Motor Operated Valves and Controls for the week of 9/23/19. The work order was walked down and ready to work and the Minor Revision was implemented on 9/18/19. Recommend the minor revision be rescinded and incorporated as a major revision and go through the review process including the groups identified above. . See EDMS for more detailed description <I> **** Actions Taken **** Discussed with Electrical Supervision and the Work Week Manager. <N> **** Equipment Description **** PPM 10.25.74 Minor Revision 003 *It should be noted that this revision resolves a personnal safety concern or damage to equipment. There have been 5 near misses in the last 5 years. Equipment has been damaged (required replacement = additional scheduled work / dose / cost impacts have occurred due to crossing wires valves. PPM 10.25.74 has been revised several times to try and eliminate the potential. Outage lessons learned CR's generated and no actions have taken place. See all of the cross references.
399633 | CR | 20190930 |  | 3 | BPA work not properly scheduled with other TR-B work |  |  |  | N | NO | <D> **** Detailed Description **** WO 02137607, BPA - Benton: 115 kV Main Bus OOS during TR-B Window 10/17/19, is an Administrative WO that is being performed by BPA off-site. The work being performed by BPA on Thursday, 10/17/19, will make the Backup Transformer be Inoperable due to the removal of the credited line, but power will be provided by a non-credited line that will keep TR-B energized and Available. This fact of TR-B being rendered Inoperable with this work was not understood by everyone in Work Control that puts schedules together. This was due to poor communication. As a result, we mistakenly separated this work from the remainder of the TR-B Maintenance window, which is scheduled to occur on Friday and Saturday, 10/18 & 19. <I> **** Actions Taken **** We contacted BPA to see if their Thursday work could be moved to Friday. Due to necessary grid stability and coordination with 4 other utilities, the Benton work cannot be moved from Thursday to Friday. Based on the information that we have gathered, the recommendation from Work Control and the Transformer Yard Coordinator is to have 2 separate TR-B windows within the 10/14 WW. <N> Operations and PSO reviewed the work. Ensured the Impact Statement has the required information for operability. No other actions necessary.
399636 | CR | 20190930 |  | 4 | CAP KPI's not presented at PARB IAW GBP-ORG-02 |  |  |  | N | NO | <D> **** Detailed Description **** GBP-ORG-02 attachment 8.1 requires that the key PI's from the Corrective Action Group are presented to the PARB on a monthly basis. However, they were not presented to the PARB during the month of September. There was not enough time to present during the scheduled meeting timeframe. <I> **** Actions Taken **** The Performance Improvement Supervisor, PI Manager, and the Plant General Manager agreed to cancel the presentation due to time constraints.
399639 | CR | 20190930 |  | 4 | TOA-FL-1B EOR | N | N |  | N | YES | <D> **** Detailed Description **** received end of roll alarm TOA FL-1B, approx 25% of filter left on roll. request mech replace filters soon <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-TOA-FL-1B
399640 | CR | 20190930 | CAQ | C | Update FSAR Table 12.2-12a, include source number 17-307 |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing FSAR Chapter 12, an employee noticed that source number 17-307 hadnâ€™t been added to FSAR Table 12.2 -12a. Revise the FSAR Table 12.2-12a to update the source activities and add source number 17-307. Since a separate Action Request is initiated to complete the process of revising the FSAR, it might seem appropriate to initiate a SELF Action Request to ensure that the LDCN process is not forgotten. However, errors and deficiencies identified in Licensing Basis Documents must enter the Corrective Action Process. SELF ARs do not enter CAP.
399641 | CR | 20190930 |  | 3 | Plant eyewash station deficiencies | N | N |  | N | NO | <D> **** Detailed Description **** During performance of the monthly eyewash station PM it was observed that we currently have 6 different types of eyewash stations all with different controls, pressure ratings and capacities. Some of these have missing parts which canâ€™t be located for replacement by the manufacturer. Recommend changing out the remaining eyewash units with CID 98102550 Guardian FSG1562 which has an optional dolly unit for transport. We currently have 2 of these units on site and are an acceptable replacement. <I> **** Actions Taken **** Initiated this condition report, notified industrial safety, my supervisor, and the main control room. Recommend assignment to industrial safety for evaluation.
399642 | CR | 20190930 |  | 3 | Elevator operating certificates not yet received |  |  |  | N | NO | <D> **** Detailed Description **** On 9/30/2019, Environmental and Regulatory Programs (E&RP) contacted Labor and Industries (L&I) to determine status of elevator operating certificates, which expire on 10/1/19. As of 9am on 9/30, L&I has not received Energy Northwestâ€™s payment for renewal. Although E&RP requested the payment to be made by 9/16/19, the check was mailed to L&I by Accounts Payable on 9/26/19. Per L&I, there is no issue with utilizing EN elevators prior to receiving updated operating certificates. <I> **** Actions Taken **** Discussed with E&RP Manager, F&CE Manager, Industrial Safety Program Manager, and Maintenance Supervisor. <N> As of 10/9/19, L&I confirmed payment was received. Certificates were mailed to Energy Northwest last week. Receipt of Operating Certificates tracked under AR 398027. No further actions required.
399644 | CR | 20190930 |  | 4 | Gate 26 (inner most gate) |  |  |  | N | YES | <D> **** Detailed Description **** Manual gate is sticking | 02-00-SEC-GATE-26
399645 | CR | 20190930 |  | 4 | lighting panel breaker will not close | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Electricians were performing emergent lighting upgrades per WR# 29151861. After opening circuit breaker 29 out of E-LP-6B-A, and repairing two F7 style fixtures above COND -AO-231A, electricians went to close the lighting breaker and it will not snap over to the closed position. As necessary, electricians need to determine what type of Square D breaker (snap in or bolt-down) is in E-LP-6B-A. It is suspected that the breaker on circuit 29 is bad. <I> **** Actions Taken **** notified supervisor write Cr and add steps to WR29151861 to install temp lighting for mechanical work on COND-AO-231A. <N> **** Equipment Description **** F7 fixture in A valve galley RW 467
399646 | CR | 20190930 |  | 3 | Procedure Enhancement SOP-RW/EDR-INFREQ |  |  |  | N | NO | <D> **** Detailed Description **** SOP-RW/EDR-INFREQ P&L 4.17 adresses using "Radwaste Additional Information" section of the Electronic OPS LOGS to publish/track the plans for handling OOS water in Radwaste sytems. We dont use the "Electronic OPS logs" any more. Recommend eliminating Step 4.17 until such time as there is new means of communicating or diseminating "a Plan". <I> **** Actions Taken **** wrote CR in an expedicious manner
399647 | CR | 20191001 |  | 3 | Laborer Support Not Identified in Work Order |  |  |  | N | NO | <D> **** Detailed Description **** WO 02147316, OSP-RB/HVAC-Q101 - RX BLDG EMERGENCY COOLING is scheduled for 10/21/19. Step 7.1.1.a. of this PPM states "REQUEST HP Laborers hang a catch on RB 522â€™ at J/7.5 (See Attachment 9.1) to collect approximately 1 drop/min of water from uncapped drain off bottom of RRA-CC-11." Neither the PM generated or the Model WO for this surveillance contain a support task for laborers. The catch should be erected the day before the surveillance is to be performed. <I> **** Actions Taken **** Notified HP/Laborer supervisor of this upcoming need. Notified scheduler, PSRO and WWM. Found this while preparing for T-2 meeting. . This is a new procedure issued 7/23/19 and has superseded SOP-HVAC/RB-TEST. <N> Labor support added to WO 02147316n and model WO 02151270. No furhter actions required.
399648 | CR | 20191001 |  | 4 | RCC surge tank level decreasing trend. | N | N |  | N | YES | <D> **** Detailed Description **** RCC surge tank level started a low downward trend on 9/22. This downward trend has continued with surge tank makeup valve occasionally opening and filling the tank. The start of the downward trend was roughly the same time that the RCC-HX-1B was tagged out for maintenance. The RCC HX area was inspected for external leaks and the drain pipes were inspected for leaks into the suppers with nothing found. <I> **** Actions Taken **** Wrote CR Informed CRS | 02-00-RCC-TK-1
399649 | CR | 20191001 | CAQ | D | EDR-V-52 is misting out of a crack in the piping | N | N |  | N | YES | <D> **** Detailed Description **** Water was previously discovered in the A valve gallery and we have been unable to locate the source. It was discovered again today nd appears to be coming out of a crack in the weld of the valve to the piping. the valve is in the high rad area in the A valve gallery | 02-00-EDR-V-52
399698 | CR | 20191001 |  | 4 | RFT-LOC-1A tripped | N | N |  | N | YES | <D> **** Detailed Description **** RFT-LOC-1A has tripped off on heater over temp at least 4x in the last 24 hours. EO's have vented and adjusted flow but it has continued to trip off. <I> **** Actions Taken **** Informed SSS | 02-00-RFT-LOC-1A
399699 | CR | 20191001 |  | 4 | HWC Alarm | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Received an alarm on the HSSF-CAB-CHEM/LAB Annunciator in the 487' RW chemsitry lab. Alarm ID TT PIT141 -PRES STAT LOW LOW, which indicates low hydrogen tube trailer pressure. <I> **** Actions Taken **** contacted CRS & wrote a CR in compliance with CI-14.4
399700 | CR | 20191001 |  | 3 | Standard found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode 002-56-01-036 was found out of tolerance and rejected. Please assign to CALSERV. <N> Out oftolerance Report uploaded into EDMS panel. No further action required.
399701 | CR | 20191001 |  | 4 | Mech Shop Sept Dose |  |  |  | N | NO | <D> **** Detailed Description **** As of this morning through 9/30/19, mechanic shop dose was 314 mrem over 285 estimated. Overage was attributed to emergent FIN activities (which was ~169 mrem) during the 9/23/19 week to address PSR-V -640 and EDR-V-40. <I> **** Actions Taken **** Generated CR. Trend Adding additional info as the overall dose received was 314 mrem compared to the Monthly goal of 285 mrem, (the shop was not 314 mrem over the 285 mrem estimate if interpreted that way from the CR). Therefore the actual overage was ~29 mrem above the monthly goal of 285 mrem. ~169 mrem of the 314 mrem received was associated with emergent FIN activities in the 9/23/19 work week.
399705 | CR | 20191001 |  | 3 | SOP-DOOR/HATCH-OPS refers to T113 door as Telescoping door |  |  |  | N | NO | <D> **** Detailed Description **** T-DOOR-T113 is the West Turbine Bldg. roll-up door. Please update SOP-DOOR/HATCH-OPS to reflect this. <I> **** Actions Taken **** Wrote CR.
399708 | CR | 20191001 |  | 4 | Received 4.840.A3 7-6 HWC trouble. | N | N |  | N | YES | <D> **** Detailed Description **** Received 4.840.A3 7-6 HWC trouble. OPS 3 reported the alarm was Supply facility trouble. Chemistry HMI Shows TT PIT-141 STAT LOW LOW. ENW.HH2OCHEM.TT PIT140 -PRES VAL ENGU shows tube trailer pressure of 2474 psi. This alarm should come in at 1500 psig for the primary alarm and 500 psig for the secondary alarm. Recomend vendor investigation of the PIT. <I> **** Actions Taken **** Wrote tis CR. Verified that HWC remained in service. | 02-00-HSSF-PIT-141
399709 | CR | 20191001 | CAQ | D | 3 Pieces of M&TE Suspended until R25 |  |  |  | N | NO | <D> **** Detailed Description **** Per Engineering Request: 2 Load Cells and 1 Rule used for Snubbers during Outages have been Suspended until Jan. 2021 for R25. As founds will be taken when ReCalibrated. Calcode #0068070 Interface Load Cell- model 1232ACK-100K-TB. DEF #7328A written. Calcode #0068071 Interface Load Cell- model 1210ACK-10K-TB. DEF #7329A written. Calcode #0068234 Starrett 24" Steel Rule- model C303SR. DEF #7330A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
399711 | CR | 20191001 | CAQ | D | EDR-P-11 failure | N | N |  | N | YES | <D> **** Detailed Description **** Investigation of WR 29151858 found that EDR-P-11 has failed. The motor and shaft up to the pump are rotating, however the pump sounds like it is pumping rocks (big ones, not pebbles). Suspect a broken impeller. <N> **** Equipment Description **** RW 437 behind shield wall | 02-00-EDR-P-11
399713 | CR | 20191001 |  | 4 | Condensate Piping Degradation as found condition | N | N |  | N | YES | <D> **** Detailed Description **** Severely degraded piping discovered during work activities in the CST Pit for work order 0214 0002-06. Piping adjacent to COND-V-784B including 2x1 reducer and flange are extremely rusted and flaking. Recommend NDE to examine pipe wall thickness and engineering determine if piping needs to be replaced. See pictures in EDMS <I> **** Actions Taken **** Notified supervision, notified PSRO of damage. Took pictures and initiated CR. | 02-00-COND-V-784B
399714 | CR | 20191001 |  | 3 | Challenge Meeting for CRD-P-1A Maintenance not Held by T-4 | N | N |  | N | NO | <D> **** Detailed Description **** As required in WCI-4, On-Line Work Control Process, work categorized as High Risk should have a Challenge Meeting completed before the end of the T-4 week. This was not completed for the High Risk Single Point Vulnerability (SPV) work being performed in the 10-14-19 WW for CRD-P-1A Maintenance. The Challenge Meeting was not completed until the T-3 week. The reason for this is the new pump for CRD -P-1A replacement was not received until the very end of the T-4 week. This prevented a walkdown from being completed. Walkdowns are required before a Challenge Meeting can be held (all holds removed) per PPM 1.3.76, Integrated Risk Management. <I> **** Actions Taken **** The Challenge Meeting was completed during the T-3 week once the pump for CRD-P-1A replacement was received. THe signed High Risk Work Plan has been uploaded. I recommend that this CR be assigned to either Reactor & Major Maintenance for late identification of parts or Supply Chain for late arrival of the pump.
399716 | CR | 20191001 |  | 3 | E-IR-66 / CMS-PT-3 can be removed from 1.3.57 HELB barriers |  |  |  | N | NO | <D> **** Detailed Description **** A HELB seal was installed in CMS-PT-3 conduit at E-IR-66 under WO 02073392. Recommend revising PPM 1.3.57 attachment 9.6 to remove references to E-IR-66 and CMS-PT-3 as they are no longer required. This has no equipment impact. <I> **** Actions Taken **** Discussed with EQ engineer. <N> Could there be a similar issue for CMS-PT-2 and CMS-PT-8? These EPNs along with CMS-PT-3 were the subject of AR CR 328392 (Moisture seals not installed in accordance with E838-9). WO 02073390 (CMS-PT-2 & CMS-PT-8 MOISTURE SEALS NOT INSTALLED IAW E838-9) is also COMPLETE. | 02-00-CMS-PT-3,02-00-E-IR-66
399718 | CR | 20191001 |  | 4 | SAFETY Concern- Lights Above Entrance to DGs Not Working |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Noticed that none of the lights above the exterior entrances to the DGs were on this morning at 0530. Other exterior lights on the RW building south side were also not on. This makes for a very dark walking path way when the sun is down and is a Safety concern. <I> **** Actions Taken **** Discussed with several EOs. No one was sure why the lights are not coming on <N> **** Equipment Description **** Exterior wall lights of the DG and RW buildings.
399719 | CR | 20191001 |  | 4 | Offgas Glycol sample showed low concentration |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Chemistry samples Offgas glycol once a month. The September initial sample was in CCW action level one as it was 28% which is lower than 30% per SWP-CHE-02. The system was resampled and it was at 33% which is within specification so the system is not in an action level currently. This AR is for data and trending purposes. <I> **** Actions Taken **** Informed Chemistry supervision, System engineer, Chemistry specialist, and MCR <N> **** Equipment Description **** Offgas Glycol system on RW 452'
399720 | CR | 20191001 | CAQ | D | need to replace power supply PPC-E/S-RWM | Y | N |  | N | YES | <D> **** Detailed Description **** While investigating PPC -CRT-RWM display for WR 29151563, found PPC-E/S-RWM output voltage at 8.5 vdc with 178 mvac ripple. Adjusted power supply. THE VOLTAGE ADJUSTMENT WOULD NOT GO UP WITHOUT INCREASING THE CURRENT ADJUST FIRST AND WAS ABLE TO OBTAIN 12.07 VDC AND 6.5 MVAC. WHILE MONITORING VOLTAGE IT WOULD DROP DOWN TO 8.9 VDC AND HAD TO INCREASE THE CURRENT ADJUSTMENT AND WENT ANOTHER 1/2 TURN ON THE CURRENT KNOB IN CASE IT WAS ON A BAD SPOT ON THE POT. . This power supply only powers the RWM display (PPC-CRT-RWM) on P603. this display is now funtioning. However, Recommend replacing power supply soon. CAT ID is 33069 <I> **** Actions Taken **** Wrote CR | 02-00-PPC-E/S-RWM
399721 | CR | 20191001 |  | 3 | Cart staged without staging label 548' Rx bldg |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of daily logs it was noted that a "Boss Hog" cart was staged on the north end of the 548' Rx bldg west of the RCC radiation monitor and MMS skid. The cart has no identifiers as to why it was staged or by whom. <I> **** Actions Taken **** CRS/SSS informed The cart has been moved and tagged. No further action required.
399722 | CR | 20191001 |  | 4 | Safety 1 flourecent bulb out of 8 lit |  |  |  | N | YES | <D> **** Detailed Description **** poor lighting in the gsb 441 I/c solder shop room 102 <I> **** Actions Taken **** talked with supervisor and wrote this cr <N> **** Equipment Description **** gsb 441'
399723 | CR | 20191001 |  | 3 | EWP Issues delaying 16.3.1/16.3.3 |  |  |  | N | NO | <D> **** Detailed Description **** I&C experienced EWP issues, delaying the continuation of 16.3.1/16.3.3. The work package was unable to be checked in from a tech's tablet, due to an error message about server problem. <I> **** Actions Taken **** Contacted EWP helpline, Informed Supervision, Wrote CR. <N> In order to not lose data entered in the work instructions the supervisor took pictures of the data and copied the data and uploaded it into the work package. When all of the data was copied and captured the package was forced in. The application had to be deleted from the affected tablet and re-applied to get the package off of the tablet. In this case it was apparent that the package had not been checked in for several shifts. Coaching was provided to ensure WOT's are checked in more often to ensure the data in saved.
399724 | CR | 20191001 |  | 4 | R3 sump is not labeled as a confined space |  |  |  | N | YES | <D> **** Detailed Description **** FDR-SUMP -R3 meets the definition of a confined space per ISPM-3 but is not posted as required. <I> **** Actions Taken **** Talked to industrial safety about the requirements wrote this CR | 02-00-FDR-SUMP-R3
399725 | CR | 20191002 |  | 3 | SPIP-SEC-18 review |  |  |  | N | YES | <D> **** Detailed Description **** Evaluate SPIP-SEC-18 to make the procedure more clear and user frienldy. <I> **** Actions Taken **** Security notification made, CR generated <N> **** Equipment Description **** Safeguards Procedure
399726 | CR | 20191002 |  | 3 | Operations Dept. Radios-Fire Drill lessons learned |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The Ops Dept. needs additional radios to allow for casualty/equipment malfunction response. The Equipment Operators have the minimum (5) number of working radios to accommodate the essential watchstanders. There are 3 additional radios in the SSS office. However, these radios should be available to Ops supervision, in the event of an actual plant event. Although radios are available in the tool crib, this does not help Operators trying to respond to time critical events where minutes/seconds count (fire response/equipment failure that could result in reportability/equipment failures that could result in a plant transient or shutdown, etc.). I recommend we double our inventory of radios in the Equipment Operator Center. 10 radios will allow for all On-Shift watchstanders to have a radio, as well as an additional shift of Training- No -training Operators. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** Operations Dept. Radios
399727 | CR | 20191002 |  | 4 | Unanticipated loss of RFW-VMP-1 indications for RFT-A |  |  |  | N | YES | <C> Updated typo in the wording of the CR per Engineering F. Schill. <D> **** Detailed Description **** During the clearance hang for D-BS-V-60A-001 in support of WO# 02119110, specifically the removal of E-FUSE -H13P840/GGF3, the control room unexpectedly received P840.A1 7-1 â€œTURB A VIB TROUBLEâ€ alarm. Further investigation revealed that RFW-VMP-1 retained overall power, but lost indication of turbine speed and vibrations for Reactor Feed Turbine A. E555-E-CP-H13/P840 is unclear as to the interaction between the fuse pulled and RFW-VMP -1. EWD-72E-035 contains unrepresented continuations of electrical lines in section E/F-6 of the drawing which may be related to Fuse GG-F03. With E537-1VA-90 for fuse GG -F03, EWD-72E-035, and EWD-72I-025 for the RFW-VMP-1, the control room staff were unable to conclusively rule out the risk of a High Thrust Bearing wear trip of RFT-A on reinstallation of the fuse. . With the increased risk of a plant transient, the conservative decision was made to lock the clearance and leave the fuse removed while the team was expanded. <I> **** Actions Taken **** Locked D-BS-V-60A-001, informed Turbine bldg watch of potential issues and compensatory actions | 02-00-E-FUSE-H13P840/GGF3
399752 | CR | 20191002 | CAQ | C | MT&E Out of tolerance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0060914 Fluke Dig. Multimeter- model 8842A found OOT & adjusted within specs. DEF #7331A generated. EFIN to Evaluate 7 usages.
399753 | CR | 20191002 |  | 3 | EWD-72E-041 Revision |  |  |  | N | NO | <D> **** Detailed Description **** Grid location 10-E shows RFT-RLY-TT/Z/1A contact 16-17. This relay EPN should be RFT-RLY-TT/Z/1A1. Reference EWD -72E-055. PortalJ EPN for the "1A" relay does not exist.
399754 | CR | 20191002 |  | 3 | Procedure enhancement of 1.3.76 |  |  |  | N | NO | <D> **** Detailed Description **** On page 27 at the top change step 10 Vice President of Operations to Site VP <I> **** Actions Taken **** None
399756 | CR | 20191002 |  | 3 | Deficiency found checking refurbed breaker. |  |  |  | N | YES | <D> **** Detailed Description **** While electricians were performing the configuration task for a new/ overhauled breaker per PPM 10.25.2, it was observed that there was excessive sparking at the charging motor/armature. Craft took a video and contacted their supervisor. This CR is for trending purposes only. <I> **** Actions Taken **** Craft contacted supervisor. Supervisor contacted engineering. Engineering recommended replacing the motor. Craft removed the charging motor from breaker being sent off for overhaul, UTC #430351, Serial #NA251051. Craft will install this charging motor in the breaker they are configuring. This CR is for trending purposes only. <N> **** Equipment Description **** COND-CB-P5. Location is T471, E-SL-63 Compt 2B. | 02-00-COND-CB-P5
399757 | CR | 20191002 | CAQ | D | RB 606 temperature low OOS. | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** RB 606 temperature was 62 degrees F, minimum per log notes is 65 degrees F. Notes state it is a H101 reading, with long notes stating "The minimum temperature is GE 40 degrees F, if the RB crane is not making a full rated lift." <I> **** Actions Taken **** CR written. MCR staff informed.
399758 | CR | 20191002 |  | 3 | Enhancement to SOP-FDR-START. |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.3.1 mentions sump pumps for W-1 thru W-5 and has a â€œreactor buildingâ€ reference. Confusing, should be Radwaste Building. <I> **** Actions Taken **** Wrote CR.
399759 | CR | 20191002 |  | 4 | FDR filters are not lasting due to hi d/p | N | N |  | N | YES | <D> **** Detailed Description **** The FDR filters are requiring frequent backwash and precoats and are not lasting long due to high differential pressure. It has been noted several times with a new FDR filter, and when FDR-TK-22 is allowed to rest for greater than 4 or 5 hours and then is decanted, the d/p increase by 10 to 15 pounds within a very short time; this is not normal. This could be rusty or dirty water in FDR-TK-22 similar to when we were experiencing the iron-water issues this past year. A new sample of the FDR-TK-22 decant water may be prudent in trying to find out why the filters are lasting very long. <I> **** Actions Taken **** wrote AR | 02-00-FDR-FU-19
399760 | CR | 20191002 |  | 4 | Radwaste Shipping software issue delaying turb vlv shipping |  |  |  | N | NO | <D> **** Detailed Description **** The Radwaste Shipping software issue (ref. CR 399558) has delayed the scheduled shipment of turbine valves for refurbishment. The refurbishment is funded for FY20 and is currently NOT in jeopardy assuming the valves can be shipped before the end of October. Recommend trend <I> **** Actions Taken **** Issue discussed with radwaste shipper to determine a resolution date. Contacted warehouse to reschedule the delivery trucks.
399761 | CR | 20191002 |  | 4 | Need to replace EDR-RMS-V/147 control switch | N | N |  | N | YES | <D> **** Detailed Description **** EDR-RMS-V/147 control switch needs to be replaced due to it is very mushy to operate and feels like it will break at any time. <I> **** Actions Taken **** wrote AR | 02-00-EDR-RMS-V/147
399763 | CR | 20191002 | CAQ | D | Rod Accumulator Trouble Alarm P603-A7 drop 6-7 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-22-03. Dispatched OPS-2 to investigate. Rod Accumulator Trouble Alarm was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear. This CR is for trending purposes only <I> **** Actions Taken **** Per ARP with CRS permission | 02-00-CRD-HCU-2203
399764 | CR | 20191002 |  | 3 | Wire landed on wrong terminal H13P840 | N | N |  | N | YES | <D> **** Detailed Description **** E-PP-7AZ/8 supply to fuses in H13P840 not landed properly. The supply to HH fuse 1/2 should be landed on the hot side of GG fuse 3. It is landed on the load side - removal of GG fuse 3 de energized the HH F1 and HH F2 loads. see edms for pic <N> research has been conducted and no work order packages or Engineering changes have been identified that would have modified the wiring associated with E-FUSE-H13P840/HHF1. it is assumed that this is a latent/ legacy wiring issue. This condition will be addressed under WP# 02151429. no further actions are required | 02-00-E-FUSE-H13P840/HHF1
399767 | CR | 20191002 |  | 4 | MT&E found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065286 Hytorc Hyd. Torque Wrench- model HY-5MXT found OOT & adjusted within specs. Not used during Calibration cycle. DEF #7332A written. No Plant Impact. No Action Required.
399778 | CR | 20191002 |  | 3 | TMU pump spare requires more NPSHa under certain conditions | N | N |  | N | YES | <D> **** Detailed Description **** The refurbished pump replacement for TMU-P-1B was tested for net positive suction head (NPSH) required at Ruhrpumpen (vendor). The NPSH required results provided by the vendor are higher than the calculated NPSH available for the TMU water basin, under certain operating conditions. Ruhrpumpen is currently troubleshooting why the NPSHr is higher than expected for this refurbished pump. Sufficient NPSH is required to meet pump performance requirements and to prevent damage from cavitation. Recommend assignment to Engineering for evaluation and resolution. <I> **** Actions Taken **** Discussed test results with pump vendor, third party reviewer, system engineer, component engineer, and design engineer. <N> **** Equipment Description **** This is a spare pump that will replace TMU-P-1B | 02-00-TMU-P-1B
399779 | CR | 20191002 |  | 3 | WO# 02080412-12 COND-AO-231A not meeting IMDS | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** With the actuator adjustment we were unable to obtain a full 10â€ stroke of the actuator. This has been a problem with the same type of actuators in the past. The controller COND-FIC-200A that sends the signal to the valve it puts out 3 PSI at 0% And 15 PSI at 100% on the manual output scale. (Working SAT) The controller is capable of putting out 0 PSI to 19 PSI in manual at the manual lower And upper limits and that corresponds to 0â€ to 9.75â€ stroke at the actuator <I> **** Actions Taken **** Valve Engineer was contacted to evaluate COND-AO-231A And determined the valve was closing and the actuator was functioning but was not Able to achieve a 0â€ to10â€ stroke with 3psi to15 PSI applied with the adjustments available. Due to the valve pushing into a soft seat it will lose some of the available stroke length. Valve Engineer concurred the valve is functioning and is investigating the IMDS issues we Have with this style actuator and make changes accordingly.
399780 | CR | 20191002 |  | 3 | PPM 15.2.4 editorial error |  |  |  | N | NO | <D> **** Detailed Description **** PPM 15.2.14, step 7.1.12 reads as follows; CHECK that FCP-3 TROUBLE alarms clear (Drop 14.5 and Drop 17.4). This step should read to verify the alarms are lit. (similar to step 7.1.11) Discrepancy found while working WO# 02139652-02. <I> **** Actions Taken **** Discussed with CRS, wrote CR. Need PPM revised. <N> PPM referenced in AR Description should be 15.2.4 (not 15.2.14) PPM 15.2.4 Rev 013, MR 003 issued 10-3-19, no further action required. Complete AR per above note.
399781 | CR | 20191002 |  | 3 | CI-9.4 requires a procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** CI-9.4, Trending requires an enhancement. Section 5.2 mentions the Plant Logging System, which is no longer used. <I> **** Actions Taken **** Initiated this condition report.
399783 | CR | 20191002 |  | 4 | MT&E found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #45321 Hytorc Hyd. Torque Wrench- model 2XLT found OOT & adjusted within specs. Not used during Calibration cycle. DEF #7333A written. No Plant Impact. No Action Required.
399784 | CR | 20191002 | CAQ | C | MT&E found out of tolerance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0064637 Hytorc Hyd. Torque Wrench- model 2XLCT found OOT & adjusted within specs. DEF #7334A generated. EFIN to Evaluate 3 usages.
399785 | CR | 20191002 |  | 3 | OI-20 updates |  |  |  | N | NO | <D> **** Detailed Description **** OI-20, Fuel Handling Expectations, minor revision needed. Step 2.7.1 should be deleated, it is an editorial error, the step exists later in the procedure. Step 2.7.7.d should be deleted based on feedback that the refuel floor log book is not maintained.
399786 | CR | 20191002 |  | 3 | Descrepancy between log instructions and SOP-COLDWEATHER-OPS |  |  |  | N | NO | <D> **** Detailed Description **** On OPS-4 rounds it states, "Verify electric heaters are functiong and set at 45 F" at CWPH. Per SOP-COLDWEATHER -OPS it states, " OPERATE PEA-RVT-11 through PEA-RVT-16 as necessary to maintain CW building temperature GT 50F" <I> **** Actions Taken **** Discussed during training week.
399789 | CR | 20191002 |  | 3 | Discrepancy on routing hoses (ABN-TSG-001,002,011) |  |  |  | N | NO | <D> **** Detailed Description **** Discrepancy found in ABNs, see below. ABN-TSG-001 4.21 - "ROUTE the hose to RB 606 in the space between the stairs and the stairwell wall and / or through the center of the stairwell, as necessary." ABN-TSG-002 4.3.12 â€“ "ROUTE and CONNECT the 4â€™â€™ hose sections from RB 441 and RB 606 in the space between the stairs and stairwell wall and / or through the center of the stairwell, as necessaryâ€¦" ABN-TSG-011 - Page 6 middle of page - "CAUTION The hoses should be routed along the stairs. DO NOT route hose through the internal gap between adjacent staircases, or drape down through the open area between the stairwell wall and the staircase since this could cause pinching or excessive kinking" These were the only ABNs we looked at, could be more. Please update ABNs. <I> **** Actions Taken **** Discussed with training
399790 | CR | 20191002 |  | 4 | Stripped screw in mcc bucket fuse clip. | N | N |  | N | YES | <D> **** Detailed Description **** While performing bucket maintenance on E-DISC-7C5CL, the fuse clip screw stripped out while performing torquing per PPM 10.25.187E. <I> **** Actions Taken **** Craft stopped work and contacted their supervisor. Craft supervisor informed them to have planning add steps to replace parts as needed and then re-perform torquing. Craft replaced the disconnect rotary switch assembly with spare bucket parts. <N> E-DISC-7C5CL supplies power receptacles on RB 501'. | 02-00-E-DISC-7C5CL
399792 | CR | 20191002 |  | 3 | (FP) RW 507 in need of assistance for safety & fire reasons |  |  |  | N | NO | <D> **** Detailed Description **** Fire protection walked down RW 507 (room C405) and found the access to reach all areas of the room were inadequate for fire brigade response paths. The area needs to maintain a clear path to allow for access and egress of the area in case of an emergency. The path is also another way that combustibles are seperated and held within their respective areas. Safety of the pathways are also a concern. Several extension cords were found running across the floor without tape or ramps. This becomes a tripping hazard. A ramp would be the better option than tape based on the amount of rolling carts in the area. Draping the cords overhead to the area needing power should be looked at also. <I> **** Actions Taken **** Contacted area owner and created CR. Request area owner, HP, and Laborers work together to clean up this area as we are striving for excellence.
399798 | CR | 20191002 | CAQ | D | DOE executed CRASH failed | N | Y |  | N | NO | <D> **** Detailed Description **** DOE indicated that Benton and Franklin County did not respond when they executed the CRASH call. <I> **** Actions Taken **** EN Telecom confirmed the Frontier circuit is down to Benton County. A high priority service ticket was placed with Frontier and their tech has fixed the problem. EN tested with Franklin County and found the CRASH operable to them. Notified EP, MCR, and Security. Recommend CAQ-D for trending.
399799 | CR | 20191002 |  | 4 | WOA-FL-1A EOR | N | N |  | N | YES | <D> **** Detailed Description **** WOA-FL-1A end of roll <I> **** Actions Taken **** informed MCR | 02-00-WOA-FL-1A
399800 | CR | 20191003 | CAQ | D | IDS 6 needs maintenance | N | Y |  | N | YES | <D> **** Detailed Description **** Security IDS zone 6 needs maintenance. Contact security at ext.2185 for further details <I> **** Actions Taken **** Comp in place, security notification made, CR/WR generated | 02-00-SEC-IDS-E/S/5/6
399801 | CR | 20191003 |  | 4 | Disconnects Need Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** While performing SOP-COLDWEATHER-OPS it was noted that WRA-DISC-7E1DL, WRA-DISC-7E1DR, AND WRA-DISC-7E5DR need to be lubricated. They will not properly engage when taken to close, and will pop into a mid-position when any amount of force is applied to the handle. This condition is indicative of a lack of lubrication, cleaning, and other routine maintenance. These disconnects power space heaters, and will need to be serviced in a timely manner so that the station is prepared for the upcoming cold weather. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RW 487 | 02-00-WRA-DISC-7E1DL,02-00-WRA-DISC-7E1DR,02-00-WRA-DISC-7E5DR
399802 | CR | 20191003 | CAQ | D | Spray pond B high level alarm. | Y | N |  | N | YES | <D> **** Detailed Description **** Received SPRAY POND B LEVEL HIGH/LOW 4.840.A5 drop 7-1. SW-LI-1C is reading 14.3 feet and has been trending up per point L071. SW-LI-1B is reading 13.5 feet and steady. Local level indication is steady at 13 feet and 4 inches. SW-LI -1C appears to be failing. <N> ADDED TO T19-SW-LI-1A-001 | 02-00-SW-LI-1C
399803 | CR | 20191003 |  | 4 | UH-17, Wellhouse 2 Unit Heater, does not run | N | N |  | N | YES | <D> **** Detailed Description **** Step 6.1.10.b.1 requires UH-17 to be energized and operable. I took the thermostat to max and it did not start. The disconnect, E-DISC-FDP40/001/6R in wellhouse 2, is closed. There doesn't appear to be a EPN in Portal J. The disconnect feeder is labeled as UH-17, which I have found in past work orders. <I> **** Actions Taken **** Wrote this CR/WR and notified MCR <N> **** Equipment Description **** NE corner inside wellhouse 2
399816 | CR | 20191003 | CAQ | D | AOV assessment - PMID 2924-03 late date |  |  |  | N | NO | <D> **** Detailed Description **** PMID-2924-03 does not show credit for previous work performed, however the late date was changed. Currently the PMID 2924-03, the late date was extended to make it to 2021, which is outside of the PM frequency of 25%. <I> **** Actions Taken **** Generated SMS 00399815 This is administrative CR. Condition was corrected via SMS 399815. . <N> SMS-AR submitted and date has been corrected in the system. No further actions required.
399817 | CR | 20191003 | CAQ | C | MT&E found out of tolerance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0066897 Votes Contacts Cable Assembly- model 85006 found OOT & adjusted within specs. DEF #7335A generated. EFIN to Evaluate 7 usages. <I> MOV Engineer Evaluated DEF and found No Issues- See EDMS for full Eval
399818 | CR | 20191003 |  | 4 | MT&E found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0067434 CDI Torque Wrench- model 501MRMH found OOT & adjusted within specs. Per PPM 1.5.4 section 4.4.3 (a-c) Torque Wrench had acceptable post use verifications @ +/- .06%. DEF #7336A written. No Plant Impact. No Action Required.
399819 | CR | 20191003 |  | 4 | MT&E found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0064089 Fluke Doc. Process Calibratorâ€”model 743B found OOT & Rejected- Not Economical to Repair. Not used in the OOT Range of Resistance Measurement. DEF #7337A written. No Plant Impact. No Action Required.
399820 | CR | 20191003 |  | 3 | E526-2 drawing editorial |  |  |  | N | YES | <D> RFW-RLY-99T1X/1A should be corrected to RFT-RLY-99T1X/1A on E526-2. Reference E526-1 and EWD-72E-033. | 02-00-RFT-RLY-99T1X/1A
399822 | CR | 20191003 |  | 3 | SWP-MAI-03 lacks details for lower level issues |  |  |  | N | NO | <D> **** Detailed Description **** SWP-MAI-03 is lacking details for addressing issues identified in section 1.1.4 that do not require use of the OCC. The detail should focus on how the station would use an emergent-issues manager and how the WWM and SM can turnover the issue and what to expect. During the recent issues with BS-V-60A, the SWP-MAI-03 guidance did not appear to be helpful to address the needs fo the SM. <N> Procedure 1.3.16 Issues Management is the procedure for dealing with those issues that fall somewhere between just the WWM handling and a full OCC. This CR is closed. Notified initiator
399823 | CR | 20191003 |  | 3 | Missed 2019 Q3 manager/supervisor continuing training |  |  |  | N | NO | <D> **** Detailed Description **** 2019 Q3 missed manager/supervisor training per Data Access Desktop report shows 30 individuals missed MT000718, Building Trust and Mastering Conflict, and 31 individuals missed MT000719, Safety Conscious Work Environment Refresher. Pilot class for the quarter was held August 7th and six subsequent sessions were held from August 29th to September 26th. <I> **** Actions Taken **** Sent email September 19th to those not on rotating shift reminding them of the need to attend and that there was still room in the last 2 session.
399825 | CR | 20191003 |  | 4 | RW 467 Decon Facility C228 Centrifuge RM bolt(s) trip hazard |  |  |  | N | NO | <C> Edited elevation description and subject per M. Bailes <D> **** Detailed Description **** During a walkdown of the RW 467 Decon Facility C228 Centrifuge room the following conditions were observed deficient: There are multiple bolts protruding from the ground that present a trip hazard. Fortunately this is a low traffic area. There is scaffolding erected in the small room which also limits access to the tripping hazar d(s). A noted deficient condition for the Scaffolding, Scaffold tag 3736 WO 02101017, is that one of the rear feet appears not fully seated on a stable surface. Suggest scaffolders/ structural engineer review and adjust as needed. <I> **** Actions Taken **** Wrote this CR, attached information for a work request. Send photos to engineering. Added to Industrial Safety Hazards tracking list. <N> **** Equipment Description **** NA for the EPN location Scaffolding also needs evaluation and adjustment as needed.
399826 | CR | 20191003 |  | 4 | Innaccurate impact statement delayed work |  |  |  | N | NO | <D> **** Detailed Description **** The impact statement for WO 02131984 did not address the need to open E-IR-67 and there was no INOP sheet made. This was caught by the implementing crew and corrected before the work was allowed to proceed. This delayed the work from days to swings. <I> **** Actions Taken **** Wrote CR. Biscussed with WWM and OPS WC Manager
399831 | CR | 20191003 | CAQ | D | RCIC-P-3 packing leakage needs an adjustment | Y | N |  | N | YES | <D> **** Detailed Description **** RCIC-P-3 packing needs an adjustemt as the leakage is currently a little excessive. <I> **** Actions Taken **** informed Shift Supervision & emailed video of leakage | 02-00-RCIC-P-3
399833 | CR | 20191003 |  | 3 | Update SOP-HVAC/WCH-OPS AND SOP-HVAC/WCH-START with a P&L |  |  |  | N | NO | <D> **** Detailed Description **** Update SOP-HVAC/WCH-OPS AND SOP-HVAC/WCH-START with a P&L stating the following for WCH-CR-51A Ensure that the oil separator and compressor heaters have been operating for a minimum of 24 hours before starting. Failure to do so may result in equipment damage. Reference CVI OMM 216-00,69 pg 121 <N> Correction CVI OMM 216-16 pg 121
399834 | CR | 20191003 |  | 3 | 2019 AFOF Plant Personnel in Force on Force Play Area |  |  |  | N | NO | <D> **** Detailed Description **** During the 10/2/2019 Annual Security Force on Force Exercise, plant personnel walked through the drill play area on multiple occasions after site public address announcements were made that the drill was in progress. Having plant personnel in the drill play area poses a safety concern. These instances also caused several unplanned time-outs adding unnecessary artificialities to the exercise. <N> Individuals were coached on the importance of adherence to Plant Public Address announcements. Additional communication was made to craft workgroups and was published in the EN News.
399835 | CR | 20191003 |  | 3 | 2019 AFOF Simulated Engagements 10/2/19 |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate the conditions that led to the simulated neutralizations of security response players during the conduct of Annual Force on Force Exercises. <I> **** Actions Taken **** Security Programs Management notified.
399836 | CR | 20191003 | CAQ | C | E-B2-1 Does Not Meet 100% Capacity Requirement DG-1 Outage |  |  |  | N | YES | <D> **** Detailed Description **** DG-1 planned maintenance outage scheduled for Monday, 10/7/19 is planned to utilize LCO 3.8.1.B.4.2 allowing 14 days LCO completion time with established risk management actions for the alternate AC sources. PPM 1.3.76 Attachment 9.3 step 9.0 requires battery capacity for E -B1-1, E-B1-2 and E-B2-1 be verified greater than or equal to 100% on the last battery capacity surveillance. It was discovered while performing this verification per WO 02148666-09 that E-B2-1 was last evaluated at 97.65% capacity per ESP-B21-F101, 60 Month Battery Testing of 250 VDC, performed on 5/16/2019 (WO 02124385). This requirement in PPM 1.3.76 references a commitment letter to the NRC: G02-05-147 regarding license amendment request for extension of DG completion time. See page 16 of Attachment 1. <I> **** Actions Taken **** Notified Shift Manager and Work Control. Initiated this CR. Currently verifying battery capacity for E-B1-1 and E -B1-2. Entered SWP-MAI-03 to resolve issue. Duty Manager assigned emergent issues manager to drive resolution due 10/4/19 1800. There is no new challenge to operability for the battery. The PPM 1.3.76 requirement for entering the extended DG outa cannot be currently met. | 02-00-E-B2-1
399837 | CR | 20191003 |  | 4 | Restore PACSS sample rack to operable |  |  |  | N | YES | <D> **** Detailed Description **** The Post Accident Containment sample rack has been out of service for several years due to multiple valve failure and confusion on how to lift the clearances for PMT. After review by operations, the following sequence of events must happen to restore the sample rack to operability. To limit confusion, a single work order should be generated to track all of the necessary steps. These are the steps required to restore operability: 1. Complete work instruction similar to WO 02073715-04. This will require a new work order to be generated and worked. 2. Lift D-PSR-V-003-ISO-001 to restore RHR-V-747 3. Perform CSP-PSR/IST-Q701 with 2 year VPI 4. Call all the PCIV's operable and lift C-PSR-PCIV -002 <I> Email message from Sid morrison added to EDMS file <N> **** Equipment Description **** PACSS sample rack
399839 | CR | 20191003 |  | 3 | CVI doecumentation update needed for COND-LCV-11 |  |  |  | N | YES | <D> **** Detailed Description **** CVI documentation for COND-LCV-11 needs to be updated to remove or otherwise address that the Bailey RQ-10 position transmitter & associated linkage is no longer hooked up to AOV COND-LCV-11. Per the AOV Program Manager, this position transmitter for COND-LCV-11 has been permanently disconnected (linkage removed - the position transmitter is still mounted to the AOV). The subject position transmitter is Item 14 on CVI DWG 589-99,6 and CVI DWG 589-99,3. CVI DWG 589-99,6 errantly still shows the linkage from the position transmitter as installed (it does not exist in the field - see photos attached to the EDMS of this AR CR 399839). Additionally, the contract 589 CVI drawings for COND-LCV-11 all appear to refernced CVI OMM 589-00,3 which has apparently been superseded by CVI OMM 503-00,14. Finally, CVI OMM 503-00,14 may also require clarification that the Baily EQ-10 position transmitter for COND-LCV-11 has been spared in place with its linkage permanently removed. Suggest resolution to the AOV Program Manager. This is a documentation cleanup only - no impact/effect upon the physical plant. | 02-00-COND-LCV-11
399840 | CR | 20191003 |  | 4 | The room lighting in RHR B pump room is inadequate | N | N |  | N | NO | <D> **** Detailed Description **** Today the Resident NRC Inspector pointed out to the Shift Support Supervisor that the room lighting in the â€˜Bâ€™ RHR pump room is inadequate. As OPS 2 I went to verify this and discovered that is a fact. I also noted that the overhead lighting of the â€˜Aâ€™ RHR pump room is inadequate as well. Please have electricians replace bulbs as necessary. <I> **** Actions Taken **** toured the areas to verify inadequate room lighting non-essential lighting <N> **** Equipment Description **** 'A RHR pump room mezzanine liand 'B' RHR pump room lighting
399842 | CR | 20191003 |  | 4 | RW 525 Comm Room lights not working | N | N |  | N | YES | <D> **** Detailed Description **** A minimum of 5 lights are out or flickering in the RW515 Comm room. Please repair for a safe work environment. <I> **** Actions Taken **** Notified the MCR and wrote a CR. non-essential lighting <N> **** Equipment Description **** RW 525 Comm room
399843 | CR | 20191003 | CAQ | B | 2018 LORQ Biennial Written Exam Overlap |  |  |  | N | NO | <C> RISK; MEDIUM CAUSE: COMPLEX INVESTIGATION TEMPLATE <D> **** Detailed Description **** During the 2018 LORQ Biennial written examination, one SRO failed written exam SRO E2 (LR002420) and was later remediated with written exam SRO E3 (LR002420). The remediation exam contained one question which exactly duplicated a question from the original exam. This does not meet the requirements outlined in IP 71111.11 Appendix F, Item 2, which states, "Re-examinations do not contain any test items which exactly duplicate test items from the original examination" TDI-23 contains a similar requirement in step 4.2.9 The student had margin so that removing this question from the examination would not result in a failure. <I> **** Actions Taken **** This CR will be reported to our NRC Resident and our NRC Liason. <N> This deficiency was identified during the Pre-NRC 71111.11 Focused Self Assessment.
399844 | CR | 20191003 | CAQ | C | Scenario Base Testing data for two 2018 scenarios lost |  |  |  | N | NO | <D> **** Detailed Description **** Scenario Based Test (SBT) packages for scenarios LR002086 and LR002087 were missing the electronic portion of the package which is made up of simulator data files and photos of the marked up EOP charts. SBT is considered a simulator performance test per section 4.4.3.2 of ANS-3.5-2009 which means that records should be retained for four years, or until superseded. This is clearly required in IP 71111.11 Appendix G, Step 8. It is also required in TDI-06 step 3.3.2.i. This data was lost do to a failed usb device. <I> **** Actions Taken **** Will inform NRC Resident and NRC Liason
399845 | CR | 20191003 |  | 3 | new badge photos failed to transfer from Security Computer |  |  |  | N | NO | <D> **** Detailed Description **** New badge photos were not successfully transferred from the Security Computer to the Corporate Network. Gaps in the transfer of DMP export files were found to be the underlying cause. <I> **** Actions Taken **** Worked with Access Authorization and Computer Engineering to send new full image table. This has partialy resolved the issue. Next action is to load badge images to replace the low-res versions in Lenel. <N> Recommend NCAQ 3 to IS
399846 | CR | 20191003 |  | 3 | Procedure enhancement for 1.3.57 |  |  |  | N | NO | <D> **** Detailed Description **** 1.3.57 references OPDRV's in attachment 9.7 and needs to be updated <I> **** Actions Taken **** Wrote CR
399848 | CR | 20191003 |  | 3 | Cobalt reduction actions aren't achieving desired results |  |  |  | N | NO | <D> **** Detailed Description **** HPI-12.91 outlines the elemental cobalt sampling of new components to ensure that components placed into the primary systems are free of cobalt that could become activated. The majority of the recent cobalt smears requested have been on components containing stellite, which contains cobalt and nickel products, both of which can become activated in the primary system. The intent of the cobalt reduction program is to minimize the introduction of new cobalt-containing items, which ultimately reduces the source term (and dose rates) in the plant. Suitable replacements for stellite (such as NOREM) have been available in the industry for an extended period of time, and the use of stellite components in repairs and replacements should be discouraged. I believe that "like for like" exchanges of components are not receiving a full cobalt reduction review to determine if non-cobalt alloys are available. <I> **** Actions Taken **** Discussed concerns with Radiological Services personnel.
399849 | CR | 20191003 |  | 3 | SOP-DG-DSA procedure change request |  |  |  | N | NO | <D> **** Detailed Description **** Add this note above every step which opens DSA-V-84. "Opening DSA-V-84 may result in DSA-PCV-1C or DSA-PCV-2C venting to atmosphere and lowering DSA air bank pressure. Reference CR 399463" <I> **** Actions Taken **** Initiated this CR.
399850 | CR | 20191003 |  | 3 | DMA model work order changes required |  |  |  | N | NO | <D> **** Detailed Description **** The planner's impact statements for DMA damper calibrations need to changed to include the following statement: "PPM 10.23.7 uses a temporary power source to stroke dampers. A TES clearance is required.". The following model work orders are impacted: 01133795, 01133797, 01133802, 01187924, 01133807, 01187925, and 01133804. <I> **** Actions Taken **** Notified the planning supervisor. Added a Job Hazard Analysis to the EDMS document file to align compliance to PPM 1.3.75 Temporary Energy Sources and ISPM-18 Safety Administrative Controls. This JHA should be added to all of the model work orders.
399851 | CR | 20191003 | CAQ | D | FDR-TK-22 decant full of soluble iron. | N | N |  | N | YES | <D> **** Detailed Description **** A sample of FDR-TK-22 was taken from a decant process per WR 29151894. Pictures of the sample can be seen in the EDMS tab. This sample appears to be heavy in soluble iron. The sample was delivered to chemistry lab for verification of iron. A determination needs to be made of the source and a plan developed to remove the iron as FDR-FU-19 run times are very short. Besides just checking with other nuclear plants a check with all types of plants that perform water treatment should be made for how they deal with soluble iron elimination. <I> **** Actions Taken **** Wrote this AR/WR and informed supervision. | 02-00-FDR-TK-22
399854 | CR | 20191003 |  | 4 | Main Turbine SHR calculates as YELLOW |  |  |  | N | NO | <D> **** Detailed Description **** Following 3rd quarter update of the Main Turbine System Health Report (TURB-LO), the calculated color of the system transitioned to YELLOW. The color calculated as WHITE in the previous update; however, it was voted in PHC on 05June2018 to be made YELLOW. Since the calculated color was WHITE, this CR is to document that the actual calculated color is now YELLOW. Primary factors for YELLOW as the system color are: 1. There remains deficiencies in the turbine supervisory system that was part of the three items that prompted PHC to drive the color YELLOW administratively. 2. Elevated Main Turbine vibrations on Bearings 4 and 7 threaten to impact generation. Currently, an ODMI and OCC-03 are in place to manage this condition. 3. High differential temperatures between the cover and base on the GOV end of the HP Turbine threaten to impact generation. Currently, an ODMI and OCC-03 are in place to manage this condition. This CR is generated to meet the expectation of a system going YELLOW and a revised System Health Improvement Plan is in progress in accordance with Section 6.5.2 of PPI ENG SYS-2-17. <I> **** Actions Taken **** Reviewed PPI ENG SYS-2-17 <N> **** Equipment Description **** System Health Report
399855 | CR | 20191003 |  | 3 | Unable to perform work on SW-TE-1BR |  |  |  | N | YES | <D> **** Detailed Description **** Unable to perform the work instructions for SW-TE-1BR, further engineering evaluation needs to be performed to better understand what is preventing the removal of the TE. Also need to evaluate whatâ€™s the worst that could happen if the TE breaks during the performance of work. OPS identified that if we lose the function of the TE, the station would be in a condition that requires plant to go to mode 3 within 12hours if not functional within 30 days. <I> **** Actions Taken **** Wrote CR, Informed Work Control & Supervision | 02-00-SW-TE-1BR
399856 | CR | 20191003 |  | 4 | Minor First-Aid |  |  |  | N | NO | <D> **** Detailed Description **** Employee while descending a scaffold ladder in the CST pit came in contact with a ladder bolt causing a minor abrasion to his left wrist. Employee had all the appropriate PPE during this task. Employee notified Industrial Safety and first-aid was self-administered and employee has returned back to work with no issues. <I> **** Actions Taken **** WPS Safety followed ISPM-1 procedure requirements while notifying Occupational Health, ENW Industrial Safety and Site Support Contractor Manager regarding the details of this first-aid. No further action is required. <N> Williams Plant Services.
399857 | CR | 20191003 |  | 4 | Flooding in CWPH Rm B107 and CWPH Floor | N | N |  | N | YES | <D> **** Detailed Description **** During the halogenation on Monday 10/2, the Chem Tech observed that when the sump in the vault below the CWPH Room B107 came on the water came out of the room drain resulting in the room flooding with over an inch of water. The water ran out underneath the door to the main CWPH area and covered an area from the rollup door to the fire pumps. See attached video uploaded to the EDMD folder for this CR. <I> **** Actions Taken **** CR Written and Supervisor notified <N> **** Equipment Description **** CWPH vault sump and pump
399859 | CR | 20191003 |  | 4 | (NRC) Hose clamp and broken label found in RHR C pump room |  |  |  | N | NO | <D> **** Detailed Description **** (NRC) A broken label plate for SW-V-777A and a 2 inch hose clamp were found on the floor in the RHR 2C pump room. <I> **** Actions Taken **** OPS 2 cleaned up the 2 inch hose clamp and broken label. A new label for SW-V-777A was ordered <N> **** Equipment Description **** RHR-P-2C pump room
399860 | CR | 20191003 |  | 3 | eSOMS Locked Up | N | N |  | N | NO | <D> **** Detailed Description **** eSOMs locked up at approximately 2130 to 2200 on 10/3/19. IS duty officer was contacted and resolved the issue. This impacted uploading the OSP-INST-H101s. <I> **** Actions Taken **** CR for trend <N> OSP-INST-H101 completed prior to 2230.
399861 | CR | 20191004 |  | 3 | FDR-LIS-119 Deenergization not clear prior to removal | N | N |  | N | YES | <D> **** Detailed Description **** During work on FDR-LIS-119 02130101, it was determined that the work order was lacking instructions for removal of power prior to replacement <I> **** Actions Taken **** Informed I&C supervision, Operations and returned to planner for work steps revision <N> **** Equipment Description **** RW 467 N7/12.4 | 02-00-FDR-LIS-119
399862 | CR | 20191004 |  | 4 | Packing Leak FP-V-P84/810 Preaction 84 HPCS Tank Room Supply | N | N |  | N | YES | <D> **** Detailed Description **** Packing Leak FP-V-P84/810 Preaction 84 HPCS Tank Room Supply. 60 drops per minute. <N> **** Equipment Description **** DG3 Room Elev. 455' Non-essential pre-action sprinkler suppression system. | 02-00-FP-V-P84/810
399871 | CR | 20191004 |  | 4 | Incomplete uploaded image for QAR MAI 0117178401 |  |  |  | N | YES | <D> **** Detailed Description **** The currently uploaded image in Portal J for QAR MAI 0117178401 is incomplete (only 2 pages) - it is only an attachment associated with the WOT, not the entire WOT. This QAR MAI document is the record documentation for R19 WOT 01171784-01 - RFW-MO-65A REPLACE MOTOR) which implemented R19 EC MALT 8216. Actual weight information for the old/original and new/replacement motor at RFW-M -V/65A was collected and recorded as part of WOT 01171784 -01. The information for the original motor removed and replacement motor installed is needed now for AR EVAL 387206. This is an administrative documentation records issue only. <N> QAR MAI 0117178401 has two images in the Records Management module. The two page image was a supplement to a 103 page WOT. The entire WOT seems to be available. Notified individual who wrote the CR. Recommend NCAQ4 | 02-00-RFW-M-V/65A,02-00-RFW-MO-65A
399872 | CR | 20191004 |  | 3 | CVI OMM 999-00,145 not updated for R19 EC MALT 8216 |  |  |  | N | YES | <D> **** Detailed Description **** CVI OMM 999-00,145 was not identified as an affected document and updated for implementation of R19 EC MALT 8216 (REPLACEMENT MOTOR (RFW-M-V/65A) FOR RFW-V-65A RFW-MO-65A). EC MALT 8216 was implemented via R19 WO 01171784. This has resulted in a lack of accessible information to acess AR EVAL 387206 (Replace RFW-M-V/65A and V/65B Mag Rotors). Interestingly, this OMM was identified as impacted by and updated for similar replacement of RFW-M-V/65B per WO 0117183 (EC MALT 8232 implementation). <N> EC MALT 8216 and EC MALT 8232 were both emergent R19 Minor Alteration modification packages. Subsequently, RFW-M-V/65A was replaced again during R23 with CID 65001902 via emergent R23 Minor Alteration EC MALT 16534 (WO 02079580). EC MALT 16534 also failed to update CVI OMM 999-00,145 with information for the resultant replacement motor at RFW-M-V/65A. The motor installed during R23 at RFW-M-V/65A was PO 329289 Item 1 CID 65001902. | 02-00-RFW-M-V/65A
399873 | CR | 20191004 |  | 4 | P840 A2 annunciator fault | N | N |  | N | YES | <D> **** Detailed Description **** P840 A2 annunciator fault on card 6-5 / 6-6 caused smoke release and most likely cleared FC fuse on the power supply since the btm half of the annunciator panel is dark. card is 30431 rev E top NC bottom NO. see EDMS for pic suspect 1.5 a fuse <I> **** Actions Taken **** entered ABN ANN established temp logs Coordinated with WWM to resolve issue. Annunciatios have been restored by replacing the card and 2 fuses. See associated WR for more details. . <N> card # 304341 rev e | 02-00-ANN-E/S-A/A2/FHB
399874 | CR | 20191004 |  | 3 | SWP-CM-02 updates needed |  |  |  | N | NO | <D> **** Detailed Description **** The following updates for SWP-CM-02 (Temporary Configuration Changes (TCCs)) should be considered: 1) Precaution and Limitation 2.9 implies that only TCHG assignments are used to track TCCs. TCHG assignments are used for tracking of most (but not all) TCCs as directed by the SWP proceedure. NICM assignments are used for tracking of non-intrusive compensatory measures (non-intrusive CMs). Precaution and Limitation 2.9 needs to be updated to address use of NICM assignments in addition to TCHG assignments for TCC tracking. 2) Section 5.3 (Temporary Modification (TM) steps 5.3.1 and 5.3.2 currently include direction for TMs AND for non-intrusive compensatory measures (non-intrusive CMs). This direction for non-intrusive CMs is not currently included in Section 5.4 (Non-intrusive Compensatory Measure (CMs)). 2a) The direction for non-intrusive CMs currently in Steps 5.3.1 and 5.3.2 needs to be removed. 2b) The direction for non-intrusive CMs currently in Steps 5.3.1 and 5.3.2 needs to be added to Section 5.4 of the procedure. Suggest resolution by Design Engineering.
399875 | CR | 20191004 |  | 3 | L013 computer point unable to Cal during CBD-TE-10 loop cal | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing WO 02139984-03 PMT following CBD-TT-10 replacement. Computer point L013 was unable to be calibrated. As found/as left readings for CBD-TT-10 SAT at all cardinal points. Computer point L013 was approx -7deg F low at every cardinal point with a allowable tolerance of +/- 5 deg F. <I> **** Actions Taken **** Informed Supervision, operations, and work week Mgr. Computer Tech will inform Computer Eng and seek direction.
399876 | CR | 20191004 | CAQ | D | FP-CP-FCP2 unexpected alarm, window 10-2 | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of PMT 02139652-04 (FSP8 capacitor replacement), an unexpected alarm was received. The PMT task performs PPM 15.2.16 for Zones 79 and 80; the alarms at FCP2, windows 9.1 and 9.2 are received, as expected. However, in addition to these, window 10-2 was also sometimes received. This was not consistent with every alarm received at 9-1 and 9-2. <I> **** Actions Taken **** Discussed with Control Room personnel; wrote CR. | 02-00-FP-CP-FCP2
399877 | CR | 20191004 | CAQ | D | CRD-HCU-2651 High Water Level alarm received | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-26-51. After investigation, Rod Accumulator Trouble Alarm P603-A7 drop 6-7 was for CRD-HCU-26-51 high water level. <I> **** Actions Taken **** followed arp. | 02-00-CRD-HCU-2651
399878 | CR | 20191005 |  | 4 | RX 606' Kelley BLDG (HP Instrument Cabinet needs Relocated) |  |  |  | N | NO | <D> **** Detailed Description **** -The HP Instrument Cabinet just inside Door R-704 should be relocated to create more space in the room for storage and it will also create easier access for HP Technicians when they enter the room nightly to check the P-10 Gas levels. Possibly move the cabinet to the back of the room which would eliminate the immediate bump hazard right when you enter the room. <I> **** Actions Taken **** -Notified HP Supervision via e-mail. -Initiated Condition Report/Work Request <N> **** Equipment Description **** RX 606' Kelley BLDG R-704
399883 | CR | 20191005 | CAQ | C | FSAR sect 8.3.1.1.7.2.1 brkr cross-tie position inaccurate |  |  |  | N | NO | <D> **** Detailed Description **** FSAR Section 8.3.1.1.7.2.1 states that for DG routine maintenance, the cross connect breakers will be installed in their cubicle; however, they will remain racked out and locked in the open position. Cross-tie breaker position is only verified during AOT DG windows, not routine maintenance. Additionally, to support the response time for a station loss of power event, the breakers need to be racked in. The breaker is administratively and physically prevented from closing by having the charging springs discharged with the control power fuses removed. <I> **** Actions Taken **** FSAR section 8.3.1.1.7.2.1 needs to be updated to reflect actual plant required conditions (breaker racked in with control power removed during AOT maintenance) or the details of the breaker position removed from this section as this is likely more detail than necessary in FSAR.
399884 | CR | 20191005 | CAQ | D | WO #02062447 issues | Y | N |  | N | YES | <C> CR reopened to cross reference additional WR 29146254, marked completion required box, then taken back to complete <D> **** Detailed Description **** Issues/ indications while performing WO 02062447 not as indicated on WO. <I> **** Actions Taken **** After transferring to Backup/ Emerg power, IAW step 4.5.2, Alarm 83E 'Emergency Power' alarm lamp was not illuminated. This alarm was verified to be working by taking it to 'Test' and back to 'On'. Alarm came in and cleared both locally and in MCR. Testing was continued, completed SAT. It was noted that MCR got the alarm H13-P800.C4 drop 10-5 during times that BOTH Normal and Emergency bkrs at MC8AA and MC7AA were OFF. | 02-00-E-TR-B
399885 | CR | 20191005 |  | 4 | Red light out for CO2 hose reel on TB501. | N | N |  | N | YES | <D> **** Detailed Description **** The red light is no longer lit (light likely burned out) for the relay associated with the CO2 hose reel on TB501. <I> **** Actions Taken **** Informed CRS. | 02-00-FP-RLY-62/CO2/3
399889 | CR | 20191006 |  | 4 | HT-H-SR14/3 Trouble Light Lit on HT-HTP-PTM/30 | N | N |  | N | YES | <D> **** Detailed Description **** Trouble light was found lit on rounds. Called the MCR and followed ARP for H2/O2 Analyzer Heat Trace Trouble. Sample line temperature of SR14/3 indicated 177.5F on HT-HTP -PTM/30. HT-TS-SR13/2 (on the same panel) was written up on 9/15/19. Reference AR 399086 / WR 29151592 <I> **** Actions Taken **** Notified MCR | 02-00-HT-H-SR14/3
399890 | CR | 20191006 |  | 3 | Issues with WO# 02148863-01 | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** WO# 02148863-01 was not performed on 10/6/19 due to multiple issues. The lighting in the field is very poor. The access space between a video console and railing next to an open hatch was very small making detector difficult to reach. The source to be used does not have adequate holder, which presents a risk of it being dropped next to an open hatch and then loss of control of rad material. Scheduled for 2 craft, but there should be three craft with one in the MCR, and two having the source user qual in the field as it is not practical to hold phone to communicate, EWP, and source in a tight area. A Walkdown before work was scheduled was not performed that would have identified these issues. <I> **** Actions Taken **** Observed these issues and communicated to Supervision. Supervision and Craft went to field to observe. Supervisor communicated with WWM and wrote CR to document.
399891 | CR | 20191006 | CAQ | D | RHR-P-2A Oil Level High | Y | N |  | N | YES | <D> **** Detailed Description **** On rounds RHR-P-2A upper and lower oil levels appeared to be approximatel +0.5-0.75'' above standstill level. Logs state level shouldn't be GT +0.25" above standstill level when pump is off . Level needs lowering or log entry changed. <I> **** Actions Taken **** Notified CRS | 02-00-RHR-P-2A
399892 | CR | 20191006 | CAQ | C | Loss power to OG-RIS-601B. | N | Y |  | N | YES | <D> **** Detailed Description **** Loss power to OG-RIS-601B, the channel status display screan is blank. Received alarms OFF GAS POST TREAT RAD HI-HI-HI, OFF GAS POST TREAT RAD HIGH, and OFF GAS POST TREAT RAD MONITORS DNSCL. OG-RIT-601B has no operate light lit and the control display screan reads no RM23 comms. | 02-00-OG-RIS-601B
399893 | CR | 20191006 |  | 3 | Procedure enhancement for Ops annunciator response procedure | N | N |  | N | NO | <D> **** Detailed Description **** During the response to the failure of OG-RIS-601B it was noted that the control room annunciator response procedure directs the collection of noble gas samples from offgas posttreatment following the failure of a channel. This is contrary to the direction of the ODCM which directs the verification of the other channels operation. If no channel was operable it would be necessary to perform this sample. <I> **** Actions Taken **** CRS informed. Effluent manager notified via voicemail.
399894 | CR | 20191006 |  | 4 | Lighting in DG-1 room |  |  |  | N | NO | <D> **** Detailed Description **** Lighting in DG-1 room is unsatisfactory and unsafe. The lighting is very poor and really not acceptable for the individuals that are performing work for this upcoming DG-1 outage.The lighting should have been addressed prior to the DG-1 outage so work could be performed in conditions with better lighting. <I> **** Actions Taken **** Contacted CRS/SM and wrote this CR
399895 | CR | 20191007 |  | 4 | TMU-C-1B shows no indication. | N | N |  | N | YES | <D> **** Detailed Description **** TMU-C-1B has no status indication at TMU-42-8R3E or E-CP -TB/MU2005. Suspect blown fuse(s).This problem was discovered and written up on 5/29/19 in a separate AR/WR. This compressor is currently selected to Standby at TMU. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TMU Pump house. | 02-00-TMU-C-1B
399899 | CR | 20191007 |  | 3 | Housekeeping T471E Backseat Cart - Repaeat of AR 399177 | N | N |  | N | NO | <D> **** Detailed Description **** Two valve backeseat cart and other items are staged in a storage location designed for one cart. This is a repeat CR from the previous month with no action taken. Assign to electrcial maintenance to correct.
399900 | CR | 20191007 |  | 4 | Excellence Model posting blocked by lockers in classroom | N | N |  | N | NO | <D> **** Detailed Description **** In Kootenai room 120, there are several lockers blocking the station excellence model and station focus area postings. See MOT OBS-2019-7695. <I> **** Actions Taken **** Notified the classroom owner (fire brigade instructor) and initiated this condition report. <N> Verified at 7:15 AM on 10/8/19 that the lockers had already been moved in Rm 120 and the Excellence Model Posters are now visible in the classroom. No further action is needed.
399902 | CR | 20191007 |  | 3 | DG1 Clearance Hang delayed as Fuse Inactive in eSoms | N | N |  | N | NO | <D> **** Detailed Description **** E-FUSE-SMDG17/F1/1/2 & E-FUSE-SMDG17/F2/1/2 are the EPNs that have been changed manually by an Operator to Active and looking at the Status section under Change Log it shows that the EPN automatically changes from Active back to Inactive. #IR0045090 (IS fixit ticket) was initiated to alert I.S. of the issue with these EPNs. The fix was not effective. A more permanent solution needs to be found to keep eSoms EPNs active. <I> **** Actions Taken **** Wrote this CR.
399903 | CR | 20191007 |  | 4 | Fail to finish schedule tasks - 02139652 | N | N |  | N | NO | <C> MRT Change: CR 399903 moved from CAQ D/T to Severity 4/Trend. <D> **** Detailed Description **** WO# 02139652 was planned to replace specific capacitors at local fire panels FSP7, FSP8, FSP9 and FSP10. The work at two of the four panels (FSP7 & FSP8) was completed, as scheduled, last week. However, the work at FSP9 & FSP10 was not completed and needs to be rescheduled. FSP9 - determined that the required isolation valve was broken and needed to be repaired, prior to operating (WO# 02137884) FSP10 - Due to issues starting and completing FSP7 & FSP8, inadequate time to complete. <I> **** Actions Taken **** Discussed with OPS and WWM - wrote CR to reschedule
399904 | CR | 20191007 |  | 4 | CW-CT-2C fans getting low on oil | N | N |  | N | YES | <D> **** Detailed Description **** CW-CT-2C fans getting low on oil None of the fans are at LOW mark yet, but a few are getting close. Recommend topping off oil in all fans on CT-2C <I> **** Actions Taken **** Informed MCR | 02-00-CW-CT-2C
399910 | CR | 20191007 |  | 3 | (Planning) No FMR hold on WO 02138257-01, 02139109-01 | N | N |  | N | NO | <D> **** Detailed Description **** WO 02138257-01, 02139109-01 require a Fire Marshal review, but a FMR hold was not applied during the planning process. Need planning to put a FMR hold on the nodel for these WO's and apply a FMR hold all the tasked WO's <I> **** Actions Taken **** Hade hard copies of the WO's and are routing them to the Fire Marshal and to records. <N> Requirements for planning holds on work instructions were covered during Planning D15. No further actions required.
399912 | CR | 20191007 |  | 4 | (eWP) Data Glance did prohibit closing WO's out of sequence | N | N |  | N | NO | <D> **** Detailed Description **** WO 02139109-01 was clsoed out of sequence and caused WO 02138257-01 to be canceled. <I> **** Actions Taken **** Hade a hard copy of WO 02138257-01 and routing it to records.
399913 | CR | 20191007 |  | 3 | Added FMR hold, but WO still went to records without going t |  |  |  | N | NO | <C> CR found at INPROG. Reviewed and moved to Approved status. <D> Tried to add FMR hold under Review - Holds, but option was not available. Put a FMR hold under closure route, but WO went to records without the Fire Marshal review. WO 02139109-01. <I> Made a hard copy and routed it. <N> AR00391089 is tracking the changes for the FMR hold code. The change will be in production prior to the end of October. AR00391089 has been cross referenced, this CR can be completed.
399914 | CR | 20191007 |  | 4 | CW-FN-3 and CW-FN-5 at Add Oil Level | N | N |  | N | YES | <D> **** Detailed Description **** CW-FN-3 and CW-FN-5 are at the Add Oil level. <I> **** Actions Taken **** N/A | 02-00-CW-FN-3,02-00-CW-FN-5
399916 | CR | 20191007 | CAQ | C | MT&E Found out of tolerance | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0063867 Agilent Function Generator- model 33250A found OOT & adjusted within specs. DEF #7339A generated. EFIN to Evaluate ALL usages.
399917 | CR | 20191007 |  | 4 | M&TE Suspended until R25 | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0062515 Biach Calibration Block was Not Used During Calibration cycle and is Now Suspended until R25. DEF #7340A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Treniding purposes only.
399918 | CR | 20191007 |  | 3 | Unable to complete CSP-INST-D201 per OPS instruction | N | Y |  | N | YES | <C> MRT Change: CR 399918 moved from CAQ C to Non-CAQ Severity 3. <D> **** Detailed Description **** During the performance of CSP-INST-D201 the offgas post-treatment source check on OG-RIS-601A was not performed per SM/CRS instruction. This source check is required by surveillance requirement 6.1.2.2. The meter was then declared INOP and RFO sampling is now required. <I> **** Actions Taken **** Supervision informed and the remainder of CSP-INST-D201 completed. <N> CSP-INST-D201 was not completed for OG-RIS-601A by SM direction. The reason for not allowing the performance of CSP-INST-D201 was the failure of OG-RIS-601B in manner that caused a trip. CSP-INST-D201 may have caused a trip of OG -RIS-601A. Having both OG-RIS-601A and B tripped would have closed OG-V-60 resulting in rising MT backpressure. OG -RIS-601B was repaired under WR 29151946 and WO 02151731. CSP-INST-D201 has been completed; OG-RIS-601A and B can be declared functional at the operating crewâ€™s discretion. No further action is required.
399919 | CR | 20191007 |  | 3 | ECP-DG1/INSP-B101 procedure issue | N | N |  | N | NO | <D> **** Detailed Description **** Section 7.1.8 of the procedure cannot be performed unless step 7.1.9 has been completed. This is a continuous use procedure and cannot be worked out of sequence. <I> **** Actions Taken **** Informed supervision of discrepency and procedure needs to be changed <N> **** Equipment Description **** Diesel generator dg1 electrical inspection Procedure updates completed as required. No further actions required.
399920 | CR | 20191007 |  | 4 | Incorrect org listed on PR Form | N | N |  | N | NO | <D> **** Detailed Description **** It was identified there was an incorrect org listed on the Personal Requirements Form, which caused SSIS to send notifications to the incorrect BOP Supervisor for seven individuals processing today. <I> **** Actions Taken **** Individuals moved to the correct org in Asset Suite. The PR form will need to be evaluated to have a drop down menu for Managers/Supervisors. This will ensure the correct oganization is correct instead of typing the organization on the form.
399921 | CR | 20191007 |  | 3 | Software Repository download script not validating | N | N |  | N | NO | <D> **** Detailed Description **** Software Repository download script not validating as expected. Script contains an error that would always return a success on the file hash functionality. <I> **** Actions Taken **** Corrected the script and validated it fails if the original file does not match the stored hash. Notified Supervisor. Notified Cyber of this issue. Recommend NON-CAQ 3. Recommend reviewing this process for improvements.
399922 | CR | 20191007 |  | 4 | camera cleaning | N | N |  | N | YES | <D> **** Detailed Description **** cameras needing to be cleaned inside PA. CCTV07/ CCTV10/ CCTV13/ CCTV34/ PTZ29 <I> **** Actions Taken **** CAS generated list, notified supervision, CR/WR generated <N> **** Equipment Description **** Cameras located inside PA.
399925 | CR | 20191007 | CAQ | C | DLO-ST-4A2 unable to be removed due to position. | Y | N |  | N | NO | <D> **** Detailed Description **** During performance of 02119140-02 it was identified that the strainer was unable to be disassembled due to the configuration being too close to the concrete pedestal on the Diesel see picture in EDMS. Working with planning to have instructions added to loosen/remove unions and threaded fittings to reposition the strainer for maintenance. <I> **** Actions Taken **** Documented in CR for tracking. <N> Work instructions and model wo were updated as required to address condition. No further actions required.
399926 | CR | 20191007 | CAQ | C | Incomplete procedure revision | N | N |  | N | NO | <D> **** Detailed Description **** AR 384274 created new procedures, OSP-SW-C101, OSP-SW-C102 and OSP-SW-C103. This activity was completed 9/6/2018. 1. The new procedures do not have an associated conditional PMRQ for tracking surveillance performance per PPM 1.5.1, which requires an SMS-AR. 2. OSP-SW-M101, OSP-SW-M102 and OSP-SW-M103 do not provide guidance or reference to perform the subject procedures when conditions require flushing the applicable heat exchangers. <I> **** Actions Taken **** initiated CR and SMS-AR (see cross-reference).
399927 | CR | 20191007 | CAQ | C | Duplicate Class-IDs Submitted to Records Control | N | N |  | N | NO | <D> **** Detailed Description **** This is a process issue, PQD's Class-ID field is currently 6-digits, placing an upper limit on the number of generated class IDs available. ITSR 0037495 addressed this issue by allowing previous Class-IDs that were created, but not used or populated for various reasons, to be used for newly created classes thus extending the life of the 6-digit Class-ID another 4-5 years. It has now been identified that some of these Class IDs that were created but unused were canceled and yet submitted to records as far back as 2006 and are now being used and creating a duplicate Class ID when submitted to Records Control. <I> **** Actions Taken **** Discussed issue with RIM and notified Training Management.
399932 | CR | 20191007 |  | 3 | Fall Protection Plan not completed PER ISPM 9 | N | N |  | N | NO | <D> **** Detailed Description **** While performing the task in WO 02142392-02 craft was working above 4' and although the crew had the proper physical controls in place the paperwork describing the fall protection plan and mitigation of the fall hazard was not in the work package and not compliant with ISPM-9. <I> **** Actions Taken **** Initiated CR, Coaching was provided and completed form 25768 was added to the work package. Recommend adding â€œis a fall protection plan requiredâ€ to form 26263 (Mobile,Fixed Crane and hoist prejob brief/lift plan) <N> Williams Plant Services. This is a site wide issue for Maintenance and Facilities.
399933 | CR | 20191007 |  | 4 | (QA) Step ladder not seismically secured in B-600 building | N | N |  | Y | NO | <D> **** Detailed Description **** While performing QA surveillance SR-19-13, it was discovered that there is an unsecured stepladder placed against the wall in FLEX building B-600. Factual Basis: â€¢ Building B-600 is a Seismic 1 area. â€¢ All equipment in a Seismic 1 area is required to be secured or evaluated to Seismic 1 loading requirements. Insights: â€¢ Miscellaneous equipment in FLEX building Seismic 1 areas need to be secured or evaluated to protect equipment required for FLEX mitigation in a seismic event. See picture in the EDMS. <I> **** Actions Taken **** Discussed with FLEX program owner, Mechanical/CIvil Design Authority and QA Supervisor. <N> PPROG supervisor and FLEX program owner report that the ladder is now secured properly
399934 | CR | 20191007 | CAQ | C | Condesate Storage Tank cleaning |  |  |  | N | NO | <D> **** Detailed Description **** CR 174074 (initiated in 2010) documents a gap from a review of actions taken to address INPO 07-008, â€œGuidelines for Achieving Excellence in Foreign Material Exclusion, Revision 1.â€ CR 174074 identified that the response to the INPO 07-008 document relied on a planned single cleaning of the Condensate Storage Tanks (CSTs) that was scheduled in 2008, however, the actual implementation of that cleaning was reported as not being robust enough to remove the type of material that would lend itself to preventing further fuel debris type failures. Assignment 174074-04 identified that the CST was one potential source of debris, however, no further corrective actions were established to address cleaning/inspecting of this potential unfiltered water source to the reactor pressure vessel such as a PM to clean the CSTs. During OE review for the apparent cause for fuel failures via AR 336352 (initiated in 2015) the failure to address the above recommendation in the corrective action process was again identified and documented via CR 338723 that recommended a PM be generated to inspect and/or clean the CSTs . CR 338723 was addressed by the system engineer who recommended that the CSTs be cleaned and inspected via creation of AR SMS-339294, which in turn created PMID 26415-01 with a 10 year frequency to clean and inspect the CSTs. The response also identified that WO 02023959 had been generated to clean the CSTs. For remainder of writeup, see word document in EDMS. Recommend assignming to appropriate level of management to ensure this activity (cleaning CSTs) gets added to a PM program and doesn't get removed from scope again. <I> **** Actions Taken **** Discussed with Project Management currently tasked to Work WOs 02140807 and 02140808 and identified additional funding to support inclusion of cleaning with inspection efforts. Recommend screening as a CAQ "C" to AR-VPOPS for resolution.
399936 | CR | 20191007 |  | 3 | (DG1LL)WOs requiring support did not have support identified | N | N |  | N | YES | <D> **** Detailed Description **** Work Orders 02120250 and 02120251 required engineering support to perform the 10.2.99 inspections. However, neither of the work orders had either a support task for engineering, or engineering resource hours tied to the work order task. This led to the responsible engineering being unaware of the required support, and the need for emergent engineering support of a planned work order task. Recommend this is captured in the T+1 report. <I> **** Actions Taken **** Discussed with OCC Engineering representative and coordinated support with the maintenance craft supervisor. | 02-00-DO-V-20A1,02-00-DO-V-20A2
399937 | CR | 20191007 |  | 3 | Late recognition of plant effect of WO 02107761 | N | N |  | N | NO | <D> **** Detailed Description **** Operation planning of WO 02107761 for E-CB-DG1/7, Detailed inspection of MOC Switch did not account for the conflict between doing this work order and Attachment 9.3 of Extended DG Outage requirements. (No work that effects the TRB may be performed while in a 14 day extended outage) <I> **** Actions Taken **** Problem identified and team expanded. After taking input from all parties the work was removed from the Outage Window to be performed as a stand alone PM.
399939 | CR | 20191007 |  | 4 | WOA-TCV-59 does not appear to be operating properly | N | N |  | N | YES | <D> **** Detailed Description **** Chemisty technicians informed operations of elevated temperatures in the counting room. The counting room temperature was 90F and the thermostat in the room was set at 70F. The inlet temperature (WCH-TI-59/1) for WOA-CC -9 was 62F and the outlet temperature (WCH-TI-59/6) was 64F. The temperature control valve (WOA-TCV-59) appeared to be closed. Radwaste HVAC airwash was secured the preceeding night. <I> **** Actions Taken **** Informed CRS and wrote CR | 02-00-WOA-TCV-59
399940 | CR | 20191007 |  | 4 | T501' W Cardox Hose Reel Lamp Not Illuminated | N | N |  | N | YES | <D> The normally-on red lamp by the Cardox hose reel is out. ** Disregard* already written up AR 349885 ****Correction: AR already written is AR 399885**** <I> Notified CRS <N> TB 501 W CR at INPROG. Approved CR, moved to SRO for OPS Review.
399943 | CR | 20191007 |  | 3 | OG-RIT-601B Configuration Database Discrepancies |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During the replacement of OG-RIT-601B RM-2300 replacement it was discovered that three Configuration Database items did not match the IDMS. Sample flow item 34, 35 and Channel Item 26. <I> **** Actions Taken **** Contacted System Engineer and changed the sample flow items to match the IMDS. When Channel item 26 is set to 000 per the IMDS it locks in the HI-HI alarm. Per System Engineer we left it at its as found value of 001. OG-RIT-601B still needs a PMT performed.
399944 | CR | 20191007 |  | 4 | BRE-36 Camera degraded | N | N |  | N | NO | <D> **** Detailed Description **** The camera failed to start back up after a power cycle during battery maintenance. The camera was replaced and will currently not move using system controls. are currently troubleshooting the issue. <I> **** Actions Taken **** Further troubleshooting with the system analyst and factory support will continue first thing in the morning. Notified Security Recommend closign to WR <N> **** Equipment Description **** BRE-36
399945 | CR | 20191007 |  | 3 | Operations is impacting operator fatigue |  |  |  | N | NO | <D> **** Detailed Description **** On September 12 at appoximately 0930, several operators received multiple calls from the operation's scheduler for overtime for September 18-20 2019. The operators were currently working night shifts and woken up for overtime that wasnâ€™t emergent On September 23 I receive verbal confirmation that the AOM of the crews had talk to the operation scheduler, and that this current practice would be stopped. On October 7, 2019 at multiple time several Operators were called for overtime once again and woken up for non emergent overtime while on nightshift. We are required to comply with 10 CFR 26 subpart 1per IBEW local 77 contract. This states that we are required to maintain our fatigue. How can we comply with managing our fatigue when operations department is impacting our fatigue?
399946 | CR | 20191007 |  | 4 | Steam Tunnel Camera shows no picture/video. |  |  |  | N | YES | <D> **** Detailed Description **** Opened the Steam Tunnel Camera and only colored pixels were displayed. Video/picture not available. OPS-3 camera tour on 10/8/19N. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG-501
399947 | CR | 20191007 |  | 3 | Cannot obtain correct data as written in ECP-DG1/INSP-B101 |  |  |  | N | NO | <D> **** Detailed Description **** While performing WO 02119144 for ECP-DG1/INSP-B101 it was discovered that step 7.1.16.e (Field Flash Ground resistance measurement) will not provide the necessary data to meet the acceptance criteria of 2.0 Megohms. This CR is being written to document the condition so that this procedure can be updated in the future to evaluate if the points need determed to obtain the correct reading. While performing this step as written the electricians were getting a dead short (open reading). This step was added as part of AR 354145 and this CR is being written to evaluate another way to get his reading in the future. This CR has no impact on operation of the DG and it was added as an enhancement to the procedure. Discussed issue with electrical DG system engineer and he recommended N/Aing this step and writing the CR so this procedure can be fixed in the future. Note: this enhancement will also impact ECP-DG2/INSP0B101.
399948 | CR | 20191007 | CAQ | D | Leak identified on DCW-FLX-12A2 (6" flex) | Y | N |  | N | YES | <C> CR reopened to add completion required check mark to referenced WO 02151742 per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** During the performance of PPM 10.20.1 section 7.3, craft identified that the upper seal on DCW-FLX-14A2 8" flex connection DCW-HX-1A2 TO DLO-HX-2A2 has a minor leak. See EDMS for pictures. <I> **** Actions Taken **** Notified MCR and OCC. Initiated CR and WR. <N> INPO 18-003 Maintenance fundamentals and technical skills is to know your gasket materials and specification of use. These old elastomers are brittle and have lost some of the elasticity, this could cause cracking if we were to retighten the bolts to try and seal the leak. With our AFI on leak path sealing mechanical maintenance recommends that the elastomers be replaced during this window. | 02-00-DCW-FLX-14A2
399949 | CR | 20191007 | CAQ | D | Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for HCU 2259 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-22-59. After investigation, Rod Accumulator Trouble Alarm P603-A7 drop 6-7 was for CRD-HCU-22-59 high water level. <I> **** Actions Taken **** Dispatched OPS-2 to investigate. Removed excess water from HCU | 02-00-CRD-HCU-2259
399950 | CR | 20191008 |  | 4 | SEC-XD-3 Failed Test | N | N |  | N | YES | <D> **** Detailed Description **** SEC-XD-3 Failed Operability Testing. <I> **** Actions Taken **** SEC-XD-3 was placed out of service. Notified maintenance, generated CR/WR. <N> **** Equipment Description **** PAAP | 02-00-SEC-XD-3
399951 | CR | 20191008 |  | 4 | TG-E/S-1 -V Green LED is no longer illuminated. | N | N |  | N | YES | <D> **** Detailed Description **** TG-E/S-1 -V Green LED is no longer illuminated. During the shift the indicator shifted in color from green to yellow to orange to burntout. Dont suspect that the power supply is bad (at least not right now) because the indications for turbine vibrations are still indicating. Please invetigate if this is an issue or if it can be repaired. TG-E/S-1 powers the Bently nevada vibration monitor to the main turbine. It is currently being used to monitor elevated turbine vibrations. <I> **** Actions Taken **** Wrote this AR to document issue and drive resoloution. | 02-00-TG-E/S-1
399952 | CR | 20191008 | CAQ | C | Metal flakes and loose stand-pipe found in DLO-F-1A1 | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of PPM 10.20.1 section 7.4 change lube oil filters. Metal flakes were found in all 7 filter elements and one of the filter stand-pipes for DLO-F-1A1 was found to be loose. See EDMS for pictures. <I> **** Actions Taken **** Notified MCR, OCC, and initiated CR and WR | 02-00-DLO-F-1A1
399956 | CR | 20191008 |  | 4 | HP department over SEPT dose budget | N | N |  | N | NO | <D> **** Detailed Description **** HP received 386 mrem against a goal of 289 mrem in the month of September. This was the result of 159mrem from emergent work throughout the month. <I> **** Actions Taken **** CR written
399958 | CR | 20191008 |  | 4 | MT&E Found out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0068449 ARM Power Supply found OOT & adjusted within specs. Not used during Calibration cycle. DEF #7341A written. No Plant Impact. No Action Required.
399959 | CR | 20191008 |  | 4 | Inaccurate cancellation info for AR CR 364760 WO 02111257 | N | N |  | N | NO | <D> **** Detailed Description **** On 10/7/19, WO 02111257 (Tube clamps downstream of COND-V-1100A missing) was taken to CANCEL status in Portal J. This WO was associated with COMP-NA AR CR 364760. The cancellation justification provided/approved was "tube clamp fixed on 02111257". Per clarification subsequently provided by Mechanical Maintenance, the AR CR 364760 issue was actually corrected as part of WO 02111259 (Missing tubing clamp for tubing downstream of RFW-V-701A) associated with COMP-NA AR CR 364776. The Unit Coordinator indicated that the cancellation justification notes for WO 02111257 were locked and could not be corrected. This AR CR 399959 is initiated to provide the administrative bridge. E-mail chain is attached to the EDMS of this AR CR 399959.
399961 | CR | 20191008 |  | 4 | MT&E found out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0065604 Heise Pressure Calibrator- model PTE-1 found OOT & adjusted within specs. Not used in the OOT Range of 10V. DEF #7342A written. No Plant Impact. No Action Required.
399963 | CR | 20191008 | CAQ | D | MS-RIS-610C Monitor screen has failed | N | Y |  | N | YES | <D> **** Detailed Description **** MS-RIS-610C Monitor screen has failed. When attempting to turn on the monitor screen for logs, buttons were pressed, sound was heard, however, the screen stayed completely dark. No trip or INOP conditions are currently in. <I> **** Actions Taken **** Notified CRS Initiated WR and CR <N> **** Equipment Description **** MCR | 02-00-MS-RIS-610C
399969 | CR | 20191008 |  | 3 | Team A craft lead missed muster meeting. | N | N |  | N | NO | <D> **** Detailed Description **** Team A craft lead missed the scheduled muster meeting. The meeting was on the induviduals calemdar, and was reviewed earlier this morning. The individual is available to cover the responsibities of ERO. <I> **** Actions Taken **** Generated CR to document missed meeting.
399970 | CR | 20191008 | CAQ | D | SGT-A high inlet moisture indication in MCR | Y | Y |  | N | YES | <D> **** Detailed Description **** Control room indication for SGT A inlet moisture is reading high. SGT-MI-7A indicates 89% moisture and SGT-MI-6A indicates 84% moisture. OPS2 was dispatched to inspect SGT sys A and investigate local moisture indication. Local indication of inlet moisture for SGT sys A indicated 44% moisture. Strip heaters were reported to be working and no indication of leakage locally was reported. SGT-MI-4A indicates 33% and SGT-TI-6A and 7A indicate 95F and 99F respectively. No SGT A alarms are in at this time. <I> **** Actions Taken **** Notified CRS. Dispatched Operator for local inspection Initiated CR <N> **** Equipment Description **** MCR | 02-00-SGT-MI-6A,02-00-SGT-MI-7A
399971 | CR | 20191008 | CAQ | C | DSA-V-16A- Excessive flange misalignment | Y | N |  | N | YES | <C> CR completed by OPS prior to entering Priority. CR Priority updated and taken back to complete. <D> **** Detailed Description **** During performance of PM internal inspection excessive misalignment of flanges was noted. This is a 1â€ nozzle style check valve that is retained between 2 flanges with resilient seals. Recommend removal of pipe strain. <I> **** Actions Taken **** Contacted OCC Engineering. The cold spring identified per CR 399971 is acceptable per PPM 10.2.28 for maintenance of Piping Systems. <N> **** Equipment Description **** D -441-D115- -P4/7.2 - SInce the piping cold spring is acceptable there is no DNC or OBDN. | 02-00-DSA-V-16A
399972 | CR | 20191008 |  | 4 | TG-ID-1 out of paper | N | N |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was observed that TG -ID-1 was out of paper and needs a new paper roll. <I> **** Actions Taken **** Notified CRS and wrote CR | 02-00-TG-ID-1
399974 | CR | 20191008 | CAQ | C | EWD-84E-045C needs to be corrected | N | N |  | N | NO | <D> **** Detailed Description **** EWD-84E-045C references EWD-84E-075 when it should reference EWD-84E-085 for the print that shows the power to SW-PCV-15B. The title also says it is for SW-TCV-15B when it is for SW-PCV-15B.
399975 | CR | 20191008 |  | 4 | Light above SS-PI-39 and SS-FI-1 is too dim | N | N |  | N | YES | <D> **** Detailed Description **** The light above SS-PI-39 and SS-FI-1 is too dim to allow an operator to get an accurate reading for logs while performing the dayshift camera tour for OPS 3 rounds. Camera location is turbine building 471TG, TG/22 <I> **** Actions Taken **** Informed CRS and wrote CR | 02-00-SS-FI-1,02-00-SS-PI-39
399977 | CR | 20191008 |  | 3 | SPIP-SEC-49 needs revised and updated | N | N |  | N | NO | <D> **** Detailed Description **** Security procedure SPIP-SEC-49 needs minor revision and updated. Security supervision notified. <I> **** Actions Taken **** CR initiated. Security supervision notified. Contact 2185 for details.
399978 | CR | 20191008 |  | 3 | Fine Metallic Particles Around TSW-P1A Shaft | N | N |  | N | YES | <D> **** Detailed Description **** Fine metallic particles observed around TSW-P-1A shaft. Possible degradation of components. Please investigate. See attached video <I> **** Actions Taken **** Notified CRS who sent FIN out to look at pump. | 02-00-TSW-P-1A
399984 | CR | 20191008 |  | 3 | (EWP) DR holds still getting attached to Maint WO's | N | N |  | N | NO | <D> **** Detailed Description **** Remove the auto population of DR hollds on Maint WO's. Originally there was a criteria to put DR holds on specific maint WO's. Later it was determined that maint did not want DR holds and planning would put WD holds on the WO's that needed them. eWP was going to stop DR holds from auto populating on maint WO's and cleam up those tasks that had them on. DR holds continue to populate. Weeks 11/11 and 1118 have 14 DR holds on the walkdown report. (3 have a DR and WD hold on them) <I> **** Actions Taken **** Will remove the DR holds for those two weeks. <N> AR00388604 - is tracking the DR hold code changes and has been added to the cross reference panel. . Changes for the DR hold are in production. . This CR is ready to COMPLETE.
399986 | CR | 20191008 |  | 3 | (planning) 021433686 not comming out in Ready status (WD Hol | N | N |  | N | NO | <D> **** Detailed Description **** WO 02143386 ESP-RHR-Q901 is checked to come out in Ready status, but a WD hold was applied. Change model to remove WD hold.
399987 | CR | 20191008 |  | 3 | Vendor calibration - old verbiage in the PO on current PO | N | N |  | Y | NO | <D> **** Detailed Description **** When Cal Lab Specialist reviewed the PO it does state that other Fluke locations require written approval by EN prior to use. Cal Lab Specialist approved the Fluke Vendor in the UK. Which is how we arrived at this issue. However, in the 494 and 496 clauses it also states we canâ€™t subcontract calibration services. Please assign to CALSERV
399988 | CR | 20191008 |  | 4 | MT&E found out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0060448 Simpson Clamp-On Ammeter- model HE94 Received by Standards Lab with bent pin on internal display board, applied tamper seals and Certified to Limited Specifications. No adjustments to calibration were made. DEF #7343A written. No Plant Impact. No Action Required.
399990 | CR | 20191008 | CAQ | C | Organizational Communication Weakness between CRRG and WRSC | N | N |  | N | NO | <D> **** Detailed Description **** Having taken part of both CRRG (Condition Report Review Group) process and WRSC (Work Request Screening Committee) screening process, plus benchmarking have revealed there is a screening gap where a CR can be closed to a WR and a WR can be closed to the CR. There is not a clear visible process where we would not put ourselves in a position where a condition would be identified and each separate screening committee would somehow check or flags that would indicate to use each otherâ€™s process to bring resolution to the issue. Leaving the issue identified but with no administrative drivers for resolution. We depend on HU interface to check and resolve issues, which at times have failed us. Other sites ensure the Unit Coordinator check with the CAP Organizer which ARs/CRs were trended to WRs, to ensure alignment with the Work Request Screening Committee. There are no flagging options on CRs in Asset Suite to identify them if they have been decided to be trended to the WR/WO process by CRRG. Also, the WRSC meeting room could use a computer and a screen to review the daily list and perform quick checks on additional information needed. Also, the meeting could be further enhanced by performing it via Skype. The meeting room has no phones for communication which does not help if WRSC needs to contact CAP or vice-versa. Issue is programmatic in nature. <I> **** Actions Taken **** Notified Unit Coordinator and Enginering CAP <N> The times the meetings are held also conflict and does not help in communication. WRSC is held 10:30AM to 11AM and CRRG is held from 10:30AM to 11:30AM. However, one meeting should communicate to the other is there are trending items. If WRSC determines cancellation of a WR to a CR, this needs to be communicated to CAP and Vice-versa. There is no time in be-tween where the UC can communicate with the CAP Organizer.
399992 | CR | 20191008 |  | 4 | HP AAP RCA Entry Turnstile is not functioning | N | N |  | N | NO | <D> **** Detailed Description **** HP AAP RCA entry Trunstile stopped working. Appears to be a board failure and possible CPU. This is one of only two turnstile units at the HP AAP. Failure of the second unit could delay West end RCA entries at that location for authorized Operations, Chemistry, and RP personnel. <I> **** Actions Taken **** RP Supervision notified. Initiated WR 29151995. <N> **** Equipment Description **** HP-EQ-42854
399994 | CR | 20191008 |  | 3 | Procedure updates for OI-15. | N | N |  | N | NO | <D> **** Detailed Description **** EAL and EOP updates to OI-15 in the EDMS folder. These changes are needed prior to 11-4-19.
399998 | CR | 20191008 |  | 4 | Listed CAT ID for rubber washer incorrect ID | N | N |  | N | NO | <D> **** Detailed Description **** The CAT ID (8192) for DCW-LG-10A2 rubber washer originally purchased was the incorrect ID to fit around the glass tube. Engaged planning and it was discovered that there was a different part number and associated CAT ID (25318356) that was the correct fit for the sight glass. <I> **** Actions Taken **** CR generated for documentation/determination of a pen and ink change to the work packages WOâ€™s 02142147-01 and 02142144-01 <N> Note added to work order referencing this ar and the cat id number.
399999 | CR | 20191008 |  | 3 | SCBA Bottles Transported in Private Vehicles at HAMMER | N | N |  | N | NO | <C> MRT Change: CR 399999 moved from AR-RADPR to AR-OPTRN. <D> **** ANONYMOUS CR - Detailed Description **** Annual live fire training at HAMMER normally begins by the individual Fire Brigade members stopping at the building and picking up an SCBA harness and SCBA mask (if you don't bring your own mask). The HAMMER worker brings full SCBA bottles out to the burn building for us to use. This time, we were told to grab a charged SCBA bottle and transport it to the job site. These bottles are charged to 4000# and are not secured in our private vehicles. This was not normal and I am not sure who directed it. I just followed the lead of the Fire Brigade co-worker that told me that we were supposed to also grab a bottle with our harness. Fresh bottles were delivered by HAMMER workers as normal during the day. <I> **** Actions Taken **** Initiated this AR/CR. The following communication was sent at 1052: "For the remaining 3 weeks of HAMMER, DO NOT take SCBA bottles with you to the Burn Building when getting your SCBA pack, until further notice. For the time being, each FB member is to place 2 SCBA bottles in the cart attached to the Gator outside the building, until the cart is full." <N> CR initiated anonymously, reviewed for Safety Conscious Work Environment (SCWE) content. Moved to CR-SRO for OPS review.
400000 | CR | 20191008 | CAQ | D | DG-RLY-DG1/K6 As found time out of tolerance | Y | N |  | N | YES | <D> **** Detailed Description **** During calibration of DG-RLY-DG1/K6 per PPM 10.25.207 and WO#02119148-01 the As found time was 15.91 seconds with a tolerance of 14.25-15.75 seconds. Relay operated Sat with all contacts changing state. <I> **** Actions Taken **** Notified supervisor and PSRO. Adjusted timing knob per PPM 10.25.207. Relay tested Sat with As left time in tolerance at 15.06 seconds | 02-00-DG-RLY-DG1/K60
400001 | CR | 20191008 | CAQ | D | DG-RLY-DG1/K60 As found time out of tolerance | Y | N |  | N | YES | <D> **** Detailed Description **** During calibration of DG-RLY-DG1/K60 per PPM 10.25.207 and WO#02119148-01 the As found time was 5.27.seconds with a tolerance of 4.75-5.25 seconds. Relay tested sat with all contacts changing state. <I> **** Actions Taken **** Notified supervisor and PSRO. Testing completed Sat per PPM 10.25.207 with As left time in tolerance at 5.15 seconds. | 02-00-DG-RLY-DG1/K60
400002 | CR | 20191008 |  | 3 | ABN-CR-EVAC issue | N | N |  | N | NO | <D> **** Detailed Description **** Section 7.18 of ABN-CR-EVAC cannot be performed following CR evacuation. Prior to leaving the MCR, NS4 is actuated and the power to RRC-V-67B is load shed. Step 7.18.4.x has a note stating this, but it is burried in the procedure and it is error likely to start this section, then have to back out. At a minimum a note should be at the beginning of this procedure saying to perform section 7.19 if MC-8C is without power. Also evaluate if this section could ever be performed as written. <I> **** Actions Taken **** CR written. <N> **** Equipment Description **** Procedure change.
400003 | CR | 20191008 |  | 4 | Security access road to PSF needs maintenance support | N | N |  | N | NO | <D> **** Detailed Description **** The old access road to the PSF needs barrels put in place to control access. Please contact security for details concerning number of barrels and placement on access road. <I> **** Actions Taken **** CR/WR initiated. Security supervision notified. Contact security at 2185 for details. <N> **** Equipment Description **** Security SDOCA. Contact security at 2185 for details.
400006 | CR | 20191008 |  | 3 | (Planning) PMID 14210-01 needs to come out in the Ready sta | N | N |  | N | NO | <D> **** Detailed Description **** PMID 147210-01 needs to come out in the Ready status. It does not need a walkdown hold. Ensure the PM Active box is checked.
400007 | CR | 20191008 | CAQ | C | As found time on DMA-RLY-TK11/1 out of tolerance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing as found time test on removed relay DMA-RLY-TK11/1 UTC# 533431, the as found time was out of tolerance at 1473.4 seconds with a range of 1732.2 - 1980 seconds. This relay was replaced with a new calibrated relay under WO#02119150-05. <I> **** Actions Taken **** Wrote CR, informed supervision and operations This equipment is no longer installed in the plant, but was installed and the as-found is out of tolerance. Requested REGE/REP assignment to determine past operability/reportability. <N> **** Equipment Description **** DMA-RLY-TK11/1 UTC#533431 removed under WO#02119150-05
400008 | CR | 20191008 |  | 4 | Indicating lights not normal on MT-BLADE-VIB-MON | N | N |  | N | YES | <D> **** Detailed Description **** Light #3 on MT-BLADE-VIB-MON lit. <I> **** Actions Taken **** Initiated CR, Informed SSS <N> **** Equipment Description **** MT-BLADE-VIB-MON
400011 | CR | 20191009 |  | 4 | M&TE Rejected |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0064733 Astro-Med Data Acquistion Recorder- model DASH 8XE found OOT & Rejected- Not able to adjust/ repair. Parts No Longer Available. DEF #7338A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only. Not Used During Calibration Cycle...
400013 | CR | 20191009 |  | 3 | SOP-COLDWEATHER-OPS change |  |  |  | N | NO | <D> **** Detailed Description **** The table of contents shows '6.2 Entry into Extreme Cold Weather Operations' starts on page 50. It actually starts on page 51.
400017 | CR | 20191009 |  | 3 | FLEX Bldg 82 and Bldg 600 Seismic Category 1 Areas |  |  |  | N | NO | <D> **** Detailed Description **** FLEX Building 82 and Building 600 are SSE qualified and Seismic Category (SC) 1 areas but are not indicated as SC 1 areas in or addressed by PPM 10.2.222, CIVES-6, or PPM 10.2.53. Additionally, the Limiting Aspect Ratio Tables (AED CAL CE-02-90-35) in each of these documents do not address either of these locations. This is an administrative issue. <N> ***General Notes*** An assignment has been made under the maint. procedure revision data base for PPM 0.2.53 and PPM 10.2.222. See the EDMS of this AR for a link to the assignments within the Maint. Procedure Revision Data base.
400018 | CR | 20191009 |  | 4 | TOA-TIS-12B Not Working Properly | N | N |  | N | YES | <D> **** Detailed Description **** TOA-TIS-12B was written up last year for not working properly and giving high temp indications and alarms. Today, the high temp/low basin level came in again. Indicated temperature read 98F and the alarm was set to 160F when the alarm came in. Actual temperature was around 60F. Setting the alarm to max has cleared the alarming condition for now but with indicated temperature and/or the alarm setpoint not accurate, future alarming conditions may occur without the ability to clear the condition. With cold weather on the way, we won't need airwash for cooling, but this should get fixed before we need it for warm weather ops. <I> **** Actions Taken **** cleared the alarm | 02-00-TOA-TIS-12B
400019 | CR | 20191009 |  | 3 | Adobe Acrobat Subscription License Notification |  |  |  | N | NO | <D> **** Detailed Description **** Adobe Acrobat subscription license notification received by users; pop up expiration warning when using software. EN is licensed through March 2020. Vendor support ticket opened and escalated for resolution. <I> **** Actions Taken **** Notified leadership. Recommend NCAQ 3 to ITMGMT.
400020 | CR | 20191009 | CAQ | C | eDNA Web Trending not accessible in ERO Centers | N | Y |  | N | NO | <D> **** Detailed Description **** Explorer locks up while attempting to trend data in the Technical Support Center (TSC) and Emergency Operations Facility (EOF) via eDNA web (via network folder). It is likely but not confirmed the same issue may exist in the Alternate TSC and Alternate EOF. Data is needed for Emergency Operations Support activities. <I> **** Actions Taken **** Informed EP Manager, EOF Lead Controller and TSC Lead Controller. <N> eDNA Trend data still available via eDNA Trend software. This is an enhancement for an operator aid in the TSC and EOF.
400021 | CR | 20191009 |  | 3 | *2019 Mid-Cycle* SWP-CM-02 and SYS-2-1 not aligned |  |  |  | N | NO | <D> **** Detailed Description **** SWP-CM-02 P/L 2.1 requires that System Engineers perform quarterly walkdowns of TMODs and NICMs. SYS-2-1 contains the requirement to walkdown TMODs in ATT 7.4, but makes no mention of NICMs. As a result, the NICMs may not be walked down as required. Reccommend reconciling the two procedures. <I> **** Actions Taken **** None required.
400023 | CR | 20191009 |  | 4 | SP-13B meter reading disagrees GT 10% with grab sample | N | N |  | N | NO | <D> During weekly conductivity in-line instrumentation calibration checks it was discovered that the SP-13B meter disagreed with the grab sample by GT 10%. The meter is still considered acceptable as long as the readings are within 20%. <I> Notified supervision, wrote CR <N> TB 441 chemistry sample room CR at INPROG. Approved CR, moved to SRO for OPS Review.
400026 | CR | 20191009 |  | 4 | (Planning) Revise instruction on WO 02143249 |  |  |  | N | NO | <D> **** Detailed Description **** Need relay ordered for task 02 if we are replacing it and need instructions clearly stating what we are doing (calibrating it or replacing it. Currently the instructions have us doing both (task 01). Also need a walkdown hold.
400027 | CR | 20191009 |  | 4 | MT&E found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0063232 Hytorc Hyd. Torque Wrench- model XLCT-2 found OOT & adjusted within specs. Not used in the OOT Range of 248-332 ft/lb. DEF #7344A written. No Plant Impact. No Action Required.
400029 | CR | 20191009 |  | 3 | PPM 10.28.38 needs updated prior to 12/10/2019 |  |  |  | N | NO | <D> **** Detailed Description **** IN-4 clean and inspect is scheduled for 12/10/2019 per WO 02125848 however six issues found with PPM 10.28.38 that need resolution first. 1. EPNS donâ€™t match: PPM 10.28.38 operates E-MBS-IN4/BIB however SOP-ELEC-IN4-SHUTDOWN uses E-CB-IN4/BIB for CB1, E-CB-IN4/MBP for CB2, E-CB-IN4/MIS for CB3. 2. EPNS donâ€™t match within procedure: E-CB-DPSS1/8 operated per 7.1.4, E-CB-DPSSL81/8 operated per 7.8.1 and 7.2.1 and E-CB-DPSS-1/8 operated per 7.8.1 (different EPNâ€™s?). I believe these EPNâ€™s should all be E-CB-DPSS1/8. 3. PPM 10.28.38 Step 7.1.5 out of sequence with SOP-ELEC -IN4-SHUTDOWN 5.1.4-5.1.6 4. Following completion of section 7.1 E-MBS-IN4/BIB (wrong EPN?) and E-CB-DPSS1/8 are left OPEN. Section 7.2 requests operations shutdown E-IN-4 per SOP-ELEC-IN4-SHUTDOWN however with the above components LEFT OPEN this requires shutting down IN4 out of sequence and leaves the operator to randomly choose a step in the SOP. This leaves battery in service vice being in bypass mode. This could drain battery and may not be safe to transfer to maintenance bypass source. There is a note in the OMM â€œWhen an external maintenance bypass is installed for the UPS, before switching to external bypass, ensure that the UPS unit is switched to AC Bypass mode and the UPS control panel display verifies the unit is Bypass Mode - Switching to the external bypass while the unit is in UPS mode may damage the UPSâ€. 5. PPM 10.28.38 step 7.1.3 does not coincide with SOP -ELEC-IN4-SHUTDOWN. SOP-ELEC-IN4-SHUTDOWN STEP 5.1.3 VERIFYS KEY 205 INSTALLED AND PLACED IN OPERATION PRIOR TO PLACING IN-4 IN BYPASS. 10.28.38 DOES NOT. 6. 10.28.38 SECTION 7.1 STEP 7.1.3 HAS CRAFT PLACE IN-4 IN BYPASS without notifying Operations. Procedure has no steps to communicate with operations until section 7.2.
400030 | CR | 20191009 |  | 3 | Employee Injury |  |  |  | N | NO | <D> **** Detailed Description **** Employee suffered a minor injury to toe while moving a banner situated on a cart. The banner slipped off of the cart and although it was caught before hitting the floor, it struck the employee on large toe causing bruising and swelling. <I> **** Actions Taken **** Employee recognized injury after work while at home. Applied ice and reported injury upon arrival to work the next day. CR written, injury documented and notifications made. <N> **** Equipment Description **** N/A
400031 | CR | 20191009 |  | 4 | Heat trace FP/5 CKT2F 02140003-01 | N | N |  | N | YES | <D> **** Detailed Description **** While performing the WOT 0214000301, replace failed heat trace, we noticed after the area was dug up that there was a second heat trace cable running down the pipe underground. The area needs to be further excavated to replace the second heat trace. The junction box located below grade is rotted out and needs to be replaced and relocated to the top side of the piping (above grade). The second heat trace will not be able to reach this new junction box location and needs to be replaced. <I> **** Actions Taken **** Supervisor and planning have been notified. <N> **** Equipment Description **** Heat Trace FP/5 CKT 2F | 02-00-HT-HTP-FP/5
400036 | CR | 20191009 | CAQ | C | 2019 Mid-Cycle Assessment PPM 1.3.10C Procedure violation |  |  |  | N | NO | <D> **** Detailed Description **** 2019 Mid-Cycle Assessment â€“ Per interviews and document review, a violation of PPM 1.3.10C, Control of Combustibles, was identified in September 2018 and continues to exist. CR 384820 was initiated documenting that PC storage racks on Turbine 441â€™ do not meet the required separation distance to cable trays. An hourly fire watch tour is currently in place for the area, but this is not a credited option listed in PPM 1.3.10C for the existing condition. The Fire Protection System Health Report, extension request documentation in the CR, and interviews with station personnel indicate that the station is waiting for a NEIL inspection scheduled for November 2019 to determine what actions to take based on whether the condition warrants a NEIL violation or not. <I> **** Actions Taken **** Discussed with Mid-cycle Assessment Team and Fire Protection Engineer
400037 | CR | 20191009 | CAQ | D | E-CB-7/DG1 seismic latches cannot be engaged | Y | Y |  | N | YES | <D> **** Detailed Description **** When E-CB-7/DG1 was racked in, the top left seismic restraint could not be engaged as required. A gap of approximately 1.5 inches was observed between front panel and cubicle. Electrical Maintenance was contacted and took photographs to investigate cause. <I> **** Actions Taken **** Contacted CRS and Electrical Maintenance | 02-00-E-CB-7/DG1
400038 | CR | 20191009 |  | 4 | FDR-P-15B failed to turn off | N | N |  | N | YES | <D> **** Detailed Description **** While pumping T-4 Sump it was notice the level flat lined for 20 minutes, an indication of no flow into the tank. Previously noted problem that was closed out CR 398894, WR 29151474. Please investigate as this is the only pump working on T-4 as FDR -P-15 A is Broke (wr 29150170, CR 396124). <I> **** Actions Taken **** cr,wr | 02-00-FDR-P-15B
400041 | CR | 20191009 |  | 3 | ENLAB Thermometers found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode APL-A170379 & APL-A170287 FRIO-TEMP Model 30710 were found OOT and rejected. Please assign to ENLAB <N> The APL-A170287 and APL-A170379 thermometers were found out of tolerance during their annual calibration check. Both thermometers were subsequently removed from service at the Environmental Services Laboratory and removed from the EN Standards Laboratory inventory and replaced with new/calibrated thermometers APL-F198529 and APL-F198527. Reviewed Standard Methods book and determined no additional actions are required for failed temperature check devices. ENES intends to also purchase a back-up set of oven thermometers. This action is complete.
400042 | CR | 20191009 |  | 4 | Badge Photos failed to transfer |  |  |  | N | NO | <D> **** Detailed Description **** Badge photos failed to transfer from security computer to the corporate network. <I> **** Actions Taken **** Photos were manually loaded into Lenel. The Issue has been resolved. No further action needed. CR written for trending purposes.
400043 | CR | 20191009 |  | 3 | Hazardous Waste Performance Indicator turns Red in September |  |  |  | N | NO | <C> MRT Change: CR 400043 moved from Severity 4 to 3/ENV. <D> **** Detailed Description **** The hazardous waste performance indicator turned red in September due to waste generation at the Industrial Development Complex (IDC). The IDC generated approximately 884,000 pounds of hazardous waste from remediation work at the outdoor firing range. This also turned the IDC hazardous waste generator status from Small Quantity Generator (SQG) to Large Quantity Generator (LQG). It is anticipated that the IDC will return to SQG status by November 2019. <I> **** Actions Taken **** Discussed with E&RP Manager and wrote CR. <N> The hazardous waste performance indicator for IDC went red due to remediation of the grounds at the former outdoor firing range. This waste includes a large volume of lead contaminated soil and wooden range timbers. The impact on the indicator and IDCâ€™s waste generator status (Small to Large) was anticipated. Shipments of the waste soil and debris have been on-going and will be completed soon. Once removed IDCâ€™s generator status should return to Small Quantity Generator and the indicator to green.
400044 | CR | 20191009 |  | 3 | Section 6.10 of SOP-WARMWEATHER-OPS needs performed/signed |  |  |  | N | YES | <D> **** Detailed Description **** Upon review of WO 02109631-01 (which is still at Working status) which back in May has Operations/Maintenance initially do the recovery from SOP -COLDWEATHER-OPS and the start of SOP-WARMWEATHER-OPS, there is a section at the end (section 6.10) that needs performed to drain the temp cooling lines to the Normal Transformers and the ASD link reactor cooling sprays. After these steps are performed it directs contacting maintenance to remove the temp cooling lines. WO 02119191 -07 is what drives the removal removal of these temp sprays in support of the 01 task which references SOP-COLDWEATHER-OPS. SOP -COLDWEATHER-OPS does not discuss these sections. These sections and the removal is actually directed and referenced in section 6.10 of SOP-WARMWEATHER-OPS. <I> **** Actions Taken **** Discussed with Operations on dayshift, Shop Manager, discussed with CRS as well for insiight that section 6.10 still needs performed/signed off and generated CR. <N> **** Equipment Description **** Transformer cooling spray and ASD link reactor cooling spra
400045 | CR | 20191009 |  | 4 | Power On light not illuminated for 44F on HTP-FP-8 | N | N |  | N | YES | <D> **** Detailed Description **** The power on light for 44F is not illuminated. Switching bulbs did not rectify the problem. <I> **** Actions Taken **** Wrote CR. Informed STA. | 02-00-HT-HTP-FP/8
400046 | CR | 20191009 | CAQ | C | (QA) Finding - Resin Dewatering PMs not performed |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Preventative maintenance (PM) was not performed on the Self Engaging Rapid Dewatering System (SERDS) as specified in plant procedures. SWP-RMP-02, Radioactive Waste Process Control Program, requires PMs on components required to dewater waste resin, however, there are no work orders, action requests or contracts to schedule the maintenance activities and ensure that they are performed as specified. Failure to perform PMs could lead to equipment malfunction that challenges industrial and radiological safety and the ability to process waste resins. Requirements: â€¢ SWP-RMP-02, Radioactive Waste Process Control Program, revision 7, step 2.2.1(b) states: â€œComponents to receive PMs will, at a minimum, be those components required to ensure processed resin meets 10 CFR 61 and disposal site requirements for free standing waterâ€. The SERDS is required to ensure processed resins meet those requirements. These PM requirements are implemented in PPM 11.2.23.44, Operation of the Self Engaging Rapid Dewatering System (SERDS): o Step 4.2 Note states: â€œMaintenance tasks, as listed and documented in Attachment 8.12 (other than prior to use items listed in Section 4.2) should be up to date prior to SERDS operation.â€ o PPM 11.2.23.44, Attachment 8.12, SERDS Maintenance Schedule, specifies 11 preventative maintenance activities and frequencies, including quarterly, semi-annually and annually. â€¢ Contrary to these requirements, no process was established to schedule and perform the specified preventative maintenance activities. Insights: â€¢ The SERDS Operator signature line on Attachment 8.12 states â€œMaintenance Items are up to Dateâ€. A review of completed shipments and interviews with a RMC Laborer and RWTS revealed a lack of understanding that this signature, and the RWTS review signature, require verification that the specified preventative maintenance activities are up to date. o An interview with a qualified SERDS Operator revealed that verification of up-to-date maintenance is based upon pre-use inspections of accessible components. The inspections performed did not include all of the maintenance specified in Attachment 8.12 but were similar to the inspections previously performed on the Self Engaging Dewatering System (SEDS) that was in-use prior to purchasing the SERDS. The SEDS procedure required pre-use maintenance only and did not include specified activities and schedule frequencies. o Interviews with RWTS specialists revealed that Attachment 8.12 review is limited to ensuring that the SERDS Operator signed the attachment to verify up-to-date maintenance. . See EDMS for full text of this Finding, including Factual Basis. <I> **** Actions Taken **** Discussed this Finding with the Chemistry/Radiological Services Manager. Quality recommends CAQ assignment to Radiation Protection. <N> **** Equipment Description **** The SERDS is a mobile, skid mounted system located on the R W 437 inside the NUPAC LHRA.
400047 | CR | 20191009 | CAQ | C | Exam Security near miss |  |  |  | N | NO | <D> **** Detailed Description **** While running a scenario wednesday morning it was noticed that the fax machine was out of paper. When paper was loaded 2 faxes from exam validation the day before came out. The EP person saw the date and classification and knew that it was from the day before and reported it immediately. An Operations Instructor was in the booth at the time also and was witness to the event. No license personnel were exposed to the paperwork and no one obtained detailed knowledge from the paperwork. <I> **** Actions Taken **** Notified Training Management. Instructed my Exam preparers to send a fax and to make a copy on both copy machines to verify that nothing is left in the cue. I am initiating a procedure change to TDI-24 to include these actions.
400048 | CR | 20191009 | CAQ | C | (QA) Conflicting Radwaste Software Testing Requirements |  |  |  | Y | NO | <C> MRT Change: CR 400048 moved from NON-CAQ Severity 3 to CAQ Severity C. <D> **** Detailed Description **** (QA) The testing requirements for the Integrated Shipping and Inventory Program (ISIP) software specified in PPM 11.2.23.2, Computerized Radioactive Waste and Material Characterization, conflict with the requirements in SWP -RMP-02, Radioactive Waste Process Control Program. PPM 11.23.2 was revised to add a requirement to test (verification and validation) ISIP requirements monthly or prior to use. SWP-RMP-02 states that ISIP is validated upon each use. Insights: â€¢ The previous revision to PPM 11.2.23.2 did not specify a testing frequency to validate ISIP output, simply stating that â€œComputer codes which support this procedure should be subjected to a documented verification/validation process to assure correct results.â€ This requirement was satisfied by verifying ISIP outputs with each use. â€¢ Interviews revealed that the change in ISIP testing frequency was added to procedure based upon industry benchmarking and vendor feedback that revealed Columbia was an outlier by testing with each use. . See EDMS for the full text of this deficiency, including requirements and factual basis. <I> **** Actions Taken **** Discussed issue with the Chemistry/Radiological Services Manager. Quality recommends assignment to Radiation Protection. <N> **** Equipment Description **** N/A
400049 | CR | 20191009 | CAQ | C | (QA) Incorrect Radwaste Software Version in Software Catalog |  |  |  | Y | NO | <C> MRT Change: CR 400049 moved from NON-CAQ Severity 3 to CAQ Severity C. <D> **** Detailed Description **** (QA) The current Software Catalog incorrectly lists Integrated Shipping and Inventory Program (ISIP) Version 3.0, Build 16 as the approved in-use version. ISIP Version 3.0, Build 17 is currently in-use for characterizing and shipping radioactive wastes. Form 26108, Software Classification, was not completed and submitted to Information Services to update the Software Catalog to Version 3.0, Build 17. Insights: â€¢ ISIP Version 3.0, Build 17 was released concurrent with completing Build 16 testing. Instead of implementing Build 16 and immediately update to Build 17, the testing was expanded to include Build 17 changes and skip Build 16 implementation. . See EDMS for full text of this deficiency including requirements and factual basis. <I> **** Actions Taken **** Discussed issue with the Chemistry/Radiological Services Manager. Quality recommends assignment to Radiation Protection. <N> **** Equipment Description **** N/A
400050 | CR | 20191009 |  | 3 | (QA) Radwaste volume not trended as required |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The volume of radwaste generated and shipped is not trended as required by the Radioactive Waste Process Control Program. Requirements: â€¢ SWP-RMP-02, Radioactive Waste Process Control Program, revision 7, step 2.8.2 states: â€œTrend the volume of Radwaste generated and shipped.â€ Insights: â€¢ SWP-RMP-02 does not state the frequency for trending or how/when to report the results. â€¢ Waste generation statistics are reported in the Annual Radiological Effluent Report. â€¢ Interviews with radwaste staff and supervision revealed that it is unclear what requirement drives waste volume and shipment trending. <I> **** Actions Taken **** Discussed issue with the Chemistry/Radiological Services Manager. Quality recommends assignment to Radiation Protection. <N> Conducted a review of the FSAR to determine if there were requirements for trending the radwaste volumes in that document that would drive the requirement listed in SWP -RMP-02, The Process Control Program. After reviewing Section 11.4 of the FSAR, I determined there were no requirements for trending the volume of radioactive waste generated at the station in the FSAR. The requirement will be removed from SWP-RMP-02
400051 | CR | 20191009 |  | 3 | (QA) SWP-RMP-01 and -02 reference outdated procedures |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) One step in SWP-RMP-01 "Radioactive Waste Management Program" and 2 steps in SWP-RMP-02 "Radioactive Waste Process Control Program" cite outdated procedures. This is a change management issue with no known actual consequence; however, a procedure pointing to outdated documents can lead to confusion. Factual Basis: â€¢ SWP-RMP-01, step 5.14 points to "PPM 1.10.2, Routine or Periodic Reports Required by Regulatory Agencies", which was superseded by "SWP-LIC-05, Tracking Routine or Periodic Reports Required by Regulatory Agencies" on 4/18/2001, and then SWP-LIC-05 was later taken to "History" status on 3/17/2011. â€¢ SWP-RMP-02, step 5.53 cites "PPM 11.2.23.42, Use of the Model 10-160B Transportation Cask", which was taken to "History" status (Cancelled) on 9/04/2018. â€¢ SWP-RMP-02, step 5.54 cites "PPM 11.2.23.43, Use of the Model 10-142 Transportation Cask", which was also taken to "History" status (Cancelled) on 9/04/2018. <I> **** Actions Taken **** Discussed issue with the Chemistry Radiological Services Manager. Quality recommends assignment to Radiation Protection. <N> **** Equipment Description **** N/A
400052 | CR | 20191009 | CAQ | C | (QA) Rad Material Shipping JFG Conflicts with SWP |  |  |  | Y | NO | <C> MRT Change: CR 400052 moved from NON-CAQ Severity 3 to CAQ Severity C. <D> **** Detailed Description **** (QA) An individual performed independent Radwaste Transportation Specialist (RWTS) functions as allowed by Radioactive Waste Shipping Job Familiarization Guide (JFG), however this conflicts with the requirements in SWP-RMP -01, 11.2.23.1, and 11.2.23.2 for qualification at the Qualification Group Level. The JFG was revised to add a section to track additional experience after initial qualification to perform independent work, but failed to address the delay in submittal of a completed JFG and the effect on PQD qualification group status required by procedures. Insights: â€¢ Interviews indicate the intent was to allow an individual to be qualified to perform work independently as described in Form 27132 and subsequently complete the experience/proficiency section prior to receiving PQD course RW000168 credit and CXAE qualification in PQD. â€¢ The individual has subsequently qualified CXAE on 9/30/19. . See EDMS for full text of this deficiency including requirements and factual basis. <I> **** Actions Taken **** Discussed issue with the Chemistry/Radiological Services Manager. Quality recommends assignment to Radiation Protection. <N> **** Equipment Description **** N/A
400053 | CR | 20191009 |  | 3 | Battery discharge test equipment may be degrading-trending |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Electricians performed annual testing of spare batteries in Building 19 Per WO# 02129890-01. The Alber test equipment is showing signs of not being reliable. testing was performed on three of the station spare batteries. two of the three battery tests had battery cells disappear from the laptop computer screen during the test, under certain circumstances this could ify a test in progress. Of the two tests that were affected, both times it was cell 9 and cell 10 that disappeared. Voltage was verified to be present on the affected cells with a Fluke DMM. And the test equipment was still measuring the appropriate Overall Battery Voltage. Also, When battery testing reaches a low voltage threshold, the software is supposed to stop the program from recording data. On one particular test of E -EQ-B1/9 (spare HPCS battery) the software continued to calculate battery capacity for an additional 1.5 hours. CR is for trending. <I> **** Actions Taken **** notified supervision, engineering and CRS. <N> **** Equipment Description **** spare batteries Bldg 19
400054 | CR | 20191009 |  | 4 | 2F Power On light on HT-HTP-FP/5 not illumninated | N | N |  | N | YES | <D> **** Detailed Description **** 2F power on light not illuminated, swapping bulb did not rectify the problem. <I> **** Actions Taken **** Wrote CR, Informed CRS | 02-00-HT-HTP-FP/5
400055 | CR | 20191009 |  | 3 | HPCS System not protected (NRC identified) |  |  |  | N | NO | <D> **** Detailed Description **** Concerns were raised about the required postings for the SW-A pump house for protecting HPCS-SW. <I> **** Actions Taken **** Wrote CR, investigating.
400056 | CR | 20191009 |  | 4 | Black barrel of unknown substance in XFMR Yard |  |  |  | N | NO | <D> **** Detailed Description **** There is a black barrel, with a rusty lid, thyat appears to be full or mostly full of an unknown substance. The barrel is sealed, but has no identification. Please investigate and remove. Barrel is near stairs to CST pit. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** XFMR Yard near base of CST Pit stairs.
400057 | CR | 20191009 |  | 4 | Pressure regulator for CAS-V-608 deficiency | N | N |  | N | YES | <D> **** Detailed Description **** The pressure regulator downsteam of CAS-V-608 is performing erratically. Small adjustments will cause the pressure to jump around by up to 20 psi. Pressure will continue to drift around without operator imput. <I> **** Actions Taken **** Wrote CR, informed STA <N> Station configuration documentation does not depcit a pressure regulator downstream of CAS-V-608. | 02-00-CAS-V-608
400058 | CR | 20191009 | CAQ | C | Configuration control issue with NLI type A23/32136 bucket | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** CGS may have procured a NEMA size 2 starter under bucket CID 32136 and installed this unit in a NEMA size 1 starter application WMA-42-7F1B (WMA-FN-54A). . On 1/09/2015, the responsible engineer for the NLI MCC bucket project requested a CGS TYPE A23 bucket under CID 32136 with a purchase part description denoting that the unit be supplied with a NEMA size 2 starter. However, Procurement Specification Deviation (PSD) 13526 issued by the project RE on 3/31/2015 identified the bucket CID as requiring a NEMA size 1 starter. CID 32136 was purchased (PO 337098) and received on 05/26/2015 with the NEMA size 2 starter part description. The only bucket procured under CID 32136 was issued to WO 02035892 on 9/23/15 and installed and verified functional in WMA-42-7F1B, (WMA-FN -54A) on 11/5/15. . PSD 13526, CGS drawing E528-31, and a Vendor Supplied Bill of Material drawing 11317684-BM-51 Rev 1 for the subject bucket type A23/32136 lists the starter size as NEMA size 1. . Asset Suite CID 32136 lists the starter as NEMA size 2 and the item was purchased, received, and installed with this NEMA size 2 description. . It is unclear at this time if a NEMA size 1 (as listed in the PSD) or NEMA size 2 starter (as listed on the CID) is physically installed in WMA-42-7F1B (WMA-FN-54A). Recommend Electrical Design Engineering confirm appropriate starter size for this application and reconcile plant installation configuration with design documentation and Asset Suite. It is assumed that the Size 1 and Size 2 Freedom series starters utilize the same contactor coil and therefore there is minimal/negligible impact to the electrical circuit powering the starter coil currently installed in WMA-42-7F1B. <I> **** Actions Taken **** Contacted the main control room, system engineer, and <N> **** Equipment Description **** WMA-42-7F1B (WMA-FN-54A)
400060 | CR | 20191009 |  | 3 | 2019 Mid-Cycle â€“ TCCs PGM approval not documented in AR EVAL |  |  |  | N | NO | <D> **** Detailed Description **** This is an administrative issue only. The Plant General Manager approval for Temporary Modifications (TMODs) and Non-Intrusive Compensatory Measures (NICMs) prior to exiting R24 was performed under SWP-OPS-05 but was not documented for each TMODs and NICMs AR EVAL EDMS. Per SWP -CM-02, extensions for a TMODs or NICMs to remain in place longer than a refueling cycle require approval of the Plant General Manager and documented in the applicable AR EVAL. Recommend that the PGM approval to be documented per SWP -CM-02. <I> **** Actions Taken **** Discussed with Design Engineerin Manager and System Engineering Manager.
400062 | CR | 20191009 |  | 4 | EPN label for receptacles does not match drawings | N | N |  | N | YES | <D> **** Detailed Description **** EPN label discrepancy between the field and electrical drawing for receptacle in RW525 com room was found during the walkdown for FiberMux replacement project. Receptacles inside the communication panel are labeled US -PP-AA CKT 7 and US-PP-AA CKT 12 (see picture attached to EDMS). These labels do not match drawings EWD-46E-210, E757-2A and OPS breaker lineup procedure SOP-ELEC-AC-LU (page 141). Per the design drawings the receptacles are E -PP-US/AA CKT 19 and E-PP-US/AA CKT 24. Need to verify the proper circuit breaker in panel E-PP -US/AA that is feeding the receptacles and make appropriate changes to document and/or field. <I> **** Actions Taken **** Discuss with the supervisor and project team issued CR. <N> **** Equipment Description **** RW 525 communication room | 02-00-E-PP-US/AA
400063 | CR | 20191009 | CAQ | D | DG1 govenor oil level low | Y | N |  | N | YES | <D> **** Detailed Description **** DG1 govenor oil level is low on both the 1A1, 1A2 engines. Per step 5.1.6 oil level should be between the top of the sightglass and 0.25" below of the top of the sightglass <N> This AR CR 400063 was incorrectly written against EPN E-DG-1 which is a DESIGN status EPN in Portal J. Added referened 1A1 and 1A2 engine EPNs (DG-ENG-1A1 and DG-ENG-1A2). | 02-00-E-DG-1
400064 | CR | 20191009 |  | 3 | 2019 AFOF Potential Impact to FOF Exercise Effectiveness |  |  |  | N | NO | <D> **** Detailed Description **** A Potential impact to a Force on Force exercise occured due to an adversary controller call on. <I> **** Actions Taken **** A time-out was called, adversaries were reset, and the drill continued without the error impacting the effectiveness of the drill. <N> A slide was added to the adversary safety brief to ensure that the correct position is notified when making controller calls during Force on Force Exercises.
400066 | CR | 20191010 | CAQ | C | DG1 gov oil sight glasses changed without procedure update |  |  |  | N | NO | <D> **** Detailed Description **** DG1 governor oil sight glasses changed without associated SOP-DG1-STBY procedure revised. CR 396453 documents a recommendation to revise all DG procedures for the new style sight glass. The due date for this revision was after the scheduled sight glass change. A procedure hold should have been placed on the sight glass replacement work orders. Recommend procedure revision asap. <I> **** Actions Taken **** SM/OCC notified. Oil level verified per CR 396453 response. PCN initiated to resolve level gap in procedure.
400067 | CR | 20191010 | CAQ | C | DG1 failed to start locally | Y | N |  | N | YES | <D> **** Detailed Description **** during local slow start of DG1 when DG-RMS-DG1/S14 was depressed the DG start circuitry did not pick up. Suspect DG-RMS-DG1/S33 which is difficult to fully operate requiring crisp operation per the P&Ls. reference AR 211494 | 02-00-DG-RMS-DG1/S33
400069 | CR | 20191010 |  | 4 | Received LP HEATER 2C LEVEL HI TRIP, H13-P840.A2.4-5, alarm. | N | N |  | N | YES | <D> **** Detailed Description **** Received LP HEATER 2C LEVEL HI TRIP, H13-P840.A2.4-5, alarm. COND-HX-2C level is normal and stable, being controlled with HD-LIC-2C and HD-LIC-2C2 in AUTO. None of the automatic actions occurred. Everything is normal other than the alarm. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. . This was a high level trip alarm with no actual high level trip. | 02-00-HD-LS-2CHT
400071 | CR | 20191010 |  | 3 | Power block system list in SWP-DES-01 |  |  |  | N | NO | <D> **** Detailed Description **** Consider revising procedure SWP-DES-01 to clarify systems that are included/excluded from of the power block. Currently, in Attachment 7.1 of SWP-DES-01 rev 17, Telecommunication Room in the Protected Area Access Point is excluded from the power block. However, in this room there are systems and component that should be part of the power block for example: Plant PBX System and its support equipment. â€¢ 48V PBX Batteries: E-B0-PBX â€¢ Inverter: E-IN-PBX/3 â€¢ Charger #1 and #2: E-C0-PBX/1 and E-C0-PBX/2 â€¢ Control panels: E-CP-PBX/ROLMCBX, E-CP-PBX/CBX, This is a document only issue and does not impact any equipment function.
400075 | CR | 20191010 |  | 4 | Potable Water Break between PWC-V-403 and PWC-V-580 | N | N |  | N | YES | <D> **** Detailed Description **** A water break was discovered at 0725 this morning that required isolation of B-11, B-12 and B-64 potable water. The leak was isolated at PWC-V-403 and PWC-V-580. <I> **** Actions Taken **** Isolated leak, imformed building occupants and posted signage as required. Contacted manager and Contracts for needed support | 02-00-PWC-V-403
400077 | CR | 20191010 | CAQ | D | SEC-MW-01 not functioning as designed | N | N |  | N | YES | <D> **** Detailed Description **** CAS is received a high alarm rate on SEC-MW-01. Request electrical maintenance to investigate. <I> **** Actions Taken **** CR/WR Generated; Compensatory measures initiated | 02-00-SEC-MW-1RA
400078 | CR | 20191010 |  | 4 | Yakima Building HP Ready Room Heating Unit Insufficient |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The recently replaced heating unit located in the HP Ready Room 441' Yakima building is not sufficient to heat the room space for which it is intended. It also must compete with cold weather ops lineup at this time. Recommend upgrading to a larger unit or adding an additional unit which would provide adequate heating requirements. <I> **** Actions Taken **** Wrote CR. Initiatiated WR. <N> **** Equipment Description **** Yakima HP Ready Room heating unit.
400079 | CR | 20191010 |  | 3 | Checklist task unable to be performed as written |  |  |  | N | NO | <D> **** Detailed Description **** The Reactor Operator Clearance Order preparation checklist (TG000029 Rev 8) Task# RO-1182 â€œPlan, issue, and implement a clearance order checklist (per 1.3.64 and OI-12) has a sub-task to â€œWrite and Perform a Temporary liftâ€ as a must perform task. Our process for writing temporary lifts has changed since this qual card was issued (2015), where CORC writes the Temp lift when creating the initial clearance, and the on-shift tag RO implements the temp lift per the schedule. With Clearance order implementation as a separate qualification, recommend an evaluation to remove the â€œissue and implementâ€ from the above task if the candidate is already qualified Clearance Order Implementation (TGRI). This is already in practice for other tasks within the TGRO checklist. <I> **** Actions Taken **** Operations Training supervision concurred with this action per telecom. Followed GEN-TQS-03 Section 5.3.7 for resolution
400080 | CR | 20191010 | CAQ | D | Rod accumulator trouble alarm CRD-HCU-2659 | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-2659 rod accumulator trouble alarm due to low nitrogen. <I> **** Actions Taken **** EO repressurized the HCU | 02-00-CRD-HCU-2659
400084 | CR | 20191010 |  | 3 | CI-13.12 requires a procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** CI-13.12 requires a procedure enhancement. The table of contents do not line up with the correct step numbers in the body of the procedure, i.e. in the table of contents, the system shutdown is listed as step 4.12, however, in the body of the procedure it is step 4.11. <I> **** Actions Taken **** Initiated condition report.
400085 | CR | 20191010 |  | 3 | PHCSC presentations not IAW DES-2-9 |  |  |  | N | NO | <D> **** Detailed Description **** The 10/7/19 PHCSC presentations for AR EVAL 385707 and AR EVAL 374701 were not in accordance with DES-2-9 section 4.6.15 direction. Per DES-2-9 section 4.6.15, the requirement is to "PRESENT the technical evaluation form and the issue prioritization form at the PHCSC meeting per SWP-SYS-01." Contrary to this direction, the presentations prepared and made for these two AR EVALs did not include these prepared forms (Form 26867 - Engineering Technical Evaluation or Form 26868 - Issue Prioritization). During the 10/7/19 PHCSC meeting, a PHCSC quorum member questioned the lack of the subject forms in the presentations but the presentations were subsequently made and acted upon by the PHCSC without them. Additional issues: 1) AR EVAL 385707 is COMPLETE status in Portal J and does not have a PHC assignment per DES-2-9 step 4.6.13 which should have been initiated before the EVAL assignment was routed for completion approval. AR EVAL 385707 needs to be re-opened to have the missing PHC assignment added to document the 10/7/19 PHCSC presentation decision in the assignment completion notes per DES-2-9 step 4.6.15 e and to have the follow-on assignments added associated with the PHCSC decision created per DES-2-9 section 4.6.16. 2) For AR EVAL 374701, the 10/7/19 PHCSC presentation decision was not documented in the PHC assignment completion notes per DES-2-9 step 4.6.15 e. . This AR CR 400085 should be assigned to System Engineering for resolution.
400086 | CR | 20191010 |  | 3 | Procedure change required OSP-ELEC-W101 |  |  |  | N | NO | <D> **** Detailed Description **** Section 7.7.6 be changed to â€œâ€¦impacting CGS from the Reliability Coordinator (CAISO).â€ Also consider reviewing other procedures such as 1.3.82 for similar impacts.
400087 | CR | 20191010 | CAQ | D | CMS-PI-3 reading zero | Y | N |  | N | YES | <D> CMS-PI-3 on CMS-SR-20 read zero "Hg vac. <I> Contacted specialist, wrote CR <N> RB 548' CR at INPROG. Approved CR, moved to SRO for OPS Review. | 02-00-CMS-PI-3,02-00-CMS-SR-20
400089 | CR | 20191010 |  | 3 | PPM 1.3.9 Section 4.7 does not reference Attachment 8.5 |  |  |  | N | NO | <D> **** Detailed Description **** As currently written, PPM 1.3.9 (Temporary Modifications) section 4.7 (Temporary Modification Log) does not point to or reference Attachment 8.5 (ELECTRONIC TEMPORARY MODIFICATION (TM) LOG INDEX W/ NICM ASSIGNMENTS). Additionally, there is inconsistency within the procedure regarding the title for Attachment 8.5 - this index includes NICM assignments and should consistently indicate as much throughout the procedure. See the PPM 1.3.9 R56 MnrR1 mark-up attached to the EDMS of this AR CR 400089. Recommend resolution by System Engineering (i.e., the Responsible Organization / Sponsor for PPM 1.3.9). <N> Additionally, the current direction in PPM 1.3.9 Attachment 8.5 is incorrect - sends the user to a location on SharePoint that does not currently exist and does not direct the user to run the report for all the appropriate TMOD statuses. See the Markup attached to the EDMS of this AR CR 400089.
400090 | CR | 20191010 |  | 4 | PMT - FD-P-12 Unsat 02149957 |  |  |  | N | YES | <D> **** Detailed Description **** 29151877 EDR-V-52 is misting out of a crack in the piping 021449957(M) - PMT - FD-P-12 - PACKING ADJUSTMENT - PMT unsat, pump packing doesnâ€™t leak, but, pump ran for approximately for 40 sec. and began to cavitate and vibrate excessively. At the pump start the pump brought up pressure on local gauges showing that it was moving water, the pump was running fine with no issues and amps looked acceptable then 40 seconds into the run the pump started to shake/vibrate excessively and the amps started to go up as if the suction to the pump was clogged. Suggest cleaning sump out/ see if the bottom is full of sediment <I> **** Actions Taken **** Secured pump, notified operations, wrote this CR | 02-00-FD-P-12
400091 | CR | 20191010 |  | 3 | 2019 AFOF Evaluate the use of an FOF Tactic |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate the continued use of specific doors as a viable tactic for contingency events. <I> **** Actions Taken **** Discussed with Security Management and initiated this condition report to develop how this condition will be further evaluated. <N> An evaluation was completed to ensure that the principles of cover and concealment were maintained during engagements. The tactic was determined to be a viable option during contingency events. No further actions necessary.
400092 | CR | 20191010 | CAQ | D | Flanges leak at EDR-V-52 |  |  |  | N | YES | <D> **** Detailed Description **** During the performance of installing a temp wrap around the leaking weld connecting the weld neck flange to the 6â€x4â€ eccentric reducer (2 small pin holes on the bottom of the weld are leaking) it was also noticed that the gaskets on both sides for EDR-V-52 are weeping (6 drops a min). Pipe wrap also leaks approx. 20 drop a min into witchs cap. <I> **** Actions Taken **** Suggest to replace the weld neck flange and eccentric reducer and installing 2 new gaskets for EDR-V-52 to repair issue. Need Planning and UCM to schedule repair. | 02-00-EDR-V-52
400094 | CR | 20191010 |  | 3 | OJT and TPE stipends paid incorrectly |  |  |  | N | NO | <D> **** Detailed Description **** On the check dated 10-11-19, the OJT and TPE stipends were paid incorrectly. Each stipend paid was one-half of one percent of the journey electrician rate over 2080 hours, for a total of 1 percent of the journey electrician rate over 2080 hours. The NBU contract requires each stipened to be paid at 1 percent of the journey electrician rate over 2080 hours, for a total of 2 percent of the journey electrician rate over 2080 hours. Furthermore, the previous years' worth of FLSA Regular Rates were not recalculated to include any OJT or TPE stipend amounts. In October 2018, all of these payments were completed properly. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR.
400097 | CR | 20191010 |  | 4 | RFT-LOC-1A excessive tripping | N | N |  | N | YES | <D> **** Detailed Description **** RFT-LOC-1A has tripped off line several times sometimes within minutes of being reset. <I> **** Actions Taken **** Informed CRS | 02-00-RFT-LOC-1A
400098 | CR | 20191010 |  | 3 | Isometric drawings for the HCO system do not match. |  |  |  | N | NO | <D> **** Detailed Description **** Isometric drawing CVI # 216-01,1201 and 216-01,1176 do not match each other or the installed configuration. These drawings need to be as-built and revised to match the as found configuration. Please assign to AR-DESDFTM as severity 3. <I> **** Actions Taken **** Informed my Supervisor
400099 | CR | 20191010 |  | 3 | 2019 Mid-Cycle - SWP-CM-02 TM & NICM periodic reviews |  |  |  | N | NO | <D> **** Detailed Description **** SWP-CM-02 Precaution & Limitation 2.11 states that Temporary Modifications (TMs) and Non-Intrusive Compensatory Measures (Non-Intrusive CMs (a.k.a., NICMs)) should be reviewed quarterly by station management to verify that the changes are still needed, to identify changes that are inconsistent with the licensing or design requirements, and to confirm that the number and age meet expectations. In addition, a periodic review should be performed to evaluate the combined effects of outstanding TMs and non-intrusive CMs in regard to mitigating systems and the integrity of radiological barriers. Although AR SELF 60391 exists for PPM 1.3.9 TMs and at least partially addresses these SWP-CM-02 reviews for TMs, a similar AR for SWP-CM-02 NICMs does not appear to exist. It is possible that the SWP-CM-02 directed periodic station management reviews for TMs and NICMs might not be occuring. A spreadsheet of current SWP-CM-02 NICMs is attached to the EDMS of this AR CR 400099. A similar spreadsheet of current PPM 1.3.9 TMs is included with the OFM CGS Daily Report.
400101 | CR | 20191010 |  | 4 | OSP-SW-Q101 was unable to be worked |  |  |  | N | NO | <D> **** Detailed Description **** WO 02143199 for performance of OSP-SW-Q101 was unable to be worked on the week of 10/7/2019. The WO was originally planned to be worked on Tuesday, but due to emergent issues, requiring system-engineering resources during the DG1 maintenance window the sonar boat surveillance was discussed to be worked on Thursday 10/10/2019. While it was known that there was the potential for both Service Water pumps to be running, the procedure does allow the sonar boat to be ran with both pumps in operation and the system in SPLASH mode. Discussions with control room to validate if we were in SPLASH mode Thursday morning were had and engineering was communicated that we were in SPLASH mode. WO 02143199-01 was taken to working and upon arriving at the spray ponds saw that both SW systems were in SPRAY mode. The procedure does not allow the boat to be ran while the SW system is in SPRAY mode. Discussions were had with both current and oncoming WWM to carry over the surveillance next week. The Late Date for the surveillance is 10/24/2019. Recommend not planning OSP-SW-Q101 surveillance during an online safety system window where resources required from engineering may potentially be pulled to higher priority emergent work. <I> **** Actions Taken **** Discussed with Supervisor, WWM, and SM . Surveillance late date is 10/24/19.
400102 | CR | 20191010 |  | 3 | Mid-cycle assessement SharePoint IS top priority list |  |  |  | N | NO | <D> **** Detailed Description **** On the SharePoint there is a list of safety concerns, but it has not been updated since July. This does not re -enforce the importance to the site. Additionally the list is separated into â€œHighâ€ â€œMedium â€œ and â€œLowâ€. Iâ€™d recommend that all safety issues are of the same â€œimportanceâ€ (it is a safety issue), if you want to identify them in some way maybe list in order of priority but donâ€™t say one is less important than another. <I> **** Actions Taken **** CR written
400103 | CR | 20191010 | CAQ | C | small clam shells found in B Spray Pond | Y | N |  | N | NO | <D> **** Detailed Description **** While performing a Service Water sediment collection for chemistry analysis, ~4-5mm sized clamshells were found in the sediment sample grab from SW Pond B. No live clams were found. There were no apparent clamshells found in the Spray Pond A sample. Both samples were delivered to Chemistry for further analysis. See EDMS for photo. <I> **** Actions Taken **** Notified Supervisor and discussed with SM
400104 | CR | 20191010 |  | 3 | Mid-cycle assessment, plant walk down |  |  |  | N | NO | <D> **** Detailed Description **** During a walk down a lot of oil pads were noticed around the plant with no way to tell how long they have been there or how often it is being cleaned up. There is potential risk here if the leak gets worse the crew will not recognize this due to turnover or a new crew on. In the past we have place a dates on the pads, evaluate if this is something we want to do in the future. This is feedback from Comanche Peak. <I> **** Actions Taken **** CR written
400105 | CR | 20191010 |  | 3 | 2019 mid-cycle assessment, timely closure of LCO/INOP sheets |  |  |  | N | NO | <D> **** Detailed Description **** 2019 mid-cycle assessment, admin process to ensure timely closure of LCO/INOP sheets. Currently there is no forcing function to close out LCO/INOP sheets. All active sheets are reviewed prior to turnover or just after turnover as described in OI-9, however since we track inoperable equipment with no TS actions the list is long. We need a task to periodically evaluate all active sheets, sort by date, and closeout if required. This will enable the CRS/SM to evaluate newer active sheets on turnover. They would still need to be knowledgeable of all active sheets as part of plant status. This is feed back from Comanche Peak. <I> **** Actions Taken **** CR written
400106 | CR | 20191010 |  | 4 | CW-FN-23 Oil Low | N | N |  | N | YES | <D> **** Detailed Description **** CW-FN-23 oil level is right at the "add oil" mark. <I> **** Actions Taken **** Wrote CR, Informed CRS | 02-00-CW-FN-23
400107 | CR | 20191010 |  | 4 | Missing signatures in PPM 10.20.1 |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of WO 02119140-014 PPM 10.2.1 missing signatures were identified in the parts used. section. <I> **** Actions Taken **** Coached the craftsman that failed to sign initials prior to the end of the shift. NOTE: Actual work order number should be 02119140-01 and 02 . <N> The missing signatures identified for parts used in WO 02119140-01/02 were corrected and uploaded to the appropriate WO tasks. There are no missing signatures or initials. Corrective action complete
400108 | CR | 20191010 |  | 4 | CF-P-13 making odd ringing noise | N | N |  | N | YES | <D> **** Detailed Description **** CF-P-13 (EDR/FDR precoat pump) made an odd ringing noise when being used. This noise has not been heard before. The pump seemed to function OK, but I could feel a strong vibration on the seal line, and believe there may be something wrong with the sealing water. Please investigate. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** RW 467 precoat gallery. | 02-00-CF-P-13
400109 | CR | 20191010 |  | 4 | Level Indicator on SWCF-TK-1 Reading Incorrect | N | N |  | N | YES | <D> **** Detailed Description **** Level indicator on peroxide tank SWCF-TK-1 is reading incorrectly. Tank was verified as empty by observing no flow from discharge line while valve was open at which point the level indicator read at 1700 gallons. Prior experience with the level indicator suggests that it is likely the rope connected to the float has slipped off of one of the pulleys. The indicator needs to be operable prior to the peroxide delivery scheduled for 10/17/2019. <I> **** Actions Taken **** Notified supervisor, notified chemistry, initiated work request, wrote this CR. | 02-00-SWCF-TK-1
400110 | CR | 20191010 |  | 3 | REMP ST-101B composite water sample identified activity | N | N |  | N | NO | <D> **** Detailed Description **** Low level Co-60 was positively identified in the REMP station 101B composite sample for the August 2019 period. ST-101B samples water flowing into evaporation ponds 3 and 4 from the plant storm drains and some equipment drains. The sample was observed to contain visible sediment and/or biological material. Suspect activity is from heavy rain washed out event in mid-August but cannot confirm this is the sole source of activity. ST-101B is not an ODCM required sampling location but is an EFSEC 332 required location. <I> **** Actions Taken **** Verified sample results and consulted with Effluents Specialist, wrote CR
400111 | CR | 20191011 |  | 4 | HT-HTP-FP/6/1 50F Low Temp light is flashing. | N | N |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was observed that HT -HTP-FP/6/1 50F Low Temp amber light is flashing. Outside temperature at the time was 30F. <I> **** Actions Taken **** Notified CRS and wrote CR. | 02-00-HT-HTP-FP/6/1
400113 | CR | 20191011 |  | 3 | High Cond Demineralizer system DP experienced | N | N |  | N | YES | <D> **** Detailed Description **** A cond demineralizer system DP of 43 PSID was experienced during the CFD F backwash and precoat. The cause of this high DP was due to operations department over the prior week recommending and implementing modifications to the published plan for CFD change outs. These modifications consisted of performing relaxes of CFDâ€™s vice backwash/precoats as scheduled in an attempt to extend the life of the resin beds. Although these efforts do result in a longer life it also puts the plant at risk of having to downpower due to high system d/p while performing backwashes or CFD relaxes. <I> **** Actions Taken **** CR written | 02-00-COND-DM-1F
400114 | CR | 20191011 |  | 4 | CCH-CR-1B not protected. |  |  |  | N | NO | <D> **** Detailed Description **** On Oct 10th CCH-CR-1B was not protected per 1.3.83. While protecting this equipment may not be required per 1.3.83 it is the normal practice. This was identified by the night shift crew but was not corrected. In addition, hanging a protection scheme was not discussed by the FIN team during the crew review. <I> **** Actions Taken **** Hung protection scheme for CCH-CR-1B.
400115 | CR | 20191011 |  | 4 | CCH-CR-1A unnecessary out of service time | Y | Y |  | N | YES | <D> **** Detailed Description **** CCH-CR-1A was tagged out for oil filter replacement on Oct 10th, the tags were lifted in the afternoon and it appears the plan it to wait until Oct 12th to perform the PMT. This will result in unnecessary out of service time. | 02-00-CCH-CR-1A
400116 | CR | 20191011 | CAQ | D | SEC-TAS-ES1T is in constant alarm |  |  |  | N | YES | <D> **** Detailed Description **** CAS received a constant alarm on SEC-TAS-ES1T. Request electrical maintenance to investigate. <I> **** Actions Taken **** CR/WR Generated; Compensatory measures initiated | 02-00-SEC-TAS-ES01T
400117 | CR | 20191011 |  | 4 | Component labels require new adhesive (NRC Identified) |  |  |  | N | YES | <D> **** Detailed Description **** Component label on panels H13-P831 and H13-P833 are falling off and currently held in place with scotch tape. <N> **** Equipment Description **** MCR
400118 | CR | 20191011 |  | 3 | LCO Crystal Report |  |  |  | N | NO | <D> **** Detailed Description **** The LCO Tracking Summary Crystal Report is including archived LCO sheets in addition to the active LCO sheets. Specifically, the report is including T19-E -PP-7AF-001, T19-FOB-E-PP-7A-001, T19-R24-RRC-A/B-001, and T19-R24-SM8-MAINT-001. These sheets have been closed and are in the LCO archive and should not be included in the LCO Tracking Summary Report. Recommend investigating and correcting how this report is being generated to have it only pull active sheets that are open. This report is utilzed during CRS turnover and needs to be accurate. <I> **** Actions Taken **** Documented in CR <N> Reassigned to IT Management to correct the report. Operations does not have the capability to correct the issue
400120 | CR | 20191011 | CAQ | C | Conflicting AR/MALT 9473 instructions with materials LOU | Y | N |  | N | YES | <D> **** Detailed Description **** AR/MALT 9473 specified use of RTV (CID 0022203923) for installation of Lexan insulator installed on new SW-TE-110B sheath. SW-TE-110B sheath is SS and CID 0022203923 Limits-On-Use specifically state "DO NOT USE SEALANT ON STAINLESS STEEL". . When AR/MALT 9473 was implemented per WO 01059229-01, additional steps were performed that were not within the scope of the MALT and were not analyzed. The stainless steel thermocouple seal fitting (CID 0000015391) stainless ferrules were removed and substituted with brass ferrules with no evidence of allowance or analysis in MALT instructions. Also, new SW-TE-110B sheath was bent by hand to achieve additional clearnce from bearing cooling tubes with no evidence of allowance or analysis in MALT. . <I> **** Actions Taken **** Contacted System Engineer for knowledge of any additional documentation that would indicate additional work outside of AR/MALT 9473 or provided analysis of actions and/or Engineering Approval and review. Engineer reviewed AR/MALT 9473 and found no supporting information allowing for the identified deviations and was unaware of any supporting Engineering Reviews/ Design Analysis which specifically allowed deviations . . Informed System Engineer of RTV Limits-On-Use specfying not for use on stainless steel and AR/MALT 9473 specification and instruction for use of this RTV on SW-TE-110B sheath contrary to Limits-On-Use. <N> **** Equipment Description **** SW-M-P/1A Upper Bearing Oil Reservoir at SWPH-A SW-M-P/1B Upper Bearing Oil Reservoir at SWPH-B | 02-00-SW-TE-110A,02-00-SW-TE-110B,02-00-SW-TE-111A,02-00-SW-TE-111B
400121 | CR | 20191011 |  | 3 | CMR 18033 deferral per SDP guidance |  |  |  | N | NO | <D> **** Detailed Description **** EC CMR 18033 is being deferred to be completed at a future date as this is associated with a return of 0.22 amps as spared margin on E-PP-3C-A (OG-CP-1) per replacement of OG-FIC-3/2 via urgent mod EC CC 18009. Per SDP calculation guidance, for plant modifications that are being processes to be issued in a timely fashion, as EC 18009, and the change is conservative (i.e., returning margin on PP-3C-A) the issuance of EC CMR 18033 can be deferred with a commitment to complete and approve the CMR before EC CC 18009 closeout and within 90 days of EC CC 18009 approval. This CR is for documentation and to track EC CMR 18033 status. . Recommend assigning this CR to AR-MODS <I> **** Actions Taken **** Initiated this CR per SDP guidance Recommend nonCAQ assignment to AR-MODS.
400123 | CR | 20191011 |  | 4 | Lighting needed RX 522 |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Relamping needed in RX 522 South Pipe Space. Currently there isn't lightiing in the room. Area is posted High Radiation area <I> **** Actions Taken **** Work request written . No work can be done in this area until sufficient lighting is provided. <N> **** Equipment Description **** RX 522 South Piipe space | 02-00-R-BLDG-MISC
400124 | CR | 20191011 |  | 4 | CBD-V-1 has become very difficult to operate | N | N |  | N | YES | <D> **** Detailed Description **** CBD-V-1 is a large valve used nearly daily for Circ Water Blowdown. This valve used to turn easily, but now it is so stiff that a leverage device is needed to open it. As this is a large valve, this is time consuming. Please adjust/repair this valve ASAP! <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** CWPH | 02-00-CBD-V-1
400125 | CR | 20191011 | CAQ | C | Update Priority 0 AED E519-2 not redlined for TMOD EC 17994 | N | N |  | N | YES | <D> **** Detailed Description **** On 10/11/19, the Responsible Engineer for TMOD EC 17994 R0 discovered that Update Priority 0 (update immediately) AED E519-2 had not been redlined or had an updated drawing revision/minor revision issued in Portal J. Fieldwork per WOT 02150654-01 for implementation of this PPM 1.3.9 TMOD had been finished on 09/23/19. Upon discovery of this CM issue, the Responsible Engineer and another individual completed afterhours redline of AED E519-2 in the main control room. . Recommend resolution by AR-EFIN to determine how this adminstrative CM issue occurred. | 02-00-BS-V-8A
400126 | CR | 20191011 | CAQ | C | (NRC) "Comp Measures" vs "Corrective Action" in POD's |  |  |  | N | NO | <D> **** Detailed Description **** It is unclear if we are considering the difference between "Compensatory Measures" and "Corrective Actions" in our POD's. Per 1.3.66, a compensatory measure is an activity which restores, enhances, or maintains operability. It is established to address a degraded or nonconforming condition, and is to be in effect for a time period prior to conduct of maintenance to restore the SSCâ€™s condition. A corrective action is an action designed to correct, mitigate consequence or preclude repetition of an undesired condition, defined problem or contributing cause. As an example, POD 396335 for trace water in the SW-M-P/1B upper bearing oil has NA for compensatory measure, but we list the following as corrective actions: #1. Increase frequency of oil sampling. This does not appear to be a corrective action; it appears to be a compensatory measure. It does not correct, mitigate or preclude repetition of the condition or cause. . #2. Change the oil in the oil reservoir. Again this appears to be a compensatory action- it removes the oil containing water and replaces it with water-free oil, but does not correct the cause. . #4. Monitor the SW-M-P/1B bearing temperature. This appears to be an action to address the degraded condition, but again does not appear to correct, mitigate or preclude the cause or condition. . This condition does not challenge the validity of the POD's or Operability status. This is a question of whether we are correctly applying the terms "Compensatory Measure" and "Corrective Action." Note that in our six currently open POD's, there are a total of 17 actions. Only one is called a compensatory measure and the rest are called corrective actions. <I> **** Actions Taken **** Reviewed guidance in PPM 1.3.66, SWP-CAP-01 and the 10 CFR 50.59 RESOURCE MANUAL. Reviewed our six currently open POD's.
400127 | CR | 20191011 |  | 3 | OPS3 LOGs Dissappeared from ESOMS. |  |  |  | N | YES | <D> **** Detailed Description **** OPS3 LOGs Dissappeared from ESOMS. while startin the morning tour for OPS 3 it was noticed there was no history for OPS 3 logs. the shift was closed out, Logs were resynced and the date reselected and the tour opened. The history was now present. tour was completed and a unqualified Individual was along for the tour and was being quized along the way. So the logs being taken were witnessed. The logs were down loaded and were reviewed by the in field supervisor. Later in the shift the Logs were being looked at by the STA and it was noticed that the for the OPS3 tour were not in the computer for that shift. At the present time we are reviewing options but a CR was desired. <I> **** Actions Taken **** attempteed to locate the logs in the brick, esoms. <N> **** Equipment Description **** esoms
400128 | CR | 20191011 |  | 4 | NRC reported the following: |  |  |  | N | YES | <D> **** Detailed Description **** DSA-V-31A and DSA-V-19A handles appeared that they may have been bumped slightly in the closed direction. DCW-V-8A1 locked closed seal looked like it was loose or slipped off the handle. Light fixture above W-DOOR- C213 conduit strain relief appears to be loose and wiring exposed. <I> **** Actions Taken **** The 2 DSA valve are ball valves and the handles were slightly offset from inline however I moved the handle back to in-line and felt no stem movement, additionally I verified the other similar DSA valves were open with valve handles all appearing in-line. The DCW valve is a small ball valve which is locked closed by a seal which had slipped off of the handle. The seal did not adequately prevent unintentionally bumping valve. I had equipment operators place a plastic bump hazard cover in place, additionally we checked and placed the plastic bump covers in place on the other 3 similar valves DCW-V-7A1, DCW-V -7A2, and DCW-V-8A2. Contacted maintenance and informed shift manager of the issue with the light fixture <N> **** Equipment Description **** light fixture above W-DOOR-C213 467 radwaste . Crew resolved all issues except for light fixture above.
400129 | CR | 20191011 |  | 4 | OG Analyzer N2 bottle low | N | N |  | N | YES | <D> **** Detailed Description **** The RIGHT OG Analyzer N2 bottle is below 300psig and needs to be replaced. <I> **** Actions Taken **** Initiated CR, Informed MCR <N> **** Equipment Description **** RIGHT OG Analyzer N2 bottle T-441' SW side
400130 | CR | 20191012 |  | 3 | SOP-CFD-BW/PC needs enhanced when doing double B/W. | N | N |  | N | YES | <D> **** Detailed Description **** During performacne of SOP-CFD-BW/PC step 5.7.20.nn says to set Fill timer to approximately 1 minute. The radwaste operator set fill timer to 1 minute. Then performed the second B/W. This resulted in the CFD not sufficiently filled for precoat. CPR-TK-14 would surge from very low in tank to top of tank (going down the overflow), CF-P-4 check valve could be heard opening and closing. System was placed in Hand, valves shut and pump stopped. The step should have left fill timer at 8 minutes. The 1 minute should only be for when tagging it out. Step nn (for each of the CFDs) should be changed to match step 5.7.3 (or equivalent for other CFDs). <I> **** Actions Taken **** Radwaste operator did 1 minute fill. Could not complete Precoat with precoat tank surging. With expanded team including SM, STA, and field supervisor came up with plan to use the fill procedure then finish precoat procedure with out adding resin and not placing CFD in service, then perform anothe B/W and precoat. <N> **** Equipment Description **** SOP-CFD-BW/PC
400131 | CR | 20191012 |  | 4 | Camera for viewing TG heater bay malfunction. | N | N |  | N | YES | <D> **** Detailed Description **** Camera 22 has code that it has "Not enough power for both camera and pen tilt motors." This prevents usage of camera from viewing operator rounds. <I> **** Actions Taken **** Initiated AR, informed MCR. <N> **** Equipment Description **** Heater Bay Camera 22
400132 | CR | 20191012 |  | 4 | Transformer 1/11 pressure low. | N | N |  | N | YES | <D> **** Detailed Description **** Transformer 1/11 pressure is at 0#. Needs to be filled with nitrogen. <I> **** Actions Taken **** Informed MCR, initiated AR. | 02-00-E-TR-1/11
400133 | CR | 20191012 |  | 4 | CW-FN-35 Oil Level At Add Oil Level | N | N |  | N | YES | <D> **** Detailed Description **** CW-FN-35, located on CW-CT-2C, oil level is at the "ADD OIL" mark indicated on the marking plate. Please add oil to the fan motor. <I> **** Actions Taken **** Wrote CR, informed supervision | 02-00-CW-FN-35
400134 | CR | 20191012 |  | 4 | SEC-XD-4 Inop | N | N |  | N | YES | <D> **** Detailed Description **** SEC-XD-4 has a flow warning and is not operating as intended. Call Security at 2185 for details. <I> **** Actions Taken **** SEC-XD-4 was taken out of service. Notified maintenance and generated a CR/WR. <N> **** Equipment Description **** PAAP | 02-00-SEC-XD-4
400135 | CR | 20191012 |  | 3 | PPM 1.3.50 (Operator Aids) is Inaccurate and Needs Update | N | N |  | N | NO | <D> **** Detailed Description **** Operator Aid 15-003 was superseded by 18-001 in January 2018. PPM 1.3.50 on Attachment 7.1 still lists the superseded 15-003 despite the fact that two procedural revisions have been implemented since. Please fix. See EDMS.
400136 | CR | 20191012 | CAQ | C | DG-4 Low Fuel Oil | N | Y |  | N | YES | <D> **** Detailed Description **** While performing OSP-FLEX-M704 it was determined per step 7.2.45 that fuel oil level is less than 7/8 full. Operator recorded tank level at Â¾ full. Per SOP-FLEX-EQUIPMENT -REFUEL, Â¾ full equates to 540 gallons. Per P&Ls 4.8 and 4.9 of OSP-FLEX-M704, DG-4 fuel inventory meets the required 24 hour run time at the load requirement for DIV1 at 230KW and therefore remains functional. <I> **** Actions Taken **** Informed CRS and Shift Manager. Emailed operations admin to request refueling per step 7.2.45 of OSP-FLEX-M704. Initiated CR for tracking of required fuel order. <N> **** Equipment Description **** Outside south of DG Bldg WO 02137581-39 will restore fuel to noprmal l;evel. | 02-00-E-GEN-DG4
400137 | CR | 20191012 |  | 4 | Scaffolding built partially in stay clear / exclusion area | N | N |  | N | NO | <D> **** Detailed Description **** Scaffolding erected partially in a stay clear area near MS -RE-3C and MS-RE-3D. This area is labeled as a stay clear and exclusion area. See EDMS for image. <I> **** Actions Taken **** Informed MCR. Wrote CR. <N> There ia a tag on the scaffold with the shift supervisors approval given the day of the build.
400138 | CR | 20191013 | CAQ | D | Suspect failed power supply in H13-P601.A1 annunciator panel | Y | Y |  | N | YES | <D> **** Detailed Description **** Received the following alarms on H13-P601.A1: 480V DIESEL AUX FEEDER TRIP (3-2), 125VDC CHARGER TROUBLE (4-3), HPCS DG ENGINE CLR FLOW LOW (4-4), DIESEL OIL STORAGE TANK LEVEL HIGH/LOW (4-5), HPCS SYSTEM GROUND (5-1) & 480V SYSTEM UNDERVOLTAGE. Alarms were coincident with an acrid electrical odor emanating from within the annunciator panel. Normal HPCS system voltages indicated on H13-P601 meters and no blown fuses were identified. OPS 2 reported no abnormal conditions locally in the HPCS switchgear area. Entered ABN-ANNUNCIATOR for contingency monitoring actions. <I> **** Actions Taken **** Notified the CRS and Shift Manager. Submitted CR and WR. | 02-00-ANN-ANN-601/A1
400140 | CR | 20191013 |  | 4 | MCR annunciator power supply wire puled out of pins | N | N |  | N | YES | <D> **** Detailed Description **** When performing WR# 29152064 electricians identified a connector inside H13-P601-A1 has two bad crimps. The wires are still electrically connected but the insulation has been pulled away from the pins. <I> **** Actions Taken **** Informed on duty CRS and weekend maintenance supervisor. <N> **** Equipment Description **** MCR, H13-P601-A1 front side | 02-00-ANN-ANN-601/A1
400141 | CR | 20191013 | CAQ | D | Transformer Yard abnormal conditions | Y | N |  | N | YES | <C> Trend to CR 400142, exact same issue. <D> In performace of WO #02001147 found several Transformer yard abnormalities. High oil level in OPDS-CVT-S1/A, OPDS -CVT-S1/C. Vibrations from NR-TS-X. Evidence of recent oil leakage from E-V-S/3. Seals on Startup transformer box cracking from age. Oil leakage under radiator and sampe valve on Backup transformer. <I> Informed SSS. Initiated AR. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review. | 02-00-E-TR-B,02-00-E-TR-S,02-00-OPDS-CVT-S1/A,02-00-OPDS-CVT-S1/C
400142 | CR | 20191013 | CAQ | D | Transformer Yard inspection conditions | Y | N |  | N | YES | <D> **** Detailed Description **** Found high oil lvl in OPDS-CVT-S1/A & S1/C. Rattling from NR-TS-X. oil leakage from E-V-S/3, and from bottom of radiator on backup transformer and sample valve. Cracked seals on Startup transformer control panel. <I> **** Actions Taken **** Informed SSS. | 02-00-E-TR-B,02-00-E-TR-S,02-00-OPDS-CVT-S1/A,02-00-OPDS-CVT-S1/C
400143 | CR | 20191013 | CAQ | C | MS-RIS-610B not functioning | N | Y |  | N | YES | <D> **** Detailed Description **** MS-RIS-610B screen has frozen. Attempting to turn off the screen or to make different selections on the screen results in no â€œbeepâ€ or any activity of MS-RIS-610B. <I> **** Actions Taken **** Notified CRS and initiated CR/WR. <N> **** Equipment Description **** MCR | 02-00-MS-RIS-610B
400144 | CR | 20191013 |  | 4 | CF-TK-42 indicates E3 on digital level indication | N | N |  | N | YES | <D> **** Detailed Description **** CF-TK-42 indicates E3 on its digital level indicator. CF -P-42B is currently running. CF-TK-41 is at 227 gallons. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-CF-TK-42
400145 | CR | 20191014 |  | 3 | DG4 procedures fuel oil level (NRC identified) | N | N |  | N | NO | <D> **** Detailed Description **** NRC identified that SOP-DG4-STBY and SOP-DG4-SHUTDOWN fuel oil level requirements were inconsistent with the levels annotated in OSP-FLEX-M704. These procedures should be in alignment with level referenced in the surveillance (7/8 FULL). <I> **** Actions Taken **** Wrote CR.
400146 | CR | 20191014 | CAQ | C | PRM-V-40 found in unexpected position | N | N |  | N | NO | <D> **** Detailed Description **** During the performance of 12.4.21, the sampling and Determination of Tritium, for 16.11.6, weekly iodine, particulate and tritium analysis, it was noted that PRM -V-40 was in a throttled position (vice full open) when performing the surveillance. This valve is the grab sample bypass valve and is used to force flow through the grab sample line instead of the normal flow path (by creating headloss/pressure drop in the normal flow path). During normal operations this valve is in line with the only flow path through the system. The system was able to maintain normal flow even with the valve throttled. It is unknown how this valve came to be positioned out of normal. There is no impact to plant operation or sample viability for the previous week (if it had been throttled since the last surveillance). <I> **** Actions Taken **** CRS/SM informed. Chemistry supervision notified via email.
400149 | CR | 20191014 |  | 4 | Poor lighting RHR Pump Rm B | N | N |  | N | YES | <D> **** Detailed Description **** The lighting is poor in RHR Pump Rm B, especially on the 441' mezzanine. The update pre-job survey was performed earlier this shift and the HP Technician stated that he was confident that he could perform his survey without compromising his safety, but he also believes that the lighting should be improved for the upcoming work. There are burned out lights that exist and dose is a concern, but the lighting should be improved before work is allowed to proceed. <I> **** Actions Taken **** Initiated this AR/CR and informed the Shift Manager and will inform RP Supervision when they arrive this morning. <N> **** Equipment Description **** Lighting in RHR Pump Rm B RX 422'/441'
400150 | CR | 20191014 |  | 4 | MT&E Found out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0068426 IET Labs Decade Resistor- model 1433-20 found OOT & adjusted within specs. Not used during Calibration cycle. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only
400151 | CR | 20191014 |  | 4 | Refrigerator Physically Damaged | N | N |  | N | NO | <D> **** Detailed Description **** A refrigerator in B34, rm. 129G displayed melted plastic in the freezer. <I> **** Actions Taken **** All items were removed from the refrigerator and it was unplugged. Facilities was called to remove the damaged refrigerator and provide a replacement. <N> Damaged refrigeratir has been removed, new refrigerator is in place. No further action needed.
400152 | CR | 20191014 |  | 3 | Additional issues with PPM 10.28.38 reference CR 00400029 | N | N |  | N | NO | <D> **** Detailed Description **** Additional issues with PPM 10.28.38 reference CR 00400029: 1. PPM 10.25.1 requires a danger clearance for other inverter IN-2 and IN-3 clean and inspects. 10.25.10 requires a danger clearance for other inverter IN-1 and IN-5 2. This is a 1st time clearance and work order, why local tags v danger tags. Risks improper paralleling of IN-4 to load. a. Sections 7.1 does not need a clearance, b. Section 7.2 has clearance boundaries established by operations manipulating local tags per SOP-ELEC-IN4 -SHUTDOWN c. Sections 7.3-7.7 can be done under a danger clearance. d. Section 7.10, 7.11, 7.12 would need local tags with way it is written (every 10 years?) 3. PPM 10.28.38 does not discuss capacitor discharge time ref OMM PG 63 a. The capacitors in the UPS maintain a residual charge for a while after turning the UPS off. The required discharge time for each UPS typeform is provided via a cabinet label and a CHARGE LED. Wait for at least the minimum time indicated on the label and ensure that the CHARGE LED has gone out before opening the door of the UPS once the UPS power has been turned off. 4. Step 7.8 has craft cycle E-CB-DPSS1/8 however OMM 9) PG 63 Turn the power on only after installing ALL of the covers. No note like this in procedure 5. PPM 10.28.38 Section 7.8 does not match SOP-ELEC-IN4 -STARTUP. There are several additional steps in SOP-ELEC -IN4- STARTUP to ensure proper operation that are not addressed in 10.28.38
400153 | CR | 20191014 |  | 3 | (Planning) Update model for WO 02119150-01 | N | N |  | N | NO | <D> **** Detailed Description **** Update model for WO 02119150-01 to include updating the UTC for the relay that is replaced.Need a step for DMA-RLY -TK11/1 so the update does not get missed.
400155 | CR | 20191014 |  | 3 | Modify PPM 10.25.74 for required MOV strokes | N | N |  | N | NO | <D> **** Detailed Description **** PPM 10.25.74 section 7.1 PMT testing requires 2 valve strokes but does not specify when this is required (eg does not differentiate a valve overhaul from a atarter coil replacement and subsequent manual stroke. In many caes, a single vavle stroke is adequate. Clarify section 7.1.21 for when a single or multiple strokes are required. This needs to be addressed in all of the volume 10 MOV testing procedures and sections for alignment. <I> **** Actions Taken **** Assign to maintenance procedure group
400156 | CR | 20191014 | CAQ | D | Material acceptance issues 1 | N | N |  | N | NO | <D> **** Detailed Description **** While accepting material for WO 02139798-01/02 SW-FE-23B it was discovered that material called out in the ASME plan did not match the acceptance tags. Orifice flanges did not have all the required information. See pictures in EDMS <I> **** Actions Taken **** Discussed with Code Programs and Warehouse inspector and had information added to the tag. Issue resolved
400157 | CR | 20191014 | CAQ | C | Material acceptance issues 2 | N | N |  | N | NO | <D> **** Detailed Description **** While accepting material for WO 02139798-01/02 SW-FE-23B it was discovered that material called out in the ASME plan did not match the acceptance tags. Two Â½â€ elbows were issued under the same CID and only one was dual certified as required by the ASME plan description. See pics in EDMS <I> **** Actions Taken **** Discussed with Code Programs and Warehouse and had another dual certified elbow issued. This should be reviewed and have the CID changed on the elbow that is not dual certified.
400159 | CR | 20191014 | CAQ | D | M&TE Rejected | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0068339 Heise Gauge CM200psig Passed Closeout Calibration using Ashcroft Sensor #0064430. Won't Pass Flushing to be able to send to Standards Lab. DEF #7346A written. Rejected- Trashed. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
400163 | CR | 20191014 |  | 4 | W/O 02147446 returned | N | N |  | N | NO | <D> **** Detailed Description **** W/O 02147446 had to be returned for a procedure rev. on PPM 12.13.20. I&C has taken over Radiological Calibrations from Chemistry and the procedure was overlooked when revisions were done to the other RAD CAL procedures. <I> **** Actions Taken **** Wrote CR, Procedure Hold until new Rev. is complete
400164 | CR | 20191014 |  | 4 | MT&E Found out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0066210 Honeywell Pressure Transducer- model TJE found OOT. Rejected- Unable to Zero & Adjust to Specs. Not used during Calibration cycle. No Plant Impact. DEF #7347A written. No Action Required. <I> **** Actions Taken **** None...Trending purposes only
400165 | CR | 20191014 |  | 4 | W/O 02134442 | N | N |  | N | NO | <D> **** Detailed Description **** W/O 02134442 was cancelled due to additional questions that were asked and not yet resolved regarding the scope of work and the support needed to complete the work. Refer to EDMS for additional information. <I> **** Actions Taken **** Wrote CR, Added EDMS Document
400166 | CR | 20191014 |  | 3 | Untimely SSAC meeting | N | N |  | N | NO | <D> **** Detailed Description **** The Senior Site ALARA Committee (SSAC) challenge meeting for work on Service Water Flow Element 23B (SW-FE-23B) was not held in a timely manner, prior to a portion of the work commencing. As a result, the task of installing scaffold for the work was started prior to the challenge meeting. GEN-RPP-13 requires SSAC challenge meetings for activities greater than/equal to 500 mrem during non-outage periods. The work on the flow element is planned for right at 500 mrem. While the team identified early that this work should be challenged, due to competing priorities and not reestablishing the ALARA planners weekly look ahead meeting following R-24, the need for the challenge meeting was not communicated or scheduled. . Enabler Missed: Job Planning and Preparation- â€¢ Prerequisite activities are completed prior to the performance of the task â€¢ Error-likely situations are identified and resolved as appropriate Worker Practices- â€¢ Effective communications are used â€¢ All individuals are actively engaged in the task . Recommend 3 to AR-RADPL
400167 | CR | 20191014 |  | 3 | Certified Letter Was Not Posted And Mailed On 10/10/19 | N | N |  | N | NO | <D> **** Detailed Description **** A certified letter was taken to the Post Office on 10/10/19, but the individual did not notice the postage was missing until they were already at the Post Office. The individual contacted their lead who directed them to finish the mail routes and return to the site. An attempt was made to contact the customer, but with no response, the lead made the decision to mail the letter the next business day. Consequently, letter GO2-19-143 was not posted and sent via certified mail to WDOH on Thursday 10/10/19 which resulted in the letter not being sent to the Department of Health within thirty days as required by WAC 246-233. <I> **** Actions Taken **** The letter was emailed to the WDOH Generally Licensed Device lead on Monday 10/14/19 by Environmental Services. The Post Office is closed on 10/14/19 so the certified letter will be mailed on 10/15/19. No additional actions required. <N> On 10/17/19, an e-mail was sent to applicable individuals outlining a new process for the handling of time sensitive mail. On 11/5/19, the new process for handling time sensitive mail was incorporated into the Mail information sheet under the Resources tab in SharePoint.
400168 | CR | 20191014 |  | 4 | Cond-DM-1D Need Septum Replacement. | N | Y |  | N | YES | <D> **** Detailed Description **** The Septums on Cond-DM-1D are shot. They need to be replaced. The D/P on Cond-DM-1D is high. The D/P on Cond -DM-1D is 15PSID, 48 hours after a Triple Backwash. (We normally only do Single backwashes). The D/P should be approximately 5-7 at this point. This is not something we can wait for months to repair. This is Costing us more Dose, Resin, Radioactive Waste, Manpower and causing the D/P to go up faster on the other 5 Demins due to more frequent relaxes and Backwashes/Precoats on Cond-DM-1D. | 02-00-COND-DM-1D
400169 | CR | 20191014 |  | 3 | (Planning) Add requirements for "work near protected equip | N | N |  | N | NO | <D> **** Detailed Description **** Add requirements for "work near protected equip) for the models of WO's 02142498-01 and 02119827-01. These two meters are rigtht next to each other and need a protected form due to while you are working one the other is protected. WO 02119827-01 is scheduled for 10/23/19, add a rewirement for that task also. This is also a trending CR for not noting form was required prior to start of task. <I> **** Actions Taken **** Completed form 26935 prior to starting field work.
400171 | CR | 20191014 |  | 4 | CRD-V-14A and CRD-V-16A appear to be leaking by their seats. | N | N |  | N | YES | <D> **** Detailed Description **** CRD-V-14A and CRD-V-16A appear to be leaking by their seats.(both piping section up/down stream of the isolation are hot). The other sources of possible back leakage are through CRD-V-14A and CRD-V-16A on the discharge line or the seal cross-connect (CRD-V-17). This leaked by causing some delay in hanging clearance for the work to be done. <I> **** Actions Taken **** SM/CRS/PSRO informed. | 02-00-CRD-V-14A,02-00-CRD-V-17
400172 | CR | 20191014 | CAQ | D | E-RLY-5051/7/73/A phenolic crack | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of ESM7RE042 WO# 02125153-01 there was a small crack near the right side of Tap Block mounting screw. Contacted system engineering .Per engineering it does not affect the operability of relay. CR is for trending purposes. See WO for pictures. <I> **** Actions Taken **** Supervision and Engineering was contacted. | 02-00-E-RLY-5051/7/73/A
400173 | CR | 20191014 |  | 4 | Electrical support task not scheduled | N | N |  | N | NO | <D> **** Detailed Description **** During the performance of WO 02137572-01, it was identified that the electrical support (02) task to complete this work was not scheduled in the week. <I> **** Actions Taken **** Notified WWM initiated CR <N> The appropriate individuals have been coached on this issue. The Electrical task 02 was needed in order for the Electrical shop to see on their schedule. Support tasks for many site groups are no longer used. Those for the shop are needed. The guidance has been given to the schedulers and refreshed on the issue. The work is now progressing.
400175 | CR | 20191014 | CAQ | D | E-RLY-5051/7/73/C phenolic crack | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of ESM7RE042 WO# 02125153-01 there was a small crack near the right side of Tap Block mounting screw. Contacted system engineering .Per engineering it does not affect the operability of relay. CR is for trending purposes. See WO for pictures. <I> **** Actions Taken **** Supervision and Engineering was contacted. | 02-00-E-RLY-5051/7/73/C
400176 | CR | 20191014 |  | 3 | SOP-DOOR/HATCH-OPS does not account for flooding | Y | N |  | N | NO | <D> **** Detailed Description **** During the performance of WO 02131440 CRD-P-1A, REPLACE AND REFURBISH, could not determine why a barrier impairment had been initiated when SOP-DOOR/HATCH-OPS â€œReactor Building, Turbine Building, Radwaste Building, And Containment Personnel, Equipment Building, and Containment Personnel, Equipmentâ€ allows the (A-2) hatch to opened. Currently the procedure does not account for or discuss flooding. During the performance of WO 02131440 CRD-P-1A, REPLACE AND REFURBISH, could not determine why a barrier impairment had been initiated when SOP-DOOR/HATCH-OPS â€œReactor Building, Turbine Building, Radwaste Building, And Containment Personnel, Equipment Building, and Containment Personnel, Equipmentâ€ allows the (A-2) hatch to opened. Currently the procedure does not account for or discuss flooding. Engineering review of this situation revised the impairment as stated: Flooding Review for Reactor Building Crane Bay Trap Door (Room R9/R10) BIP 19-0312: In the below case for Reactor Building rooms R9/R10 (CRD/COND Pump room) the Reactor Building Crane Bay Trap Door will be opened to support maintenance on the CRD pumps. Opening this floor hatch will provide a flow path for a flood in room R105 to flow directly into rooms R9/R10. Note that this floor hatch is located on the ceiling of rooms R9/R10, therefore a room R105 will not be impacted by a flood in rooms R9/R10. Calculation ME-02-02 -02 was reviewed for this evaluation. Flood Scenario: The floor hatch in room R105 is located on the Reactor Building 441' Elevation and opening the floor hatch allows for water to flow directly from room R105 into rooms R9/R10 which are located on the Reactor Building 422' Elevation. In this scenario the flood occurs in room R105 and it is assumed all of the water flows through the open floor hatch into the rooms below. In order to determine the potential impact to equipment in rooms R9/R10 the flood height in the room needs to be calculation and is done so using the following assumptions: 1) There is no flow path out of room R9/R10 (CRD/COND Pump Room) 2) The EDR sump in room R10 is full and there is 25 gpm flow into the sump and the sump pumps are inactive (ME-02 -02-02) 3) The leakage rate through the doors, except those from the stairwells is assumed to be a maximum of 4 gpm which includes penetration leakage. (ME-02-02-02) 4) Compensatory Measure is an hourly flood tour. 5) The single failure is the Moderate Energy Line Crack in room R105. In this scenario the flood is caused by a Moderate Energy Line Crack in a 2"CRD(2)-4 line with a flowrate of 177.2 gpm in room R105. Assuming all of the water flows through the open floor hatch and into rooms R9/R10, in conjunction with the assumed 25 gpm flow into the EDR sump and the 4 gpm of door leakage this results in a total flow rate of 206.18 gpm into rooms R9/R10. With an hourly flood tour in place as a compensatory measure, the flood height in rooms R9/R10 after 1 hour is 7.191 inches. This flood height is bounded by calculation ME-02-02-02 in which postulates a flood height 11.5 feet with a flow rate of 363.70 gpm in rooms R9/R10. All impacted equipment was evaluated in calculation 5.51.58 and was determined to have no impact on safe shut down. Therefore it is acceptable to open the floor hatch and doing so will not impact safe shutdown. Conclusion: Based on the above evaluation, it is acceptable to open the floor hatch in room R105 and doing so will not impact any equipment that is required for safe shutdown. For compensatory measures recommend an hourly flood tour while the floor hatch is open. Recommend CR to Operations to revise procedure if required. <I> **** Actions Taken **** Notified PSRO and initiated CR
400177 | CR | 20191014 | CAQ | D | OG-V-149B indicates open on P820 with OG-V-125B open | N | N |  | N | YES | <D> **** Detailed Description **** air purge should be off with OG-V-125B open. Solenoid operated valve fails open on loss of power. This is purge air to SJAE B train. Checked CAS-FI-2A and 2B locally. CAS-FI-2B indicates 0 scfm. Suspect indication only issue. <I> **** Actions Taken **** checked CAS-FI-2B - zero scfm checked OG sys flow - no change in flow | 02-00-OG-V-149B
400178 | CR | 20191014 |  | 4 | Scaffold support task not scheduled | N | N |  | N | NO | <D> **** Detailed Description **** During the performance of WO 02137572-01, it was identified that the scaffold support (03 and 04) tasks to complete this work was not scheduled in the week. <I> **** Actions Taken **** Notified WWM and initiated CR <N> The Schedulers have been coached on not removing this scaffolding task from the schedule. The work is now progressing.
400181 | CR | 20191014 |  | 4 | Small oil leak on fill pipe to CW-FN-36 | N | N |  | N | YES | <D> **** Detailed Description **** The threaded bellow the sight glass going into the lower union has a slow leak and needs to be taken apart and redoped during the next CT outage. <I> **** Actions Taken **** wrote cr | 02-00-CW-FN-31
400182 | CR | 20191014 |  | 3 | small caution tag printer not printing correctly | N | N |  | N | YES | <D> **** Detailed Description **** tag labels do not appear in the text area on the small caution tag printer in MCR. This has been an unresolved issue for some time now. Suggest assign to IS as a priority to address. <N> **** Equipment Description **** small CT printer in MCR
400183 | CR | 20191014 |  | 3 | MT-DOOR-A2 flooding barrier LL | Y | N |  | N | NO | <D> **** Detailed Description **** During performance of WO 02131440 (CRD-P-1A replacement) a barrier impairment was prepared due to MT-DOOR-A2 (A2 hatch) being impaired open while transporting equipment to the CRD pump room and an hourly flood tour was designated as a compensatory measure. This hatch is not normally open in Mode 1, 2, or 3 when the flood barrier applies and compensatory measures need to be vetted through design engineering. This was caught during implementation which delayed the opening of the hatch. Based on design engineeringâ€™s review of the calculations associated with reactor building flooding it was determined that an hourly flood tour was adequate, however this is a potential error trap in that the analysis could have determined more robust compensatory measures were needed. Now that more work is being performed outside of refueling outages it is imperative that the right groups are engaged during the planning and work control process to ensure that our previous work instructions and permits make sense for Mode 1 as they may have been generated based on Mode 4 or 5 assumptions. <I> **** Actions Taken **** CR generated. <N> CR 400183 is assigned to AR-OPSPROC, despite the requested action being for planning and work control to ensure that we do repeat the near-miss. I would like for CR 400183 to be assigned to work control. CR 400176 will update the SOP. (Per I Bitner)
400184 | CR | 20191014 |  | 3 | Make-Up Training for Maintenance Craft | N | N |  | N | NO | <D> **** Detailed Description **** During third quarter 2019 cycle training, there were eight individuals who missed all or some of the scheduled maintenance continuing training. This CR is being initiated to ensure make-up training is scheduled and completed. There are no challenges to qualifications at this time. <I> **** Actions Taken **** Discussed at Maintenance TAG Meeting
400185 | CR | 20191015 | CAQ | D | EDR-V-66 indicates dual position while full open. | N | N |  | N | YES | <D> **** Detailed Description **** EDR-V-66 has both green and red lights lit while the valve is full open. Valve is full open (in full contact of the open indication actuator), the closed indication actuator is not in contact. <I> **** Actions Taken **** Informed CRS and continued to use the valve for water flow. | 02-00-EDR-V-66
400195 | CR | 20191015 |  | 3 | Questionable Decision-Making on CRD-P-1A | N | N |  | N | NO | <D> **** Detailed Description **** During clearance hang activities to support CRD-P-1A, it was noted that the boundary isolations were leaking by a considerable amount. This was discussed by Operations and Maintenance, who ultimately cycled the isolation valves and determined that the leakage had slowed to an acceptable rate. Upon removal of the pump, the HP tech in the area reported approximately 1/2 gallon per minute leaking from the breach. When challenged on the likelihood of the leak to escalate or an isolation to catastrophically fail, it became apparent that these potential outcomes were not taken into account before deciding to continue with the removal of CRD-P-1A. It should be noted that the pump was being replaced as a preventative maintenance item and not because it showed signs of degraded performance. The potential for exposure to increased system leakage or full system pressure seems like an unnecessary hazard to expose our workers to, especially when the work is not tied to an emergent issue related to plant safety. <I> **** Actions Taken **** Discussed concerns with the work week manager and radiological operations leadership.
400197 | CR | 20191015 | CAQ | C | QAR file lost due to WO taken to finished from assignment. | N | N |  | N | NO | <D> **** Detailed Description **** Two tasks from the monthly fire brigade package were returned to supervisor by mistake. They were accepted as is which returned them to the assignment tab in data glance. The WO tasks were then reviewed and taken to finished from assignment instead of advanced to working and then completed. The reviewing supervisor was not trained that completing WO tasks from the assignment screen resulted in no QAR file being generated. DG needs to be changed to generate a QAR whenever a WO task is completed if possible. This issue needs to be communicated to supervisors to prevent loss of WO data. <I> **** Actions Taken **** Wrote CR <N> Below is the Configuration DataGlance uses for the â€˜Finish Support Tasksâ€™ function from the Supervisor Assignment tab. . Finish Support Task This activity supports taking support tasks directly to FINISHED status in Asset Suite from the Supervisorâ€™s Assign panel. This activity is only available when the Asset Suite Task status is APPROVED 30 or READY 45 and the JOB-TYPE (table TIDWOTSK) is equal to one of the following: AD ADMINISTRATIVE CO CLEARANCE ORDER: HANG OR LIFT NH SHOP PM - OPS REVIEW NOT REQUIRED NP PM - OPS REVIEW NOT REQUIRED NO OTHR PM- OPS REVIEW NOT REQUIRED NS ESSENTIAL PM - OPS REVIEW NOT REQUIRED OS OPERATIONS SUPPORT SC SCAFFOLDING ERECTION/REMOVAL SH SHOP WORK SP SUPPORT TASK XX ADMINISTRATIVE SUPPORT WORK ORDER TASK . This activity is the same as performing option 5 on M300 for the task. None of these tasks should require completion comments and go directly to finished status. When using this function, write the following closeout text to the M301 completion comments â€˜Support task finished by eWP. A QAR will also not be created for these tasks finished in this manner. . A couple more clarifications: â€¢ A Quality Record is not created for these tasks. â€¢ If the task requires Operations Authorization (a Control Room Communications â€˜1â€™) then you have to go through the entire process. â€¢ During the SRO review pre-work, the Control Room Communications flag can be changed from a â€˜1â€™ to a â€˜2â€™ or â€˜3â€™ and then the Set To Finished option will be available on the Supervisor Assignment tab. â€¢ Once a task is taken to working status a QA record will be generated.
400198 | CR | 20191015 |  | 4 | No Load Area Not Kept Free of Loads | N | N |  | N | NO | <D> **** Detailed Description **** In the clean machine shop (GSB 441'), there is a treadmill staged on top of a floor panel that is marked "NO LOAD" - it is not known who this treadmill belongs to. I was unable to relocate the treadmill due to interferences preventing ease of movement. <I> **** Actions Taken **** None taken - owner is unknown.
400199 | CR | 20191015 |  | 3 | Essential PM tasks not showing in Dataglance | N | N |  | N | NO | <D> **** Detailed Description **** Two tasks (-04 and -06) under WO 02139153, Fire Brigade Station Inventory, do not have QARs attached in Portal J â€œDocumentsâ€ or available to be viewed in Dataglance. Tasks are part of an essential PM (PMID 14416) and completed on a monthly basis. Previous months activities reviewed and completed SAT per WO 02138244 with no calibrations due or expiring materials prior to next scheduled completion date 10/15/19 (per WO 02140751). No comp measures or additional actions required at this time. <I> **** Actions Taken **** Informed HP Supervision, PM Coordinator, EP Supervision and Shift Manager. <N> Software is working as designed. Tasks 021391533-04 &06 were â€œSet to Finishedâ€ from the Supervisor Authorization panel in DataGlance, If the user would have walked it thru the different statusâ€™s (working, field work complete, release to supervisor, supervisor review, work complete) a QA record would have been generated. . Below is the logic that sits behind the Set to Finished options. Finish Support Task This activity supports taking support tasks directly to FINISHED status from the Supervisorâ€™s Assign panel. This activity is only available when the Asset Suite Task status is APPROVED 30 or READY 45 and the JOB-TYPE is equal to one of the following: AD ADMINISTRATIVE CO CLEARANCE ORDER: HANG OR LIFT NH SHOP PM - OPS REVIEW NOT REQUIRED NP PM - OPS REVIEW NOT REQUIRED NO OTHR PM- OPS REVIEW NOT REQUIRED NS ESSENTIAL PM - OPS REVIEW NOT REQUIRED OS OPERATIONS SUPPORT SC SCAFFOLDING ERECTION/REMOVAL SH SHOP WORK SP SUPPORT TASK XX ADMINISTRATIVE SUPPORT WORK ORDER TASK . This activity is the same as performing option 5 on M300 for the task. None of these tasks should require completion comments and go directly to finished status. A QAR will also not be created for these tasks finished in this manner. . A couple more clarifications: A Quality Record is not created for these tasks. . If the task requires Operations Authorization (a Control Room Communications â€˜1â€™) then you have to go through the entire process. . During the SRO review pre-work, the Control Room Communications flag can be changed from a â€˜1â€™ to a â€˜2â€™ or â€˜3â€™ and then the Set To Finished option will be available on the Supervisor Assignment tab.
400200 | CR | 20191015 |  | 3 | Dat Glance issue with WO 02152034 | N | N |  | N | NO | <D> **** Detailed Description **** WO 02152034 disappeared when task 01 was validated. It appears that because some of the documents are very large that data glance timed out while attepmting to update the package. Task 01 would not come through to EWP until some of the attached documents were removed, and it still took quite some time for the package to be generated in EWP <I> **** Actions Taken **** worked with EWP personnell to resolve and Wrote CR to document. WO 0215034 was finally generated in EWP <N> There was two tasks on this work order that needed to be created in eWP. The WO was taken to return status in an attempt to align the statuses. The 02 task created after a short time but the 01 task timed out several times. There were several drawings associted with the tasks and that seemed to be what was holding the creatio up. The drawing were unchecked and the task created some time later. NOTE: the package was printed in order for work to start but the package was worked in eWP.
400201 | CR | 20191015 |  | 3 | SOP-CW-LU needs to be updated with valves CBD-V-42, CBD-V-40 | N | N |  | N | NO | <D> **** Detailed Description **** SOP-CW-LU needs to be updated with valves CBD-V-42, CBD-V -40 & CBD-V-41 reference WO 02119508 EC 16616. C-CBD-V-42 -001 is currently hanging for configuration control. <N> EPN CBD-V-42 is only DESIGN status in Portal J MEL. . CBD-V-40, 41, and 42 are all listed in the current revision of SOP-CW-LU (Rev 9) on page 18. There is a rev bar beside the valves. But CBD-V-42 is still listed in design status on the D030 panel.
400202 | CR | 20191015 |  | 4 | CW-CT-1B High Level | N | N |  | N | YES | <D> **** Detailed Description **** CW-CT-1B level is high at 11.5 inches. Logs require a CR be written when cooling tower level is high. <I> **** Actions Taken **** Wrote CR, informed supervision | 02-00-CW-CT-1B
400203 | CR | 20191015 | CAQ | D | DW O2 trending up slowly | Y | N |  | N | YES | <D> **** Detailed Description **** DW O2 trending up slowly. Since 10/12/19. On mids that day N2 M/U to the DW was stopped. The N2 M/U rate must have exceeded the O2 ingress rate. CMS-SR-20 was the last sample rack work but may not be the source. Suggest inspect sample racks communicating with containment for leakage at the rack. see EDMS for trend and pic <N> Common Cause Evaluation for DW O2 Increase [AR 386401] resulted in a corrective action to update surveillance procedures for CMS to address in-leakage due to O-Ring degradation/damage. . Procedure markups were provided in December 2018 and January 2019 [AR 386261-01 and AR 386401-02, respectively], expected completion of procedure updates is December 2019 [AR 386261-02 and AR 386401-03]. . AR-SMS 399024 for new PM for O-Ring Replacement has been initiated and approved on 10/15/2019. | 02-00-C-TK-1
400204 | CR | 20191015 |  | 3 | SOP-PW-LU needs update for PWC-V-218 (CLOSED) and PWH-V-207 | N | N |  | N | NO | <D> **** Detailed Description **** SOP-PW-LU needs update for PWC-V-218 (CLOSED) and PWH-V-207 (OPEN) Ref CR371573 and WO 01155239 for spared GPWH-HX-2. Positions currently maintained with C-GPWH-HX-2 -001.
400206 | CR | 20191015 |  | 4 | MPF revolving door and handicap entrance left unlocked | N | N |  | N | NO | <D> An EN employee contacted the MPF Facility Manager by telephone at 730 Sunday morning October 12th to report that the revolving door was unsecured. The employee had arrived at the building to work and noticed the door unlocked. <I> Facility Manager responded to the MPF and locked the revolving door. The handicap door adjacent to the revolving door was also unlocked; Facility Manager locked this door as well. On Monday morning Facility Manager contacted Bechtel security guard to inquire if he had knowledge of unsecured door. (Bechtel has been provided a key to these doors to unlock/relock the doors on their working Fridays.) The guard reported that he must have forgotten to secure the doors before leaving Friday. Condition reported by email to EN Facilities Leasing Manager, Bechtel building management and Bechtel safeguards and security. This CR initiated for trending. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
400207 | CR | 20191015 |  | 3 | OLNC injection line plugging | N | N |  | N | YES | <D> **** Detailed Description **** During Online Noble Chem (OLNC) platinum injection the pressure on the injection lines is building more rapidly than during previous applications. Injection line plugging is a known issue in the industry. The OLNC application is currently on Day 2 of 10. There is a high probability that the Alternate injection path will need to be impemented per PPM 12.18.3 section 7.6. It is recommended that the appropriate connections be established per the procedure in anticipation of needing the alternate injection lines up to step 7.6.10.h. This will require support from Maintenance and Operations to connect the lines and open the isolation valves. A contingency task for this activity is currently in WO 02138302 and dose has been allocated for the connection of the alternate injection lines. <I> **** Actions Taken **** Informed Chemistry Management, Work Week Manager and ALARA. | 02-00-RFW-V-906B,02-00-RFW-V-908B
400208 | CR | 20191015 |  | 4 | Emergency exit door left open at MPF | N | N |  | N | NO | <D> Facility Manager received a call at 1815 Monday, October 14, 2019 from Bechtel that emergency exit door (#9) at the base of the south stairwell had been found in an open condition. The person who discovered the condition resecured the door, but reported the situation due to concern that there was no alarm sounding (the door has a sign indicating "emergency exit only alarm will sound"). <I> Facility Manager contacted F&CE Supervisor to inquire if alarm has been deactivated or is a silent alarm and if anyone should be notified. Supervisor believed alarm is no longer functioning. Tuesday morning door was checked to ensure self closure is working properly (yes) and door does not alarm. Unclear how door was left ajar as closer causes door to shut tight on testing. CR initiated for trending. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
400209 | CR | 20191015 |  | 4 | Remove Scaffold Inside Building 40 | N | N |  | N | NO | <D> **** Detailed Description **** Rigging scaffold #4339 was installed on 4/8/19 for work on PWC-P-102. The work appears to be complete, but the scaffold has not been removed. The Location is inside Building 40, Pump house #2. The installing work order was 01158000-09 â€œEmergent Maintenance Work, Scaffold Supportâ€. No remove task was listed on the scaffold tag log. The Mechanical Supervisor listed on the scaffold is no longer at CGS. The scaffold tag log also lists the wrong building location for the scaffold. Please remove the scaffold. <I> **** Actions Taken **** Initiated CR and WR 29152104 <N> **** Equipment Description **** name
400211 | CR | 20191015 |  | 4 | PWR-CRA-2 deficiencies identified | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02137572-01 it was identified that the south bridge stops (wooden) are degraded and cracked. They will need to be replaced in the future during the next PM. Additionally the mechanical upper limit was damaged in 2017 see CR 374030 (COMP-NA), WR 29139970 (COMPLETE) electricians were able to repair the limit so itâ€™s functional, however it is bent up and needs to be replaced. <I> **** Actions Taken **** Notified MCR and initiated CR and WR, WR needs to be actioned and bundled with the next PM to make these repairs. | 02-00-PWR-CRA-2
400212 | CR | 20191015 |  | 4 | CRD-HX-2A no EPN label | N | N |  | N | NO | <D> **** Detailed Description **** During the performance of WO 02124163-12 CRD-HX-2A Disassemble for Inspection craft identified that the heat exchanger did not have an EPN label. Craft stopped, notified supervision and expanded the team. Component was verified through drawings, ISOâ€™s, and confirmed in the D030 panel. <I> **** Actions Taken **** Supervision notified, EPN label was made and installed on CRD-HX-2A
400213 | CR | 20191015 | CAQ | C | SLC-RV-29A- Failed as-found set point testing. | Y | N |  | N | YES | <D> **** Detailed Description **** While performing as-found testing, the subject valve failed its set point test by lifting low at 1345 PSI (1400 PSI +42/ -28) and failed its seat leakage test with 10ml/min seat leakage (allowable leakage of .5 ml/min.). The failed valve had been removed from the system and replaced by a pre-tested rotating spare. <I> **** Actions Taken **** Contacted IST Coordinator. <N> **** Equipment Description **** R -552-R513- -M2/3.6 - | 02-00-SLC-RV-29A
400214 | CR | 20191015 | CAQ | D | CRD-HCU 30-03 has spurious alarms | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU 30-03 has spurious alarms. The alarm comes in and immediately clears. Field investigation revealed a possible Loose connection. Tapping on the conduit coming out of the left side of the local alarm indicator, (labeled "HCU Status"), on the HCU, resulted in a momentary Low Pressure alarm flashing in and out, (very fast). The conduit coming out of the local alarm panel goes to a junction box labeled "RBJM, JML-7, Div-A" | 02-00-CRD-HCU-3003
400215 | CR | 20191015 |  | 4 | Monthly Chemical Storage area inspection discrepancies | N | N |  | N | NO | <D> **** Detailed Description **** The monthly inspection of Mechanical Maintenance chemical storage areas discovered the following discrepancies: Expired chemicals found in Hot tool crib flammable liquid storage cabinet, light bulb burned out in T441 painter area walk-in flammable liquid storage cabinet #30. <I> **** Actions Taken **** Delivered expired chemicals to RW 437, Contacted FIN electrical to replace light bulb. No further action is required.
400216 | CR | 20191015 |  | 3 | Security Comp exports did not transfer to corp network | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Another CR to document the ongoing issue. The exports from the Security Computer did not transfer thru the diodes to the corp server. Badge photos were lost. <I> **** Actions Taken **** IS contacted CompEng to do manual export and drop files to corp share folder. IS then did manual import process and recovered the images. No further action needed to resolve the issue today. The team has scheduled a meeting to look at ways to improve the process.
400219 | CR | 20191015 |  | 3 | Recommend reevaluation of TS 3.0.3 guidance in PPM 1.3.1 | N | N |  | N | NO | <D> **** Detailed Description **** Recommend reevaluation of TS 3.0.3 guidance in PPM 1.3.1. PPM 1.3.1 Step 4.1.17.b has TS 3.0.3 guidance that does match that of TS 3.0.3 bases. PPM 1.3.1 indicates that the power reduction is required within two hours where the TS bases requires this action within one hour. Recommend operations and licensing are involved in revising this guidance.
400220 | CR | 20191015 |  | 3 | SOP-PW-LU needs updated to reflect PWC-V-417 remains closed. | N | N |  | N | NO | <D> **** Detailed Description **** SOP-PW-LU needs updated to reflect PWC-V-417 remains closed. Per WO 02032541 cancellation notes the new transformers do not require supplemental cooling and I cannot find any procedure that references opening this valve. SOP-COLDWEATHER-OPS has a step to verify piping drained only. No plans in place to fix potable water leak identified under CR 393749/WR 29148830, WO 02032541 has been canceled. C-PWC-V-417 -001 currently hanging for config. control.
400221 | CR | 20191015 |  | 3 | Electric shop could not perform scheduled work | N | N |  | N | NO | <D> **** Detailed Description **** With Upcoming work on RHR-V-24B, electricians had a work order to repair/replace lighting in the RHR Valve room on RX 471'. After spending the morning performing a task preview, pre-job brief, Hi-Rad brief and staging tools and new light fixtures, electricians learned that the scaffold platform that was in place to support lighting had been removed the day before. There are currently four functional LED lamps installed in the Valve room that provide adequate lighting for RHR valve work next week. <I> **** Actions Taken **** Notified supervisor, write CR and closed out work order. <N> **** Equipment Description **** RX 471 M0/8.3 area lighting
400222 | CR | 20191015 |  | 4 | MCR - Loose Floor Board | N | N |  | N | NO | <D> **** Detailed Description **** There is a loose floor board behind H13-P800 in the main control room that is a potential tripping hazard. The floor board has been temporarily repaired, but requires more premenent attention. <N> **** Equipment Description **** Behind H13-P800
400223 | CR | 20191015 |  | 3 | (PCR) SOP-DOOR/HATCH-OPS revision needed. |  |  |  | N | NO | <D> **** Detailed Description **** Procedure enhancements needed for SOP-DOOR/HATCH-OPS. recommendations are in EDMS. <I> **** Actions Taken **** informed SSS
400224 | CR | 20191015 |  | 4 | Oil leak coming from tap changer on E-TR-M4 | N | N |  | N | YES | <D> **** Detailed Description **** While performing a system walkdown of the transformer yard it was discovered that there is oil leak coming from the E-TR-M4 tap changer. E-TR-M4 is not in-service and this CR is being written to document the condition. <I> **** Actions Taken **** Talked with EOs on walkdown and htey placed oil pads under the impacted leak. | 02-00-E-TR-M4
400225 | CR | 20191015 |  | 3 | 11.2.9.31 Op of The MG DMC-2000 ED | N | N |  | N | NO | <D> **** Detailed Description **** PPM 11.2.9.31, Operation of The MG DMC-2000 Electronic Dosimeter was identified during HP cycle training to need some enhancements in regards to setting electronic dosimeters for use by visitors. <I> **** Actions Taken **** Discussed with the HP Instructor, SME and took action to write the CR.
400227 | CR | 20191015 |  | 3 | HPI-12.48 Needs Enhancements |  |  |  | N | NO | <D> **** Detailed Description **** HPI-12.48, Handling of Contaminated/Potentially Contaminated Equipment for the Standards Laboratory needs enhancements. This was discovered during HP Cycle training. During reference of the procedure it was discussed that certain sections of the procedure lead to confusion as to actions that should be done with equipment while it is still at the station versus when it arrives at the Kootenai standard labs. <I> **** Actions Taken **** Discussed with HP Instructor and took action to write a CR.
400229 | CR | 20191015 |  | 4 | 70 TON GROVE CRANE DEFICIENCIES |  |  |  | N | NO | <D> **** Detailed Description **** A hydraulic leak was observed coming from the rear, bottom section of the cab which leaks onto the deck of the crane while in motion causing a slip hazard on the deck of the crane. . Some of the other issues are that the crane can â€™t be shut off while the boom is extended the computer become confused and you must manually retract the boom. The seat in the crane is damaged and is slanted. The air conditioner is also nonexistent. The leak has been secured and the crane is still functional at this time. <I> **** Actions Taken **** Initiated CR and notified the ENW rigging coordinator. Recommend meeting with all the shops that use this crane and capture any repairs that are not listed. <N> **** Equipment Description **** 70 ton Grove Crane
400231 | CR | 20191015 |  | 4 | SCBA harness Cal Sticker ID number did not match Unit ID |  |  |  | N | NO | <D> **** Detailed Description **** During the monthly inspection of Fire Brigade Station #1 equipment, WO 02140751, a SCBA Harness was pulled from service. This was due to a discrepancy between the ID number on the unit and the ID number on the Cal Sticker. These two numbers did not match. The Cal Sticker had an ID number 0067841 and the unit ID number was 0067979. The unit pulled from service passed all operational checks. The harness was replaced. The ID and Cal due date of the replacement was recorded in the work order. The work order does not specifically have the inspector verify that these two numbers match. <I> **** Actions Taken **** discussed discrepancy with Cal lab, HP Supervision and Rad Support personnel. Calibration Lab personnel were helpful in acquiring a replacement harness.
400232 | CR | 20191015 | CAQ | C | FLEX-GEN-DG5 Low Coolant Temperature | N | Y |  | N | YES | <D> **** Detailed Description **** FLEX-GEN-DG5 was found to have a low coolant temperature alarm locked in. Coolant temperature was verified low by temperature reading 57 degrees F on display screen and engine block was cold to the touch. The power cord was plugged into FLEX-GEN-DG5 and power was available to the outlet. The exact same issue has previously occurred in December 2017 (Ref: WR# 29140421). Low coolant temperature prevents performance of OSP-FLEX-Q705. (Scheduled to be completed 10/15/2019) Note: M208 key is required for entry into building 600. Key located in SSS key locker. <I> **** Actions Taken **** Informed supervision, wrote CR <N> **** Equipment Description **** Building 600, Key M208 | 02-CM-FLEX-GEN-DG5
400233 | CR | 20191015 |  | 3 | AED-MEC M974-2 Requires update |  |  |  | N | YES | <D> **** Detailed Description **** DEH-P-1A and DEH-P-1B do not match the layout of drawing AED-MEC-974-2. The mechanical drawing M974-2 shows that Pump/Motor DEH-P-1A to be on the left while looking west at the skid and DEH-P-1B to be on the right. During walk -down inspection of the DEH motors it was noted that DEH -P-1B was located on the left side of the skid while looking west and DEH-P-1A was loacted on the right side while looking west. This does not match AED-MEC-M974-2. <I> **** Actions Taken **** Notified Supervisor after walk-down, wrote CR. <N> **** Equipment Description **** Turbine Bld 471' elevation -D0,5.5- | 02-00-DEH-M-P/1A,02-00-DEH-M-P/1B,02-00-DEH-P-1A,02-00-DEH-P-1B
400234 | CR | 20191015 |  | 3 | Procedure enhancment SOP-RRC-START |  |  |  | N | NO | <D> **** Detailed Description **** SOP-RRC-START attachment 6.1 has the OPRM enabled region starting at 24.6% Reactor Power. This should be 19.6% for C25 based on the COLR. <I> Per 4.603.A7 for drop 3-7 (OPRM TRIP ENABLED) this alarm occurs when OPRM ENABLED parameters are satisfied (Values specified in the COLR). Current COLR values are: Section 5.1 - the applicable MODE for OPRM Upscale amplitude trip (Sp) and Confirmation Count (Np) is THERMAL POWER GE 19.6% RTP. Section 5.2 - THERMAL POWER value for Technical Specification 3.3.1.1, Required Action J.1 is THERMAL POWER < 19.6% RTP. Section 5.3 - OPRM Not Bypassed setpoints for SR 3.3.1.1.17 APRM Simulated Thermal Power (Pb) GE 24.6 % Recirculation Drive Flow (Wb) < 60 % What this means is the OPRM Upscale Trip must be OPERABLE when reactor power is GE 19.6%. For TSSR 3.3.1.1.17, when RRC drive flow is LT 60%, the OPRM must not be bypassed if APRM simulated power is GE 24.6%. Recommend sending to Reactor Engineering (RXENG) for disposition.
400235 | CR | 20191015 |  | 4 | Annual spare battery testing on E-EQ-B1/9 below 100% | N | N |  | N | YES | <D> **** Detailed Description **** Annual testing was completed on Spare batteries in Bldg 19 per WO# 02129890. The calculated capacity for E-EQ-B1/9 was 99.66%. Although the battery still meets all acceptance criteria of ESP-BSPARE-A101, a CR is being generated to trend the potential degradation of spare battery cells for HPCS-B1-DG3 battery. <I> **** Actions Taken **** write CR. . E-EQ-B1/9 contains the spare cells for HPCS-B1-DG3 battery. This is stored in bldg. 72, not plant installed. <N> **** Equipment Description **** E-EQ-B1/9 BLDG 19
400236 | CR | 20191015 | CAQ | C | Annunciator work performed by potentially unqualified person |  |  |  | N | NO | <D> **** Detailed Description **** On 10/13/19 there was a HPCS annunciator that was not working as expected and operations requested support to restore the annunciator. The urgency to restore the annunciator is that it is a 30 day action statement. The urgency was passed along to the weekend Supervisor and craft. The craft stated that they were uncomfortable and not familiar working on annunciators. After further discussion with operations it was determined that work on the annunciator would continue. The Supervisor was on location and a knowledgeable operations person wrote instructions in the WR. He also supported the task by getting parts and explaining the operation and function of the system. The Supervisor nor the craft were aware that there was an Annunciator qual (ELAR-EL000194). When this issue was discussed after the weekend some of the following concerns and hindrances were also brought up. How much electrical troubleshooting can be performed prior to the work requiring a qualified person? Where does a person look to see all the quals for a disciplines? How do you determine when or what qual is required for work? These concerns come up more with emergent work. WO tasks are planned with instructions and qualification assigned to the task. Walkdowns are performed to ensure the WO is correct, with the correct qualifications. Currently weekend work is staffed with Supervisors that are not as familiar with other disciplines work, instructions required or qualification requirements. WRâ€™s do not have assigned qualifications attached. Qualifications do not clearly state the scope of work that requires the qual, this mostly is determined by the disciplines that perform the work. The training for EL000194 purpose is for troubleshooting and repair of annunciators.
400238 | CR | 20191015 |  | 3 | Program Qualification Procedure Issues |  |  |  | N | NO | <D> **** Detailed Description **** Several issues with GBP-HR-52 â€œFirst Responder Programâ€ was noted that requires a procedure revision. It also was noted that SWP-OSH-04 â€œFirst Responder Programâ€ should have been superseded by GBP-HR-52, but was not and is essentially a duplicate of GBP-HR-52. <I> **** Actions Taken **** Notified the Occupational Health Supervisor and provided the detailed changes needed to GBP-HR-52. Notified the Performance Improvement Manager. The de-activation of SWP-OSH-04 is being worked on by Human Resources at this time.
400241 | CR | 20191015 |  | 3 | Incomplete PPM 10.2.53 update for AR CR 398177 resolution |  |  |  | N | NO | <D> **** Detailed Description **** PPM 10.2.53 R46 MnrR1 was recently issued and intended to include updates for resolution of AR CR 398177 (2019 DBAI (NRC) PPM 10.2.53 does not ref D-SCAFFOLD-455). However, the issued revision did not include all of the updates provided in the PPM 10.2.53 mark-up attached to the AR CR 398177 EDMS - mark-up page 1/2 was addressed while mark-up page 2/2 was not. Please update PPM 10.2.53 to include addressing of the AR CR 398177 PPM mark-up page 2/2. See the e-mail attached ot the EDMS of this AR CR 400241. <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
400242 | CR | 20191016 |  | 3 | PPM 1.3.76 Not Clear on SPV Risk |  |  |  | N | NO | <D> **** Detailed Description **** When evaluating for MEDIUM RISK per PPM 1.3.76: Major Rev. 057, page 45, item 8 states "Does the activity place an SSC in a configuration that would result in a unit trip or transient upon coincidental failure of a redundant system, train, or channel, e.g. RPS, ESF channel tripped and not bypassed, CRD or Stator cooling water pump removed from service? Reference SPV (Single point vulnerable) list for examples." Later when evaluating for HIGH RISK, see page 51, item 10., nearly identical wording "Does the maintenance activity place an SSC in a configuration that would result in a unit trip or transient upon coincidental failure of a redundant system, train, or channel, e.g. RPS, ESF channel tripped and not bypassed, CRD or Stator cooling water pump removed from service? Reference SPV list for examples. Answer NO if the activity is controlled by station procedure activities which have scheduled frequency of annual or less. (e.g. surveillance testing) SOPs are exceptions to the annual requirement." It appears the only difference between MEDIUM and HIGH risk SPV (Single point vulnerable) activities are "maintenance activity" for HIGH RISK vs "activity" for MEDIUM, and the allowance for "scheduled activities with a frequency of annual or less" can be considered NOT to be high risk. A freqency of 18 months, 24 months, multiple years, etc. are all LESS frequent than an annual frequency. Is this what is meant? I believe what is meant is if an activity is performed annually or more often (greater frequency) the risk may be considered to not be HIGH. Why would removing a CRD pump or SCW pump from service every year NOT be considered high risk when the impact of a failure of the remaining single point SSC is a plant trip? When we state "SOPs are exceptions to the annual requirement" does this mean SOP's are always HIGH RISK? Does it mean they are never HIGH RISK? If we do this at ANY frequency whether following WO instructions, a clearance order, an SOP or surveillance procedure, the impact is the same if the remaining single-point SSC fails. We need to understand what our philosophy on SPV activities truly is, whether performing SPV work more frequently actually reduces risk, and then make PPM 1.3.76 clear. As currently written I could determine the CRD-P -1A work in progress is actually MEDIUM risk. <I> **** Actions Taken **** No immediate actions required. . Note that per Attachment 9.8 of PPM 1.3.76, CRD pumps are listed as items that are plant transient initiating single point pieces of equipment and time with this SPV should be limited and treated as HIGH risk.
400243 | CR | 20191016 |  | 3 | Admin actions may detract from Nuclear Safety |  |  |  | N | NO | <D> **** Detailed Description **** Over the past few months there have been 2 instances where through either an ACMP or an ODMI the station has directed unnecessary redundant administrative work for the operating crews. In both examples Operations was asked to make more easily accessible or bundle log readings that they were already being taken and were available through the eSOMS logging program. This does not align with an Operations led philosophy, makes the station less efficient and erodes Nuclear Safety margin by, however briefly, distracting the operating crew. Examples ACMPs assigned for CR 400168 and CR 397437. <I> **** Actions Taken **** Wrote CR.
400244 | CR | 20191016 |  | 4 | TB441 water leak near CAS compressors getting worse. | N | N |  | N | YES | <D> **** Detailed Description **** The water leak from the ceiling above the CAS compressors is getting worse. See AR# 00399592 <I> **** Actions Taken **** Informed SSS and SM, wrote CR. <N> **** Equipment Description **** TB441 G-6
400246 | CR | 20191016 |  | 3 | GSB RP Office Inadequate TV Screen | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** It has been identified that the GSB RP Office Needs a larger TV Screen. It is too small and hard to see. This would make it easier for the RP Staff, to be actively engaged for the D15 and any Training. <I> **** Actions Taken **** Talked with RP Supervision. Initiated CR. <N> **** Equipment Description **** GSB
400248 | CR | 20191016 |  | 3 | Late eSoms entry | N | N |  | N | NO | <D> **** Detailed Description **** I&C technician changed vacation plans and did not notify supervision of his change resulting in a late eSoms entry. <I> **** Actions Taken **** Notified shop manager.
400249 | CR | 20191016 |  | 4 | CRD-P-1A piping does not configure to new pump | Y | N |  | N | YES | <D> **** Detailed Description **** During the reassembly of CRD-P1A seal circulating piping does not configure to new pump and the bearing housings on each end have 2 additional ports that that need pipe plugs. Additionally the Â½â€ stainless steel unions threads are degraded and could be a leak path when reassembled <I> **** Actions Taken **** Notified MCR, WWM, and planning. Initiated CR and returned package to planning for revision. <N> The differences with the newly installed pump are because the new pump was removed from CRD-P-1B, refurbished and then installed in CRD-P-1A. The work package was revised and the pump installation was completed and is currently running. No further action is necessary. | 02-00-CRD-P-1A
400250 | CR | 20191016 | CAQ | D | R-DOOR-R304 Latch mechanism disconnected | Y | Y |  | N | YES | <C> CR reopened to cross reference AR 393977 and additional WR 29145363, marked completion required box, then taken back to complete <D> **** Detailed Description **** The large handle latch/dog mechanism for R-DOOR-R304 is broken and feels s if it is disconnected from the operating rod. The handle flops around easily and can be rotated up such that it impacts the door frame which would prevent opening the door. The card reader, mag-latch assembly, and normal latch are all working properly to allow access and egress. R-DOR-R304 is both a fire and flood barrier and these functions do not appear to be affected by the broken dog mechanism as the door would pass the normal fire door surveillance. <I> **** Actions Taken **** Discussed with SM and Fire Marshall. Initiated barrier impairment for degraded door after discussion with the Fire Marshall. <N> **** Equipment Description **** RW 501 entrance into RB. | 02-00-R-DOOR-R304
400252 | CR | 20191016 | CAQ | C | PMID 17351 was not corrected as part of CR 00377412 | N |  |  | N | YES | <D> **** Detailed Description **** Currently PMID 17351 (AMA-CF-52 Carbon Filter Replacement) does not align with PM requirements within PPM 13.14.4 (Emergency Equipment Maintenance and Testing). Frequency is A02 within asset suite but is specified in PPM 13.14.4 as 96 weeks. AR-SMS 00400247 has been initiated to correct this. An evaluation was completed under CR 00377412 for this issue but was not corrected as the intention of corrective actions (AC1.4 & AC1.5) implemented. Current WO is 02118459. With a frequency of W96 next late date should be 06/25/2020. <I> **** Actions Taken **** Initiated CR and SMS. | 02-00-AMA-CF-52
400253 | CR | 20191016 |  | 4 | CRD-HX-2A deficiencies identified during PM | Y | N |  | N | YES | <D> **** Detailed Description **** During the license renewal inspection, it was identified that there was a tube that was plugged and some corrosion on the crossover plate gasket area, and there were no gaskets available for reassembly. New heat exchanger was procured and installed, all original piping was transferred over. See EDMS for pictures. <I> **** Actions Taken **** Notified the main control room, my supervisor and NDE for documentation on license renewal purposes, and initiated this condition report | 02-00-CRD-HX-2A
400255 | CR | 20191016 |  | 3 | R24LL 1.3.64 change to support WW entry | N | N |  | N | NO | <D> **** Detailed Description **** R24LL 1.3.64 change to support WW entry, update 1.3.64 step 2.1.11 to include wetwell access also. ref AR 399534 R24LL: SOP-ENTRY-WETWELL change. <I> **** Actions Taken **** wrote CR
400256 | CR | 20191016 |  | 4 | OCA camera UPS out of specification | N | N |  | N | NO | <D> **** Detailed Description **** While doing preventive maintenance on cameras, four OCA camera UPSâ€™s were found out of specification. All cameras are operable. Contact English or Bears with details. <I> **** Actions Taken **** Notified Security, IS leadership and system analyst. NCAQ-4 close to WR <N> **** Equipment Description **** OCA sites
400263 | CR | 20191016 |  | 3 | Remove E-DP-S1/2F from 1.20.10 Long Range Outage Plan | N | N |  | N | NO | <D> **** Detailed Description **** Currently E-DP-S1/2F is included on the long range outage plan 1.20.10. This component should be removed from 1.20.10 , as its maintenance can be performed online <N> The cross referenced SMS AR has the changes for this PM in the Attributes panel. I have notified the site PM coordinator. This CR is closed based on the cross referenced SMS AR.
400266 | CR | 20191016 |  | 4 | MT&E found out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #C011749 found OOT & Rejected- Unable to adjust. Not used during Calibration cycle. DEF #7348A written. No Plant Impact. <I> **** Actions Taken **** No Action Required.
400267 | CR | 20191016 |  | 3 | Upcoming WOA PM work for lube inspect | N | N |  | N | NO | <D> **** Detailed Description **** WOT 02135367 performs the 5 year lube and inspect of the WOA Manual EHOs in the 10/21/19 week. (due date of 11/8/19, late date 2/6/2021). WO 02119308-01 also is planned in the week to perform OSP-INST-X301 (due 10/7/19, Late date 2/2020) which strokes all the Manual EHOs as part of the 18 month surveillance to work in conjunction with the WOA inspect and lube rack pinion EHOs. CR 399524 (WR 29151862) was recently generated referencing the EHO spring alignment on WOA-V-51B being slightly out of pocket. Recommend upcoming Ops crew(s) review CR 399524 as part of the task preview for information. CR 399524 referenced that it is common for these type of valves (springs) to be slightly out of plumb. Currently WR 29151862/or WO 02151249 is not planned in the week to adress/perform anything other than the standard lube rack/pinion inspection/lube on WOA-V-51B. <I> **** Actions Taken **** Generated CR for informational purposes. <N> Email sent informing crews and WWM of information provided in this CR. No further action required. Copy in EDMS.
400268 | CR | 20191016 |  | 4 | Power cable not fully seated, no connection | N | N |  | N | YES | <D> **** Detailed Description **** A power cord was observed to be not fully seated in a PDU in 525RW comm room. Cord was traced to NET4-NETSW-02 redundant power supply. This switch provides network connectivity for level 4 cyber appliances. The switch has redundance supplies so its function is not currently impacted. The power cord on PDU-1A outlet 13 should be fully seated to restore power to the 2nd supply. This is not a reportable condition. This does not impact Operations. <I> **** Actions Taken **** Discussed with SM, Initiated CR and WR | 02-00-NET4-NETSW-02
400269 | CR | 20191016 | CAQ | C | MT&E found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0068239 Control Company Stopwatch- model 1051 was found OOT & adjusted within specs. EFIN to Evaluate 10 usages. DEF #7349A generated and will be attached to CR.
400270 | CR | 20191016 |  | 4 | (QA) Water puddle behind E-MC-1B | N | N |  | Y | YES | <D> **** Detailed Description **** During Quality waldown of the TB441. A quality auditor noted a small puddle of water directly behind E-MC-1B. There is industry OE on water intrusion into electric panels. SSS and SM were informed and were to follow up with inspections of the electric panel to ensure no water intrusion. | 02-00-E-MC-1B
400271 | CR | 20191016 | CAQ | C | DG-1 governor oil levels may be low OOS. | Y | N |  | N | YES | <C> MRT Change: CR 400271 moved from NON-CAQ Severity 3 to CAQ Severity C. Procedure for safety related equipment that could not be performed as written. <D> **** Detailed Description **** DG-1 govornor oil leves are at ,or slightly below, the upper sight glass marks. ( North and South Engines.) These sight glass gauges were replaced during the last overhaul of these engines, but the instructions for the required oil levels in the OPS-2 rounds are the same. Previously, the old sight glasses were full. Request further evaluation to determine if the oil levels are satisfactory or if the log notes have to be changed. See attached photos in EDMS. <I> **** Actions Taken **** Notified supervisors. <N> **** Equipment Description **** DG-1 This AR CR 400271 was written against EPN E-DG-1 which is DESIGN status (i.e., not currently a valid EPN). Added EPNs for the north and south engines for DG-GEN-DG1. | 02-00-E-DG-1
400272 | CR | 20191016 |  | 4 | Inadquate / Intermittent Lighting above PRM-SR-2 | N | N |  | N | NO | <D> **** Detailed Description **** Lighting directly above PRM-SR-2 is intermittent When lighting is out, makes it difficult to see in that corner <I> **** Actions Taken **** Informed supervisor Initiated CR
400273 | CR | 20191016 | CAQ | D | FP-P-110 weep hole excessive leakage. | N | Y |  | N | YES | <D> **** Detailed Description **** FP-P-110 had excessive leakage coming out of the cooling jacket water weep hole. See EDMS file for pictures. Unable to perform 15.1.4. Notified CRS and SM. FP-P-110 returned to standby lineup. <I> **** Actions Taken **** Initiated CR <N> **** Equipment Description **** Building 33 | 02-00-FP-P-110
400274 | CR | 20191016 |  | 4 | 2F No Continuity light is blinking on HTP-FP-5 | N | N |  | N | YES | <D> **** Detailed Description **** The 2F No Continuity light on HTP-FP-5 is blinking. Panel is located on the north wall in the CST pit. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** North wall in CST pit
400275 | CR | 20191016 |  | 4 | High level in CW-CT-1C | N | N |  | N | YES | <D> **** Detailed Description **** CW-CT-1C level is high, approximately 15.25". <I> **** Actions Taken **** Initiated CR <N> **** Equipment Description **** Located to the west of the East Electrical building | 02-00-CW-CT-1C
400276 | CR | 20191016 |  | 3 | PO.6 Milestone in jeopardy and turning yellow |  |  |  | N | NO | <D> **** Detailed Description **** he PO.6 outage milestone is in jeopardy for completion by the due date. This CR has been initiated per PPM 1.20.1 step 3.1.3.b. A recovery plan will be developed per PPM 1.20.1.
400277 | CR | 20191016 |  | 4 | PS-FI-1 Unresponsive | N | N |  | N | YES | <D> **** Detailed Description **** During quarterly corrosion coupon change out on PS-CPST -TSW/1, it was observed that PS-PI-1 was unresponsive to flow isolation or startup. Flow indicator is either OOS or flow is inadequate to produce response. <I> **** Actions Taken **** Flow restored to corrosion coupon station per PPM 12.9.10 following coupon change out . CR initiated for potentially out of service flow indicator. <N> **** Equipment Description **** TB 441', Aux Boiler room northeast corner. | 02-00-PS-FI-1
400278 | CR | 20191016 |  | 4 | CRD-P-1A oil leak on the outboard bearing housing cover | Y | N |  | N | YES | <D> **** Detailed Description **** During reassembly and oil add to bearing housing of CRD-P -1A WO 02131440-01 an oil leak was discovered on the outboard bearing housing cover from offsite refurbishment. Approximately 15 drop per minute. <I> **** Actions Taken **** Notified MCR, WWM initiated CR. Returned package to planning for revision to repair <N> See EDMS for picture | 02-00-CRD-P-1A
400279 | CR | 20191016 |  | 4 | CW-FI-2, -3, -4, -5 Unresponsive | N | N |  | N | YES | <D> **** Detailed Description **** It was observed during quarterly CW corrosion coupon station change outs that flow indicators CW-FI-2, CW-FI-3, CW-F-4, and CW-FI-5 were unresponsive to rack isolation or restoration. Flow may be restricted and inadequate to produce response or flow indicators have become fouled and are OOS. <I> **** Actions Taken **** Flow was restored to CW corrosion coupon station as directed per PPM 12.9.10. As prescribed flow rates were undetectable, supervision was contacted for direction. <N> **** Equipment Description **** TB 441', CW corrosion coupon station near condensate pumps. | 02-00-CW-FI-2,02-00-CW-FI-3,02-00-CW-FI-4,02-00-CW-FI-5
400280 | CR | 20191016 |  | 4 | CW-V-31 Leak | N | N |  | N | YES | <D> **** Detailed Description **** Corrosion coupon change out was performed per PPM 12.9.10. During valve manipulation to adjust line flow, CW-V-31 began to leak. <I> **** Actions Taken **** Efforts to further open or close CW-V-31 caused leaking to increase. Temporary catchment placed under valve. CR initiated. <N> **** Equipment Description **** TB 441', CW corrosion coupon station near condensate pumps. | 02-00-CW-V-31
400282 | CR | 20191016 |  | 4 | TMU-V-1 has a pin hole leak on the body of the valve | N | N |  | N | YES | <D> **** Detailed Description **** Water is dripping out of a pin hole leak on the body of the valve. Picture in EDMS <I> **** Actions Taken **** contacted OPS and supervisor | 02-00-TMU-V-1
400283 | CR | 20191016 | CAQ | C | Extent of Condition - FLEX Equipment Refuel Tank Levels | N | N |  | N | NO | <D> **** Detailed Description **** Extent of condition needs to be performed on FLEX equipment listed on TM-2185 table 3 and OPS SOPs and OSPs for administrative fuel oil levels (desired fill to level) and LCS requirements for functionality (i.e. what tank level would the equipment not be able to complete its 10 hour mission time before refueling per TM-2185). Ref AR 400145.
400285 | CR | 20191016 |  | 4 | SAFETY-Plant Installed Ladder Needs Antislip Replaced | N | N |  | N | NO | <D> **** Detailed Description **** The ladder going from the RX 501' to the RX 512', used to access the TIP mezzanine, needs the anti slip rung covers replaced. The top and bottom rungs have no covers and the rest are degraded. <I> **** Actions Taken **** Informed RP Supervision <N> **** Equipment Description **** Installed plant ladder located on the RX 501'
400286 | CR | 20191016 | CAQ | C | Re-evaluate Alternate On-line Noble Chem injection point | N | N |  | N | NO | <D> **** Detailed Description **** EC 8950 installed the Online Noble Chem system that injects platinum into the Feedwater system. As part of this modification, GE RICSIL 093 â€On-Line NobleChem (LNC) Injection Tap Obstructionâ€ was taken into consideration. The RICSIL was a preliminary notification and the issue was still being evaluated. To address the possibility of plugging, an alternate injection point into RWCU was included in the design. The use of RWCU for injection assumed that the temperature of RWCU will be cooler than the primary injection line and therefore, platinum plate -out due to hot surface contact is not expected to occur. Both Feedwater and RWCU are at 420 degF, so this assumption is incorrect. Therefore this assumption in the modification which was used to choose this injection point was incorrect. Also, the NobleChem vendor has seen plate -out of platinum on the process piping for several inches downstream of the injection point. RWCU-V-39 is just 3â€ downstream of the alternate injection point chosen in EC 8950 (RWCU-V-136 and 137). The platinum injection at this point is likely to affect this check valve. Downstream of the check valve are the flow orifice (used for delta flow indication) and RWCU-V-40 (LLRT valve). Based on this information, the choice of an alternate injection point at this point in the RWCU system needs to be reconsidered.
400288 | CR | 20191016 | CAQ | D | E-C1-7 AC "on" lamp is flickering. | N | Y |  | N | YES | <D> **** Detailed Description **** E-C1-7 AC "on" lamp is flickering. Please relamp degraded light bulb. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** rw-467 | 02-00-E-C1-7
400289 | CR | 20191016 |  | 3 | PPM 5.2.1 and 5.5.2 Enhancement to fill suppression pool | N | N |  | N | NO | <D> **** Detailed Description **** PPM 5.2.1 could be revised to include an alternate method to fill the suppression pool due to lowering suppression pool level to preclude the need to emergency depressurize. This new alternate method could be a change to PPM 5.5.2 to fill the suppression pool from SW-SYS-B via a cross connect to RHR-B and then through wetwell sprays and would be a backup to fill via 5.5.23 with HPCS if HPCS is unavailable. <I> **** Actions Taken **** Informed OPS EOP Coordinator.
400290 | CR | 20191016 |  | 4 | SCH-V-709A leaking and GSB chiller low corrosion inhibitor | N | N |  | N | YES | <D> **** Detailed Description **** During the monthly sample of the GSB chiller for corrosion inhibitor the sample point valve was found to have a one milliter/minute leak. The corrosion inhibitor was below spec and in CCW action level 2 which requires restoration to normal values within 30 days. The valve will need to be fixed prior to the chemical addition or the chemicals will just go down the drain with the leak. <I> **** Actions Taken **** Contacted Chemistry Supervision, MCR and chemistry system specialist. initated a work request to get valve fixed <N> **** Equipment Description **** GSB basement Service building Chiller needs valve fixed | 02-00-SCH-V-709A
400291 | CR | 20191016 |  | 4 | Service Building chiller need corrosion inhibitor addition | N | N |  | N | NO | <D> **** Detailed Description **** GSB Chiller needs corrosion inhibitor addition and sodium hydroxide add to increase pH. Analysis performed on 10-16 -19 put the chiller in CCW action level 2 which requires correction within 30 days. There is a leaking valve off SCH-V-709A which is the chemistry sample point. it is roughly a mL/min. It needs to be fixed prior to addition so the chemicals don't just go down the drain again. See AR#400290 <I> **** Actions Taken **** Notified MCR, chemistry supervision and chemistry system specialist <N> **** Equipment Description **** GSB basement SBChiler
400293 | CR | 20191016 |  | 3 | Update procedures for increased CBP lube oil cooler limits | N | N |  | N | NO | <D> **** Detailed Description **** This is a documentation issue only. Evaluation under AR 310551 determined that the maximum Condensate Booster Pump Lube Oil Cooler outlet temperature could be increased from 110 deg F to 120 deg F, and SOP-COND-OPS and SOP-COND-START were update to reflect the change. SOP-COND-SHUTDOWN, SOP -COND-FILL and SOP-TSW-FLUSH should also be updated to reflect the change in acceptable operating temperature. <N> AR CR 310551 went to COMPLETE status in 2015.
400294 | CR | 20191016 |  | 3 | Update AED SPC 350 for increased CBP lube oil cooler limit | N | N |  | N | NO | <C> MRT Change: CR 400294 moved from CAQ Severity C to NON-CAQ Severity 3. This is a design spec "SPC" and not a drawing. As long as it is non-safety related these are Non-CAQ. <D> **** Detailed Description **** This is a documentation only. Evaluation under AR 310551 determined that Condensate Booster Pump Lube Oil Cooler outlet temperature could be increased from 110 deg F to 120 deg F, and SOP-COND-OPS and SOP-COND-START were update to reflect the change. AED SPC 350 should also be updated to reflect the change in acceptable operating temperature. <N> AR CR 310551 went to COMPLETE status in 2015.
400295 | CR | 20191016 |  | 3 | Continued challenges to Operator Fundamentals |  |  |  | N | NO | <D> **** Detailed Description **** eSoms iPads continue to be unreliable at synchronizing with eSoms database. This directly impacts operators' abilitiy to identify degrading parameters and equipment trends. <I> **** Actions Taken **** Requeste d help from Computer Services with no reliable success. <N> The eSOMS upgrade is being performed in XREF AR 399247 no further action is warranted under this CR. Supervisor for ITBOA approves to be closed to teh XREF.
400296 | CR | 20191016 |  | 3 | eSoms station has wrong units |  |  |  | N | NO | <D> **** Detailed Description **** Seq 85, Sta 86 (RCC HX INLET TEMP) in CRO1 shiftly logs has PSIG for units. The correct units are degrees Fahrenheit. .
400297 | CR | 20191016 | CAQ | D | Invalid level recieved on Pumphouse 1A |  |  |  | N | NO | <D> **** Detailed Description **** Individual attempted to gain access into a vital area in which he did not have access. The area was swept by security and the individual was coached. <I> **** Actions Taken **** Security supervision notified. Area was swept and walked down. CR generated.
400302 | CR | 20191017 |  | 4 | M&TE Rejected | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0064139 IMI Sensors Hand-Held Shaker- model 699A02 was Not used during Calibration cycle. No Plant Impact. Rejected- No Longer Needed per Engineering. DEF #7351A writtn. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
400303 | CR | 20191017 |  | 3 | Additional risk with no diesel driven pumps available | N | N |  | N | NO | <C> MRT Change: CR 400303 moved from CAQ Severity C to NON-CAQ Severity 3. <D> **** Detailed Description **** The station is in a circumstance that does not appear to be accounted for in PPM 1.3.85 On-Line Fire Risk Mitigation or in LCS RFO 1.10.1. With both diesel driven fire pumps unavailable, loss of non-vital power coincident with a fire would result in a situation where there would be no pumps supplying fire-fighting water. The loss of FP-P-110 results in the secondary water supply being non-functional and entry into RFO 1.10.1.A and B, however the RFO 1.10.1 basis does not require the primary water supply to have a functional diesel driven fire pump even if FP-P-110 is not available. For example, a fire in the transformer yard could result in a plant trip, loss of non-vital power, and no pumps supplying the fire protection ring header. Recommend evaluating if this scenario is, in fact, accounted for in probabilistic risk assessments or conducting a risk assessment and adjusting plant procedures and/or Licensee Controlled Specifications accordingly. <I> **** Actions Taken **** CR generated
400305 | CR | 20191017 |  | 4 | FLEX Training Needed (Twice a Year) | N | N |  | N | NO | <D> **** Detailed Description **** -It would be beneficial for FLEX training to be offered twice a year to ENW HP Technicians and Chemistry Technicians instead of just Annually. Getting 3-4 hours of training a year on the Front end Loader and Excavator is not sufficient. This training should be considered to be given/offered twice a year which would help us gain better efficiency if there was a need to use these machines. It would also make us more comfortable on these to operate them twice a year, which would also increase our personal safety if we had to actually use these in a Real Emergency. It should also be a limited number of students per training class (3 a session) to give us an appropriate amount of seat time. <I> **** Actions Taken **** -Initiated Condition Report <N> Benchmarking has been performed in the industry for training on FLEX debris removal equipment. Columbia performs this training on a frequency that is the highest in the industry. No changes to the freequency are required. Familiarity with the equipment is what is expected. To supplement this expectation quick cards are provided with the equipment to assist in the operation. Facilities, HP's and Chemistry technicians have provided information in the past that they cannot afford the resources to perform this training more than once per year with competing activities. Therefore, this CR should be trended with no further action required.
400306 | CR | 20191017 |  | 3 | Actions for TREQ 18-0141 | N | N |  | N | NO | <D> **** Detailed Description **** Non-training solutions for TREQ 18-0141 need to be generated. 1)Recommend generating a brefing (powerpoint or other communication) with management expectations for validating work hours in eSoms. 2) generate a "cheat sheet" for the craft to use with instructions for logging into and validating eSoms work hours. <I> **** Actions Taken **** discussed these actions with maintenance manager and completed performance analysis on TREQ 18-0141.
400307 | CR | 20191017 |  | 4 | MT&E found out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0064069 Hytorc Hyd. Torque Wrench- model Stealth 4 found OOT & adjusted. Not used during Calibration cycle. DEF #7350A generated. No Plant Impact. <I> **** Actions Taken **** No Action Required
400308 | CR | 20191017 |  | 3 | PWC-P-4A and PWC-P-4B are currently caution tagged | N | N |  | N | YES | <D> **** Detailed Description **** PWC-P-4A and PWC-P-4B are currently caution tagged with the following note PWC-P-4A/B have insufficient discharge pressure to fill the RB air wash basin without PWC-P-1, PWC-P-2 & PWC-P-3 running. Run only as needed. CR 349680. I cannot find an active work request that will fix this issue. Caution tags have been hanging since 2016. WO02081544 for PWC-P-1 replacement@ complete. If no other pumps are being replaced and this is normal it may be more appropriate to have a note placed in SOP-WARMWEATHER-OPS stating this is normal instead of leaving caution tags hanging. | 02-00-PWC-P-4A
400311 | CR | 20191017 |  | 3 | Quarterly CORC Caution Clearance Audit 10CFR50.59 | N | N |  | N | NO | <C> MRT Change: CR 400311 moved from CAQ Severity C to NON-CAQ Severity 3. <D> **** Detailed Description **** Quarterly CORC Caution Clearance Audit 10CFR50.59 The Quarterly CORC Caution Tag Audit (WO 02141536) has documented the caution clearances that have been hanging for GE 30 days. There are 13 new Caution clearances added to this total since the last audit: C-IRM-RMS-S6 -002A, C-BS-V-39A -001, C-CF HEAT TRACE-001, C-HV-V-30E -001, C-FP-SYS-P85 -001, C-HV-V-31A -001, C-IR -V-IR8/V6 -001, C-MD-V-DVS -001, C-MS-V-115B -001, C-RWCU -V-32 -001, C-SW-P-1B -002, C-TEA-FN-1C -001, C-CW-PHIC-1 -002. <N> Request Technical Services/Systems Engineering Manager (or designee) to determine whether a 50.59 review is required.
400312 | CR | 20191017 |  | 4 | CRD-P-1A inboard Bearing cooler leak | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of CRD-P-1A PMT WO 02131440-08 it was discovered that the inboard bearing cooler is leaking 1 drop every 2 seconds. This is a factory rebuild issue. The gasket will need to be replaced. <I> **** Actions Taken **** Notified MCR, WWM, planning initiated CR and WR | 02-00-CRD-P-1A
400313 | CR | 20191017 |  | 4 | Emergency Lighting Panel has a red blinking service light. | N | N |  | N | YES | <D> **** Detailed Description **** Emergency lighting panel ELP-7AB/11 has a red blinking service light in. Appears to be a battery fault. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** SW stairwell in the TB.
400314 | CR | 20191017 |  | 3 | PPM 1.10.11 reference to RPI-3.0 missing. | N | N |  | N | NO | <D> **** Detailed Description **** PPM 1.10.11 and RPI-3.0 have a step that conflict with one another. PPM 1.10.11 Step 5.5.2.a.1 and RPI-3.0 Att. 7.3 Step 1.c both direct an action be issued but differ on type of assignment and title of individual to assign to. . Suggest the step be removed from PPM 1.10.1 and consideration given to whether the step is required in the RPI. . This is a documentation only issue. Suggest 3 / AR-LIC to correct the discrepancy. <I> **** Actions Taken **** Discussed the issue with the Regulatory Affairs Manager and Performance Improvement Supervisor. Action will be created per RPI-3.0 direction at this time.
400315 | CR | 20191017 |  | 4 | Unable to complete tower cleaning due to crane failure | N | N |  | N | NO | <D> **** Detailed Description **** During WO 02119845, the crane used to support the cleaning of the cooling tower distribution deck experienced mechanical difficulties. As a result, cleaning on the last remaining cooling tower, CW-CT-2B, was not fully completed. This CR has been initiated in accordance with SWP-PRO-01, to document the inability to complete the entire scope of the PM. The CW cooling tower distribution troughs were thoroughly cleaned in R24 and have accumulated very little sediment/debris in the interim. Delaying the cleaning of CW-CT-2B 6 months until the next PM occurrence will not challenge the capacity of the tower distribution deck or adversely impact the capability of the cooling tower to perform its design function. <I> A small amount of hydraulic oil was spilled during this mechanical failure, Environmental estimates 1 quart. Not reportable per GBP-ENV-18.
400316 | CR | 20191017 |  | 3 | CRD-P-1A PMT Instructions did not meet expectations | N | N |  | N | NO | <D> **** Detailed Description **** The work instructions for the CRD-P-1A (Control Rod Drive Pump 1A) PMT (WO 02131440-08) did not meet the expectations of the station for implementation. We should expect that we provide craft and Operations clear and unambiguous work instructions that defines/describes who is doing what and when. This is especially true when we are performing High Risk work, as is the case with CRD-P-1A. The work instructions that were provided missed the mark in several areas. A few examples (but not all) include: * The Electricians did not have instructions to take starting currents as called out for in the PMT (Prereq 3.6). * A Test Engineer was called for in Prereq 3.10, but there was no support task for Engineering to provide a person to fulfill the duties nor instructions on their responsibilities. * It was not clear who would be reviewing the data to verify performance of the pump that would allow the placement of CRD-P-1A into normal service (Task 4.11). * The PMT was assigned to Mechanical craft, even though it required a lot of coordination between many groups that would not normally be provided by a shop. * The PMT required data to be taken by 2 EOs and 1 RO. These resources were not accounted for in the Resources sections of the Work Instructions. <I> **** Actions Taken **** This issue was discussed as a Thumbs Down by Work Control as a failure to Meet Commitments at the Daily Production Meeting and the OFM. The Work Week Manager is working with Operations, Engineering, and Maintenance to ensure that we complete the PMT as required to ensure functionality of CRD-P-1A.
400318 | CR | 20191017 |  | 4 | Chemistry Dose budget excedded for September 2019 | N | N |  | N | NO | <D> **** Detailed Description **** The Chemistry dose budget was exceeded for September 2019. The dose estimate was 153 mR with a goal of 138 mR. The Chemistry department received 208 mR. The extra dose can be attributed exclusively to the work associated with PSR-SR-49 restoration following valve repair on PSR-V-640.
400320 | CR | 20191017 |  | 4 | CRD-P-1A needs vibration monitoring locations identified | N | N |  | N | NO | <D> **** Detailed Description **** electricians obtained vibration data on CRD-M-P-1A per work order 02131440. It is typical to have rotating equipment marked with either a magnetic disc or twist on connector to connect vibration test equipment to. the discs/twist on base should be installed to ensure consistent data is obtained on future Work Orders. Only the inboard and outboard pump locations are required. Gear box and Motor points are already identified. <I> **** Actions Taken **** Notified Vibration engineer to validate test locations and generate CR/WR <N> **** Equipment Description **** CRD-P-1A R422 N6/4.1
400322 | CR | 20191017 |  | 3 | I&C work orders for need revised | N | N |  | N | NO | <D> **** Detailed Description **** The new halogenation/dehalogenation skids are continuously online with no requirement to secure blow down. Typically I&C calibrations were performed during the time blowdown was secured in the past. The new system no longer requires blowdown to be secure to perform calibrations. Work orders will require additional steps to ensure permitted required data is maintained during I&C calibrations. Instruments affected are per NPDES-01 Table 7.3. Recommend assignment to planning, planning can contact originator for further information. <I> **** Actions Taken **** Spoke with Chemistry and Enviromental Groups Discussed with Manager and planning Wrote CR
400324 | CR | 20191017 | CAQ | C | MS-RIS-610C is non-functional | N | Y |  | N | YES | <D> **** Detailed Description **** Card replacement per WO 02150314 did not fix the screen issue. Since maintenance was performed on MS-RIS-610C and post-maintenance testing cannot yet be complete the channel for MS-RIS-610C remains non-functional and need to be placed in trip condition to comply with RFO 1.3.6.3.A. <I> **** Actions Taken **** CRS/SM Informed | 02-00-MS-RIS-610C
400325 | CR | 20191017 |  | 3 | Respiratory Protection Inventory Gap | N | N |  | N | NO | <D> **** Detailed Description **** Washington Administrative Code Chapter 296-842 (17015) requires that emergency respirators have inspections documented using the "serial number ... or other identifying information." Currently, respirator masks are inspected monthly. Some have serial numbers, but a large portion do not, and the work packages used to perform this task direct the identifier section to be marked "N/A" if a serial number is not present . This does not appear to be in compliance with the intent of the code, which is to ensure that an individual can verify a specific mask has been inspected. <I> **** Actions Taken **** Discussed with Health Physics staff.
400327 | CR | 20191017 |  | 4 | Late eSOMS entry in Maintenance | N | N |  | N | NO | <D> **** Detailed Description **** individual was asked to work 0600-1800 on Mon- Wed and assumed he was working those hours on Thursday as well but was not entered into esoms. <I> **** Actions Taken **** Updated his esoms hours and advised his supervisro of the situation.
400328 | CR | 20191017 |  | 3 | Rad Monitors Display Incorrect Time | N | N |  | N | YES | <D> **** Detailed Description **** Multiple rad monitors display the incorrect time. Rad monitors with incorrect times displayed are: CMS-RIS-27A/B CMS-RIS-12A/B TSW-RIS-5 TEA-RIS-13 WEA-RIS-14 OG-RIS-601A/B The drift on each rad monitor varies, some are off by 20 minutes and others by over 2 hours. Incorrect times inject risk into interpreting the data throughout the database screens, which could lead to an incorrect assessment during troubleshooting or walkdowns. There is no governing document, PM, or procedure to verify if the time displayed is accurate. Reccomend updating surveillances with a step to validate and correct time. (See Docs for recommended) <I> **** Actions Taken **** Informed Supervisor Spoke with shop supervisor Initiated CR <N> Approximate Time Differentials From Current Time: CMS-RIS-27A â€“ 3 Hours CMS-RIS-27B â€“ 1 Hour & 15 Mins CMS-RIS-12A â€“ 1 Hour CMS-RIS-12B â€“ 2 Hours TSW-RIS-5 â€“ 1 Hour TEA-RIS-13 â€“ 1 Hour & 45 Mins WEA-RIS-14 â€“ 2 Hours OG-RIS-601A â€“ 20 Mins OG-RIS-601B â€“ 2 Hours | 02-00-CMS-RIS-12A,02-00-CMS-RIS-12B,02-00-CMS-RIS-27A,02-00-CMS-RIS-27B,02-00-OG-RIS-601A,02-00-OG-RIS-601B,02-00-TEA-RIS-13,02-00-TSW-RIS-5,02-00-WEA-RIS-14
400329 | CR | 20191017 | CAQ | D | EPN SW-V-70B showing retired status in Asset Suite | N | N |  | N | NO | <D> SW-V-70B is showing as retired status in Asset Suite and should be at active status. SW-V-70B is scoped into the IST program and is regularly tested under OSP-SW/IST-Q702. The motor operator for this valve has its motor control center locked in the OFF position. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review. Engineering has already made changes to EPN status to match drawings and align with EC 12165. . Issue is resolved and was corrected upon identification. CR was progressed ahead of initiator being able to cancel the CR. No further action necessary.
400330 | CR | 20191017 | CAQ | B | TR-B Inoperability window missed | Y | N |  | N | NO | <C> MRT Change: CR 400330 moved from Severity C to Severity B. RISK: Medium. CAUSE: Complex. Severity: B/OPSCM Investigation Template required. <D> **** Detailed Description **** TR-B inoperability window was missed the CRS when BPA took down the Benton 115KV line for planned work WO 02137607. BPA called the Main Control Room at 0800 on 10/17/2019 reported they were performing â€œswitchingâ€ on the 115KV line. An RO fielded the phone and reported it to the CRS. Both the RO and CRS did not understand this to mean that the Benton 115KV line would be supplied from White Bluffs. <I> **** Actions Taken **** TR-B declated inoperable. TSAS 3.8.1.A entered.
400331 | CR | 20191017 |  | 3 | RWM and RMCS System Descriptions need to be updated | N | N |  | N | NO | <D> **** Detailed Description **** SD000154 and SD000148 need to be updated to reflect the change in power supplies to the RWM, RPIS, RDCS, DMM and related indications. Most of these items are now powered by US-PP (IN-1). System text and Learning Objectives need to be updated. Also SD000148 needs to be updated to reflect the deactivation of RSCS (Learning Objective). <I> **** Actions Taken **** Discussed with Operations Training.
400332 | CR | 20191017 |  | 4 | Hydraulic leak on Crane | N | N |  | N | NO | <D> **** Detailed Description **** While performing the cleaning on CW-CT-2B, with a suspended load in the air, the crane used for suspending the 8â€ pipe sprung a leak in the hydraulic system. The crane operator immediately lowered the 8â€ pipe and transferred the crane to the mechanics shop for repair. Approximately 1 quart of the hydraulic fluid was spilled to the ground. The majority of the fluid was contained on the deck of the crane. The control room was notified of the spill as well as E&RP. Approximately 100 feet of 6â€™ hose, 10 feet of 8â€ pipe and a 3â€™X3â€™X3â€™ metal basket with the hose bracket inside was left on the top of CW-CT-2B. These item will have to remain on cooling tower until the crane is available to remove them. A FME walkdown was performed on all cooling towers to make sure no other items were left on top of the towers. <I> **** Actions Taken **** Notified control room and E&RP of the leak
400333 | CR | 20191017 |  | 3 | Fire Brigade inventory discrepancies Bldg 82 | N | N |  | N | NO | <D> **** Detailed Description **** (2) SCBA Harness in Bldg. 82 has calibration due dates prior to the next inventory. (1) 30 psi gage found broken. <I> **** Actions Taken **** Notified RP Supervision and STD Lab Technician Harnesses will be replaced when calibrated harnesses become available. New 30 psi gage was ordered from the warehouse and was delivered to the Standards Lab for calibration. It will be replaced when calibration is complete.
400334 | CR | 20191017 | CAQ | D | Benton 115Kv line to CGS LT 115kV during BPA maintenance | Y | N |  | N | NO | <D> **** Detailed Description **** Benton 115Kv line to CGS LT 115kV during BPA maintenance. Per OSP-ELEC-W101 7.1.11c this condition report is being written. Currently E-TR-B is powered from the White Bluffs 115kV line and indicates 118kV for all 3 phases. 7.1.11c directs initiating a CR to engineering for trending/evaluation. Expected maintenance time is 10/17/19 at approx 1600-1700. <I> **** Actions Taken **** Wrote this CR per procedural direction. <N> E-TR-B was inoperable due to planned BPA maintenance at the time the voltage checks were performed. No engineering evaluation is required.
400336 | CR | 20191017 |  | 4 | Gamma Vision - Faulty Analysis Engine from Vendor | N | N |  | N | YES | <D> **** Detailed Description **** Following vendor installation of Gamma Vision version 8.10 (FW-SOFT-TECH-GVISION) chemistry personnel saw an unusual trend in sample results. The vendor was contacted and able to determine that a faulty analysis engine had been provided during installation, causing the software to not correctly apply background subtraction to gamma spectroscopy results. The nature of the error caused by this faulty analysis engine is conservative. The loss of background subtraction from samples would potentially cause the misidentification of licensed material in samples where no material was actually present. The background rate in the chemistry counting room is at a low enough level that only extremely low activity samples measured for extended count times (in excess of one hour), such as those measured for free release, would be impacted. Chemistry responded to all identified positive results as though real while attempting to determine the cause of the unusual results. The vendor has provided the necessary software solution. <I> **** Actions Taken **** Spoke with chemistry supervisor and RPM, and contacted vendor. Corrected analysis engine with assistance from vendor | 02-00-SOFT-TECH-GVISION
400337 | CR | 20191017 |  | 3 | Quarterly CORC Danger/Local Clearance Audit 10CFR50.59 | N | N |  | N | NO | <C> MRT Change: CR 400337 moved from CAQ Severity C to NON-CAQ Severity 3. <D> **** Detailed Description **** Quarterly CORC Danger/Local Clearance Audit 10CFR50.59 The Quarterly CORC Danger/Local Tag Audit (WO 02141534) has documented the Danger/Local clearances that have been hanging for GE 30 days. There are 2 new Local clearances added to this total since the last audit: L-CTMA-AC-1 -001 and L-PWC-SV-301 -001. There are 2 new Danger clearances added to this total since the last audit: D-FP-ENG-1 -001 and D-FP-ID-85/3 -001. Request Technical Services/Systems Engineering Manager (or designee) to determine whether a 50.59 review is required.
400338 | CR | 20191017 | CAQ | D | Standard found out of tolerance | N | N |  | N | NO | <D> Calcode# 0066976 MKS Model 6690A11TRA Head to Torr was found out of tolerance and adjusted to manufacturers specifications. <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
400339 | CR | 20191017 |  | 3 | Unqualified Individual Performed ERO Duties | N | N |  | N | NO | <C> MRT Change: CR 400339 moved from CAQ Severity C to NON-CAQ Severity 3. <D> **** Detailed Description **** An individual previously qualified EPBI (TSC Manager Secretary) assumed the duty cycle and participated in the July 2019 drill while unqualified. The individual had the qualification inactivated in Sept. 2018 prior to beginning an extended leave of absence. Upon returning to work in March 2019, the qualification was not reactivated and two CBT courses (EP000243 and EP000379) expired while the individual was away on leave (12/31/18). <I> **** Actions Taken **** Reactivated qualification, notified individual of required courses to be taken prior to assuming the watch for the upcoming duty cycle and notified EP Manager.
400341 | CR | 20191017 | CAQ | D | Quality records transmittal not timely | N | N |  | N | NO | <D> **** Detailed Description **** Two completed Quality Surveillance records stored in approved interim storage were not transmitted to permanent storage within six months as required by QAP-ASU-03, Quality Assurance Records. Requirement: â€¢ QAP-ASU-03, step 2.2.4 states: â€œAfter the in-process record file is completed, the file shall be kept in an interim storage status until final transmittal to permanent record storage files. Due to business needs and time needed for assembly of files, record files may be kept in an interim storage status up to six months.â€ Factual Basis: â€¢ Surveillance report SR-18-17 was completed on 6/6/18 and SR-18-19 was completed on 9/5/18. Both were retained in interim storage for greater than six months, contrary to the requirement in QAP-ASU-03. <I> **** Actions Taken **** Completed surveillance files SR-18-17 and SR-18-19 were transmitted to permanent storage on 10/17/19. . Recommend Severity D assignment to AR-QUALITY. <N> **** Equipment Description **** N/A
400343 | CR | 20191017 | CAQ | D | Siren D4 Vault found open | N | Y |  | N | NO | <D> **** Detailed Description **** During a siren inspection tour, the vault door for siren D4 was found in the fully open position consistent with being blow open by the wind. Latch was found to be sticking upon closing it and is suspected to be the cause. Performed a visual inspection of the vault to verify no damage had occurred which was confirmed. Closed the vault and obtained peer verification to confirm it was latched. D5 may have a similar problem with the latch and I verified it was fully closed and latched before leaving the site. <I> **** Actions Taken **** Notified EP of findings and plans to address the isssue. Recommend NCAQ for evaluation for facilities to evaluate the latch. <N> **** Equipment Description **** Siren Site D5 and D6 . The title is incorrect the correct sirens are D5 and D6. Siren performance was not affected.
400344 | CR | 20191018 |  | 3 | EWP Problem - WO 02152187, FP-ENG-110 Leak Repair |  |  |  | N | NO | <D> **** Detailed Description **** Unable to take WO 02152187 task 02 HC D-FP-P-110 -003 or WO 02152187 task 03 LC D-FP-P-110 -003 to FINISHED in EWP. <I> **** Actions Taken **** Verified work was done and took these tasks to FINISHED in ASSETSUITE. <N> eWP SME contacted Shift Manager and was given approval to close out tasks in Data Glance. This task required Ops authorization (in Ops view) to advance the Work Order status.
400345 | CR | 20191018 | CAQ | D | FP-ENG-110 discharge pressure outside range | N | Y |  | N | YES | <D> **** Detailed Description **** During FP-ENG-110 run the discharge pressure was 162#, given range was ~120-160# - WO 02140395; PPM 15.1.4 | 02-00-FP-ENG-110
400346 | CR | 20191018 |  | 3 | Enhance OI-53 and OSP-ELEC-W101 |  |  |  | N | NO | <D> **** Detailed Description **** See cross referenced CR 265318 and EDMS document. The wording (and lack of wording) in both OI-53 and OSP-ELEC -W101 could lead a person to conclude that supplying TRB from White Bluffs through the Benton - 451B#1 115 kV line and Hanford 2 Tap meets the Operability criteria for TRB. TS 3.8.1 bases states the backup offsite power supply "is from the 115 kV Benton substation". The Benton and White Bluffs substations are tied together through B3S4. The feed from White Bluffs then goes through the Benton - 451B#1 115 kV line and the Hanford 2 tap. Our position has been and continues to be that this path does NOT satisfy TRB Operability. This needs to be directly stated in OI-53 and OSP-ELEC-W101. <I> **** Actions Taken **** Recommend assignment to OPS procedures. Do not allow closure again with no action.
400347 | CR | 20191018 |  | 3 | SOP-ELEC-115KV-OPS needs enhancement. |  |  |  | N | NO | <D> **** Detailed Description **** SOP-ELEC-115KV-OPS needs enhancement. A note should be added immediately before step 7.1.3 to expect P800.C4.4-5 XFMR TR-B UNDERVOLTAGE and P800.C4.6-5 115KV OIL CKT BKR OPEN alarms. Also, in step 7.1.4, Munro should be notified at telephone number 509-465-1837 instead of Dittmer being notified to obtain a terminal clearance. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR.
400349 | CR | 20191018 |  | 3 | RX 522 dose rate increase found during monthly survey | N | N |  | N | NO | <D> **** Detailed Description **** Dose rates on NW side of RX 522, shielded area increased from 3 to 8 mr/hr G/A (survey #20190919-3) to 10-15 mr/hr G/A with contact dose rates of 40 mr/hr(survey # 20191018 -1). Area posted HRA CA. Possible cause may be noble metals injection. <I> **** Actions Taken **** Documented survey
400350 | CR | 20191018 |  | 3 | Fastenal Machine Failed to Vend | N | N |  | N | NO | <D> **** Detailed Description **** The Fastenal machine in the breezeway between the Deschutes building and the Willamette building failed to vend the rubber lanyard in position 57 when I presented my Fastenal badge card and selected item 57 for vend. The machine provided a message that the item SKU was empty. Given that the response was different than expected (trigger), I stopped, verified both visually and through the use of olfactories the presence of a rubber lanyard in position 57, used the HU tool touch, read, read and the remade my selection. The result was the same. Recommend non-CAQ assignment to the contract lead to reach out to Fastenal to resolve. <I> The machine would not allow me to cancel my order, so I just got some batteries instead since I figured I'd use them in my pager prior to ERO duty cycle.
400351 | CR | 20191018 |  | 4 | Delays in hanging D-TRB-GND4160-001 | N | N |  | N | NO | <D> **** Detailed Description **** Delays were encountered with hanging D-TRB-GND4160-001 due to the craft expecting BPA to have been here at 0600 to install high side grounds per D-TRB-G115-001. The craft were expecting that D-TRB-G115-001 would be their assurance that E-TR-B was de-energized, not the BPA terminal clearance. In discussion with the WWM BPA had been requested to arrive at CGS at 0700 and the plan the WWM and SM had discussed the day before was to install the ground buggy at 0630 before BPA arrived. <I> **** Actions Taken **** Discussed with WWM and Transformer Yard Coordinator to capture lessons learned.
400352 | CR | 20191018 | CAQ | D | Received Rod Accumulator Trouble Alarm for CRD-HCU-0231 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-0231. Alarm was for high water level. | 02-00-CRD-HCU-0231
400353 | CR | 20191018 | CAQ | D | Rod Accumulator Trouble Alarm CRD-HCU-0231 | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-0231 was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear | 02-00-CRD-HCU-0231
400354 | CR | 20191018 | CAQ | D | E-CB-B/8 counter | Y | Y |  | N | YES | <D> **** Detailed Description **** during performance of 02112832-08 discovered counter not consistantlly counting. (advanced from 607 to 609 after cycling 10 times) <I> **** Actions Taken **** informed supervisor initiated CR, will be addressed in task 01 <N> The counter linkage was adjusted under WO 02112832-01 and is working SAT. This CR for trending only. | 02-00-E-CB-B/8
400355 | CR | 20191018 | CAQ | C | Evaluate the reliability of FP-P-110 and FP-ENG-110 | N | Y |  | N | YES | <C> Re-opened with the concurrence of J. Twomey and upgraded it from a D/TRNDREP to a C/TEFP. <D> **** Detailed Description **** A review of pervious 2 years of CR against FP-P-110 and FP-ENG-110 showed 19 instances where there were issues associated with this equipment. The most common issues encountered were failure to start, unexpected auto start, oil/coolant leaks, hot bearings, low coolant level, over heating of coolant, and failure of hotstart heater. These issues are normally discoverd during monthly or annual testing and may not accuratley reflect the total time that the system is not heatlhy due to the limited amount of times this pump is run. Please evaluate if it is possible to increase the heatlh and reliability of this pump and engine. Please see cross references for ARs <I> **** Actions Taken **** Was requested to generate this AR to raise this issue. <N> This pump and engine were the subject of a recent Singlepoint Vulnerability Evaluation performed under AR -383328. The actions that precipitate out of the SVE will address those concerns raised under this CR. This CR should be trended with no additional action required to the SVE AR-383328. | 02-00-FP-P-110
400356 | CR | 20191018 |  | 3 | Enhancement to Transformer Diagnostic testing for TTR | N | N |  | N | YES | <D> **** Detailed Description **** While performing WO 02112838-01 it was discovered that the transformer turns ratio (TTR) acceptance criteria was in Line to line voltage instead of Line to neutral voltage. The test equipment BPA uses gives the number in line to line voltage and the PMs should be updated to reflect a criteria for turns ration using line to line voltage. Recommend assignment to system engineering to validate TTR numbers in each diagnostic transformer test MWOs so they can be interpreted quicker in the field using line to line voltages. This condition has no impact on the operation of E-TR-B and it is to identify an enhancement to the transformer diagnostic testing WOs. | 02-00-E-TR-B,02-00-E-TR-M2,02-00-E-TR-M3,02-00-E-TR-M4,02-00-E-TR-N1,02-00-E-TR-S
400357 | CR | 20191019 | CAQ | D | E-DISC-7AA3B will not open | Y | Y |  | N | YES | <D> **** Detailed Description **** A PMT was performed on E-DISC-7AA3B. It was cycled several times, left closed, the Cubicle door was opened and voltages were checked. The door was shut and E-DISC-7AA3B would not open. Several attempts were made to open the breaker. None were successful. | 02-00-E-DISC-7AA3B
400361 | CR | 20191019 |  | 3 | Incorrect Notification Information in SOP-ELEC-115KV-OPS |  |  |  | N | NO | <D> **** Detailed Description **** Steps 7.1.4 and 7.2.11 state "NOTIFY Dittmer Dispatch Center at 360-418-2281..." This is incorrect. Dittmer is the contact for 500 KV terminal clearances. These steps should instead state "NOTIFY Munro Dispatch Center at 509-465-1837/1839..." for requests on 115 kV lines. <I> **** Actions Taken **** No further immediate actions needed.
400362 | CR | 20191019 | CAQ | D | CCTV 23/23T Requires Maintenance | N | Y |  | N | YES | <D> **** Detailed Description **** CCTV 23/23T is not functioning as designed and requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Initiate CR/WR. Compensatory measures initiated. Security Supervision notified. | 02-00-SEC-CCTV-23,02-00-SEC-CCTV-23T
400363 | CR | 20191019 |  | 4 | Received Oscillograph Started, H13-P800.C4.4-3, alarm. |  |  |  | N | NO | <D> **** Detailed Description **** Startup and Backup voltages are as follows: E-TR-S A: 238kv B: 235kv C: 237kv E-TR-B A: 119kv B: 118kv C: 118kv The following sensors were tripped and are reset: J7 500kv Neutral ground O.C. BPA reports the following: Cause was Ashe-Marion #2 momentary fault. Relaying involved a single pole. No damaged equipment. line reclosed. No emergent outage needed. 230kv and 115 kv not involved. 0546 10/19/19. 500kv involved. No RAS initiated.
400364 | CR | 20191019 |  | 4 | HT-HTP-FP/6/1 ckt 53F power on light socket broken | N | N |  | N | YES | <D> **** Detailed Description **** I broke the socket attempting to replace the bulb. It needs to be replaced. <I> **** Actions Taken **** wrote this CR/WR and notified the control room | 02-00-HT-HTP-FP/6/1
400365 | CR | 20191019 |  | 4 | FP-P-110 lube oil level is about a quarter inch above low. | N | Y |  | N | YES | <D> **** Detailed Description **** The lube oil level of FP-P-110 is not out of spec, but it is getting close and needs oil added. FP-P-110 is protected at this time due to FP-P-1 being out of service. <I> **** Actions Taken **** Wrote this CR/WR and notified the Main Control Room | 02-00-FP-P-110
400366 | CR | 20191019 |  | 4 | Lighting in DG-2 Room Poor | Y | N |  | N | YES | <D> **** Detailed Description **** There are several lights out in the overhead of the DG-2 room that will require scaffold to access to replace bulbs. The room is dimly lit. <N> **** Equipment Description **** DG-2 Room
400367 | CR | 20191019 |  | 4 | Step needs yellow paint - Safety |  |  |  | N | NO | <D> **** Detailed Description **** There is a step on the pathwath from building 17 to building 9 on the south side that has a single step that should be painted yellow for better awarenesss. <I> **** Actions Taken **** Notified Mgmt and wrote CR. <N> **** Equipment Description **** South pathway(sidewalk) between building 17 and building 9.
400368 | CR | 20191019 |  | 4 | Possible roof leak 487' RW bldg |  |  |  | N | YES | <D> **** Detailed Description **** A puddle was found in the 487' RW bldg men's room. The ceiling tiles above are visibly wet. The puddle is relatively small about 1 foot in diameter and it did not appear to be leaking currently. Recommend further investigation. <I> **** Actions Taken **** CRS, control room operator and HP informed <N> **** Equipment Description **** ceiling tiles east end of 487' RW men's room
400369 | CR | 20191019 | CAQ | D | Roof Leak into the HPCS DG room | Y | N |  | N | YES | <D> **** Detailed Description **** Water was discovered on the floor in the HPCS DG room there were "wet Floor" post but i couldnt find a CR for the leak. Leak appears to be coming from the side of one of the roof plugs or removalbe blocks. <I> **** Actions Taken **** cr/wr <N> **** Equipment Description **** HPCS DG room
400370 | CR | 20191019 |  | 3 | eSOMS Preventing Operator Rounds Values from Being Input |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing OPS3 rounds, the eSOMS software on the iPad prevented input of values for two of the logs (Which SCW demineralizer is in service and which SCW filter is in service). Logs were uploaded and the values were again attempted to be input via software on a desktop computer. Again the software would not accept any value to be input into that field. Log information was added as a note but the value space had to be left blank. <I> **** Actions Taken **** Informed supervision, wrote CR . <N> **** Equipment Description **** eSOMS software Need IS help to correct.
400371 | CR | 20191020 |  | 4 | Roof Leak in GSB HVAC Room | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Due to the recent heavy rain, a leak in the GSB building HVAC room was discovered. It appears to be leaking from a roof drain. The leak was severe enough to collect on the floor creating a puddle that ran from behind the HVAC unit over to the refrigerator located in the same room. Plant laborers mopped up the puddle and caution signs were staged to alert of the possibility of a slick floor should the leak persist. Please look into roof repair. <I> **** Actions Taken **** Informed supervision, wrote CR <N> **** Equipment Description **** GSB 456 HVAC Room
400372 | CR | 20191020 |  | 4 | Main Turbine Bearing #4 vibes rising faster than anticipated | N | N |  | N | YES | <D> **** Detailed Description **** Main Turbine Bearing #4 vibes have been gradually rising over the last few months. There was a step change for the worse on August 14th that caused a revision to the ODMI. This input a notification to the CRS if Bearing #4 vibes reached 8.7 mils. EDNA Trends point (T1 1225A) shows a linear increase over the last 50 days from ~6.6 mils to ~7.95 mils. At the current rate we should reach our ODMI setpoint in approximately 28 days. Per sub assignment #6 of AR#395842 we are forced into a down power for a balance shot within 2 weeks of reaching 8.7 mils. This is projecting to occur late November rather than the currently planned April 2nd 2020. <I> **** Actions Taken **** Snapshot of EDNA trend attached. Monitoring of trend will continue by Control Room staff. . Rev 2 of ODMI 395842 if sustained vibration levels reach 10 - 14 mils, we will reduce power in 5% increments down to 80% or to the point that vibration is LT 10 mils. Rate of rise is ~ 0.027 mils/day. Current vibration is slightly reduced now to ~6.9 mils. At this rate 10 mils can be expected by mid-February 2020. <N> **** Equipment Description **** Turbine Building 501' | 02-00-MS-DT-1C
400373 | CR | 20191020 | CAQ | D | T-118 | N | N |  | N | YES | <D> **** Detailed Description **** T-118 did not pass the daily door test. <N> **** Equipment Description **** T-118 located on the second story GSB, turbine side
400374 | CR | 20191020 |  | 4 | Flow controller COND-FIC-200F not controlling COND-V-231F. | N | N |  | N | YES | <D> **** Detailed Description **** Post relax, COND-FIC-200F won't controll COND-V-231F. <I> **** Actions Taken **** CRS notified. <N> **** Equipment Description **** RW467 west valve gallery | 02-00-COND-FIC-200F
400375 | CR | 20191020 |  | 4 | E-TR-M2 Desiccant Dryer No Light | N | N |  | N | YES | <D> **** Detailed Description **** No lights are illuminated for the E-TR-M2 desiccant dryer. Also the desiccant is still sluffing out of the little mesh retaining column. <I> **** Actions Taken **** Informed MCR | 02-00-E-TR-M2
400376 | CR | 20191020 |  | 4 | E-TR-5/52 Negative Pressure | N | N |  | N | YES | <D> **** Detailed Description **** E-TR-5/2 pressure is -0.2psig. Acceptable range is 0 - 4. This pressure will continue to decrease as ambient temperature decreases. <I> **** Actions Taken **** Informed MCR | 02-00-E-TR-5/52
400377 | CR | 20191020 |  | 4 | WCH-CH-51B Cooler Vacuum Pressure at -20 in Hg | N | N |  | N | YES | <D> **** Detailed Description **** During rounds, found out of spec reading of -20 inches Hg as read on WCH-PI-51B/3, WCH-CH-51B Cooler Vacuum Pressure. <I> **** Actions Taken **** Generated CR/WR . Per SOPSOP-HVAC/WCH-OPS, WCH-PI-51B/3 should read between 0" and 15" Hg. | 02-00-WCH-CR-51B
400378 | CR | 20191020 | CAQ | D | ARM-RIS-30 Downscale Alarm | N | Y |  | N | YES | <C> CR reopened to add completion required check mark to referenced WO 0211856 per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** Received a ARM Downscale alarm for ARM-RIS-30 (H13-P602 .A5.6-1); the alarm was reset. This is a repeat issue which recurs infrequently . WR 29151147 was recently closed out, documenting this same thing. Recommend either fixing the equipment issue or adding a note to the ARP saying that an occasional downscale alarm is ok and expected. The ARM is being carried on sheet A19-ARM-RIS-30-001. | 02-00-ARM-RIS-30
400379 | CR | 20191021 | CAQ | D | Accumulator Trouble Hi Water Level HCU 2259 | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-2259 Accumulator Trouble alarm was received. Ops 2 responded and drained it. Alarm was reset. | 02-00-CRD-HCU-2259
400380 | CR | 20191021 |  | 3 | Procedure enhancement SOP-AS-SHUTDOWN |  |  |  | N | NO | <D> **** Detailed Description **** SOP-AS-SHUTDOWN step 5.2.10 doesnt appear to have a sign off spot . Please add. <I> **** Actions Taken **** wrote cr
400383 | CR | 20191021 |  | 4 | Small caution tag printer in Main Control Room not printing. | N | N |  | N | NO | <D> **** Detailed Description **** Small caution tag printer in Main Control Room has faults and will not print. Tried to calibrate several times and was unsuccessful. Indicating lights are as follows: STATUS red, PAUSE yellow, DATA off, SUPPLIES red, NETWORK green. <N> **** Equipment Description **** Main Control Room CRO2 desk. Per AR 400182, MCR caution printer media re-calibrated. SAT Duplicate AR, may be canceled or COMP/NA
400385 | CR | 20191021 |  | 3 | OPDS procedure suggestion |  |  |  | N | NO | <D> **** Detailed Description **** New procedures SOP-ELEC-OPDS-TRB and SOP-ELEC-OPDS-TRS provide guidance for removal of/ return to service of TRB and TRS. A large majority of each procedure is performed by electricians, with one page performed by Operations. Suggest that the procedures be split into separate Maintenance and Operations procedures. AR 261654 is the driving AR, markups have been added this 400385 EDMS <I> **** Actions Taken **** Discussed with maintenance procedure writer who concurred with suggestion. Final decision to be made by Electrical Shop.
400388 | CR | 20191021 |  | 4 | IPM8 32778 failed RAD CAL. low counts on detector #24 | N | N |  | N | NO | <D> **** Detailed Description **** During the performance of the radiation source calibration of IPM-8 HP-EQ-32778 it was discovered that detector # 24 [ left foot detector] has low background and low source counts. The detector or head amp needs replaced. <I> **** Actions Taken **** Stopped calibration , Notified HP supervision, wrote work request <N> **** Equipment Description **** HP-EQ-32778
400390 | CR | 20191021 |  | 3 | ABN-ELEC-DG3-CROSSTIE/SM8, SM7, & 5.6.2 editorials requested |  |  |  | N | NO | <D> **** Detailed Description **** Editorial changes requested to ABN-ELEC-DG3-CROSSTIE/SM8: - Step 7.3.10 lists the incorrect sync selector switch and panel, it should be the E-CB-4/2 on panel H13-P601. It is important that sync selector switches be correctly identified for turning on and off since if two off the same PTs are placed in on, it could blow PT fuses and render the associated equipment unavailable. Recommend looking at the other infrequently used ABNs to ensure they are correct. Example, ABN-ELEC-DG3-CROSSTIE/SM7 has no step at the end of Att. 7.3 to turn off E-CB-4/2 sync selector and must be corrected. - Note prior to Step 7.2.5 references a step which doesn't exist, the steps only go to 7.2.10. Editorial requested for 5.6.2: - Step 8.6.4.a substeps should be numbered 1, 2, 3. Currently the second substep has no number. These should be numbered the same as the following step 8.6.4.b.
400394 | CR | 20191021 |  |  | WCI-4 & PPM 1.3.76 challenge meeting reqs not aligned |  |  |  | N | NO | <D> WCI-4 and PPM 1.3.76 challenge meeting requirements are not aligned PPM 1.3.76 Integrated Risk Management requires all PPM 1.3.76 Integrated Risk Management requires all applicable work order tasks be at READY status prior to the applicable work order tasks be at READY status prior to the (HRWP) challenge meeting. Or at APPROVED status with all (HRWP) challenge meeting. Or at APPROVED status with all holds except a HRP hold removed. PPM 1.3.76 also requires holds except a HRP hold removed. PPM 1.3.76 also requires that a challenge meeting will be completed prior to T-4. that a challenge meeting will be completed PRIOR to T-4. WCI-4 Online Work Control Process (rev 48) directs all WCI-4 Online Work Control Process (rev 48) directs all departments to advance WOâ€™s to READY (status 45) by the end departments to advance WOâ€™s to READY (status 45) by the end of the T-4 week. WCI-4 also directs that challenge meetings of the T-4 week. WCI-4 also directs that challenge are conducted and complete by the end of the T-4 week. meetings are conducted and complete by the END of the T-4 week. . Recent HRWP challenge meetings were conducted for DG1, CRD-P-1A and TMU-P-1A. For all of these work windows, planning and preparation was done â€œjust-in-timeâ€ â€ in an attempt to comply with procedural requirements. Due to the â€œjust-in-timeâ€ compliance, the work window planning and preparation lacked sufficient details.
400395 | CR | 20191021 |  | 3 | WC1-4 & PPM 1.3.76 challenge meeting reqs not alligned |  |  |  | N | NO | <D> **** Detailed Description **** WCI-4 and PPM 1.3.76 challenge meeting requirements not aligned PPM 1.3.76 Integrated Risk Management requires all applicable work order tasks be at READY status prior to the (HRWP) challenge meeting. Or at APPROVED status with all holds except a HRP hold removed. PPM 1.3.76 also requires that a challenge meeting will be completed PRIOR to T-4 . WCI-4 Online Work Control Process (rev 48) directs all departments to advance WOâ€™s to READY (status 45) by the end of the T-4 week. WCI-4 also directs that challenge meetings are conducted and complete by the END of the T-4 week. . Recent HRWP challenge meetings were conducted for DG1, CRD-P-1A and TMU-P-1A. For all of these work windows, planning and preparation was done â€œjust-in-timeâ€ in an attempt to comply with procedural requirements. Due to the â€œjust-in-timeâ€ compliance, the work window planning and preparation lacked sufficient details. The challenge meetings identified details that caused the challenge meeting to be â€œfailedâ€ or work to be rescheduled within the work window to reduce risk or work that was not properly bundled to reduce risk. . In another example, the need for one HRWP (E-TR-B) was not even identified until T-4 which required â€œjust-in-timeâ€ effort to complete the HRWP. No challenge meeting was conducted for this work because it was considered repetitive. . CR 399419 documents a similar issue for safety system windows and provides benchmarking information that should be considered. CR 399419 has no open assignment. . Finally, documentation of challenge meeting issues and failures is inconsistent which makes assessing a performance trend difficult. . Recommend assignment to Work Control as the process/procedure owner. One action should be to evaluate the discrepancy between WCI-4 and PPM 1.3.76 and develop a challenge meeting milestone that reduces/eliminates the behavior of â€œjust-in-timeâ€ readiness. <I> **** Actions Taken **** Shared information with my department manager.
400396 | CR | 20191021 |  | 4 | DG2 and DG3 Poor Lighting Issues | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** DG2 and DG3 have Many overhead lights burned out or flickering. Was not able to check DG1, as it is Protected at this time. These areas need to be relamped. <I> **** Actions Taken **** Notified HP Supervisor and HP Lead. Initiated CR/WR <N> **** Equipment Description **** DG2 DG3
400399 | CR | 20191021 |  | 3 | SM000015 Lesson Plan in CBT needs enhancement | N | N |  | N | NO | <D> **** Detailed Description **** SM000015 Lesson Plan in the Hazmat Emergency Coordinator CBT needs enhancement. SWP-ENV-02 and -03 are referenced. Those procedures have been superceded to GBP-ENV-17 and -18. <I> **** Actions Taken **** Wrote CR.
400400 | CR | 20191021 | CAQ | D | SW-FS-23B as found OOT | Y | Y |  | N | YES | <D> **** Detailed Description **** During calibration of SW-FIS-23B, SW-FS-23B was found OOT low at 13.37â€ H20 (Tolerance is 14.6â€ H2O +- .25â€ H2O). Adjusted FS per 10.24.9 to as left value of 14.64â€ H2O. <I> **** Actions Taken **** Notified supervision, adjusted per IMDS and 10.24.9. Trending only <N> **** Equipment Description **** RHR B | 02-00-SW-FS-23B
400401 | CR | 20191021 |  | 3 | OI-54 and 1.3.1 changes to align qualifications |  |  |  | N | NO | <D> **** Detailed Description **** Attached in the EDMS are the recommended changes to OI-54 and PPM 1.3.1, highlighted in yellow, to align the procedures with the qualificaiton directory for inactive licenses and to align the SRO hours as counting for IA hours for hours maintenance and recertification since the IA assists the SRO. <N> Please contact John Hedgecock with questions.
400402 | CR | 20191021 |  | 3 | Procedure enhancement for LCS |  |  |  | N | NO | <D> **** Detailed Description **** Note 11 on page 1.7.1-8 of LCS says to go to page 1.7.1-3 aand I think it should be 1.7.1-5 <I> **** Actions Taken **** Wrote CR
400404 | CR | 20191021 |  | 3 | Quorum Not Met at Plant Health Committee Sub-Committee | N | N |  | N | NO | <D> **** Detailed Description **** Mainenance did not have a representative at PHCSC. THis caused the meeting to be canceled due to lack of quorum This caused rework for the committee and the presenters on the agenda.
400407 | CR | 20191021 |  | 3 | Trend in IEBS Corporate Transfer |  |  |  | N | NO | <D> **** Detailed Description **** Badge photos are not consistently transferring to the corporate network. <I> **** Actions Taken **** Notified Security Management, initiated CR <N> Approval to move the date out by the ITBOA Supervisor.
400408 | CR | 20191021 |  | 3 | Enhancements to SNE I Qualification Guide |  |  |  | N | NO | <D> **** Detailed Description **** While performing the SNE I qual guide minor enhancements were identified to improve it. Add PPM 1.3.84 in lieu of PPM 1.3.1 on page 13 Admin model. Add PPM 9.3.11 to the Heat Balance Module (pg23). Remove Tech Spec 3.2.4 (pg 26) as it has been removed from technical specifications. <I> **** Actions Taken **** *Notified supervisor and wrote CR to improve the qualification guide.
400411 | CR | 20191021 |  | 3 | Update/clarify TSP-HCV/X58-C801 section 7.6 |  |  |  | N | NO | <D> **** Detailed Description **** New PMRQ 26534-01 proposed for R25 for hardened containment vent requires valve timing as well as valve stroking. PM references PPM 5.5.14 which is the operational procedure but not useful to perform the PM as it wwould blow the rupture discs. PM can be done per section 7.6 of TSP -HCV/X58-C801 which already functionally strokes the valves. Section 7.6 also does the valve program VPI but does not document it well. Update procedure per attachment in EDMS. Submitted SMS/AR 400410 to clarify PMRQ 26534 scope to perform valve stroke and timing. This is a future PM/procedure issue for R25 readiness, not an operability concern. <I> **** Actions Taken **** Discussed with affected engineering groupds for alignment and PM/procedure scope.
400412 | CR | 20191021 |  | 3 | Unable to perform NVMe hard drive imaging |  |  |  | N | NO | <D> **** Detailed Description **** Hard drive imaging for WO 02145592 in support of EC 17398 (ACUMEN) was not able to be performed. The hardware tools for imaging would not communicate with the NVMe hard drives. This does not impact Operations. Recomend assign to the ACUMEN project for documentation of resolution. <I> **** Actions Taken **** Discussed with RE and wrote CR.
400413 | CR | 20191021 |  | 3 | New AIr filters from the Warehouse smell moldy |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Facilities was supplied air filters from the Warehouse that smell moldy. The filters look normal but some the boxes appear to be very old. Cat ID's 58403870 and 58405746 Recommend assignment to Supply Chain <I> **** Actions Taken **** Talked to supply chain Manager, Supervisor and Procurement specialist about my concern with the filters. Set an Email with pictures of the air filter boxes. Wrote this CR. <N> **** Equipment Description **** Cat ID 58403870 Cat ID 58405746
400414 | CR | 20191021 |  | 3 | PMID 12235-04 not scoped for R24 | Y | N |  | N | NO | <D> **** Detailed Description **** WO 02087948 is an outage PM to perform a full diagnostic scan of SW-MO-2A. This has historically been an outage activity however it was determined that it could be performed online. The process for adjusting the PM was not initiated and this was not identified until after the T-20 during a PM late date review for work supporting the SW A online maintenance window. This work is required to meet NRC commitments and cannot be deferred until R25 requiring it to be performed. This work will exceed 50% of the 72 hour LCO and is considered high risk. Any additional work on this valve will be performed in future outages. Recommend assignment to outage management for Extent of condition reviews. This has no impact on the equipment and is an adminstrative issue only. <I> **** Actions Taken **** Scoped the work for the SW A online maintenance window Discussed with Engineering, PSO and Operations <N> CR edited at the request of initiator to enter the correct PMID 12235-04 and SW-MO-2A .
400415 | CR | 20191021 | CAQ | D | FP-V-169 PACKING LEAK | N | Y |  | N | YES | <D> **** Detailed Description **** FP-V-169 packing leak. 1/8" solid stream during FP-P-111 run. <I> **** Actions Taken **** Valve was unlocked and placed on it's backseat (re-locked) to stop leak. Notified CRS. <N> **** Equipment Description **** Flocculator Building. SE Corner. | 02-00-FP-V-169
400416 | CR | 20191021 | CAQ | D | Pittimg oberved on the shell of the RHR-HX-2B | Y | Y |  | N | YES | <D> **** Detailed Description **** During the PM cleaning of the seal cooler for RHR-HX-2B localized pitting amd signficant wall thinning was observed. The pitting was on the shell of the heat exchanger. Several locations were identified as needing repair. This was an expected condition and an ASME repair plan has been issued for this work. This work was conducted under WOT 0213669701 and RHR B is in a system outage. <I> **** Actions Taken **** Initiated repair and NDE support. <N> Per ME-02-85-70, the minimum wall for circumferential stress (bounding) is 0.125". UT was performed on RHR-HX-2B and the lowest min wall measured was 0.148" at area 2 in the attached NDE report in the EDMS. UT did not reveal any pits in the shell of RHR-HX-2B that were below required min wall. <R> REP/REGE assignments cancelled with compliance manager concurrence. | 02-00-RHR-HX-2B
400417 | CR | 20191021 |  | 4 | CW-CT-1A Missing Stairwell Door. | N | N |  | N | YES | <D> **** Detailed Description **** CW-CT-1A enclosed stairwell door is no longer on it's hinges and leaned against the wall inside. <I> **** Actions Taken **** Notified CRS. <N> **** Equipment Description **** CW-CT-1A Enclosed Stairwell | 02-00-CW-CT-1A
400418 | CR | 20191021 |  | 4 | Use Oil Found in Employee Parking Lot |  |  |  | N | NO | <D> **** Detailed Description **** A container of used oil was found in the employee parking lot. <I> **** Actions Taken **** The used oil was taken to the 180-day area and disposed of in a used oil drum <N> **** Equipment Description **** Employee parking lot.
400419 | CR | 20191021 | CAQ | D | ISP-CRD-Q404(K1 LED did not illuminate on CRD-LS-613B) | Y | N |  | N | YES | <D> **** Detailed Description **** While performing ISP-CRD-Q404(02139469-01) step 7.1.36, the Trip Status LED for K1(CRD-LS-613B) failed to illuminate. The RPS text box, CPU points and Annunciator all worked as expected. <I> **** Actions Taken **** Notified CRS and Shift Manager on wrote CR. <N> **** Equipment Description **** 501 MCR room
400420 | CR | 20191021 |  | 3 | Removed WOA Components Still Referenced in Specifications |  |  |  | N | NO | <D> **** Detailed Description **** WOA-RIS-31A, WOA-RIS-31B, WOA-RIS-32A, and WOA-RIS-32B were removed per EC 11373. However, these EPNs are still discussed in AED SPC 15B.2 (Sections 3.6.5.1.e and Table 3.6.6.3-1) and AED SPC 351 (2.6.4.8 and 2.6.4.9). Evaluate and update these specifications as required.
400421 | CR | 20191021 |  | 3 | Recommend enhancement to OSP-FLEX-Q705 |  |  |  | N | NO | <D> **** Detailed Description **** Recommend enhancement to OSP-FLEX-Q705. Recommend step 7.3.8 be made condition allowing DG5 fuel tank to be filled if required. For the short 30 minute quarterly runs very little fuel is used and the fuel gauge will remain at the full mark if the tank is competely full prior to the start.
400422 | CR | 20191021 | CAQ | D | DEH fluid â€“fluid and turbine OEM recommended limits exceeded | Y | Y |  | N | YES | <D> **** Detailed Description **** Lab results for a DEH fluid sample taken on 09October 2019 returned three values that exceeded the DEH fluid OEM recommended limits, two of which also exceed the turbine OEM recommended limits. Each of these limits are related to high particulate count for the given size range. Particle count for a 100ml sample should be: 5-10 Micron - LT 9700, 10-25 Micron â€“ LT 2680, and 25-50 Micron â€“ LT 380 The subject sample returned counts for these particle sizes of: 5-10 Micron - 38808, 10-25 Micron â€“ 9972, and 25-50 Micron - 452 EPRI DEH Fluid Maintenance Guide Section 4.4.3.8 and Table 4-24 provide turbine OEM particle count recommendations. For a Siemens/Westinghouse unit such as CGS the limits are [See document in EDMS.]: 5-10 micron particle limit is 24,000 10-25 micron particle limit is 5,360 25-50 micron particle limit is 780. All other measured parameters are within normal band. Trend information: This is the third high test, and second test that revealed both fluid and turbine OEM limits have been exceeded and illustrates a degrading trend. The first high test counts did not exceed turbine OEM limits. However, last time the the 5-10 micron count exceedance was around 10% greater than the turbine OEM limit. This time the 5-10 micron count is 160% the turbine OEM limit. The cause is either failed insulation in vicinity of DEH lines, or steam leak(s) blowing near DEH lines, such that the DEH lines are exposed to excessive heat. The very large leak reported high above the TG471 mezzanine may be contributing to this condition, but there may be others. Action required: Investigate where heat is reaching the DEH lines. <I> **** Actions Taken **** informed supervisor and manager <N> This CR condition was previously identified in CR 00398969. No additional actions are required based on this CR. CR 00398969 has generate the necessary corrective actions. | 02-00-DEH-TK-2
400423 | CR | 20191021 | CAQ | D | APRM-CHS-4 (AR11) monitor failed. | Y | Y |  | N | YES | <D> **** Detailed Description **** APRM-CHS-4 (AR11) monitor failed. Can't wake up the monitor, all push button still provide audible sound when actuate. This issue will prevent us from performing TSP -APRM-C301. Need to investigate and repair. <I> **** Actions Taken **** CRS/SM informed | 02-00-APRM-CHS-4
400424 | CR | 20191021 |  | 3 | Lack of 24 hour Machinist impacted RHR safety system window. |  |  |  | N | YES | <D> **** Detailed Description **** 24 hour coverage of Machinists during the RHR safety system window. This had an impact on RHR-M-V/48B work which is critical path. Two machinists were on day shift, and worked until their fatigue rule hours were used up, and they had to leave prior to violating the fatigue rules. This caused the work on RHR-M-V/48B to stop. RHR-M-V/48B is currently critical path and the delay of critical path should be a critique item when reviewing the performance associated with the RHR safety system review at T+1 <I> **** Actions Taken **** Discussed issue with Mechanical shop supervisor, and the OCC. Validated that this would not affect other work associated with the RHR safety system window. Electricians started work on RHR-MO-3B which wasnâ€™t scheduled to start until after RHR-M-V/48B was complete. Author recommends a Non-CAQ severity level 3 assigned to the Mechanical shop to address the negative impact on the safety system window. | 02-00-RHR-MO-48B
400425 | CR | 20191022 |  | 3 | (QA)RHR-M-V/24B, AR-EVAL 398238 WO Not Routed for QC Review |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) WOT 02113824-16, was not routed to QC for review work activities per AR EVAL 398238 on Quality Class 1 RHR-M -V/24B.. AR EVAL 398238 required modification activities to drill holes for inspection ports on DE and ODE Bearing Brackets and installation of new 3/8â€ S/S plugs or T -Drains as applicable per the AR EVAL 398238. This modification requires QC inspections per QAP-ASU-07 and QAP-ASU-10. The work order was planned with Peer Verification hold points instead of QC inspection. . The Mechanical craft and Supervisor questioned the PV hold points during the Pre Job briefing and notified QC prior to performing the work activity as Peer Verification. The PV Hold points were annotated to QC Inspections hold points by QC and inspections performed by QC and accepted. <I> **** Actions Taken **** Notified OCC and Engineering, Maintenance Planning, and Quality Services Supervision. PV hold points changed to QC inspections. <N> **** Equipment Description **** Shop work activities per the AR EVAL 398238 have been inspected by QC and accepted.
400428 | CR | 20191022 |  | 3 | No identified 24/7 Warehouse personnel for the RHR B Window |  |  |  | N | NO | <D> **** Detailed Description **** The storekeeper/Warehouse person scheduled for working swings had only intended to work his normal shift of 1600 to 0200. He had not been told to change his hours to 1800-0600 in support of the RHR B System Maintenance Outage window. The expectation is that we have 24/7 coverage at the warehouse when the OCC is manned. <I> **** Actions Taken **** Discussed the situation with the storekeeper. He agreed to stay until dayshift personnel arrived to relieve him. He also stated that he would adjust his schedule for the remainder of the RHR B window.
400436 | CR | 20191022 |  | 3 | Cannot Locate AED PRC 30158 | N | N |  | N | NO | <D> **** Detailed Description **** While working on AR/CR 392850. It was discovered that AED PRC 30158 does not have an image of the document in Asset Suite only the document summary coversheet. Normally this is a non-issue because hard copies of documents can be found in the Document Control area or alternatively as a record on either microfilm or microfiche. However in the case of AED PRC 30158, no microfilm or microfiche could be located. This is a documentation issue only and does not impact any SSCs at Columbia. For resolution recommend locating the missing documentation and uploading an image to Asset Suite. <I> **** Actions Taken **** Notified my supervisor Wrote this CR <N> My closure notes were inaccurate. It was incorrect to create Rev 001 and associate the image to that Rev. Correct action was to attach image to Rev 000. This has been resolved.
400437 | CR | 20191022 |  | 3 | MId-Cycle 2019: PI Recommendations | N | N |  | N | NO | <D> **** Detailed Description **** During the mid-cycle assessment, the performance improvement peer provided recommendations to be evaluated by Performance Improvement. <I> **** Actions Taken **** Discussed peer PI recommendations with Performance Improvement Manager, wrote CR and initiated assignments. <N> Recommend disposition as 3 to AR-PERFIMP
400438 | CR | 20191022 |  | 3 | Potential Data Recording Gaps for the Dehalogenation System | N | Y |  | N | NO | <D> **** Detailed Description **** It was noted late in the Dehalogenation project implementation that the eDNA system, may not adequately collect/store all data points from the Dehalogenation system without any gaps. The eDNA system may have down times and outages which will result in data recording gaps. The NPDES permit clearly states that the data points for the Dehalogenation system must be continuously monitored. To avoid potential regulatory noncompliance if a data gap exists, the Dehalogenation Project team has elected to incorporate a backup data recording function in the Engineering change. . This CR is used to document this change in scope. A data logger function will be considered and be placed in the Dehalogenation trailer. The design of the internal data logger will require a new revision to EC 16616. . Recommend assigning this CR to the Owed to Group â€œAR-CMCâ€. <I> **** Actions Taken **** Actions Taken â€“ This issue was discussed with the PM, E&RP, Chemistry, and Operations, and the Design Engineering Manager. The 2nd action â€“ I initiated this CR.
400439 | CR | 20191022 | CAQ | C | WEA-SR-25 erratic vacuum level post maintenance | N | Y |  | N | YES | <D> **** Detailed Description **** This does not affect plant operations. There is an erratic trend (â€œsaw-toothingâ€) in the vacuum levels measured daily at WEA-SR-25 following the return to service on 10/02/19. Large step change increases and decreases in vacuum have been observed from day to day readings. This variance in vacuum was not observed prior to the maintenance in WO 02134942. Potentially related: the maintenance included the replacement of the scroll vacuum pump, WEA-FN-25, and difficulties were encountered with leak testing (CR 399248). See EDMS for NIQ plot of the vacuum trend on WEA -SR-25. <I> **** Actions Taken **** Spoke to systems engineer and supervsior, wrote CR. | 02-00-WEA-SR-25
400440 | CR | 20191022 |  | 3 | PSR-SR-49 flow adjustment needed | N | N |  | N | YES | <D> **** Detailed Description **** The flow rate on PSR-SR-49 is trending down following work on PSR-V-640. The flow was set at 1.4 gpm on per PPM 12.5.39 when the sample rack was restored and has trended down since that time. The current flow rate is 0.38 gpm with an acceptable range of 1.0 to 1.6 gpm. Flow adjustment can be performed per 12.5.39 section 6.7. This will require a Locked High Rad Area entry. This activity has been performed previously on WO 01040571 as an example. <I> **** Actions Taken **** Informed Chemistry supervision. | 02-00-PSR-SR-49
400441 | CR | 20191022 |  | 4 | ILC candidate failed systems exam #4 | N | N |  | N | NO | <D> **** Detailed Description **** One candidate failed ILC systems exam #4. Remediation is tracked under xref'd AR 00396810-13. <I> **** Actions Taken **** Reviewed exam with candidate. Interviewed candidate to identify causes and concerns.
400442 | CR | 20191022 |  | 4 | Found leak-by on BD-V-17 with Midas meter | N | N |  | N | YES | <D> **** Detailed Description **** Craft identified leak-by with Midas meter when searching for leak-by issues on Aux boiler AS-BLR-1 Note, unable to quantify leak with Midas meter <I> **** Actions Taken **** contact Ops to Attempt reseat of valve write CR to document in valve needs replaced, replacement will need WO and weld docs | 02-00-BD-V-17
400443 | CR | 20191022 |  | 4 | FP-V-426, 2 DPM leak inside ASD Building | N | N |  | N | YES | <D> **** Detailed Description **** 2 DPM leaking from upstream side flange connection for FP -V-426. Leak cannot be isolated by closing FP-V-426. <I> **** Actions Taken **** Notified CRS | 02-00-FP-V-426
400444 | CR | 20191022 | CAQ | C | MS-RIS-610C front display was replaced | N | N |  | N | NO | <D> **** Detailed Description **** MS-RIS-610C front display was replaced. the LOU requires the IMDS for MS-RIS 610C beupdated to include the required display DIO switch setting and that the SYstem engineer is to review GEK-113823D for determination of any new PMs and initiate an AR-SMS for any new in-service PM requirements. . <I> **** Actions Taken **** Wrote CR to document and to request assignments for the System engineer to update the IMDS and to review for any new PM requirements.
400445 | CR | 20191022 |  | 4 | OLNC injection lines need cleaned in R25 | N | N |  | N | YES | <D> **** Detailed Description **** The OLNC injection lines continue to build back pressure indicating a progressive blockage of the lines. During the October 2019 platinum application, pressure on the B injection line increased from 1120 psi to ~1550 psi in the first two days of injection. The rate of pressure increase has reduced at this time and appears to be under control allowing completion of the 2019 platinum application. The injections lines need to be cleaned in R25 to allow continued annual OLNC application without needing to switch to an alternate injection path. WO 02137220 was added to R24 to clean the lines, but was not effective as it did not actually clean or replace the lines as planned. The scope of work was to remove the ~2 foot piece of Â¼â€ stainless steel tubing that is inserted in the A & B RFW pipe. Reports from the field indicate the section of tubing was not removable which is contrary to drawing D-VLV-008. The planning for the R25 work order should specifically communicate the details of D-VLV-008 Note 2 which states, â€œThe Â¼â€ tubing shall slide freely into and out of assembly prior to and after installation in the fieldâ€. EC-8950 added Note 9 which designates this line for OLNC. The tubing was designed to be removable. If it cannot be removed, then it will need to be ground out and re-welded after cleaning or replacement. Many other plants in the industry clean their OLNC injection lines every outage to keep them clean. <I> **** Actions Taken **** Discussed with GE-Hitachi Services personnel. Informed Chemistry Management. Discussed with station management at a High Risk Challenge Meeting to implement the alternate injection, which was ultimately rejected. | 02-00-RFW-V-906A,02-00-RFW-V-906B,02-00-RFW-V-907A,02-00-RFW-V-907B,02-00-RFW-V-908A,02-00-RFW-V-908B,02-00-RFW-V-909A,02-00-RFW-V-909B
400447 | CR | 20191022 |  | 4 | Safety concern: wasp activity at TMU pump house | N | N |  | N | NO | <D> **** Detailed Description **** While performing work out at the TMU pump house, bldg 51, it was noticed that a large quantity of wasps were flying all around the front of the building and landed on and near the door. They were also concentrated near the trailer near the building. <I> **** Actions Taken **** Informed supervisor and wrote a CR/WR <N> **** Equipment Description **** bldg 51
400448 | CR | 20191022 | CAQ | D | Restricted Valve Movement on SW-V-154G | Y | N |  | N | YES | <D> **** Detailed Description **** PPM 12.9.10 for corrosion coupon change outs directs that SW-V-154G be opened three full turns to restore flow to the coupon rack. Valve was only able to rotate 2.25 from full isolation to full open. Changed condition suggests the valve is restricted or impeded in some way. <I> **** Actions Taken **** Valve opened fully. Chemistry specialist over SSW notified, CR initiated. <N> **** Equipment Description **** SSW B Pumphouse, isolation valve near south wall | 02-00-SW-V-154G
400449 | CR | 20191022 | CAQ | C | Numac Universal Front Panel Display CAT ID 37512 | N | Y |  | N | YES | <D> **** Detailed Description **** When trying to install CAT ID 37512 Bottom right stud that goes through keyboard extender daughter board prevents the Panel Display from being mounted. Had the stud trimmed down to the nut per 10.2.10 and Venderâ€™s approval. There is 3 other Universal Front Panel Displays in the warehouse that are exactly the same. There is a potential of fitment issues with other Numac Drawers. This issue needs to be addressed. See attached photos. <I> **** Actions Taken **** Notified Supervisor, Engineering, and Vender | 02-00-MS-RIS-610A,02-00-MS-RIS-610B,02-00-MS-RIS-610C,02-00-MS-RIS-610D
400450 | CR | 20191022 |  | 3 | Job Hazard Analysis form (JHA) per ISPM-14, needs review | N | N |  | N | NO | <D> **** Detailed Description **** The Job Hazard Analysis form (JHA) lists two signature blocks; one for "Originator" and one for "Supervisor". ISPM-14 directs the JHA originator and supervisor to complete the JHA. There may be an inconsistency in our process concerning who is supposed to actually sign the "supervisor" block; the originator's or the Supervisor overseeing the work. This question was raised after reviewing the JHA attached to WOT# 02140090-04 (Pre-Mod THD Testing for ACUMEN), in which the supervisor block was not signed, even though the work is complete. Believe the ISPM needs to be clarified, to include the specific direction. <I> **** Actions Taken **** Wrote CR
400452 | CR | 20191022 | CAQ | D | SW-FIS-23B AL indication is approx 0 and alarm is still in | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** during perfromance of WOT 0213979801 (flush and return to service SW-FIS-23B) we flushed the high and low legs for approx 2 min each, and returned the FIS back to service. once the FIS was in service, the FI indication was barley off 0. Noticed a slight bounce in the indication but it remained at or near zero. talked to the techs that initially valved FIS-23B OOS and they said the FI was reading near Zero then. Confirmed with Ops that P812.R2 Drop 2-3 is still in alarm <I> **** Actions Taken **** Notified CRS, Supervisor and created CR/WR to investigate the problem. <N> **** Equipment Description **** 444 Mez in RHR-B pump room
400453 | CR | 20191022 |  | 4 | Deluge 68 leak | N | N |  | N | YES | <D> **** Detailed Description **** There is a leak on Deluge 68 System. The nipple between The Deluge valve and Alarm Test Valve FP-V-D68/803 is leaking at the threads where it threads into the alarm valve. There is a threaded union on the oposite side of FP-V- D68\803 where it can be broken apart and repaired. OPS wrote a CR for the leak 400443 WR 29152216 but if identified the leak as being at FP-V-426 but if investigated a little further it is apparent it is leaking a little higher at the nipple. <N> **** Equipment Description **** ASD Buildind | 02-00-FP-V-D68/803
400454 | CR | 20191022 | CAQ | D | Contract Employee lost badge | N | N |  | N | NO | <D> **** Detailed Description **** Contract Employee failed to maintain proper control of badge. <I> **** Actions Taken **** Badge placed on hold, employee escorted offsite by Security, protected area access restricted, Security Supervision notified, Shift Manager Notified.
400455 | CR | 20191022 | CAQ | C | MCR TCC at P820 (Board B) may be misaligned with SWP-CM-02 | N | N |  | N | YES | <D> **** Detailed Description **** A Temporary Configuration Change (TCC) exists in the Main Control Room (MCR) at E-CP-H13/P820 (Board B) associated with AR CR 398021 WR 29151055. It has an SWP-MAI-02 Work In Progress sign hanging on the associated cart behind Board B indicating it is associated with WR 29151055 and an Expected Completion Date of 6/30/21. See the photos attached to the EDMS of this AR CR 400455. The WR does not indicate what type of TCC this installation is (e.g., a TASM, PCTC, or NICM) and there does not appear to be any AR type EVAL associated with this installation in Portal J as would be expected per SWP-CM-02 to document the associated supporting Technical Evaluation and LBID review. Per Engineering walkdown of the TCC completed on 10/22/19, the TCC installation does not pose an immediate threat to the continued function, operation, or qualification of any SSCs surrounding the TCC installation. The TCC cables currently duct taped to Board B are lightweight items. Regardless, this TCC should be investigated on 10/23/19 to ensure it fully aligns with SWP-CM-02 requirements or is provided with the required supporting documentation to become fully aligned with SWP-CM-02 requirements. <I> **** Actions Taken **** As described in the AR CR Detailed Description. The investigation completed as described in this AR CR Detailed Description was prompted and completed due to an e-mail question with photos from the Design Engineering Manager following a 10/22/19 PHC presentation by BOP System Engineering. Main Control Room personnel and OCC personnel were notified. <N> See edms for Paul Hand's input. M&TE in compliance and exempt from SWP-CM-02, pdf page 25 on Exemptions. | 02-00-E-CP-H13/P820
400456 | CR | 20191022 |  | 4 | Glycol Resistivity Low on GY-TK-10A2 | N | N |  | N | YES | <D> **** Detailed Description **** Resistivity Low on GY-TK-10A2 | 02-00-GY-TK-10A2
400457 | CR | 20191023 | CAQ | C | RHR-MO-3B required additional grease per 10.25.4 | Y | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing PPM 10.25.4, WO# 02148853-01, electricians draw grease samples from actuator housing to determine the quality of the grease. Per step 7.2.3.c and step 7.3.3.c, grease must be added and a CR written to evaluate the low, as-found levels. There is evidence of grease (MOV LL) leakage from several plugs in the main gear housing. 80 pumps of grease were added to ensure the worm gear/motor pinion gear are submerged. <I> **** Actions Taken **** Notified Supervisor, Add grease per 10.25.4 and generated CR <N> **** Equipment Description **** RHR-MO-3B RHR-MO-3B the low grease leval did not impact the valve from performing its design function. The grease inspections have been performed regularly since the last refurb in 1994 via WO CB94-03. (1994, 1996, 1997, 1999, 2003, 2005, 2007, 2009, 2011, 2012, and 2016. Refurb WO 02048843 was created to refurbish the actuator. - Bill Trappett - MOV Program Owner. 10/23/19
400458 | CR | 20191023 | CAQ | D | TRS Voltage high due to Low Load on grid | Y | N |  | N | NO | <D> **** Detailed Description **** TRS Voltage on H13-P800 was 242 KV on A phase, 240 on B phase and 242 on C phase. Contacted BPA per OSP-ELEC-W101 Ashe 230 KV per BPA was 245 KV, voltage could not be lowered due to low load, BPA expects voltage to return to less than 242 KV on Ashe 230 KV by morning.(~0700). <I> **** Actions Taken **** Informed CRS/SM
400459 | CR | 20191023 | CAQ | D | OG-DY-7B will not turn on | N | N |  | N | YES | <D> **** Detailed Description **** OG-DY-7B would not turn on during the attempted regen of OG-DY-30B . Tried cycling power supply breaker to no effect. <I> **** Actions Taken **** Initiated CR. Informed MCR. | 02-00-OG-DY-7B
400460 | CR | 20191023 | CAQ | D | MS-RIS-610D screen starting to fade | N | Y |  | N | YES | <D> **** Detailed Description **** MS-RIS-610D screen beginning to fade. <I> **** Actions Taken **** Informed CRS/SM | 02-00-MS-RIS-610D
400468 | CR | 20191023 |  | 3 | FP-V-P82/750-Replacement valve lacks drilled/tapped hole. | N | N |  | N | NO | <D> **** Detailed Description **** During walk down of WOT it was discovered that the replacement valve (CID 54205865) did not have the required drilled and tapped hole in the side of the valve body. Replacement valve has 2 â€˜flatsâ€™ on the side of the body, one flat is drilled, tapped and plugged from the manufacturer and the other flat is not. The Flat that is not drilled and tapped is the one needed for the field configuration of the subject valve. <I> **** Actions Taken **** Contacted Procurement Engineering who in turn contacted the manufacturer. The manufacturer stated we could drill and tap this ourselves, but had no specific instructions to offer to accomplish this or we could order a new valve with flats drilled and tapped to our liking. Either of these options requires revision of Substitution Evaluation SE-3125R00 (AR-OBS 399841).
400469 | CR | 20191023 | CAQ | D | M&TE OOT | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0068590 Proto Torque Wrench- model 6064C 200in found OOT & adjusted within specs. Per PPM 1.5.4 section 4.4.3 (a-c) Torque Wrench had acceptable post use verifications @ +/- .06%. DEF #7352A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only
400472 | CR | 20191023 | CAQ | C | Calculation issue on OSP-INST-H101 | Y | N |  | N | NO | <D> **** Detailed Description **** A log taking error on the CRO2 daily logs on night shift 10/23/19 led to a miscalculation on the OSP-INST-H101 on 10/23/19 day shift. The Identified Leakage Rate, Total Average Leak Rate, and 24 HR Average Leakage Rate were miscalculated in the surveillance. The actual leakage rates are 3.23, 3.23, and 3.24 gpm respectively. IS and Ops administration have been informed of the issue and will work on a solution. Once corrected, the surveillance will need to be unverified in eSOMS and recalculated to fix the issue. <I> **** Actions Taken **** Wrote CR and informed Ops Admin.
400473 | CR | 20191023 |  | 4 | 2 Pieces of M&TE OOT | N | N |  | N | NO | <D> **** Detailed Description **** 2 Teltek Dig. Thermometers- model Infomer I's found OOT & adjusted within specs. Calcode #0065313 . DEF #7354A written. Calcode #45000. DEF #7355A written. Neither were used during Calibration cycles. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only
400474 | CR | 20191023 |  | 4 | PWC-SEW-9 eyewash has low flow out of left side | N | N |  | N | YES | <D> **** Detailed Description **** While performing safety eyewash inspections it was observed that PWC-SEW-9 eyewash has low flow out of its front left side when facing the eyewash. <I> **** Actions Taken **** Wrote CR and informed CRS | 02-00-PWC-SEW-9
400475 | CR | 20191023 |  | 4 | eSOMS late entry for Maintenance |  |  |  | N | NO | <D> **** Detailed Description **** A new maintenance craft worker was not entered into eSOMS until 3 days after he started work. No covered work was performed during this time, but he should have been entered prior to his start date. <I> **** Actions Taken **** Added worker to appropriate watchbill and notified shop manager.
400476 | CR | 20191023 |  | 4 | Panel door off of original/nonactive M1 Transformer | N | N |  | N | YES | <D> **** Detailed Description **** The original old Main M1 transformer located on the southern spare pad. The panel door is located in front of the panel on the ground. Door needs to be re-installed or removed from the Transformer yard to prevent airborne material from injuring personnel or hitting energized lines/bus or damaging equipment. Recommend looking at the remaining M1 panel door and the two panel doors on the other original Main M3 transformer on the north spare transformer pad. <I> **** Actions Taken **** Contacted Shift Manager (SM). SM is sending Ops 4 to remove the door panel from the yard and store it in the Ops area until it can be re-installed. <N> **** Equipment Description **** Transformer Yard original M1/non-active transformer located on the southern spare transformer pad.
400478 | CR | 20191023 |  | 3 | Pipe wall thinning downstream a normally closed valve | N | N |  | N | YES | <D> **** Detailed Description **** In a FAC cross discipline review meeting, a planned R25 line replacement that should not be wearing, was identified. The line is located between HD-V-3B and Condenser at nozzle 43. Upstream of the normally open HD-V -3B is HD-LCV-10A2. HD-LCV-10A2 is closed during normal operation. Thinning rates in the line indicates that there is flow in the line when the valve is closed. This indicates that HD-LCV-10A2 is leaking by. With high temperature condensate from the first stage MSR drain tank on the upstream side of the valve there is less concern of wear. However, downstream of the valve are condenser vacuum conditions, so any leakage would be flashing to steam which can induce the erosive effects seen in the FAC wall thickness measurements. HD-LCV-10A2 leakage should be investigated to prevent further damage to the downstream piping and condenser penetration. <I> **** Actions Taken **** The downstream piping is in scope for replacement in R25 WO 02148902 <N> **** Equipment Description **** The line is located between HD-V-3B and Condenser at nozzle 43. TG 445' B4/12.5 | 02-00-HD-LCV-10A2
400479 | CR | 20191023 |  | 3 | SPARE RRC MOTOR TESTING | N | N |  | N | NO | <D> **** Detailed Description **** This CR does not impact plant installed equipment. This applies only to the spare RRC pump motor. . It has recently been revealed there may be a need to perform additional motor testing on the spare RRC motor (CID 0065004205) that is currently being stored (since 2009) at an off-site vendor facility. This additional motor testing was not initially identified as part of the large motor storage strategy when this motor was shipped for refurbishment and long-term storage. Refer to AR-AS 393007-02 for detailed discussion on this recommended testing. This additional testing has been estimated at $550+ which was not identified in the initial project budget. . The intent of this lessons learned CR is to capture the potential gap in developing a long-term storage strategy for this and similar large motors, and to also identify the impact on the FY20 RRC project budget. Actions are currently being taken to address the funding gap. <I> **** Actions Taken **** Actions are currently being taken to address the funding gap. <N> **** Equipment Description **** Cat ID 0065004205
400480 | CR | 20191023 | CAQ | D | Higher than expected Cell 1&12 Lug to Post con resistance | Y | Y |  | N | YES | <D> **** Detailed Description **** While performing ESP-B02B-A101 12 Month Battery Inspection (02118466-01) Higher than expected Cell 1 and 12 Lug to Post connection resistance measured. ESP-B02B-A101 7.3 Connection Resistance 7.3.2 MEASURE Cell 1 and 12 Lug to Post connection resistance recorded an initial reading of 115.3 micro ohms (Limit is 137 micro ohms) which was higher than expected and the connection appeared to move when reading was taking indicating a possible loose connection. Performed Attachment 9.4, Disposition of Connection to retorque connection with an As-Left torque of 63 in-lb. Final Connection resistance reading of Cell 1 and 12 Lug to Post connection was 29.3 micro ohms. <I> **** Actions Taken **** Electrical Supervision informed and Main Control room informed. Performed Att. 9.4 of ESP-B02B-A101 Disposition of Connection. Final connection Resistance of 29.3 micro ohms | 02-00-E-B0-2B
400481 | CR | 20191023 |  | 4 | MT&E found out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0066184 MSA Gas Analyzer- model Altair 4X found OOT. Not used during Calibration cycle. No Plant Impact. Standards Lab waiting for parts and Calibration gas to Recalibrate. DEF #7356A written. No Action Required. <I> **** Actions Taken **** Trending purposes only
400483 | CR | 20191023 |  | 3 | Form 27029 iDC Characterization Data Sheet needs enhancement |  |  |  | N | NO | <D> **** Detailed Description **** While processing records with RIM it was noted that Form 27029, iDC Calibrator Data Sheet, needs enhancement andmost recent one transmitted (1/15/19) is missing the printout attachments. It was noted that on the form the calibration date is listed on the bottom of the form - but normally it is also listed ate the top of the form with a specific line entry and labeled as calibration date. This is the standard RIM normally look to as the documents are indexed. Also it was further noted that the attachments (printouts) are not included and the form should include a statement to see attachments when they are included. This form should be revised to include these enhancements. Copies of the attachments need to be obtained and re-submitted to Plant Files as an addendum to the exisitng datas sheet. <I> **** Actions Taken **** Discussed with RIM personnel and corrections. Informed RP Supervision. Revision to Form 27029 initiated in APW. Requested reprint of data printout to resubmit. Request AR assignment to AR-RPSPT to complete follow-up actions.
400484 | CR | 20191023 |  | 4 | Several light fixtures out near CRD valve area. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Several light fixtures are completely out around the CRD valve area in RB 522, near MC-8B, 8BA room. Please investigate and repair. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** Light fixtures near CRD valve area, RB 522, NW.
400485 | CR | 20191023 |  | 3 | SWP-CM-02 exclusions and exemptions |  |  |  | N | NO | <D> **** Detailed Description **** SWP-CM-02 (Temporary Configuration Changes) Attachment 9.2 (Typical Examples of Temporary Configuration Changes) currently includes a listing of typical examples of changes that would NOT be considered Temporary Configuration Changes (TCCs) and thus would be exempted from the requirements of SWP-CM-02. This existing two page listing of non-TCC SWP-CM-02 exemptions is not currently referenced by the exclusions section of the procedure. If it is to be retained, the listing of non-TCC exemptions should be given its own Attachment number (e.g., Attachment 9.3) and should be referenced in some fashion by procedure Section 3.0 (Exclusions). Additionally, some of the existing Attachment 9.2 listed non-TCC exemptions (which include non-intrusive data acquisition and test equipment (provided the non-intrusive types of measuring devices comply with certain requirements)) may not be defined well enough. What are the non-intrusive types of measuring devices? Who makes the call that the specified criteria are satisfied (and where is that call to be documented)? The currently listed non-TCC exemptions in Attachment 9.2 should be reviewed as part of the SWP-CM-02 update for this AR CR 400485 to ensure acceptability per the Design Engineering Manager.
400487 | CR | 20191023 |  | 3 | CVI Drawing 317-00,532 REV 31 has incorrect EPN listed |  |  |  | N | NO | <D> **** Detailed Description **** CVI Drawing 317-00,532 REV 31 incorrectly lists EPN BD-V-12 in place of EPN BD-V-14 which is a recognized EPN. The correct EPN label is in the field attached to the valve. BD-V-14 is listed on the flow drawing M513 and is located in Asset Suite on the D030 panel. BD-V-12 isn't listed anywhere but on the ISO drawing. Drawing 317-00,532 needs to have the EPN BD-V-12 changed to BD-V-14.
400490 | CR | 20191023 | CAQ | D | Siren D13 single amp failure | N | Y |  | N | NO | <D> **** Detailed Description **** The Weatherwarn monitoring system identified a partial alarm at siren D13. <I> **** Actions Taken **** Notified: EP Upon arrival, the technicians found 9 out of 10 amplifiers remained function. Amplifier #8 failed and has been replaced, restoring the siren to full capacity. Recommend NCAQ-4 for trending. <N> **** Equipment Description **** Site D13
400491 | CR | 20191023 |  |  | Reports Failing to run in PeopleSoft |  |  |  | N | NO | <D> **** Detailed Description **** At 2:53pm 10/21/2019 Payroll SQRs started failing to run Jobs running in Process scheduler unable to connect to PeopleSoft to run. Processes errored out. <I> **** Actions Taken **** Around 4:30 I Started looking into it, I was unable to run a job to success, but I was able to connect to the Database manually. I then called our DBA and we could not see any issues in the Database. It looked like a cache issue I called Jon and recommended restarting the Services and Clearing cache. Jon agreed and I bounced the services clearing cache. The system was up by 6:09 pm
400492 | CR | 20191023 |  | 3 | Customer MT&E found out of tolerance | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** NCW-9597 TORQUE MULTPLIER FOUND OUT OF TOLERANCE NCW-DHK09557 TORQUE WRENCH FOUND OUT OF TOLERANCE NCW-DPG36165 TORQUE WRENCH FOUND OUT OF TOLERANCE - NEED TO ASSIGN TO NINE WIND CANYON
400493 | CR | 20191023 |  | 4 | Exam Failure - NLO Requalification Cycle 19-4 |  |  |  | N | NO | <D> **** Detailed Description **** A Non-Licensed Operators failed the Cycle 19-4 requalification exam. Qualifications have been removed pending remediation. Remediation and re-examination will be conducted in accordance with TDI-02 and TDI-10 <I> **** Actions Taken **** Performed exam analysis; conducted trainee dificiency analysis; removed qualifications; developed a remediation plan; informed crew supervision/management; documented failure.
400494 | CR | 20191023 |  | 4 | APEL Fuel Oil sediment | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Apel Fuel Oil is offscale high with sediment and the sample has a high amount of separation. <I> **** Actions Taken **** Informed chemistry supervision, the CRS and wrote a CR. Images are available. <N> images in EDMS file.
400496 | CR | 20191023 | CAQ | D | Failure to maintain physical control of badge inside PA |  |  |  | N | NO | <D> **** Detailed Description **** Individual failed to maintain physical control of badge inside PA. Badge was secured inside vehicle located in the Security vehicle trap. <I> **** Actions Taken **** Individual escorted offsite, Badge placed on hold, Security Supervision notified, Shift Manager notified.
400497 | CR | 20191023 |  | 4 | EN MAIL MIS-DELIVERED/ MIS-SORTED AT POST OFFICE |  |  |  | N | NO | <D> **** Detailed Description **** OUR MAILROOM ATTENDANT WENT ON OUR DAILY MAILRUN AND WHEN THEY RECIEVED THE MAIL BIN FROM THE POST OFFICE AND CAME BACK TO SITE TO SORT THE MAIL, THE BIN WAS NOT ENERGY NORTHWEST MAIL IT WAS A MIXTURE OF MAIL FOR PNNL, MISSION SUPPORT ALLIANCE AND CH2MHILL MAIL ALONG WITH 4 ITEMS OF EN MAIL. <I> **** Actions Taken **** NOTIFIED SUPERVISION. GENERATIING CR FOR TRENDING PURPOSES.
400498 | CR | 20191023 |  | 4 | Training records not sent correctly |  |  |  | N | NO | <D> **** Detailed Description **** RP sent training records with multiple barcode sheets when only one was needed. This would have created exeptions since all training records are sorted by a unique class number. <I> **** Actions Taken **** Informed sender of records of CR and request to pick up said records. Informed my supervision. CR written for trending purposes. <N> Records have been corrected and resubmitted. No further action required.
400499 | CR | 20191023 |  | 3 | Consider PM for spot check of rounds/security door access |  |  |  | N | NO | <D> **** Detailed Description **** Industry OE indicates that evidence of falsification of records or deliberate misconduct in regards to rounds, tours, and duties is on a degrading trend. Recommend PM be developed to drive management review (AR action) of security logs, door checks, etc. as a further barrier and mechanism to ensure that this behavior does not occur. This recommendation is driven from NSIAC steering group questions to member plants. <I> **** Actions Taken **** Initiated CR
400500 | CR | 20191023 | CAQ | C | EC17309 Closeout Not Processed Correctly |  |  |  | N | NO | <D> **** Detailed Description **** EC17309 was not processed correctly for turnover configuration. It appears the DES-2-22 and DES-2-23 were not followed to ensure the correct actions were taken to allow the modification to progress from ACTIVE to MODIFIED status. This is purely administrative and does not affect the equipment in the plant. Recommend assigning to Computer Engineering to process the EC correctly. <I> **** Actions Taken **** Discussed with Design Manager and initiated CR.
400501 | CR | 20191023 | CAQ | C | Loss power to OG-RIS-601A | N | Y |  | N | YES | <D> **** Detailed Description **** Loss power to OG-RIS-601A, the channel status display screen is blank. Received alarms OFF GAS POST TREAT RAD HI-HI-HI, OFF GAS POST TREAT RAD HIGH, and OFF GAS POST TREAT RAD MONITORS DNSCL. <I> **** Actions Taken **** Dispatched Operator to investigate local OG sample rack Notified CRS Initiated WR/CR <N> **** Equipment Description **** RW 501 | 02-00-OG-RIS-601A
400502 | CR | 20191023 |  | 3 | PDIS-COMP-IC Unable to Load Sequences to RWM | N | N |  | N | YES | <C> initiator had system crash before CR was taken to APPROVED. He then notified the owed to group instead of contacting CAP for assistance. Taken to approved. <D> During installation of new PDIS-COMP-IC, post maintenance testing (PMT) per WO 02140090-11 (EC 17398 ACUMEN Core Monitoring System) was unable to successfully complete. The PMT is to load a control rod sequence file to the Rod Worth Minimizer using the RS232 connection from the newly installed computer. PDIS-COMP-IC was unable to successfully connect with the RWM. The existing connection to the RWM RS232 from PPC-CPU-3DM was tested and was able to successfully load a sequence file. The issue is with the revised RWM-SOFT-RWM software installed on PDIS-COMP-IC. This issue does not prevent transfer to ACUMEN as the core monitoring system of record, but does impact completion of WO 02140090-02 and EC 17398 as currently written because PPC-CPU-3DM cannot be removed without another method to load sequences to the RWM. <I> Manually reset and reinitialized RWM per SOP-RWM-START and it did not correct the communication issue. | 02-00-PDIS-COMP-IC,02-00-RWM-SOFT-RWM
400503 | CR | 20191023 |  | 3 | OPDS Trouble Alarm Circuits | N | N |  | N | YES | <D> **** Detailed Description **** During design review of the OPDS as part of system turn over and project close out activities, it was identified that the Hardware/Software Failure output contact (OUT103) on the two TRB OPDS SEL-2411 automation controllers (OPDS -CONT-3/3L and OPDS-CONT-3/3N) were not wired as part of the main control room board C trouble alarm circuit C3-4.6 â€œ115kV General Troubleâ€ and likewise the two TRS OPDS SEL -2411â€™s (OPDS-CONT-3/3H and OPDS-CONT-3/3J) were not wired in the board C alarm circuit C3-4.7 â€œ230kV General Troubleâ€. . The SEL-2411 OUT103 form-C contact is programmed to change state if an on board hardware/software failure occurs which is used in this design to indicate to an operator, via the general trouble alarm, that an OPDS component that normally provides either an alarm or trip signal to the control room (i.e., the SEL-2411 located in the RW 525 Communications Room) is now out of service due to an internal hardware or software failure. . Each SEL 2411 automation controller OUT103 form-C contact in an OPDS relay set should be connected as intended in their associated General Trouble Alarm circuits to trigger an alarm on internal failure of an SEL-2411 to aid Equipment Operators, Maintenance, and Engineering in identifying and remediating OPDS relay set component issues should they occur. . During design review of the OPDS it was also identified that there are currently no local Communication Failure alarms on the OPDS TRB Annunciator Panel OPDS-ANN-B2/5F and OPDS TRS Annunciator Panel OPDS-ANN-S2/5F. Output contact OUT209 on the OPDS SEL-451s (OPDS-RLY-B3/5E, OPDS-RLY-B4/5E, OPDS-RLY-S3/5E, and OPDS-RLY-S4/5E) are programmed change contact state when a communication failure occurs between the SEL-451 and SEL-735 or between the SEL-451 and SEL-2411. . A communication failure between an SEL-451 and SEL-735 or between an SEL-451 and SEL-2411 will trigger the Ann C3-4.6 â€œ115kV General Troubleâ€ for a communication failure for TRB OPDS and Ann C3-4.7 â€œ230kV General Troubleâ€ for a communication failure for TRS OPDS as expected, although a local annunciator on the OPDS-BLG-B or OPDS-BLG-S is not available to indicate that a communication failure occurred. The SEL-451, SEL-735 and SEL-2411 currently have programmed LED indicators to signify a communication failure between specific devices. However this critical information is not shown on the local annunciator panel as intended by the design. . The OUT209 contacts should be connected to the associated local annunciator circuits to trigger a SET 1 or SET 2 Communication Failure alarm to aid operators, maintenance, and engineering in identifying a communication failure, and therefore to establish status of the OPDS relay trip set. . The identified items regarding uninstalled OPDS trouble alarm and complete communication failure alarm circuit wiring do not impact the intended function of the TRB and TRS OPDS to detect and provide main control room open phase alarm and trip protection signals to mitigate consequence to availability of supported ESF systems from open phase fault conditions should they occur on the qualified offsite power sources to Columbia. . The identified alarm circuits should be corrected/installed at the next available opportunity. <I> **** Actions Taken **** Reviewed associated OPDS drawings. . Reviewed associated OPDS device settings. <N> **** Equipment Description **** OPDS-ANN-B2/5F (SEL-2523) located in OPDS-BLDG-B in TF Yard . OPDS-ANN-S2/5F (SEL-2523) located in OPDS-BLDG-S in TF Yard . OPDS-CONT-3/3L, OPDS-CONT-3/3N, OPDS-CONT-3/3H, OPDS-CONT-3 /3J in RW525 Comm. Room in OPDS-RACK-3 | 02-00-OPDS-ANN-B2/5F,02-00-OPDS-ANN-S2/5F,02-00-OPDS-CONT-3/3H,02-00-OPDS-CONT-3/3J,02-00-OPDS-CONT-3/3L,02-00-OPDS-CONT-3/3N
400504 | CR | 20191023 | CAQ | D | SW-FI-71B indicates low SW flow | Y | Y |  | N | YES | <D> **** Detailed Description **** SW-FI-71B indicates 40 gpm. Minimum recommended range is 44 gpm. Minimum Operability Value is 42 gpm. This is the SW flow through FPC B heat exchanger. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-SW-FI-71B
400505 | CR | 20191023 |  | 3 | MS-RIS-610C dip switch digital label not programmed | N | Y |  | N | YES | <D> **** Detailed Description **** A day after installation of a new Universal Front Panel Display of MS-RIS-610C, during a walkdown to look at the new NUMAC display, it seems we did not program the dip switch setting for the application digital label. This is an aesthetic condition and does not impact the function of the equipment. Another problem seems to be the vendor manual for the Universal Front Panel Display was not processed per SWP-DOC-01, section 4.11. So we need a WR to program the dip swiitch on the MS-RIS-610C at earliest convenience and an action to AR-SEEIC to process vendor manual for all applicable systems. WO 02150314 had the proper instructions to perform the programming. Not sure how we missed it or if we missed it somehow. Work is AWAIT/C should be re-opened. It says GE-HITACHI and Should say Process Radiation Monitor Attached pictures and vendor manual to EDMS <I> **** Actions Taken **** Notified FIN | 02-00-MS-RIS-610C
400506 | CR | 20191023 | CAQ | D | met tower supervisory trouble | N | Y |  | N | YES | <D> **** Detailed Description **** recieved multiple alarms 824.M.1-7 "METEOROLOGICAL TOWER SUPERVISORY TROUBLE." The alarms codes are 01 COM LINK FAIL and 02 COM LINK FAIL. | 02-00-E-CP-CSB
400507 | CR | 20191023 | CAQ | D | FPC-V-152B | N | N |  | N | YES | <D> **** Detailed Description **** leakage from FPC-V-152B appears to have increased to approx .75 gpm as noted during SW flow adjustment <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-FPC-V-152B
400508 | CR | 20191024 |  | 4 | CF-P-41A/B low oil | N | N |  | N | YES | <D> **** Detailed Description **** CF-P-41A/B both new feed pumps with small oil bullseye are low out of log spec. The log for these new pumps is midline or higher. While both pumps have oil in the bullseye it is below the midline. <I> **** Actions Taken **** Informed CRS | 02-00-CF-P-41A,02-00-CF-P-41B
400509 | CR | 20191024 | CAQ | D | DG -2 lube oil sump below minimum after quarterly surv. run. | Y | N |  | N | NO | <D> **** Detailed Description **** DG-2 engines 1B1 & 1B2 are 0.75 inches below spec. Add lube oil to plus or minus 0.5 inches of the factory stamp FULL mark, using the appropriate oil listed in PPM 10.2.13 <I> **** Actions Taken **** CRS notified. <N> **** Equipment Description **** DG-2 room.
400513 | CR | 20191024 |  | 3 | Electronic Portions of HP Calibrations Missing Vital Checks | N | N |  | N | NO | <D> **** Detailed Description **** During the week of 10/21/2019, three radiation source calibrations on IPM-8 and ARGOS 5AB model whole body contamination monitors could not be completed as scheduled due to deficiencies with detectors that were not identified or repaired during the electronic task predecessors. Work order tasks 02142892-01, 02142893-01, and 02143357-01 were all C-grade activities that could not be completed the day they were scheduled due to faulted detectors, which requires correction by I&C personnel. Each of these work orders has a predecessor activity for I&C to either clean, inspect, and repair or perform an electronic calibration. In all three cases, the faulted detectors were apparent when running the background information for the units. Recommend that the I&C predecessor work package add information to view the background information for the detectors and repair any that are faulted or broken prior to releasing the monitors for radiation source calibration. <I> **** Actions Taken **** Coordinated with I&C to perform repairs so that the work packages could be completed in the same work week. Discussed concerns with Rad Ops personnel to develop potential fixes.
400514 | CR | 20191024 |  | 4 | EWP library with incorrect Procedure Revision |  |  |  | N | NO | <D> **** Detailed Description **** Craft noticed while pulling ISPM-20 into a work order from EPP to the tablet that the procedure was Rev: Major 15/Minor 2. We are currently on Rev: Major 16/Minor 4. The metadata was updated prior to pulling procedure up on tablet. This was previosly noted in CR# 389199. <I> **** Actions Taken **** Contacted EWP and wrote this CR. . IS - Initiated a manual sync of the document libraries that are used on the eWP tablets. Identified and corrected an issue with the nightly scheduled sync jobs. Initiated those jobs and confirmed that the latest revisions were downloaded from SharePoint and displayed on a tablet. <N> **** Equipment Description **** .
400517 | CR | 20191024 |  | 3 | EPNs not updated following implementation of EC | N | N |  | N | NO | <D> **** Detailed Description **** EC 4264 authorized replacement of the main generator hydrogen dryer flow instrument, the EC was implemented by WO 01103946. Following replacement of the components there was a step in the work instructions to notify supervisor to update EPNs in passport, this step was signed (supervisor notified) but the EPNs were not updated to the new equipment. The following EPNs need to be updated: . H2-FIS-1/1, manufacturer â€“ KURZ, Model 504-FT-12, SN MD3474A H2-FT-1/1, manufacturer â€“ KURZ, Model 504-FT-12, SN MD3474A H2-RLY-FIS1/1, Manufacturer â€“ Square D, Model 8501KPD12V51 H2-E/S-1, Manufacturer â€“OMRON, Model 582K-00712 . These EPNs should be updated in passport to ensure documentation aligns with what is installed in the plant. <I> **** Actions Taken **** Verified with design engineering and initiated CR to document and drive resolution.
400518 | CR | 20191024 | CAQ | D | Wet 22 System pressure gauge | N | N |  | N | YES | <D> **** Detailed Description **** While performing 15.1.1 Fire suppression sprinker system inspection it was found that the system pressure gauge is not reading correctly. Gauge needs to be replaced <N> **** Equipment Description **** Wet 22 487 RW | 02-00-FP-PI-W22A
400519 | CR | 20191024 |  | 4 | ARGOS at MCR needs repair. | N | N |  | N | YES | <D> **** Detailed Description **** ARGOS with SN HP-EQ-42803 located at the MCR needs maintenance. The detector 10a has low counts when exposed to known source. The sensor for personnel is in continuous response. These issues became apparent while performing WO 02142893 <I> **** Actions Taken **** Discussed issue with I&C personnel, and HP Supervision. Monitor has been placed Out of Service. | 02-00-HP-EQ-42803
400520 | CR | 20191024 |  | 4 | PWR-CRA-1 crane operational checks | N | N |  | N | YES | <D> **** Detailed Description **** An RMC Laborer performed the operational checks on PWR-CRA-1. It failed to function in the Up position. All the other functions would operate as expected. ie. North, South, East, West, and Down. The crane was not under a load during operational checks. It is positioned all the way North and is in the Trolley Pit, a Posted High Radation Area. <I> **** Actions Taken **** Stopped work and notified RP Supervision Shut power off at crane disconnect. <N> **** Equipment Description **** RW 437 Trolley Pit | 02-00-PWR-CRA-1
400521 | CR | 20191024 |  | 4 | RW 437 Grapple Charging Cable broke. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Charging cable for the new grapple broke. The wire broke at the point where it connects to the charging cable connector. This cable charges one of the two batteries that operate the grapple <I> **** Actions Taken **** Notified RP Supervision Contacted the RWTS <N> **** Equipment Description **** RW 437 Processing Area
400524 | CR | 20191024 |  | 3 | PMID MWO #s not in alignment with PPM 13.14.4 |  |  |  | N | NO | <D> **** Detailed Description **** In support of the Asset Suite 9 (AS9) upgrade model work orders (MWO) that still contain alpha characters within them are being backgrounded to new numbers. This is due to AS9 not being compatible with alpha character work orders. In this process several MWOs have been changed which are referenced within PPM 13.14.4. These changes were not communicated to Emergency Preparedness prior to implementation so that all the impacts could be recognized addressed. <I> **** Actions Taken **** Discussed situation with the EP Planner and discussed path forward. This is an administrative issue. No PM frequencies were changed. See EDMS for list of MWOs changed.
400525 | CR | 20191024 |  | 3 | R25 P06 spreadsheet fails to update |  |  |  | N | NO | <D> **** Detailed Description **** The R25 P06 spreadsheet that has been used by engineering does not always update when the â€œUpdate External Review Dataâ€ button is clicked. The spreadsheet gives a notice and looks like it updates, but it actually does not update. This may have to do with how the spreadsheet is filtered at the time. This was just discovered after supervisors have been using this data to select scope. The scope data that they are reviewing is not correct, since it was not saved correctly when the engineers clicked the save button. Multiple attempts have been made to save the same data and confirmed later that is has not saved. This is causing major rework, since it is unknown if the supervisors reviewed the correct scope recommended by the system engineers. The CRD HCU and SSPV PMs are a prime example. The scope was entered into the spreadsheet multiple times. It shows as updated. Closing and reopening the spreadsheet and getting â€œExternal Review Dataâ€ brings back data that has not been updated. <N> The spreadsheet developer discussed with Engineering. No more actions necessary.
400527 | CR | 20191024 |  | 4 | RW 487' Lighting out in janitorial closet | N | N |  | N | YES | <D> **** Detailed Description **** The lights in the janitorial closet on RW 487' are completely out. This is a safety hazard since there are tripping hazards in the room. <I> **** Actions Taken **** Informed Shift Manager. Wrote CR. <N> **** Equipment Description **** RW 487' janitorial closet lighting
400528 | CR | 20191024 | CAQ | D | 3 Pieces of M&TE Rejected | N | N |  | N | NO | <D> **** Detailed Description **** 3 Pieces of M&TE Rejected. Calcode #0064143 Astro-Med Data Acquisition Recorder- model DASH 8XE was Not Used During Calibration cycle. Unable to power up unit. No Longer Supported by Mfg. DEF #7357A written. Calcode #0068032 Thomas/Betts Crimper- model ERG4001 Passed Calibration and Now Rejected- missing parts- unable to order. DEF #7358A written. Calcode #0064702 Ashcroft Gauge 30psi was Not Used During Calibration cycle. Needle broken on gauge- can't take readings. DEF #7359A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
400529 | CR | 20191024 |  | 4 | M&TE OOT | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0067681 Mitutoyo OD Mic- model 103-260 found OOT & adjusted within spces. Not Used During Calibration cycle. DEF #7360A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
400530 | CR | 20191024 | CAQ | D | M&TE Rejected | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #0059181 Amp Crimper- model 59824-1 Passed Post Use Veifications with GO/NOGO Plug Gages. Ratchet Does NOT Hold. Rejected. No Plant Impact. DEF #7362A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
400535 | CR | 20191024 |  | 3 | OPDS Test Anomaly for certain HIF | N | N |  | N | NO | <D> **** Detailed Description **** During OPDS design testing to validate recent changes to TRS and TRB OPDS relay settings a test anomaly was identified for High Impedance Faults (HIF) at the primary of the TR-S bushings and TR-B bushings under standby (no -load) system operating conditions. . Test results indicate for certain simulated HIFs with the line energized with the transformer operating in standby sufficient overcurrent is produced that will exceed minimum pickup of the OPDS relay that will initiate a trip signal. Since the test procedure was written with a general no trip acceptance criteria for transformer standby operating conditions the result is considered a test anomaly. . The purpose of the OPDS is to detect open phase faults on the primary of the TR-S and TR-B high voltage interconnections. The capability to respond to high impedance fault contributions in the detection logic was added later by the NRC as another provision and subsequently adopted by the NEI OPC VII that Columbia is committed to. The objective to include high impedance fault contribution at the protection system level is to augment legacy ground fault protection (not replace it) in order to cover line faults that range from a high impedance short circuit to a pure open circuit (with no ground fault). . The observed test result does not invalidate this overall design objective, however, the test was not setup to recognize that certain high impedance ground faults would generate sufficient overcurrent levels to actuate the OPDS relays even with the transformers operating in standby (i.e., the high voltage tie line is energized with no-load connected to the respective transformer). . The purpose of this AR CR is to note the subject test anomaly and to provide the appropriate evaluation (accept as-is disposition) and any recommended follow up actions. . Recommend this AR-CR be assigned to Design Engineering (Owed to group DEI) as a severity 3 with assignment to document the evaluation of the test anomaly. . NOTE: This CR describes a documentation issue with a design test for OPDS and does not affect operability or functionality of a plant SSC. <I> **** Actions Taken **** Discussed with Engineering Management.
400536 | CR | 20191024 |  | 4 | CWPH Sump Flooding | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During Halogenation on 10-23-19 at approximately 1100, the sump drain below PS-V-25 in the B100 sample room began to discharge water. Water flow continued for about 10 min and then ceased, allowing the flooded water to recede back into the sump. <I> **** Actions Taken **** Contacted MCR to inform of situation and ask for possible direction. Was told CRS would be notified. Initiated CR. <N> **** Equipment Description **** CW Pump House Sampling room drain, B100.
400537 | CR | 20191024 |  | 4 | High Alarm Rate TN4HKB | N | N |  | N | YES | <D> **** Detailed Description **** High Alarm Rate TN4HKB Trouble Alarm Contact Security x2185 for information <I> **** Actions Taken **** CR/WR Initiated. Security Supervision Notified, Electrical Supervisor Notified. | 02-00-SEC-TN-4
400538 | CR | 20191024 |  | 3 | review 115kv source operability decisions in oi-53 |  |  |  | N | NO | <D> **** Detailed Description **** Oi 53 does not credit the White Bluffs 115 kv supply. Since OI 53 was last revised I believe the BPA added a capacitor bank at White Bluffs. Perhaps the White Bluffs line could be credited - IE either source available might make the back up power supply operable. Suggest Design Authority review this as he will be familiar with requirements and changes.
400539 | CR | 20191024 |  | 3 | Inconsistent Guidance on Audible SRD Alarm Testing |  |  |  | N | NO | <D> **** Detailed Description **** PPM 11.2.6.1 (Issuance and Retrieval of Personnel Dosimetry) is inconsistent in the guidance for performing audible alarm tests with self-reading dosimeters. Section 5.2.2 provides clear guidance for performing this task for individuals receiving DLRs (i.e., radiation workers). Section 5.3.1 provides vague guidance that does not align with section 5.2.2 for individuals only receiving SRDs (i .e., visitors). Section 5.3.1 should state that audible alarm testing for visitors should be performed in accordance with section 5.2.2. <I> **** Actions Taken **** Discussed gaps and expectations to comply with section 5.2.2 with technicians performing visitor briefs.
400540 | CR | 20191024 |  | 4 | CST cobalt-60 concentration spike | N | N |  | N | NO | <D> **** Detailed Description **** The CST experienced a spike in Co-60 on 10/3/19. The concentration is 2.72e-5 uci/ml. Since, the concentration is trending down but remains elevated. <I> **** Actions Taken **** Discussed at chemistry trending committee. Documenting for Trend. <N> **** Equipment Description **** CST
400541 | CR | 20191024 |  | 3 | Performance of SVs interfered with OLNC |  |  |  | N | NO | <D> **** Detailed Description **** The performance of PM 17302-01, ISP-MS-Q901 and PM 17326 -01, ISP-MS-Q911 caused the SP-1 to be cycled due to the root valves shutting from the Main Steam rad monitors. that this work should not be scheduled during OLNC since it interferes with our ability to get reliable data due to perturbation of the sample line. <I> **** Actions Taken **** Informed WWM, wrote CR <N> Need to change â€œThe performance of PM 17302-01, ISP-MS-Q901 and PM 17326 -01, ISP-MS-Q911 caused the SP-1 to be cycled due to theâ€ To read â€œThe performance of PM 16922-01, ICP-MS/PRM-Q401 and PM 16923-01, ICP-MS/PRM-Q402 caused the SP-1 to be cycled due to theâ€ Added Progress notes to the activities for PMID-RQ's 16923 -01 and 16922-01 to not schedule during the OLNC. Once the changes are made to the initial description of this CR it can be closed.
400542 | CR | 20191024 |  | 3 | Editorial Changes to OSP-INST-X301 |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of OSP-INST-X301, editorial errors were identified. Step 7.22.2 directs verification of AOA -V-51A indication. This step should read AOA-V-51B as the overall step of 7.22 is to open AOA-V-5B. Additionally, step 7.30 directs verification of WNA-AD-51B1. This step is wrong and should read WMA-AD-51B1. <I> **** Actions Taken **** OSP-INST-X301 corrections were identified and the CRS was notified.
400543 | CR | 20191024 |  | 4 | CW-CT-2A water level is >11 inches | N | N |  | N | YES | <D> **** Detailed Description **** CW-CT-2A water level is 12 inches. OPS 4 rounds direct initiation of a CR when >11 inches. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-CW-CT-2A
400544 | CR | 20191024 |  | 3 | eCNF application not working as expected |  |  |  | N | NO | <D> **** Detailed Description **** The Electronic Classification Notification Form (ECNF) application is not working as expected. <I> **** Actions Taken **** IS was notified of the condition. IS analyst is working with the application owner to evaluate and correct the issue. <N> Cause narrowed down to printer onfiguration issue on Internet explorer. Instructions in the 2nd screen of the ecnf app are in place for users to set the correct configuration.There are still additional actions needed to correct some Win 10 machines. EP has recommended NCAQ 3 to ITMGMT. IS will add additional assignments.
400545 | CR | 20191024 |  | 3 | Revise PPM 11.2.14.4 |  |  |  | N | NO | <D> **** Detailed Description **** PPM 11.2.14.4 step 6.9.9 states â€œRECORD any changes in the STS database to reflect the leak test and inventory activities. Please remove this step and work order related steps as the current STS software makes this process labor intensive with very little value added. In the future when Access Suite is updated a batch update choice would be convenient whereby eliminating having to update each source individually as they are generally inventoried and leak tested at the same time. <I> **** Actions Taken **** Discussed with RPSPO
400546 | CR | 20191024 |  | 3 | OG-RIT-601A IMDS incorrect | N | Y |  | N | YES | <D> **** Detailed Description **** Sample flow item 034 is 0035 and supposed to be 0050. Sample flow item 035 is 0010 and supposed to be 0005. OG -RIT-601A Sample Flow item 034 is 50 and Sample Flow item 035 is 0005 (Correct per Engineering) <I> **** Actions Taken **** Contacted Engineering Contacted Supervisor | 02-00-OG-RIS-601A
400547 | CR | 20191024 |  | 4 | Multiple issues with FP-SYS-P85 | N | N |  | N | YES | <D> **** Detailed Description **** While attempting to restore FP-SYS-P85 after maintenance (WR 29150923) , multiple issues were discovered. First, the alarm won't clear in the control room (FCP.2.16-5), which was apparently known by some but not documented on the existing WR prior to lifting the clearance. Second, the air compressor wasn't running and the air pressure indicator was pegged high (GT 60 oz) with the header depressurized. The pressure switch was mechanically agitated and the compressor started. There was also water coming out of the threaded gage connection, indicating it had overranged as a result of the system pressurizing, meaning that check valve FP-V-P85/18 leaked by. Need to replace FP-V-P85/18, FP-PI-P85/3, and calibrate/replace FP-PS-P85/3. Also the original problem that caused the alarm still appears to exist. <I> **** Actions Taken **** Closed FP-V-85/17 to isolate and therefore stop the compressor. Wrote caution clearance C-FP-SYS-P85-002 for config control. <N> **** Equipment Description **** ASD bldg | 02-00-FP-PI-P85/3,02-00-FP-PS-P85/3
400548 | CR | 20191024 |  | 3 | BWRI Exam Failures |  |  |  | N | NO | <D> **** Detailed Description **** Two students in BWRI did not achieve a passing grade on the final exam for the course. Remediation required, including administering a re-examination, per TDI-02 and documented on final TAR. <I> **** Actions Taken **** Reviewed examination with the students. Supervisors informed.
400549 | CR | 20191024 |  | 3 | Stator copper has higher trend post R23 | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The stator copper is sampled once a month on the demin outlet, the stator inlet and the stator outlet. There is usually an initial spike in copper post outage but the spike has not gone back down to normal on the stator inlet and the outlet sample points. It was trending down on the last sample. The dissolved oxygen for the system has remained in normal ranges so air in leakage is not a concern at this time. The trend needs to be investigated and this CR is written for trending purposes. <I> **** Actions Taken **** Notified the MCR, Chemistry Supervision, System engineer, and Chemistry system specialist
400550 | CR | 20191024 | CAQ | D | OG-RIS-601A has a floating neutral | N | Y |  | N | YES | <D> **** Detailed Description **** During the performance of WR 29152252 it appears the neutral isnâ€™t tied to the ground on OG-RIS-601A. There is 120VAC between Hot and Neutral but not between Hot and ground. <I> **** Actions Taken **** Notified Supervisor and CRS | 02-00-OG-RIS-601A
400552 | CR | 20191024 |  | 3 | Evaluate risk incurred with FP pump surveillances | N | N |  | N | NO | <D> **** Detailed Description **** Currently, the station performs required surveillances of FP-P-2A, FP-P-2B, FP-P-1, and FP-P-110 all in the same week. The first three are tested on one day, and FP-P-110 is tested the following day. This potentially sets the station up to be unable to perform all surveillances if a problem is encountered, and results in late dates not being spread out. The station should evaluate spreading these surveillances out over the course of a month rather than all in one week in the event problems are encountered resulting in protecting other fire pumps due to another non-functional fire pump discovered during surveillance activities. <I> **** Actions Taken **** Discussed with SM.
400553 | CR | 20191024 |  | 4 | South door lock into flocculator is broke. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** South door lock into flocculator is broke. The lock has started to come apart and I broke off my key in lock because it would not come out. Part of the key is still stuck in the lock. <I> **** Actions Taken **** Contacted supervision and wrote this CR. <N> **** Equipment Description **** South door into flocculator bldg.
400554 | CR | 20191024 | CAQ | D | Security recieved a constant malfunction on IDS 09 10 | N | N |  | N | YES | <D> **** Detailed Description **** Security recieved a constant malfunction on IDS 09 10. The affected zones need maintenance. Contact security for details. <I> **** Actions Taken **** CR/WR initiated. Security supervision notified. Compensatory measures initiated. | 02-00-SEC-IDS-E/S/9/10
400555 | CR | 20191025 | CAQ | D | Drywell O2 increasing with feed and bleed in progress | Y | N |  | N | YES | <D> **** Detailed Description **** In response to rising O2 concentration in the drywell, Operations has been performing a feed and bleed using N2 low flow makeup and periodic venting of containment. In spite of this, O2 levels continue to rise, exceeding the capacity of feed and bleed to lower O2 concentration which is currently 2% and up slow. Recommend the station prioritize and investigate potential leakage sources. <I> **** Actions Taken **** Discussed with SM. | 02-00-CMS-SR-20,02-00-CMS-SR-21
400556 | CR | 20191025 |  | 4 | COND-V-231D | N | N |  | N | YES | <D> **** Detailed Description **** when performing a backwash, cond-v-231D open light did not extinguish and prevented the backwash from starting. the switch had to be manipulated by another operator while i pushed the backwash start button to get the cycle to start suspect sticky limit switch <I> **** Actions Taken **** informed the mcr initiated CR.WR | 02-00-COND-V-231D
400560 | CR | 20191025 |  | 3 | Potential loss of procedural guidance. |  |  |  | N | NO | <D> **** Detailed Description **** In the past, SOP-HVAC/RB-TEST provided procedural guidance for starting Reactor Building Emergency Cooling System fans for supplemental cooling when desired. This SOP was recently converted to an OSP but the purpose of providing supplemental cooling was not transferred to the OSP. Recommend adding a section to SOP-HVAC/RB-OPS or similar that provides guidance to start these fans for supplemental cooling
400561 | CR | 20191025 |  | 3 | CRO1 tablet continues to fail to synchronize. |  |  |  | N | NO | <D> **** Detailed Description **** CRO1 tablet continues to fail to synchronize. This time, I also had to re-authorize when I initiated the attempt to synchronize. <I> **** Actions Taken **** Wrote this CR.
400562 | CR | 20191025 |  | 4 | Alarms during Halogenation | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The D030 Config Error alarm would come in on the Pace Setter Platinum (PSP) Controller in the Suez Halogenation trailer several times a minute and then self clear. The HeStop Alarm and Emergency Stop 1 alarm also came in and did not self clear. In the Dehalogenation Trailer the HalGAlm Alarm would come in on the PSP and self clear several times a minute. Pictues of alarm hisories are available. <I> **** Actions Taken **** Called specialist, contacted supervision, ended halogenation early.
400563 | CR | 20191025 |  | 3 | Procedure change OSP-RB/HVAC-Q101 |  |  |  | N | NO | <D> **** Detailed Description **** the second note under step 7.0 discusses starting fans for supplemental cooling which does not apply to this surveillance. This note should be removed. Also, step 7.1.1 installs a catch to gather condensation from an open drain. In this procedure, the fan runs for less than 10 seconds. The volume of condensation will be minimal and does not justify the time and dose to justify a catch to be installed. recommend removing step 7.1.1 (install catch) and 7.1.7 (request catch be removed) and renumber the remaining steps . Also evaluate removing the HP support task associated with the catch.
400564 | CR | 20191025 | CAQ | D | Insulation Damage Found on CMS-SR-21 | Y | N |  | N | YES | <D> **** Detailed Description **** During walk down of CMS-SR-20/21, severe insulation damage on CMS-FIS-2 located on CMS-SR-21 was found. Heat trace insulation for CMS-FIS-2 was found severely cracked, with a large section that had detached and fallen on the ground. Overall insulation quality of CMS-SR-21 is poor, with several other areas degraded. See EDMS for photos. <I> **** Actions Taken **** Iinitiated CR | 02-00-CMS-FIS-2,02-00-CMS-SR-21
400565 | CR | 20191025 |  | 4 | TSW-F-1A stuck in 'backwash' mode | N | N |  | N | YES | <D> **** Detailed Description **** TSW-F-1A stuck in 'backwash' mode D/p is 0, therefore no demand for backwash <I> **** Actions Taken **** Informed MCR | 02-00-TSW-F-1A
400566 | CR | 20191025 |  | 3 | Work stopped due to contamination of work area |  |  |  | N | NO | <D> **** Detailed Description **** Contamination found on tools and man lift used to replace lamps on RW 437 Worker requested contamination survey of tools used for the work. Contamination levels of up to 2,000 dpm/100cm2 and 10,000 dpm/pa-las on tooling and manlift( # E-EQ-SL6) decking. Affected areas deconned and work allowed to continue. Refer to survey 20191025-1 for details <I> **** Actions Taken **** Notified On Call HP Supervisor <N> Area was surveyed and decontaminated. No further actions required at this time per the RP Operations Supervisor.
400567 | CR | 20191025 | CAQ | D | SJAE CONDSR RAD HIGH alarm locked in. | N | Y |  | N | YES | <D> **** Detailed Description **** SJAE CONDSR RAD HIGH, H13-P602.A5.4-3, alarm is locked in. OG-RIS-612 and OG-RR-604 are both indicating about 45mr/hr, and the alarm setpoint is 49 mr/hr per the ARP. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-OG-RIS-612
400568 | CR | 20191025 |  | 4 | CAS-C-1B oil level low | N | N |  | N | YES | <D> **** Detailed Description **** On rounds CAS-C-1B oil level was approximately 1/8 of the sight glass or slightly lower. Logs state level should be between 1/8 and 1/2 level of the sightglass. Per the log instructions compressor is operable until level is out of sight low. Oil needs to be added soon. <I> **** Actions Taken **** Informed CRS | 02-00-CAS-C-1B
400569 | CR | 20191025 |  | 4 | Sink Hole by walk way between N2 tank and fuel oil tanks. | N | N |  | N | YES | <D> **** Detailed Description **** noticed a small depression where the dirt was dissappearing upon further investigationit appears to be a broken irrigation valve cover under the dirt that is broken and all the dirt above is falling in. area above is spongey. Placed a cone over the area. Please excavate and remedy the hole to make it safe. could be a hidden hazard if covered in snow. placed a cone over the the hole <I> **** Actions Taken **** placed a cone over the hole and wrote cr. <N> **** Equipment Description **** irrigation box by walkway between CN-TK-1 and FO-tk-1 cover
400570 | CR | 20191025 |  | 3 | FP-V-D51/306 bump hazzard | N | N |  | N | YES | <D> **** Detailed Description **** While performing PPM 15.3.12 it was noticed that FP-V -D51/306 (1/2" ball valve) is positoned in a way that could be easily bumped out of position when traveling through door T-102. It is approxamately 10"-12" from the the edge of the door when it is opening. The valve should be re -positioned further down the line or a more robust means of keeping the valve in the open position should be installed. Valve currently only has a breakable seal on the handle. | 02-00-FP-V-D51/306
400571 | CR | 20191025 | CAQ | D | Erratic control of flow through OG-SR-3 | N | Y |  | N | YES | <D> **** Detailed Description **** During normal operations the control room operator noted a high (radiation) level alarm on the off gas pretreatment radiation monitor. The shift chemist was sent to investigate. During the investigation moisture was noted in OG-FIC-3/2 and the Moisture Blowdown of OG Drains portion of 12.2.2, Sampling System Components Locations and Valve Lineup, was initiated. During the performance of the line blowdown excessive moisture was noted. After blowing down the line the flow as indicated on OG-FIC-3/2 pegged high >150 mm (normal flow is approximately 60 mm, 51-93 mm) even with the flow control valve fully shut. After 20 minutes normal radiation levels were noted by the control room operator as indicated by the OG pretreatment radiation monitor. On-shift chemist then performed a followup sample of the OGPT and noted that flow as indicated on OG-FIC-3/2 had returned to normal (60mm) but with moisture in the line <I> **** Actions Taken **** Chemistry supervisor notified. CRS/SM and control room operator notified. Compensatory sample taken. | 02-00-OG-FIC-3/2
400572 | CR | 20191025 |  | 3 | RCC-P-1C Motor High Temperature | N | N |  | N | YES | <D> **** Detailed Description **** RCC-P-1C appears to be increasing in temperature. . AR# 390197 was written in regards to high motor temperature on the 'B' motor on 2-20-19, which had a motor temperature of 214F . It states a FLIR camera was used to measure the exhaust temperatures. In that AR, RCC -P-1C motor temperatures were stated to be approx. 175 -185F. Using a FLIR camera today, the motor internal casing, viewed through the exhaust ducts, was 200F for the upper part of the motor, and 222F for the lower part of the motor. AR 390197 states the continuous rating for the 'B' motor to be 95C.95C is 203F. It is assumed that 'C' is also 95C as the motors appear identical. Ambient temp. today was 78F. Engineering needs to evaluate motor. <I> **** Actions Taken **** discussed with SSS and notified CRS. | 02-00-RCC-P-1C
400573 | CR | 20191025 |  | 3 | Editorial PCR - TSP-THERM-C101 |  |  |  | N | NO | <D> **** Detailed Description **** TSP-THERM-C101 step 7.2.4 says to verify "e.g. '2 LOOPS ON' " but ACUMAN does not have a 2 LOOPS ON parameter. There is an "Active Loops 2" parameter that should be used instead. <I> **** Actions Taken **** Discussed with CRS, wrote CR.
400574 | CR | 20191026 |  | 4 | RFT-SI-A Indicating Suspiciously Low | N | N |  | N | YES | <D> **** Detailed Description **** RFT-SI-99T/1A, the speed indicator for the RFW-DT-1A, indicates 4500 RPM lower than expected for full power operation. All other RFT indications are normal. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** T 441 This instrument was de-energized when the RFT-A overspeed circuit was inadvertently de-energized and is scheduled to be restored during the December 2019 sequence exchange (reference CR 399764; WO 02151429). | 02-00-RFT-SI-99T/1A
400577 | CR | 20191026 | CAQ | D | Received Rod Accumulator Trouble Alarm for HCU 2203. | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-22-03. Alarm was due to accumulator water level. <I> **** Actions Taken **** Drained accumulator to clear alarm. | 02-00-CRD-HCU-2203
400578 | CR | 20191026 |  | 4 | Security camera CCTV 23T needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security camera CCTV 23T is not operating by design and needs maintenance. Contact security at 2185 for details. <I> **** Actions Taken **** CR/WR initiated. Security supervision notified. Equipment taken out of service. | 02-00-SEC-CCTV-23
400579 | CR | 20191026 |  | 3 | Procedure enhancement of SOP-ELEC-AC-LU. |  |  |  | N | NO | <D> **** Detailed Description **** E-CB-PP3CA/16 is now a SPARE breaker in OFF per EC 18009. SOP-ELEC-AC-LU page 179 needs to be updated to reflect this change. <I> **** Actions Taken **** Hung caution clearance.
400580 | CR | 20191027 | CAQ | D | Received Rod Accumulator Trouble Alarm for HCU 1419. | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-14-19. Alarm was due to low N2 pressure. Accumulator was recharged and alarm cleared. <I> **** Actions Taken **** Accumulator was recharged and alarm cleared. | 02-00-CRD-HCU-1419
400581 | CR | 20191027 | CAQ | D | Rods required increased drive header pressure to move | Y | N |  | N | YES | <D> **** Detailed Description **** During the performance of OSP-CRD-M701, rods 54-43 and 30 -11 required increased drive water pressure to move from position 48 to 46. Initial drive header pressure was 265 psid and final drive header pressure was 295 psid when they moved. Rods did not indicate stuck during movement. CR written for trending. <I> **** Actions Taken **** Increased drive header pressure per ABN-ROD, informed CRS and STA/IA, returned drive header pressure to normal after movement. | 02-00-CRD-DRVE-3011,02-00-CRD-DRVE-5443
400587 | CR | 20191027 | CAQ | D | Annunciator glitch during ISP-MS-Q943 | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of ISP-MS-Q943, I/C craft were repeatedly bringing in RC-2 half trips (P601 A11 2-2). Normally this alarm locks in and has to be reset using WMA-RMS-FAZ/3BXY before the anunciator can be reset. At step 7.10.14 when this alarm came in, it went to reset immediately after the RO acknowledged the alarm at P601. <I> **** Actions Taken **** Supervision was involved and after thorough review it was determined to be an issue with the annunciator and the ISP was continued. The same RC-2 half trip was brought in multiple times after with no further event. Suggest closing to trend. Proper annunciation was observed several times during this surveillance. The surviellance was completed SAT adn this condition appeared to be associated with annunciator only. There are no operability concerns with any equipment tested during performance of ISP-MS-Q943. Recommend trending this condition. | 02-00-E-CP-H13/P601
400588 | CR | 20191027 |  | 4 | Failed E-light annual inspection | N | N |  | N | YES | <D> **** Detailed Description **** 02143173-01 EBU SWS2/2 and 2/3 faild the 1.5 hour run. Both lights failed to stay illuminated the full 1.5 hours. Both LED indications were bad battery. We do not currently have any batteries in stock in building 19, where we store batteries. <I> **** Actions Taken **** Supervisor and CRS were notified. An impairment needs to be written and lanterns need to be placed by the defective EBU. New batteries need to be ordered. Non-essential lighting in the turbine building. Impairament 19-0277. <N> **** Equipment Description **** E-BU SWS2/2 479' TG Stairwell E-BU SWS2/3 488' TG Stairwell | 02-00-E-BU-SWS2/2,02-00-E-BU-SWS2/3
400589 | CR | 20191027 |  | 4 | RW 487 SE Corner Grating needs to be secured down | N | N |  | N | NO | <D> **** Detailed Description **** During a Routine survey by HP a section of grating was found to be missing a clip that would secure the grating down. If the East side of the grating is stepped on the west side will lift up. The section of grating is small and it does not appear that the entire section of grating could raise completely and fall but it can cause a tripping hazard. THis area has very little foot traffic. The section is SE corner of the RW 487' approx R4/10.3 near Decon COND Vapor Body <I> **** Actions Taken **** Secured the grating with tie wraps to mitigate the grating being able to raise when stepped on. Initiated this CR. Notified RP supervision and MCR <N> Image E0205 was mistakenly added and does not pertain to the CR
400590 | CR | 20191028 |  | 4 | Security XD 3 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security XD 3, explosive detector in the PAAP is not operating by design and needs maintenance. Contact security at 2185 for details. <I> **** Actions Taken **** CR/WR initiated. Security supervision notified. Equipment taken out of service. | 02-00-SEC-XD-3
400591 | CR | 20191028 |  | 4 | Security XD 6 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security XD 6, explosive detector in the PAAP is not operating by design and needs maintenance. Contact security at 2185 for details. <I> **** Actions Taken **** CR/WR initiated. Security supervision notified. Equipment taken out of service. | 02-00-SEC-XD-6
400602 | CR | 20191028 |  | 4 | Building 9 sprinkler escutcheon hole in ceiling too big | N | N |  | N | YES | <D> **** Detailed Description **** A sprinkler in the Building 9 mens bathroom has a gap around the escutcheon. The hole in the drywall ceiling is too large for the escutcheon to cover and needs to be repaired. This is a Facilities job. <N> **** Equipment Description **** Building 9 mens bathroom
400603 | CR | 20191028 |  | 3 | Expired Standard in Environmental Services Lab |  |  |  | N | NO | <D> **** Detailed Description **** On 10/27/19 the EPA 8260C method used to analyze the CGS groundwater samples was attempted to be calibrated. It was found that the verification standard used for the Ketone analytes had expired on 10/5/19. The analytical hold time for the first set of quarterly groundwater monitoring wells ends on 10/29/19. A replacement standard will not be available before the hold time ends. The first set of quarterly groundwater monitoring wells will have to be re -sampled in order to be analyzed with valid standards. <I> **** Actions Taken **** Initiated CR. Notified environmental services supervisor and sampling coordinator. Replacement standard has been put on ordering sheet. Recommend CR assignment to AR-ENLAB
400608 | CR | 20191028 | CAQ | D | EDNA pont W150 reading incorect | Y | N |  | N | YES | <D> **** Detailed Description **** Reading obtained with te pump running and secured show the RTD is providing a reading technician recommends disconnecting the terminal connections and using a simulation to shot a signal in the loop to identify where the signal is degrading going to TDAS. If no other indications, then recommend replacing RTD. <I> **** Actions Taken **** Wrote CR | 02-00-RHR-TE-509
400609 | CR | 20191028 |  | 4 | HTP-FP-5 Low Temp light flashing and Power On light is out | N | N |  | N | YES | <D> **** Detailed Description **** 2F Low Temp light is flashing and 16F Power On light is not lit on HTP-FP-5. <I> **** Actions Taken **** Initiated CR. Checked that the 16F Power On lightbulb was not burn out. <N> **** Equipment Description **** North wall in CST pit.
400610 | CR | 20191028 |  | 3 | eSOMS late entry for Maintenance |  |  |  | N | NO | <D> **** Detailed Description **** Late entry for Maintenance worker org code 52234. Manloading showed worker as scheduled to be here, but eSOMS did not reflect the same information. <I> **** Actions Taken **** Supervisor corrected eSOMS. No further actions required.
400611 | CR | 20191028 |  | 4 | HTP-FP-8 44F Loss of Continuity light is flashing. | N | N |  | N | YES | <D> **** Detailed Description **** HTP-FP-8 44F Loss of Continuity light is flashing. According to placard on the panel, 44F is for a 4" anti -siphoning vent. <I> **** Actions Taken **** Initiated CR <N> **** Equipment Description **** Western wall on the outside of Flocculator building
400612 | CR | 20191028 |  | 3 | Late eSOMS entry for Maintenance |  |  |  | N | NO | <D> **** Detailed Description **** Late entry for Maintenance worker org code 52235. Manloading showed worker as scheduled to be here, but eSOMS did not reflect the same information. <I> **** Actions Taken **** Supervisor corrected eSOMS. No further actions required.
400613 | CR | 20191028 |  | 4 | ASD door lock is really difficult to operate. |  |  |  | N | YES | <D> **** Detailed Description **** The lock for door A-100 for the ASD building is stiff and really difficult to operate and remove the key from. <I> **** Actions Taken **** Initiated CR <N> **** Equipment Description **** West wall of ASD building.
400616 | CR | 20191028 |  | 3 | Deltas observed with procedure 11.2.9.15 AMS-3 CAM |  |  |  | N | NO | <D> **** Detailed Description **** Deltas were noted in procedure 11.2.9.15 while performing on the job training for the use of AMS-3 airborne contamination monitors. No prerequisites are listed in section 3.0 yet there is a qualification associated with the task. Additionally, section 5.1.5.b calls for an indication of 42 LPM flowrate. The AMS-3 units in the field have a calibration reference mark at 30 LPM. <I> **** Actions Taken **** Informed supervision and generated CR
400619 | CR | 20191028 | CAQ | D | Double doors leading into 467RW vital island will not open | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of breaker transport into the 467RW vital island, the double doors across from the 467RW control room leading into the vital island could not be opened. Security and Craft failed at multiple attempts to open these doors. These doors appear to have 3 cam style bolts where the center one maybe in-operative. Reccomend further investigation and repair by machinist/mechanics. <I> **** Actions Taken **** This AR/CR and associated WR written in order to rectify the issue. <N> **** Equipment Description **** Double doors that lead into vital island at M.0/13.0 467RW
400621 | CR | 20191028 | CAQ | C | Water present at the discharge of HPCS-V-80 and 81 at start | Y | Y |  | N | YES | <D> **** Detailed Description **** Water present (1/8 of a cup) at the discharge of HPCS-V-80 and 81 at start of the quarterly test, as well as about a teaspoon of water on the actual seal. <I> **** Actions Taken **** informed the crs and wrote a cr . HPCS-V-80 and -81 are both normally OPEN per SOP-HPCS-LU and M520. They are the drains from the HPCS-P-1 mechanical seal. | 02-00-HPCS-P-1
400622 | CR | 20191028 |  |  | OFFGAS EXHAUST FLOW HI/LOW alarm locked in |  |  |  | N | YES | <D> Alarm P672 A9 1-8 OFFGAS EXHAUST FLOW HIGH/LOW was recieved. No change noted on OG-FR-620 or on EDNA traces. OG-FIS-35 and 36 are reading normally. EDIT- This is a duplicate CR due to Asset Suite error. This AR/CR should be closed <I> Informed Shift Supervision, monitored parameters, established temp log with CRO1 <N> At the request of the initiator, this CR will be cancelled. | 02-00-OG-FIS-35,02-00-OG-FIS-36,02-00-OG-FR-620
400623 | CR | 20191028 |  | 4 | OFFGAS EXHAUST FLOW HI/LOW alarm locked in | N | N |  | N | YES | <D> **** Detailed Description **** Alarm P672 A9 1-8 OFFGAS EXHAUST FLOW HIGH/LOW was recieved. No change noted on OG-FR-620 or on EDNA traces OG-FIS-35 and 36 are reading normally. <I> **** Actions Taken **** Informed Shift Supervision, monitored parameters, established temp log with CRO1 | 02-00-OG-FIS-35,02-00-OG-FIS-36,02-00-OG-FR-620
400626 | CR | 20191028 |  | 4 | Industry issue with interpretation of RIS 2016-011 |  |  |  | N | NO | <D> **** Detailed Description **** This CR does not contain a violation of site procedures, FSAR requirements or current regulations by CGS. This CR documents an industry regulatory issue. . Recent industry meetings on Very Low level Waste (VLLW) disposal have identified an issue with NRC guidance for using the 10 CFR 20.2002 process for licensees that have been approved by the NRC. The issue being discussed pertains to Agreement state radioactive material licensees disposing of VLLW at an unlicensed disposal facility. In RIS 2016-011 the NRC states that in cases where a nuclear reactor facility is located in an Agreement State, the NRC has the legal basis for performing the reviews and granting approvals for this disposal process. Guidance prior to RIS 2016-011 directed that the alternate disposal process would have been approved by the Agreement State instead of the NRC. CGS has not sent VLLW radioactive waste to an unlicensed burial site. All radioactive waste shipments have been to NRC licensed facilities. <I> **** Actions Taken **** RPM notified. RP to participate in industry forums and discussions on the issue. Close to trend.
400628 | CR | 20191028 |  | 3 | FORM 26981 needs to be revised |  |  |  | N | NO | <D> **** Detailed Description **** Form 26981 Rev2 sheet 2 of 3, block 8 currently states 'As-Found Seat Tightness' but should say 'As-Left Seat Tightness'. <I> **** Actions Taken **** Wrote CR <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
400629 | CR | 20191028 |  | 3 | New light fixture in MT-ELEV-3 required due to change |  |  |  | N | YES | <D> **** Detailed Description **** As part of the state elevator enhancements, a second access hatch was added to MT-ELEV-3 on the turbine bldg side. The new hatch interferes with the south lighting fixture in the elevator cab. KONE recommends that both 36" light fixtures be removed and a single 48" LED be installed to meet the correct lumen(s) requirement. <I> **** Actions Taken **** South lighting fixture was removed to allow the hatch to be installed. Notified the FIN supr that electrical support is required to complete the state required enhancements. KONE will have MT-ELEV-3 out of service until the end of shift 10/31. <N> AR-EVAL-400660 has been initiated and assigned to AR-EFIN | 02-00-MT-ELEV-3
400630 | CR | 20191028 |  | 3 | Operations Procedure Consideration |  |  |  | N | NO | <D> **** Detailed Description **** Consider adding a procedural process to insert control rods using the SCRAM test switches for rod line control during a plant transient. Based on a recent BWROG Reactivity Control Review Committee meeing, it was noted that many plants have this option in case the normal control rod drive control system is not functional during a transient, and rod line needs to be reduced. This issue was discussed at the site Reactivity Management Review Committee today and it was concluded that this option should option should be considered. Recommend assignment to Operations.
400631 | CR | 20191028 |  | 4 | Training attendance record sent without supporting documenta |  |  |  | N | NO | <D> **** Detailed Description **** Records recieved training attendence records from training without supporting documentation. Supporting documentation is needed for processing. <I> **** Actions Taken **** Notified supervision, and sender. Created CR for trending purposes only. <N> These were ETAR records resubmitted to Records after documentation was not attached following original submittal. These ETAR records do not have training material attached to them, and Records Coordinator for Training Department was directed by an individual in Records Control to resubmit the records with a note stating why there was no attachment. Another Records Management Specialist processed these records and initiated CR, with the understanding that these records require documentation. Training Records Coordinator is working with Document Control Lead to understand whether these documents require to be sent to Records Control or not. These ETARs are currently locked in the cabinet and the afternoon Training WBL student will unlock these to send over to Document Control Lead for alignment and resolution.
400632 | CR | 20191028 |  | 3 | Student Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** HP technician failed HP continuing training exam. Remediation is scheduled and will consist of objective review followed by retaking exam <I> **** Actions Taken **** Training Supervisor and RP Supervision notified. Failure documented in eTAR. This is for trending only. eTAR Class ID #856655 <N> Individual was administered remedial exam and passed the exam. No further actions needed.
400633 | CR | 20191028 |  | 4 | Radwaste Processing Challanged by PWR-CRA-1 | N | N |  | N | YES | <D> **** Detailed Description **** PWR-CRA-1 is broken and limiting the ability to offload resin. Radwaste control room tanks are filling up and the ability to backwash filters is now limited. There is only 10 cuft in FDR-TK-22, 14 cuft in RWCU-TK-104B (104A is full), and 170 cuft in CPR-TK-92B (CPR-TK-92A is full). <I> **** Actions Taken **** Added PWR-CRA-1 to the PCL list. This CR identifies the impact due to the broken crane only. | 02-00-PWR-CRA-1
400634 | CR | 20191028 |  | 3 | WO 02114325 Implementation Issues |  |  |  | N | NO | <D> **** Detailed Description **** WO 02114325 was found to have insufficient work instructions to perform the work as scheduled. Based on the existing work instructions, incorrect resources were assigned and therefore adequate walk downs were not completed. As an example, Task 03 requires detailed work instructions on performing hard drive cloning and resources should changed from Computer Engineering (ENIS) to IS resource (ISAN). Resource hours will need to be verified during walk downs <I> **** Actions Taken **** Discussed with WWM, I&C Supervision, Comp Eng Supervisor, and generated CR. . Need to understand how this was not caught on the walkdown. WO 02114325 was scheduled to be done today. It is a PM WO scheduled every 4 years, but has NOT yet been performed. This has been on the scheduled since T-7. | 02-00-DEH-COMP-3
400635 | CR | 20191028 |  | 3 | eSOMS Calculation Error for Hydrogen Total Leakage Log |  |  |  | N | NO | <D> **** Detailed Description **** Hydrogen leakage (7-day average) calculated log entry on Ops 3 logs have been frequently calculating in error. Once the reading is calculated in error once and the log has been reviewed, the error â€œcarries forwardâ€ on subsequent shift logs since it is a running average. Reading is erroneously high. <I> **** Actions Taken **** Informed ops support. Initiated CR to address potential bug in eSOMS calculation method. <N> **** Equipment Description **** ESOMS OPERATOR ROUNDS (OPS 3)
400636 | CR | 20191028 |  | 4 | North side PAAP loose sheet metal on roof | N | N |  | N | YES | <D> **** Detailed Description **** Loos sheet metal North Side of PAAP next to security IDS zones. <I> **** Actions Taken **** Security located loose sheet metal, notified supervision, CR/WR generated <N> **** Equipment Description **** North side of PAAP entrance roof
400637 | CR | 20191029 |  | 4 | Door D104 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** The door knob on D104 needs maintenance. It appears that the throw is getting stuck. <I> **** Actions Taken **** Security notification made, CR/WR generated | 02-00-D-DOOR-D104
400638 | CR | 20191029 | CAQ | D | MW-01 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** MW -01 needs maintenance. Contact security at ext. 2185 for further details. <I> **** Actions Taken **** Comp in place, security notification made, CR/WR generated | 02-00-SEC-MW-1RA
400639 | CR | 20191029 |  | 4 | Received P602-A6 3-4 ASD/A Input Xfmr Trouble | N | N |  | N | YES | <D> **** Detailed Description **** On 10-29 at 0305 MCR received 4.602.A6 drop 3-4 ASD/A Input Xfmr Trouble. Reactor power pressure and Level remained normal and steady for 100% Reactor power. No changes in RRC flow were in progress. Average air temperature was approximately 29-30F. Local inspection noted no abnormalities, suspected low air temperature may be at fault. <I> **** Actions Taken **** Informed CRS. Dispatched operator to investigate. | 02-00-RRC-TR-1A1
400647 | CR | 20191029 |  | 4 | Steam Leak on SMA-HC-1 "L" | N | N |  | N | YES | <D> **** Detailed Description **** Steam leak identified on SMA-HC-1 on L coil. Isolated by closing HS-V-S6L and HCO-V-S6BB. Opened HCO-V-S6BD to drain. <I> **** Actions Taken **** Notified CRS and isolated steam leak | 02-00-SMA-HC-1
400648 | CR | 20191029 |  | 4 | HS-V-713A Leakby | N | N |  | N | YES | <D> **** Detailed Description **** HS-V-713A leaking by with steam. Mechanical agitation lessened leakage but did not stop it completely. <I> **** Actions Taken **** Generated WR/CR | 02-00-HS-V-713A
400649 | CR | 20191029 | CAQ | D | 2 Pieces of M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** 2 Pieces of M&TE OOT & adjusted within specs. EFIN Evals: Calcode #45250 Teltek NW Dig. Themometer- model Informer I Not used for data. DEF #7353A written. Calcode #0067109 NCS Refrigeration Monitor- model LMP-3000. Per Certificate of Conformance, As-Found was in Tolerance. DEF #7361A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
400651 | CR | 20191029 | CAQ | C | FP-ENG-1 Exhaust fit up issues |  |  |  | N | YES | <D> **** Detailed Description **** During the fit up of the FP-ENG-1 the turbo exhaust to our exhaust stack has a misalignment issue from the new 4 bolt turbo mounting plate that was installed at Cummins. It looks to be offset by approximately 2â€. Recommend assignment to fire protection engineering to work with maintenance for resolution. . See EDMS for pictures <I> **** Actions Taken **** Notified MCR, WWM, Fire protection engineer, planning and initiated CR. | 02-00-FP-ENG-1
400652 | CR | 20191029 |  | 3 | MLAB task requires hours adjustment to Model PM |  |  |  | N | NO | <D> **** Detailed Description **** WOT 02120139-01 (perform flammable cabinet checks) is normally scheduled for one hour, to include pre-job briefs and paper closure. This task and model PM should be scheduled for four hours total. <I> **** Actions Taken **** Discussed with work week manager, who requested that a CR be written. <N> WOT 02120139-01 model WO have been adjusted. No further actions required per the RP Operations Supervisor.
400653 | CR | 20191029 |  | 3 | MLAB task requires hours adjustment to Model PM |  |  |  | N | NO | <D> **** Detailed Description **** WOT 02141064-01 (In-plant respirator inspection) is currently scheduled for a two hour duration, to include pre-job briefs and paper closure. This task requires activities that may require multiple days, so the task and model PM should be scheduled for two ten hour days. <I> **** Actions Taken **** Discussed with work week manager, who requested that a CR be written. <N> WOT 02141064-01 and model WO have been adjusted. No further actions required per the RP Operations Supervisor.
400655 | CR | 20191029 |  | 4 | OG-FIC-3/2 changed without instructions for chemistry |  |  |  | N | NO | <D> **** Detailed Description **** This past weekend, on 10/25/19, OG-FIC-3/2 was replaced with a new model through EC-18009. The new model reads in units of SCFH, while the previous model read in units of mm. Daily readings of this indicator are made by chemistry via CI-15.2, Daily Monitor Data. The guidance in CI-15.2 instructed chemistry technicians to adjust flow on OG-FIC -3/2 to between 51mm and 93mm. This instruction is not compatible with the new meter, which reads in SCFH. A task was included in EC-18009 to update CI-15.2, but this was not coordinated with the installation due to emergent issues (CR 400571) requiring early installation of the flow indicator. This left the chemistry shift technician with incomplete instruction for taking readings on OG-FIC-3/2 the morning following installation. The issue has been resolved with the release of CI-15.2 REV 034 on 10/29/19. <I> **** Actions Taken **** Spoke with supervision. Provided a table in EC-18009 to chemistry technicians for converting SCHF to mm on OG-FIC -3/2. Updated CI-15.2 to reflect the change in units at OG-FIC-3/2.
400656 | CR | 20191029 |  | 4 | Audible PA Speaker White Noise |  |  |  | N | YES | <D> **** Detailed Description **** There is audible white noise coming from the PA speakers. IS Reply to Email/Voicemail: ChangeGear ticket IR-0046907 has been generated for this issue. Please note that it is common for the PA background audio level to change when control is transferred to the Simulator for a drill. <I> **** Actions Taken **** Initiated CR and informed supervision. Called and emailed IS to initiate ChangeGear ticket IR-0046907 PA is working to support EP functions - this is just a slight white noise that does not impact the function of the PA. <N> **** Equipment Description **** PA Speakers
400657 | CR | 20191029 |  | 3 | Procedure clarification of SOP-HWC/HSSF-SHUTDOWN. |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.4.1 of SOP-HWC/HSSF-SHUTDOWN states "Verifiy replacedment bottle is LT 2265psig." As a general rule when we replace gas bottles we verify a "GT" pressure. Not sure why this currently states to verify a "LT" pressure. Doesn't make sense, please verify statement and intent to ensure it reads "GT". <I> **** Actions Taken **** CR written <N> **** Equipment Description **** SOP-HWC/HSSF-SHUTDOWN
400658 | CR | 20191029 |  | 4 | Bananna Jacks need to be installed for PPM 16.4.6 & 16.4.9 |  |  |  | N | YES | <D> **** Detailed Description **** Bananna Jacks need to be installed due to high risk of shorting something out while hooking up test leads during work on 16.4.6 & 16.4.9. The location of terminals are not easy to access and all it would take is a mini grabber to fall off to put the plant in a unwanted condition. I/C shop has had issues in past with leads falliing off HRA relays and bringing in unexpected 1/2 scrams. They have since then installed bannana jacks on all HRA relays and have had no issues since. <I> **** Actions Taken **** Wrote this CR <N> **** Equipment Description **** 501MCR
400662 | CR | 20191029 |  | 3 | COND-P-2C TSW heat exchanger fouling | N | N |  | N | YES | <D> **** Detailed Description **** While performing SOP-TSW-FLUSH on the off-line COND-P-2C lube oil cooler (TSW-HX-6E) it was noted the flow as read on TSW-FG-1C was only around 2 to 3 gpm, while the flushing flows on COND-P-2A and 2B were full scale at GT 20 gpm. I cycled TSW-V-4E fully open and closed a couple of times but the flow rate never increased above the 2 to 3 gpm rate. This may be a sign of heat exchanger fouling or the new flow gauge TSW-FG-1C is in need of replacement. | 02-00-TSW-HX-6E
400665 | CR | 20191029 |  | 3 | R25 procedure change to SOP-ELEC-BOP-TEMPPOWER |  |  |  | N | NO | <D> **** Detailed Description **** SOP-ELEC-DIV2-TEMPPOWER was revised for installation and removal of temporary power for Building 62 (CAS) per EC -16093. (AR 390820, AR389321), however SOP-ELEC-BOP -TEMPPOWER section 25 and 26 E-MC-5A Temporary Power Installation/removal from E-SL-81 needs to be update to reflect the EC 16093 change. Mark-up attached in EDMS <I> **** Actions Taken **** Wrote CR
400666 | CR | 20191029 |  | 4 | CAS-C-1B has multiple oil leaks. | N | N |  | N | YES | <D> **** Detailed Description **** While adding oil to CAS-C-1B per WR 29152297, multiple oil leaks were identified on the compressor. One is on the east end where oil is dripping from the compressor discharge head. The second is on the compressor discharge line to the tank / receiver at the flex coupling between the compressor and tank / receiver. The third is on the oil scavenging line on the north side of the compressor dripping from a one inch pipe nipple where the pipe thread sealant looks old. There are pictures in the EDMS tab and in the attributes of the work request generated from this AR/CR. <I> **** Actions Taken **** Informed supervisor and wrote this AR/WR. <N> **** Equipment Description **** TG 441 G5/6.5 | 02-00-CAS-C-1B
400667 | CR | 20191029 | CAQ | C | RBM DNSC ALARM during W/O 021453697 | Y | N |  | N | NO | <D> **** Detailed Description **** received RBM DNSC alarm during W/O 02153697 APRM CHASSIS 4 repairs. The RBM B had a non critical self test fault. ARRM 4 is a reference APRM for this unit. APRM 4 was bypassed on P603 at the time. This alarm was not marked as expected during the maintenance activity. see EDMS for pics. Edge rod selected. RBM B input from APRM 2 is functional.
400668 | CR | 20191029 |  | 3 | DES-2-9 Attachment 8.2 step 1.1.13a does not work as written |  |  |  | N | NO | <D> **** Detailed Description **** DES-2-9 Attachment 8.2 (Creating an AR EVAL in Asset Suite) Step 1.1.13 (Excercise option 06 "Notify Owed-To of Action Requestion) cannot be performed if the AR EVAL initiator is a member of the Owed-To group because option 06 is unavailable to that initiator. As a result, DES-2-9 Attachment 8.2 Step 1.1.13 a was recently added directing the initiator to Excersise option 07, "Auto-Approve Action Request" instead. Although option 07 is available to the initiatator, it is not the only action actually required to advance the AR EVAL to APPROVED status. The direction provided by DES-2-9 Attachment 8.2 Step 1.1.13 a needs to be modified to reference DES-2-9 Step 4.3.7 which describes all the actions actually required to accomplish the desired result. . This is an administrative issue only.
400671 | CR | 20191029 |  | 4 | ROA-HC-1; R7D, R7E, R7F, R7K have small steam leaks | N | N |  | N | YES | <D> **** Detailed Description **** Pinhole steam leaks on the following heating cools: R7D, R7E, R7F, R7K of ROA-HC-1 (west side of HVAC unit). Associated trap EPNs incorporated for multiple work requests. | 02-00-HCO-T-R7D,02-00-HCO-T-R7E,02-00-HCO-T-R7F,02-00-HCO-T-R7K,02-00-ROA-HC-1
400673 | CR | 20191029 |  | 4 | CW PH out of spec low |  |  |  | N | YES | <D> **** Detailed Description **** CW PH was found out of spec low at 8.08 <I> **** Actions Taken **** Informed chemistry, informed CRS, wrote CR. | 02-00-CW-PHE-1
400674 | CR | 20191029 |  | 4 | TMU-V-6 Leaking | N | N |  | N | YES | <D> **** Detailed Description **** TMU-V-6 has ~1 GPM leak possinly at the packing. <I> **** Actions Taken **** Informed CRS, Wrote CR | 02-00-TMU-V-6
400676 | CR | 20191029 |  | 3 | Procedure enhancement for 4.603.A8 |  |  |  | N | NO | <D> **** Detailed Description **** tile 6-6 is for RBM downscale or trouble, but the actions do not address the trouble alarm. Reccomend we develop RBM trouble actions <I> **** Actions Taken **** Worte CR
400678 | CR | 20191029 |  | 4 | Late decision to move the SM-72/75 Work Window at T-2 |  |  |  | N | NO | <D> **** Detailed Description **** Due to the length of the Maintenance Window for the TMU-P -1B Replacement spanning 2 weeks and not finishing until late in the November 4 Work Week, the preferred confidence run of 7 days for TMU-P-1B before starting the SM-72/75 Maintenance Window in the November 11 Work Week was not going to be possible. This fact was known at the Scope Freeze T-7 Meeting for the November 11 WW. The WWM for that week asked during the T-7 Meeting if a shorter confidence run would be acceptable and the answer from Operations was yes and they were comfortable with the SM -72/75 window being performed in the November 11 WW. During the T-3 Review by the Operations crew, the Shift Manger again challenged the short confidence run and why we would not move the SM-72/75 Maintenance Window. With the second Challenge, Operations changed their position and directed that the work be rescheduled. This decision could have and should have been made long before T-2. This requires Rework for the station and personnel to re-schedule the SM-72/75 window and represents risk by moving the work late in the process. Due to the resultant underloading of the Electrical shop from the late removal, we are going to have to find more Electrical work to move in to the week. This is an Error Likely situation as we are moving work in to a Work Week very late in the normal process. Additionally, as part of PSOâ€™s Cycle Planning, we work with various departments, including Operations, to put out annual calendars and Cycle Plans well ahead of time to the station. On the original 2019 Work Week Calendar, the SM -82/85 Maintenance Window was scheduled for the October 28 WW, followed directly by the SM-72/75 Maintenance Window in the November 4 WW. This would not support a 7 day confidence run either. When we are making plans for our work weeks, we should make decisions that are supported by our processes & procedures and that we are willing to stand by as we get closer to implementation unless something unexpected happens or something changes. In the case of the SM-82/85 and SM-72/75 windows, nothing changed and nothing unexpected happened. We just did not stand by our decisions that had been made several times previously. <I> **** Actions Taken **** Working with the UC, Electrical shop, and Operations to reschedule the SM-72/75 Maintenance Window. Determining Electrical work that can be put in place of the removed work.
400679 | CR | 20191029 |  | 4 | Cardstock first aid injury |  |  |  | N | NO | <D> **** Detailed Description **** Individual in org 52120 received cardstock cut while putting cardstock in a box for recycling. The cardstock slipped under the individualâ€™s left thumb nail causing a small cut that required a band-aid. This has been classified as a first-aid injury IAW WAC 296-27. All notifications IAW ISPM-1 section 4.1.2 have been completed. <I> **** Actions Taken **** Applied band-aid, completed incident report, and made communications with Occ Health, Industrial Safety, and the MCR IAW ISPM-1.
400680 | CR | 20191029 |  | 3 | Generator Hydrogen Purity nearing 95%, 1 MWe loss accruing | N | N |  | N | NO | <D> **** Detailed Description **** Generator H2 Purity has been decreasing since the start of Cycle 25, from >98.5% down to ~95.5% currently. The rate of decline is slowing. Consider performing a H2 bleed and feed soon to take advantage of the additional 1 MWe of electrical generation possible at >98.5%. Because the rate of decline is slowing, waiting until the Generator reaches 95% may result in waiting several weeks. <I> **** Actions Taken **** Initiated CR. Discussed with Main Generator System Engineer and Control Room Supervisor.
400681 | CR | 20191029 |  | 4 | ISPM-1 First-Aid Report difficulties |  |  |  | N | NO | <D> **** Detailed Description **** ISPM-1 needs clarification to assist Managers and Supervisors with taking the required actions during a first-aid injury. The following deltas were identified when attempting to follow ISPM-1: â€¢ No definition in ISPM-1 for â€œfirst-aidâ€ injury â€¢ Step g. requires â€œemployeeâ€™s incident reportâ€, was able to find form 26135 in controlled docs although not referenced in the procedure. The form states (Completed by Safety) in the top right corner and â€œLog No:â€ indicating safety is the group that completes the Plant Tracking Log. â€¢ After discussions with Industrial Safety, the injured individual and/or supervisor is supposed to complete the plant tracking log entry. When entry attempted, the manager was not in the system under the supervisor panel and an entry could not be made. Recommend action to Industrial Safety to evaluate ISPM-1 for improvements in First-Aid injury reporting. <I> **** Actions Taken **** Contacted industrial Safety. <N> Industrial Safety performed a minor editorial revision on ISPM-1 to clarify the requirements for reporting first aid injuries and added the definition per WAC 296-27.
400683 | CR | 20191029 |  | 4 | E-CB-3/31 Lockout ckt available lamp flickers | N | N |  | N | YES | <D> **** Detailed Description **** E-CB-3/31 Lockout ckt available lamp flickers changed bulb - no change. Started after transferring E -SM-3 to TR-s and back to normal. Lamp is on BD C in MCR. suspect issue at E-SM-3. | 02-00-E-RLY-86T/3/31
400686 | CR | 20191029 |  | 4 | TDAS point X413 Out of Service | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02141089-01, ISP-CMS/PRM-M402, step 7.6.2, the data for TDAS point X413 all read -99, which is out of tolerance for all data points required. <I> **** Actions Taken **** Informed Operations and Supervision and it was determined to continue surveillance, and per step 7.6.12 write a Work Request for repair. <N> **** Equipment Description **** 501RW MCR
400687 | CR | 20191029 |  | 3 | ILC-23 remediation plans did not document line Involvement |  |  |  | N | NO | <D> **** Detailed Description **** During review of ILC-23 remediation packages from 2018, five remediation plans were approved by the Operations Training Supervision with no remediation plan approval documented by Operations. This is not in accordance with TDI-02 which states â€œline management must be involved in the remediation plan development.â€ Recommend form 26430, Operations Training Performance Deficiency Analysis and Remediation, be updated to state Operations Supervisor in the approval signature line, currently states â€œSupervisorâ€. This was identified during the Initial License Class Focused Self-Assessment. <I> **** Actions Taken **** Discussed with Operations and Training Management.
400688 | CR | 20191029 |  | 3 | ILC Mentoring Process not meeting all OI-27 Requirements |  |  |  | N | NO | <D> **** Detailed Description **** During the review of ILC-24 Observations of Training and through interview it was determined that the ILC mentoring process is not fully meeting the intent of OI-27, Hiring, Initial Class Selection, and Monitoring. There was no observation data available to establish crew mentors have performed their observations once per shift cycle IAW OI-27 Step 7.2.2. Also, interviews with students indicate when the mentoring meetings are occurring the topics have been limited to class performance and plant issues. OI-27 step 7.2.5 has a much more extensive list of topics as needed. This was identified during the Initial License Class Focused Self-Assessment. <I> **** Actions Taken **** Dicussed with Operations and Training Management.
400689 | CR | 20191029 |  | 3 | SRM lesson plan content did not contain one objective |  |  |  | N | NO | <D> **** Detailed Description **** System description SD000132 R12,mr1, for Source Range Monitor System, does not contain content for system learning objective 12005c â€œstuck detector.â€ The objective content was discussed during the PowerPoint presentation. This was identified during the Initial License Class Focused Self-Assessment. Recommend the addition of the objective content to the system description for sustainability. <I> **** Actions Taken **** Discussed with Operations and Training Management.
400690 | CR | 20191029 |  | 3 | DO-TK-2 analysis delayed due to california wildfires |  |  |  | N | YES | <D> **** Detailed Description **** The laboratory that performs the weekly EDG fuel analysis is located near San Francisco, CA. The laboratory currently is surrounded by wildfires and without offsite. power. DO-TK-2 surveillance sample is currently enroute, but receipt of results is uncertain. <I> **** Actions Taken **** A second DO-TK-2 sample has been taken and is being sent to another laboratory for analysis. Requested that the environmental lab get certified to perform this test in house. They have the equipment but need certification. <N> The DO-TK-2 Diesel sample, Chemistry Sample #19-2835, was shipped to Exelon PowerLabs on 10/29/19 and tested per ASTM D5452-06 under Environmental Services contract 353642. Diesel fuel samples are normally sent to SGS North America for testing by Chemistry. An Analysis of Diesel Fuel Oil report was provided by Exelon PowerLabs on 10/31/19. See EDMS Docs panel for copy of report and invoice. This assignment is complete. | 02-00-DO-TK-2
400691 | CR | 20191029 | CAQ | D | TSC-CP-RAD/1 is not working due to low counts on TSC-RIS-1B | N | Y |  | N | YES | <C> CR reopened to add completion required check mark to referenced WO 02136858 per SWP-CAP-01, then taken back to complete <D> **** Detailed Description **** The source for TSC-RIS-1B (the airborne radiation monitor for iodine) has decayed to a point that it is not strong enough to keep the monitor on scale , as designed, during operation. This problem has been known since 2015 and several AR's have been written. WO 2136858 is the latest work order written in the process of getting the unit back in service. <I> **** Actions Taken **** Notified Drill participants at TSC/OSC Notified Supervision | 02-00-TSC-CP-RAD/1
400692 | CR | 20191029 | CAQ | C | Part sealing surface angle in question AR for Procurement | N | N |  | N | NO | <D> **** Detailed Description **** It appears that the angle on the new part for CAT ID 74201463 .5IN X 37 DEG CONNECTOR (CRD-HCU P6 connectors) isnâ€™t the same a the new caps CAT ID 59300164. This sealing surface angle issue is causing leaks due , the sealing surface is just the tip of the connector. If a small blemish on that surface appears the connector tip the HCU will leak. Procurement should inspect the connectors and caps for conformity, FIN has had issues with installing new connectors and having them leak requiring craft to order new parts until they get on that seals. <N> **** Equipment Description **** hcu's Engineering to determine if CAT ID in question is currently installed in an HCU. If so then a new CR needs to be written to evaluate Operability of each affected HCU.
400694 | CR | 20191029 |  | 4 | Simulator THOR Abort |  |  |  | N | NO | <D> **** Detailed Description **** A Thor Abort occured during the 10/29/19 EP Drill. The simulator was reset within 1 minute and no data was lost. SR 3071 created to troubleshoot the issue. <I> **** Actions Taken **** Immediately backktracked 1 minute and reset. No issues after that. SR 3071 created to troubleshoot the issue.
400695 | CR | 20191029 |  | 3 | DEH spare computer needs repairs | N | N |  | N | NO | <D> **** Detailed Description **** It was identified that the spare computer for the DEH computers, needs added repairs before it can be used as a refurbished unit in the plant. It has 3 broken fans. Replacement fans will need to be purchased and work instructions will need to be added to work package. <I> **** Actions Taken **** Wrote CR, cross referenced WO.
400696 | CR | 20191029 |  | 4 | incorrect field copy revision |  |  |  | N | NO | <D> **** Detailed Description **** WO 2118522 MASTER 5 field copy was an incorrect revision. Control room noticed that the EWP was at working with an incorrect MASTER 5 revision. EWP was validated and the correct version was loaded. When paged checked, there was a difference between the field copy and the required copy. There were no revisions or dates in the master 5 which made it difficult to find the change. This is an error likely situation. <N> **** Equipment Description **** Main control room
400697 | CR | 20191029 | CAQ | D | IDS 5-6 Malfunction | N | N |  | N | YES | <D> **** Detailed Description **** CAS received a malfuction alarm on IDS 5 6. <I> **** Actions Taken **** Compensatory measures were posted. A walkdown of the area was conducted. Tumbleweeds were found and removed from the zone. A loose pin was also found on pole 26 in zone 5. Electrical maintenance was notified and a CR/WR was generated. | 02-00-SEC-IDS-E/S/5/6
400699 | CR | 20191029 |  | 4 | CW-FN-27 will not shutdown from control room. | N | N |  | N | YES | <D> **** Detailed Description **** While commencing de-icing operations, CW-FN-27 has failed to shutdown. OPS4 has verified that CW-FN-27 is running. <I> **** Actions Taken **** informed CRS and Maintanence. | 02-00-CW-FN-27
400700 | CR | 20191029 |  | 4 | HSSF-CAB-CHEM/LAB alarm | N | N |  | N | YES | <D> **** Detailed Description **** Recieving frequent Hydrogen Tube Trailer Pressure Low Low alarms (TT PIT-PRES STAT LOW LOW). Pressure has increased from ~600# to orver 1100#, but alarms are still being recieved. <I> **** Actions Taken **** Informed CRS and wrote CR. <N> **** Equipment Description **** 487' RW Chem Lab | 02-00-HSSF-CAB-CHEM/LAB
400701 | CR | 20191029 | CAQ | D | CMS-F-SR21/2 Iodine charcoal filter holder assembly | Y | N |  | N | YES | <D> **** Detailed Description **** The Iodine charcoal filter holder assembly is not between the two indents pushing the assembly approximately 5/16â€ further in. Could be a potential leak path into the drywell. <I> **** Actions Taken **** Notified CRS Notified Supervisor | 02-00-CMS-F-SR21/2
400702 | CR | 20191029 |  | 4 | E-VM-DPS1/4 was found to have low voltage | N | N |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was observed that bus voltage at E-VM-DPS1/4 was reading 118V. The minimum voltage that logs require is 126V and the maximum voltage is 140V. It is suspected that the battery charger output breaker, E-CB-C1/4/CB2, is tripped, but would have to make another trip to the river to confirm breaker position. See also, AR 394633 WR 29149186 and AR 394845 and WR 29149279 <I> **** Actions Taken **** Informed CRS and wrote AR. | 02-00-E-CB-C1/4/CB2,02-00-E-VM-DPS1/4
400703 | CR | 20191029 | CAQ | D | DSA-C-1C leaking at unloader diaphram and fittings | Y | N |  | N | YES | <D> **** Detailed Description **** While conducting PMT on DSA-C-1C, 02131989-05, air leakage was detected at the unloader diaphram and 90 degree fitting on top of the diaphram. Leakage is minor and does not affect the operation of the compressor. Maintenance was not conducted on the unloader. <I> **** Actions Taken **** informed WWM, Maintenance management, and ops and wrote cr to generate WR <N> **** Equipment Description **** DG3 dsa compressor room | 02-00-DSA-C-1C
400704 | CR | 20191030 |  | 3 | TMU-42-7R2B starter coil did not pick up as expected | N | N |  | N | YES | <D> **** Detailed Description **** During TMU-42-7R2B starter replacement, step 4.4.6, close test switch, a spark was seen on front right of bucket when test switch closed, and coil did not pick up. Put bucket in a safe condition (on stabs) until engineering evaluation. Control power fuse removed and taped to front of bucket. <I> **** Actions Taken **** informed maintenance management and ops and wrote CR <N> **** Equipment Description **** TMU pump house . WO 02082367 was performed with the bucket still in the MCC compartment with secondary wiring connected. The power supply that was used to perform the pickup/dropout steps had a GFCI. The purpose of the GFCI trip interrupt device is to monitor current between the hot and neutral so it trips if there is a current imbalance. So when the spark was observed, I believe there might have been either a loose connection of the test leads from the test equipment to the bucket or a mismatch of the current because the secondary connection of the bucket was still connected to the supervisory component. When a different power supply with no GFCI was used, the test was satisfactory. There was a problem with test setup configuration that if the testing had been performed with the bucket fully racked out of the MCC cubicle and tested on a bench this sparking would not have seen and the test would have passed. Therefore there was/is no engineering evaluation required. | 02-00-TMU-42-7R2B
400705 | CR | 20191030 |  | 3 | Plant Main Corridor Dose Rates Elevated During Past 3 Weeks | N | N |  | N | NO | <D> **** Detailed Description **** The 441' Plant Main Corridor general area dose rates have been elevated over the past 3 weeks from a maximum of 1 mrem/hr @ head level at the "T" in the hallway, to 2 mrem/hr at the same location. Additionally, all along the overhead condensate line in the corridor (hallway), at head level (6'), the dose rate has increased from <1 mrem/hr to 1.4 - 1.5 mrem/hr. The dose rate at head level as you enter the Turbine 441' from the hallway, is 1 - 1.5 mrem/hr @ head level for ~40' distance north. This are was previously <1 mrem/hr. The shine from the overhead condensate line is the source of the increased dose rates in the turbine building. <I> **** Actions Taken **** Documented the new weekly main plant corridor survey (20191030-2) and initiated this AR/CR.
400706 | CR | 20191030 |  | 4 | 4.DG3 drop 6-1 Low Air Pressure alarm in during DG3 bar-over | Y | Y |  | N | YES | <D> **** Detailed Description **** 4.DG3 drop 6-1 Low Air Pressure alarm came in during DG3 bar-over. This occurred while DSA air start motors were isolated via DSA-V-2C1/1 and DSA-V-2C1/2. DSA-PI-11 indicated 175 psig. DSA-PI-12 indicated 182 psig. DSA-PI-7 and DSA-PI-8 both indicated 257 psig. The ARP says this is an anticipated alarm when one or both air headers are isolated, but none of the pressures described were below the expected alarm setpoint. <I> **** Actions Taken **** Informed MCR. Wrote CR. . See M512-1. Per the ARP, the low air pressure alarm for the headers comes from DSA-PS-11 and DSA-PS-12. When DG3 is barred over, we isolate the air headers by CLOSING DSA-V -2C1/1 and DSA-V-2C1/2. DSA-V-2C1/1 isolates DSA-PS-11 and DSA-V-2C1/2 isolates DSA-PS-12. DSA-PI-11 and DSA-PI-12 are both UPSTREAM of these isolation valves. <N> **** Equipment Description **** DG3 Low Air Pressure alarm
400707 | CR | 20191030 |  | 3 | SD000166, Rod Block Monitor, System Description |  |  |  | N | NO | <D> **** Detailed Description **** SD000166, RBM system description, no longer is relevant as it describes the RBM system as it existed prior to PRNM but the system description is being maintained as evidenced by a minor revision in Aug 2019 . RBM system is now a part of PRNM and is described in SD001819. Recommend archiving SD000166.
400708 | CR | 20191030 |  | 3 | Evaluate adding sections to SOP-DG-DSA for compressor start. |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of PMT for DSA-C-1C, WO 02131989-05 requires OPS to start the compressor using SOP-DG-DSA. There are no applicable sections for starting any of the DSA compressors and in order to accomplish the task, non -conditional steps were required to be N/A'd with SM concurrence. SOP-DG-DSA needs to be evaluated for adding a section in the event of post maintenance testing or other reasons.
400713 | CR | 20191030 |  | 3 | OSP-TIP-B301 not performed as scheduled |  |  |  | N | NO | <D> **** Detailed Description **** Operations chose not to perform OSP-TIP-B301 as scheduled. This surveillance should have been scheduled with in conjunction with TIP runs as this evolution takes credit for the surveillance. TIP runs are scheduled for next week and Operations does not want to take on additional risk by performing this surveillance/evolution twice. This is a Safety over Production decision. <I> **** Actions Taken **** Contacted the Unit Coordinator to ensure that these evolutions are scheduled together in the future. Informed that a P-6 scheudule tie was made. . Per UC, the rescheduling alignment for these WO's are complete. No additional PSO action required. <N> Had Unit Coordinator create a LPRM FEG and bundled the work together for future occurances to prevent issue in future. No other action is necessary.
400714 | CR | 20191030 |  | 4 | Steam Leaks Found on â€˜Aâ€™ TOA system | N | N |  | N | YES | <D> **** Detailed Description **** While performing SOP-COLDWEATHER-OPS, leaks were found near â€˜Aâ€™ TOA steam traps. The inlet and outlet valves for the traps were closed and their drain valves opened per CRS direction. Per SOP-COLDWEATHER-OPS, it states if steam leaks are found, submit a Work Request to repair the leaks, and hand a Clearance Order to isolate and drain the heating coil. The valves repositioned were HCO-V-T1AA â€“ CLOSED, HCO-V-T1AD-OPEN, HCO-V-T1AB-CLOSED; HCO-V-T1CA -CLOSED, HCO-V-T1CD-OPEN, HCO-V-T1CB-CLOSED. <I> **** Actions Taken **** Notified CRS | 02-00-TOA-HC-1A
400719 | CR | 20191030 |  | 3 | LACK OF MAINTENANCE VEHICLES |  |  |  | N | NO | <D> **** Detailed Description **** ELECTRICIANS RESERVED VEHICLE THE DAY BEFORE SCHEDULED WORK. UPON ARRIVAL TO THE KIOSK IT WAS DISCOVERED THAT THE RESERVATION HAD BEEN CANCELED. THIS LEAD TO A HUGE DELAY. NO VEHICLES WERE AVALIBLE. MAINTENANCE NEEDS MORE VEHICLES. WHEN MAINTENANCE IS NEEDED TRANSPORTATION MUST BE IMMEDIATLELY AVALIBLE ANYTHING SHORT OF THIS IS UNACCEPTABLE. <I> **** Actions Taken **** SUPERVISOR INFORMED <N> **** Equipment Description **** LACK OF VEHICLES
400724 | CR | 20191030 |  | 3 | Operations department exceeded September dose goal. |  |  |  | N | NO | <D> **** Detailed Description **** In September, the Operations department received 650 mrem against a dose goal of 329 mrem. Baseline dose was 176 mrem. Scheduled dose was 166 mrem. Dose received due to emergent issues was 169 mrem (per reported dose to SSS). Dose received for activities that do not have a WOT (EDR, FDR, FPC bw/pc) was 13 mrem (per reported dose to SSS). Dose received by FIN was 155 mrem. FIN was budgeted 60 mrem for Heater Bay inspection on 9/17/19 which did not occur due to Plant conditions. FIN entered the Heater Bay on 9/21/19 and received 145 mrem. When the emergent dose and FIN dose (over budgeted) is deducted from the total received dose, Operations received 373 mrem for scheduled activities, 44 mrem over the month goal. This CR is for trending purposes only. <I> **** Actions Taken **** The Operations Dose Champion will work with ALARA planning and Chemistry to ensure that FDR and RWCU demineralizer bw/pc activities are budgeted. Based on current trend, will work to get EDR and FDR demineralizer bw/pc budgeted into the baseline dose. <N> Determining what the expected dose for backwash/precoat activities will take some time to finalize. Ensuring proper dose budgeting for the department is an ongoing and continuous aspect of the Dose Champion's duties.
400725 | CR | 20191030 |  | 4 | No lighting RW 467' Pipe or Duct space room. W-DOOR-C230. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Outside of the room lighting is also out. <I> **** Actions Taken **** Wrote this CR. and informed supervision. <N> **** Equipment Description **** RW 467' PIPE OF DUCT SPACE W-DOOR-C230 INSIDE OF THE ROOM A ND OUTSIDE OF ROOM C230 is the room number. The door accessing this area is W-DOOR-C228. Confirmed that all lighting is out in area C230 and that a flashlight is staged at the door just inside the room.
400726 | CR | 20191030 |  | 4 | CT-1B cable chase lid blown off. | N | N |  | N | YES | <D> **** Detailed Description **** The lid of part of the cable chase on top of CT-1B blew off and is laying nearby. See picture. <I> **** Actions Taken **** Wrote CR, Informed CRS. <N> **** Equipment Description **** On top of CT-1B
400727 | CR | 20191030 | CAQ | D | Siren C21 partial alarm | N | Y |  | N | YES | <D> **** Detailed Description **** While doing the weekly siren poll test C21 reported a partial failure. This alarm indicates a problem with one of the 10 amplifiers/drivers. The siren will operate in an event but will be slightly degraded. <I> **** Actions Taken **** Notified EP and dispatched a tech to repair. Recommend closing to WR. CAQ-4 <N> **** Equipment Description **** Franklin County C21
400729 | CR | 20191030 |  | 4 | WOA-HC-1 has a steam leak | N | N |  | N | YES | <D> **** Detailed Description **** During WOA-HC-1 startup numerous leaks were observed. All All six of the coils have varying degrees of leakage and three of the coils were isolated to stop the worst leaks. Closed valves HS-V-W9N, HCO-V-W9AB, and opened HCO-V-W9AD on WOA-HC-1 to isolate the worst leak. Closed HS-V-W9M and HCO-V-W9FB and opened HCO-V-W9FD to isolate WOA-HC-1M. Reference 0291435534. <I> **** Actions Taken **** Initiated CR. Notified supervisor. | 02-00-WOA-HC-1
400730 | CR | 20191030 |  | 4 | WRA-SUH-3 fan was not turning in "auto" or "on". | N | N |  | N | YES | <D> **** Detailed Description **** WRA-SUH-3 fan was not turning in "auto" or "on". Breaker was verified to be closed (PP-7FAB-ckt 5) per EWD. fan is required for sop-coldweather-ops <I> **** Actions Taken **** wr/cr | 02-00-WRA-SUH-3
400731 | CR | 20191030 |  | 3 | PM program gaps | N | N |  | N | NO | <D> **** Detailed Description **** This condition report identifies a process issue, not an equipment issue, and was requested by PHC with the recommendation that it be assigned to the Maintenance Manager. E-CB-5/54 was put into service in 2005 as part of the EC that installed the HWC system. This EC did not create PMâ€™s for the circuit breaker but they were initiated in 2011 when the lapse was recognized by the breaker program owner. PM 22860-01, detailed inspection of the breaker, was originally created as on-line with a frequency of A04 and a due date of 6/1/12. On 6/28/12, SMS 263986 changed the PM from on-line to outage, the existing work order was cancelled, and the due date was changed to 5/15/13 to align it with outage R21. This work order was subsequently cancelled on 12/16/15 with the comment â€œwork not performedâ€ yet it appears that the PM was credited and the due date advanced. On 4/27/16, the PM frequency was changed from A04 to A06 by SMS 344445 (Rolls Royce). On 1/24/17, SMS 360477 changed the frequency from A06 to A08 (VBM). During the circuit breaker hardened grease investigation (CR 358027), the E-CB-5/54 length of service since its last overhaul and plant impact if it were to fail placed it on a list of forty-one breakers judged to be most likely to fail due to hardened grease, which is now being tracked as #8 of the stationâ€™s top 10 equipment reliability issues. On 2/7/18, SMS 355802 reset the PM frequency to A04 with a due date of 5/15/21. In summary, no preventive maintenance has been performed on this breaker since being put into service in 2005. Although the gap between 2005 and 2011 is due to not initiating a PM when the equipment was installed, the PM has gone eight more years without having been performed. While some of the date changes were necessary and are well documented, such as when the PM was changed from on-line to outage, other changes are not. This appears to be the case with WO 02027748 which seems to have been cancelled without a SMS or other justification.
400732 | CR | 20191030 |  | 3 | Not demonstrating Safety First and Risk Management |  |  |  |  | NO | <D> **** ANONYMOUS CR - Detailed Description **** A majority of my coworkers and I were in the Willamette building when the Willamette and Deschutes building evacuation drill commenced on 10/30/19. I chose not to return to my office to retrieve my coat when the alarm sounded and went to the assembly area without a coat. It was 22 degrees outside. . Many employees entered the â€œburningâ€ building to retrieve their coats. Not the safe choice. . Several people decided to enter a separate building that was not subject to the evacuation. Were they accounted for? Knowingly sending people into 22 degree weather without their coat for a drill, as opposed to a real fire event, is a questionable decision for minimizing risk. The individuals conducting the evacuation drill were wearing their winter coats. At least their risk was minimized. . Consider conducting building evacuation drills in the warmer months. <N> This ANON CR was reviewed and approved. Request to assign to TEFP from Facilities.
400734 | CR | 20191030 |  | 4 | TSW Through Wall Leak NICM Temp Fix Missing | N | N |  | N | YES | <D> **** Detailed Description **** There is a through wall leak on a 6â€ TSW pipe near TSW-V -649 above the coupon station in the Aux Boiler room (T453 E3/4.2). This was previously identified on 5/24/2019 (AR# 394123, WR# 29149149). NICM was installed on the piping per the work request on 5/30/2019 and generated WR# 29149149 to permanently fix the leak. On operator rounds 10/30/2019, it was noted that the NICM was no longer installed and the pipe is leaking one drop per second. A bucket was installed underneath the leak to prevent it from leaking into plant drains. Please reinstall NICM to stop leak or install temporary catch to direct TSW leakage away from plant drain systems due to high TOCs in TSW until permanent fix can be performed. <I> **** Actions Taken **** Installed bucket, wrote CR, informed supervision <N> **** Equipment Description **** 6" TSW piping in Aux Boiler room, T453 E3/4.2
400735 | CR | 20191030 |  | 3 | 4.601.A4 drop 1-5 RCIC Turbine Trip not updated for EC 16687 |  |  |  | N | NO | <D> **** Detailed Description **** The RCIC Trubine Trip ARP still lists RCIC Disch Press Low as a potential trip. With EC 16687 implemented the Low Disch Pressure Trip is bypassed. RCIC-RMS-PIS1 is in Override. <I> **** Actions Taken **** Recommend update the ARP.
400737 | CR | 20191030 |  | 4 | TDAS remote +5 vdc power supplies failing | N | N |  | N | YES | <D> **** Detailed Description **** During TDAS remote power supply checks PM several of the +5 VDC power supplies exhibited low voltage and high ac ripple. These need to be replaced. TDAS remote #4 (4.55 vdc 496.5 mvac ripple) TDAS remote #10 (4.56 vdc 512.48 mvac ripple) TDAS remote #11 (4.67 vdc 381.08 mvac ripple) TDAS remote #12 (4.51 vdc 586.4 mvac ripple) <I> **** Actions Taken **** Notified supervision, computer engineer and wrote CR/WR. | 02-00-TDAS-MUX-10,02-00-TDAS-MUX-11,02-00-TDAS-MUX-12,02-00-TDAS-MUX-4
400739 | CR | 20191030 |  | 4 | CO-V-2B Packing Leak | N | N |  | N | YES | <D> **** Detailed Description **** CO-V-2B, located in the Aux Boiler room, was found to have a packing leak, creating a puddle on the ground beneath it. Plant laborers were contacted about installing a drip catch beneath the valve to direct the leak into a nearby scupper rather than puddling on the floor. Please make packing adjustment to stop leak. <I> **** Actions Taken **** Contacted plant laborers about installing catch, wrote CR, informed supervision | 02-00-CO-V-2B
400742 | CR | 20191030 |  | 4 | Poor lighting Alpha RHR Pump Room Mezzanine. |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Numerous florescent light lamps are flickering or burned out. <I> **** Actions Taken **** Wrote this CR; informed supervision <N> **** Equipment Description **** Mezzanine RHR Alpha Pump Room
400743 | CR | 20191030 | CAQ | D | CRA-FN-1C1 failed to start | Y | Y |  | N | YES | <D> **** Detailed Description **** While attempting to restart CRA-FN-1C1 for PMT on WO 02079198. When the control switch was placed in AUTO-AFTER- ON, the green light for CRA-FN-1C1 went out briefly and came back on. The EO in the field noted the green light went out briefly, the red lilght came on briefly and the green light came back on. Replaced the red indicating light in the MCR that appeared to be failed. CRA-FN-1C2 started as expected, RCC-V-71C opened as expected and containment temperatures remain unchanged. <I> **** Actions Taken **** Notified CRS | 02-00-CRA-FN-1C1
400744 | CR | 20191030 |  | 3 | Procedure enhancement: SOP-COLDWEATHER-OPS |  |  |  | N | NO | <D> **** Detailed Description **** While performing SOP-COLDWEATHER-OPS an astute operator noticed a discrepancy and inquired of me the following points which were reserched, the actual EPN in portal J is HT-HTP-FP/23 for step 6.1.3.e. The breakers in the panel are labeled 1,2 and A with a fourth breaker found off unlabeled . Print E-937 and CVI DWG 322-00,34,7 were used to verify only the breakers labeled 1,2 and A are required to be closed. Please change the procedure to reflect the additional information. <I> **** Actions Taken **** see above as well as contacting the in field supervisor.
400745 | CR | 20191030 |  | 4 | TDAS Terminal Server administrative password not working |  |  |  | N | YES | <D> **** Detailed Description **** This unit is working correctly to fulfill it's function. But we are no longer able to change the administrative password. The Cyber PM will need to be adjusted. Suggest this be sent to Cyber Security as a Trend Only. <I> **** Actions Taken **** Notified Cyber Security | 02-00-TDAS-COMP-TSRVR
400746 | CR | 20191030 |  | 4 | Configuration management issue identified in WO 02118127-26 |  |  |  | N | YES | <D> **** Detailed Description **** During the walkdown of WO 02118127-26 a configuration management issue was identified that the flange on FP-ENG-1 exhaust, at field weld #1 on drawing 215-00,14215 is a slip on fitting and not a weld neck as the drawing states for item 5 in the list of materials. Current work order instructions do not allow for this work to be performed as written. Package will be returned for revision; recommend assignment to engineering for further direction. <I> **** Actions Taken **** Notified my supervision, initiated this condition report and notified the main control room . CVI ISO 215-00,14215 is the DE piping from FP-ENG-110, not FP-ENG-1. Please see CVI ISO 215-00,6638 for the DE piping from FP-ENG-1. | 02-00-FP-ENG-1
400747 | CR | 20191030 |  | 3 | (ERO Drill) Objective E.4 Demonstrated with Issue |  |  |  | N | NO | <D> **** Detailed Description **** During the Oct 29 Team D ERO Training Drill, Drill Objective E.4, Demonstrate the ability to provide the required content for the follow-up information messages timely and accurately was demonstrated with issue. There was a gap of one hour and thirty five minutes between CNF #3 and CNF #4. PPM 13.4.1 Section 4.4.1 states that about once per hour or when radiological or plant conditions change, initiate a follow-up message by Crash phone and fax to offsite agencies. This objective was not completed in a timely manner given the one hour and thirty five minutes between notifications. All other Initial and follow-up notifications were completed accurately and timely. This issue was critiqued following the drill. This did not impact Drill and Exercise Performance. <I> **** Actions Taken **** Critiqued at the Team D Critique, Notified the Team D EOF Manager and EP Manager.
400748 | CR | 20191030 | CAQ | C | AED PRC 12177 contains an error for design pressure | N | N |  | N | YES | <D> **** Detailed Description **** During reviews for an upcoming design change for RCC-RV-34A an error was discovered in a Procurement Specification (AED PRC 12177) regarding design pressure. The design pressure listed in AED PRC 12177 is 300 psig. The associated relief valve data sheet (AED RVDS RCC-RV-34A) lists the basis documents as DCP 84-1214-0A and AED CAL NE-02-84-29. These documents specify a design pressure of 270 psig (not 300 psig). AED SPC 1 page 44 contains a note that states â€œRCC-RV-34A & RCC-RV-34B and associated valve flanges design pressure 270 psigâ€¦â€. The currently installed relief valve contains carbon steel SA105 class 150 flanges that meet the 270 psig design pressure so therefore there should not be any issues with currently installed plant equipment. The resolution of this CR should be to update AED SPC 12177 with the correct design pressure of 270 psig (not 300 psig). <I> **** Actions Taken **** Discussed with Minor Mods Supervisor and Relief Valve Component Engineer | 02-00-RCC-RV-34A,02-00-RCC-RV-34B
400749 | CR | 20191030 |  | 3 | Student Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** HP technician failed HP continuing training exam. Remediation is scheduled and will consist of objective review followed by retaking exam <I> **** Actions Taken **** Training Supervisor and RP Supervision notified. Failure documented in eTAR. This is for trending only. eTAR Class ID #856799
400750 | CR | 20191030 | CAQ | D | SW-RIS-605 VR29 Out of Tolerance. | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02117306-01, Step 7.2.59, the As-Found data for the VR29 regulator Board was out of tolerance low at 14.87 VDC (14.90-15.10). <I> **** Actions Taken **** Informed Operations and Supervision. Continued with surveillance. Regulator will be adjusted later in surveillance per section 7.5 <N> Reference ODCM tracking sheet O19-PPM 16.8.4-001.
400752 | CR | 20191030 |  |  | Failed cooling tower temperature elements |  |  |  | N | YES | <D> Various cooling tower temperature elements and their associated conduits and supports have failed and are in need of replacement. Failure is due to corrosion of carbon steel components, which are at or near the waterline of the upper distribution deck. These temperature elements are run-to-failure components and are used to monitor system health and thermal performance. | 02-00-CW-TE-1A1,02-00-CW-TE-1A2,02-00-CW-TE-1C1,02-00-CW-TE-2A1,02-00-CW-TE-2A2,02-00-CW-TE-2A4,02-00-CW-TE-2B2,02-00-CW-TE-2C2,02-00-CW-TE-2C3
400753 | CR | 20191030 |  | 3 | EGM-1-13 minor corrections needed |  |  |  | N | NO | <D> **** Detailed Description **** During cursory review of PPI ENG EGM-1-13 (QUALITY REVIEW BOARD), the need for a few relatively minor corrections was identified: 1) To align with Form 27060 (QUALITY REVIEW GRADING SHEET (EGM-1-13)), PPI ENG EGM-1-13 Attachment 6.1 GRADING CRITERA page 9 "5 - Meets Expectations" should be corrected to "5 - Exceeds Expectations". 2) The phrase "Attention to detail -" is repeated (back-to-back) in PPI ENG EGM-1-13 Attachment 6.2 (QRB Product Review Attributes) page 12 Attribute 17. The second "Attention to detail -" should be eliminated. 3) Minor editorials thoroughout. See the PPI ENG EGM-1-13 R1 MnrR3 mark-up attached to the EDMS of this AR CR 400753. This is an administrative issue only.
400754 | CR | 20191030 |  | 4 | CPR-TK-92B high level alarm did not come in on setpoint. | N | N |  | N | YES | <D> **** Detailed Description **** CPR-TK-92B high level alarm did not actuate on the red needle setting. Alarm check showed that the alarm module stiff functioned. <I> **** Actions Taken **** Wiped red needle back and forth, going below and above current level. This had no effect. | 02-00-CPR-LIS-97B
400755 | CR | 20191031 |  | 4 | OG-RF-20B Main Seal Leak | N | N |  | N | YES | <D> **** Detailed Description **** Main seal on OG-RF-20B is leaking, also have leaks at the unloader valves, mounting plate gaskets on both cylinder heads <I> **** Actions Taken **** Initiated this CR, notified Supervisor, advised Control Room to leave OG-RF-20C in lead position. <N> **** Equipment Description **** RW 452 | 02-00-OG-RF-20C
400756 | CR | 20191031 |  | 4 | Y axis on EDNA Met temp data off by factor of 100 |  |  |  | N | YES | <D> The Y axis for Met Tower temperature data EDNA points is off by a factor of 100. Data appears to be tracking such that indicated temperature on the trace of 2870F corresponds to actual local temperature of 28.7 degrees. Please update the data field to the correct number of units. <I> Discussed with SM. <N> MET-TEMP-11A, 11B 10A, 10B CR at INPROG. Approved CR, moved to SRO for OPS Review. WR 29152510 written and cross referenced. | 02-00-MET-TE-10A,02-00-MET-TE-10B,02-00-MET-TE-11A,02-00-MET-TE-11B
400770 | CR | 20191031 | CAQ | C | DSA-PI-11 indicates LOOS during DG3 run | Y | N |  | N | NO | <D> **** Detailed Description **** DSA-PI-11 indicates Low out of spec in the DG3 run logs. indicated pressure was 178 psig. Minimum pressure in the DG3 run logs is 180 psig. Shiftly Diesel logs indicate a minimum pressure of 170 psig for the same pressure indicator. The low air pressure alarm comes in at 160 psig on either starting air header. The normal starting air header pressure reading is approximately 180 psig. Recommend evaluating and determining what the actual minimum log pressure should be and adjusting the logs accordingly. <I> **** Actions Taken **** Informed MCR. Wrote CR.
400771 | CR | 20191031 |  | 3 | Funding request for TSW-P-1A in incorrect year caused rework |  |  |  | N | NO | <D> **** Detailed Description **** Low dollar funding request to complete EC for TSW-P-1A was placed on R&O log by PM in incorrect fiscal year (FY20 rather than FY21 ). The request was processed by Asset Management then had to be subsequently reversed causing rework. <I> **** Actions Taken **** Decision and updates reversed. PM notified. CR written. Implementing process improvment to log to minimize future potential errors. <N> Proper coaching was communicated to the individual who made the error, the supervisor was informed of this issue, and changes have been made to the functionality of the Risks & Opportunities log to prevent this from happening in the future.
400772 | CR | 20191031 |  | 3 | R25 procedure change to SOP-ELEC-DIV1-TEMPPOWER Section 5.33 |  |  |  | N | NO | <D> **** Detailed Description **** R25 procedure change to SOP-ELEC-DIV1-TEMPPOWER Section 5.33 RW 507 Welding Receptacles Temporary Power Installation, update procedure to perform in any mode. <I> **** Actions Taken **** wrote cr
400773 | CR | 20191031 |  | 3 | R25 procedure change to support temp power to RFW-LR-608 |  |  |  | N | NO | <D> **** Detailed Description **** R25 procedure change to support temp power to RFW-LR-608 RFW-LR-608 recorder use to be fed from E-PP-7AA/4 and is now fed from E-PP-US/D ckt 4. SOP-ELEC-DIV1-TEMPPOWER section 5.39/5.40 for RFW-LR-608 temp power needs to be removed. These two sections needs to be added and updated to SOP-ELEC-PP/US-TEMPPOWER. SOP-ELEC-USPPMAINT attachment 6.2 for circuit 4 needs RFW-LR-608 added. <I> **** Actions Taken **** wrote CR
400776 | CR | 20191031 | CAQ | C | Standard found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode # 0063402 Heise Model HQS-2 Pressure gauge was found out of tolerance and adjusted. Please assign to CALSERV <N> Investigation completed. Investigation summary loaded into EDMS panel. No impact to CGS for the out of tolerance standard. No further actions required.
400782 | CR | 20191031 |  | 4 | Failed cooling tower temperature elements | N | N |  | N | YES | <D> **** Detailed Description **** Various cooling tower temperature elements and their associated conduits and supports have failed and are in need of replacement. Failure is due to corrosion of carbon steel components, which are at or near the waterline of the upper distribution deck. These temperature elements are run-to-failure components and are used to monitor system health and thermal performance. | 02-00-CW-TE-1A1,02-00-CW-TE-1A2,02-00-CW-TE-1C1,02-00-CW-TE-2A1,02-00-CW-TE-2A2,02-00-CW-TE-2A4,02-00-CW-TE-2B2,02-00-CW-TE-2C2,02-00-CW-TE-2C3
400783 | CR | 20191031 |  | 3 | LEFM Firewall administrative password not working |  |  |  | N | YES | <D> This unit is working correctly to fulfill it's function. But we are no longer able to change the administrative password. The unit will need to be booted to recover the password . Suggest this be sent to Computer Engineering. The unit is still password protected. <I> **** Actions Taken **** Notified Cyber Security | 02-00-TDAS-COMP-TSRVR
400784 | CR | 20191031 |  | 4 | Corroded FP pipe on top of Cooling Towers | N | N |  | N | YES | <D> **** Detailed Description **** The 3â€ FP pipe at the top of various cooling towers is severely corroded, with through-wall holes at multiple locations. This pipe is normally drained and capped on both ends, and is used to supply water for cleaning the tops of the cooling towers during refueling outages. The condition of this pipe caused some delays in tower cleaning in R24 and, if not replaced before R25, the pipe may be unusable on multiple cooling towers. The FP lines in need of replacement can be found at the top of CW-CT-1A, CW-CT -1C, CW-CT-2A, and CW-CT-2C. Reference CVI DWG 223-00,118 for pipe details. <N> **** Equipment Description **** 3" FP pipe by stairwell, top of CW-CT-1A, -1C, -2A, and -2C
400785 | CR | 20191031 | CAQ | D | MW01 | N | N |  | N | YES | <D> **** Detailed Description **** Alpha head on the south end is loose. <I> Compensatory measures were put into place unpon receiving alarms. | 02-00-SEC-MW-1RA
400787 | CR | 20191031 |  | 3 | Standard found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode 0067862 Interface Model 1110ACK-3K LOAD CELL 3K was found out of tolerance. Although this was out of tolerance for our â€œdrift toleranceâ€, it was not out of tolerance per the vendor certificate. Please assign to CALSERV <N> Investigation summary uploaded inot the EDMS panel. The out of tolerance standard did not have any impact to CGS assets. All six CGS assets when cyelce back through the calibration lab were all found to be in tolerance.
400788 | CR | 20191031 |  | 4 | WHCO-P-1B run light is broken off in socket. | N | N |  | N | YES | <D> **** Detailed Description **** WHCO-P-1B run indicating light broke while being extracted. Please remove bulb base from socket and replace bulb. ( 120 PSB ). <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** RW 437 | 02-00-WHCO-P-1B
400790 | CR | 20191031 |  | 4 | HD-LIC-12B will not control in AUTO | N | N |  | N | YES | <D> **** Detailed Description **** HD-LIC-12B (SS-EV-1B Drain Tank LCV) will not control in AUTO. The controller responds properly to Manual adjustments. No change of state occurs to the ing zone indicator (the little metal ball), when moving the Auto or Manual adjustments. An attempt to place the controller in AUTO, after matching the actual Indicated level with the AUTO setpoint, did not work. Once in AUTO, the output pressure would go downscale regardless of AUTO setpoint position. Priority should be placed on repairing this controller. P&L 4.6, of SOP-SS-START, warns against extended operation with a high-level dump valve OPEN. The SS-EV-1B Drain tank inputs are not consistent enough to maintain level with Manual control. HD-LIC-12B is currently in Manual with an Output signal of 0 PSIG, maintaining the Drain tank empty. CR generated to prompt repair and evaluate OPEN Dump valve condition, per SOP. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** TG 471E | 02-00-HD-LIC-12B
400791 | CR | 20191031 |  | 3 | ICP-MS/PRM-X301/302/303/304 schedule duration Impacts |  |  |  | N | NO | <D> **** Detailed Description **** ICP-MS/PRM-X301/302/303/304 schedule duration Impacts were not fully recognized. MS-RIS-610A thru D rad channels Cals are scheduled for 15 hours each typically scheduled over 2 days. LCS 1.3.6.3 allows 6 hours out of service time or require the channel be declared inop and placed in trip in 24 hours. Placing the channel in trip would prevent completion of the surveillance. These rad monitors were added by LCS 1.3.6.3 since the last performance of these surveillances. Previous performances were typically schedule over several days to align with I&C resources and specialty quals as there was no requirement to place the channel in trip. I&C will need to address how the surveillances can beworked to completion accomplished without undue delay by scheduling resources or changing the surveillance sequencing to reduce the out of service time. Daily schedules need to be adjusted to work to completion. <I> **** Actions Taken **** Associated work orders and models are now updated to reflect LCS requirement to place the channel in trip as required by LCS 1.3.6.3.
400792 | CR | 20191031 |  | 4 | Turbine Building Roof Hatch Found Open | N | N |  | N | YES | <D> **** Detailed Description **** The turbin building roof hatch (east side above the tubin building elevator) was found open. Informed CRS and SM. Verified with WWM and HP that there is no ongoing work. MCR verified that the TG building negative pressure is being maintained. <I> **** Actions Taken **** Informed CRS, SM, WWM. Initiated WR to close the hatch. <N> **** Equipment Description **** Turbine building roof hatch
400794 | CR | 20191031 |  | 3 | PPM 11.2.9.41 , AMS-4 Continous Air Monitor, needs revision. |  |  |  | N | NO | <D> **** Detailed Description **** PPM 11.2.9.41 needs revision. PPM 11.2.9.41, section 5.4.3 states two down arrow presses are needed to arrive at the correct menu section. The procedure should require three down arrow presses. The second change needed is in section 5.7.5. section h. This section needs to be removed. This section is about filter media change out, not AMS-4 operation. This step conflicts with 5.2 section 2.6 and the NOTE above this section. The third change involves 5.2.5. This section should direct user to section 5.7, Filter media replacement. To facilitate this, 5.2.5, should state: Change filter media in accordance with 5.7, and the present steps (a, 1) moved to section 5.7 Fourth change: Please consider appropriate prerequisites This procedure does not include prerequisites. <I> **** Actions Taken **** Stopped training, talked to Supervision, wrote CR with procedure issues and suggestions for remedy.
400795 | CR | 20191031 |  | 4 | AMS-4 42796 taken out of service. Please repair. | N | N |  | N | NO | <D> **** Detailed Description **** AMS-4 42796 taken out of service. This AMS-4 will not complete a background count. <I> **** Actions Taken **** Followed procedure and noticed the AMS-4 was not functioning correctly. This CR was written, and the AMS-4 was tagged out of service and moved to the appropriate location. WR needed?
400799 | CR | 20191031 |  | 4 | REA-DPS-1B leaks internally. | N | N |  | N | YES | <D> **** Detailed Description **** REA-DPS-1B was found to be leaking internally and could not be tested satisfactorily per WO# 02095357-01. <I> **** Actions Taken **** Contacted Supervisor and Shift Manager. | 02-00-REA-DPS-1B
400801 | CR | 20191031 |  | 3 | (QA) WR Not Closed Out Per PPM 1.3.68 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Work Request (WR) 29148601 was not closed out, but had been completed on 5/14/19 when Tamper Seal # 112124 was installed on E-CP-LSP/PWA. Review of this WR revealed it was still in H/APPR status in October 2019, contrary to PPM 1.3.68 "Work Management Process". When a WR is properly closed out per PPM 1.3.68, it ends up in plant Records. This is a procedure use and adherence issue with no known consequences. Requirements: (see EDMS for Details) Factual Basis: (see EDMS for Details) Insights: â€¢ Interviews revealed the standard practices used by other workers is to ask the Fix-It-Now (FIN) Senior Reactor Operator (SRO), a FIN Supervisor, or a Production SRO to close out a WR when the work has been completed. â€¢ Interview revealed that each group is responsible for getting their own completed WR to Records. â€¢ As of 10/23/19, the Route List for WR 29148601 was awaiting approval from Alert Group â€œOPSSSSâ€ Operations Crew Supervisors. (OPSSSS is no longer used and was replaced by OPSSRO). â€¢ After notification by Quality, the FIN SRO completed and closed out WR 29148601 on 10/26/19. <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Tamper Seals. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to ITMGMT. <N> Reccomend Cat 3 ITMGMT The cause is known as individuals do not need to create a WR for tamper replacement. The risk is low as the tamper was replaced in a timely fashion per procedure. Assignment 01 has been created to add a note to SWP-CSW-14. The WR has been closed out.
400802 | CR | 20191031 |  | 3 | (QA) 2 WRs Not in Records (Not Closed Out Per PPM 1.3.68) |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Work Requests (WRs) 29147665 and 29146206 are not in Records, but had been completed on 6/18/19 and 6/20/19, respectively. Review of these WRs revealed both were still in H/APPR status in October 2019, contrary to PPM 1.3.68 "Work Management Process". When a WR is properly closed out per PPM 1.3.68, it ends up in plant Records. This is a procedure use and adherence issue with no known consequences. Requirement: (see EDMS for Details) Factual Basis: (see EDMS for Details) Insights: â€¢ Interviews revealed the standard practices used by other workers is to ask the Fix-It-Now (FIN) Senior Reactor Operator (SRO), a FIN Supervisor, or a Production SRO to close out a WR when the work has been completed. â€¢ Interview revealed that each group is responsible for getting their own completed WR to Records. â€¢ After notification by Quality, the FIN SRO completed and closed out WR 29146206 on 10/17/19. â€¢ After notification by Quality, the FIN SRO completed and closed out WR 29147665 on 10/21/19. â€¢ After notification by Quality, the FIN SRO cancelled and closed out WR 29148009 on 10/21/19. <I> **** Actions Taken **** Contacted the Engineering Supervisor over Computer Engineering. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to Computer Engineering.
400803 | CR | 20191031 | CAQ | C | (QA) No Completed Cyber Security PMDD Forms in Records |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Completed Cyber Security Portable Media & Digital Device (PMDD) Evaluation Forms were not being maintained as Records, contrary to SWP-CSW-15 â€œPortable Media and Digital Device Useâ€. These records are required by NEI 08-09 â€œCyber Security Plan for Nuclear Power Reactorsâ€ Addendum 1. Requirements: (see EDMS for Details) Factual Basis: â€¢ Completed Form 27167 records generated from 2017 through 2019 cannot currently be found within Records under DIC 1837.6, contrary to the NEI requirement to keep the Records for at least 3 years. â€¢ Records and Information Management confirmed that there is no folder for Records with DIC 1837. Insights: â€¢ Currently, completed forms are uploaded to EDMS folder of the associated Action Requests. â€¢ Information Services indicated that the completed forms have not yet been sent to Records. <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Security. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to ITMGMT. <N> Reccomend Cat D to ITMGMT The cause is known as individuals did not submit the signature documents to Records. Consequence is low/medium as it could result in a regulatory finding. This issue was completed where all PMDD forms were submitted to Records. Individuals have been coached to follow the procedures.
400804 | CR | 20191031 |  | 3 | Passwords found in external share |  |  |  | N | NO | <D> **** Detailed Description **** Passwords to an individuals personal Microsoft One Drive account that contained large amounts of EN data were found during a clean up activity on Energy Northwest external share site. The passwords are avaialbe to a group of EN personnel but due to the properties of the external share they could be made available to any user that has access to external share site. This is not in alignment of GBP-IS-08 section 3.4 for passwords. <I> **** Actions Taken **** Discussed with individual, Ops Training Manager, CIO, and Legal services. Removed document from external share
400806 | CR | 20191031 |  | 3 | High Risk Challenge meeting standards |  |  |  | N | NO | <D> **** Detailed Description **** GAP: Performance of High Risk work challenge meetings has not consistently been performed in a manner that meets the Energy Northwest standards of Excellence. Although ultimately the purpose of these meetings (To challenge the organizations who have been involved in the critical or non-routine maintenance activity to ensure proper planning and preparation for work to be performed) is met, the station displays a predominant behavior of conducting these meetings more as a planning meeting than a challenge meeting. Planning and challenge team members are not adequately prepared in all cases to appropriately present and challenge High Risk Work plans to efficiently meet the expected outcomes. Required attendees based on type of risk identified (e.g. nuclear, industrial, radiological, corporate) are not always present due to improper classification of categories or late identification. Roles and responsibilities of the meeting challengers are not consistently implemented Additonal information (supporting examples and suggested actions) is attached in the EDMS. <I> **** Actions Taken **** Discussed with a cross-discipline team of meeting attendees to capture the issues identified.
400807 | CR | 20191031 | CAQ | C | (QA) SWP-CSW-26 & -27 do not Specify Records Requirements |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) SWP-CSW-26 â€œCyber Security Patch Managementâ€ and SWP -CSW-27 â€œCyber Security Vulnerability Management and Reportingâ€ do not contain instructions under the Documentation section to maintain records. Vulnerability assessments are not maintained as records as required by NRC-endorsed Addendums to NEI 08-09 or the CSP-01 â€œCyber Security Planâ€. Both procedures generate a completed Form 27032 â€œCyber Threat and Vulnerability Event Logâ€ to meet the above requirements when sent to plant Records. Requirements: (see EDMS for Details) Factual Basis: â€¢ Unsigned completed vulnerability assessment forms are maintained on the cyber team site. Insights: â€¢ Hard copy forms with signatures do not exist because none of the vulnerability assessments have been fully completed (reviewed for needed mitigating actions and signed). (see CR 381377) â€¢ After notification of this issue by Quality, the Cyber Security team created a new assignment 03 under AR-CR 399487 â€œAlternate vulnerability screening method not documentedâ€ to correct this issue within SWP-CSW-27. <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Security. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to ITMGMT. <N> Reccoment Cat C to ITMGMT The cause is known, this is an error in the procedure documentation as it does not contain guidance to ensure the Records process is completed. Consequence is low/medium as it could result in a regulatory finding. Assignment 01 will address SWP-CSW-26. SWP-CSW-27 will be addressed under CR 398487 assignment 03. (Note: Reference in this CR to AR 381377 should be 381337)
400808 | CR | 20191031 |  | 3 | Large amount of EN info found on personal cloud account |  |  |  | N | NO | <D> **** Detailed Description **** A large amount of Energy Northwest Initial License Class (ILC) Material found on a personal Microsoft One Drive account. This is not in alignment with GBP-IS-43 which requires all cloud storage locations to be evaluated prior to use for EN data <I> **** Actions Taken **** Notified Individual, Individuals SM, Operation Training Manager, CIO and Legal. This is not reportable for 10CFR 73.54
400811 | CR | 20191031 | CAQ | C | (QA) CR Not Initiated on 3CDAs Missing 4 Total Port Blockers |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) No condition report (CR) was initiated for four port blockers missing from a total of three Critical Digital Assets (CDAs), contrary to the requirements in PPM 10.1.28 â€œPort Blockersâ€ and SWP-CAP-01 â€œCorrective Action Programâ€. Initiation of a CR is entry point to Corrective Action process required by NEI 08-09 rev 6 â€œCyber Security Plan for Nuclear Power Reactorsâ€ Addendum 1. Requirements: (see EDMS for Details) Factual Basis: â€¢ For PMID 26577, Computer Engineering (CE) completed Quarterly PM WOT 02128768-01 on 5/4/19 with notes identifying two port blockers missing on the front of a NET4-FW-ASACENTER device and one port blocker missing from each front of devices: NET3-NETSW-2/A & NET3-NETSW-2/B. â€¢ Asset Suite shows no CR was initiated to date by CE for 4 missing port blockers on 3 devices noted above. â€¢ On 5/24/19, CE emailed Cyber Security (CS) about the missing port blockers, and CS directed CE to track the missing port blockers, but CS did not initiate a CR for the missing port blockers nor direct CE to initiate a CR. â€¢ PMID 26577 is to perform multiple Cyber Security tasks, including checking for evidence of tampering, but this PMID does not specify using PPM 10.1.28 to verify which unused ports require port blockers. â€¢ After notification by Quality, Supervisor over CE emailed stating that work has now been completed to install missing port blockers in NET4-FW-ASACENTER under WR 29152111 on 10/16/19. â€¢ NET3-NETSW-2/A & NET3-NETSW-2/B are in scope of PM WOT 02128770-01, which is currently at "Working" status. <I> **** Actions Taken **** Contacted Engineering Supervisor over Computer Engineering. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to Computer Engineering. <N> **** Equipment Description **** Missing port blockers installed by WR 29152111 on 10/16/19 for NET4-FW-ASACENTER. NET3-NETSW-2/A & NET3-NETSW-2/B are in scope of PM WOT 02128770-01, which checks for port blockers on unused ports, and is currently at "Working" status.
400812 | CR | 20191031 |  | 4 | Excessive packing leackage from CO-P-2B. | N | N |  | N | YES | <D> **** Detailed Description **** Excessive packing leakage was observed on Aux Boiler Feed Pump CO-P-2B. Per SOP-AS-OPS precatution and limitations 4.1, packing leakage should be about 40-60 drops per minute and approximately 2-3 gallons per minute was observed. <I> **** Actions Taken **** Initiated CR. | 02-00-CO-P-2B
400813 | CR | 20191031 |  | 3 | WO 02128770 Cyber PM - SEC Challenges |  |  |  | N | YES | <D> **** Detailed Description **** Work has completed on performing Cyber Security PMs for the Security Computer System, with some unresolved issues. 1. Unable to login to the ePO to perform password change. Coordinate with vendor for password recovery. 2. Unable to login to MOXA network switches. Coordinate with vendor for password recovery. 3. Unable to login to oseladm account on level 2 data diode. Coordinate with vendor for password recovery and possibkle replacement . <I> **** Actions Taken **** Attempted PM activities, documented challenges, wrote CR, notified vendor support, verified all devices remain operational. | 02-00-SEC-NETSW-10/A,02-00-SEC-NETSW-10/B,02-00-SEC-NETSW-11A/A,02-00-SEC-NETSW-11A/B,02-00-SEC-NETSW-12A/A,02-00-SEC-NETSW-12A/B,02-00-SEC-NETSW-14A/A,02-00-SEC-NETSW-14A/B,02-00-SEC-NETSW-15A/A,02-00-SEC-NETSW-15A/B,02-00-SEC-NETSW-16A/A,02-00-SEC-NETSW-16A/B,02-00-SEC-NETSW-20A/A,02-00-SEC-NETSW-20A/B,02-00-SEC-NETSW-21A/A,02-00-SEC-NETSW-21A/B
400814 | CR | 20191031 |  | 3 | Level 4 EPO not alerting upon test event |  |  |  | N | YES | <D> **** Detailed Description **** On 10/31/19, during scheduled testing under cyber monthly PM, it was discovered that the level 4 EPO server performed its basic detective and protective function but did not produce the expected alert of the function during the test. Recommend troubleshooting to include reboot of device by Computer Engineering. Recommend review of device twice a week to meet CSDG-01 guidance to review logs when components are not alerting. Not reportable under 10 CFR 73.54. <I> **** Actions Taken **** Advised CSPM. Confirmed that the detection and prevention function is still operational. Recommend troubleshooting to include reboot of device by Computer Engineering. Recommend review of device twice a week to meet CSDG-01 guidance to review logs when components are not alerting. | 02-00-NET4-COMP-EPO
400816 | CR | 20191031 | CAQ | B | Part 37 refresher training expired |  |  |  | N | NO | <C> RISK: Medium (B). CAUSE: Cause is Clear. Severity B. Document and Correct. Actions are created. <D> **** Detailed Description **** During a self-assessment it was identified that an EN employee with access to Part 37 material, that had changed positions within EN, did not maintain their refresher training. In 2016, this Qualification was set to Inactive when the employee changed positions within EN, so the part 37.43(c)(3) requirement to refresh training every 12 months was not satisfied. Access to Part 37 material should have been removed upon changing position, access was not removed. It was verified that the individual had NOT gained access to the Part 37 material area after the required training refresher time had expired. <I> **** Actions Taken **** Communicated the condition to RP Supervision, Security Personnel, and Access Authorization. The individuals access was promptly removed. <N> CAQ, Severity/Responsible Group: B/RADPR Risk (Probability/Consequence): Medium (B) Cause Uncertainty: Cause is Clear Qualification list wasn't verified against access report for Part 37 areas.
400819 | CR | 20191031 |  | 3 | Hot Spots Require Flush Plans |  |  |  | N | NO | <D> **** Detailed Description **** While reviewing the semi-annual survey results for hot spot trending, the following hot spots need to be evaluated for flushing or shielding based on increased trends on either on-contact or 30 cm dose rates: Hot spot #s 24, 25, 35, 39, 43, 50, 71, 75, 80, and 85. <I> **** Actions Taken **** Reviewed survey results for hot spots and evaluated potential trends in dose rates. Those results determined that flushing or shielding plans would be more effective than increasing the survey periodicity of these areas.
400820 | CR | 20191031 |  | 3 | Security Computer not transferring files to Corp Network |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The datapump export files from the Security Computer have not been sent thru the diodes to the Corp Network <I> **** Actions Taken **** Comp Engineering is working to resolve
400821 | CR | 20191031 | CAQ | D | SW-V-171A stuck in the shut position. | Y | Y |  | N | YES | <D> **** Detailed Description **** SW-V-171A stuck in the shut position. Valve need to be opened per SOP-COLDWEATHER-OPS. Need to investigate and resolve the issue. <I> **** Actions Taken **** CRS/SM informed. <N> Per discussion with dayshift Shift Manager and notes in WR 29152463 SW-V-171A was opened with assistance to allow for draining per SOP-COLDWEATHER-OPS. . | 02-00-SW-V-171A
400822 | CR | 20191031 |  | 4 | Cooling Tower 2B/2C Bus 52 Trouble | N | N |  | N | YES | <D> **** Detailed Description **** MCR received Cooling Tower 2B/2C Bus 52 Trouble alarm (H13-P824.M.2-1). SCI-RLY-OEA2/2/5 is in CLOSED, causing the alarm. All CW fans are running. Ops 4 reported normal voltage on Bus 52 (460v) and that LP-5RA/15 is closed. All of this indicates that there is a problem with Supervisory rather with than the equipment being monitored. Request Maintenance investigate and repair as required. | 02-00-SCI-RLY-OEA2/2/5
400823 | CR | 20191031 |  | 3 | Potential emhancement to IS/Training security Procedures |  |  |  | N | NO | <D> **** Detailed Description **** During the Vision upgrade project the question was asked about exam security during migration of data. The Exam Group reviewed the data obtained and determined that it contained no specific exam information. IS promptly brought this to Operationâ€™s Trainingâ€™s attention. The individuals with access to vision data bases were issued badges and placed on exam security to be conservative. The IS group only had 7 people with access to this data. GBP-REC-04, Confidential and Proprietary Information and GBP-IS-22, Access Control Standards, already govern access to this information but could be improved to be more specific. <I> **** Actions Taken **** Place all individuals with access to the Vision data base on exam security. Great questioning attitude by IS.
400824 | CR | 20191031 | CAQ | C | (QA) CDA Baseline/Data Sheets Show Incorrect Configurations |  |  |  | Y | NO | <C> An NRC resident inspector questioned as to whether or not this CR should be a Condition Adverse to Quality. After further review, this will be changed to CAQ. SD Metzger 11/14/19 <D> **** Detailed Description **** (QA) Configurations for two Direct Critical Digital Assets (CDA) is incorrect on Forms 26793 â€œCDA Security Control Baselineâ€ and 27011 â€œCDA Master Data Sheetâ€ (CMDS) for NET3-FW-ASACENTER and for NET3-FW-ASACENTER. These forms contain inaccuracies and inconsistencies regarding the number of digital ports available on the devices and which of those ports are connected. Neither form contains the correct configuration in PPM 10.1.28 â€œPort Blockersâ€, final Engineering Change (EC) 13492, and as found on the two devices installed in the plant. These forms are used to document how CDAs comply with sections of NEI 08-09. Inaccuracies and inconsistencies in these documents can lead to questioning the validity of the assessment conclusions that were reached. Factual Basis: (see EDMS for Details) Insights: â€¢ DES-2-25 â€œEngineering Change Design Modification Closeoutâ€ step 3.2.1a requires the Responsible Engineer (RE) to review Controlled Documents on the Affected Document List (ADL) for completeness, but this ADL review does not include any completed CDA Security Control Baseline or CMDS because these filled-in forms are not in the Controlled Documents module. No other steps in DES-2 -25 require the RE to ensure any completed CDA Security Control Baseline or CMDS align with the final EC. <I> **** Actions Taken **** Contacted Design Engineering Manager. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to Design Engineering. <N> Reccomend Cat D Des Eng The cause is known as it is not required for individuals to ensure the digital master data sheet is updated prior to EC close out. Consequence is low/medium as it could result in a regulatory finding. This issue will be addressed under CR 398342 assignment 02 where the process for ensuring the digital master data sheet is updated prior to closing the EC is fixed.
400825 | CR | 20191031 |  | 4 | Hotwell Iron trend | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Insoluble Iron in the condenser hotwell is displaying a general trend up. Starting on 9/5/19, the concentration of Iron has increased from 14.3 ppb to 27.3 ppb on 10/31/19. This is a similar trend to the one that occured in 2018 when MS-V-120B was found stuck open. The trend is an indication of potential FAC in the main condenser from steam erosion. This should be evaluated by System Engineering and the station FAC engineer. Metals analysis is a diagnostic parameter for Condensate and does not have any regulatory limits associated with the parameter per SWP-CHE-02 section 6.5.7. Feedwater Iron remains in the normal range indicating that the Condensate Filter Demins are successfully removing the Iron. Sampling frequency is weekly. <I> **** Actions Taken **** Informed Chemistry supervision and management. Sent trend information to System Engineering and Code Programs.
400826 | CR | 20191101 |  | 4 | Air/H2 Seal Oil D/P LOOS per SO-PI-200 | N | N |  | N | YES | <D> **** Detailed Description **** The Seal Oil DP as calculated per SO-PI-200 is 10.5 psid, below the minumum of 11 psid. Hydrogen pressure was 77 psig as read on the 441 and SO-DPI-23A read 16 psid. <I> **** Actions Taken **** Notified CRS and wrote CR | 02-00-SO-PI-200
400827 | CR | 20191101 |  | 4 | DW-V-100/55 leaks by seat | N | N |  | N | YES | <D> **** Detailed Description **** DW-V-100/55 leaks by seat approx 5-6 drops/min <I> **** Actions Taken **** Capped with a camlock cap Informed MCR . Initiated AR CR 400859 (TCC compensatory measure installation prior to evaluation), AR EVAL 400860 per SWP -CM-02, and TCHG AS 400860-01 per DES-2-9. | 02-00-DW-V-100/55
400858 | CR | 20191101 |  | 3 | PPM 16.4.3 procedure needs re-wording |  |  |  | N | NO | <D> **** Detailed Description **** In 16.4.3 step 4.2 reads â€œIf the Offgas Pretreatment Radiation Monitor is out of service due to testing greater than 4 hours, then ODCM RFO 6.1.2.1 Function 2 Compensatory Measure H applies.â€ This statement is incorrect and miss -leading. Anytime OG-RIS-612 is non-functional ODCM 6.1.2 .A, and 6.1.2.H applies immediately. The incorrect wording was also copied and pasted on the IMPACT7 statement for WO 02143294-01. The IMPACT 7 should provide information to help the user a good example would be â€“ entered per log entry Example â€œEntered ODCM RFO 6.1.2.A and 6.1.2.H for performance of PPM 16.4.3 which renders OG-RIS-612 nonfunctional. The offgas treatment system has been verified not bypassed (it is in Treat mode) per 6.1.2.H.1. Verified temporary Area Radiation Monitor in place to meet 6.1.2.H.3. Chemistry and EP informed; compensatory measures are in place per PPM 13.14.11. â€œ <N> **** Equipment Description **** PPM 16.4.3 Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
400859 | CR | 20191101 |  | 4 | TCC installed for AR CR 400827 | N | N |  | N | YES | <D> **** Detailed Description **** As described in AR CR 400827, a Temporary Configuration Change (TCC) - a camlock cap - was installed downstream of DW-V-100/55 as a compensatory measure for leakby. This TCC should have been evaluated per SWP-CM-02 prior to installation - it appears the TCC will likely be a Non-Intrusive Compensatory Measure (NICM). <I> **** Actions Taken **** Initiated this AR CR 400859. Initiated AR EVAL 400860 per SWP-CM-02 and TCHG AS 400860 -01 per DES-2-9. | 02-00-DW-V-100/55
400861 | CR | 20191101 |  | 4 | PPC-PRN-A1 Is displaying shutlle fault. | N | N |  | N | YES | <D> **** Detailed Description **** PPC-PRN-A1 Is displaying shutlle fault. This alarm can be reset and the printer will then print the alarm cache. Suspect the the many spurious alarms from MC-6N, OG loop seal 20/21, CW tower vibrations among others is negativly impacting the longevity of this machine. Recomend addressing the shuttle fault and the spruious alarms from MC-6N. | 02-00-PPC-PRN-A1
400862 | CR | 20191101 |  | 4 | Temporary Outage Corporate Network Switch not removed |  |  |  | N | YES | <D> **** Detailed Description **** During the last refuel outage, a corporate network switch (P612) and two corporate computers (P630) were installed to support outage maintenance. After the outage, the computers were removed, but the Network Switch was left in place. Suggest this CR and WR go to Telecom <I> **** Actions Taken **** Notified Operations. <N> **** Equipment Description **** E-CP-C91/P612 Bay 2 | 02-00-E-CP-C91/P612
400864 | CR | 20191101 |  | 3 | TMOD EC 18010 R0 is not ACTIVE or better status |  |  |  | N | YES | <D> **** Detailed Description **** Installation WOT 02151113-01 for TMOD EC 18010 R0 implementation has been at WORKING status since 10/30/19 but TMOD EC 18010 R0 remains at APPROVED status and its '340-I TCHG OPS' Milestone has not yet been signed by the CRS/Shift Manager. PPM 1.3.9 and PPM 10.1.27 both specify actions for the CRS/Shift Manager and the Work Supervisor or designee related to CRS/Shift Manager completion of the '340-I TCHG OPS' Milestone. Generally, the '340-I TCHG OPS' Milestone is signed by the CRS/Shift Manager before the implementation WOT is advanced to WORKING. . Part of the problem that occurred is that the TMOD Responsible Engineer did not perform actions specified in SharePoint guidance for Installation of Temporary Modifications - this guidance is referenced by ENG-DES-50 and required to be completed. The guidance for the TMOD Responsible Engineer to enter 'I' into the Install or Remove field on the M117 panel for the implementing WOT and to enter 'R' into the Install or Remove field on the M117 panel for the restoration WOT had not been completed. Both of these were corrected 11/01/19 by the initiator of this AR CR 400864. The TMOD Responsible Engineer also had actions to notify and inform the PSRO for additional actions to be completed which did not occur (the M111 panel 'Review Required' box is not checked for the implementation or restoration WOTs). . Recommend resolution assignment to AR-EFIN to drive completion of the incompleted administrative actions for TMOD EC 18010 R0. Recommend that the CRS/Shift Manager consider completion of PPM 1.3.9 and PPM 10.1.27 actions for signature of the TMOD EC 18010 R0 '340-I TCHG OPS' Milestone. Once the '340-I TCHG OPS' Milestone is signed, TMOD EC 18010 R0 should automatically advance to ACTIVE status since implementation WOT 02151113-01 is already WORKING status. . This is an administrative issue. <I> **** Actions Taken **** As described in the AR CR Detailed Description. . Per conversation with the Shift Manager, the existing step in implementation WOT 02151113-01 to ensure the '340-I TCHG OPS' Milestone for TMOD EC 18010 is signed before field changes are made has not yet been reached. Currently, the only process issues for TMOD EC 18010 are the missed administrative steps during TMOD preparation as described in the AR CR Detailed Description. Existing steps in the implementing WOT 02151113-01 instructions will ensure the TMOD '340-I TCHG OPS' Milestone is signed as required. | 02-00-E-TR-M2
400865 | CR | 20191101 | CAQ | D | Received Rod Accumulator Trouble for CRD-HCU-4611 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-4611. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-4611 was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear. | 02-00-CRD-HCU-4611
400866 | CR | 20191101 | CAQ | D | CRD-HCU-4611 abnormal High Water level alarm | Y | N |  | N | YES | <C> See CR 400865 <D> **** Detailed Description **** CRD-HCU-4611 alarmed for High Water level on 11-1-19. No moisture, whatsoever, could be drained from the P6 connector. The High Water level alarm remained locked in after blowing down from the P6. Slight mechanical agitation was applied to the High Water level switch. This cleared the alarm. This AR generated for trending purposes. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RX 522 | 02-00-CRD-HCU-4611
400868 | CR | 20191101 | CAQ | D | CRD-HCU-4611 â€“ minor leak from P6 connector | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-4611 has a minor leak from its P6 connector. The HCU was isolated and the threads of the connector and cap were cleaned off. Neolube was applied to the threads and the cap was torqued to the max of 200 inch lbs. Unfortunately, this did not fix the leak. This is a minor leak that should not require immediate attention. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** RX 522 | 02-00-CRD-HCU-4611
400869 | CR | 20191101 |  | 4 | TMU-MO-1B limits | N | N |  | N | YES | <D> **** Detailed Description **** TMU-MO-1B limit switchs are opertating correctly however closed limit seems to be engaging before vavle is full closed. Recomend MOV engineer evaluate. <I> **** Actions Taken **** Notified Supervisor | 02-00-TMU-MO-1B
400870 | CR | 20191101 | CAQ | C | PPM16.8.4 Standby Service Water System Effluent Monitor CH B | N | Y |  | N | NO | <D> **** Detailed Description **** During the performance of WO# 0211730601 CC/RC - Standby Service Water System Effluent Monitor - CH B it was discovered that the 109Cd source strength is not enough to perform section 7.11 LLD Setpoint Determination. The 109Cd source has a short half-life and has decayed to the point where it will no longer give the desired cps. <I> **** Actions Taken **** Notified Supervision, contacted Chemistry and HP to see if there is another source available that would meet our requirements. HP or Chemistry support may be needed so purchase a new source if there is not one available.
400871 | CR | 20191101 |  | 3 | RFW-P-1B trip oil pressure is high out of spec. | N | N |  | N | YES | <C> MRT Change: CR 400871 - moved from 4/Trend Repair to Severity 3 assigned to AR-OPSST. <D> **** Detailed Description **** RFW-P-1B trip oil pressure is 141 psig as read on RFT-PI -4G/1B. The high spec. is 140 psig. This pressure has been high out of spec the last 4 out of 5 shifts. The previous WO addressing this condition has been cancelled. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** TG-441 | 02-00-RFW-P-1B
400872 | CR | 20191101 | CAQ | D | TRB accumulator drain icing | Y | N |  | N | YES | <D> **** Detailed Description **** The drain valve on the TRB air accululator is icing again. request heat trace tape be applied to the drain l ine for cold weather months to prevent ice buildup and having to heat gun the valve to death repeatedly <I> **** Actions Taken **** informed the MCR initiated CR/WR <N> AR type EVAL needed for the proposed configuration change (application of heat trace tape)? | 02-00-E-TR-B
400885 | CR | 20191102 |  | 4 | T-4 Sump Hi-Hi Level alarm came in while pump running. | N | N |  | N | YES | <D> **** Detailed Description **** T-4 currently has only one operational pump, FDR-P-15B. FDR-P-15A has been broken for a long time. We routinely pump T-4 for at least a couple of hours every shift. Today, during pumping of T-4, the sump Hi-Hi- level came in and is still in as of this writing. Please investigate whether issue is large water introduction into sump, or possible issues with FDR-P-15B. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 441 Condenser bay | 02-00-FDR-P-15B
400886 | CR | 20191102 |  | 3 | Work order task 02120144 01 needed ALARA planning at T0. |  |  |  | N | NO | <D> **** Detailed Description **** Work order task 02120144 01 did not include ALARA planning at T0. Work order task 02120144 01 did not include ALARA planning at T0. Mechanics were hampered during their task performance by a lack of ALARA planning. HP investigated this task and found this model work order is generated to support work on HPCS pump every 6 months. The work order needs to be routed to ALARA for planning prior to being taken to STATUS READY or WORKING. Additional work orders which have been generated for upcoming work and need to be ALARA planned: 0227887, 02135860, 02142698, 02153713. Please modify the model work order to include routing to ALARA Planning. <I> **** Actions Taken **** Contacted mechanic supervisor, investigated work order, and wrote this CR. <N> The noted future PM occurence Work Orders have been updated to include RWP hours. Model was also updated to include RWP hold.
400887 | CR | 20191102 |  | 4 | CAS-F-19A has a small leak on the horizontal brass fitting | N | N |  | N | YES | <D> **** Detailed Description **** CAS-F-19A has a small leak on the horizontal brass fitting above the level indicator. Please see attached video. <I> **** Actions Taken **** wr written this is on the CAS Sytems. . Oil in this filter indicates either oil carryover from one of the CAS compressors or an oil leak in CAS-DY-2A. Since the air flows from CAS-DY-2A through CAS-F-18A, -19A and -20A sequentially, these filters should also be inspected for oil. | 02-00-CAS-F-19A
400888 | CR | 20191102 |  | 3 | T441 West end Housekeeping issues |  |  |  | N | NO | <D> **** Detailed Description **** Mulitple housekeeping issues equipment not yet removed post R24 with work in progress signs expired in June. WO 0213600, 02078358, 02114705, 02137959. Scaffold material staged WO 01158000 work in-progress sign 9/30/19 in proximity to SCW skid. Same area sits portal monitors used for the outage sitting just south of an authorized storage area for HP lockers. <I> **** Actions Taken **** Contacted SM and maintenance
400889 | CR | 20191102 |  | 4 | CAS-F-19A appears to have oil water in (bubbling leak) | N | N |  | N | YES | <D> **** Detailed Description **** CAS-F-19A appears to have oil water in it as evidenced by air leak reported in AR 400887 (bubbling leak). Please evaluate cleaning the filter and verifing the trap blowdown is functioning and the upstream and downstream filters are drained and clean. please see attached video and pictures. <I> **** Actions Taken **** after discussion with supervision it was decided to write a second wr and CR. . See also CR 400887. Oil in this filter indicates either oil carryover from one of the CAS compressors or an oil leak in CAS-DY-2A. Since the air flows from CAS-DY-2A through CAS-F-18A, -19A and -20A sequentially, these filters should also be inspected for oil. | 02-00-CAS-F-19A
400890 | CR | 20191102 | CAQ | C | (QA) 3 Total Required Port Blockers Missing on 2 Direct CDAs |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Two Direct Critical Digital Assets (CDAs), NET4-FW -ASACENTER and NET4-KVM-SW/1, were missing port blockers, contrary to PPM 10.1.28 "Port Blockers" and the two Engineering Changes (ECs) that installed these CDAs. Not having port blockers installed in unused ports on a CDA represents a Cyber Security vulnerability. Requirements: (see EDMS for Details) Factual Basis: (see EDMS for full Details) Insights: â€¢ PPM 10.1.28 is updated for configuration control after installation of Port Blockers on a device, but the procedure is updated from the EC documents, not created as an â€œas-builtâ€ verification after a walkdown. â€¢ Quality recommends the line performs an Extent of Condition to look for similar issues with other CDAs. â€¢ Upon notification of this issue by Quality, WR 29152111 was initiated on 10/15/19 to add Port Blockers to the unused ports on both NET4-FW-ASACENTER and NET4-KVM-SW/1. (WR completed 10/16/19) <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Security, and the Engineering Supervisor over Computer Engineering. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to Computer Engineering. <N> Reccoment Cat D to Computer Eng The cause is known, this is an error in which the individuals completing the installation of port blockers need to ensure alignment to the required documents. Consequence is low/medium as it could result in a regulatory finding. This issue will be addressed under CR 399489 assignment 02 & 04 where a validation will be completed to ensure alignment of 10.1.28, the port blockers in the field, and the CDA documentation.
400891 | CR | 20191102 | CAQ | C | (QA) 5 Incomplete Cyber PM WOTs by CE at Closed Status |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Five Quality Assurance Records (QARs) are incomplete Cyber Preventive Maintenance (PM) Work Order Tasks (WOTs) for Computer Engineering (CE) resources. These WOTs at â€œClosedâ€ status are incomplete for not documenting a pre -job brief, not identifying who performed the work, and blanks on sign-off lines for steps in WOT Instructions. These Cyber Security PMs are required by CDA Security Control Baselines to meet a commitment in CSP-01 â€œCyber Security Planâ€ to implement the requirements in NEI 08-09 rev 6 â€œCyber Security Plan for Nuclear Power Reactorsâ€ Addendum 1. Requirements: â€¢ SWP-PRO-01 â€œProcedure and Work Instruction Use and Adherenceâ€ step 4.5.9 requires â€œINITIAL OR SIGN the step as being performed and â€œPRINT name AND INITIALS on the front cover sheet of the procedure.â€ Factual Basis: (see EDMS for Details) Insights: â€¢ Although many of the Cyber Security PMs were created as first-time evolutions within the last 2 years; Supervisors and Managers are required to provide oversight to ensure workers meet standards and expectations regardless of how many changes occur to industry standards and station procedures. <I> **** Actions Taken **** Contacted Engineering Supervisor over Computer Engineering. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to Computer Engineering. <N> WOT 02128769-01 is not CLOSED, but has been at COMPLETE status since 7/29/19. Reccomend Cat D to Comp Eng The cause is known, this is an error in which the individuals completing the PMs need to sufficiently document the steps and follow procedure for completing PMs. To ensure the PMs are completed accurately additional oversight is needed. Consequence is low/medium as it could result in a regulatory finding. This issue will be addressed under CR 398340 assignment 06 where a process for additional oversight will be established to ensure the correct information is completed for the WO instructions for the PMs, sufficient evidence is part of record, and the process is fixed.
400892 | CR | 20191102 | CAQ | C | (QA) 1 QAR Shows Incomplete Performance of Cyber PM WOT |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) One Quality Assurance Record (QAR) contains no evidence of Critical Digital Asset (CDA) passwords being reset in accordance with SWP-CSW-30 â€œControlled Media and Critical Digital Asset Password Standardsâ€ for six of the CDAs listed in one Essential Preventive Maintenance (PM) Work Order Task (WOT). QAR WOT 0212875901 contains objective evidence that password resets were not reset for six of the CDAs, but it does not even list many of the other CDAs in the scope of this PM. SWP-CSW-30 implements the requirements of 10CFR73.54 under the Energy Northwest Cyber Security Plan to achieve high assurance CDA passwords are adequately protected against cyber-attacks. Requirements: (see EDMS for Details) Factual Basis: (see EDMS for Details) Insights: â€¢ Many Cyber Security PMs were created as first-time evolutions in the last 2 years, but Supervisors and Managers are still required to provide oversight to ensure workers meet standards and expectations. â€¢ Interviews revealed the table mentioned above was a tool used for password resets for certain CDAs. â€¢ The â€œCE Quarterly PMs Sortâ€ spreadsheet has a row for each CDA, and a column for each required PM reference, but it does not have a column on the far right for the performerâ€™s initials. â€¢ On 8/22/19, in AR-CR 398340 â€œCyber PMs not conducted as aligned to industry [benchmarking]â€ the line identified that some PMs for select password resets were not conducted; however, this CR does not cite the specific gap for not complying with station procedures to initiate a CR when not performing the entire PM scope. <I> **** Actions Taken **** Contacted Engineering Supervisor over Computer Engineering. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to Computer Engineering. <N> Reccomend Cat D to ITMGMT The cause is known, this is an error in which the detail needed to adequately prove that the PMs are completed with sufficient evidence. Consequence is low/medium as it could result in a regulatory finding. This issue will be addressed under CR 398340 assignment 03 which will ensure the correct detail for the WO instructions for the PMs are created, sufficient evidence is part of record, and the process is fixed.
400893 | CR | 20191102 | CAQ | C | (QA) Not Complying with SWP-CSW-21 for 2 Random PMs/year |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) The Essential Cyber Security Preventive Maintenance (PM) to randomly test Cyber Security monitoring tools was created with a specified 5-year testing frequency, contrary to a site-wide Cyber Security procedure that requires this testing at a minimum of twice a year. The â€œrandomâ€ frequency meets one of several monitoring frequencies required by NEI 08-09 â€œCyber Security Plan for Nuclear Power Reactorsâ€ Addendum 1; however, this NEI standard does not define the term, â€œrandomâ€. Requirements: (see EDMS for Details) Factual Basis: (see EDMS for Details) Insights: â€¢ The NEI 08-09 standard does not specifically define â€œrandomâ€ testing, which can lead to differing interpretations of â€œrandomâ€ for Cyber Security PMs. â€¢ Interviews revealed Maintenance Planning picked the 5-year interval to meet the â€œrandomâ€ frequency specified in Essential PMID-RQ 26571, contrary to PPM 1.5.13, which states that Engineering owns Essential PMs. â€¢ On 8/22/19, in AR-CR 398340 â€œCyber PMs not conducted as aligned to industry [benchmarking]â€ the line identified that PMs were not conducted; however, this CR does not cite the specific gap for not complying with Cyber Security procedures requiring testing of cyber security intrusion monitoring tools at "random" intervals. â€¢ After notification of this issue by Quality, the Cyber team created assignment 04 under AR-CR 398340 to ensure that â€œrandomâ€ interval Cyber PMs are addressed. <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Security. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to ITMGMT. <N> Reccomend CAT D to ITMGMT The cause is known, this is an error in which the process ensure PMs where created at random intervals. Consequence is low/medium as it could result in a regulatory finding. This issue will be addressed under CR 398340 assignment 04 which will ensure the correct PMs are created and the process is fixed.
400894 | CR | 20191102 | CAQ | C | (QA) 7 Incomplete Cyber PM WOTs by Cyber at Closed Status |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) 7 Incomplete Cyber PM WOTs by Cyber at Closed Status (QA) Seven Quality Assurance Records (QARs) are incomplete Cyber Preventive Maintenance (PM) Work Order Tasks (WOTs) by Cyber Security resources. These WOTs at â€œClosedâ€ status are incomplete for not documenting the pre-job brief, not identifying who performed the work, and blanks on sign-off lines for steps in WOT Instructions. These Cyber Security PMs are required by CDA Security Control Baselines to meet a commitment in CSP-01 â€œCyber Security Planâ€ to implement requirements in NEI 08-09 rev 6 â€œCyber Security Plan for Nuclear Power Reactorsâ€ Addendum 1. Requirements: (see EDMS for Details) Factual Basis: (see EDMS for Details) Insights: â€¢ Many Cyber Security PMs were created as first-time evolutions within the last 2 years, but Supervisors and Managers are still required to provide oversight to ensure workers meet current station standards and expectations regardless of how many changes occur to industry standards and Cyber procedures. <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Security. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to ITMGMT. <N> WOT 02137782-01 is not Closed, but has been at COMPLETE status since 8/19/19. Reccommend Cat D ITMGMT The cause is known, this is an error in which the individuals completing the PMs need to sufficiently document the steps and follow procedure for completing PMs. To ensure the PMs are completed accurately additional oversight is needed. Consequence is low/medium as it could result in a regulatory finding. This issue will be addressed under CR 398340 assignment 06 where a process for additional oversight will be established to ensure the correct information is completed for the WO instructions for the PMs, sufficient evidence is part of record, and the process is fixed.
400895 | CR | 20191102 |  | 3 | (QA) 7 of 10 Cases of Incorrect or Blank Software Info |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) 7 of 10 sampled software/firmware had either blank or incorrect software information in Asset Suite fields required by DES-4-12 â€œEquipment Revision Tracking and Control (RT&C) Processâ€ and MUGM-01 â€œMEL Users Guide Manualâ€, contrary to SWP-CSW-01 â€œSoftware Quality Assurance Programâ€. Missing or incorrect software information in the Master Equipment List (MEL) does not meet the stationâ€™s configuration control requirements Requirements: â€¢ SWP-CSW-01 step 5.3.2 states, â€œEngineering UPDATES all software information related to Unit 02 software (considered Plant) for the Software Catalog In accordance with DES-4-12 and MUGM-01.â€ Factual Basis: (see EDMS for Details) Insight: â€¢ The Software Catalog is electronically generated from the Master Equipment List (MEL) fields within Asset Suite, which must be populated correctly for the Software Catalog to remain correctly up to date. <I> **** Actions Taken **** Contacted the Engineering Supervisor over Digital Designs. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to Design Engineering.
400896 | CR | 20191102 | CAQ | C | (QA) Required Cyber PMs Not Created for 2 SR Direct CDAs |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Required Cyber Security Preventive Maintenance (PM) tasks were not created for two Safety-Related (SR) Direct Critical Digital Assets (CDAs), contrary to the CDA Security Control Baseline assessment. Actual consequence is at least one recurring PM task was never performed as part of our Cyber Security mitigation controls for physical protection, configuration management, contingency planning, and system hardening to meet the NEI 08-09 â€œCyber Security Plan for Nuclear Power Reactorsâ€ Addendum 1 Appendix E. Requirements: (see EDMS for Details) Factual Basis: (see EDMS for Details) Factual Basis: (see EDMS for full Details) â€¢ In all five sections on approved/signed Form 26973 state, â€œPM ID#: PMs have been established under AR 224656-63" â€¢ AR-EVAL 224656-63 was closed by System Engineering . . . Insights: (see EDMS for full Details) â€¢ AR-EVAL 224656-63 did not specifically direct System Engineering to create Cyber Security PMs to meet any of the five CDA Security Control Baseline requirements. â€¢ On 8/22/19, in AR-CR 398340 â€œCyber PMs not conducted as aligned to industry [benchmarking]â€ the line identified that some PMs for select password resets were not conducted; however, this CR does not cite the specific gap for Engineering Changes (ECs) not ensuring the creation of PMs to meet a CDA assessment. <I> **** Actions Taken **** Contacted Engineering Supervisor over Digital Designs. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to Design Engineering. <N> Reccomend Cat D to ITMGMT The cause is known, this is an error in which the process did not require a separate assignment for Cyber and Maintenance PMs. This resulted in only the Maintenance PMs being created. Consequence is low/medium as it could result in a regulatory finding. This issue will be addressed under CR 398340 assignment 07 which will ensure the correct PMs are created and the process is fixed.
400897 | CR | 20191102 | CAQ | C | (QA)ARMA:Trend in Insufficient Rigor in Work Performed by CE |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Unrecognized trend in insufficient rigor in work performed by Computer Engineering (CE) within the last 2 years as evidenced by multiple performance gaps noted in 10 Condition Reports. The gaps include leaving blanks on Work Orders for Pre-Job Briefs and Work Performed By, not using â€œNAâ€ per procedures, not completing entire Preventive Maintenance (PM) scope, not initiating a Condition Report for missing port blockers per procedure, not closing out a Work Request (WR) per procedure, not properly closing out an Engineering Change (EC) per procedure, not configuring a device per a design specification, not populating Asset Suite per procedures with software information, and not creating Software Quality Assurance (SQA) documents required by procedures. Factual Basis: (see EDMS for Details) Insights: â€¢ Many Cyber Security PMs were created as first-time evolutions within the last 2 years, but Supervisors and Managers are still required to provide oversight to ensure workers meet station standards and expectations. â€¢ Computer Engineering has moved under a few different Managers or Supervisors in the last 2 years, which may have resulted in less than adequate oversight of their work performance. <I> **** Actions Taken **** Contacted Engineering Supervisor over Computer Engineering. . This is an Area Requiring Management Attention (ARMA) identified in Quality Audit AU-CSQ-19. . Recommend assigning to Computer Engineering.
400898 | CR | 20191102 | CAQ | C | (QA) Finding: Program Deficiencies in Cyber PMs & PBs |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Program Deficiencies in the Cyber Security aspects of Preventive Maintenance (PM) and Port Blockers (PB) as evidenced by an accumulation of failures to implement industry standards. Gaps are against the Critical Digital Asset (CDA) Security Control Baseline assessments and procedures that implement the requirements in industry standard NEI 08-09 rev 6 â€œCyber Security Plan for Nuclear Power Reactorsâ€, which the Nuclear Regulatory Commission endorsed to meet the 10 CFR 73.54 regulation. Diverse gaps include PMs for CDAs not created, CDA PMs not performed per intervals in procedures, and CDA PMs not performed entirely, missing PBs on installed Direct Safety-Related (SR) CDAs, PBs not matching configuration documents, and noncompliance with the Cyber Security port blocker procedure that requires initiating a Condition Report (CR) for missing PBs. Requirements: (see EDMS for Details) Factual Basis: (see EDMS for Details Insights: â€¢ Many Cyber Security PMs were created as first-time evolutions within the last 2 years, but Supervisors and Managers are still required to provide oversight to ensure workers meet station standards and expectations regardless of how many changes occur to industry standards and Cyber procedures. â€¢ This is a similar issue to a Quality-identified AR-CR 360636 â€œ(QA) Lack of Thoroughness in Essential EP PM Implementationâ€ where other groups performed work for the Emergency Preparedness (EP) Program. This issue was turned around by an increase in oversight by EP. â€¢ Cyber Security sponsors PPM 10.1.28 â€œPort Blockers, but Computer Engineering inspects some PBs. <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Security. . This is a Finding identified in Quality Audit AU-CSQ-19. . Recommend assigning to ITMGMT. <N> Reccomend Cat D to ITMGMT The cause is known, this is an error in the amount of oversight that is being applied to ensure PMs and PBs are being completed sufficiently is lacking. To ensure the PMs and PBs are completed accurately additional oversight is needed. Consequence is low/medium as it could result in a regulatory finding. This PM issue will be addressed under CR 398340 assignment 06 where a process for additional oversight will be established to ensure the correct information is completed for the WO instructions for the PMs, sufficient evidence is part of record, and the process is fixed. The Port Blocker issues will be addressed under CR 399489 assignment 03 where a process will be used to control the port blockers.
400899 | CR | 20191102 | CAQ | C | (QA) Finding: Program Deficiency in Cyber-related Records |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Program Deficiency in the Cyber Security related Records aspect for a failure to effectively implement industry standards. These Records are required to meet industry standard NEI 08-09 rev 6 â€œCyber Security Plan for Nuclear Power Reactorsâ€, which the Nuclear Regulatory Commission endorsed to meet the 10 CFR 73.54 regulation. Quality identified two Records issues during the 2018 Cyber Security audit, and several different Records issues during this 2019 Cyber Security audit. Diverse gaps with respect to Quality Assurance Records (QARs) indicate a Program Deficiency. Gaps in last 2 years include completed forms for Portable Media and Digital Devices not in Records, alternate controls/frequencies not in Records, 2 site-wide procedures not specifying Record requirements, licensing document change form missing signatures, 3 Cyber-sensitive Engineering Changes not password-protected in Record storage, Cyber test results not in Records, and a Record submittal form missing required signatures. Requirements: (see EDMS for Details) Factual Basis: (see EDMS for Details) â€¢ The NEI 08-09 section 4.13 requirements for records has not changed within the last 2 years. â€¢ Previous AU-CSQ-18 audit identified Records issues different than any of the AU-CSQ-19 audit issues cited above, i.e., no 2019 Records issues were repeats of the 2018 Records issues. â€¢ AR-CR 389673 was for an unsigned Transmittal form for a hasty correction of AR-CR 386989. <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Security. . This is a Finding identified in Quality Audit AU-CSQ-19. . Recommend assigning to ITMGMT. <N> Reccomend Cat C to ITMGMT The cause is known, this is an error in the amount of oversight that is being applied to ensure Records are implemented to meet industry standards. To ensure Records completed accurately and submitted timely additional oversight is needed. Consequence is low/medium as it could result in a regulatory finding.
400900 | CR | 20191102 |  | 3 | Investigate CFD resin D/P issue. | N | N |  | N | YES | <D> **** Detailed Description **** Currently, the situation with the Condensate Filter Demineralizers is early exhaustion of resin due to high D/P across the filter. Today, COND-DM-1C was backwashed and precoated, as it was at 22 PSID and had no high-level relaxes left. This was over two days ahead of schedule. The issue appears to be getting worse, and requires investigation. Possible issues could be filter septa clogging (probably most likely), a change in the way Graver manufactures our resin that makes it less porous/more likely to compact down, or actual collection of mechanical debris on top of the resin that increases D/P. Please investigate ASAP, as this issue is costing the plant a lot of money and is causing issues with resin storage space. <I> **** Actions Taken **** Notified SMgt, wrote CR. . Per RWCR watch, we have room in the CPR tanks for 3 more CFD backwashes. There are 3 more CFD's over 20 psid. Although this is not a TS or non-TS SSC issues, it has the potential to cause us to lower power in response to high d/p across the CFD's. <N> **** Equipment Description **** RW 467/507 | 02-00-COND-DM-1A,02-00-COND-DM-1B,02-00-COND-DM-1C,02-00-COND-DM-1D,02-00-COND-DM-1E,02-00-COND-DM-1F
400901 | CR | 20191102 |  | 3 | CFD resin storage space getting critical | N | N |  | N | NO | <D> **** Detailed Description **** We are close to running out of room to store CFD resin. CPR-TK-92A already contains 375 cubic feet and is full, and as of today, CPR-TK-92B 285 cubic feet, leaving 90 CF remaining. That is enough for only three more CFD resin loads. If the schedule for CFD BW/PC adheres, we will be out of storage space as of Wednesday, November 6th. We have been seeing a lot more resin going into storage since the problems with short resin lifecycles began (see CR 400900 for more information). Please expedite resin transfer to vendor. <I> **** Actions Taken **** Notified SMgt, wrote CR. . Although this is not a TS or non-TS SSC issues, it has the potential to cause us to lower power in response to high d/p across the CFD's. <N> **** Equipment Description **** CPR-TK-92A, CPR-TK-92B, RW 437.
400902 | CR | 20191102 |  | 4 | COND-V-110A appears to be leaking 1/4 to 1/2 cup/sec | N | N |  | N | YES | <D> **** Detailed Description **** COND-V-110A appears to be leaking 1/4 to 1/2 cup/sec. attempted moderate force in the closed direction it is a drain linefor the Condesate inlet for the Gland Seal steam Condenser. <I> **** Actions Taken **** wr/cr | 02-00-COND-V-110A
400903 | CR | 20191102 | CAQ | D | RHR-P-2A Mislabeling | Y | Y |  | N | YES | <D> **** Detailed Description **** RHR-P-2A has vibe points that are label North and East. OSP -RHR/IST-Q702 asks for vibes from North and West. Either OSP-RHR/IST-Q702 needs updated to North and East points along with vibe machine program or RHR-P-2A needs East point relabed West. <I> **** Actions Taken **** Notified Supervisor | 02-00-RHR-P-2A
400904 | CR | 20191102 |  | 4 | COND-P-2A has some of the sound insulation on the Air exhaus | N | N |  | N | YES | <D> **** Detailed Description **** COND-P-2A has some of the sound insulation on the Air exhaust screen. this is a small bit see picture. wrote CR for trending/history <I> **** Actions Taken **** recommend close to trending or history | 02-00-COND-P-2A
400905 | CR | 20191102 |  | 3 | unable to view documents in eWP |  |  |  | N | NO | <D> **** Detailed Description **** The CRO2 computer will not open documents via eWP. A small black 'X' appears in the upper left corner of the viewing window. This happens for PDFs such as work orders and word documents such as impact statements and work order instructions. <I> **** Actions Taken **** attmepted several work orders with the same results. <N> The ability to not view documents from the Open Panel, in DataGlance, is due to the Adobe plug-in not being installed on their computer. Users that need the Adobe plug-in installed on their computer will either need to do one of the following: 1. Installing the Software themselves by using the following steps: . 1a. Open an internet browser to the current 1b. Type in the word â€œSoftwareâ€ on the Task Bar and it will bring up the following link: http: http ://software/cmapplicationcatalog/#/SoftwareLibrary/AppListPa geView.xaml 1c. Select â€œAdobe Acrobat Reader DC (Browser Intergraded for eWP)" 1d. Select Install 1e. The installation will take about 5 to 10 Minutes 1f. Once that Software is installed documents will now be viewable in the DataGlance open mode. . 2. Call the Help Desk (with their workstation service tag number) and request the â€œBrowser Integrated version of Adobe Acrobat Reader DCâ€ package be installed on their workstation. . The ability to not open documents from the edit panel is due to the following: The package is checked out to a tablet - Normally when a package is not checked out to a tablet, documents may be viewable and editable. But since the package is checked out to a tablet, the documents are not viewable due the tablet having the ability to edit documents.
400906 | CR | 20191102 | CAQ | C | RHR-P-2A Upper Bearing Oil | Y | Y |  | N | YES | <D> **** Detailed Description **** Per 10.2.13 approved lubricants RHR-P-2A has Mobil DTE 732 in both upper and lower bearings. After samples were taken it appears the lower bearing is Mobil DTE 732 however the upper bearing is not Mobil DTE 732 and appers to be Mobil DTE Extra Heavy. Need Engineering to verify oil types in both upper and lower bearing of RHR-P-2A. No oil was added after samples. <I> **** Actions Taken **** Noified OPS and Supervisor | 02-00-RHR-P-2A
400907 | CR | 20191102 |  | 4 | Water level indication becoming a station issue |  |  |  | N | NO | <D> **** Detailed Description **** We currently have broken level indicators for the CW basin, Spray pond, and TMU pump house. These are all causing random alarms in the Main Control Room. These deficiencies need to be fixed in a more timely manner <I> No new equipment issues - see individual AR for IODS.
400916 | CR | 20191103 |  | 3 | WO 0212234903 planned with invalid Barrier Impairment |  |  |  | N | NO | <D> **** Detailed Description **** WO 0212234903 references a BI 15-0091 which has been closed, this is the BI from a previous performance of this surveillance. No new BI was prepared for this work. <I> **** Actions Taken **** Wrote and approved BI 19-0432 to allow work to continue.
400917 | CR | 20191103 |  | 3 | 2019 Mid Cycle- Performance Gap OP.1-13 |  |  |  | N | NO | <D> **** Detailed Description **** Related Objective: OP.1-13. Operators know the objective of the procedure and the basis for procedure steps prior to manipulation. They operate the plant in accordance with approved, up-to-date operating procedures and information. Problem Statement: Operations supervisors have not utilized administrative procedures effectively to ensure Procedure Usage and Adherence is followed. This has led to inappropriate use of conditional steps, removing equipment from service for maintenance without a formal evaluation, and not closing active LCO/INOP sheets when work was completed. The Work Authorization Worksheet is not being consistently used to assess plant impact when authorizing work and there is not a forcing function to evaluate LCO/INOP sheets closure. <I> **** Actions Taken **** Informed leadership team. Recommend assignment to Operations
400918 | CR | 20191103 |  | 3 | 2019 Mid Cycle- Performance Gap OF.1-4 |  |  |  | N | NO | <D> **** Detailed Description **** There are long standing issues that have not been resolved effectively. In some cases, the resolution is not known or understood Related Objective: OF.1-4. Solutions to plant operational problems are focused on both the immediate concerns and the long-term resolution of the issues. Temporary solutions are limited to mitigating the actual or potential effects of operational problems until permanent resolutions can be implemented. Problem Statement: Consequences of not eliminating long standing issues has resulted in an unplanned downpower (COND-LCV-11), potential equipment damage due to degraded equipment (RWCU-V-35), outage impacts with new emergent scope (turning gears), and potential reduction in safety (lighting issues). <I> **** Actions Taken **** Informed leadership team. Initiated CR. Recommend assignment to Operations.
400919 | CR | 20191103 |  | 3 | 2019 Mid Cycle- Performance Gap MA.1-5 |  |  |  | N | NO | <D> **** Detailed Description **** Precision maintenance practices during component reassembly and testing Related Objective: MA.1.5. Maintenance personnel perform precision work by ensuring equipment is reassembled to exacting specifications. Problem Statement: Maintenance and supplemental workers, have not consistently applied precision maintenance practices during component reassembly and testing. This has resulted in safety system component unavailability and rework. Contributing, workers and supervision are failing to comply with written procedural guidance or work instructions. Assumptions were made in the field regarding â€œpen and inkâ€ changes (e.g. RHR-V-53A in R24) and there was a lack of questioning attitude. <I> **** Actions Taken **** Informed leadership team. Initiated CR. Recommend assignment to Maintenance. <N> Actions to address performance gaps are being tracked under AR-00392031. No further actions required under this AR.
400920 | CR | 20191103 |  | 3 | 2019 Mid Cycle- Performance Gap MA.2-13 |  |  |  | N | NO | <D> **** Detailed Description **** Maintenance and Work Order Quality Related Objective: MA.2.13- Maintenance procedures and documents are clear and technically accurate, provide appropriate direction, and are used to support safe and reliable plant operation. Applicable operating experience is incorporated during document preparation and revision. Problem Statement: There are multiple examples of work instruction quality contributing to events or delays in the field. Some of these examples include working on the wrong component, missing steps or procedural requirements in work instructions, steps written in the wrong order, ECâ€™s not being incorporated, missing Limitation of Use (LOU), missing signoffs, and lack of consistency in work orders <I> **** Actions Taken **** Informed leadership team. Initiated CR. Recommend assignment to Maintenance.
400921 | CR | 20191103 |  | 3 | 2019 Mid Cycle- Performance Gap MA.2-16 |  |  |  | N | NO | <D> **** Detailed Description **** FME events during R24 Refueling Outage Related Objective: MA.2.16- Maintenance activities are planned and performed to prevent the introduction of foreign material into components and systems. Programs are implemented to clearly establish a foreign material prevention philosophy and provide guidance for the recovery of foreign material. AR-CR: Problem Statement: During the 2019 refueling outage, personnel contributed to several events that could have had an undesirable effect on plant equipment including the nuclear fuel. This has the potential for unplanned extensions to maintenance windows. <I> **** Actions Taken **** Informed leadership team. Initiated CR. Recommend assignment to Maintenance.
400922 | CR | 20191103 |  | 3 | 2019 Mid Cycle- Performance Gap WM.1-3 |  |  |  | N | NO | <D> **** Detailed Description **** Pre-Outage Preparations challenging outage readiness Related Objective: WM.1.3- Station leaders demonstrate the accountability and teamwork needed for work management by supporting station prioritization, work selection, scope stability, and adherence to the published schedule. AR-CR: Problem Statement: Pre-Outage Preparation and Strategy were not aligned, challenging outage readiness. Prior to R24, scope additions, material requests, weekly resource availability, and the 2-week â€œno fly zoneâ€ were not appropriately controlled and/or utilized during the R24 pre-outage window, resulting in decreased readiness and poor outage schedule adherence. Vertical slice ineffectiveness and inadequate application of resource / qualification look-ahead tools, contributed to this outcome. <I> **** Actions Taken **** Informed leadership team. Initiated CR. Recommend assignment to PS&O.
400923 | CR | 20191103 |  | 3 | 2019 Mid Cycle- Performance Gap WM.1-30 |  |  |  | N | NO | <D> **** Detailed Description **** Inadequate Work Implementation Preparation/Readiness Related Objective: WM.1.30- Personnel prepare for work implementation commensurate with the level of risk, the importance of the component to work execution, and their knowledge and experience with the scheduled work. Work group interfaces and coordination points are identified as part of the preparation. Problem Statement: In some instances, opportunities to identify and correct work challenges, conflicts, and instructions are not taken advantage of prior to implementation during the preparation phases of Work Management. As a result, these challenges come to fruition during work implementation, leading to real and potential risk impacts, scope revisions, and general schedule delays and changes to both current and future work weeks (when scope is rescheduled to other work weeks). <I> **** Actions Taken **** Informed leadership team. Initiated CR. Recommend assignment to PS&O.
400924 | CR | 20191103 |  | 4 | 2019 Mid Cycle- Performance Gap PI.1-3 |  |  |  | N | NO | <D> **** Detailed Description **** Untimely and Sustained Improvement Performance Inadequacy Related Objective: PI.1.3- Leaders and individuals identify and promptly report deficiencies, near misses, and precursor events. They encourage the identification of opportunities for improvement by recognizing and publicizing good catches, thereby contributing to a low -threshold reporting culture. Problem Statement: Some corrective action plans and strategies to address recurring behavioral challenges and long-standing, cross-functional station issues have not resulted in timely and/or sustained improved performance. Notable impacts include Leadership Fundamentals, Industrial Safety, and non-critical equipment conditions. Contributing, non-CAQ (conditions not adverse to quality) backlogs, over the past year, have increased. Many of these non-CAQ backlog actions to address equipment issues are not traceable to the work management system to assist in driving resolution. Some non-critical equipment trends exhibit similar programmatic gaps in addressing recurring issues, results of which can be observed throughout the plant such as lighting and safety shower condition(s). <I> **** Actions Taken **** Informed leadership team. Initiated CR. Recommend assignment to Performance Improvement. <N> This gap was previously identified under 398728 and actions created. Performance Improvement peer recommendations were captured in 400347 and assignments were created and dispositioned to AR-PERFIMP. Both were cross referenced to this CR. No additional actions are required, PI Manager approves closure to previous CRs .
400925 | CR | 20191103 |  | 3 | OSP-INST-H101 Discrepancy | N | N |  | N | NO | <D> **** Detailed Description **** Completion of TSP-THERM-C101 and OSP-RRC-D701 were not documented correctly during OSP-INST-H101. The eSOMS log for OSP-INST-H101 was logged as â€˜N/Aâ€™ vice â€˜OKâ€™ for both surveillances. Paper copies of the surveillances show they were accomplished within their required periodicities, but improperly documented for OSP-INST-H101. This CR is to identify that no surveillance requirements were missed, although improperly documented in eSOMS. <I> **** Actions Taken **** Validated all SRs were completed withing periodicity and documented this issue with this CR. <N> This is a log taking issue only. The identified surveillances were completed as required within the specified periodicity.
400926 | CR | 20191103 | CAQ | D | E-TR-7/71 Transformer oil level indicates High. | Y | N |  | N | YES | <D> **** Detailed Description **** E-TR-7/71 transformer level indicates High. Please investigate. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** SM-7 room | 02-00-E-TR-7/71
400927 | CR | 20191103 | CAQ | D | CMS-RIS-12A screen failed. | Y | N |  | N | YES | <D> **** Detailed Description **** CMS-RIS-12A screen failed. It usually has current activity displayed. It is now black, and depressing buttons did not cause it to come on. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CMS-RIS-12A
400928 | CR | 20191103 |  | 3 | eSoms failed to upload to CRO1 iPad again |  |  |  | N | NO | <D> **** Detailed Description **** the function worked multiple times today and then failed when trying to upload the 1200 logs.
400929 | CR | 20191103 | CAQ | D | E-IR-TR/B Has a small N2 leak where the braided N2 hose atta | Y | N |  | N | YES | <D> **** Detailed Description **** E-IR-TR/B Has a small N2 leak where the braided N2 hose attaches to the outside of the cabinet. After replacing the n2 bottle the connection was snooped and found to be bubbling. Will require bypassing sudden pressure relay just like replacing the bottle. <I> **** Actions Taken **** wrote wr and Cr | 02-00-E-IR-TR/B
400930 | CR | 20191103 |  | 4 | Seal H2O line oon COND-P-2A leaking | N | N |  | N | YES | <D> **** Detailed Description **** Seal H2O line oon COND-P-2A leaking. The flanged connection on outboard side is leaking <I> **** Actions Taken **** Contacted MCR and wrote this CR | 02-00-COND-P-2A
400931 | CR | 20191103 |  | 3 | (Dose) evaluate moving the vent locations for RHR fill veric |  |  |  | N | YES | <D> **** Detailed Description **** For a better dose reduction please evaluate changing the vent valve locations for the RHR fill verification. the system vent location would be the same but piping would be added to run the location of the vent valves to a lower dose area. with the addion of the addition vent locations for these it has lead to a higher dose for these procedures. this would be similiar to where we moved the vent valve from the top of the rhr heat exchanger to the floor level by the door. <I> **** Actions Taken **** wr <N> **** Equipment Description **** various An AR type EVAL is needed for proposed station configuration change(s).
400932 | CR | 20191103 |  | 3 | Whse 5 (bldg 80) RCA boundary is obsecured by boxes. |  |  |  | N | NO | <D> **** Detailed Description **** Whse 5 (bldg 80) RCA boundary is obsecured by boxes. The east side of both RCA boundaries are obsecured such that the RCA postings are not visible. The location of boxes next to the boundary also make it impossible to survey the RCA boundary. Please move boxes and provide means to ensure additional material is not stacked next to the RCA boundary. <I> **** Actions Taken **** Wrote CR and notified HP Supervision. <N> Dispositioned to AR-SCS per request from Facilities
400933 | CR | 20191103 |  | 3 | Dose Saving Idea |  |  |  | N | NO | <D> **** Detailed Description **** With the NRCâ€™s continued emphasis on maintaining our emergency fill systems(ECCS and RCIC) filled and vented we should evaluate installing continuous vents into the system. Small instrument lines that vented the high points continuously back to the suppression pool would alleviate the need to check for voids. This would save immense amounts of dose and time/resources over the remaining life of the plant. <N> An AR type EVAL is needed for the proposed station configuration changes.
400934 | CR | 20191103 | CAQ | D | CVB-V-1CD failed rear disk | Y | N |  | N | YES | <D> **** Detailed Description **** During OSP-CVB/IST-M701 steps 7.1.8l and 7.1.8n for CVB-V -1CD, the red "Full Open" light never illuminated. The lightbulbs were checked to be good. <I> **** Actions Taken **** Informed shift supervision, CRS declared CVB-V-1CD inoperable. Noted condition on the OSP-CVB/IST-M701 | 02-00-CVB-V-1CD
400935 | CR | 20191104 | CAQ | C | ESOMS OSP-INST-H101 function failed | Y | Y |  | N | YES | <D> The ESOMS OSP-INST-H101 function failed. Operator rounds were able to be taken in the field. However, the process to populate and calculate the H101s failed. Paper logs were taken and approved at time 2319. <I> IS was called and informed of the problem. They stated it would take some time to fix. <N> ESOMS program has failed. This issue is preventing all operator rounds from being stamped as reviewed. In addition, the Water Balance calculation is not functioning correctly, giving erroneous values. ... CR at INPROG. Approved CR, moved to SRO for OPS Review.
400939 | CR | 20191104 | CAQ | D | Received Rod Accumulator Trouble for CRD-HCU-1411 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-1411. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-1411 was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear. <I> **** Actions Taken **** Wrote Cr Informed CRS | 02-00-CRD-HCU-1411
400940 | CR | 20191104 |  | 4 | Yakima Cafeteria thermostat broken | N | N |  | N | YES | <D> **** Detailed Description **** The Yakima cafeteria thermostat has been tampered with and destroyed. As a result, what is left of the thermostat is stuck calling for full heat, making the cafeteria and the adjacent areas very uncomfortably warm. Please replace, reset, and lock up the thermostt to relieve this condition. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** Yakima Building cafeteria behind ice maker.
400941 | CR | 20191104 |  | 3 | ASHE Communication Improvement |  |  |  | N | NO | <D> **** Detailed Description **** During the WRA-AC-51 annual maintenance under WO 02122349, 525â€™ Communication Room temperature exceeded 80F. This resulted in causing two MCR annunciators H13-P800.C4.8-6 â€˜BPA-500KV FOTT TROUBLEâ€™ and H13-P800.C4.9-7 â€˜BPA 230KV FOTT TROUBLEâ€™. These annunciators were expected and discussed in the associated impact statements. Additionally, ASHE received an alarm for the communications room high temperature that was not discussed in the work order documents. This was not communicated to ASHE as an expected condition for the work. Recommend updating the model work order, impact statements, and SOP-HVAC/RW -SHUTDOWN to reflect the possible actuation of the ASHE annunciator. This will improve the stations predictability and reliability with ASHE operations. <I> **** Actions Taken **** Submitted CR for corrective actions.
400942 | CR | 20191104 | CAQ | C | (QA) Noncompliance with Legacy Step in SWP-CSW-01 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Organization Vice Presidents have not appointed Software Owners, contrary to SWP-CSW-01 â€œSoftware Quality Assurance Programâ€. The current actual practice of appointing Software Owners is not compliant with this procedure step. Factual Basis: (see EDMS for Details) Insights: â€¢ Lower level procedures are not aligned with SWP-CSW-01 on this legacy requirement, and current practices are following the lower level procedures for appointing Software Owners. â€¢ Currently, both DES-6-3 â€œSoftware Lifecycle Management â€“ Plantâ€ and SWP-CSW-11 â€œSoftware Quality Assurance Process for Non-SSC Softwareâ€ identify the software owner as the department needing the software. â€¢ DES-4-8 â€œMaintenance of Configuration Informationâ€ Attachment 10.5 states, â€œThe software owner is identified in the Asset Suite Work Management D071 - Equipment/Component/UTC Parameters panel via the D030 â€˜Parameters1â€™ button.â€ <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Security. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to ITMGMT.
400943 | CR | 20191104 |  | 3 | MT-DISC-ELEV/1 THRU 4 Not listed in procedures. |  |  |  | N | NO | <D> **** Detailed Description **** MT-DISC-ELEV/1, MT-DISC-ELEV/2, MT-DISC-ELEV/3 & MT-DISC -ELEV/4 are not listed in any procedures, so no restoration positions are available. E-DISC-ELEV/4/LTG is commonly used for lighting in MT-ELEV-4 and is not listed. <I> **** Actions Taken **** Wrote CR. <N> MT-DISC-ELEV/1(2,3,4) are legacy EPNs - BDC 85-0193-0A. EPN E-DISC-ELEV/4/LTG is associated with EC PDC 12277.
400945 | CR | 20191104 |  | 3 | CW-PHITS-1 IMDS needs updated |  |  |  | N | YES | <D> **** Detailed Description **** Circ Water system had halogwenation skid installed that changed the configuration and function of CW-PHITS-1. IMDS was not updated to reflect the changes made to the system. Recommend assign to engineeering for IMDS update <I> **** Actions Taken **** Discussed with manager Wrote CR | 02-00-CW-PHITS-1
400946 | CR | 20191104 |  | 3 | (QA) SWP-CSW-27 cites non-existent Cyber Security Analyst |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) SWP-CSW-27 â€œCyber Security Vulnerability Management and Reportingâ€ states the role of â€œCyber Security Analystâ€ is responsible for the requirements in section 2.3 therein. Having an incorrect non-existent role specified in a procedure can lead to confusion and a loss of productivity. Factual Basis: â€¢ SWP-CSW-27 revision 003, includes responsibilities in section 2.3 for the â€œCyber Security Analyst or Delegate.â€ Insight: â€¢ This is a change management issue because the role of â€œCyber Security Analystâ€ should have been changed to â€œCyber Security Specialistâ€ when ISDI-CYBER-23 â€œCyber Security Training & Communications Planâ€ was created on 2/25/15. <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Security. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to ITMGMT. <N> This is an procedure quality issue that will be addressed by 399487-02. Reccomend Cat 4 to ITMGMT.
400947 | CR | 20191104 |  | 3 | Carpet in poor condition in RWCR | N | N |  | N | NO | <D> **** Detailed Description **** The carpet needs to be replaced in the RWCR. It is torn in some areas, stained in some areas and has tape holding corners down in some spots <I> **** Actions Taken **** Wrote CR and included it on my hoisekeeping report <N> **** Equipment Description **** RWCR
400948 | CR | 20191104 |  | 3 | (QA) GBP-IS-09 Contains Outdated Information |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) GBP-IS-09 â€œCyber Security Programâ€ Rev. 004-000 lists outdated forms. Outdated information in a procedure can lead to confusion and a loss of productivity. Factual Basis: â€¢ On 12/21/17, Forms 27095 & 27096 were placed in â€œHistoryâ€ status. â€¢ On 1/31/19, GBP-IS-09 rev 004-000 was issued with Forms 27095 & 27096 listed on page 9. Insights: â€¢ GBP-IS-09 rev 004-000 resolved AR-CR 386985 by removing several forms. Forms 27095 & 27096 were discovered during an extent of condition by the line, and added to the â€œDescription of Changesâ€ as being removed; however, these two forms were not removed from page 9 prior to issuing the revision. <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Security. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to ITMGMT. <N> Cat 4 ITMGMT. Issue was addressed and corrected in Revision 004 minor 001 issued on 10-30-2019. This revision is linked in document tab.
400949 | CR | 20191104 |  | 4 | All CFDs experiencing fast buildup of diff pressure | N | N |  | N | YES | <D> **** Detailed Description **** All CFDs are experiencing shortened run lenghts due to a faster than normal build up of dP. CR 400825 Hotwell Iron Trend may be related. Other possible cause is an issue with the backwash system. This could cause issue with the upcoming CFD-D septa replacement, scheduled 12/9/19, if the issue is not resolved. <I> **** Actions Taken **** Notified system engineer. | 02-00-COND-DM-1A,02-00-COND-DM-1B,02-00-COND-DM-1C,02-00-COND-DM-1D,02-00-COND-DM-1E,02-00-COND-DM-1F
400950 | CR | 20191104 |  | 4 | TN7 needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Exit turnstile 7 in the PAAP needs maintenance. Contact security at ext. 2185 for further details <I> **** Actions Taken **** Security notification made, CR/WR generated | 02-00-SEC-TN-7
400952 | CR | 20191104 | CAQ | C | 10 CFR 50.46 Notification 2019-05 Bypass Leakage | Y | N |  | N | NO | <D> **** Detailed Description **** GE Hitachi Notification Letter 2019-05 SAFER Lower Limit on Differential Pressure for Bypass Leakage (attached to EDMS) reported an error in an ECCS-LOCA acceptable evaluation model, in accordance with 10 CFR 50.46 (a)(3 )(ii). This error is not significant at 0 degrees-F PCT change but is reportable annually per 50.46. . The error affects GE14 and GNF2 fuel. The design safety function of the fuel is not impacted because peak cladding temperature (PCT) remains well below 2200 degrees-F. An action to update calculation NE-02-03-08 is needed to include GE Hitachi Notification Letter 2019-05 in the next annual report per 10 CFR 50.46.
400953 | CR | 20191104 |  | 3 | EC 16607 drawing incorrect with as found information |  |  |  | N | NO | <D> **** Detailed Description **** CVI Drawing 217-00,84,50 (RX building FP wiring diagram) included with EC 16607 (modification to resolve fire detector accessibility) is incorrect. The changes to Zone 13 detector circuitry include two new detectors (13-20A and 13-21A). However, existing detectors 13-19, 13-20, 13-21 and 13-22 will be removed and re-installed to accomodate the modification to the circuit. The drawing shows the terminal points for the existing detectors as changing to the new detector type. The drawing should show these detectors with the original terminal points. This has also been verified in the field. <I> **** Actions Taken **** Discussed with Engineering and wrote CR Will obtain red-line drawing of existing detector circuitry (for affected Zone 13 detectors) and furnish to Engineering to update drawing. <N> The associated Cable Termination Instruction (CTI) sheets will be updated with the corrected drawing information. Rev 2 of the EC will be updated to reflect the change to the drawing.
400955 | CR | 20191104 |  | 3 | Operations Department exceeded October dose goal. |  |  |  | N | NO | <D> **** Detailed Description **** In October, the Operations department received 409 mrem against a gola of 235 mrem. Baseline dose was 181 mrem, scheduled dose was 58 mrem, and unscheduled dose was 16 mrem. Per reported dose to the SSS, emergent dose was 23 mrem, unplanned dose (EDR, FDR, FPC demin bw/pc) was 21 mrem, and FIN received no dose. The RHR-B maintenance outage was projected for 57 mrem, which Operations received 115 mrem. With emergent dose deducted from the total received dose, Operations received 386 mrem, 151 mrem over the month goal. This CR is for trending purposes only. <I> **** Actions Taken **** The Operations Dose Champion will continue to work with ALARA Planning and Chemistry to ensure that FDR and RWCU demineralizer bw/pc activities are budgeted; Will work with ALARA Planning to get EDR and FDR demineralizer bw/pc budgeted into the baseline dose based on current trend. <N> The Operations Dose Champion continuously works with ALARA Planning to improve the identification of tasks which receive dose and to provide feedback from the operating crews.
400957 | CR | 20191104 |  | 4 | Chemistry Dose Budget exceeded for October 2019 |  |  |  | N | NO | <D> **** Detailed Description **** The Chemistry dose budget was exceeded for October 2019. The dose estimate was 193 mR with a goal of 174 mR. The Chemistry department received 188 mR. The extra dose is directly related to emergent work for flow adjustment on PSR-SR-49. The emergent work was planned for 30 mR and completed for 10 mR. This was good performance by the technician performing the work.
400958 | CR | 20191104 |  | 3 | PPM 10.4.4 Revision Request |  |  |  | N | NO | <D> **** Detailed Description **** Update PPM 10.4.4 â€œMobile Crane Operation, Inspection, Testing and Maintenanceâ€, sections 4.8 and 7.9 to document engineering evaluations for use of SPYDER-CRANE-1 inside the CGS Reactor Building. Add a caution statement to the procedure on ventilation requirements if/when the internal combustion engine is used inside enclosed areas due to the carbon monoxide exhaust hazard. The crane was recently used to remove a Control Rod Drive Pump from the Reactor Building 422 elevation. <I> **** Actions Taken **** Contacted the CGS Site Rigging Coordinator who advised me why SPYDER-CRANE-1 is currently located inside the CGS Reactor Building crane bay. UNIC w295CMRS Spyder Crane information is included in EDMS. EC EVAL 10525 R0 provides a specific engineering evaluation for use of the Spyder Crane at R441' truck/rail bay hatch A-2 (MT-DOOR-A2) to lift CRD-M-P/1A(B) and CRD-P-1A(B). The Spyder Crane is not generically evaluated - must be evaluated on a case-by-case basis. EC EVAL 10350 evaluated use of the Spyder Crane on T441' in support of the R20 Condenser Replacement Project. <N> **** Equipment Description **** Mobile Crane - See EC Evaluation 10525 for use in the R441â€™ truck bay at hatch A-2 to lift CRD-M-P/1A(B) and CRD-P-1 A(B), See EC Evaluation 10350 for the use in Turbine Generator Building EL. 441â€™ in support of the Condenser Replacement Project during Refueling Outage R20.
400960 | CR | 20191104 |  | 3 | During data center / collocation review discrepancies noted |  |  |  | N | NO | <D> **** Detailed Description **** During data center / collocation review discrepancies were noted; process will be revised and placed into an electronic work flow. <I> **** Actions Taken **** Notified supervision, created CR to document, recommend NON-CAQ 3 to ITMGMT.
400961 | CR | 20191104 |  | 3 | SPES-1.6.17 should be revised |  |  |  | N | NO | <D> **** Detailed Description **** Instructions for creating procurement specification deviation (PSD) does not provide adequate guidance to inform/communicate with SCS when a new PSD is created to ensure active Purchase Orders (PO) are updated to incorporate the new PSD requirements. Example: EC 17682 was created for PSD-17682 in May 2019 against Procurement Specification 12505 â€œProcurement Specification for Reactor Water Cleanup Heat Exchangersâ€, the requirement of the new PSD was not communicated with SCS and a purchase order is in progress for this procurement. Once found out (at end of October 2019) SCS revised the PO include these requirement. In this case the vendor was fully aware of the new requirements but this is an error likely situation. Specification for Reactor Water Cleanup Heat Exchangersâ€, procurement. Once found out (at end of October 2019) SCS <I> **** Actions Taken **** Discussed with Procurement Engineering and SCS. Recommend assigning to Procurement Engineering (Owner of this procedure) to add a step in this procedure to inform Supply Chain Services when a PSD is generated to incorporate deviations in Purchase orders that in progress. Recommend assigning to Procurement Engineering (Owner of this procedure) to add a step in this procedure to inform Supply Chain Services when a PSD is generated to incorporate deviations in Purchase orders that in progress.
400963 | CR | 20191104 |  | 3 | main gear oil in limit switch enclosure of TMU-MO-1B | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** during the performance of PPM 10.25.222 (WO# 02117297-01), step 7.2.15.f.(2), electricians noted about 20mL of MobilGear 600 XP68 in the limit switch enclosure. The procedure says "if oil is present, Then determine the origin and document in the comments section of attachment 9.1". This CR is for trending. Valves, it is difficult to determine the actual origin of <I> **** Actions Taken **** Notified engineer and Write CR. <N> **** Equipment Description **** TMU-MO-1B TMU pumphouse
400965 | CR | 20191104 |  | 3 | Cold Shutdown Boron Weight in PPM 5.1.2 |  |  |  | N | NO | <D> **** Detailed Description **** The RPV Control â€“ ATWS Emergency Operating Procedure (PPM 5.1.2) Table 10 references only the change in SLC-TK-1 level as the means for calculating the minimum amount of boron required to inject into the reactor vessel to ensure a cold shutdown. This is also true of the Flowchart Training Manual (PPM 5.0.10) Step 5.5.4.f. This minimum amount, however, can also be calculated using the SLC flow into the reactor (SLC-FI-1) over time. This alternate method should also be included in both PPM 5.0.10 and 5.1.2 which would allow more flexibility in determining if the Cold Shutdown Boron Weight requirement is met â€“ especially if the SLC boron tank level indication becomes unreliable.
400966 | CR | 20191104 |  | 4 | COND-CP-DM/1 drop 2-6 is partially lighted | N | N |  | N | YES | <D> **** Detailed Description **** COND-CP-DM/1 drop 2-6 (CND-DM-1F vessel 1 F High D/P) is partially lighted. the Light will get brighter when all lights are tested but still has a low glow when the alarm is reset. <I> **** Actions Taken **** wr | 02-00-COND-CP-DM/1
400969 | CR | 20191104 |  | 3 | R25 procedure change SOP-ELEC-SM7-MAINT |  |  |  | N | NO | <D> **** Detailed Description **** Step 5.1.11.d to sample TEA per ODCM and LCS is not required. EC 4789 removed old TEA sample rack 26,26A, and 38. These use to be fed from E-PP-7FAB CK 2. The new system TEA-SR-26 and TEA-M-FN/93 is fed from E-MC-5D/13BR and 13BL. Delete step and ensure SOP-ELEC-SH-5-MAINT contains a step to sample TEA per ODCM and LCS. Remove step 5.1.12 REA being OOS and Chemistry to take comp measures. The new stack monitor sample pump and trace heat is powered from E-PP-8FB. <I> **** Actions Taken **** wrote CR
400970 | CR | 20191104 |  | 3 | Procedure enhancement for ISP-HPCS-X302 |  |  |  | N | NO | <D> ISP-HPCS-X302 caution before step 7.1.3 on page 8 says making HPCS unavailable will put us in paragon orange. 1.5.14 changed and this is not the case anymore. <I> Wrote CR <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
400971 | CR | 20191104 |  | 4 | RW 437- Evidence of Floor Drains Over Flowing | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Prior to entering behind the shield wall to continue work on EDR-P-11, it was noted on the camera view that there was an orange rusty ring on the floor around two of the floor drains. <I> **** Actions Taken **** Informed the HP Technician that was going to be entering the room and advised him to survey the areas so we could assess the situation prior to allowing work to commence in the area. The contamination survey revealed the area to be above 100,000 dpm/100cm2 beta-gamma, as per PPM 11.2.7.1 the area would be deemed a High Contamination Area, the area is currently posted as such so a posting change was not needed. Spoke with the Rad Waste EO about the issue and the electricians that had entered to relamp the area a week ago. The rusty rings seem to have been there for some time and only because the lighting is so much better now that they became visible on the view of the camera. See pictures in EDMS. Recommend this go to trending.
400972 | CR | 20191104 |  | 3 | 2019 Mid-Cycle Assessment- LF.1 Open and Off track |  |  |  | N | NO | <D> **** Detailed Description **** Overall, the assessment teamâ€™s review of the associated 2018 WANO LF .1 (Leadership Fundamentals) AFI corrective actions aligned with the AFI closure effectiveness review which identified this AFI to be Open and Off-track. . <I> **** Actions Taken **** Informed station leadership team an initiated this CR. This CR and any associated actions should be tracked under the original AR for LF .1 which is AR 385691
400973 | CR | 20191104 | CAQ | C | Editorial procedure change required for OSP-LPCS/IST-Q702 |  |  |  | N | NO | <C> MRT Change: CR 400973 moved from NON-CAQ Severity 3 to CAQ Severity C. The Changes are to Surveillance parameter. <D> **** Detailed Description **** Step 7.3.58.2.c incorrectly references a 0-300 instead of 0-500 gage. This step only effect the performance of the CPT(2 yr PM) and should be reviesed during the next 2 year procedure reveiw. <I> **** Actions Taken **** Wrote CR.
400974 | CR | 20191104 |  | 3 | 2019 Mid-Cycle Assessment- 0F.2 Open and Off track |  |  |  | N | NO | <D> **** Detailed Description **** Overall, the assessment teamâ€™s review of the associated 2018 WANO OF.2 AFI corrective actions found that actions were put in place following the AFI, however, the AFI was closed and the effectiveness review determined this AFI was closed with no further actions. The assessment team identified the risk mitigation piece of the AFI was not satisfactorily addressed. The station has the potential to have continued risk mitigation issues unless additional actions are taken to close this gap. <I> **** Actions Taken **** Informed station leadership team an initiated this CR. This CR and any associated actions should be tracked under the original AR for OF.2 which is AR 385687.
400976 | CR | 20191104 |  | 3 | 2019 Mid-Cycle Assessment- IS.1 Open and Off track |  |  |  | N | NO | <D> **** Detailed Description **** Overall, the assessment teamâ€™s review of the associated 2018 WANO IS.1 (Industrial Safety) AFI corrective actions found there have been some improvements since this Industrial Safety AFI was issued including: â€¢ There have been multiple examples of workers stopping work rather than working through uncertainty â€¢ Establishment of Safety First as a station focus area â€¢ The Daily 15 (D-15) has been rearranged to present safety as the first topic of discussion. â€¢ It is also noted very recent efforts to address some safety deficiencies like safety showers and inadequate lighting as just been initiated. However, overall, the industrial safety performance is not acceptable. Personnel sometimes do not recognize risk and sometimes risk decisions are made at an inappropriate level. The station has recorded five OSHA recordable injuries and one lost time injury in 2019. There have recent examples where the lack of risk recognition have led to or could have resulted in injuries <I> **** Actions Taken **** Informed station leadership team an initiated this CR. This CR and any associated actions should be tracked under the original AR for IS.1 which is AR 385690.
400977 | CR | 20191104 |  | 3 | 2019 Mid-Cycle Assessment- ER.1 Open and Off track |  |  |  | N | NO | <D> **** Detailed Description **** The assessment teamâ€™s review identified actions taken in response to the 2018 WANO Peer Review Equipment Reliability AFI have been predominantly focused on engineering performance. Progress in changing needed behaviors to support equipment reliability within key support groups at Columbia has been inconsistent, resulting in additional equipment reliability challenges. Response to this AFI included dependence on the actions taken in response to AFI OF.2 and LF.1, which have not been fully effective. Therefore, there is a direct impact to successful completion of actions to address this AFI <I> **** Actions Taken **** Informed station leadership team an initiated this CR. This CR and any associated actions should be tracked under the original AR for ER.1 which is AR 385689.
400978 | CR | 20191104 |  | 3 | 2019 Mid-Cycle Assessment- Objective 5 Not Met |  |  |  | N | NO | <D> **** Detailed Description **** As part of the 2019 Mid-Cycle Assessment the team was tasked with assessing several objectives. Objective 5 stated the following: Determine if station personnel are appropriately challenging of activities. Verification methods included: â€¢ Perform field observations â€¢ Observe pre-job briefings/D-15s, key station meetings â€¢ Documentation reviews/meeting notes The team concluded this objective was not met. Based on a review of mid-cycle assessment team observations, results found that while positive behaviors are being demonstrated in the field and at meetings, overall, the leadership team is not consistently demonstrating the expected level of engagement (challenge) that is needed to drive continuous improvement at the station. Many of the observations document a level of engagement that is not occurring at the appropriate levels and at times, not being coached by other attendees. <I> **** Actions Taken **** Informed station leadership team an initiated this CR. This CR and any associated actions should be tracked under the original AR for LF.1 which is AR 385691.
400981 | CR | 20191104 |  | 3 | Multiple drawings need update due to WR29152261 |  |  |  | N | YES | <D> **** Detailed Description **** E526-1A, E536-6A, and EWD-45E-027 will need to be updated due to the spare BMISC-11 BK-2 and WH-2 now being used. <I> **** Actions Taken **** WR29152261 <N> CTI from WR 29152261 is attached to the EDMS Doc button for this AR. | 02-00-SCI-MUX-IMET/1,02-00-SCI-MUX-OMET/1
400982 | CR | 20191104 |  | 3 | Letter delivered to Post Office without postage and returned |  |  |  | N | NO | <D> **** Detailed Description **** Letter was picked up from the MPF as part of normal mail route. Letter did not have postage applied when picked up, was processed through post office and returned to Energy Northwest. EN mail staff carry stamps during mail route to ensure that all letters get stamped. <I> **** Actions Taken **** Contacted orginal sender to determine if there was any time constraints to consider when mailing again. Repackaged letter in new envelope and mailed next day. Coached staff. Wrote CR. <N> This was discussed at D15 and staff were reminded to validate postage has been applied. No further action is required.
400984 | CR | 20191104 |  | 3 | (NRC) 2019 Chem-Rad â€“ Walkdown comments |  |  |  | N | NO | <D> **** Detailed Description **** While doing a walkdown a NRC inspector noted the following: At 467 RW HP Instrument Storage Room, the metal storage cabinet for Ludlum Model 177 survey meter storage has a hole cut for AC power cord to pass through. The hole does not have any type of protective grommet or covering on the metal edges to protect cords from scuffing or cutting. Creating a potential electrical shock hazard if the power cord is cut. <I> **** Actions Taken **** Contacted RP Supervision and discussed. Notified Chem/RP Analyst for tracking.
400985 | CR | 20191104 |  | 3 | MD-V-87 remaining open may be impacting hotwell iron levels | N | N |  | N | YES | <D> **** Detailed Description **** Based on data from Operations, Chemistry, EFIN and others, MD-V-87 remaining open may be impacting hotwell iron levels and CFD run times. AR 398564 ODMI and OCC documents need to be revised to allow for closure of MD-V-87 since opening of the valve has not made a significant impact on HP turbine casing differential temperatures. Closing MD-V-87 would also gain ~1.3 MWe. Also, revison of EC 17964 will be needed to close MD-V-87 and still maintain the turbine drain valves closed via installed jumper. <I> **** Actions Taken **** Discussed CFD and hotwell iron trends with EFIN, Ops, Chemistry and system engineer. Discussed MD-V-87 closure with Turbine Engineer and BOP Supervisor. <N> **** Equipment Description **** T -476- - -C0/7.9 - | 02-00-MD-V-87
400987 | CR | 20191104 |  | 3 | (NRC) 2019 Chem-Rad â€“ Walkdown comments |  |  |  | N | NO | <D> **** Detailed Description **** While doing a walkdown an NRC inspector noted the following: At ARM-RIS-27, Rad Waste 437 Tank 5 Area has a ladder storage location directly below the ARM - Ladder Storage # 14.1. The meter to detector cables are in very close proximity and in some instances touching the ladder. There is a risk that the ladder could come in contact with the detector or meter, or become tangled with the cables when the ladder is removed from, or retuned to, storage rack. Should evaluate this ladder storage and also look at other ARM locations for similar conditions. <I> **** Actions Taken **** Contacted RP Supervision and discussed. Contacted Chem/RP Analyst for assignment, tracking, and trendiing. <N> A second walkdown on 11/6/2019 in 467 RW B Valve Gallery also noted a ladder stored below ARM-RE-21 (Note this area is not a numbered permanent ladder storage location.)
400989 | CR | 20191104 | CAQ | C | OG-RIS-601B Possible Sticking Button | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02135943-01, the SELECT button was depressed, and screen began to advance automatically several pages, then stopped. <I> **** Actions Taken **** Informed Supervision and Operations. Buttons would not respond for a few minutes, then responded. Per Supervision, contiinued and completed WO satisfactory.
400994 | CR | 20191104 |  | 4 | SO-P-H2S Hydrogen Seal Oil Pump leaking oil | N | N |  | N | YES | <D> **** Detailed Description **** SO-P-H2S (hydrogen side seal oil pump) has begun leaking about one drop of oil every 3-4 seconds. This ends up forming a large puddle of oil. Please investigate and repair. <I> **** Actions Taken **** Notified SMgt, wrote CR. <N> **** Equipment Description **** TB 441 W Seal Oil Room. | 02-00-SO-P-H2S
400995 | CR | 20191104 |  | 3 | Inaccurate signage entering RCA |  |  |  | N | NO | <D> **** Detailed Description **** Signage at the RCA entrance states â€œNote â€“ cellular phones are not allowed in the RCA.â€ This is old information that is no longer accurate. PPM 1.3.72 has been revised to allow cell phones in the power block while in airplane mode. Recommend replacing signage. Recommend replacing verbiage to read â€œWireless transmitting devices such as cellular phones are controlled per PPM 1.3.72. If you bring a wireless transmitting device into the RCA ensure you comply with PPM 1.3.72â€ <I> **** Actions Taken **** Initiated CR
400996 | CR | 20191104 | CAQ | D | Received Rod Accumulator Trouble for CRD-HCU-4247 | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-4247. Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-4247 was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear. <I> **** Actions Taken **** Wrote CR | 02-00-CRD-HCU-4247
400997 | CR | 20191104 | CAQ | C | Lack of verification and validation during design reviews |  |  |  | N | NO | <C> MRT Change: CR 400997 moved from NON-CAQ Severity 3 to CAQ Severity C. Some reviews are conducted on CAQ designs <D> **** Detailed Description **** The Self-Assessment performed in AR 399414 (uploaded to EDMS folder for the self-assessment AR) identified a deficiency as a contributor to the number of Field Change Requests related to ECs. Design Changes are being issued with detail errors that should have been caught during the verification/validation process of the detailed design review and design change development. . There are no equipment or component issues with the plant. <I> **** Actions Taken **** Identified deficiencies were discussed with the DE Manager as part of the Self-Assessment AR/SA 399414. AR initiated to track evaluation of deficiency and implementation of resulting corrective actions.
400999 | CR | 20191105 |  | 3 | CRO1 tablet fail to syncronize again. |  |  |  | N | NO | <D> **** Detailed Description **** The CRO1 tablet is failing to synchronize again. This problem continues to occur on a relatively frequent, intermittent basis. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR.
401000 | CR | 20191105 |  | 4 | CWPH electrical building doors are in need of replacement. | N | N |  | N | YES | <D> **** Detailed Description **** WPH electrical building doors are in need of replacement. The back double doors are difficult to open and have large spots where they have rusted thru. the front doors are difficult to operate due to binding. please evaluate repairing or replacing doors. <I> **** Actions Taken **** wr <N> **** Equipment Description **** CW area
401003 | CR | 20191105 |  | 3 | (NRC) 2019 Chem-Rad - Walkdown comments |  |  |  | N | NO | <D> **** Detailed Description **** While doing a plant walkdown 11/4/2019 an NRC inspector noted the following: The External Alarm Modules (EAM) for the AMP Survey Meter portable ARM attachment have identification numbers for the purpose of tracking. These numbers are nearly identical to the installed plant ARM-RIS numbers (i.e., 1, 2, 3, etc.) and this could cause confusion and lead to association with the installed equipment. In some instances the EAM may be temporarily installed in the plant ARMs, such as for compensatory measures. These EAMs should have separate numbering and identification. <I> **** Actions Taken **** Contacted RP Supervision and discussed. Notified Chem/RP Analyst for tracking.
401004 | CR | 20191105 |  | 3 | 5.5.25 change requested |  |  |  | N | NO | <D> **** Detailed Description **** PPM 5.5.25, Alternate Injection Using the SLC System, is directed from PPM's 5.1.1, 5.1.2, 5.1.4, 5.1.6, 5.1.8, and SAG-1 as an alternate RPV injection system. However, if this high pressure, low volume injection system was needed to assist in maintaining RPV level, it is possible that power is not available to the Demineralized Water pumps which 5.5.25 directs as the makeup source to the boron or test tank. Recommend adding the option to re-fill the tanks with FP water from adjacent hose stations if needed to ensure adequate core cooling and demineralized water is unavailable due to a loss of E-TR-S powering E-MC-1C and E-MC 5BA. Note also that PPM 5.0.10, 9.0, EOP Support Procedure to EOP Flowchart Cross-Reference, should be updated to reflect that PPM 5.1.8 directs PPM 5.5.25. <I> **** Actions Taken **** We coach CROs in the simulator, that when they direct the field actions of PPM 5.5.25, if E-TR-S is unavailable, there is no water available for the operator to perform the actions. It is not desired to inject FP water into the core unless absolutely necessary, but making this change will allow SLC injection to continue when the tank is empty utilizing Fire Protection if required.
401005 | CR | 20191105 | CAQ | D | HPCS-RLY-51V/B right flag was dropped | Y | N |  | N | YES | <D> **** Detailed Description **** HPCS-RLY-51V/B right flag was dropped. contacted MCR and reset the flag. recommend trend only.pic attached <I> **** Actions Taken **** cr | 02-00-HPCS-RLY-51V/B
401006 | CR | 20191105 |  |  | SPWH-HX-1 manway gasket enhancement. |  |  |  | N | YES | <D> **** Detailed Description **** While performing biennial inspection on SPWH-HX-1, it was noted that the Garlock 9900 gasket material (CID 8235) used to seal the manway to the vessel leaks during fill and flush activity required by the work order. The fill and flush evolution exposes the new gasket to a lower pressure and temperature than in-service and the gasket tends to â€˜weepâ€™ under these conditions. After the vessel has heated up and pressure increases the leak stops. Also, there is a brazed connection between the draw up bolt and the manway that should not have excess force applied to get a leak to stop. This joint would benefit from a more resilient material (rubber) than the Garlock 9900 for future installation. Recommend evaluation to determine if a different material can be used. <I> **** Actions Taken **** Wrote CR <N> **** Equipment Description **** S -420- - -H0/3.6 - | 02-00-SPWH-HX-1
401008 | CR | 20191105 | CAQ | C | OSP-SW-/IST-Q701 year VPI scheduled to go late. PMID 0001695 | Y | N |  | N | NO | <C> MRT Change: CR 401008 moved from NON-CAQ Severity 3 to CAQ Severity C. Scheduled tech spec surveillance date challenged <D> **** Detailed Description **** When AR 386484 was implemented to split the CPT and VPI into 2 PMIDs the PMID 16954-01 for the 2 year VPI incorrectly credited completion of the Nov 2018 OSP -SW/IST-Q701, where the VPI were not performed. The 2 year VPI were last performed Nov 7, 2017 and goes Tech Spec late May 8th, 2020. The PMID late date is Nov 2020. Recommend scheduling PMID 00016954-01 to be performed during the next, February, performance of OSP-SW/IST-Q701. <N> WO 02153474 has been rescheduled to 2/4/2020 and tied to Quaterly surveillance 02136601. Verified that the PMID will auto generate at correct interval. C. Nordhaus, 12/5/19.
401011 | CR | 20191105 |  | 4 | GEM-5 at PAAP out of service due to HV fault | N | N |  | N | YES | <D> **** Detailed Description **** The Security PAAP GEM-5 HP-EQ-42738 is Out of Service due to HV Out of range / low counts fault. Appears to be foot detector # 1. Currently is tagged OOS. <I> **** Actions Taken **** Contact RP supervision. Initiated WR Notified FIN I&C and discussed possible causes. Contacted manufacturer (Mirion -Canberra) Technical Rep | 02-00-HP-EQ-42738
401013 | CR | 20191105 | CAQ | D | Documented torque values are less than vendor CVI table. | Y | Y |  | N | YES | <D> **** Detailed Description **** During supervisor review of work order 02079198-01 it was noticed that the documented torque values for the overload block and auxillary contact block appear to be lower than recommended in CVI-999-00,174,1 for a #8 screw in Spectrum buckets. Recommend we validate torque values applied, are in accordance with the vendor CVI table. <I> **** Actions Taken **** Wrote this AR, and contacted the Shift Manager. <N> **** Equipment Description **** RX 522, MC8B room. | 02-00-CRA-42-8B6B
401014 | CR | 20191105 |  | 4 | Circ Water Pump House Flooding | N | N |  | N | NO | <D> **** Detailed Description **** November 1st at 0951 the chemistry sample room in the circ water pump house began flooding. This continued until 1007 when the water began draining. <I> **** Actions Taken **** CR initiated <N> **** Equipment Description **** Circ Water Pump house Chemistry Sample room
401015 | CR | 20191105 |  | 4 | (QA) 5 of 5 Recent CATIDs Missing Required CDA Clause |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) 5 of 5 sampled Catalog IDs (CATIDs) for Critical Digital Assets (CDAs) do not have a CDA clause code on D205 panel in Asset Suite, contrary to SWP-CSW-24 â€œCyber Security Procurementâ€. The potential consequence is that Cyber Security may not be involved before installation for Cyber acceptance testing of the device without the CDA Clause, but there are no known actual consequences. Factual Basis: â€¢ SWP-CSW-24, section 3.1 requires the CDA clause to be present in order to properly implement cyber security acceptance testing requirements for the component. â€¢ These CATIDs do not have required CDA clause code on D205 panel: 37313 (for SEIS-SMA-2A), 30183 (SEIS-KVM-1), 20661 (PDIS-CPU-DATA1), 28863 (HT-TIS-PRM/B1), & 34283 (SW-PIC -15A). Insights: â€¢ Some CDAs were implemented prior to SWP-CSW-24, rev 0 (12/28/15), which initially implemented the requirement; however, these CDAs CATIDs were not later updated with the CDA clause to ensure consistent application. An extent of condition is warranted to ensure CDA CATIDs are properly coded. <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Security. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to ITMGMT. <N> Reccomend CAT 4 to ITMGMT The cause is known as this was an error in which cyber did not provide sufficient guidance for establishing the responsibility to correctly link CATIDs to CDAs. Consequence is low. This issue will be addressed under CR 399488 assignment 02.
401016 | CR | 20191105 | CAQ | D | (QA) ISDI-CYBER-13 Wrongly Cites CS-01 for Cyber Level |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) ISDI-CYBER-13 â€œCyber Security Defensive Architectureâ€ incorrectly states Cyber levels are identified in CS-01 â€œCritical Systems Listâ€, which does not include Cyber levels. Instead, CDA-01 â€œCritical Digital Asset Listâ€ is the document that identifies Cyber levels. Factual Basis: â€¢ ISDI-CYBER-13 step 3.4.1 states, â€œThe Critical Systems (and their corresponding cyber level) are identified in CS-01.â€ However, this is incorrect. Cyber levels are identified within CDA-01 instead. â€¢ Defensive level determinations are documented in Form 26997 â€œCritical Digital Asset Revisionâ€, which is used to update CDA-01. â€¢ After notification by Quality, the Cyber group fixed this in ISDI-CYBER-13 rev 001-002 on 10/23/19. <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Security. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to ITMGMT. <N> Reccomend Cat 4 to ITMGMT The cause is known as this was an error in which cyber pointed to the wrong document. Consequence is low. This issue was corrected in ISDI-CYBER-13 Revision 001 Minor 002.
401017 | CR | 20191105 |  | 3 | (QA) Noncompliance with Update Required by ISDI-CYBER-28 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) ISDI-CYBER-28 â€œCDA Backup Programâ€ was not updated annually, contrary to a requirement in section 2.1.3 therein. This is a procedure use and adherence issue with no known consequence. Factual Basis: â€¢ ISDI-CYBER-28 revision 000, section 2.1.3 states that the Cyber Security Program Manager â€œEnsures this procedure is updated annuallyâ€. â€¢ ISDI-CYBER-28 revision 000 was issued 12/20/2017; however, there was no update in 2018, and a minor revision (000-001) was issued on 08/06/2019, which exceeds the duration of the annual requirement. Insights: â€¢ The update requirement for ISDI-CYBER-28 is not a scheduled action within the organization. â€¢ There is no known regulatory requirement to update ISDI -CYBER-28 annually. <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Security. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to ITMGMT. <N> Reccomend Cat 3 to ITMGMT The cause is known as this was error in meeting the procedure guidance. Consequence is low. There is not a regulatory commitment to update the document annually. Benchmarking will be done to ensure industry alignment and the document will be updated.
401018 | CR | 20191105 |  | 4 | COND-HX-8B Incorrect Title in Asset Suite |  |  |  | N | YES | <C> MRT Change: CR 401018 moved from CAQ Severity D/Trend Repair to NON-CAQ Severity 4/Trend Repair. Enhancement only. <D> **** Detailed Description **** The name for COND-HX-8B on the D030 panel in asset suite incorrectly says "SJAE CONDENSER HEAT EXCHANGER A" when it should read "SJAE CONDENSER HEAT EXCHANGER B". <I> The name description in Portal J for COND-HX-8B has been corrected to "SJAE CONDENSER HEAT EXCHANGER B". no further actions are required. <N> **** Equipment Description **** T -445- - -F8/12.5- | 02-00-COND-HX-8B
401019 | CR | 20191105 |  | 4 | Water Pooling outside Chemistry breakroom | N | N |  | N | YES | <D> **** Detailed Description **** Water is pooling outside the chemistry break room on the 487' RW building under WOA-FN-5. This water is also working its way under the wall of the chemistry breakroom and collecting inside. This is causing damage to the walls and floor. <I> **** Actions Taken **** CR initiated <N> **** Equipment Description **** WOA-FN-5 Same issue as AR CR 401041 / WR 29152530 (WCH-V-614 Pipe Cap is leaking at a rate of 1 dpm)? | 02-00-WOA-FN-5
401021 | CR | 20191105 |  | 4 | eDNA Trend not working for ASD | N | N |  | N | YES | <D> **** Detailed Description **** There is no data available for glycol resistivity and temperature From eDNA Trend. eDNAtrend points affected are ENWBU.MODBUSLS ASD001,ASD002,ASD003,ASD004,ASD005,ASD006 ,ASD007,ASD008. RRC-IMD-ASD1A/1,1A/2,1B1,1B2. Recommend Computer Engineering take action . <I> **** Actions Taken **** Wrote CR,Notified Supervisor and Control room supervisor. | 02-00-RRC-IMD-ASD1A/1,02-00-RRC-IMD-ASD1A/2,02-00-RRC-IMD-ASD1B/1,02-00-RRC-IMD-ASD1B/2
401022 | CR | 20191105 |  | 4 | D104 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** D104 door knob (non-security component) is not functioning as designed and requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Initiate CR/WR. Security Supervision notified. | 02-00-D-DOOR-D104
401024 | CR | 20191105 |  | 3 | Part lead times do not correspond with our T week process |  |  |  | N | NO | <D> **** Detailed Description **** On multiple occasions we have encountered trouble with parts acquisition for the emergency diesels DG-1, DG-2, and DG-3. This is a repeatable problem with some of the lead times being as long as 26-50 weeks out on some parts. Our scheduling process does not order parts till T-14 and as the math shows, this is not enough time to receive the parts needed for the safety system window. This is a strain on resources and has a cost associated with expediting these parts to meet our maintenance window. Recommend evaluating upcoming parts needed and changing the min-max to align with the upcoming maintenance windows. Also develop a plan to accommodate for early purchases for known maintenance so we do not impact the procurement resources during implementation. <I> **** Actions Taken **** Notified work week manager and system engineering, initiated this condition report
401025 | CR | 20191105 |  | 3 | Potable Water Quality Assurance proceedure 12.1.2 |  |  |  | N | NO | <D> **** Detailed Description **** In proceedure 12.1.2 section 6.1.2 concerning raw water coliform sampling line B says TMU sample may be taked at "PWC-V-462 or similar". PWC-V-462 is the main floculator drain valve and not able to be sampled from. Typically our TMU samples are collected from PWC-V-748. An update should be made to the proceedure in order to clarify the correct sample point(s) to be used. <I> **** Actions Taken **** Specialist notified and CR written.
401027 | CR | 20191105 |  | 4 | WRA-PCV valve inspections could not be performed |  |  |  | N | YES | <D> **** Detailed Description **** When attempting to perform internal license renewal valve inspections it was determined that removal of the valves required significantly more work than was originally scoped. The AC units will have to be evacuated and piping removed along with hangers in order to get the valves removed. Additionally given the size it is recommended that the examination be destructive which would require replacement. This was all identified when the work was started. This work will need to be rescoped for a future WRA-AC-51 maintenance window. <I> **** Actions Taken **** Cancelled tasks 9 and 10 on WO 02122349. Generated this CR and WR's to bundle with annual PM for chiller maintenance. Notified planning supervisor, mechanical supervisor, license renewal project manager | 02-00-WRA-PCV-51A,02-00-WRA-PCV-51B
401029 | CR | 20191105 |  | 4 | E-CB-TR72 BREAKER INSPECTION PER 10.25.13 | N | N |  | N | NO | <D> **** Detailed Description **** WHILE PERFORMING INSPECTION PER 10.25.13 STEP 7.8.3 CRAFT FOUND MISSING COTTER PIN ON CLOSED LEVER ARM LINK. <I> **** Actions Taken **** NOTIFIED SUPERVISOR AND REPLACED MISSING COTTER PIN. THE AS LEFT REPLACEMENT DOES NOT COMPROMISE THE OPERATION OF THE BREAKER.
401032 | CR | 20191105 |  | 4 | HCO-T-W55 is shooting steam and moisture out of the top. | N | N |  | N | YES | <D> **** Detailed Description **** HCO-T-W55 is shooting steam and moisture out of the top. It appears to be coming out of a machined orifice on top of the steam trap. Unable to isolate at this time due to location of HS-V-W55 ( steam supply) . <I> **** Actions Taken **** wr/cr | 02-00-HCO-T-W55
401033 | CR | 20191105 |  | 3 | WO# 02130440-01 and 03 needs rewritten. |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** WO# 02130400-01 and 03, which was scheduled to start on 11/04/19, needs to be rewritten to perform testing that is required for the new CTMA switches ( CTMA-DPS-1/1 and 2/1 ) <I> **** Actions Taken **** Contacted Supervisor.
401034 | CR | 20191105 |  | 3 | Model Work Order 02136200 Update |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of OSP-SW/IST-Q701 under WO 02136628-01, the expected control room log entries were not made. Additionally, the WO did not go to H/OPS following completion. This task was generated from model WO 02136200, which is new and this is the first accomplishment of the task. The model WO needs to be updated to cause the task to route to H/OPS and generate the correct control room log entries. <N> Model WO 01133019 and all outstanding (active) work orders) upfated/ verified flagged with H/OPS and surveillance type SV, control room comm set to 2. All future work orders for PMRQ 00016954-03 will go to H/OPS and make l;og entries in ESOMS. No additional actons required.
401035 | CR | 20191105 |  | 4 | HCO-T-W55 has pinhole steam leak | N | N |  | N | YES | <D> **** Detailed Description **** While performing a system walk-down on Radwaste Building 487â€™, a 5ft steam plume was observed from (NSR) steam trap (HCO-T-W55), which services the Hot Instrument Shop Humidifier (WOA-HU-5). Water is collecting on the floor and causing water damage to the Hot Instrument Shop walls. This issue/equipment is not Technical Specification, LCS, ODCM, Safety Related, or Augmented Quality System, Structure, or Component (SSC) related. <I> **** Actions Taken **** Called SSS, and informed supervisor. Initiated Work Request to have catch basin installed and leak repaired. | 02-00-HCO-T-W55
401036 | CR | 20191105 |  | 4 | HT-HTP-FP/23 circuit 19 F No continuity | N | N |  | N | YES | <D> **** Detailed Description **** HT-HTP-FP/23 circuit 19 F has No continuity light flashing and a new light bulb in the power socket won't light. | 02-00-HT-HTP-FP/23
401037 | CR | 20191105 | CAQ | D | (QA) SWP-CSW-27 is not in alignment with SWP-SEC-11 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) SWP-CSW-27, â€œCyber Security Vulnerability Management and Reportingâ€ does not include instructions to comply with SWP-SEC-11, â€œProtection of Sensitive But Unclassified Informationâ€ SWP-CSW-27 includes instructions to add sensitive information to a CR description without password protecting the file. The procedure also includes instructions to attach a sensitive information form to EDMS, but does not reference SWP-SEC-11 or provide guidance to meet SWP-REC-11 requirements. Factual Basis: (see EDMS for Details) Insights â€¢ Hard copy forms with signatures do not exist yet because none of the vulnerability assessments have been fully completed (reviewed for needed mitigating actions and signed). (see CR 381337) â€¢ After notification of this issue by Quality, the Cyber Security team created a new assignment 04 under AR-CR 399487 â€œAlternate vulnerability screening method not documentedâ€ to correct this issue. <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Security. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to ITMGMT. <N> Reccoment Cat 4 ITMGMT. The cause is known as this was an error in which cyber did not provide sufficient guidance for the sensitive nature of vulnerability documents. Consequence is low. This issue will be addressed under CR 399487 assignment 04.
401038 | CR | 20191105 | CAQ | D | (QA) CDA Vulnerability Assess/Scan Not Per SWP-CSW-27 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Current Critical Digital Asset (CDA) vulnerability assessment and scanning practices do not meet two requirements in SWP-CSW-27 â€œCyber Security Vulnerability Management and Reportingâ€. SWP-CSW-27 meets the requirements within NEI 08-09 â€œCyber Security Plan for Nuclear Power Reactorsâ€ Addendum 1. Requirements: (see EDMS for Details) Factual Basis: â€¢ Actual vulnerability assessment and scanning practices vary from SWP-CSW-27 in the following areas: o Not performed at random intervals o Not performed by a Cyber Security Analyst or delegate for the CDA SEC-COMP-NAS/A o A vendor performs the vulnerability assessments or scanning for SEC-COMP-NAS/A; however, the NEI 08-09 does not currently allow a vendor to perform vulnerability assessments or scanning, and SWP-CSW-27 does not currently allow a vendor to be the delegate for the Cyber Security Analyst. Insights: â€¢ Cyber self-assessment AR-SA 397657 identified a Deficiency in AR-CR 399487 â€œAlternate vulnerability screening method not documentedâ€ describing that alternate vulnerability screening methodologies and frequencies were not properly documented/approved; however, this AR-CR did not cite specific gaps in meeting â€œrandomâ€ intervals or allowing a vendor to perform vulnerability assessments or scanning. <I> **** Actions Taken **** Contacted the Assistant IS Manager over Cyber Security. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to ITMGMT. <N> Reccomend Cat D to ITMGMT The cause is known as this is an issue where alternative frequencies and methods for vulnerabilities need to be outlined. There is industry alignment to support these alternatives but EN has not clearly documented the basis. Consequence is low/medium as it could result in a regulatory finding. This issue will be addressed under CR 399487 assignment 01 where the basis will be clearly documented and approved by CSAT.
401039 | CR | 20191105 |  | 3 | Tape found on monitors | N | N |  | N | NO | <D> **** Detailed Description **** Duct tape was found on the approach sensor at the entrance to and the occupy sensor for each of three ARGOS-5 monitors at the HP primary access point. An extent of condition walk down of all of the plant ARGOS-5 units was performed. The same condition was found with the one monitor at the HP alternate Access point and one of the monitors at the MCR. This condition would not have rendered the ARGOS-5 units inoperable. After exit from the ARGOS-5 unit a person still has to pass through two separate GEM-5 gamma detectors prior to exiting the protected area. <I> **** Actions Taken **** HP supervisionmanagement was notified Tape from the sensors Extend of condition walkdown
401040 | CR | 20191105 |  | 4 | Report of abdominal discomfort |  |  |  | N | NO | <D> **** Detailed Description **** While performing the initial repetition of one component of the physical agility test at the security training facility they reported to the security training instructor that they felt minor discomfort in the abdominal area. The physical agility exam was immediately discontinued by the training instructor. With concurrence from HR/occupational health and concurrence from the individual who reported discomfort they were sent home with instructions to rest, apply ice, and report to occupational health first thing in the morning. The individual was also instructed that if further medical treatment was necessary prior to that time to notify the security operations supervisor. The individual expressed they did not want to seek any further medical attention at the time they elected to go home. <I> **** Actions Taken **** Reported to managment the events described above.
401041 | CR | 20191105 |  | 4 | WCH-V-614 Pipe Cap is leaking at a rate of 1 dpm | N | N |  | N | YES | <D> **** Detailed Description **** While performing a system walk-down on Radwaste Building 487â€™, a leak was observed from (NSR) WCH-V-614 pipe cap at a rate of 1 drop per minute. This valve is located on the WOA-AH-5 (Hot Instrument Shop Air Handler) coil drain line. This issue/equipment is not Technical Specification, LCS, ODCM, Safety Related, or Augmented Quality System, Structure, or Component (SSC) related. <I> **** Actions Taken **** Initiated Work Request to have pipe cap tightened to stop leak. <N> Same issue as AR CR 401019 / WR 29152530 (Water Pooling outside Chemistry breakroom )? | 02-00-WCH-V-614
401042 | CR | 20191105 | CAQ | D | (QA) â€œDigitalâ€ Flag Incorrect for SEIS-SA-1 in MEL |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) â€œDigitalâ€ flag was incorrectly set at â€œYâ€ for Equipment Piece Number (EPN) SEIS-SA-1 within the Master Equipment List (MEL) during the implementation of Engineering Change (EC) 15891 â€œSeismic System Replacementâ€. This error resulted in Asset Suite showing a â€œNâ€ flag for CDA (Critical Digital Asset) without having a Form 27012 â€œNon-CDA Analysisâ€ on file to justify the exception for having a Non-CDA within a Cyber Security-defined â€œCriticalâ€ System. Requirements: (see EDMS for Details) Factual Basis: â€¢ Asset Suite shows a â€œCircuit Over Voltage Protectionâ€ EPN SEIS-SA-1 has a â€œYâ€ for Digital. â€¢ Asset Suite shows the EPN SEIS-SA-1 has a â€œNâ€ for the CDA flag. â€¢ No CSAT-approved Form 27012 â€œNon-CDA Analysisâ€ was found to justify SEIS-SA-1 not being a CDA. Insights: â€¢ An interview with Cyber Security personnel revealed that the â€œYâ€ for Digital for SEIS-SA-1 was an error when entered into Asset Suite during implementation of EC 15981. <I> **** Actions Taken **** Contacted Engineering Supervisor over Digital Designs. . This is a Deficiency identified in Quality Audit AU-CSQ-19. . Recommend assigning to Design Engineering. . The D041 Panel Digital code value was changed to N and this AR referenced in the Comments Section. <N> Reccomend Cat D Design Eng The cause is known as this was an error in which an individual did not correctly set the digital flag to â€œNâ€. Consequence is low/medium as it could result in a regulatory finding. This issue will be addressed under CR 398339 assignment 02 where the a comparison will be completed to ensure the flags are correctly selected. This is part of assessment clean-up actions.
401043 | CR | 20191105 | CAQ | C | Increasing trend of Feedwater Soluble Nickel | N | N |  | N | YES | <D> **** Detailed Description **** Soluble Nickel (SNi) in feedwater has shown a slight increase from about 0.07ppb to about 0.25ppb from June 2017 to October 2018. The increase is small but seems to correlate with and track with changes in RWCU Delta flow. The relationship between these two parameters is unknown and may only be coincidence, but the graph of the two shows some striking similarities that cannot be explained. See attached graph in EDMS. This trend in feedwater Ni should be investigated further. | 02-00-LD-FI-620
401044 | CR | 20191105 |  | 3 | Procedure DES-4-2 Discrepancy |  |  |  | N | NO | <D> **** Detailed Description **** DES-4-2 â€œPreparation and Revision of Columbia Generating Station Design Specification), section 4.1 direct the use DIC 1880 when creating a new Design Specification however this number doesnâ€™t appear to be a valid number per DIC index ( reference: http://thecurrent/sites/RIM/Shared %20Library/DIC%20Index.xls) The proper DIC number need to be determined when creating a new design specification document and it neededs to match SWP-DOC-01. This is an administration issue only and has no impact on the plant. <I> **** Actions Taken **** discussed issue with supervisor and issued this CR
401045 | CR | 20191105 |  | 4 | ECA Hold for WOT 02153118-10 not identified until 11/5/19. |  |  |  | N | YES | <D> **** Detailed Description **** An ECA hold for contingency WOT 02153118-10 was not identified/placed until 11/5/19. ECA holds are for modification packaes which should be cleared by T-20. WOT 02153118-10 is a contingency WOT that is currently scheduled for 01/29/20 (currently at T-12). The AR EVAL associated with the modification required to clear this ECA hold is AR EVAL 378315. Though the PHCSC approved AR EVAL 378315 on 4/1/19 to send to AR-MODS, the AR EVAL presenter did not sent a modification assignment to AR-MODS until 10/14/19. | 02-00-DMA-M-AD32/2
401046 | CR | 20191105 | CAQ | B | (NRC) 2019 Chem-Rad, ARM calibration frequency change | N | Y |  | N | YES | <C> RISK: Medium. CAUSE: Clear. Severity B. Document and Correct. Actions are created. <D> **** Detailed Description **** Plant Area Radiation Monitors (ARMs) are described in FSAR Section 2.3.4, which includes a statement to calibrate every 18 months. ARM-RIS-11 through 13 and 15 through 20 were calibrated on 6/27/2018 per WO-02100573 and are still within 18 months. ARM-RIS-2 was calibrated on 8/28/2019. The ARMs listed in equipment information have not been calibrated within the past 18 months. The ARMs have keep alive sources and a downscale alarm to notify operations if the instrument has failed. The following PMIDs should have the calibration frequencies evaluated; 25754, 25755, 25756, 19838, 19850, and 19851 <N> CAQ, Severity/Responsible Group: B/RADPR Risk (Probability/Consequence): Medium (B) Cause Uncertainty: Cause is Clear License based documents weren't reviewed prior to calibration frequency change. | 02-00-ARM-RIS-1,02-00-ARM-RIS-10,02-00-ARM-RIS-21,02-00-ARM-RIS-22,02-00-ARM-RIS-23,02-00-ARM-RIS-24,02-00-ARM-RIS-25,02-00-ARM-RIS-26,02-00-ARM-RIS-27,02-00-ARM-RIS-28,02-00-ARM-RIS-29,02-00-ARM-RIS-30,02-00-ARM-RIS-32,02-00-ARM-RIS-33,02-00-ARM-RIS-34,02-00-ARM-RIS-4,02-00-ARM-RIS-5,02-00-ARM-RIS-6,02-00-ARM-RIS-7,02-00-ARM-RIS-8,02-00-ARM-RIS-9
401047 | CR | 20191105 | CAQ | B | (NRC) 2019 Chem-Rad, CMS-RIS-27Acalibration frequency change | N | Y |  | N | YES | <C> RISK: Medium. CAUSE: Clear. Severity B. Document and Correct. Actions are created. <D> **** Detailed Description **** The PMID for calibrating the radiation instrument CMS-RIS -27A is 16456. The PM frequency has been extended from 3 years to 6 years per AR-371027 on 9/6/2017, but a rigorous technical justification for this extension was not provided. A calibration per the PMID was scheduled to be performed in 2017 per WO-02072707, but the work was canceled following the change to PM frequency. The most recent calibration of this instrument was per WO-02029303 on 12/11/2013. This instrument contains a keep alive source and a downscale alarm to notify operations if the instrument has failed. <I> **** Actions Taken **** The next scheduled calibration of this instrument is 1/14/2020 per WO-02122961. For extent of Condition, the calibrations for CMS-RIS-27B were reviewed per PMID 16457 and found that the last calibration was completed in 2016 per WO-02083530, and the calibration frequency was extended to 6 years. <N> CAQ, Severity/Responsible Group: B/RADPR Risk (Probability/Consequence): Medium (B) Cause Uncertainty: Cause is Clear License based documents weren't reviewed prior to calibration frequency change. This AR-CR is being addressed under AR-CR 401046. Per SWP -CAP-01, an assignment under resolving AR-CR 401046 has been created to address the issue documented in this AR-CR. Appropriate cross references have been added. | 02-00-CMS-RIS-27A
401048 | CR | 20191105 |  | 4 | tsw-v-h6 was clogged and diddnt pass water. | N | N |  | N | YES | <D> **** Detailed Description **** tsw-v-h6 was clogged and diddnt pass water. while venting thru TSW-V-H6 water didnt pass. <I> **** Actions Taken **** wr/cr | 02-00-TSW-V-H6
401049 | CR | 20191105 |  | 4 | Smoke Alarm in Building 88 | N | N |  | N | NO | <D> **** Detailed Description **** On 11/1/2019 a plant employee caused a smoke alarm while using the microwave in the Building 88 lunch room. <I> **** Actions Taken **** S/M was notified, CR generated.
401050 | CR | 20191106 |  | 4 | WRA-C-51B compressor making abnormal noise | N | N |  | N | YES | <D> **** Detailed Description **** While conducting PMT on WRA-AC-51, 02122349-05, WRA-AC-51 has a two compressor system, compressor WRA-C-51B sounds abnormal and could fail in the future <I> **** Actions Taken **** informed WWM, Ops and maintenance manager and wrote CR/WR <N> **** Equipment Description **** W525 H8/13 communication room | 02-00-WRA-C-51B
401051 | CR | 20191106 |  | 4 | HT-HTP-FP/27 Low Temp light flashing | N | N |  | N | YES | <D> **** Detailed Description **** HT-HTP-FP/27 was found to have the Low Temp light flashing. Outside ambient temp was 36F. HT-HTP-FP/27 is located outside of the Protected Area, just North of the Transformer Yard. <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** North of Xfmr Yard, Outside of PA | 02-00-HT-HTP-FP/27
401056 | CR | 20191106 |  | 3 | VMware Horizon for Ipad |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** When using Windows (VMware Horizon) on the Ipad you cannot get to the Ipad photos folder. Example to email a photo that was taken on the Ipad. <I> **** Actions Taken **** brought it in the D15
401057 | CR | 20191106 |  | 3 | Update SOP-ELEC-115KV-OPS |  |  |  | N | NO | <D> **** Detailed Description **** The purpose of this AR is to provide guidance and pictures on how to complete section 7.2.10. The pictures will allow removing the yard coordinator or system engineer to be removed as part of the 115KV walkdown in section 7.2.10. Also, Bullet 1 of this section should removed because typically these ground devices are part of the clearance. And the ground devices are removed as part of section 7.2.3c. The pictures shown in EDMS will help personnel know what to look for to satisfy this section of the procedure if they are incorporated into SOP-ELEC-115KV-OPS.
401065 | CR | 20191106 | CAQ | D | PPM 16.8.6 late on 11/6/19 | N | Y |  | N | YES | <D> **** Detailed Description **** HIgh voltage adjustment is required to complete the channel calibration, unitl this can be completed the CFT cannot be completed. Currently waiting on new source to be able to complete the channel calibration and radiological calibration. Estimated time of delivery for the source is 11/19/19. PPM 16.8.6 goes late 11/6/19. <I> **** Actions Taken **** wrote cr per PPM 1.5.13 | 02-00-SW-RIS-605
401066 | CR | 20191106 | CAQ | C | Smart Stacks Corrosion Rate Results |  |  |  | N | NO | <D> **** Detailed Description **** Smart Stacks were installed in December 2018 (EC 16612) to provide the station with information on whether or not cathodic protection (CP) is adequately provided for buried piping systems at Columbia. The determination of adequate CP is based on NACE (National Association of Corrosion Engineers) criteria of <1 mpy corrosion rates. Phase one of the Smart Stacks project included installing 8 stacks in different locations. As per the vendor (RSCS), the corrosion rates calculated from 6 smart stacks data are all less than 1 mpy which means that Columbiaâ€™s cathodic protection is adequate in these locations as per NACE criteria. However, 2 out of 8 locations show greater than 1 mpy corrosion rates (SMT-5 shows 2.34 mpy and SMT-8 shows 1.61 mpy). See EDMS for locations. The two smart stacks (SMT-5 and -8) showing greater than 1 mpy corrosion rates, are located in areas where corrosion rates are expected to be the greatest (due to congested areas, mixed metals, building transitions, contaminated soil due to water runoff, etcâ€¦). The smart stack locations were reviewed and approved by two NACE CP4 qualified individuals. Given the results obtained from those 2 stacks, thereâ€™s a need for additional focused cathodic protection at the subject locations where neither the NACE -850mv criteria or <1 MPY pipe wall loss criteria is being met. There is no current concern in regards to the piping integrities in these areas given the fact that Smart Stack no. 5 is in the vicinity of an 18â€ SW line that was UT inspected in 2003 and 2018 and showed a similar corrosion rate (~2.4 mpy calculated). With this corrosion rate the pipe is projected to remain above its minimum design thickness (0.184â€ as per EC 15440) for +80 years. Similarly for SMT-8 location, the remaining life (to stay above its minimum design thickness of 0.238â€) is projected to be +160 years for 1.61 mpy corrosion rate. Recommend assignment to Buried Piping Engineer (AR-CPROG) to plan on follow-up buried piping inspections in the areas of the two locations to ensure the measured corrosion rates. <I> **** Actions Taken **** Discussed with previous CP engineer and Code Programs' Supervisor and initiated this CR
401068 | CR | 20191106 | CAQ | C | MT&E Found out of tolerance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** F&J Dig. Flowmeter- model DMF-1L found OOT & Rejected- No Data Available & Unable to Repair. DEF #7363A generated for Chemistry to evaluate ALL usages. <N> New CR to be written to evaluate past operability impact of out of tolerance MT&E use on plant systems once impacted systems are identified. Per Chemistry- Qualitative data only. No Actions Required A copy of the evaluation has been uploaded into EDMS. No further action required.
401069 | CR | 20191106 |  | 3 | HPI-12.91 Procedural Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Recommend adding a note to step 6.2, Elemental Cobalt Sampling stating â€œNote: DO NOT submit smears to Chemistry that are visibly dirty / rusty. Iron will mask detectable cobalt.â€ This enhancement was discussed in RP continuing training. <I> **** Actions Taken **** RP supervision and training were informed of the enhancement.
401070 | CR | 20191106 |  | 3 | R25 procedure change to SOP-ELEC-USPP-MAINT att 6.2 |  |  |  | N | NO | <D> **** Detailed Description **** R25 procedure change to SOP-ELEC-USPP-MAINT att 6.2 Remove SEIS-RSA-1 and SEIS-SC-1 and replace with SEIS -COMP-1, SEIS-KVM-1, and SEIS-COMP-NCC. These are the new component in the Seismic monitoring system. Descriptions for MET-WDR-4 is wrong and duplicated. <I> **** Actions Taken **** wrote CR
401071 | CR | 20191106 |  | 4 | SP-13B Meter and Recorder Readings vs Grab Sample | N | N |  | N | YES | <D> **** Detailed Description **** SP-13B Meter and Recorder Readings is greater than 10% different from the grab sample. Both need calibrated. <I> **** Actions Taken **** Supervision informed and CR written. <N> **** Equipment Description **** Turbine Bldg 441 chemistry sample room. | 02-00-PSR-CITS-3B
401072 | CR | 20191106 | CAQ | C | ME-02-14-01 revision did not update LCS B1.7.2 |  |  |  | N | NO | <D> **** Detailed Description **** ME-02-14-01 was revised in October 2018 to use 30 years worth of met data instead of 6 years. The six year analysis concluded that SW could have maintained the Control Room below 85F for a LOCA occurring between November 1st and February 1st for the 6 year period analyzed. LDCN-LCS-13-051 added this conclusion to LCS bases 1.7.2. The 30 year analysis concluded that the spray ponds would have not met the 30 day inventory requirement 2 out of the 30 years in November for the time period analyzed. Therefore, the conclusion that could be made from the 30 year analysis is that SW could have maintained the Control Room below 85F for a LOCA occurring between December 1st and February 1st with a high probability of success starting November 1st for the 30 year period analyzed. Per procedure DES-4-1, the preparer of a calculation revision is supposed to review Passport Document References to determine if any documents are referenced by the calculation. The Reference by Document Number field for this calculation does not list any affected documents. Recommend (1) is to add LBD LCS LCS-01 to the TIMC012 panel in Portal J for the calculation ME-02-14-01. While not specific to the section affected, it will provide indication to review the LCS for impact from a calculation revision. Recommendation (2) is to revise LCS B1.7.2 to remove the following sentences: â€œIn general, this calculation will support the capability of SW to maintain control room temperatures LE 85Â°F from November 1st through January 31st. Otherwise, a specific evaluation may be prepared.â€ The current sentence â€œEngineering should evaluate the ambient environmental conditions against the analysis in ME-02-14-01 (Ref. 4) to determine if the calculation is bounding.â€ is the proper action to take. <N> Assignment to licensing is recommended to address the LCS 1.7.2 basis change.
401073 | CR | 20191106 | CAQ | D | Rod accumulator Trouble Alarm. | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-4611 due to low N2 pressure. <I> **** Actions Taken **** Recharged accumulator to and cleared alarm. | 02-00-CRD-HCU-4611
401077 | CR | 20191106 |  | 3 | Tweek process for DG maint. windows is not working |  |  |  | N | NO | <D> **** Detailed Description **** CR 401024 was generated to document part lead times not corresponding with our T-Week process regarding Diesel Maintenance windows which provides challenges in receiving the parts prior to, or in some cases at all, for these windows. Currently, there are ~45 parts required for performance of PPM 10.20.18 that have an ETA of after February 2020. The DG3 online maintenance window is scheduled for the week of January 27, 2020. As mentioned in CR 401024, this either requires the station to pay extra to expedite parts to ensure they get here in time or puts CGS at risk of not receiving the parts and being able to complete the full extent of the Diesel Engine preventative maintenance. This has the potential to impact the equipment reliability of our Emergency Diesel Generators while also potentially impacting the work schedule if parts do not show up and work scope cannot be completed within that work week. There are also extra costs we continually accrue every diesel maintenance window due to the need to expedite parts that have lead times GT T-14 when parts are typically ordered. Additionally, with PPM updates required every two years for all three divisions of Diesel Engine maintenance, our current T-week process also does not support timely and adequate implementation of the procedure changes. For the upcoming 2020 DG3 window, a revised PPM 10.20.18 was drafted and turned into the procedure group at T-16. This adds additional risk as it requires an expedited revision and review of the maintenance procedure from both procedure writing, engineering, and maintenance to ensure that the proper revisions are made and implemented correctly prior to going into the maintenance window. This current DG3 window is not an outlier. PPM 10.20.1 (procedure for 2 year DG1 maintenance) latest revision was issued on 10/02/19 with the DG1 maintenance window that performed this procedure being scheduled and worked the week of 10/7/19. This allowed 5 days between procedure being issued and procedure performance. PPM 10.20.16 for the 12 year maintenance on DG2 was issued on 2/28/18 for implementation of the DG2 window Scheduled and worked starting the week of 3/26/18. This does not allow for adequate task previews and walkdowns for the craft to catch any potential errors in the procedure directing maintenance prior to performing the work in the field. This has the potential to impact not only the reliability of the equipment, but also safety of the craft performing the work. Maintaining our current process of planning diesel windows within the normal T-20 process is not working. We are generating extra costs to expedite parts. We are running the risk of not completing the correct maintenance due to parts not arriving on time. We are adding additional risk due to the expedited procedure revision/review process for the reliability of the equipment and the safety of the craft performing the work. It is recommended to consider utilizing a different process for performing diesel maintenance to ensure we are performing the right work, with the right procedures, during the right maintenance window. This eliminates the increased risk and safety while also reducing costs. One recommendation would be to make diesel windows a dedicated project that would ensure we have the proper resources and timeline to ensure proper execution of the maintenance window. Another option would be to move the maintenance windows to a T-30+ process allowing more time to properly plan and identify and procure required parts to ensure proper maintenance window execution. <I> **** Actions Taken **** Discussed with supervisor <N> Changed Owed to Group to AR-RXMAINT at the request of Reactor Maintenance supervisor responsible for the D/G system windows. PSO supporting.
401078 | CR | 20191106 |  | 4 | MT&E Found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0065279 Air Techniques Analog Photometer- model 2HA-N Passed Meter and Linearity Checks at the Standards Lab. Sent out for Vendor Cal & Realignment. Found OOT & Adjusted within specs. Not used in the OOT Range on Internal Ref. PAO & DOP. DEF #7364A written. No Plant Impact. No Action Required.
401079 | CR | 20191106 | CAQ | C | Completed surveillance missing from WO in QAR records |  |  |  | N | NO | <D> **** Detailed Description **** WO 0212691201 was completed 5/8/2019. The WO documentation completion was recorded in eWP and did not transfer the appropriate surveillance OSP-DO-Q701. Archived QAR records were searched with no success. OQE for succesful completion exists in eSOMS, eWP, test equipment MT&E and the WO cover page. This issue appears to be an eWP/ Assest Suite interface issue, similar to CR 395467. <I> **** Actions Taken **** CR initiated. <N> Task (02126912-01) is now at CLOSED status. Both the DataGlance Logs and the Asset Suite status changes have been reviewed with no findings of anything unusual. Worked Surveillance, with signatures, has been printed and submitted to records. . Copy of submitted record has been attached to EDMS.
401080 | CR | 20191106 |  | 3 | New badge photo failed to transfer from security computer |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** New badge photo was not successfully transferred from the security computer, to the corporate network. Gaps in the transfer of DMP export files are the underlying cause. <I> **** Actions Taken **** Computer engineering will send a new full image table manaully to correct the issue. Notified Security Services Mgr/ Computer Eng and IS Analyst.
401081 | CR | 20191106 | CAQ | C | Torque values were not updated to our approved procedures. |  |  |  | N | NO | <C> MRT Change: CR 401081 moved from NON-CAQ Severity 3 to CAQ Severity C. This is due to the torque values being incorrect. This is not just a documentation issue. <D> **** Detailed Description **** Torque values for NLI bucket WRA-DISC-7F3R were not updated to our approved PPM 10.25.187A. These torque values are in Rev 5 of CVI 999-00,214. Rev 5 is also not updated into our system for use. We are currently at Rev 3. Recommend having CVI 999-00,214 updated to Rev 5 in asset suite. <I> **** Actions Taken **** Writing this CR. We got an email from engineering to use the torque values in CVI 999-00,214 Rev 5, to continue on with our work. Contacted shift manager and made him aware of our impending actions. <N> **** Equipment Description **** WRA-DISC-7E5B is located RW 525 H4/10.9 . WRA-DISC-7E5B not not a valid EPN in Asset Suite. The wrong epn was entered into the CR description the correct EPN is WRA-DISC-7F3B. This was identified by the initiator of this AR. The correct EPN that should have been used was WRA-DISC -7F3R. The CR was updated at the request of the initiator.
401085 | CR | 20191106 |  | 4 | Seal oil adjustments |  |  |  | N | NO | <D> **** Detailed Description **** SO-V-210 and 217 control the hydrogen side seal oil pressure and are typically adjusted to maintain the hydrogen side seal oil within +/- 2 inches H20 of the air side pressure . The valves are currently in specification at approximately 1.5 inches on the air side. If these valves are adjusted to be on the H2 side seal performance would improve and H2 purity should increase. Recommend adjusting the regulators to zero or slightly on the H2 side to optimize performance of the seals. Adjustments can be made in accordance with SOP-SO-OPS section 5.5 <I> **** Actions Taken **** Discussed with OPS and supervisor and initiated CR to document and drive adjustments <N> **** Equipment Description **** Regulating valves are located in the seal oil room on the north side of the skid
401086 | CR | 20191106 |  | 4 | TSW-TCV-11 instrument tubing vibrating | N | N |  | N | YES | <D> **** Detailed Description **** During walkdown of the main generator and support systems TSW-TCV-11 instrument tubing was observed vibrating. This line should be secured to prevent fatigue failure of the instrument line and loss of control to TSW-TCV-11. TSW -TCV-11 is the control valve for the exciter doghouse cooler. See EDMS for picture of the valve and identification of the vibrating tube <I> **** Actions Taken **** Discussed with OPS and Supervisor, initiated CR and WR to correct the condition. | 02-00-TSW-TCV-11
401087 | CR | 20191106 |  | 3 | Several eDNA signals are without history and non-responsive | N | N |  | N | NO | <D> **** Detailed Description **** Several Cycle Isolation Monitoring data signals in eDNA (service ENW .CONDENSE) do not contain the history on the data points and are others are non-responsive. For example, there is a "not responding" freeze error in eDNA when trying to pull any data from ENW.CONDENSE.M160ABCD. See EDMS for complete listing of affected data points. This error began when the signals changed services earlier this year. <I> **** Actions Taken **** Initiated CR. Attached list of signals in EDMS.
401088 | CR | 20191106 | CAQ | D | failed EBUs | N | N |  | N | YES | <D> **** Detailed Description **** E-BU-EB2/1 and E-BU-2/2 both are failed and have impairments. Perform 10.25.156 attachment 9.19 to restore and/or repair light as needed per supervision. <I> **** Actions Taken **** cr supervision <N> **** Equipment Description **** E-BU-EB2/1 and E-BU-2/2
401089 | CR | 20191106 | CAQ | C | CMS-SR-20 Particulate Filter Dark Green Color | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02141471-01, the removed Particulate Filter Had a dark green color. This is possible indictaion of a clogged filter. <I> **** Actions Taken **** Notified Supervision. Continued with surveillance as this is an ongoing condition. Reccommend changing filter more often.
401090 | CR | 20191106 |  | 3 | Tablet Malfunction |  |  |  | N | NO | <D> **** Detailed Description **** We went to check in a work order on a tablet and the check in icon was grey and wouldnt allow us check the package in. <I> **** Actions Taken **** Contacted EWP to assist us with the issue. We logged the individual out of the tablet and logged someone new into it and the icon became accessible. <N> This malfunction occured while working WO 02126629 in EWP. This CR is for tracking purposes. No further actions will be taken.
401092 | CR | 20191106 | CAQ | C | (QA) CR 381337 Not in Compliance with SWP-CAP-01 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) CR 381337 â€œCyber Vulnerabilities not reviewed in required time frameâ€ (Severity C) is not in compliance with SWP-CAP-01, â€œCorrective Action Programâ€. CR 381337 was written to identify that vulnerability assessments were not reviewed in the required time frame. This CR does not show up on the Correction Action (CA) backlog reports visible to management because there are no open CA assignments for vulnerability assessment reviews that have not been completed Requirements: (see EDMS for Details) Factual Basis: â€¢ AR 381337 CAQ severity C was originated on 06/12/2018. Assignment 02 for "screening" and was taken to â€œCompleteâ€ status on 11/15/18; however, "screening" is only the first step of the vulnerability review process. Assignment 04 for "mitigation" performed the next vulnerability review process step on each Form 27032 for each vulnerability review. â€¢ Assignment 05 is an ASGN action and remains open to â€œReview completed vulnerability screening forms. Provide recommended actions to implement patching/configuration changes.â€ Determining recommended actions is a part of a vulnerability assessment per SWP-CSW-27 step 5.2.6; therefore, assignment 05 should be a CA assignment to resolve the original Condition Adverse to Quality. â€¢ There is no evidence of CARB approval for a Corrective Action established longer than 180 days. â€¢ AR 381337 has been open for greater than 365 days, but vulnerability assessments have not been completed awaiting reviews of mitigating actions and approval signatures. Insights: â€¢ Interview with Cyber management revealed each prepared Form 27032 is not in Records yet because the mitigation actions were not yet reviewed/approved with a management signature required for the forms to be considered "complete", and these signatures will occur under Assignment AS 381337-05. â€¢ Interview with the Cyber staff revealed that the NRC increased the scope of the vulnerabilities after the CR was initiated, which added a significant additional amount of vulnerabilities to review. <I> **** Actions Taken **** Contacted the Assistant IS manager over Cyber Security. . This Deficiency was identified during the AU-CSQ-19 audit. . Recommend assigning to ITMGMT. <N> Reccomend Cat C to ITMGMT Cause is known, this is an error in the classification of the assignment type used. QA identified that the assignment should have been a CA type not a ASGN type. Risk is low as there was an action to ensure the items are reviewed and completed.
401093 | CR | 20191106 |  | 3 | OI-27 procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Need to align and removed duplioction of ARB requirments between OI-27 and TDI-09. Eample OI-27 requires and ARB after exam 5 in 6.2.1. TDI-09 reques one after exam 6 in 4.3.3
401094 | CR | 20191106 | CAQ | D | OCA Camera 89 requires additional maintenance. |  |  |  | N | NO | <D> **** Detailed Description **** While preforming routine maintenance on OCA Camera 89 it was found to need follow up work. Contact Security for details. <I> **** Actions Taken **** Notified security superision. Close to WR. NCAQ-4 <N> **** Equipment Description **** Camera site
401095 | CR | 20191106 |  | 4 | Tripping Hazard in Front of Bldg. 38 & 39 |  |  |  | N | YES | <D> **** Detailed Description **** There is a tripping hazard in front of building 38 and 39 located on the Northside of the building ontop of the metal manhole cover. There is a large metal bolt sticking out of it that could cause someone to trip. Both building have the same issue. See photo attached to EDMS Docs. Suggest the bolt be driven in or removed. <I> **** Actions Taken **** Discussed with E&RP Supervisor wrote CR/WR. <N> **** Equipment Description **** Manhole in front of Building 38 and 39.
401096 | CR | 20191106 |  | 4 | Universal Waste Storage Issue on Radwaste 467' |  |  |  | N | NO | <D> **** Detailed Description **** The universal waste storage area on the Radwaste 467â€™ was inspected as part of the weekly hazardous waste inspection. It was noted that the storage container was full of universal waste bulbs and dated 7-25-2018. Per GBP-ENV-17 4.3.12(f), universal waste must be shipped off no longer than one year after accumulation begins. It is unclear whether or not these bulbs were generated from the current re-lamping effort in the plant, but if the date is accurate they need to be removed from the plant and shipped offsite as soon as possible. If the lamps were generated recently, the date should be changed to reflect the correct accumulation start date (when the first bulb was added to the empty container). <I> **** Actions Taken **** Discussed with E&RP manager, initiated CR. <N> **** Equipment Description **** Cart with waste lamps - RW 467' corridor by dirty tool crib
401097 | CR | 20191106 |  | 4 | Training Enrollment Emails not Sent |  |  |  | N | NO | <D> **** Detailed Description **** This is not a qualification issue. Anyone enrolled in training on Monday, November 4, 2019 and Tuesday, November 5, 2019 did not recieve an email conformation. This was a result of an issue related to the Daylight Savings Time change on Sunday morning November 3, 2019 Information Services has corrected this issue, however, back logged emails were not sent to enrollees. <I> **** Actions Taken **** Notified Training Management, identified personnel affected, contacted personnel with training scheduled on Thursday, November 7, 2019. Developed time line to resend remaining emails. <N> Training Support WBL student has a list of individuals as provided by IS to unenroll and reenroll individuals in Plateau to ensure they receive the appropriate e-mail notification. This is being worked on today, 11/7/19.
401098 | CR | 20191106 |  | 3 | MT&E found smearably contaminated upon return to tool crip |  |  |  | N | NO | <D> **** Detailed Description **** During normal survey of tools returned to the RW 467' clean tool crib an 8" dial caliper ID #0066417 was found to have 2kdpm/100cm2 smearable on the tool and 5kdpm/PA direct frisk on the foam in the case. The foam was removed and the tool deconed. The case and tool are now <1kdpm/100cm2. The case and tool are label Radioactive Material. They are at RCA access area to determine historical use. <I> **** Actions Taken **** Deconned tool and case. Initiated CR Notified HP Supervision. Saved tool at RCA Access to find out historical use.
401099 | CR | 20191106 |  | 3 | Generator H2 leakage procedure guidance |  |  |  | N | NO | <D> **** Detailed Description **** Recommend a procedure enhancement to either ABN-HVAC or ABN-GENERATOR to provide guidance on minimum TEA fans running vs amount of main generator H2 leakage to ensure that H2 dissipates from the turbine building in a safe manner.
401100 | CR | 20191106 | CAQ | D | DG Engine 1A2 Governor Oil Level is Low | Y | N |  | N | YES | <D> **** Detailed Description **** DG Engine 1A2 Governor Oil Level is Low at 1/8 inch LT minimum. Request Maintenance add oil as required. <I> FIN notified to add oil to both DG-1 engine governors. | 02-00-DG-ENG-1A2
401101 | CR | 20191107 |  | 3 | OSP-ELEC-M701, M702, M703 Enhancement |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** While performing the monthly DG-1 run, and OSP-DO-Q701 (transfer pump operability), Step 7.3.83 has you N/A the â€a.â€ sub-steps. While omitting the first two of these sub-steps make sense the third is a pounded step and is not covered in the OSP-DO-Q701. Recommend evaluating if the third step should be marked N/A, or the step re-written to clarify the intent. <I> **** Actions Taken **** initiate AR, inform CRS. <N> **** Equipment Description **** OSP-ELEC-M701 step 7.3.83
401102 | CR | 20191107 |  | 3 | Conflict position for D-CTMA-AC-1&2-001 |  |  |  | N | NO | <D> **** Detailed Description **** Ops4 reported there is a conflict position for D-CTMA-AC -1&2-001 during his tour. An equipment tag was hung in the "ON" instead of the "OFF" position as required by the clearance order. This clearance had not been released to work. Recommand a minor fact finding to resolve this issue. <I> **** Actions Taken **** Upper management will be informed. <N> See picture in EDMS
401103 | CR | 20191107 | CAQ | D | IDS 18&19 |  |  |  | N | YES | <D> **** Detailed Description **** IDS 18&19 Malfunction. <I> **** Actions Taken **** Compensatory measure posted. | 02-00-SEC-IDS-E/S/18/19
401108 | CR | 20191107 |  | 3 | TMU-P-1-B clearance lift electrical support needed |  |  |  | N | NO | <D> **** Detailed Description **** WO 02134237-05 is coded as an Operations support task to lift the clearance for TMU-P-1B replacement. After the clearance is lifted the pump circuit breaker is racked in per SOP-ELEC-BKR-OPS. This requires electrician support to check the floor tripper mechanism gap. I recommend adding an Electrical support task to make this more ideal to plan for. <I> **** Actions Taken **** Notified maintenance
401113 | CR | 20191107 |  | 4 | Security BRE 32 Flooring Requires Maintenance |  |  |  | N | NO | <D> **** Detailed Description **** Security BRE 32, located at the northwest corner of the PA, the black rubberized flooring material is dethatching from the subfloor. This is a minor obstruction to the chair casters, and a slight tripping hazard in that the flooring may be razed above the other flooring greater than 3/8â€. For additional information contact security at X2185 <I> **** Actions Taken **** Initiated CR/WR and informed supervision. Requested Security Lt ensure potential tripping hazard is mitigated in the interim. <N> **** Equipment Description **** Security BRE 32, located at the northwest corner of the PA, North side of the BREâ€™s interior.
401117 | CR | 20191107 |  | 2 | Safety near miss during shipping activities |  |  |  | N | NO | <C> Re-opened at request of Owed To Department. <D> **** Detailed Description **** While a worker was raising the landing gear on the A cask trailer in RW437 another worker motioned the driver to move the truck to exit RW437 truck bay. Another worker noticed this and called all stop before the truck started moving. This event could have resulted in a serious injury if not caught by the standby worker. <I> **** Actions Taken **** Stop work was issued. Work discussed in detail covering roles and responsibilities before recommencing. Policy developed to delineate means to designate how one individual at a time will control giving direction to the truck driver, how this is communicated to the work group and how hand offs will occur. CR written. Management notified. Lessons learned: Worker Practices-Individuals are aware of their surroundings and guard against error likely situations. When moving materials there should be one point of contact directing truck movement. This role should be discussed during take 2 prior to start of evolution. <N> The following standard/expection was reinforced with personnel involved with RW shipping activities: During the Take-2, all workers (including truck driver) will be present. Workers will discuss roles and activities that will take place to include directing the truck driver and any handoffs that will be occurring. Only 1 spotter at a time will be wearing a safety vest so there is a visual cue to the work group who has control of truck movement.
401118 | CR | 20191107 |  | 4 | Checksource for CMS-ROT-12A sticking |  |  |  | N | YES | <D> **** Detailed Description **** Checksource for CMS-ROT-12A was sticking durinf performance WO 02141471-01 ISP-CMS/PRM-M401 section 7.12. Need to make adjustment to ensure free movement of the check source. <I> **** Actions Taken **** Wroter CR/WR | 02-00-CMS-RIT-12A
401121 | CR | 20191107 |  | 3 | Man down Deschutes building. |  |  |  | N | NO | <D> **** Detailed Description **** There was a man down in the Deschutes Building. Ambulance took injured person to Kadlec hospital. Medical supplies were reported to be restocked. <I> All paperwork was completed in accordance with ISPM and SWP procedures. A D15 learning was presented to via the Daily ACEMAN and Information Services did a standdown with their staff to cover the topic. No further actions will be taken. <N> OI-34 notifications completed.
401123 | CR | 20191107 |  | 3 | Office Environment Accident - Person Transported Offsite |  |  |  | N | NO | <D> **** Detailed Description **** On Thursday, November 7, 2019 at 9:03 a.m., a 2222 call was received concerning an injured individual in a room in the Deschutes Building. An Energy Northwest employee had fallen from a chair. Occupational Health, Emergency Responders including the fire brigade leader, fire brigade EO and others responded. The Hanford Fire Department (HFD) was summoned. Engine 1923 and Medic 1923 arrived on-site at 9:18 a.m. The patient was evaluated, treated at the scene and transported to Kadlec Medical Center for further evaluation at 9:41 a.m. A supervisor left site to meet the person at Kadlec Medical Center. <I> **** Actions Taken **** Documented the off-site medical transport via this CR. Assisted Occupational Health Staff. Notified Emergency Preparedness for ERO purposes. Org code 72510. CR 401121 also notes information concerning this event. The HP Emergency Responder noted that the Patient Information Sheet (form 24461) was not found in the Emergency Responder kit in the west end of the Deschutes building. <N> All paperwork was completed in accordance with ISPM and SWP procedures. A D15 learning was presented to via the Daily ACEMAN and Information Services did a standdown with their staff to cover the topic. No further actions will be taken.
401124 | CR | 20191107 |  | 3 | License Renewal Inspction |  |  |  | N | YES | <D> **** Detailed Description **** The License Renewal Project planned internal and external inspections of WRA-PCV-51A. The mechanics identified that if the work was started it was likely they would not have been able to complete it becuase no spare parts were included as part of the planning. <I> **** Actions Taken **** Mechanics stpped the job before it was started. License Renewal project will replan the work for a later implementation. | 02-00-WRA-PCV-51A
401127 | CR | 20191107 |  | 3 | Recommend Window Installation |  |  |  | N | YES | <D> **** Detailed Description **** Twice a day, the turbine building watchstander will open RFW-CP-RFT/1A and 1B to read gauges within. These are bump-sensitive cabinets that contain pressure switches which trip the feed turbines. While the risk of a competent operator accidentally tripping a feed turbine is very low, the risk could be further reduce by eliminating the need to open the panel so frequently. It is worth considering whether we could install windows on the cabinet doors during the next refueling outage, which would be in accordance with the Excellence Model attribute of â€œReliableâ€, behavior â€œPrevent, not react.â€ <I> **** Actions Taken **** Informed MCR AR type EVAL needed per DES-2-9 for evaluation/authoriziation of the proposed configuration change? AR EVAL 401218 submitted. <N> **** Equipment Description **** T441 | 02-00-RFW-CP-RFT/1A,02-00-RFW-CP-RFT/1B
401128 | CR | 20191107 |  | 4 | 10.27.45 needs a revision |  |  |  | N | YES | <D> **** Detailed Description **** After walking down WR 29151161 we identified the RMS is the procedure was not properly labeled. At step 7.16 it refers to the switch as S2. The switch is SLC-RMS-EHC/2/3. EWD-10E-001 and E-IR-H22-P011 used for verification. <I> **** Actions Taken **** Provided a marked up copy to Maintenance procedure group. Supervisor and Ops notified <N> Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications | 02-00-SLC-TIC-2
401129 | CR | 20191107 | CAQ | C | LLRT test of RHR-V-17A and RHR-V-17B not in compliance | Y | N |  | N | YES | <D> **** Detailed Description **** During R24 Appendix J Post Outage Report development it was identified that the LLRT test of RHR-V-17A and RHR-V-17B are not in compliance with ANSI/ANS-56-2002, Containment System Leakage Requirements. Specifically, Section 6.2, Direction of Testing states that when a reverse-direction test is performed, all parts of the component that serves as containment barriers (such as bonnets and packing) shall be challenged or tested by additional tests. The LLRT of RHR-V-17A and RHR-V-17B that serve as inboard primary containment isolation valves (PCIVâ€™s) require testing in reverse direction due to the absence of a boundary or block valve in the penetration X-11A and X-11B design. The valve model consists of 16â€ gate with flex-wedge. Therefore, the application of LLRT test pressure in the non-accident direction may or may not challenge the packing gland while under LLRT test. The most current LLRT test results were well within their assigned admin value of 1415 sccm with recorded leakage values of 3.0 sccm for the combined test of RHR-V-16A and RHR-V-17A (Ref. WO 02085174) and 20 sccm for the combined test of RHR-V-16B and RHR-V-17B (Ref. WO 02048842). . Research indicates that the packing barriers of both RHR -V-17A and RHR-V-17B were challenged during satisfactory performance of the most recent primary containment Integrated Leak Rate Test (ILRT) conducted per surveillance TSP-CONT-C801, WO 01143404 June 2009. Historical review indicates that no complete repack activities have been implemented for either RHR-V-17A or RHR-V-17B. Also review of motor operator diagnostic data indicate acceptable packing loads currently exist for both PCIVâ€™s. . Further review for EOC identified three additional inboard PCIVâ€™s with similar configuration. RCIC-V-68 for penetration X-4 RCIC Turbine Exhaust to Suppression Pool, RCC-V-5 for penetration X-5, RCC Drywell Supply, and FPC -V-156 for penetration X-101, Suppression Pool Cleanup Return. A search of asset suite did not identify any current packing leaks on each of these PCIVâ€™s. Also review of motor operator diagnostic data indicate acceptable packing loads exist for these PCIVâ€™s. Additionally, all listed PCIVâ€™s have EQ PM Requirements to conduct a full PM per PPM 10.25.4, Lubrication and Inspection of Limitorque MOVâ€™s on a minimum 4 year bases. Section 7.1.12 provides detailed instructions for inspection of the packing gland for proper function and to address any noted leakage condition. . The most recent R24 Refuel Outage Type B and C LLRT results per WO 02111209 derived a minimum pathway total summation of 7617.7 sccm or just 10.45% (Ref. CR 398329) of the primary containment operability limit of 0.6 La /72,922 sccm. Therefore it is reasonable to conclude that considering the subject PCIVâ€™s leak tightness and available overall leakage margin that the primary containment remains capable of performing its design function. <I> **** Actions Taken **** Notified CR/SM / Supervision <N> **** Equipment Description **** RB550 L1/4.4 | 02-00-FPC-V-156,02-00-RCC-V-5,02-00-RCIC-V-68,02-00-RHR-V-17A,02-00-RHR-V-17B
401130 | CR | 20191107 |  | 3 | Potential Trend in eSom late entries in Maintenance |  |  |  | N | NO | <D> **** Detailed Description **** Seven condition reports have been generated since September 2019 documenting late eSoms entries. Events should be evaluated for a potential adverse trend. <I> **** Actions Taken **** Discussed with management. Generated CR.
401131 | CR | 20191107 |  | 3 | unable to perform scheduled work on Spare RWCU motor |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Electricians went to Warehouse #1 to perform annual maintenance on the spare RWCU motor (UTC# 553267) (CAT ID# 58167585) and determined that the work could not be performed because the motor is still in the shipping crate and staged in the horizontal position. Work steps in WO#02142136-01 says to verify the motor is staged in the Verticall position. It appears that the motor has been staged in the horizontal position since January of 2019. A WR# 29146895, was generated upon receipt to the warehouse to initiate the proper set-up and storage of the motor, but somewhere in the Work Request process there was a missed opportunity to properly prioritize the work. The Annual work cannot be performed as scheduled now and the motor should be evaluated to ensure that no damage has been done by extended horizontal storage. <I> **** Actions Taken **** Notified Supervision and Generate CR <N> **** Equipment Description **** Spare RWCU UTC 553267 Warehouse 1
401132 | CR | 20191107 |  | 3 | Enhancement to 11.2.24.1 |  |  |  | N | NO | <D> **** Detailed Description **** 11.2.24.1 Step 3.3.1 should have the instruction of "perform air activity trending survey per the instructions in the PM WOT Package" and be replaced with the information from the historical WOP which states " Submit any filter media that indicate a significant increase in counts (e.g. >2 times average for the previous 4 weeks) to Chemistry for isotopic analysis. <I> **** Actions Taken **** Discussed with HPS Initiated this CR
401133 | CR | 20191107 |  | 4 | Failed internal drive in SERVER122 (Oracle DB DR server) |  |  |  | N | YES | <D> **** Detailed Description **** pdisk0, a 146GB internal SAS drive in SERVER122 is showing signs of a predictive failure. The drive is 1 of 4 in a RAID5 array that creates an additional storage drive on the server. There is no OS or application data on this drive. The drive has not yet failed and there has been no data lost. <I> **** Actions Taken **** Case opened with IBM. They are sending a replacement drive with a field technician. Drive replaced the afternoon of 11/7/19. Recommend NCAQ 4 as the failed drive has been replaced <N> **** Equipment Description **** This is corporate server equipment. Non-plant impacting. No Cyber security implications.
401135 | CR | 20191107 |  | 3 | AR EVAL 398537 not initiated per DES-2-9 Attachment 8.2 |  |  |  | N | NO | <D> **** Detailed Description **** AR EVAL 398537 was not initiated per DES-2-9 Attachment 8.2 direction. Instead of being sent to Owed To Group ARRG as directed by the DES-2-9 attachment, the AR EVAL was sent to Owed To Group AR-ENGMGMT. As a result, the AR EVAL has been stuck at NOTIFY status with AR-ENGMGMT since 08/28/19. . Recommend resolution by the originator of AR EVAL 398537. . This is an administrative issue only. <N> The Owed To Group for AR EVAL 398537 was reset from AR-ENGMGMT to ARRG by a member of AR-ENGMGMT which allowed ARRG to perform the appropriate next steps of the DES-2-9 process for evaluation of the proposed permanent configuration change. AR EVAL 398537 has been restored to adequate conformance with the DES-2-9 process and is no longer administratively stuck in an out-of-process state.
401137 | CR | 20191107 | CAQ | C | (NRC) 2019 Chem-Rad, RP review for AR closure |  |  |  | N | NO | <D> **** Detailed Description **** This CR is to document an NRC observation. The observation was that someone in the Radiation Protection Department hadn't reviewed the closure comments of ARs 371328 and 371641.
401138 | CR | 20191107 |  | 4 | TMU-P-1B failed to start during PMT. |  |  |  | N | YES | <D> **** Detailed Description **** TMU-P-1B failed to start for PMT reference WO 02134237 task 04 and 12. Attempted to start TMU-P-1B from the control room. Took TMU-RMS/P-1B to start for about 10 seconds and pump failed to start after about 3 minutes. The RMS was then taken to stop for 10 seconds. Opened TMU-V-1B off its closed seat and reclosed the valve to ensure permissive contact made up to start the pump. Second pump start failed. TMU-RMS/P-1B taken to stop after second failed attempt to prevent inadvertent start. <N> THE DATA COLLECTED INDICATES TMU-RLY-62/P1B TDC CONTACT 1 AND 5 IS CLOSED WHEN IT SHOULD BE OPEN. TMU-RLY-62/P1B AND CONTACTS SHOULD BE CHECKED DEENERGIZED/OPEN BEFORE A JUMPER IS INSTALLED ACROSS CONTACTS 9 AND 10 OR BREAKER WILL CLOSE WHEN DC POWER IS APPLIED. PBONO 11-8-19 | 02-00-TMU-P-1B
401141 | CR | 20191107 | CAQ | D | WRA-DISC-7F3BR high readings found during PM | Y | Y |  | N | YES | <D> **** Detailed Description **** While performing PM WO# 02109232-01 DLRO readings through the closed disconnect were high out of spec for the "guide value" but were within operability criteria. <I> **** Actions Taken **** Informed supervision and documented in WO <N> **** Equipment Description **** MCC 7F is located on W525 | 02-00-WRA-DISC-7F3BR
401142 | CR | 20191107 |  | 3 | Procedure revision is needed for 10.25.187A |  |  |  | N | NO | <D> **** Detailed Description **** A step to close the disconnect is needed at the end of this procedure to bring this relatively new procedure in line with the other versions of 10.25.187 and to align with PCSC <I> **** Actions Taken **** informed supervision
401143 | CR | 20191107 |  | 4 | CW-FN-19 oil level at 'ADD OIL' mark | N | N |  | N | YES | <D> **** Detailed Description **** CW-FN-19 oil level at 'ADD OIL' mark 4 gallons of oil was last added to this motor on 5/10/2019 <I> **** Actions Taken **** Informed MCR | 02-00-CW-FN-19
401144 | CR | 20191107 |  | 3 | NRC Inspection REMP Recommendation |  |  |  | N | NO | <D> **** Detailed Description **** NRC auditor recommended an overall evaluation of Columbiaâ€™s Radiological Environmental Monitoring Program (REMP) sampling locations to validate they are located at the highest calculated annual average ground-level D/Q locations and align with the Radiological Assessment Branch Technical Position Rev. 1 and ODCM requirements. <I> **** Actions Taken **** Disscussed recommendation with NRC audit team and EN staff during 11/7/19 daily inspection debrief meeting. Initiatied CR.
401145 | CR | 20191107 | CAQ | D | TDAS-MUX-4 has low +15 VDC power supply | N | Y |  | N | YES | <D> **** Detailed Description **** after replacing the +5 vdc power supply for tdas-mux-4 under wr 29152428 we found the +15 vdc supply low at 12.69 vdc. <I> **** Actions Taken **** generated work request to fix, TDAS-mux-4 is currently working sat. | 02-00-TDAS-MUX-4
401146 | CR | 20191107 |  | 3 | Enhancements to EC Revision Procedure |  |  |  | N | NO | <D> **** Detailed Description **** Currently the EC revision procedure directs the user to us strikethroughs, underlines, revision triangles and revision bars to document the information that changed between revisions of the EC package. This method of documenting changes leaves the EC cluttered and can make it difficult to follow. Recommend revising the EC revision procedure to remove clutter and streamline how the changes between revisions are documented so that the EC package is cleaner and easier to follow. This is a documentation issue only. <I> **** Actions Taken **** Notified my supervisior Wrote this CR <N> Engineering Procedures govering ECs are IP-ENG-001, ENG -DES-50 and the EC module guidance on sharepoint
401148 | CR | 20191107 | CAQ | C | B5b Fuel Tank Corrosion Due to Overheating | N | Y |  | N | YES | <D> **** Detailed Description **** During performance of 02120261-01 B5b Pumper Truck Regular Maintenance it was observed that the fuel tanks have become corroded due to overheating of fuel. Fuel analysis indicate that the fuel is contaminated with rust and the flash point is negatively affected. This is a repeat issue and attributed to fuel tank heaters being unnecessarily used. All diesel fuel provided at CGS is winter grade fuel year round, this includes the B5b diesel fuel. This maintenance cycle, the fuel tanks are scheduled for replacement and continuing with the current practice will quickly degrade these new tanks. The current tanks were replaced as new when CGS purchased and outfitted the B5b approximately 10 years ago. The B5b currently has an oil pan heater, engine coolant heater and three fuel tank heaters. Please see EDMS for additional information/documents <I> **** Actions Taken **** A fuel sample was obtained and sent off for analysis The Flex Program Owner was contacted <N> **** Equipment Description **** B-600 | 02-00-B5B-P-1
401149 | CR | 20191107 | CAQ | C | ME-02-94-44 Enhancement (NRC Identified) |  |  |  | N | NO | <D> **** Detailed Description **** The NRC resident inspector identified possible discrepancies in ME-02-94-44 (DSA Capabilities). Specifically, for the HPCS DG, the calc provides air consumption amounts for multiple starts. The amounts are implied to be per an independent train (2 air start motors); however, after the amounts given, in parenthesis, the amount is divided by 2 and implies the amount before was for all 4 air start motors. The amounts stem from 8.3.290 which state the test is performed per independent train, with DSA-V-84 closed. The calculation should be updated to correct these discrepancies, and reviewed for any others . This is administrative in nature, and does not impact any SSC. Recommend assign to AR-DMC. <I> **** Actions Taken **** Discussed with supervisor, initiated this CR.
401151 | CR | 20191107 |  | 3 | EWP/Data Glance Issues |  |  |  | N | NO | <D> **** Detailed Description **** WO 02147739 tasks 09 & 10 wont status correctly. Task 09 is finished in Data Glance and task 10 is stuck at approved in data glance. Both 09 & 10 are at status 30 in Asset Suite. <I> **** Actions Taken **** Initiated CR for tracking. <N> Both tasks (02147739 - 09 & 10) are now at finished status. Reviewed both the DataGlance Logs and the Asset Suite status changes and didn't find anything unusual.
401152 | CR | 20191107 |  | 3 | 2019 Chem-Rad Inspection â€“ Walkdown comments |  |  |  | N | NO | <D> **** Detailed Description **** While doing a walkdown and source check observation an NRC inspector noted the following: The Mini-89 source check range HP-EQ-42715, Source IDs 2 -99-028 and 2-99-029 has 5 Rad material labels. Most importantly, one of the labels did not contain activity units as required by PPM 11.2.14.4 and per 10 CFR Parts 20 and 30. The number of labels (5) was considered potential confusing to a worker and unnecessary. Only one label necessary for each source and with the required information in PPM 11.2.14.4. It should also be noted two of the labels we so small it could not be read unless you kneel down on your knees and get very, very, close (these labels are intended for very small source containers not a large device such as this). <I> **** Actions Taken **** Contacted RP Supervision and discussed. The labeling shortfalls were promptly corrected by Health Physics personnel. <N> Additional information omitted: A 3rd label was a standard label, typically placed on standard radioactive material containers IAW PPM 11.2.14.9. Its presence is not necessary for sealed sources and devices (SSD) in addition to the required SSD labels.
401153 | CR | 20191107 |  | 3 | current unbalance did not meet acceptance criteria | N | N |  | N | YES | <D> while performing PMT on E-DISC-7E5B the current unbalance did not meet the + or- 10 percent acceptance criteria. the unbalance was 24.7% between A phase, B phase and C phase. <I> notified supervisor and wrote CR. <N> Evaluation to determine the correct formula to be used when calculating voltage and current imbalance was performed under AR 387609-01. Recomendation from this evaluation report needs to be implemented by the planners by adjusting the PMT instructions. Only voltage imbalance needs to be calculated - No need to calculate the current imbalance because "the current at normal operating speed with unbalanced voltage will be greatly unbalanced in the order of approximately 6-10 times the voltage unbalance" I have uploaded a copy of the evaluation report in the EDMS folder. | 02-00-E-DISC-7E5B
401154 | CR | 20191107 |  | 4 | 2019 Chem-Rad Inspection â€“ Walkdown comments |  |  |  | N | NO | <D> **** Detailed Description **** During a walkdown and source check observation an NRC inspector noted the following: While observing a demonstration of instrument source checks, the Model 14C selected had been previously been checked during the shift as part of the nightly chores. However this instrument, while available for use, did not indicate on a label, any scale or scales that are not source checked. These typically are not checked on x1000 scale, and usually not the x0.1 scale. It should be noted, two other Model 14C instruments stored in the instrument room did have the required labels. Other instruments with similar limitations on scales and available for use, also had the required labels. This could be an indication of an isolated incident in this case. <I> **** Actions Taken **** Contacted RP Supervision and discussed. The labeling shortfalls were promptly corrected by Health Physics personnel. <N> An extent of condition was performed and found no other deficiencies in labeling. The label has been corrected on the Model 14C referenced in this CR.
401155 | CR | 20191107 |  | 3 | (NRC) Housekeeping and labels at monitoring wells | N | N |  | N | NO | <D> **** Detailed Description **** During an NRC walk down of the CGS groundwater monitoring wells, the inspector recommended painting the well housing of MW-10,11 and 12 to mitigate rust. Additionally, these wells were not properly labeled. Well housings should be painted and labeled. <I> **** Actions Taken **** Generated WR. Map in EDMS shows locations of MW-10, MW-11 and MW-12. <N> **** Equipment Description **** MW-10 east of building 64 MW-11 in 600 area MW-12 in 600 area WR 29152630 has been actioned and WO 02149284 task #49 has been initiated for F&CE to paint and label the applicable CGS groundwater monitoring wells. This AR/CR can now be closed.
401156 | CR | 20191107 |  | 3 | eSOMS Operator Rounds - Water Balance will not initiate |  |  |  | N | NO | <D> **** Detailed Description **** eSOMS Operator Rounds - Water Balance will not initiate a new day to be populated by 'GETDATA' function. 11/7/2019 water balance is not available in the eSOMS que. This could potentially be due to previous issue identified in AR 400935. Recommend prompt resolution for the calculated readings are necessary in plant status reports. This is a software issue requiring IS technical support. <I> **** Actions Taken **** initiated CR, messaged IS data analyst.
401157 | CR | 20191107 |  | 4 | LORQ Biennial Requal Written Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** One licensed operator failed the biennial written exam administered on 11/7/19. Remediation will be IAW TDI-02 and TDI-08. <I> **** Actions Taken **** De-certified individual in PQD. Notified Operations and Operations Training Management. Recommend Severity Level 4.
401158 | CR | 20191107 |  | 4 | WO 02103780 lacked details to allow flushing. |  |  |  | N | NO | <D> **** Detailed Description **** During the performance of WO 02103780 Water drip from 2" Piping replacement it was identified that no flushing steps were incorporated in the work instructions. A flush plan was created and will be used during the restoration of the system. No further actions required. <I> **** Actions Taken **** generated AR, Contacted WWM and Chemistry
401159 | CR | 20191107 | CAQ | C | Need to evaluate for adequate level of detail in RERR report |  |  |  | N | NO | <D> **** Detailed Description **** During the recent radiological safety inspection, a concern was raised by the NRC inspector on whether the Annual Radiological Effluent Release Report (RERR) should have provided more detail in the table of solid waste shipped offsite (Reference Page 22 of the 2018 RERR attached to EDMS). The station needs to evaluate the need to provide more detail as it relates to matters such as "oil" or source of the effluent (water from the Standyby Liquid Control System), etc. based on regulatory requirements and industry guidance. <I> **** Actions Taken **** Discussed the matter with the RP Manager as well as the NRC inspector. <N> CRBB - This CR is a Bring Back from Chemistry to acquire more information to get in alignment with Severity & Priority.
401160 | CR | 20191107 |  | 3 | WO task 0207750403 not performed |  |  |  | N | NO | <D> **** Detailed Description **** O task 02077504-03 needs to be revised to state WCH-CB-7E4E vice E-MC-7E4E. This work was also scheduled 2 days after the other PMTs for WCH-CR-51A which left it in service. Performance of this task requires that WCH-CR-51B be in service instead. <I> **** Actions Taken **** Work not performed. I recommend rescheduling for a time when WCH-CR-51B is in service.
401161 | CR | 20191107 |  | 4 | SMA-V-21 (SMA-AH-1 Heating supply) will not OPEN | N | N |  | N | YES | <D> **** Detailed Description **** SMA-V-21 will not OPEN. Per SOP-COLDWEATHER-OPS, this valve should Auto Open with outside ambient temp less than 60F. Current outside ambient is 34F and SMA-V-21 will not open even after being cycled from off back to AUTO. Please investigate/repair. Drawings are particularly lacking for this valve and its controllers. Suspect this is part of the OBHV PLC upgrade. <I> **** Actions Taken **** informed MCR <N> **** Equipment Description **** GSB 456 | 02-00-SMA-V-21
401162 | CR | 20191107 |  | 4 | CO-P-2B excessive oil leakage | N | N |  | N | YES | <D> **** Detailed Description **** CO-P-2B is losing high quantities of oil from its inboard pump bearing. The type of oilers these pumps use are crude and unreliable. We have had issues with these for 25+ years. The oiler will be nearly full for a period of time, then lose all of its oil in a hour. Normally this is caused by improper oil level adjustment, Controlled by the of the Auto Oiler. (Typically set Too high). These are a long term issue. | 02-00-CO-P-2B
401163 | CR | 20191107 |  | 3 | SO-P-H2S has excess oil leakage. | N | N |  | N | YES | <D> **** Detailed Description **** SO-P-H2S is leaking oil from its seal at a current rate of one drop every 6 seconds. This is continuing to get worse. This is an significant pump on the Seal Oil Skid. As the leakerate increases, we can install a funnel and route it to the Oil Sump in the room. This needs to be evaluated to determine if it will last till next Outage. | 02-00-SO-P-H2S
401164 | CR | 20191108 |  | 4 | ELPSS panel needs maintenance |  |  |  | N | YES | <D> **** Detailed Description **** The ELPSS panel located in the 437 RW needs maintenance. Contact security at ext. 2185 for further details <I> **** Actions Taken **** Security notification made, CR/WR generated <N> **** Equipment Description **** 437 RW
401167 | CR | 20191108 |  | 4 | CW Chemistry Trouble Alarm Received |  |  |  | N | YES | <D> **** Detailed Description **** CW Chemistry Trouble Alarm Received at 0505. CW blowdown automatically isolated as expected. Notified Chemistry and dispatched Ops 4. | 02-00-CL-SKID-1
401168 | CR | 20191108 |  | 4 | Halogenation/Dehalogenation Trip 11/8/19 |  |  |  | N | YES | <D> **** Detailed Description **** At approximately 5:00 AM 11/8/19, the Continuous halogenation/dehalogenation system tripped and shut down due to an indication of high Total Residual Halogenations (TRH) in the blow down water. All shutdown features and alarms worked as designed. Cause of the trip was a false reading on the Hach 17 TRH meter due to dirty detector cell windows. A picture is included in the EDMS folder of the material cleaned out of the cell. The cell cleaning is recommended once per month which this unit was scheduled for. The manufacture Manual also states that this may have to be done more often based on experience with the system. This unit is under SUEZ control for operation and maintenance. <I> **** Actions Taken **** The detector cell windows have been cleaned and the unit is back to normal operations. Suez has committed to cleaning the windows on a two week schedule. <N> **** Equipment Description **** Blow Down TRH Meter
401169 | CR | 20191108 |  | 4 | TR M3 Desiccant Status Amber |  |  |  | N | YES | <D> **** Detailed Description **** Amber light is illuminated for E-TR-M3 <I> **** Actions Taken **** Informed MCR | 02-00-E-TR-M3
401170 | CR | 20191108 |  | 4 | NRC identified. Radiological gloves found in drip tray. |  |  |  | N | NO | <D> **** Detailed Description **** Radiological gloves found in drip tray in room R-H22/PO21. This is a Combustion Free designated space per 1.3.10C. <I> **** Actions Taken **** Informed Hp. Glove was removed from room. <N> **** Equipment Description **** Reactor building room. R-H22/P021.
401171 | CR | 20191108 |  | 3 | Form 27060 could be improved for SDP product grading |  |  |  | N | NO | <D> **** Detailed Description **** During the 11/6/19 Design Engineering monthy Product Quality Review Board (PQRB) meeting, it was noted that Form 27060 (QUALITY REVIEW GRADING SHEET (EGM-1-13)) could be improved for more meanigful/better grading of Standard Design Process (SDP) products. Resolution may involve revision of Form 27060 or creation of a new similar form specifically for SDP products. Revision of EGM-1-13 may also be necessary. The Form Owner for Form 27060 also needs to be changed to indicate the current Design Engineering Manager. Recommend AR-DESENG resolution of this AR CR 401171 as part of in-progress resolution of existing AR CR 400753. This is an administrative issue only.
401172 | CR | 20191108 |  | 4 | Generator Condition Monitor chart paper nearly EOR | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The generator condition monitor on the TB 471W is showing red and nearing the end of its roll. recommended replacing prior to it running out. <N> **** Equipment Description **** TB 471W
401173 | CR | 20191108 |  | 3 | Editorial Changes and Enhancements to DES-4-5 |  |  |  | N | NO | <D> **** Detailed Description **** As identified in a 4.0 Critique during the management observation focus on Procedure Use and Adherence, it was identifed that there were some enhancements and editorial changes that are needed to DES-4-5, Reviewing Technical Submittals / Vendor Transmittals. The changes that are needed are as follows: * Section 3.2.5, vendor submittals are uploaded to EDMS. This is good for singular activities but not to a project where vendor submittals are collected and held within the EWIP folder. They are held there until EC closeout and then submitted to RIM for record management keeping. * o Section 3.2.6 mentions how to process Form 12310, Vendor Information Documentation Transmittal but not Form 25405, DMS Reference Document Index Sheet. * o Section 3.2.7, VIT should be VTI as it is just an editorial error. Additionally, the CVIs for a project do not go through the participants of VTI as it is a project activity and not all participants need to see this document. . <I> **** Actions Taken **** Discussed with DE Manager and it was agreed that a CR was to be written to document these editorial changes and enhancements. Followup actions will include a revision to the procedure, DES-4-5
401174 | CR | 20191108 |  | 4 | Permissive contact need EC17117 update to work as intended | N | N |  | N | YES | <D> **** Detailed Description **** Verified spared in place relay TMU-RLY-63X/FIS/5B contacts (terminal 10 and term 9) are not closed, this configuration will not allow TMU-P-1B to start. Recommend updating EC 17117 to install permanent splice conductors to term 9 and term 10 on spared relay TMU-RLY-63X/FIS/5B. See history in WR 29152623 <I> **** Actions Taken **** Notified PM, CRS and SM of discover . To address this issue, AR-MODS issued FCR EC17117R002A.FCR on Saturday 11/9/19. Please complete this AR CR 401174 - no further actions under CAP required. | 02-00-TMU-P-1B
401175 | CR | 20191108 |  | 3 | Reevaluate package routine and minor changes to W/O package |  |  |  | N | NO | <D> **** Detailed Description **** W/O package 02141461 HP Mechanical checks of Sam 9. Can we modify this packaged to be a Bi annual package since it only requires WD 40 on January and July. This package is currently a monthly package. We do operational checks nightly on all stationary equipment so the rest of the package is redundant. Also the package is titled Sam 9s. We have changed to TEM. Can we get this changed as well have changed to TEM. Can we get this changed as well? <I> **** Actions Taken **** Emailed Supervision and wrote this CR. <N> **** Equipment Description **** W/O package 02141461
401176 | CR | 20191109 | CAQ | D | CRD-HCU-2651 rod accumulator trouble, high water level | Y | N |  | N | YES | <D> **** Detailed Description **** Due to high moisture level <I> **** Actions Taken **** OPS 2 drained moisture per SOP-CRD-HCU | 02-00-CRD-HCU-2651
401177 | CR | 20191109 |  | 4 | GDS screen time frozen | N | N |  | N | YES | <D> **** Detailed Description **** PDIS-MON-GDS1, on panel H13-P601 in the MCR, time is still at 11/7/2019 14:21:12. All other GDS functionality seems to be updating and valid. PDIS-MON-GDS2, on the H13-P602 panel, time is up to date. | 02-00-PDIS-MON-GDS1
401178 | CR | 20191109 |  | 3 | Turbine building housekeeping |  |  |  | N | NO | <D> **** Detailed Description **** Carts and other materials left in Turbine builidng 441 West end, not in designated storage areas, without current 'staged' or 'work in progress' signs; much of it seems to be left over from the outage. See pictures in EDMS. <I> **** Actions Taken **** Informed SSS, generated AR. See pictures in EDMS. <N> **** Equipment Description **** T441 W by Condensate booster pumps. | 02-00-T-BLDG-MISC
401180 | CR | 20191109 |  | 4 | FDR-FC-23 not able to maintain flowrate | N | N |  | N | YES | <D> **** Detailed Description **** While processing FDR-TK-6 it was noted that FDR-FC-23 was not able to maintain required flowrate. The flow controller was set at 80 gpm on initial start up(with the demand at 65% ) of the system and flow was stable at around 80 gpm and FDR-FU-19 had a D/P of 18 psid. After processing about 35% out of FDR-TK-6 it was noted that filter D/P had only gone up to 20 psid but the flowrate was down to 70gpm with the demand on the controller at 100%. Recommend investigating cause for controller not being able to maintain required flow. <I> **** Actions Taken **** informed CRS and initiated AR/ WR. | 02-00-FDR-FC-23
401181 | CR | 20191109 | CAQ | D | CRD-HCU-3855 high moisture | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-38-55 high moisture. Cleared by OPS 2. | 02-00-CRD-HCU-3855
401182 | CR | 20191109 | CAQ | C | CAS/SAS/SCC HVAC alarm in constant | N | Y |  | N | YES | <D> **** Detailed Description **** The HVAC alarm for the radio consoles in CAS/SAS/SCC is in constant alarm. The temperature on the equipment in DG3 is currently holding at 87 degrees. <I> **** Actions Taken **** Security notification made, Initated hourly checks to monitor temperature, notified IS, notified, SM and initiated CR/WR. . This HVAC is for the Plant radios used by OPS and Security. This radio network would also be required in an Emergency. WWM and mechanical maintenance component manager have been contacted. PMID 26049 and 26050 to replace filters for these AC units were performed annually, but this was recently changed to A02. Craft replaced filters and reset the AC units. Need to reset the PM frequency to annual (A01) or 18 month (M18). <N> **** Equipment Description **** Radio equipment located in DG3, radio consoles are located in CAS/SAS/SCC Per MRT feedback received on 11/12/2019, reopened and assigned as CAQ C to OPSST to get SMS initiated for PM update.
401183 | CR | 20191109 |  | 4 | CAS-C-1B no oil flow visible from CAS-FG-3B or 4B. | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1B no oil flow visible from CAS-FG-3B or 4B.there is normally a small amount of oil flow in one or both of these. There is specific notes in the logs for the inner seperator (CAS-FG-3B) "if flow is sluggish at full load initiate a WR to clean the return line strainers". notes for outer flow glass (CAS-FG-4B) only adress excessive flow. Sump pressure was 118 and the line pressure was 114 pounds on the panel. <I> **** Actions Taken **** wr,cr Compressor was securd. | 02-00-CAS-C-1B
401184 | CR | 20191109 |  | 4 | TSW-V-19B is leaking aprox 1 drop every 3 seconds | N | N |  | N | YES | <D> **** Detailed Description **** TSW-V-19 is leaking aprox 1 drop every 3 seconds <I> **** Actions Taken **** wr | 02-00-TSW-V-19B
401185 | CR | 20191109 |  | 4 | TSW-V-22B is leaking by approx 1 drop every 3 seconds | N | N |  | N | YES | <D> **** Detailed Description **** TSW-V-22B is leaking by approx 1 drop every 3 seconds <I> **** Actions Taken **** wr cr. | 02-00-TSW-V-22B
401186 | CR | 20191109 |  | 4 | R-DOOR-R100 Found Propped Open | N | N |  | N | YES | <D> **** Detailed Description **** R-DOOR-R100 was found propped open during the performance of 15.1.2 Weekly Fire Door checks. This door is a 1.5 hour rated non-essential fire door. It was propped open under WR 29147313, which supports WA State Elevator Inspections and Repairs. A barrier impairment was not issued to support the work. This resulted in an unplanned fire door impairment when discovered. <I> **** Actions Taken **** MCR notified and BI 19-0442 issued. | 02-00-R-DOOR-R100
401187 | CR | 20191110 |  | 4 | packing leak from SS-V-710A | N | N |  | N | YES | <D> **** Detailed Description **** packing leak from SS-V-710A <I> **** Actions Taken **** wr | 02-00-SS-V-710A
401188 | CR | 20191110 |  | 4 | WR 29123794 / WO 02082274 needs to be coded for safety | N | N |  | N | YES | <D> **** Detailed Description **** COND-V-148A leak by was identified as leaking by and causing the downstream pipe to be very hot, FIN team evaluated it and recommended insulation on the pipe. OPS is wiping up oil frequently in the direct vicininity of this pipe since it was identified in 2015 and was recommended to be repaired in R23. The WO is still at Plan. It is hoped that if this is keyed as a persenal safety concern it might get fixed the next outage. Until then please dont insulate it as this would just hold the oil that is spraying off the coupling, <I> **** Actions Taken **** elevating for next outage repair . Updated the Nuc panel on WO 02082274 and WR 29152648 Problem Type to IS (Industrial Safety). | 02-00-COND-V-148A
401192 | CR | 20191110 |  | 3 | PROCEDURE ENHANCEMENT: OSP-CRD-M101 | N | N |  | N | NO | <D> **** Detailed Description **** Step 7.1.1 has 4 sign offs to check 2 valve position indications. The first two valves positions are indicated with a shared light the same as the last two valves. There should be one sign off spot for each.
401193 | CR | 20191110 | CAQ | C | Received FPC RM COOLER FLOW LOW/ TEMP HI alarm | Y | Y |  | N | YES | <D> **** Detailed Description **** **** Received FPC RM COOLER FLOW LOW/ TEMP HI, H13.P812 .R1.4-2. The alarm cleared with no action taken. This is a repeat occurrence â€“ reference WR 29151738. <I> **** Actions Taken **** Informed CRS and generated this AR. | 02-00-RRA-CC-20
401194 | CR | 20191110 |  | 4 | PWH piping has small leak | N | N |  | N | YES | <D> **** Detailed Description **** During PMT check on the PWH system, it was noted that a small leak (4 drops/min) was found on a section of piping that was not replaced or repaired. Note, this leak is not on valve 9 but on the copper piping from the PWH tank to PWH valve 9. <I> **** Actions Taken **** Took pictures and notified ops. | 02-00-PWH-V-9
401195 | CR | 20191110 |  | 3 | GSA B WOT 0213788402 Not Performed as Scheduled |  |  |  | N | NO | <D> **** Detailed Description **** WOT 0213788402, HC D-FP-V-P82/750-001 is a Graded Schedule Code "B" task. This CO renders sprinkler P66 Non -Functional. This requires a continuous fire tour within 1 hour as specified in LCS 1.10.2.A.2 and FPSI 19-0244 (at least 2 people, each person will obtain an extinguisher from the 467 tool crib). The continuous fire tour individuals need to be briefed and in place prior to hanging the clearance order. Crew supervisors were previewing this activity and asked if we would have the fire tour individuals on site at 05:00 to support the task. SM called the Component Group Manager with this question and was informed there were no individuals scheduled to be on-site at 05:00 to supoprt the continuous fire tour requirement. <I> **** Actions Taken **** Confirmed we do not have individuals to perform the required required fire tour to support scheduled CO hang at 05:00 11/11/19. Informed WWM. <N> Per MRT feedback received on 11/12/2019, changed to Non-CAQ 3 to Mechshop as this was clarified as a scheduling issue.
401196 | CR | 20191110 | CAQ | D | RHR A Discharge Pressure High Even With SW A Operating | Y | Y |  | N | YES | <D> **** Detailed Description **** All three RHR loops are usually at keepfill pump pressure, ~150 psig. Periodically this pressure will rise to the point where the crew reduces pressure by performing a partial fill and vent. Normally when the associated SW loop is in operation, the cooling of the shell side in the RHR HX will also cause pressure to reduce back down to keep fill pump pressure. SW-P-1A has been in operation for over 24 hours now (since 09:03 11/9/19) and RHR-PI-612A still indicates ~ 200 psig. An EDNA plot of Computer Point X155 show RHR A discharge pressure dropping consistent with this SW pump start, so it appears RHR-PI-612A may be reading erroneously. <I> **** Actions Taken **** Submitted WR with this CR. | 02-00-RHR-PI-612A
401197 | CR | 20191111 | CAQ | D | SGT-DPIC-1A1 control issues | Y | N |  | N | YES | <D> **** Detailed Description **** While venting containment with SGT-DPIC-1A1 in auto, SGT-FN -1A1 flow is maintained consistently around 5400 cfm. A note in SOP-CN-CONT-VENT states: to prevent a fan trip, SGT flow should be GT 2000 cfm but LT 5378 CFM. Also, when shutting down SGT-FN-1A1 with SGT-DPIC-1A1 in manual at 100% (closed), SGT-FN-1A1 flow is around 3500 cfm well above the 2000 cfm the other three units achieve at minimum flow. <I> **** Actions Taken **** Placed the controller in manual and lowered flow to LT 5378 cfm for venting. | 02-00-SGT-DPIC-1A1
401198 | CR | 20191111 |  | 3 | CSP-PH-W101 Procedure Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** CSP-PH-W101 Attachment 10.1 requires two values recorded for RWCU-CR-601 but fails to specify each as either SP-1 or SP-8 as detailed in the procedure (Sections 8.3.5 and 8.3.6). <I> **** Actions Taken **** Initiate a CR.
401199 | CR | 20191111 |  | 3 | PPM 12.4.21 Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Prodecure provides instruction for resetting digital flow meter. Section 7.2.8 directs to select units of Time but then 7.2.9 instructs to reset units of volume, a step previously performed in 7.2.7. <I> **** Actions Taken **** Initiate CR.
401200 | CR | 20191111 |  | 3 | NRC: Material Storage | N | N |  | N | NO | <D> **** Detailed Description **** The NRC resident had the following questions regarding material storage in the protected area: 1. Three orange construction barrels stored against the SW piping and spray pond wall. These barrels were moved to the North side of the fence at the entrance to SW A Pumphouse. 2. Ladder 7 in the aux condensate pump room stored improperly. Ladder storage was corrected to hold it securely in the brackets. 3. The RHR B pump room contains 9 radiological posting stancions, two swing gates and a PC laundry bag holder up against a wall. Is this permanent storage? Contacted HP for resolution 4. Sump covers for R-1 are askew. Straightened out covers. <I> **** Actions Taken **** Corrected or documented issues as decribed above. Contacted HP's about item 3.
401206 | CR | 20191111 |  | 4 | TOA-FL-2B is at end of roll | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FL-2B is at end of roll <I> **** Actions Taken **** inform CRS and initiate AR/WR. | 02-00-TOA-FL-2B
401209 | CR | 20191111 | CAQ | D | ISFSI Cask Status AMBIENT TEMPERATURE display Yellow | Y | N |  | N | YES | <D> **** Detailed Description **** while performing OSP-SFS-D101 it was noted that ISFSI Cask Status AMBIENT TEMPERATURE display Yellow. IAW step 7.4 a AR/WR must be submitted. The cuase is due to BLDG 104 RM Temp. at 62.7 <I> **** Actions Taken **** inform CRS and initiate AR/WR. | 02-00-SFS-CP-ISFSI/TMS
401211 | CR | 20191111 |  | 3 | editorial change needed for ISP-CMS/PRM-X308 | N | N |  | N | NO | <D> **** Detailed Description **** ISP-CMS/PRM-X308 has a typographical error. Step 7.5.6 is incorrect. Step should say "CMS-SR-21" <I> **** Actions Taken **** Wrote CR
401212 | CR | 20191111 |  | 3 | RCC pH is above chemistry action level | N | N |  | N | NO | <C> MRT Change: CR 401212 moved from 4/Trend Repair to Severity 3 assigned to CHEM. Need actions to be documented <D> **** Detailed Description **** Initial and backup sample of weekly RCC showed pH at 8.71. This is above the CCW Action level 2 of SWP-CHE-02, Table 6.3.9. <I> **** Actions Taken **** Informed Chemistry Supervision, Informed Chemistry Specialist, Informed MCR, wrote CR to document chemistry trend and level excedence.
401213 | CR | 20191111 |  | 3 | SOP-CRD-HCU Section 5.13: Outdated Note on piston reseal | N | N |  | N | NO | <D> **** Detailed Description **** The note in section 5.13 of SOP-HCU-CRD has the following: NOTE: This section is for HCUs with a history of water leakage around the piston seal. ROD ACCUM TROUBLE alarms due to water which occurs weekly or more often is justification for performing this section to reseat the seal. . That note is very outdated and should be removed all together. The current reactivity management guidelines and industry best practice is to take a level 5 reactivity management event if an HCU alarms 3 or more times in a month for the same cause. A year ago we discussed this in the reactivity management review committee meeting. It was decided that we would be proactive. Since we are trying to prevent the Level 5 hit from occurring, we are asking for reseal on HCUs that alarm twice in any 30 day period.
401215 | CR | 20191111 |  | 3 | PPM 1.5.4 Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.5.4 "Control of Measuring and Test Equipment/Transfer Standards/Portable Tools" section 4.1. 8(k .3) states that HP is to survey tools being returned to the RCA tool crib using the SAM 9/11 small articles monitor. The small articles monitor across from the tool crib is out of service and cannot be repaired. This conditions has existed for an extended amount of time, making it impossible to comply with this procedure step. The next closest small articles monitor (outside of the Radwaste Control Room) is a SAM 12 model. PPM 1.5.4 should be revised to state that HP should survey all tools being returned to the RCA tool crib. This allows the use of the RWCR small articles monitor, the bag monitor (BM-285), or handheld friskers. <I> **** Actions Taken **** None taken.
401216 | CR | 20191111 |  | 4 | Work Order Step Inappropriately Marked as Not Applicable | N | N |  | N | NO | <D> **** Detailed Description **** While reviewing monthly tool crib surveys for the RW 467, it was noted that a survey for September could not be found in VSDS. The monthly survey was performed on work order task 02140485-01 and completed on September 7, 2019. Step 4.2 states to "Document results on a Columbia Generating Station Health Physics Survey Map ... and place a copy of the survey map in this Work Order Package." Contrary to this, the step was inappropriately marked "N/A" and neither portion of this step was performed. <I> **** Actions Taken **** Reviewed work order history and survey records from VSDS.
401220 | CR | 20191111 |  | 3 | DES 2-9 Estimate Process Contradicts GBP-AM-11 | N | N |  | N | NO | <D> **** Detailed Description **** DES 2-9 Section 4.6.11.b. states "contact the corporate Estimator to discuss the design change options". GBP-AM-11 states the opposite per Section 4.2 New Project Request (0-4 Year Request) a.-f has the Project Manager involved with the Corporate estimator not the engineering department. <I> **** Actions Taken **** Recommend assigned to design engineering
401221 | CR | 20191111 |  | 3 | CMS-SR-20 and CMS-SR-21 Maintenance procedures | N | N |  | N | NO | <D> **** Detailed Description **** Operations shut down CMS-SR-20 and CMS-SR-21 per SOP-CN -OPS. This closes their penetration isolation valves. In the Channel Calibration and Monthly procedures there needs to be a prerequisite verifying the racks are not isolated per SOP-CN-OPS. This would prevent maintenance personal from starting the rack and causing vacuum to rise damaging the detector. <I> **** Actions Taken **** Had a discussion with the CRS about topic Discussed this with my Supervisor <N> The procedures that need to be revised are ISP-CMS/PRM -M401,2 & ISP-CMS/PRM-X306,8
401222 | CR | 20191111 | CAQ | D | FP-V-33 packing leak | N | Y |  | N | YES | <C> MRT Change: CR 401222 moved from 4/Trend Repair to CAQ Severity D/Trend Repair. Fire Protection 2 System <D> **** Detailed Description **** There is a steady stream was water issuing from the packing of FP-V-33. This gate valve is currently shut, but will be opened to support testing of FP-P-1. It is likely that packing leakage will increase further when the valve is opened. At the current leak rate this does not present any housekeeping or safety issues. Request maintenence evaluate leakage and repair as necessary. <I> **** Actions Taken **** Notified SM. <N> **** Equipment Description **** CWPH | 02-00-FP-V-33
401225 | CR | 20191111 |  | 3 | HP Instructions needed for two pieces of new RMC Equipment | N | N |  | N | NO | <D> **** Detailed Description **** HP Instructions need to be developed for new RMC Equipment. A new variable speed peristaltic pump was purchased recently to clean FD-SUMP-T2. Currently the pump will be controlled by work order instructions. However, future use of the pump would benefit from having instructions. AR-EVAL 00399518, Install new speed drive/ disconnect to motor for FD-SUMP-T2, requires the pump not be plugged into a safety-related bus. New ultrasonic sink was purchased prior to R24. Work order instructions were used to operate the ultrasonic sink on the Rx 606. HPI should be written to assist with Laborers setting up and operating the Ultrasonic Sink on the Rx 606. <I> **** Actions Taken **** Informed supervision.
401226 | CR | 20191111 | CAQ | D | As-Found out of tolerance SGT-RLY-TK/2A2 | Y | N |  | N | YES | <D> **** Detailed Description **** As-Found out of tolerance SGT-RLY-TK/2A2. As-Found was 44.57 seconds Tolerance range 37.28 - 41-11 seconds. Allowable from E514-30 is 44.73 - 33.72 seconds. <I> **** Actions Taken **** Adjusted relay to within tolerance. As-Left is 40.16 seconds <N> **** Equipment Description **** E-MC-8BB/8D | 02-00-SGT-RLY-TK/2A2
401227 | CR | 20191111 |  | 4 | E-CVT-500KVA crackling.sparking noise | N | N |  | N | YES | <D> **** Detailed Description **** during trans yard inspection, an intermittent cracking/sparking noise was noted. the noise came and went several time over a period of minutes <I> **** Actions Taken **** informed supervisor initiated CR/WR | 02-00-E-CVT-500KV/A
401228 | CR | 20191111 |  | 4 | Weeds around electrical rack at TMU Pumphouse | N | N |  | N | NO | <D> **** Detailed Description **** The electrical rack outside TMU pumphouse that is used to wire the PDU for the crew trailer has weeds as high as the dissconnects all the way around the rack. <I> **** Actions Taken **** Contacted Supervision <N> **** Equipment Description **** TMU pumphouse
401230 | CR | 20191111 |  | 4 | Bldg. 30 CWPH 8 of 25 overhead lights out - need relamping | N | N |  | N | YES | <D> **** Detailed Description **** Noted during a walkdown of the Circ. Water Pumphouse that 8 of 25 large overhead lights are not functioning. Suggest planning and scheduling some relamping work in the pump house. <I> **** Actions Taken **** Documented the condition in this CR. Photos in EDMS. Notified Electrical Component Manager. <N> **** Equipment Description **** Circulating Water Pumphouse Bldg. 30 relamping needed - 8 o f 25 overhead lights out.
401231 | CR | 20191111 |  | 4 | TG 441 metal transition piece loose FB turnout | N | N |  | N | YES | <D> **** Detailed Description **** During a walk down of the TG 441 I noticed that a metal door transition piece at the doorway to the Fire Brigade turnout station was loose which presented a slightly elevated edge and potentially a trip hazard. <I> **** Actions Taken **** The metal transition was taped with red tape to identify and mitigate the issue until a more permanent solution can occur. See EDMS for photos. <N> **** Equipment Description **** Metal transition to FB turnout station TG 441
401232 | CR | 20191111 |  | 4 | Failed EBU's | N | N |  | N | YES | <D> **** Detailed Description **** During performance of WO# 02140846-01, E-BU-SWA5/4 and E-BU-SWA5/14 we not lit after 90 minute performance test. When re-energized, fault indicator show a battery fault of both units. <I> **** Actions Taken **** FSIP 19-0285 was generated and lanterns staged. New batteries will need to be ordered and decision made wether or not to upgrade to LED's. <N> **** Equipment Description **** EBUSWA502 | 02-00-E-BU-SWA5/14,02-00-E-BU-SWA5/4
401233 | CR | 20191111 |  | 3 | RB 471 lighting deficiency in area under perm. scaffold | N | N |  | N | YES | <D> **** Detailed Description **** During a walkdown of the Reactor Bldg. it was noted that under some permanent scaffolding adjacent from the SE elevator there is an area that could use some temporary lighting (stringers) or preferrably permanent relamping of existing fixtures. See EDMS for photos <I> **** Actions Taken **** Document pohtos of the conditions. Initiated this CR. Notified Electrical Component Manager. <N> **** Equipment Description **** RB 471 adjacent from the SE elevator by the RP dressout are a.
401235 | CR | 20191111 |  | 3 | Cobalt Component Replacement is not following schedule |  |  |  | N | NO | <D> **** Detailed Description **** Attachment 7.2 of PPM 1.11.25 lists 32 cobalt containing valves and outages in which they were to be replaced with non-stellite valves. The schedule shown in the attachment is from R20 to R25. None of the valves shown to be replaced in R25 are in outage scope. One of these valves has been replaced so far, three (Cond-V-135A-C) had work orders for replacement cancelled and the remainder show no sign of activity. The station needs to either move to complete these replacements or remove the attachment from the procedure. <I> **** Actions Taken **** Notified my supervisor and the RPM
401236 | CR | 20191111 |  | 3 | Acrid Odor Smelled While Performing TMU-P-1B Breaker Racking | N | N |  | N | YES | <D> **** Detailed Description **** While performing breaker racking operations for TMU-P-1B, the closing fuses were installed per SOP-ELEC-BKR-OPS. When the closing spring charging motor actuated, a slight acrid odor was noticed. Control power fuses were removed per CRS direction. After inspection of the breaker cubicle, no visible damage was observed. <I> **** Actions Taken **** Informed supervision, wrote CR | 02-00-TMU-CB-TMU1B
401237 | CR | 20191111 | CAQ | B | RCIC suction pressure was noted to be low during turnover. | Y | Y |  | N | YES | <C> Risk: Medium (Operability) Cause: Unclear Operations is investigating misposition. <D> **** Detailed Description **** RCIC suction pressure was noted to be low during turnover and RCIC-P-3 was not running. The pressure switch which starts RCIC-P-3 is not the same indication as the control room pressure indication. A trace of RCIC suction pressure showed a repeating pattern of pressure decay followed by rise in pressure and the pattern stopped this morning. An EO was dispatched to check pressure indication locally. RCIC-PIS-34 pressure indicated 80 psig; RCIC-PIS-1 indicated 47 psig which was not expected as they are both on the same line. The EO discovered an isolation valve for RCIC-PIS-34 closed and was directed to open the valve. RCIC-P-3 started when the isolation valve was opened. <I> **** Actions Taken **** Supervision was informed.
401238 | CR | 20191112 |  | 4 | FP-V-SGT/11 PACKING LEAK | N | N |  | N | YES | <D> **** Detailed Description **** FP-V-SGT/11 (RX 572) WAS FOUND TO HAVE A LEAK FROM THE PACKING. (APPROX. 15 DROPS PER MINUTE.) THERE IS A SUBSTANTIAL AMOUNT OF WATER ON THE FLOOR AS A RESULT. FP -V-SGT/21 IS ALSO LEAKING SLIGHTLY AND BOTH VALVES SHOULD HAVE THE PACKINGS TIGHTENED ENOUGH TO STOP THE LEAKS. <N> **** Equipment Description **** RX 572 | 02-00-FP-V-SGT/11,02-00-FP-V-SGT/21
401239 | CR | 20191112 | CAQ | D | PPC not functioning |  |  |  | N | YES | <D> **** Detailed Description **** PPC is not functioning. When trying to start the program it states "Trying to connect to ppcv using TELNET" and shortly after states the connection timed out. <N> **** Equipment Description **** MCR PPC thermal power monitoring TDAS is the primary monitoring system at the moment.
401240 | CR | 20191112 | CAQ | D | Oscillograph start | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. The alarm was due to the following sensor: J7 (500 kV Neutral Ground Overcurrent) and J15 230KV Undervoltage All sensors have been reset. E-TR-S and E-TR-B voltages are 238/235/238kV and 118/117/118 kV respectively. BPA Dittmer reports the cause of the grid disturbance was a 115KV Franklin Benton #1. The single pole fault automatically reclosed. The fault was on the 115kV system and did not involve the 230kV or 500kV lines. No damage or emergent outage was noted. <I> **** Actions Taken **** Wrote CR Followed ARP
401241 | CR | 20191112 |  | 4 | building 1 gap around Sprinkler Escutcheon | N | N |  | N | YES | <D> **** Detailed Description **** While performing Fire protection system inspection a gap was found around a sprinkler escutcheon in the main hallway just above the I&C door. A new ceiling tile needs to be notched and installed around sprinkler head. <N> **** Equipment Description **** Building 1
401245 | CR | 20191112 |  | 3 | PPM 15.1.17 update for work in 12/2/19 | N | N |  | N | NO | <D> **** Detailed Description **** As part of craft walkdown for upcoming WO 02146944 for Ventilation deluge System Air Flow Test for REA-FN-2A in the 12/2/19 work week, there is a section under 7.3.12 that cleans the nozzles if the event any are found plugged. As part of this step after cleaning it directs slowly opening SA-V-100/4. However after checking that the nozzles are clear, there are no step to close SA-V-100/4. This section is only performed if any of the nozzles are blocked, however the procedure should be updated to direct closing SA-V-100/4 following the peformance of step 7.3.12 b) 2) if performed.
401246 | CR | 20191112 |  | 3 | Cognitive Trend in Work Order Documentation | N | N |  | N | NO | <D> **** Detailed Description **** Since September 1, there have been sixteen instances in the Health Physics department where work packages were returned for corrections related to inadequate placekeeping or completeness of documentation. Please perform a trend evaluation on these events to determine if additional actions are needed. <I> **** Actions Taken **** Discussed the issues with the radiological services team.
401247 | CR | 20191112 |  | 3 | Primary Host Drive Failure | N | N |  | N | YES | <D> **** Detailed Description **** The out of band dragon siem has a primary host drive failure. The secondary host is working properly but we are getting email notifications for full hard drive. This is not reportable under 10 CFR 73.77. <I> **** Actions Taken **** The out of band dragon is currently a corporate asset and an attempt to restart the failed drive was unsuccessful. The device is currently end of life, we do not have a backup and it is not currently supported by the vendor due to its age. Recommend replacing the device with a McAfee SIEM or redirecting out of band traffic to the EP SIEM. <N> **** Equipment Description **** 525 Comm Room | 02-00-NET2-COMP-SIEM/1
401248 | CR | 20191112 |  | 4 | 3 controllers missing labels in 487' RW Counting Room C317 | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** during a walkdown to replace WOA-MC-9B, I found where I thought the controller was located, but it was only identified with "9B". Also, two other controllers are in close proximity. Please verify that the controllers on the north wall of the 487' RW Counting Room C317 are: WOA -MC-9A, WOA-MC-9B and WOA-TIC-9. If these are the correct EPN's, then put a temporary label on them. <I> **** Actions Taken **** Wrote this CR and I am submitting a Label Request for each of the 3 devices <N> **** Equipment Description **** WOA-MC-9A, WOA-MC-9B, WOA-TIC-9
401250 | CR | 20191112 |  | 3 | License Agreement approval outside Delegation of Authority | N | N |  | N | NO | <D> **** Detailed Description **** A software license agreement was signed not in accordance with the Delegation of Authority roster which assigns budget authority for purchases. <I> **** Actions Taken **** Issue occurred in Dec 2018. Once identified, event was investigated, CR generated, and coaching performed. <N> Recommend CAT 3 to ITMGMT.
401252 | CR | 20191112 |  | 4 | CVI/ISO 317-00,532 Drawing Error (BD-V-12 Should Be BD-V-14) | N | N |  | N | NO | <D> **** Detailed Description **** CVI//ISO 317-00,532 has a drawing error needing correction. The valve identified as BD-V-12 does not exist in Asset Suite Database. In the field, the valve is labeled BD-V-14. Recommend revising drawing to indicate BD-V-14. BD-V-14 is a blowdown valve for the Aux Boiler. <I> **** Actions Taken **** CR written. <N> This CR is a duplicate of CR 400487. CR 400487 is addressign the drawing issue. Recommend that his CR be trended to CR 400487.
401253 | CR | 20191112 |  | 3 | Add Frequently Performed Operations Flush to SOP-SYSTEM-FLUS | N | N |  | N | NO | <D> **** Detailed Description **** The flush of 1â€RWCU(13)-1 is frequently performed after transferring resin from RWCU TK 104A/B to a resin liner for disposal. The flush is performed as a generic flush requiring reviews by the Shift Manager, Control Room Supervisor, System Engineer, and RP Supervisor as required by SOP-SYS-FLUSH. The flush WO instructions have not changed the last three performances. Adding the flush instructions to SOP-SYS-FLUSH or another appropriate procedure would remove the need for the Shift Manager, Control Room Supervisor, System Engineer, and RP Supervisor to review the flush plan prior to implementation of the flush. The flush process is described in MWO 02125896-08. <I> **** Actions Taken **** Notified RP Supervisor Cross-referenced MWO 02125896-08
401254 | CR | 20191112 |  | 3 | Inconsistences in SOP-SYS-FLUSH | N | N |  | N | NO | <D> **** Detailed Description **** SOP-SYS-FLUSH Step 6.1.2 requires the System Engineer review the flush plan; whereas, Prerequisite Step 3.1.5 omits the System Engineer from the review group. The current conservative practice is to include the System Engineer in the review group for all generic flush plans developed under SOP-SYS-FLUSH. <I> **** Actions Taken **** No immediate action required.
401255 | CR | 20191112 |  | 3 | CW-FT-4 IMDS Addenda error | N | N |  | N | NO | <D> **** Detailed Description **** Number 3 in the Addenda refers to CS-FIC-4 and should be CW-FIC-4 <N> EPN CW-FT-4 does not exist in Asset Suite MEL - likely meant EPN CW-LT-4.
401256 | CR | 20191112 | CAQ | C | FP-ENG-1 would not start Manually | N | Y |  | N | YES | <C> MRT Change: CR 401256 moved from CAQ Severity D/Trend Repair to Severity C assigned to MNTPLAN. Need actions to be documented <D> **** Detailed Description **** FP-ENG-1 would not start manually, per SOP-FP-START. Both the Manual 1 and Manual 2 positions were attempted with no sucess. In the Manual 1 position the engine could be heard to attempt to turn over very briefely, despite the crank pushbutton being pushed and held. The was no evidence of attempt to start in the Manual 2 position. Highly suspect poor charge on FP-P-1 Batteries. FP-P-1 local control switch was placed in OFF and a COSCO requested from MCR. <I> **** Actions Taken **** Attempted start in Manual 1 and Manual 2 position. Left Local Control Switch in OFF and requested COSCO for Config. Control. <N> **** Equipment Description **** CWPH | 02-00-FP-ENG-1
401257 | CR | 20191112 |  | 3 | false notification for Phishing test | N | N |  | N | NO | <D> **** Detailed Description **** I received an email notification that I had â€œmissed open enrollmentâ€. My heart instantly dropped because I have been struggling to understand some of the changes and I feared I had majorly misunderstood the window for updating my benefits. I have a chronically ill wife and this could be a devastating mistake for me. I hoped this was just a very poorly timed â€œphishingâ€ test and clicked on the Report Phishing Attempt button. To my relief, it was just a test. This is a very very poor decision to test us like this. Many people have medical issues and it is a great burden in their lives. I talked with others who felt the same panic I did. Please be more considerate of others next time. <I> **** Actions Taken **** wrote this cr <N> Met with Shop to understand concerns and communicated that Cyber will not be running Open Enrollment Phishing tests during Open Enrollment in future.
401259 | CR | 20191112 | CAQ | C | Values for SDV trip differ in the LCS, EC, and ARP | Y | N |  | N | NO | <D> **** Detailed Description **** 4.603.A7 (tile 1-2) and 4.603.A8 (tile 1-2) lists the Scram Discharge Volume High Level trip setpoint as GE 529'7". However 4.603.A7 (tile 1-3) and 4.603.A8 (tile 1-3) titled "SDV Level High Trip" states the setpoint for the same parameter as 5 inches lower at 529'2". EC 12271 (page 88) states that the value should be changed from 529'7" to 529'2", however LCS still lists the spec as 529'7". Please evaluate the actual setpoint and modify documents to reflect the most up to date numbers. <I> **** Actions Taken **** Notified training and operations supervisors, initiated this CR.
401260 | CR | 20191112 | CAQ | C | Manual PCIVâ€™s not Listed in IST Program for Leakage Signific | Y | N |  | N | YES | <D> **** Detailed Description **** During review of Local Leak Rate Test (LLRT) components it was identified that four Primary Containment Isolation Valves (PCIVâ€™s) that are contained and leak tested in the Primary Containment Leak Test Program are not designated as leakage significant â€œLâ€ in the In-service Test Program (IST). The four PCIVâ€™s are RCIC-V-184 and RCIC-V-740 for Penetration X-54Aa, Disbanded Air Supply to RCIC-V-66 and MWR-V-124 and MWR-V-125 for Penetrations X-94 and X-95 respectively, Non-Used Miscellaneous Waste Radioactive. The lack of an â€œLâ€ designator is inconsistent with other similar manual PCIVâ€™s contained in both the PCLRT and IST Programs that fulfill seat leakage function in support of Overall Primary Containment Integrity. . Research indicates that both RCIC-V-184 and RCIC-V-740 for penetration X54Aa isolation were removed from the IST Program upon implementation of disbandment modification MDC 95-0269-0A. However, the capping of the penetration relied on a blind flange boundary that does not meet primary containment design requirements. . Review of the LLRT database indicates that both the X-54Aa PCIVâ€™s and the X-94 and X-95 penetration PCIVâ€™s have been tested in accordance with the PCLRT Program and have repeatedly demonstrated leak-tight integrity by successfully passing their LLRT assigned admin limit of 110 sccm. Therefore the primary containment overall design function has not been challenged. The four PCIVâ€™s have also been verified as contained and controlled in accordance with PPM 1.3.29, Locked Valve Checklist. . Recommend assignment to IST Program Owner (AR-PPROG) to evaluate leakage designation requirements for resolution of program inconsistencies. <I> **** Actions Taken **** Notified Supervision, IST Program owner and CRS/SM <N> **** Equipment Description **** RB535- J6/7.1 - RB504 -J4/7.4 - | 02-00-MWR-V-124,02-00-MWR-V-125,02-00-RCIC-V-184,02-00-RCIC-V-740
401261 | CR | 20191112 |  | 4 | ILC candidate failed systems exam #6 | N | N |  | N | NO | <D> **** Detailed Description **** One ILC candidate failed ILC systems exam #6. Remediation is being conducted under TDI-02 and tracked with AR 00396810-14. <I> **** Actions Taken **** Reviewed exam with student. Informed supervision.
401262 | CR | 20191112 |  | 4 | Roll up door to GSB manual chain drive shaft is not working | N | N |  | N | NO | <D> **** Detailed Description **** Roll up door to GSB manual chain drive shaft is not working, it appears the drive shaft is disconnected from the gear box. Please fix <I> **** Actions Taken **** write cr <N> **** Equipment Description **** gsb roll up door
401263 | CR | 20191112 | CAQ | C | Update LCS 1.3.1.1-2 F7a and F7b to match IMDS | Y | N |  | N | NO | <D> **** Detailed Description **** The RPS instrumentation setpoints in LCS Table 1.3.1.1-2 for Functions 7.a and 7.b do not reflect the current setpoints in the Instrument Master Data Sheets for instruments CRD-LIS-601A, B, C, D and CRD-LS-613A, B, C, D. The setpoint change is discussed in EC 12271 (page 88) as part of the SDIV plant modification. It is not clear why the setpoints in the LCS table were not changed at the time of installation. The instrument names were changed in LCS Revision 95 but the setpoints were not changed. The existing LCS values do not appear to be relevant to anything at this time and should be revised to be consistent with the other RPS functions (in that the actual trip setpoints are specified in the table.) <I> **** Actions Taken **** This appears to be a documentation issue associated with the LCS. The values in the IMDS are supported by calculation as implemented in the field. The LCS provides a convenient listing of all the nominal trip setpoints. These setpoints were removed from the Tech Specs upon conversion to the ITS at amendment 149 and the infomration was relocated to the LCS.
401264 | CR | 20191112 |  | 4 | EDR-V-57 | N | N |  | N | YES | <D> **** Detailed Description **** during performance of sop-rw/edr-ops backwaching of EDR -DM-9, EDR-V-57 (hold valve) popped open for approx 5 seconds when it should have remained shut and caused a hi- filter d/p alarm <I> **** Actions Taken **** initiated CR?WR informed supervisor | 02-00-EDR-V-57
401265 | CR | 20191112 |  | 3 | Chemistry unable to complete WO 02142220 task 03 | N | N |  | N | YES | <D> **** Detailed Description **** Chemistry was unable to complete WO 02142220 task 3, setting up the temporary sample and EP noble gas monitor carts, because the required equipment is missing. The compensatory noble gas monitor for the turbine building effluent air system (CNGM), HP-EQ-42851, is not in the lead cave where it normally resides on RW 525. The TEA CNGM is swapped out yearly for a calibrated device; this was last performed 11/19/18 via WO 02127477. The next WO for this calibration is 02136430 set to start 11/20/19, and the replacement meter and probe is available in the RW 467 tool crib. Further investigation found that the CNGM for the rad waste effluent air system, HP-EQ-42850, is missing from the lead cave where it normally resides in RW 487, as well. The CNGMs for the TEA and WEA systems need to be located and reinstalled in the lead caves. <I> **** Actions Taken **** Spoke to HP, EP, Chemistry, I&C, work week manager, calibration lab. Reviewed previous work orders and CRâ€™s for the effected equipment. | 02-00-HP-EQ-42850,02-00-HP-EQ-42851
401266 | CR | 20191112 | CAQ | C | RPS design spec Pbypass setpoint not updated | Y | N |  | N | YES | <D> **** Detailed Description **** This is a document issue only. Design specification data sheet, CVI 02C72-03,3, Sheet 19, was not updated to specify the setpoints for Reactor Protection System Trip Bypass - Turbine Stop Valve and Control Valve Fast Closure Trip Bypass. Calculation E/I-02-92-1070 (CMR-95-0003) determined the analytical limit and allowable value. IMDS for MS-PS -3A, -3B, -3C and 3D specifies the nominal trip setpoint. There is no impact on the safety function to not be bypassed at greater or equal to 29.5 %RTP (TS Table 3.3.1.1-1, Functions 8 and 9)[Pbypass]. <I> **** Actions Taken **** Recommend assignment AR-DEI to correct the AL, AV and NTSP in CVI 02C72-03,3, Sheet 19, Reactor Protection System Trip Bypass - Turbine Stop Valve and Control Valve Fast Closure Trip Bypass, Items 4.1.17.7, 4.1.17.8 and 4.1.17.9. Markup attached to EDMS. | 02-00-MS-PS-3A,02-00-MS-PS-3B,02-00-MS-PS-3C,02-00-MS-PS-3D
401268 | CR | 20191112 |  | 4 | Temporary Cart for TEA-SR-26 became inoperable | N | Y |  | N | YES | <D> **** Detailed Description **** TEA-SR-26 temporary sample cart sample pump pully came off of pump shaft. <I> **** Actions Taken **** Informed supervision & CRS <N> **** Equipment Description **** 525' RW bldg | 02-00-TEA-SR-26
401271 | CR | 20191112 |  | 4 | HD-LIC-5A21 degrading cycling of level and demand | N | N |  | N | YES | <D> **** Detailed Description **** Recommend online troublleshootinreplacement of HD-LIC-5A21. HD-LIC-5A21 was first noted to be cycling through a greater range than usual in late July after R24 startup. CR 398564 (notes) noted this cycling level and demand during HP turbine differential temperature troubleshooting in late August . The cycling of HD-LCV-5A21 was oberved by the AOV engineer on 9/19 via camera TG/19 and MR/07. The valve appeared to be responding to signal without overshooting indicating that it may be a control loop issue. HD-LCV -5A21 positioner was replaced in R24 under WO 02143181 followed by a diagnostic and loop cal. Slight binding was noted at the 75-100% open position, but normal operation does not historically exceed 30% open at 100% power. AR 00395828 and 00395319-04 recommend valve rebuild in R25 under WO 02149256. No other control loop issues noted. These HD controllers are known to have age related failures. HD-LIC-5A21 had capacitors replaced in 2007, but the circuit board and components are ~30 years old. PM replacement is due in 2025. Online replacement is considered low risk as previous experience with HD-LCV-5A21 failing open has shown that there is no significant impact to the 5A heater or HP turbine, though extraction flow to the heater would be reduced as flow increases through the preseparator drain tanks. <I> **** Actions Taken **** Discussed with AOV engineer. <N> **** Equipment Description **** W -501- - - -MCR | 02-00-HD-LIC-5A21
401274 | CR | 20191112 | CAQ | D | RB 606' UV detector trouble alarm | N | N |  | N | YES | <D> **** Detailed Description **** The reactor building 606' uV fire detector trouble alarm comes in multiple times a day. This requires dispatching an operator to confirm no fire exists and reset the detector alarm, costing both manhours and dose. Request craft investigate and repair the cause of this alarm. <I> **** Actions Taken **** Notified SM. <N> **** Equipment Description **** RB 606' | 02-00-FP-UVD-19A,02-00-FP-UVD-19B
401275 | CR | 20191112 |  | 4 | Wrong version displayed on PPC U12 status screen |  |  |  | N | YES | <D> **** Detailed Description **** During review of final configuration for DMDS updates as a part of the ACUMEN project (EC17398), it was observed that the U12 status screen (status.exe) was showing the previous version number. Review of the WO installation documents show the step to update that screen was missing. The update to the screen was just to update the displayed version, there were no functional changes, so there is no negative impact to the current state. There is no impact to Operations. . The updated file should be installed on TDAS-CPU-VMS-WS and PPC-CPU-VMS/WS. The updated files are already included on the hard drive containing the approved code, the executable just needs to be installed. No reboot or downtime is necessary for installation. <I> **** Actions Taken **** Generated CR and WR | 02-00-PPC-CPU-VMS/WS,02-00-TDAS-CPU-VMS/WS
401276 | CR | 20191113 | CAQ | D | FP-V-395 has a leak | N | Y |  | N | YES | <D> **** Detailed Description **** FP-V-395 is leaking approximately 1 drop every 2 seconds. The leak is located between the valve and the pipe it is bolted to. This valve is vertically mounted and the leak is on the top flange. This valve is located in the TG 441 North of the Main Condenser in the stairwell. (It is the main stand pipe isolation). | 02-00-FP-V-395
401277 | CR | 20191113 |  | 4 | Cond-V-1021 has a packing leak | N | N |  | N | YES | <D> **** Detailed Description **** Cond-V-1021 has a packing leak. It is located in the heater bay 471 TG. This can be observed on camera: Turbine Building 471, camera TG/10. The Camera is between the Evaps. Pan west and look for a small valve about 6 feet from floor on the end of the Evap. It is a vent off LS -32BL. You must zoom in to read the label part of the EPN is obstructed. The leak is difficult to see and intermittent. This steam leak appears to be small enough to fix with packing adjustment. It does not appear large enough to have damaged the valve or blown out the packing. | 02-00-COND-V-1021
401278 | CR | 20191113 |  | 3 | Radwaste Processing Challenges | N | N |  | N | YES | <C> Reviewed ANON CR for SCWE content per SWP-CAP-01, moved to CR-SRO for review. <D> **** ANONYMOUS CR - Detailed Description **** The EDR and FDR processing systems are currently being challenged beyond their capacity by a number of bad water sources, including-but-not-limited-to FDR-TK-22 and the T-2 sump. In response, the current lineup is to send all water except FDR-TK-22 decant through the EDR system. As a result, the life expectancy of an EDR filter has plummeted from a week or more in days of yore to a shift or two presently. It is prudent that we identify and address all of our bad water sources. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** EDR and FDR processing
401279 | CR | 20191113 |  | 4 | Radwaste Processing Challenges |  |  |  | N | YES | <C> Reviewed ANON CR for SCWE content per SWP-CAP-01, moved to CR-SRO for review. ... Same as CR 401278 <D> **** ANONYMOUS CR - Detailed Description **** Radwaste is currently facing EDR and FDR processing challenges that are threatening to overwhelm the capacity of the system. Bad water from FDR-TK-22, T-2, and other sources have cut the life expectancy of an EDR filter from a week a more to just one or two tanks worth of clean water. It is prudent that we thoroughly identify the causes for our poor filter performance while we are still afloat. <I> **** Actions Taken **** Informed the MAIN CONTROL ROOM <N> **** Equipment Description **** EDR and FDR processing
401281 | CR | 20191113 |  | 3 | REMP air sampler found short on timer hours | N | N |  | N | NO | <D> **** Detailed Description **** During weekly filter change out on 11/12/2019, REMP air sample Station 5 located at the Baxter Substation in Franklin Country was found approximately 50 hours short on time. On 11/5/2019 at approximately 0730 power had been cut by Big Bend Electric. After speaking with a Technician, it was determined that station would be down until 11/7/2019. On 11/7/2019 it was verified that station power had been restored and sample pump was operating normally. Sampling from this location is not an OCDM Table 6.3.1-1(2) requirement or an EFSEC 332 requirement. Recommend AR to Environmental Services to determine if this should be reported as a deviation in annual REMP report. <I> **** Actions Taken **** Verified sample pump operational. Wrote CR.
401285 | CR | 20191113 | CAQ | C | Standard found out of tolerance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode 0067782 nterface Model 1110ACK-10K LOAD CELL 10K was found out of tolerance. Although this was out of tolerance the vendor certificate. CR entry delay due to employee out on leave. Please assign to CALSERV <N> Reverse trace ran and analyzed on Calcode 0067782 which is a load cell standard. The out of tolerance condition discovered during a verification of the load cell standard prior to use in the calibration lab. Standard calibrated back into tolerance prior to use after vendor calibration. Reverse trace analysis and subsequent investigation did not uncover any impact to CGS assets.
401286 | CR | 20191113 | CAQ | C | Standard found out of tolerance |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode 41678 Revere Model UPSI-25-B-S1365 LOAD CELL 25K was found out of tolerance. Although this was out of tolerance the vendor certificate. CR entry delay due to employee out on leave. Please assign to CALSERV <N> Calibration standard Calcode 41678 Revere Model UPSI-25-B-S1365 LOAD CELL 25K for found to be out of tolerance in the "Tension" mode of operation. The standard is used on CGS assets is used in the "Compression" mode which was in tolerance. The issue was discovered prior to placing the standard into service after a return from vendor calibration. The standard was calibratied back into tolerance at the lab prior to use. A reverse trace analysis was performed on the standard analyzing use prior to the vendor calibration The revese trace analysis identified that the standard, for CGS assets, was alway used in the compression mode of operation which was indentified in tolerance as a result of the as found vendor calibration. THe investigation analysis is loaded into the EDMS panel. This out of tolerance situation was analyzed to have no impact to any CGS assets calibrated using this standard.
401287 | CR | 20191113 |  | 3 | RCIC-PIS-34 Instriument Isolation Valve Position |  |  |  | N | NO | <D> **** Detailed Description **** Per PPM 3.1.6F, the instrument isolation valve for RCIC -PIS-34 is maintained in a throttled position 1/4 turn. A preliminary review of other Barton pressure indicating switches isolation valve position revealed some inconsistent practices. For example, LPCS-PIS-5 isolation valve is also throttled 1/4 turn open but RHR-PIS-22A/B/C isolation valves are maintained full open (see PPM 3.1.6 series procedures). . This CR should be evaluated, with some industry benckmarking, to understand common practices for instrument isolation valve position control. The overwhelming position for instrument isolation valves is normally full open. Why we are throttling a few instrument isolation valves should be better understood and documented. <N> Throttling to 1/4 turn open is to help dampen pressure spikes to the PIS instrument. The instrument line should have a snubber installed. PPM 3.1.6 and 10.27.87 say to leave the valve 1/4 turn open, but do not explain why. The IMDS also does not address the 1/4 turn open.
401288 | CR | 20191113 |  | 4 | Ground Erosion Under Asphalt |  |  |  | N | NO | <D> **** Detailed Description **** There is a small area on the roadway between Bldg 35 and the Kootenai Bldg where the ground has eroded away under the asphalt. It is a large enough area that it would collapse if a vehicle was driven over it. Location is about 10 ft West of where a recent repair was made to the asphalt in front of Bldg 35 (Klickitat). Photos attached in EDMS. <I> **** Actions Taken **** Notified facilities. Placed orange cone over affected area.
401291 | CR | 20191113 |  | 4 | Records Sent to Doc Control Not Listed on Transmittal |  |  |  | N | NO | <D> **** Detailed Description **** For Trending Only - Records submitted to Doc Control by Standards Lab were not listed on Transmittal Form. <I> **** Actions Taken **** Notified sender to correct issue, wrote CR. <N> I retrieved the missed documents from the stack of records submitted to Records and resubmitted the transmittal and documents to records.
401292 | CR | 20191113 |  | 4 | LIGHTING DEFIECIENCIES | N | N |  | N | YES | <D> **** Detailed Description **** While conducting a procedural revision review, lights in the locations listed below in RX 548' were noted as non- functional or deficient. In addition, lighting inside all Fume Hoods in Chemistry Lab, RW 487', need to be replaced. <N> **** Equipment Description **** CMS-SR-20 room (behind Door 514), step on riser to left of sample rack skid, look up to the overhead. CMS-SR-21 room (behind Door 511), central overhead fixture in front of sample rack skid. CMS-SR-21 room (behind Door 511), step on riser to left of sample rack skid, look up to the overhead. Southeast corner, approaching SLC berm, close to HVAC with labels P-DIV-2, 5417, 5015, and 5416. Southwest corner, near contaminated area as you approach the SW elevator.
401293 | CR | 20191113 | CAQ | D | FP-P-1 did not start | N | Y |  | N | YES | <C> CR reopened to cross reference additional WP 02154736, marked completion required box, then taken back to complete <D> **** Detailed Description **** During the performance of WO 02118127-10 SOP-FP-START engine would not start. Vendor recommended to roll the engine manually and to ensure no observable binding issues are present. Coordinated with operations to hang clearance to perform vendor recommendations. <I> **** Actions Taken **** Notified operations, management and wrote CR and work request to perform task. | 02-00-FP-P-1
401295 | CR | 20191113 |  | 4 | TO-DMS-1 sight tube is dark and cannot be read | N | N |  | N | YES | <D> **** Detailed Description **** The sight tube located on the side of TO-DMS-1 is dark, opaque, and unreadable. See images in EDMS. Replace the clear flexible tubing with new, clear tube. <I> **** Actions Taken **** autogenerated WR to perform replacement of clear tubing <N> **** Equipment Description **** Lube oil reservoir room, mounted on west wall above tank | 02-00-TO-DMS-1
401296 | CR | 20191113 |  | 4 | TG-EF-1, Bently Nevada vector filter incorrect readings | N | N |  | N | YES | <D> **** Detailed Description **** TG-EF-1, the right most module of the Bently Nevada turbine supervisory system, is displaying erroneous data on the MCR panel (H13-P820, Board B). There are several discrepancies with the data and it does not match the information provided on the analogue modules nor the information collected by the OEM computer attached to the system. The values being shown include: 1. negative numbers for vibration level on some bearings, 2. phase angle in excess of 360 degrees, and 3. Negative phase angles on occasion. <I> **** Actions Taken **** discussed with supervisor | 02-00-TG-EF-1
401299 | CR | 20191113 |  | 3 | Low Nitrite concentration in Service Building Heater | N | N |  | N | NO | <D> **** Detailed Description **** During performance of monthly sample of Service Building Heater, discovered that the Nitrite concentration was ~ 0ppm, resample and analysis resulted in the same results <I> **** Actions Taken **** Informed supervision, generated CR. <N> **** Equipment Description **** 422' Service Building, south west.
401302 | CR | 20191113 |  | 4 | MT-ELEV-3 machine room phone needs replaced | N | N |  | N | NO | <D> **** Detailed Description **** The phone in the Turbine Bldg Elevator machine room does not function properly. The earpiece is not loud enough to hear and the phone and cord are brittle from age. The phone number is # 2701 <I> **** Actions Taken **** Initiated CR <N> **** Equipment Description **** MT-ELEV-3 machine room, TG 518'
401303 | CR | 20191113 |  | 3 | MD-V-84 degradation may be impacting hotwell iron levels | N | N |  | N | YES | <D> **** Detailed Description **** MD-V-84 degradation may be contributing to hotwell iron levels and CFD run times. Recent thermal performance and AOV program investigation/discussion indicate that MD-V-84 is likely stuck nearly full open. AR 400985 previously identified that the opening of MD-V-87 was a potential source of increased hotwell iron levels. Chemistry sample data will confirm/refute this since the valve was closed on 11/6/2019. MD-V-84 leak-by has been significant since at least 2017 when cycle isolation monitoring was installed. However, after partial completion of R24 WO 02118045, leak-by increased further. The most recent thermal performance estimate is that MWe losses have approached the theoretical maximum for this valve (full open) of 5.3 MWe. Recent field investigation by AOV program owner also indicates that this valve could be fully open (CR 399343). Recommend troubleshooting of this valve during upcoming downpower or planned turbine maintenance window (WR initiated). WO 02146127 for replacement of MD-V-84 is coded FOB, however full replacement does not appear necessary based on R24 inspection during WO 02118045. Recommend action to planning to revise WO. <I> **** Actions Taken **** Discussed issue with AOV and Thermal peformance program owners and relevant supervisors. <N> **** Equipment Description **** T -476- - -B7/7.9 - | 02-00-MD-V-84
401307 | CR | 20191113 |  | 3 | PHSC presentations being requested not defined in procedure |  |  |  | N | NO | <D> **** Detailed Description **** There is no guidance for generating presentations that are being required for PHSC meetings. As part of the DES-2-9 process an AR is screened and evaluated for a project and it is taken to PHSC for review. It is being required that presentations be generated that are not required by procedure prior to the meeting. The requirement and content for this presentation should be incorporated into DES-2-9 as well as the storage for the presentation. This will streamline the process and will allow all work to be completed during the evaluation process rather than well after all evaluation paperwork has been completed.
401308 | CR | 20191113 |  | 3 | CRD-P-SPAREMOTOR not available to walkdown |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** electricians found the Spare CRD Motor in Bldg 78 that is still in the shipping container. This work is on the upcoming schedule as this discovery is part of the T-3 walkdown list. The UTC 358339 (CAT ID 65004366) needs to have power connected to the space heater and oil in the bearing reservoirs. The PM to rotate the shaft and inspect the motor cannot be performed until this motor is uncrated and moved to an accessible area. Reference WO#02145995-01 <I> **** Actions Taken **** Notified Supervisor, Write CR and WR <N> **** Equipment Description **** CRD-P-MSpare currently located in warehouse Bldg 78 . Motor assembly has been removed from its shipping container and placed at B-188 in an accessible area. P. Barnes 11/21/19 no furthur action required from mechanical maintenance.
401309 | CR | 20191113 |  | 4 | CTMA-FL-1A | N | N |  | N | YES | <D> **** Detailed Description **** Cooling Tower Electrical Building #1, CTMA-FL-1A Filter Dirty light is lit. Recommend clean/replace filter. <I> **** Actions Taken **** Supervision Notified CR/WR Generated | 02-00-CTMA-FL-1A
401311 | CR | 20191113 |  | 4 | CTMA-FL-2A | N | N |  | N | YES | <D> **** Detailed Description **** Cooling Tower Electrical Building #2, CTMA-FL-2A Filter Dirty light is lit. Recommend clean/replace filter. <I> **** Actions Taken **** Supervision Notified CR/WR Generated | 02-00-CTMA-FL-2A
401312 | CR | 20191113 |  | 3 | HCO-V-W61 is not found in SOP-AS-LU. |  |  |  | N | NO | <D> **** Detailed Description **** HCO-V-W61 has been tagged in eSoms and has no restoration position in our procedures. <I> **** Actions Taken **** Wrote CR.
401313 | CR | 20191113 |  | 4 | Large unidentified steam leak between 6A and 6B FWHs | N | N |  | N | YES | <D> **** Detailed Description **** There is an S5 steam leak between feedwater heaters 6A and 6B in the heater bay. Leak is visible on cameras TG 17 and TG 21. Leak appears to be coming from 6A side. <I> **** Actions Taken **** Informed SM, updated FLM map | 02-00-RFW-HX-6A
401314 | CR | 20191113 |  | 3 | Eyewash Station #13 Exceeded Inspection Window | N | N |  | N | NO | <C> MRT Change: CR 401314 moved from 4/Trend Repair to Severity 3 assigned to AR-MNTPROG. Document the actions taken. <D> **** Detailed Description **** During the hazardous waste inspection on the Radwaste 437', it was noted that the last inspection of Eyewash Station #13 was 9/26/2019. This is outside of the monthly inspection manufacturer requirement. The unit was pressurized and appears to be in good condition, but should be inspected to verify it's ready to use. <I> **** Actions Taken **** Notified E&RP Supervisor, initiated CR. <N> **** Equipment Description **** Eyewash Station #13 on Radwaste 437'. Near safety shower. EYEWASH STATION IS NOW CURRENT WO 02142762-01 PM PERFORMED. PEB 11/24/19
401315 | CR | 20191113 |  | 4 | FP-PI-P82/2 gauge not reading system pressure | N | N |  | N | YES | <D> **** Detailed Description **** while conducting PMT on FP-V-P82/750, noticed gauge FP-PI -P82/2 was reading low, need to change out gauge <I> **** Actions Taken **** notified ops, maintenance management and wrote cr <N> **** Equipment Description **** DG3 mezzanine 453 Preaction 82 is a non-essential fire sprinkler suppression system. FPSI 19-0286 to address clapper not resetting (WR 29152712) | 02-00-FP-PI-P82/2
401316 | CR | 20191114 |  | 4 | FP-V-P82/767 did not isolate when changing Press indicator | N | N |  | N | YES | <D> **** Detailed Description **** when changing out failed pressure indicator (FP-PI-P82/2) per work request 29152710, received System 82 PreAction fire alarm, caused by the leaking Pressure indicator isolation valve, FP-V-P82/767 <I> **** Actions Taken **** Informed ops, maintenance management, and wrote CR/WR <N> **** Equipment Description **** D455 P1/3.6 Non-essential pre-action fire suppression system. | 02-00-FP-V-P82/767
401317 | CR | 20191114 |  | 4 | Preaction 82 Priming Pressure not available | N | N |  | N | YES | <D> **** Detailed Description **** During performance of SOP-FP-OPS, section 5.5 for Preaction 82, priming pressure as indicated on FP-PI-P82/2 remained at zero after opening FP-V-P82/764. Plunger did not hold clapper valve in position and could easily be pushed in which indicates no pressure being supplied. Drain solenoid was not energized and no water flowed from drains with priming valve open. Possible cause could be clogged strainer, FP-ST-P82/1. <I> **** Actions Taken **** Isolated preaction system 82 and closed priming water valve to prevent spurious actuation. Faceplated on clapper valve was reinstalled and CRS notified of out of position valves needing configuration control. FP-V-P82/750 and FP-V -P82/764 are closed. <N> P82 is a non-essential fire suppression system. FPSI 19 -0286. | 02-00-FP-V-P82/750
401318 | CR | 20191114 | CAQ | D | Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 239kv B: 239kv C: 239kv E-TR-B A: 118kv B: 118kv C: 118kv The following sensors were tripped and are reset: J7 and J12 BPA reports the following: a. Cause was Ashe-Slatt #1 500kv b. Relaying involved a single pole c. No damaged equipment d. Line reclosed e. No emergent outage needed i. 0137 j. 500kv k. No RAS <N> 500kv Ashe-Slatt line feeds ASHE north/south bus, does not affect TR-S or TR-B Operability.
401323 | CR | 20191114 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0059155 Mitutoyo Depth Mic- model 129-144 found OOT & adjusted within specs. Not used during Calibration cycle. DEF #7366A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
401324 | CR | 20191114 | CAQ | D | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 238kv B: 235kv C: 238kv E-TR-B A: 118kv B: 118kv C: 118kv The following sensors were tripped and are reset: J7, J11, J12 BPA reports the following: a. Cause was Ashe-Slatt #1 500kv lock out, b. Relaying involved a multiphase pole c. Damage to equipment is being assessed, d. Line is locked out e. Linemen are at fault, clearance being generated by BPA, f. NO, g. NO, h. NO i. 0452 , j. 500kv, k. NO <N> ASHE-SLATT 500kv line feeds to 500kv ASHE north and south bus, does not affect TR-S or TR-B Operability.
401325 | CR | 20191114 |  | 3 | Security Equipment Reliability Trend |  |  |  | N | NO | <D> **** Detailed Description **** Security equipment reliability in search equipment performance indicator continues to trend towards yellow over the past year with a period of time coming up with typically higher failure rates. <I> **** Actions Taken **** Notified Security Management, initiated CR for trending purposes.
401327 | CR | 20191114 |  | 3 | Foreign Material Found in FD-SUMP-T2 |  |  |  | N | YES | <D> **** Detailed Description **** During performance of WO 02147739 01, Foreign Material was found in FD-SUMP-T2, which included adjustable wrench and a couple of electronic devices. Pictures are in EDMS. <I> **** Actions Taken **** Informed supervision Laborers are determining the best way to remove the items <N> See cross referenced CR 401460 for additional information regarding the retrieval of items found in the sump. | 02-00-FD-SUMP-T2
401328 | CR | 20191114 |  | 3 | 12.5.44 procedure enhancement |  |  |  | N | NO | <D> **** Detailed Description **** 12.5.44, RCS Dissolved Hydrogen and Oxygen Monitoring, procedure possible improvements noted and passed on to specialist. <I> **** Actions Taken **** specialist informed/ emailed suggested improvements
401330 | CR | 20191114 | CAQ | D | CRD-HCU-2239 High Water | Y | N |  | N | YES | <D> **** Detailed Description **** MCR received â€œRod Accumulator Troubleâ€ alarm. Alarm was due to high water level. Ops 2 drained the accumulator per SOP-CRD-HCU and the alarm is clear. | 02-00-CRD-HCU-2239
401331 | CR | 20191114 |  | 4 | HCO-T-W54 steam leak has worsened | N | N |  | N | YES | <D> **** Detailed Description **** HCO-T-54 (WOA-AH-4 Heating Steam trap) steam leak has become signigicantly worse. (Reference AR 389748 for past write up from early 2019) A 1ft plum is discharging from the top of the trap and condensing on adjacent white iron. The catch that has been in place, is no longer adequate. A metal bucket was placed above the trap to direct condensation into the existing catch. Please repair trap and/or install a more adequate catch/diverter. The steam leak is not impacting any adjacent equipment. See attached EDMS for pic. <I> **** Actions Taken **** Informed SSS <N> **** Equipment Description **** RW 507 | 02-00-HCO-T-W54
401334 | CR | 20191114 | CAQ | D | Thermal Detector inadvertently struck in DG1 | N | Y |  | N | YES | <D> **** Detailed Description **** Craft inadvertently struck thermal detector FP-THD-79/3 while changing out flourescent fixtures to new LED fixtures under WO #02153581-01. No trouble or fire signal was sent to control, but craft noticed that FP-THD-79/3 was not seated properly and needs to be corrected. <I> **** Actions Taken **** Craft stop work and immedieately notified control and supervision of the bump thermal detector. Supervisor notified Control Room and Engineering, initiated CR with Work Request to re-seat the thermal detector FP-THD-79/3 | 02-00-FP-THD-79/3
401335 | CR | 20191114 | CAQ | D | Leakby on TEA compensatory sample cart | N | N |  | N | YES | <D> **** Detailed Description **** The TEA compensatory sample cart has leak by on the sample line flow indicator and air is being drawn in through the seal where the flow indicator is inserted into the sample line. This leakby renders the compensatory sample cart useless, as the pump is drawing air from the room on RW 525 instead of from the TEA exhaust through the TEA particulate/iodine filters. Normal flow indication through the sample line of the cart is approximately 60-100 LPM, but with the leakby the cart indicates over 600 LPM. The seal around the sample line flow indicator on the TEA temporary sample cart needs to be repaired before it can be utilized again as a compensatory measure. <I> **** Actions Taken **** Investigated source of eroneous flow indication. Contacted supervisor, maintenance, and control room. <N> **** Equipment Description **** TEA compensatory sample cart, located on RW 525.
401336 | CR | 20191114 |  | 3 | OE -Fatality at LaSalle Generating Station |  |  |  | N | NO | <D> **** Detailed Description **** On 11/12/19, there was a diver fatality while performing maintenance activies at the lake screen house at LaSalle Generating Station. This CR is being generated to initiate Stop Work Activities in accorcance with SWP-CAP-08 until lessons learned from this event can be evaluated for applicability to CGS. Recommend Non-CAQ 3 to AR-PERFIMP to track OE Evaluation <I> **** Actions Taken **** CR initiated at PGM request to issue Stop Work Order
401337 | CR | 20191114 |  | 4 | E-TR-M3 DIGITAL TEMP DISPLAY PARTIAL FAILURE | N | N |  | N | YES | <D> **** Detailed Description **** CHANNEL 4 OF THE DIGITAL TEMPERATURE DISPLAY APPEARS TO BE FAILING. IT IS ONLY READING THE NUMBERS PARTIALLY. <I> **** Actions Taken **** INITIATED CR, INFORMED MCR | 02-00-E-TR-M3
401339 | CR | 20191114 | CAQ | C | LD-E/S-600 Exceeds rated voltage accuracy | Y | N |  | N | YES | <C> Per MRT feedback received 11/19/2019, CR was reopened and dispositioned to C / SENSSS to ensure a spare power supply is procured. <D> **** Detailed Description **** During troubleshooting the RWCU increasing delta flow issue (AR 360065, 364889, 373390, 376273) the 24Vdc power supply that supplies all of the RWCU delta flow instrumentation (Flow transmitters, SRU, Square rooters, Summer, Flow switches) was reviewed. The historical voltage readings from 2007 to 2019 vary from 25.9Vdc to 24.05 Vdc, with many readings above 25.2 Vdc. Per the original GE Leak Detection System Instrument Data Sheet (see CVI 02E31-05,8) for the system, the rated accuracy of this power supply is +/-5% (22.8 to 25.2 Vdc). The safety related equipment supplied by the power supply (Flow transmitters, SRU, Square rooters, Summer, Flow switches) have a normal design power supply voltage requirement of 22 to 26Vdc and a maximum of 20 to 28Vdc, so the voltage is acceptable for the operation of the system components. It is unknown why the power supply would be high, or if it has another degradation mechanism that could potential affect the delta flow indication. The drift in delta flow indication is towards the trip setpoint (i.e. drift is in conservative direction) and there is no indication that the system would not meet its design function to isolate the RWCU system on high delta flow. The instruments have been calibrated and surveilled several times and show no indication that they are not functioning normally. The power supply appears to be original equipment. Failure of this power supply will cause a shutdown of the RWCU system. We do not have a spare power supply. Recommend power supply replacement. | 02-00-LD-E/S-600
401340 | CR | 20191114 | CAQ | D | (Doble) Updated and initial SFRA and leakage reactance tests |  |  |  | N | YES | <D> **** Detailed Description **** As part of the Doble Transformer condition assessments for E-TR-S, B, N1, and N2 Doble is recommending Sweep Frequency Response Analysis (SFRA) and leakage reactance testing be performed on each transformer. This testing is being recommended as part of their report to better quantify condition of each transformer. This CR has no impact on operation of the transformers. This CR is being written up to document the recommendation from Doble and to generate WR/WOs to perform the work when the transformer is out of service. | 02-00-E-TR-B,02-00-E-TR-N1,02-00-E-TR-N2,02-00-E-TR-S
401342 | CR | 20191114 | CAQ | D | (Doble) Increase performance of diagnostic testing for trans |  |  |  | N | YES | <D> **** Detailed Description **** As part of the Doble condition assessment review it is being recommended by Doble to perform diagnostic testing more frequently on E-TR-S, B, N1 and N2 based on age. The purpose of this CR is to document the need for the change in frequency for the diagnostic testing of these transformers. The change in frequency has no impact in operation of the transformers and this CR has no impact on operation of these units. Generated AR-SMS 401341 to change frequency for diagnostic PMs on each impacted transformer. <N> This CR documents a vendor recommendation to be evaluated and does not directly affect component operabilty. | 02-00-E-TR-B,02-00-E-TR-N1,02-00-E-TR-N2,02-00-E-TR-S
401344 | CR | 20191114 | CAQ | D | (Doble) Update oil testing PMID for transformers |  |  |  | N | NO | <D> **** Detailed Description **** As part of the Doble condition assessment review it is being recommended by Doble to incorporate additional oil testing for transformers into PMID 21625-02. The recommendation is to test all transformers for furanic content, metal in oil, corrosive sulfur and PCBs. AR-SMS 401343 was initiated to update PMID 21625-02. <N> This CR documents a vendor recommendation to be evaluated and does not directly affect component operabilty.
401346 | CR | 20191114 | CAQ | C | (Doble) Determine cause for elevated oxygen content in DGA s |  |  |  | N | NO | <C> Per MRT feedback received 11/19/2019 this item should be CAQ. <D> **** Detailed Description **** (Doble) Determine cause for elevated oxygen content in Transformer DGA samples. This could be coming from sample process or potentially a leak on the transformer. This CR will evaluate the sampling process as well as look into any potential leaks on the transformer to try and reduce the level of oxygen being see in transformer DGA samples. The increase in oxygen has no impact on operation of the transformers. This CR will look at the cause and reduce the oxygen content in the oil for each transformer. Recommend assignment to System engineering. <N> This CR documents a vendor recommendation to be evaluated and does not directly affect component operabilty.
401347 | CR | 20191114 |  | 3 | VBModule utility testing impact to Prod Active Directory |  |  |  | N | NO | <D> **** Detailed Description **** While performing testing between VBModules and AS9, a utility unexpectedly updated production Active Directory. <I> **** Actions Taken **** IS team corrected the overwritten data and initiated this CR. Addtional task needed to evaluate how to isolate the testing environment to ensure the utility does not impact production data in the future. <N> Recommend CAT 3 to ITMGMT.
401348 | CR | 20191114 | CAQ | C | (Doble) Atmospheric gas pattern change for E-TR-S |  |  |  | N | YES | <D> **** Detailed Description **** Doble recommends investigating the cause for the atmospheric gas pattern change being see in DGA samples since the 2013 degassing of E-TR-S along with the reason for large fluctuation in oxygen and nitrogen. This condition has no impact on operation of the transformer but correcting this condition will ensure that the transformer can be operated until it is scheduled to be replaced on the LRP. Recommend assignment to System engineering. <N> This CR documents a vendor recommendation to be evaluated and does not directly affect component operabilty. | 02-00-E-TR-S
401349 | CR | 20191114 | CAQ | C | (Doble) Repair source of atmospheric leak for E-TR-N1 |  |  |  | N | YES | <D> **** Detailed Description **** Doble recommends identifying the cause of the atmospheric leak on E-TR-B and repair. The doble transformer condition assessment for E-TR-B identified elevated oxygen being seen at the oil analysis lab. Dobleâ€™s recommendation is to determine the cause of the increase and repair at earliest convenience. This condition has no impact on operation of the transformer but correcting this condition will ensure that the transformer can be operated until it is scheduled to be replaced on the LRP <N> This CR documents a vendor recommendation to be evaluated and does not directly affect component operabilty. | 02-00-E-TR-B
401350 | CR | 20191114 |  | 3 | Engineering Procedure CIVES-2 Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Engineering procedure CIVES-2, Design and Modification of Electrical Raceway and Support Systems provides information, guidelines, and direction for the design and modification of electrical raceway, consisting of cable trays, conduits, wireway gutters, boxes, and their support systems. TM-2043 is to identify Augmented Quality systems, structures, and components (SSC's) subject to requirements affecting quality as a result of NRC commitment or Columbia Generating Station position. It also provides seismic category, and MEL (D041) requirements for Augmented SSCâ€™s. Since TM-2043 is not referenced in CIVES-2, the requirements of TM-2043 can be easily missed and therefore, this CR suggested that CIVES-2 should be revised to include reference to TM-2043. This is a procedural issue and no equipment operability is impacted. <I> **** Actions Taken **** Discussed with supervision and wrote this CR. <N> recommend that this be a non-CAQ severity level 3 AR-CR assigned to AR-DMC as the group is the owner of CIVES-2.
401351 | CR | 20191114 |  | 4 | Glass globe (vapor guard) left off when fixtures relamped | N | N |  | N | NO | <D> **** Detailed Description **** The glass globe guard left off of fixtures when they were relamped. The globe is part of the vapor tighrt system for these fixtures. Ref drawing E 837 and associated lighting floor plans. <I> **** Actions Taken **** Wrote CR. <N> **** Equipment Description **** Valve and pipe chase areas in the power block.
401352 | CR | 20191114 | CAQ | C | PPMs 10.20.18 & 10.20.22 torque discrepancies | Y | N |  | N | NO | <D> **** Detailed Description **** The torque for DLO-P-6 and DLO-P-12 motor mounting fasteners in PPMs 10.20.18 and 10.20.22 are different than values stated in PPMs 10.20.14 and 10.20.17. It appears that the pumps may have been replaced but the revision descriptions do not provide specifics. The torque was lowered to 5 ft-lbs. The current torque value in 10.20.18 and 10.20.22 is 15-16 ft-lbs. <I> **** Actions Taken **** The HPCS diesel outage is in January, so request for correct torque values be expedited. <N> This CR documents a discrepancy between DLO pump motor mounting bolt torque values. Regardless of which torque values were applied there is a reasonable assurance of Operability of DLO-P-6 and DLO-P-12. DLO-P-6 and DLO-P-12 are Operable. Depending on which torque values were actually applied to the motor mounts the pumps could be non-conforming.
401353 | CR | 20191114 |  | 4 | Ipad cord stolen from office |  |  |  | N | NO | <D> **** Detailed Description **** An Ipad cord was removed from my office outside of normal working hours. My battery was at 97% on the morning of 11/14/19, but I am unsure when the cord disappeared. <I> **** Actions Taken **** Initiated CR.
401354 | CR | 20191114 |  | 4 | Training Record was submitted to Records without documents |  |  |  | N | NO | <D> **** Detailed Description **** During the indexing process it was discovered that a training record was submitted to records without the supporting documents. <I> **** Actions Taken **** TAR was pulled from indexing and the supervision was notified. This CR was written and the training department was notified for return of the record for correction. <N> This TAR submitted did not contain accompanying documentation because it was a credit to a student for attending classroom HP continuing cycle training, which is not to be sent to records. This was also a record from March 2019 time frame which is being processed in November 2019. Individual submitting TARs such as this to be sent to Records Control has been coached, however legacy issues may exist as Records processes previously submitted Records Transmittals.
401355 | CR | 20191114 |  | 4 | Chemistry in need of backup compensatory cart at TEA | N | N |  | N | YES | <D> **** Detailed Description **** Chemistry has faced significant challenges due to three failures of the TEA temporary sample cart in the last three months; see reference CRs. The TEA temporary sample cart is a compensatory measure when TEA-SR-26 is non-functional. The cart maintains sample flow though the particulate and iodine filter units (ODCM function) and provides effluent flow to the â€œfrisker in the bricksâ€ (EP function). The cart is a simple device constructed in house and consists mostly of a pump, flow meters and four valves. Chemistry needs a backup compensatory cart to prevent a single failure of this device from challenging the plants ability to meet ODCM, EP, and work scheduling commitments. <I> **** Actions Taken **** Spoke to supervisor, reviewed recent CRs. <N> **** Equipment Description **** TEA compensatory sample cart on RW 525
401356 | CR | 20191114 |  | 4 | PeopleSoft unavailable |  |  |  | N | NO | <D> **** Detailed Description **** PeopleSoft application was unavailable temporariily at 1800 on 11/13/19. USers could not logon for approximately 1 hour. <I> **** Actions Taken **** PS analyst rebooted the application server and access was restored. Recommend NCAQ4 to ITMGMT
401358 | CR | 20191114 |  | 4 | Ops Training record was submitted to records w/o documents |  |  |  | N | NO | <D> **** Detailed Description **** During the indexing process it was discovered that an Operations TAR was submitted to records without the supporting documentation. <I> **** Actions Taken **** The TAR was pulled from indexing and the supervision was notified. This CR was written and the Ops training department was notified for return of the record for correction. <N> Operations Training management evaluated and determined that this record, being now 18 months old, is determined to be lost and cannot be duplicated, as per SWP-REC-02, section 4.3.4 and section 4.3.6. The risk is low as the individual whose record of qualification this is, is no longer in the Operations department nor performing this work, and this related qualification is inactive. No further action needed.
401360 | CR | 20191114 |  | 3 | SOP-CW-OPS revision needed |  |  |  | N | NO | <D> **** Detailed Description **** SOP-CW-OPS section 5.7 revision needed to include new NPDES instrumentation for monitoring CW blowdown pH. <I> **** Actions Taken **** Confirmed with Chemistry supervision and notified Ops Procedure supervisor. The revision language has been placed in the EDMS document file of this CR.
401362 | CR | 20191114 |  | 3 | Consider clarification for PPM 1.10.11 |  |  |  | N | NO | <D> **** Detailed Description **** Consideration should be given to modify the definition of a Defect in PPM 1.10.11 (pg.6-7) as there is some difference in interpretation. The section should be restructured/reworded in order to better align with the intent of the regulatory definition of a Defect given in 10 CFR 21. . This issue is administrative in nature. <I> **** Actions Taken **** Discussed with Regulatory Affairs Manager.
401366 | CR | 20191114 |  | 4 | TSC Emergency EXIT sign Burned out |  |  |  | N | YES | <D> **** Detailed Description **** TSC emergency exit sign (west side) lamp is not illuminated. <N> **** Equipment Description **** TSC exit sign (west side)
401369 | CR | 20191114 | CAQ | C | FP-B0-1B currently wired to BATT#1 AMP meter (B1) in FP-CP-1 | N | Y |  | N | YES | <C> Per MRT feedback received on 11/19/2019, this item was dispositioned to C/TEFP to validate if there is a configuration management issue or a labeling issue. <D> **** Detailed Description **** When taking Batter charging current, battery FP-B0-1B doesnâ€™t line up with batters #2 labeling on FP-P-1 control panel. Per EWD-62E-027, 24VDC BATT #2 (FP-B0-1B) should be tied to B2 amp meter. Currently indication from BATT #2 is coming from FP-B0-1A. Current wiring in the field dos not match plant print. Suggest inspection of wire termination location and or EPN labeling on battery base. <I> **** Actions Taken **** FP-B0-1B currently wired to BATT#1 AMP meter (B1) in FP -CP-1 or EPN labeling issue. Not an operability issue | 02-00-FP-B0-1B,02-00-FP-BO-1A
401371 | CR | 20191114 | CAQ | D | E-B0-1B | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** E-B0-1B HAD LOW SPECIFIC GRAVITY READINGS. ACCEPTABLE AVERAGE IS 1.205 AND THE MEASURED AVERAGE WAS 1.166 <I> **** Actions Taken **** PLACE ON EQULIZE SUPERVISOR AND CRS <N> **** Equipment Description **** E-B0-1B
401372 | CR | 20191114 |  | 4 | Oscillograph start 500kv McNary/Coyote Springs | N | N |  | N | NO | <D> **** Detailed Description **** Oscillograph start @2333 on 11/14/19. Momentary relaying on McNary Coyote Springs 500kv line. <I> **** Actions Taken **** Followed ARP.
401373 | CR | 20191115 |  | 3 | CW-V-62 Request for Permanent Inadvertent Contact Device |  |  |  | N | NO | <C> Per MRT feedback received on 11/19/2019, this CR was dispositioned to AR-OPSST to review potential permanent solution for PCSC <D> **** Detailed Description **** CW-V-62 is a ball valve near ground level and obscured by piping above. It is suceptible to being inadvertently operated and now has a temporary inadvertent contact device installed. This valve is a sample point for the Dehalogenation Skid. Of note, the permanent device must be capable of being installed without the use of zip-ties as the valve is in the Circulating Water Building near the roll-up door. <I> **** Actions Taken **** Installed temporary inadvertent contact device
401374 | CR | 20191115 | CAQ | C | LCS 1.8.6.1 required CR for not meeting completion time. | N | Y |  | N | YES | <C> Per MRT feedback received on 11/19/2019, this cr has been dispositioned to C / SEEIC to review the LCS and ensure it has all the information for the battery testing information. <D> **** Detailed Description **** LCS 1.8.6.1 requires a CR for not meeting completion times per condition "O" . Completion times not met due to battery E-B0-1B being on equalize following performance of ESP -B01B-F101 60 MO BATTERY TEST. This is normal and expected following this test. <I> **** Actions Taken **** Generated CR | 02-00-E-B0-1B
401384 | CR | 20191115 |  | 3 | (E) WO 02138944 incorrect MTE entered and missing | N | Y |  | N | NO | <D> **** Detailed Description **** WO 02138944 incorrect MTE entered on 15.2.1 and missing MTE in Data Glance. Closed WO so current WO could be worked. Need get the correct MTE and send a hard copy of correct MTE to records. <N> Incorrect procedure is listed 10.25.1 is incorrect and should be 15.2.1.
401385 | CR | 20191115 |  | 3 | OSP-INST-H101 Reading Failed to Upload in eSOMS | N | N |  | N | NO | <D> **** Detailed Description **** While reviewing CRO 2 logs the STA/IA recognized the log entry for Fire Suppression Water supply did not populate. The expected entry would be GT 320K gallons but was not there. STA/IA and CRS checked the H101 logs (since this reading automatically populates there) and recognized the same issue on the H101. The H101 log had already been reviewed and approved by the CRS at 0947. CRS did not recognize that the reading was missing from the H101. <I> **** Actions Taken **** Informed the Shift Manager. Verified with CRO2 that fire suppression water is satisfactory (GT 320k gallons). Attempted to un-approve the H101 log and manually add the reading. This was unsuccessful and forces a reading of â€œLT 320kâ€ which cannot be changed. Inserted a note next to the log entry stating the reading is incorrect and actual value is GT 320K. Re-approved OSP-INST-H101 log at 1320. Initiated this CR for tracking and trending.
401386 | CR | 20191115 | CAQ | D | Low operating oil pressure for FP-P-1 | N | Y |  | N | YES | <D> **** Detailed Description **** While running FP-P-1 for PPM 15.3.9 section 7.11 it was noted that oil lubricating pressure started out at 65 psig and slowly lowered to about 45 psig during the 1 hour run. Per SOP-FP-START step 5.3.4 the extended run time values are 60-90 PSI for normal oil pressure. Also, step 5.2.5 requires the engine to be shutdown or oil added if oil pressure cannot be maintained greater than 30 PSI. Oil level was check after the 1 hour run and level did not change. Maintenance says it was changed from 20W to 30W for a FLEX modification. Recommend engineering evaluation for new oil pressure band for extended FP-P-1 and 110 runs. <I> Engineering review of FP-ENG-1 lubricating oil did not identify any use of 40W oil at any time. The data reviewed while investigating use of lubricating oil on FP-ENG-1 identifies that SAE 30 engine oil has always been used in the FP-ENG-1 engine. Engineering position is the engine lubricating oil is NOT the issue causing low oil pressure levels. Fuel found in the oil on 11-16-19 is the probable cause of low oil pressure. <N> Correction oil was changed from 40W to 30W | 02-00-FP-P-1
401387 | CR | 20191115 |  | 3 | Incorrect Revision of PPM 10.27.113 Performed in eWP |  |  |  | N | NO | <D> **** Detailed Description **** On 11/15/19 PPM 10.27.113 (SFP Level Indication Ch 1) was performed under an outdated revision in eWP. Performed major rev 2 instead of major rev 3. New rev requires EP notification of FPC-LIT-21A being removed from service. This was caught by the CRS while authorizing PPM 10.27.117 (Channel 2 CFT) later in the shift. CRS noticed that PPM 10.27.117 had a requirement to notify EP of FPC-LIT-21B removed from service. CRS then looked at the completed PPM 10.27.113 and discovered it had been revised to include the same requirement. PPM 10.27.113 was authorized in eWP the day before. eWP normally prevents authorizing work on an incorrect revision, requiring the work package be validated first. This may be an issue with eWP software which makes this situation error-likely. <I> **** Actions Taken **** Informed the Shift Manager. Supervisor who authorized the surveillance is not at work today and will be informed via text message. Verified there are no other changes to the surveillance on the new revision CRS determined the surveillance is satisfactory. Emailed EP to inform them FPC-LIT-21A was removed from service and restored. <N> **** Equipment Description **** eWP (Data Glance)
401388 | CR | 20191115 |  | 3 | Gaps Identified during Challenge Meeting (OPDS Closeout) |  |  |  | N | NO | <D> **** Detailed Description **** As part of preparation for the closeout inspection against NRC Bulletin 2012-01 â€œDesign Vulnerabilities in Electrical Power Systesmâ€, station management conducted a challenge meeting to assess Design Engineeringâ€™s readiness for inspection. The challenge meeting identified two gaps that need to be addressed prior to the inspection. The close -out inspection for NRC Bulletin 2012-01 is a one-time inspection utilizing NRC Temporary Instruction TI-2515/194 â€œInspection of the Licensee's Implementation of Industry Initiative Associated with the Open Phase Condition Design Vulnerabilities in Electric Power Systems (NRC Bulletin 2012-01)â€. The need for a formal self-assessment was not clearly communicated to the project team nor was it scheduled to support timely completion in advance of the inspection challenge meeting. In addition, a required presentation reflecting the design of CGSâ€™ off-site power schemes (original design and newly added Open Phase Detection System) was not finalized prior to the challenge meeting. The intent of this CR is to document these gaps and drive the completion of both deliverables as well as ensure lessons learned are captured for the organization. In addition, an action is required to confirm sufficient guidance is provided to ensure self -assessments are scheduled, tracked and completed for one-time NRC inspections as appropriate. Recommend 3 level and assignment to Design Engineering (AR-DESENG) for resolution. <I> **** Actions Taken **** Wrote CR; aligned resources to ensure both deliverables will be completed prior to NRC on-site inspection.
401389 | CR | 20191115 | CAQ | D | FP-P-1 not running as expected | N | Y |  | N | YES | <D> **** Detailed Description **** Currently the FP-ENG-1 is not performing at higher RPM (1750 rpm) the engine run satisfactory at 1720-1740rpm range. This issue could be several of thing and should be investigate when practical. Suggest to investigate fuel pump and delivery system as well as timing. The engine could starving of fuel or the timing could be retarded causing the issue found at 1750-1760 rpm. <I> **** Actions Taken **** Contact CRS, SM brought vendor to site for non-intrusive evaluation. Vendor confident engine has no issue running for 30 hour confidence run at current settings, but, recommends to investigate High rated RPM issue when practical | 02-00-FP-ENG-1
401390 | CR | 20191115 | CAQ | D | FP-P-1 Cooling Water Pressure High | N | Y |  | N | YES | <D> **** Detailed Description **** Performance of PPM 15.1.3 step 7.22 identified cooling water pressure for FP-P-1 (FP-PI-6) at 66 lbs. Indicated range is 0-66 psig at churn. <I> **** Actions Taken **** Initiated CR. Informed Shift Manager. Request evaluation. <N> **** Equipment Description **** CW Pump House | 02-00-FP-P-1
401391 | CR | 20191116 |  | 4 | Received H13-P800.C4.4-3 Oscillograph started alarm |  |  |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. Plant controller and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 238kv B: 234kv C: 237kv CR#398435 for "B" phase E-TR-B A: 118kv B: 118kv C: 118kv The following sensors were tripped and are reset: J15 BPA reports the following: a. Cause was momentary relaying Grand Coulee-Chief Jo 500Kv line; b. Relaying involved a single pole reclosing; c. No Damaged equipment; d. line reclosed; e. No emergent outage needed; f. 230kv or 115kv was not involved; g. No line equipment outage needed; h. No; i. 0128; j. 239KV, 118KV; k. No; l. N/A <I> **** Actions Taken **** Informed CRS. CR initiated per ARP
401393 | CR | 20191116 | CAQ | D | FP-P-1 30 hour run secured due to lube oil leaks. | N | Y |  | N | YES | <D> **** Detailed Description **** FP-P-1 30 hour run was secured after about 8 hours of run in, when excessive lube oil leakage was discovered. Oil has leaked from the NE cylinder head cover and the SW bottom crank case gasket. The engine was running rough ( metallic ) and oil pressure was 30 psig. ( required press. GT 30 psig IAW SOP-FP-START step 5.2.5. ). <I> **** Actions Taken **** Secured FP-P-1 IAW SOP-FP-SHUTDOWN and supervisor direction. <N> **** Equipment Description **** CWPH | 02-00-FP-P-1
401394 | CR | 20191116 |  | 4 | Security Checkpoint Electrican Receptacle | N | N |  | N | YES | <D> **** Detailed Description **** There is a broken electrical receptacle at the security checkpoint on the outer wall. This item needs to be replaced. <I> **** Actions Taken **** Initiate CR/WR. Security supervision notified. <N> **** Equipment Description **** Security Checkpoint outer wall in lane 1.
401395 | CR | 20191116 |  | 3 | Fluorescent Light Tube Cart Stored in Undesignated Area | N | N |  | N | NO | <D> **** ANONYMOUS CR - Detailed Description **** The large fluorescent light tube cart was recently parked alongside the Green Bag Trash Monitor BM-285 on RW 467', across from the tool crib. There is a Work In Progress sign that expires at the end of 2019, which is beyond the allowed duration. The location where the light cart is currently stored has already been designated and taped off for HP-EQ-42725 (Green Bag Trash Monitor). There is a sticker on the floor which states that the only equipment that is allowed to be within the taped of boundary, is HP -EQ-42725. The light cart should have it's own designated storage location, obtained and marked in the proper way. <I> **** Actions Taken **** Initiated this AR/CR. <N> CR initiated anonymously, reviewed for Safety Conscious Work Environment (SCWE) content. Moved to CR-SRO for OPS review.
401396 | CR | 20191116 |  | 3 | Editorial change needed for OSP-SGT-B701 | N | N |  | N | NO | <D> **** Detailed Description **** OSP-SGT-B701 needs an editorial change to renumber the steps on page 7. Page 6 ends with step 7.3.14, but page 7 begins with 7.3.1 instead of continuing with step 7.3.15. <I> **** Actions Taken **** CRS approved after hours editorial change IAW SWP-PRO-02. Performed pen and ink change to re-number steps IAW note in section 5.6 of SWP-PRO-02 to allow completion of the surveillance. Processed change to the native procedure document in APPW. <N> The requested action was corrected by an after hours editorial revision. OSP-SGT-B701 revision 008/001 was implemented 11/16/19.
401397 | CR | 20191116 | CAQ | C | Fuel discovered in the lube oil for FP-ENG-1 | N | Y |  | N | YES | <D> **** Detailed Description **** Following inspection of oil leakage on FP-ENG-1 the dipstick was pulled to validate oil level and it was discovered that there was fuel in the oil. The level on the dipstick indicated that level in the oil sump was past the full mark, was thinner and smelled of diesel fuel. <I> **** Actions Taken **** OCC was notified and CR generated. ENG to be removed and shipped back to vendor for repair | 02-00-FP-ENG-1,02-00-FP-P-1
401398 | CR | 20191116 |  | 3 | PPM 15.3.9 Revision | N | N |  | N | NO | <D> **** Detailed Description **** PPM 15.3.9 section 7.11.5 to 7.11.11 needs some correction. While running FP-ENG-1 as part of receiving the engine back from the vendor, Cummins, when the engine RPM was taken to 1728 RPM, FP-P-1 fire pump was unable to achieve the required 125 PSI per the PPM 15.3.9 procedure as currently written. . This condition is not a surprise to the FP System Engineer. FP-P-1 pump performance is monitored and trended. Current trending has already identified the FP-P-1 is currently at 10% degradation. The 125 PSI requirement in the procedure should be revised to incorporate a range of 112 PSI to 125 PSI. This is within acceptability of LCS SR 1.10.1.10 of 2000 GPM at 108 PSI. . This is an enhancement to PPM 15.3.9. Assign to fire protection to work with maintenance procedure writers to correct the condition. <I> **** Actions Taken **** Contacted SM and intiated CR.
401399 | CR | 20191116 |  | 4 | Urinal overflowing in Yakima Bldg (GSB) 441' | N | N |  | N | YES | <D> **** Detailed Description **** A urinal in the men's restroom located in the 441' Yakima (GSB) building was reported to not be flushing correctly and overflowing. This has been a problem in the recent past and on other occasions before the last repair. <I> **** Actions Taken **** Taped bag over urinal, cleaned up "water" on floor, initiated CR & Work Request for repair. <N> **** Equipment Description **** Men's Restroom urinal 441' Yakima (GSB)
401400 | CR | 20191116 |  | 4 | Safety Concern - Mounting device for NRRPT Plaque inadequate | N | N |  | N | NO | <D> **** Detailed Description **** The recently hung NRRPT plaque in the RP department's crew meeting room (441' Yakima/GSB) was crooked, so an adjustment was attempted. In doing so, it was realized that the relatively heavy plaque had been mounted by hanging it on a single screw head and the grrove in the particle board was worn to the point that there is no lip to prevent it from falling. The wall that it was mounted on is made of drywall and does flex, which could allow it to fall. It is not unusual for someone to be sitting or standing near or against this wall, especially during the morning D15. The plaque could fall onto someone sitting below it or standing near it. <I> **** Actions Taken **** Removed plaque from the wall and placed it in a safe location until a more robust method of mounting it can be determined and executed. Initiated this CR & attached work request. <N> **** Equipment Description **** 441' Yakima (GSB) RP Department's crew meeting room
401401 | CR | 20191116 |  | 4 | COND-CP-DM/1 bad alarm card, blown fuse | N | N |  | N | YES | <D> **** Detailed Description **** COND-CP-DM/1 bad alarm card, blown fuse This is a follow up CR to to CR #400966 and W/R # 29152511 Found bad card for COND-CP-DM/1 drop 2-6 and blown fuse Fuse- 5amp 250v, 3AG type. See EDMS for pics of fuse and card <I> **** Actions Taken **** Informed MCR, card and fuse removed | 02-00-COND-CP-DM/1
401402 | CR | 20191116 |  | 3 | First Responder Patient Transport Suggestion | N | N |  | N | NO | <D> **** Detailed Description **** When someone is injured or in need of medical attention, our only options are to use the gurney, assist them walking out on their own, or wait for Hanford EMT's to bring in their own gurney. A significant amount of the time, the individual does not require Cervical Spine Stabilization and providing a way to safely and more easily move an individual out of the RCA or building to receive treatment, is desireable. Another legitimate consideration is the psyche of the patient and how being seen and transported on a gurney affects them. Most of them do not want to do it. Manuevering a gurney, especially in an elevator, is also not something to look forward to. A suggestion to purchase a few basic wheel chairs and stage one at the HP AAP & PAP, and the PEC has many supporters amongst the First Responders. It would allow more dignity and position of comfort to the patient and be more efficient. <I> **** Actions Taken **** Suggested the idea during multiple Post Fire Brigade Drill / Man Down Critiques. Discussed with Trainers and co-First Responders. Initiated this AR/CR as a suggestion. This may also allow us to eliminate gurneys, which are quite expensive and Hanford brings their own anyway. We no longer package patients.
401403 | CR | 20191116 |  | 4 | D.C. power failure alarm at COND-CP-DM/1 ann. panel. | N | N |  | N | YES | <D> **** Detailed Description **** D.C. Power failure alarm is locked in at COND-CP-DM/1 anunciator. The blue D.C. power light is lit, and the alarm is most likely associated with COND-DM-1F high D/P anunciator card failure. According to the ARP the annunciator has shifted to A.C power. Verified D.C. P/S disconnect shut per the ARP.. <I> **** Actions Taken **** Notified supervisor and performed ARP steps. <N> **** Equipment Description **** RWCR | 02-00-COND-CP-DM/1
401404 | CR | 20191117 |  | 4 | COND-V-231E leaks by. |  |  |  | N | YES | <D> **** Detailed Description **** COND-V-231E leaks by when COND-DM-1E is removed from service for relax. Flow indicated 0-650 gpm ( bouncing ) on the totalizer, and a steady 0 gpm after shutting COND-V -1077E. <I> **** Actions Taken **** Notified supervisor. <N> **** Equipment Description **** RW 467 | 02-00-COND-V-231E
401408 | CR | 20191117 |  | 4 | Lighting Safety Concern - 572' RHR HX A Room is Dark | N | N |  | N | YES | <D> **** Detailed Description **** RX Building, 572' RHR Heat Exchanger Room "A" is completely dark except for one small light just inside the door. The main room itself, which is controlled by three of the four light switches, is completely dark. <I> **** Actions Taken **** Initiated this AR/CR. <N> **** Equipment Description **** RX 572' RHR HX Room A
401409 | CR | 20191117 |  | 4 | Lighting Safety Concern - RW 467' C230 Pipe Space is Dark | N | N |  | N | YES | <D> **** Detailed Description **** This room is labeled "C230 Pipe or Duct Space" and is located behind Door C-228 at the north end of the RW 467' Valve Gallery "A". Some know it as the old Metallurgy Room. The room is completely dark with no functioning lights available at all. There are significant overhead sources of radiation from piping in the northern portion of this room, but the southern end is much lower in regards to the dose rate. This is the first time that I have seen the lighting be completely absent in this room. <I> **** Actions Taken **** Initiated this AR/CR. <N> **** Equipment Description **** RW 467' C230 Pipe Space
401410 | CR | 20191117 |  | 4 | TSW-DPIS-5B at the high spec | N | N |  | N | YES | <D> **** Detailed Description **** TSW-DPIS-5B is at the high spec of 2.5 psid on the OPS 4 logs. This is an indication of the D/P across TSW-F-2B. The filter is also backwashing and D/P is not lowering. Recommend cleaning the filter. <I> **** Actions Taken **** Informed MCR. Wrote CR. | 02-00-TSW-DPIS-5B
401411 | CR | 20191117 |  | 3 | HAMMER Live Fire Training Facilities/Support Degraded | N | N |  | N | NO | <D> During the recent Live Fire Training at HAMMER, the Flame Pad was not available for use. This was the second year in a row that it was not available. This prop is valuable because it is live fire and it gives the Fire Brigade their only chance to use foam in a real life scenario. This prop being unavailable two years in a row results in both a lack of training/experience and Energy Northwest not getting what they paid a lot of money for. Additionally, there wasn't a water jug and cups on location for the crew, which is contrary to every other training experience we are used to. The Porta-Potty was also missing. The nearest bathroom was ~3 times as far to walk (in your turnout gear), which was both inconvenient and not efficient. I assume that HAMMER is supposed to supply both H2O and local bathroom access in the contract we have with them. <I> There were some complaints aired amongst fellow fire brigade members, but there was no real assurance that it would be any different next time. Initiated this AR/CR in the hope that Energy Northwest gets what they paid for and the Live Fire training experience will be back to what is has been, prior to 2018. . I am usually able to autoapprove INPROG CR's. Because this is anonymous, I don't have that ability. This needs to get APPROVED so it can be evaluated. <N> CR initiated anonymously, reviewed for Safety Conscious Work Environment (SCWE) content. Moved to CR-SRO for OPS review.
401412 | CR | 20191117 |  | 3 | Unmarked cable connected to telephone cabinet | N | N |  | N | NO | <D> **** Detailed Description **** Unmarked cable connected to telephone cabinet. Cable routed through large opening in the rear, unsecured door of the 'Telephone Utility to PDTS Interface' cabinet. Front door of cabinet is locked, but this rear door is not. Recommend either routing cable in a more permanent manner or tagging it appropriately as temporary and securing rear door to cabinet. <I> **** Actions Taken **** Informed SSS Pics in EDMS <N> The cable has been removed. Close NCAQ-4
401413 | CR | 20191117 |  | 4 | Lighting Safety Concern - RW 467' A & B Valve Galleries | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The RW 467' A & B Valve Galleries are not well lit. Portions of the Valve Galleries have been converted to LED lighting, but the lighting is still lacking. There are two reasons for this. First, not all of the lighting has been replaced with working bulbs and/or LED fixtures, Second, the lighting fixtures are almost up to the ceiling, which is quite high. The large valves, piping, and many long term scaffolds/decking are blocking the overhead light sources from reaching the areas below. There may be a two-fold solution. Continue changing the existing light fixtures over to LED and install some temporary lighting. <I> **** Actions Taken **** Initiated this AR/CR. <N> **** Equipment Description **** RW 467' A & B Valve Gallery Lighting
401414 | CR | 20191117 |  | 4 | RFT-LOC-1A found tripped | N | N |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was obvserved that the only lights lit on RFT-LOC-1A were the alarm light and the overtemp. overload light. A restart of the RFT-LOC-1A was attempted per SOP-LO-START section 5.2. Step 5.2.2.b directs the operator to "verify oil level in gear chamber between min and max on the sightglass." The oil sightglass appeared to be empty. There was a large amount of oil underneath the lube oil conditioner and two white oil soak pads were completely saturated with oil. The exact location of the leak could not be verified. <I> **** Actions Taken **** Notified CRS and wrote CR | 02-00-RFT-LOC-1A
401415 | CR | 20191117 |  | 3 | Fire Brigade Turnout Gear in Bldg 62 not washed or inspected | N | N |  | N | NO | <D> **** Detailed Description **** Originally, the Fire Brigade members wore turnout coats, helmets, and hip waders (as pants) from a small shared pool of distributed cabinets around the plant. They were never washed or inspected and the afternoon drill crew literally had to wear coats that were sometimes wet with the morning crew's sweat. This was finally grieved under state hygeine laws and we all were outfitted with personal professional turnout gear. These are washed and inspected once per year (after live fire). While they are away, we rely on Bldg 62 gear in case of fire or a drill. This gear is shared, not washed, and not inspected. This is problematic in both the hygeine aspect and the required annual inspection. <I> **** Actions Taken **** Discussed openly during our Fire Brigade training on November 14, 2019. Committed to initiate this CR.
401416 | CR | 20191117 |  | 3 | EWP copy Document not fuctioning as needed | N | N |  | N | NO | <D> **** Detailed Description **** Work Orders that are at ready or working do not populate in the copy document screen. Copy documents need to function no matter what the status it is in portal J or EWP <I> **** Actions Taken **** Contactted EWP and notified supervision <N> **** Equipment Description **** . Tested the copy function in production on two different test WO Tasks and the software is working properly. Was able to copy documents in both a Working and Ready status.
401417 | CR | 20191117 |  | 3 | Standby Location for AED on RX 606' is not Optimal | N | N |  | N | YES | <C> Per MRT feedback on 11/19/2019, this CR was dispositioned to 3 / PERFIMP to ensure updates were made to the procedure and maps regarding AED location on RX 606' <D> **** Detailed Description **** Unlike all the other AED (Automated External Defibrillators) that are on Standby at Energy Northwest, in case there is a medical emergency, the AED on RX 606' is not mounted and clearly labeled on the wall. Instead, it is on a shelf, inside of a storage cabinet in the SW corner. There is a sign on the outside of the cabinet. During an emergency, it would be more optimal to have an AED out in the open, clearly identified and accessible, just like a Fire Extinguisher. This could literally make the difference between life and death, should the AED in a "Storage" vs "Standby" configurement be overlooked by a rescuer. All AED's should be mounted and displayed the same way. <I> **** Actions Taken **** Discussed with Fire Brigade / First Responders and Trainer and committed to initiating this CR. <N> **** Equipment Description **** RX 606' Automated External Defibrillator AED in SW corner
401418 | CR | 20191117 |  | 4 | Lighting Safety Concern - RW 452' C143 Off Gas Filter Room | N | N |  | N | YES | <D> **** Detailed Description **** The RW 452' "C143 Off Gas Filter Room" behind "Door C-119" is very poorly lit, especially just inside the door and just beyond the filter cubicle. <I> **** Actions Taken **** Initiated this AR/CR. <N> **** Equipment Description **** RW 452' C143 Off Gas Filter Room behind "Door C-119"
401419 | CR | 20191117 |  | 4 | Lighting Safety Concern - RW 452' "C138 Corridor" | N | N |  | N | YES | <D> **** Detailed Description **** The RW 452' "C138 Corridor" behind "Door C-120" has burned out fluorescent tubes in the first fixure, just as you enter the corridor. The rest of the corridor and back room is well lit, with the exception of the cubicle that contains OG-FU-11B. That room/cubicle is completely dark and needs to be relamped. <I> **** Actions Taken **** Initiated this AR/CR. <N> **** Equipment Description **** RW 452' "C138 Corridor" and cubicle containing OG-FU-11B
401420 | CR | 20191117 |  | 4 | Lighting out 487' RW | N | N |  | N | YES | <D> **** Detailed Description **** A light fixture on the south end of the hallway outside of the 487' RW chemistry lab.has both lights out. <I> **** Actions Taken **** control room informed <N> **** Equipment Description **** light fixture south end of hallway outside chemistry lab
401421 | CR | 20191117 |  | 4 | lighting out on 548' Rx Bldg Northeast corner | N | N |  | N | YES | <D> **** Detailed Description **** two 6' lights out near the RCC radiation monitor <I> **** Actions Taken **** control room informed <N> **** Equipment Description **** light fixture in the northeast corner of the 548' Rx Bldg
401422 | CR | 20191117 |  | 4 | CO-P-2B is using an excessive amount of oil. | N | N |  | N | YES | <D> **** Detailed Description **** CO-P-2B is using an excessive amount of oil for its' bearing housing. Oil is having to be added to completly refill one or the other of the bearing housing resevoirs approximately every other night shift. <I> **** Actions Taken **** Initiated CR. Notifed Supervisor. <N> **** Equipment Description **** Aux Boiler room TB'441 | 02-00-CO-P-2B
401423 | CR | 20191118 | CAQ | D | SEC-Door C408 Not Functioning As Intended | Y | Y |  | N | YES | <D> **** Detailed Description **** SEC-Door-C408 is not functioning as intended. Please contact Security at x2185 for details. <I> **** Actions Taken **** Posted compensatory measures. Generated CR/WR. <N> **** Equipment Description **** Main Control Room Door | 02-00-W-DOOR-C408
401424 | CR | 20191118 | CAQ | D | oscillograph start alarm | N | N |  | N | NO | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. The alarm was due to the following sensors: J9 (115 kV Neutral Ground Overcurrent) and J15 230KV Undervoltage All sensors have been reset. E-TR-S and E-TR-B voltages are 239/235/238kV and 118/117.5/118 kV respectively. BPA Munro reports the cause of the grid disturbance was a 115KV Benton - Franklin line tripping. The single pole fault automatically reclosed. The fault was on the 115kV system and did not involve the 230kV or 500kV lines. No damage or emergent outage was noted. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR.
401425 | CR | 20191118 |  | 4 | Substantial Dust Accumulation on SA-V-246 |  |  |  | N | NO | <D> **** Detailed Description **** There is a substantial accumulation of dust and fuzz on SA-V-246 in the 441' corridor. See photos in EDMS. <I> **** Actions Taken **** Contacted HP/Laborers.
401430 | CR | 20191118 |  | 4 | (NRC) Housekeeping Issues |  |  |  | N | NO | <D> **** Detailed Description **** The following housekeeping issues were identified: 1. "brag rags" on the pedestal by RCIC-P-3 2. RHR A pump room - debris in corner of room by RHR B pump room door, in the corner. Blue zip ties on the floor. 3. DG1 room - scaffold poles and knuckles stored somewhat randomly on the floor under the stairway up to the intake/HVAC level. There are Storage Authorization Permits #215 and #236 on the wall in this area. <I> **** Actions Taken **** Disposed of rags and zip ties. Notified HP/Laborers of floor debris. Floor debris in RHR A pump room has been cleaned up by the RMC laborers. No further action required.
401432 | CR | 20191118 |  | 3 | â€œDrawout Disconnect Deviceâ€ symbols wrong on drawings | N | N |  | N | NO | <D> **** Detailed Description **** â€œDrawout Disconnect Deviceâ€ symbol shown on E501-1 is used to depict 480V Molded Case Circuit Breakers throughout the plant. A list of these devices can be found on AED PMO MOT-BKR-2-7. Molded Case Circuit Breakers are NOT drawout type devices when installed in Columbiaâ€™s 480V buses and are instead physically bolted to the bus bars. These drawing errors are found throughout the EWD and E series drawings for each of these devices. These errors have resulted in Clearance Order issues in the past and late planning issues and schedule hits as the impact for maintenance on a drawout type device is very different from that of a device bolted to the bus bars of a MCC (drawout type devices can be worked on and replaced online, bolted devices require an entire bus outage to perform work on). continued under actions taken........ <I> **** Actions Taken **** Recommend eliminating the â€œDrawout Disconnect Deviceâ€ symbols from all engineering drawings for all Molded Case Circuit Breakers listed on MOT-BKR-2-7.
401434 | CR | 20191118 |  | 4 | Slip/Fall Hazard at BLDG 9 SE exit on sidewalk step landing | N | N |  | N | YES | <D> **** Detailed Description **** Industrial Safety Issues List item (Step at Bldg 9 SE exit to Bldg 17 S entrance) recently corrected to increase visibility and pedestrian awareness by application of glossy yellow paint on step riser and landing surface. . During rainy weather on 11/17, painted step's landing surface was found to be a Slip/Fall Hazard due to very slippery condition attributed to inclement (wet) weather on glossy painted smooth concrete surface. Painted material should be modified to include an abrasive component to increase friction and mitigate Slip/Fall Hazard caused by wet slippery surface. <I> **** Actions Taken **** Informed Maintenance Craft of hazard during Monday AM D15 Initiated CR to address condition. <N> **** Equipment Description **** Step landing at BLDG 9 SE exit.
401435 | CR | 20191118 |  | 3 | Main generator major inspection findings (R24) | N | N |  | N | YES | <D> **** Detailed Description **** During the main generator robotic inspection in R24 several general tests were performed to determine the overall health of the generator. Overall material condition is good with tight core and core wedges and no indications of movement (greasing or dusting). One test performed is the Siemens Multi-frequency Core Analysis System (SMCAS) which tests the core iron for imperfections or degradation in the insulation between the steel core iron laminations. There are several indications at specific locations in the core that have been monitored during the major inspections. Five of the monitored locations have increased in magnitude since the last test, this is an indication of degraded insulation between core iron laminations. Slots 10, 12, 15, 33 and 44 have all increased from the 2011 inspection to the 2019 inspection. . Based on the increasing trend in the locations identified above Siemens recommends performing a LOOP test of the stator core during the next major inspection (2027, R28). Loop testing requires rotor removal, installation of several loops of cable and a large power source to energize the â€œLOOPâ€ to excite the core for evaluation of the indicated locations. Degraded insulation results in hot spots in the core that can be viewed by thermography during the loop testing. Degraded insulation can potentially be repaired by etching if the indications are close to the surface or by separation of the laminations and insertion of thin micarta insulating material if the indications are deeper in the core iron. . This CR is documenting a long term equipment reliability issue and does not pose an immediate threat to operation of the main generator, this is an indication that additional testing is recommended for R28 and a rewind and core repairs may be needed in the future. <I> **** Actions Taken **** Discussed with Siemens and notified supervisor. Initiated CR to document the condition and raise awareness of future testing requirements or recommendations. See EDMS tab for full inspection report. | 02-00-E-GEN-1
401436 | CR | 20191118 |  | 3 | Outage Long Range Plan / Scoping Process Improvements | N | N |  | N | NO | <D> **** Detailed Description **** Following benchmarking, review of PO.6 results (scope identification), and review of outstanding / backlog outage activities, improvements for outage long range planning and scope identification have been recognized. A cross-functional team will be formed to close identified gaps, streamline the scope prioritization process, and to support future outage scope selection process (thereby improving plant health). The Long Range Outage Plan (LROP) Team will convene on a regular basis (initially monthly) to collaborate on closing gaps and improving our processes. 3 to Outage Management. <I> **** Actions Taken **** Discussed with PSO Leadership. Initiated CR. First meeting set up.
401438 | CR | 20191118 | CAQ | C | Evaluate applicability of NRC EA-19-062 to CGS | N | N |  | N | NO | <D> **** Detailed Description **** Enforcement Action EA-19-062 was issued to Plant Hatch based on the allowance to use training-only for reactivation of SRO for Supervising Core Alterations. The NRC cited 10 CFR 55.53 (f)(2) which requires a minimum of 40 hours of on-shift SRO U/I prior to re-activation. Qual group RFAE, Core Alterations Supervisor, allows for eight hours U/I for inactive SROs to count for time on shift, LO001742. Recommend evaluating the requirements of qualification directory 4.6 RFAE against 10 CFR 55.53 and EA-19-062 for potential impact. <I> **** Actions Taken **** Informed Training and Operations Management. Informed NRC resident.
401442 | CR | 20191118 |  | 3 | PMID 15002 16.4.9 improper schedule dates | N | N |  | N | NO | <D> **** Detailed Description **** PPM 16.4.9 PMID 15002 has due dates of 12/2/2019, 1/7/2020 and 10/4/2021. THis is a quarterly PM and should be scheduled evert 3 months similair to PMID 14999 for PPM 16.4.6. The two should be scheduled the same week. Last performed week of 11/5/2019 . <I> **** Actions Taken **** Contacted PM Coordinator Wrote CR
401443 | CR | 20191118 |  | 4 | Frayed cord/GFCI tripped on cord (1/2) at forklift at #88 | N | N |  | N | NO | <D> **** Detailed Description **** Frayed cord has been excessed. Frayed extension cord plugged into forklift outside 88, tripped GFCI. Identified frayed location, extension cord was excessed. Generated CR and FIN notified to replace Extension cord. <I> **** Actions Taken **** Notified FIN, generated CR. <N> **** Equipment Description **** Extension cord at forklift staged outside bldg #88
401447 | CR | 20191118 |  | 4 | SEA-FN-51 | N | N |  | N | NO | <D> **** Detailed Description **** While performing W/O # 02126959-01, step 7.1.1 of ppm 15.2.11 says to check that certain fans are running. SEA -FN-51 is tagged off with an equipment tag ( 24-000929). this fan is tagged off because of the need to replace the belt. with the fan not running we can not perform the testing of SEA-SMD-52 which is the duct detector for the associated fan. <I> **** Actions Taken **** contacted the CRS about the tag who then directed me to the PRSO, PSRO stated why the fan was tagged out and that we could not perform our testing. notified my supervisor and documented with this CR. <N> **** Equipment Description **** SEA-FN-51 ***General Notes*** reopened the CR to add a work request cross reference.
401449 | CR | 20191118 |  | 4 | check valve downstream of FP Main Drain valve in BLDG 9 | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of section 7.6 for testing Main Drain test of FP system in bldg 9 under PPM 15.1.23 (WO 02124563-01) it was identified the check valve that ties into the tee "discharge" from the FP-V-B9/03 discharge had leakby as indicated by water flowing back up and out of the small scupper. <I> **** Actions Taken **** Generated CR. This is only an issue when the FP Main Drain valve (FP-V-B9/03) is cycled as part of the test portion of section 7.6 for of PPM 15.1.23. This did not impact the performance of the procedure for that section. CR generated to pursue WR on the common check valve for houskeeping purposes only when the valve is cycled in the future. <N> **** Equipment Description **** No EPN, for valve. Drain valve is labeled FP-V-B9/03 in the field. Check valve suspected of leakby back into scupper is valve located off the common discharge tee.
401450 | CR | 20191118 |  | 3 | Observation Card does not align with 18-003 | N | N |  | N | NO | <D> **** Detailed Description **** Devonway Maintenance Fundamentals Observation Card does not align with the maintenance fundamentals and technical skills 18-003. Revise observation card to be aligned with maintenance fundamentals and technical skills 18-003. . Recommend assignment to performance improvement to revise card <I> **** Actions Taken **** Discussed with maintenance CICâ€™s initiated CR
401453 | CR | 20191118 |  | 3 | AR-CR 400872 inappropriately trended to maintenance. | N | N |  | N | NO | <D> **** Detailed Description **** AR-CR 400872 requested heat trace be applied to the drain valve on the TRB air accumulator due to icing that occurs in the winter months. This comp measure requires an AR -EVAL and a change to SOP-COLDWEATHER-OPS. Instead of generating these actions, the AR was taken to COMP-N/A and trended to maintenance. Recommend actions to generate an AR-EVAL to Operations and action to Ops procedures to update SOP-COLDWEATHER-OPS once the AR-EVAL is approved. <I> **** Actions Taken **** Wrote CR.
401458 | CR | 20191118 |  | 3 | Procedure change required OSP-RHR-A704 | N | N |  | N | NO | <D> **** Detailed Description **** Step 7.1 as written directs performing a system vent to lower pressure to approximately 110 psig if pressure is GT 110 psig. This should read something similar to: "IF system pressure is GT approximately 110 psig, THEN vent the system to approximately 110 psig as follows: ..." to allow for normal minor fluctuations in keepfill system pressure. Also evaluate similar procedure steps on alternate keepfill systems.
401460 | CR | 20191118 |  | 3 | FD-SUMP-T2 Cleaning Results not 100 percent Effective | N | N |  | N | YES | <D> **** Detailed Description **** RMC Laborers have significantly reduced the sludge, foreign material, tablets, crescent wrench in the bottom of the sump; however, RMC Laborers were not able to remove all of the material without entering FD-SUMP-T2. The material removed included battery, stylus, tablet, crescent wrench, and 3 300-gallon totes of black water/mud/sludge. Picture in EDMS. Material located at RW 437 Sorting Table drying out. . The remaining material is not being removed by the peristaltic pump nor long handle scoop. Cleaning operation was terminated after discussion with EFIN Supervisor/Engineer. RMC Supervision, and RP Supervision were notified. EFIN owns the ED/FD system. . Samples were taken of the water coming in the inlet pipe and sump. Sample Number 2970 - FD-SUMP-T2 Inlet Pipe - 47,000 ppb TOC Sample Number 2993 â€“ FD-SUMP-T2 â€“ 15,000 ppb TOC . Attached in EDMS are pictures of FD-SUMP-T2 showing Foreign Material and post cleaning results. <I> **** Actions Taken **** Informed engineering and RP Supervision Completed Energy Northwest Loss of FME Integrity â€“ Notification and Recovery Form 26337. Uploaded completed form to AR-CR 00401460, and AR-CR 00401327, Foreign Material Found in FD-SUMP-T2. Form 26337 was also forwarded to the FME Coordinator. | 02-00-FD-SUMP-T2
401461 | CR | 20191118 |  | 4 | Near miss- broken office chair | N | N |  | N | NO | <D> **** Detailed Description **** While seated in my office chair, a bolt from the bottom of the chair fell off. I flipped over the chair and inspected the remaining three bolts. All three appeared to be fully threaded and secure. I made a note to have the bolt reattached, but flipped it back over and continued using the chair. Five minutes later, while leaning on the left arm support, a loud pop occurred, the chair tipped left and I rolled out to the side. The chair lost both bolts on the right side, causing it to tip left. <I> **** Actions Taken **** Chair removed from service. Checked other office chairs in area. Informed supervisor. <N> D-15 Thumbs down write up submitted for Wednesday 11/20.
401462 | CR | 20191118 |  | 3 | November EP ERO Callout Drill | N | N |  | N | NO | <D> **** Detailed Description **** On November 6, 2019 at 1915, an ERO Call-Out drill was successfully conducted when all centers activated within the required timeframe with all required Essential positions filled. However, a review identified some instances where additional essential ERO personnel did not respond as expected. <I> **** Actions Taken **** Investigated instances where expectations were not met. <N> **** Equipment Description **** Recommend non-CAQ 3 to EP
401463 | CR | 20191118 |  | 4 | Replacement CCH purge units cannot be repaired | N | N |  | N | NO | <D> **** Detailed Description **** The scope of WO 02141601 is to repair the internal epoxy coating on purge units purchased under PO 353387. These unused purge units were purchased to replace the degraded purge units currently installed on CCH-CR-1A and CCH-CR-1B. The painters were successful in removing the paint that was flaking off and were able to prepare the affected areas per the paint manufacturerâ€™s recommendation. This CR is to document that a section of the replacement purge units could not be accessed due to interference from the internal spined refrigerant tube that travels the length of the purge cylinder. With this interference, there is no way to verify the condition of the coating or prepare it for painting. This information was conveyed to Procurement Engineering and they indicated that this condition complicates the commercial grade dedication process that is required in order to install these units on the safety related chillers. Furthermore, it is a known condition that the original epoxy coating on the York purge units degrades over time. Without the capability to replace all of the epoxy on the replacement units, it is likely that the original epoxy coating would begin to degrade after a few years of installation. Recommend cancellation of work order 02141601 to repair the purge units and cancellation of work orders WO 02142517 and WO 02142516 to replace the purge units. An assignment has been created under AR EVAL 358871 for System Engineering to work with Procurement and Design Engineering to determine a new path forward for the replacement of the CCH purge units. A potential solution may involve sending the (6) replacement units to a 3rd party vendor to be used as part of an effort to reverse engineer new units made of stainless steel. A bridging strategy is already in place to address the degraded condition of the purge units - PMIDâ€™s 721-15 and 722-15 inspect and clean the purge units on an annual basis. <N> **** Equipment Description **** Spare purge units purchased under 353387.
401464 | CR | 20191118 |  | 3 | Handheld GPS Timecode Sync device needs Cyber Evaluation | N | N |  | N | NO | <D> **** Detailed Description **** As a part of TimeSync cyber project (EC13304), a handheld GPS-sync'd time source (CID: 33249) was selected to be used for periodic syncing of the time code servers installed on level 3 and 4 networks. This device is also used by the Open Phase Detection project for sync of its timecode servers. This device provides an IRIG-B clock signal to synchronize the timecode servers to. This tool has not been evaluated for applicability of the M&TE portion of SWP-CSW-15. . This does not impact Operations. This is not reportable. . Recommend to Cyber Security to perform evaluation. <I> **** Actions Taken **** Discussed with Cyber Security Program Manager and generated CR.
401465 | CR | 20191118 |  | 3 | Possible wobble in TMU-P-1B shaft | N | N |  | N | YES | <D> **** Detailed Description **** During system walkdown a slight wobble was noticed in the pump shaft for TMU-P-1B. The wobble appears to be minor, and is of a magnitude that is difficult to discern with the naked eye (see video in EDMS). Recommend acquiring additional vibration readings to ensure vibrations are within an acceptable range. TMU-M-P/1B bearing temperatures and current draw are within the anticipated range, as is TMU-P-1B discharge pressure. Baseline vibration data was acquired on 11/12/19 and found to be within an acceptable range. <I> **** Actions Taken **** Discussed with Component Engineering Supervisor. | 02-00-TMU-P-1B
401466 | CR | 20191118 | CAQ | D | (NRC OPDS 2019) Missing Fastener Screw OPDS-BLDG-B HVAC Duct | Y | N |  | N | YES | <D> **** Detailed Description **** During walkdown of the TR-B OPDS, it was identified that there was a missing fastener screw outside of the OPDS-BLDG -B (Bluiding #44 in the Transformer Yard) for the HVAC Duct. See attached pictures in EDMS of the CR. <I> **** Actions Taken **** Pictures of the location of the missing Fastener screw were taken. | 02-00-OPDS-BLDG-B
401467 | CR | 20191118 |  | 3 | COND-P-2A/2B oil level high | N | N |  | N | YES | <D> **** Detailed Description **** COND-P-2A and COND-P-2B oil level is at 3/4th. The specification is GE 1/2 and LE 11/16. | 02-00-COND-P-2A,02-00-COND-P-2B
401468 | CR | 20191119 |  | 4 | RW 487' Broken Light Switch Toggle | N | N |  | N | NO | <D> Light switch toggle in the RMC Laborers closet is broken. The closet is located on RW 487'. (Door C-325) This is the fifth Condition Report/Work Request Initiated Since 2011 on this same toggle switch. Reference Work Request #'s: 29092931 (2011), 29127958 (2016), 29139995 (2017), 29146387 (2019). <I> Initiated Work Request #5 on this same toggle switch. Notified Supervision via e-mail.
401469 | CR | 20191119 |  | 4 | RX 522' Broken Light Switch Toggle (North Pipe Space) | N | N |  | N | NO | <D> **** Detailed Description **** Light switch toggle just inside the RX 522' N Pipe Space Door is broken. (outside HRA). This is the second CR/WR written on this light switch in the past year. <I> **** Actions Taken **** Initiated CR & WR <N> **** Equipment Description **** RX 522' N PIpe Space Door
401470 | CR | 20191119 |  | 3 | ALARA Suggestion: LHRA TG 441' NE Stairwell |  |  |  | N | NO | <D> **** Detailed Description **** On 9/9/2016, CR#00354651 was initiated to modify NE Stairwell gate so HP Techs could utilize a Camera for their Weekly VHRA/LHRA Door Checks. By doing this, we saved 50-70 mRem a year. This lasted for a while but then the camera was removed due to a barrier permit (I believe). We should do whatever needs to be done to utilize this technique of verifying this door is locked to save dose while also adhering to all impairments. Every mRem Counts... <N> AR type EVAL for proposed station configuration change?
401472 | CR | 20191119 |  | 4 | AR-CR 401373 inappropriately trended to maintenance. |  |  |  | N | NO | <C> AR-EVAL assignment under 401473 to AR-OPSST. <D> **** Detailed Description **** AR-CR 400872 requested a permanent locking device be applied to CW-V-62. This is a permanent change to the plant configuration and requires an AR-EVAL. PPM 1.3.68 section 4.3 step 1.3 requires any WR requesting a change to the plant to return to the originator for submission of an AR-EVAL and canceled. Instead of generating this action, the AR was taken to COMP-N/A and trended to maintenance. Recommend an action to generate an AR-EVAL to Operations. <I> **** Actions Taken **** Wrote CR.
401473 | CR | 20191119 |  | 3 | PPM 10.25.46 needs revision | N | N |  | N | NO | <D> **** Detailed Description **** During performance of fabrication task on WO 02134237-41, it was noted that PPM 10.25.46 rev 18 page 20 â€˜method 2bâ€™ lacks guidance to complete the patch plate. The PPM does not call out what the â€˜cement bonding materialâ€™ is nor does it call out what side of the patch plate the sheet metal screw heads should be on when the assembly is complete (screw heads inside or outside the control room panel). <I> **** Actions Taken **** wrote CR
401475 | CR | 20191119 |  | 4 | M&TE OOT | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0064310 Ectron TC Test Set- model 1100CF found OOT & adjusted within specs. EFIN Eval: No impact on any of the referenced WO's. OOT range of 57.080 mV @750 Deg C is not used and was not used in any of the WO's listed. No Plant Impact. DEF #7368A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only
401486 | CR | 20191119 | CAQ | D | DG3 Room Lighting | N | N |  | N | YES | <D> **** Detailed Description **** During a DG3 HPCS Diesel Room Walkdown, I noted 8 light fixtures out. Considering the station has a major outage window coming up the last week on Jan. 2020, I believe a plan should be made now to get the lights fixxed. <I> **** Actions Taken **** Wrote this CR. Will pass this information to the DG3 Work Window Leader. Listed DG-ENG-1C under equipment info, but CR is for the room, not the engine. <N> **** Equipment Description **** DG3 room | 02-00-DG-ENG-1C
401488 | CR | 20191119 |  | 3 | Missing Guidance for Non-Radworker Radiopharmaceuticals | N | N |  | N | NO | <D> **** Detailed Description **** While responding to a GEM5 alarm at the security PAAP, it was noted that there is no procedure guidance for responding to radiopharmaceutical treatments for non -radworkers at the station. It was also noted that there does not seem to be guidance for vetting non-radworkers, short term non-RCA workers, and non-RCA visitors for potential radiopharmaceutical impacts to liquid effluents and waste streams. <I> **** Actions Taken **** Discussed observation with Quality Assurance Auditors and HP leadership team.
401489 | CR | 20191119 |  | 3 | Discrepancy in Condensate Resin Tank Levels | N | N |  | N | NO | <D> **** Detailed Description **** While processing resin from CPR-TK-92A and 92B, the laborers had difficulty filling the liner with an adequate amount of resin. Near the end of processing, the liner was being flooded with mostly water and very little resin. According to the most recent calculations (from 11/18/2019), TK-92A is roughly 85% full and TK-92B is roughly 60% full. Either the calcuations are incorrect, and the tank levels are significantly less than those calculated, or there is an issue with the processing that is preventing resin from moving from the tanks into a liner. The team needs to determine an appropriate way to verify tank levels are being accurately calculated. If levels are correct, we need to develop a plan for correcting whatever deficiency is preventing the processing of these tanks. <I> **** Actions Taken **** Discussed issue with HP leadership team.
401490 | CR | 20191119 |  | 3 | FP-V-172 & FP-V-33 Hard-To-Operate | N | Y |  | N | YES | <D> **** Detailed Description **** During performance of a Fire Protection System Vulnerability Evaluation (SARC 383328), several equipment operators were interviewed to determine if the operators had any concerns with the FP System. Operators identified that valves FP-V-172 associated with FP-P-110 recirculation line-up, as well as, FP-V-33 associated with FP-P-1, FP -P-2A, and FP-P-2B are extremely difficult to operate due to differential pressure conditions. Both valves are gate valves. This is a classic condition of trying to throttle flow under differential pressure with gate valves. The FP System Engineer has witnessed first-hand how difficult operating the valves is during pump flow tests. The valve can require up to three operators utilizing the approved leverage enhancing devices to achieve the correct valve position for the correct flow in the test. . This CR is being written to document the concern for additional corrective actions in the future. . The prescribed condition is purely an industrial safety concern for the equipment operators. FP-V-172 and FP-V-33 are not degraded and this condition does not affect the valves from performing their design function of providing sectional isolations within the FP Piping System/Water Supply. . Recommended solution is to place this issue on the plant safety concerns list and pursue a design change to replace the gate valves with globe valves that accommodate differential pressure. This approach will eliminate the hazard through engineering controls. <I> **** Actions Taken **** Presented issue to site safety committee, compiling risk rank form in accordacne with DES-2-9 to request a design change. Reference AR 401076 for technical evaluation. <N> **** Equipment Description **** Flocculator/Water Treatment Bldg - FP-V-172 - Grade Level CWPH - FP-V-33 - Grade Level | 02-00-FP-V-172,02-00-FP-V-33
401491 | CR | 20191119 |  | 3 | E-CB-ASD/IN/1A/CB1* and E-CB-ASD/IN/1A/CB2* showup as retire | N | N |  | N | NO | <D> **** Detailed Description **** E-CB-ASD/IN/1A/CB1* and E-CB-ASD/IN/1A/CB2* showup as retired however these are still active EPNâ€™s. Portal J and Esoms need to be updated to reflect Active. E-CB-ASD/IN/1B/CB1* and E-CB-ASD/IN/1B/CB2* need to be updated as well. <N> See Cross Refs AR for history behind why these were set to RETIRED status.
401492 | CR | 20191119 |  | 4 | TOA-FL-2A center spool fell off bracket and unwound | N | N |  | N | YES | <D> **** Detailed Description **** The center spool of TO-FL-2A fell off its bracket and unwound, covering about 3/4 of the center filter. See attached images. Filter needs to be replaced soon. <I> **** Actions Taken **** Notified CRS | 02-00-TOA-FL-2A
401493 | CR | 20191119 |  | 4 | Documentation discrepancy for computer device | N | N |  | N | NO | <D> **** Detailed Description **** Computer has been located and documentation was updated for user and location. No futher actions required. <I> **** Actions Taken **** Notified supervision, created CR to document condition and resolution.
401498 | CR | 20191119 |  | 3 | enhancement needed to model WO 01025535 01 | N | N |  | N | NO | <D> **** Detailed Description **** WO 01025535 01 is the annual metals sampler cal check for Chemistry. A sampler has since been installed on SP-13B. This sample point needs to be added to the table in the work instructions so it will be present next year. A cal check was performed satisfactory on the metals sampler installed on SP-13B and written under the current chart. <I> **** Actions Taken **** Informed Chemistry Supervision. Wrote CR
401499 | CR | 20191119 | CAQ | D | CRD-HCU-46-47 High Water Level alarm received | Y | N |  | N | YES | <D> **** Detailed Description **** Received Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU-46-47. After investigation, Rod Accumulator Trouble Alarm P603-A7 drop 6-7 was for CRD-HCU-46-47 high water level. <I> **** Actions Taken **** Dispatched OPS-2 to investigate. OPS-2 drained water to restore the HCU. Initiated CR. <N> **** Equipment Description **** RB 522 | 02-00-CRD-HCU-4647
401502 | CR | 20191119 |  | 4 | Building 80 water gong not ringing | N | N |  | N | YES | <D> **** Detailed Description **** While performing 15.1.23 it was noticed that the water gong for building 80 wet system is not ringing. Water gong needs to be repaired or replaced. <N> **** Equipment Description **** Building 80
401503 | CR | 20191119 |  | 3 | ESP-SM7UV-M401 | N | N |  | N | YES | <D> **** Detailed Description **** Procedure enhancements needed to facilitate using new test equipment. See attached EDMS. <I> **** Actions Taken **** notified supervision and wrote this CR <N> **** Equipment Description **** . Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
401504 | CR | 20191119 |  | 3 | ESP-SM8UV-M401 | N | N |  | N | YES | <D> **** Detailed Description **** Procedure enhancements needed to facilitate using new test equipment. See attached EDMS. <I> **** Actions Taken **** notified supervision and wrote this CR <N> **** Equipment Description **** .Revision has been migrated into Maintenance Programs database at link below. If you have any questions please contact Maintenance Services Supervisor. http://thecurrent/sites/NG.OPS .PGM/Maintenance/MS/Lists/Procedure%20Modifications
401505 | CR | 20191119 |  | 4 | Small puddle forming in Aux Blr room from heater bay leak | N | N |  | N | YES | <D> **** Detailed Description **** There is a puddle forming on the SW floor of the Aux Boiler room by the condensate return tank. The water is coming from a crack in the ceiling/471 heater bay floor. The location of the leak is appears to be in the general area of the #6 heater, which was written up last week for a significant steam leak from an inspection port flange (AR 401313). Water was dripping about one drop / 7 sec. HP was notified to survey the puddle. <I> **** Actions Taken **** Notified OPS supervisors and HP. <N> **** Equipment Description **** Aux. Boiler Room
401506 | CR | 20191119 | CAQ | C | WMA-TS-8A1 and 8A2 setpoints do not align with vendor data |  |  |  | N | YES | <D> **** Detailed Description **** Vendor information received from Framatome on 11/19/19 indicates that the set and reset temperatures for Battery Room temperature switches WMA-TS-8A1 and WMA-TS-8A2 require a minimum separation of 10Â°F. The IMDSâ€™s for these instruments indicate a separation of only 4Â°F (Trip of 75Â°F and Reset of 79Â°F.) A review of the Battery Roomsâ€™ historical temperatures indicate that the temperature switches are operating properly. The installed instruments have been successfully calibrated at the setpoints indicated on the IMDS, so the current licensing basis design is upheld and there is no concern for operability. These instruments are used to control in-duct heaters to maintain battery rooms above Tech Spec Limit of 60Â°F. To meet station blackout requirements, the battery roomâ€™s temperature should be maintained greater than 74Â°F during normal operation. Recommend an EVAL assignment to verify that the instrument model specified is correct for this application. See EDMS folder for referenced catalog cutsheets. <I> **** Actions Taken **** Informed Supervisor. <N> This CR documents a request for an evaluation to verify the correct temperature switch model application. If the temperature switch model is determined to be inadequate then a new CR should be written to evaluate functionality/operability. | 02-00-WMA-TS-8A1,02-00-WMA-TS-8A2
401507 | CR | 20191119 |  | 3 | Lessons Learned for Enmergent Issues TMU-P-1B / FP-P-1 | N | N |  | N | NO | <D> **** Detailed Description **** Lessons learned identified during two emergent plant issues during the week of 11/11/19; TMU-P-1B and FP-P-1 are documented and attached in EDMS. <I> **** Actions Taken **** Discussed with Operations manager and another Duty Manager for reviwe and verification. Suggest that PPM 1.3.16 be reviewed for revision by recent managers that implemented the process
401508 | CR | 20191119 |  | 4 | BRE 35 Door needs maintenance | N | N |  | N | YES | <D> **** Detailed Description **** The door latch for BRE 35 appears to be sticking. Contact security at ext. 2185 for further details <I> **** Actions Taken **** Security notification made, CR/WR generated <N> **** Equipment Description **** BRE 35 located south of the TSC
401509 | CR | 20191119 |  | 3 | unable to install new filter assembly during PM | N | N |  | N | YES | <D> **** Detailed Description **** the PM for changing filters on TMU-F-2/2A, wanted to install a new filter housing/Style, it was the wrong type of filter and would have required welding. The PM was completed by changing the filters in the existing units. This CR/WR is to caputre that a WO will be needed to weld in the new style filter housing and ensure the pm is only written to change filters and not the entire unit every time. SEE WO 02038599 on TMU-F-3 for planning purposes After assembly installed, PM should need CATID's 22930 and 58407643 replaced. <I> **** Actions Taken **** Discussed with engineering and procurement on what would be needed to install a new style filter unit 1 time then only replace the filters on the PM. <N> Discussed CR with Planning Supervisor, no action needed as this has been already addressed in WR. COMP/NA CR. | 02-00-TMU-F-2
401511 | CR | 20191119 |  | 3 | Incorrect serial number noted during inspection of FP-P/M-2B | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO 02046143-10 it was identified that the serial number in EC package 17692 and WO instruction step 4.1 was different than the physical S/N on the motor (CID 34448) at the warehouse. The S/N called out in the EC/WO pkg is A02 20181942-001 R 0001. The S/N on the motor was identified as A02 20181526-001 R 0001. Recommend Engineering review and make necessary changes to EC and planning to change WO instructions to reflect. <I> **** Actions Taken **** CR generated for documentation. P/M has not been pulled from the warehouse and is not installed in the plant <N> Discussed CR with Planning Supervisor, no action needed by Planning as this has been already addressed in WO.
401513 | CR | 20191119 |  | 4 | Scheduled work unable to be performed. | N | N |  | N | NO | <C> Incorrect serial number issue for part being worked by AR -SECOMP under AR 401511, cross refernced to this CR. <D> **** Detailed Description **** FP-M-P/2B IS NOT ON SITE IN ACCORDANCE WITH EC 17962. WO 02105231-04 AND 02046143-15 BOTH WERE UNABLE TO BE PERFORMED <I> **** Actions Taken **** CR SUPERVISION <N> **** Equipment Description **** FP-M-P/2B
401514 | CR | 20191119 | CAQ | D | Trend of low pressure on CMS-PI-5 at CMS-SR-20 | Y | N |  | N | YES | <D> **** Detailed Description **** The pressure indicator CMS-PI-5 has had a quick downward trend in pressure indication on CMS-SR-20. Pressure dropped from 2.5 psig to appoximately 0.5 psig on Nov 1st and has remained low. Readings are taken daily by chemistry and logged in Nuclear IQ. <I> **** Actions Taken **** Spoke with system engineer. | 02-00-CMS-PI-5,02-00-CMS-SR-20
401515 | CR | 20191119 |  | 3 | Exam Failure | N | N |  | N | NO | <D> **** Detailed Description **** Two students failed an exam in ME000070 Basic Rigging initial training <I> **** Actions Taken **** Notified students' supervisor.
401516 | CR | 20191119 |  | 4 | FP-HT-2T NOT DRAINING | N | N |  | N | YES | <D> **** Detailed Description **** WHILE PERFORMING 15.1.19 IT WAS DISCOVERED THAT FP-HT-2T IS NOT DRAINING AS EXPECTED. THE BARREL OF THE HYDRANT IS FULL UP TO THE PUMPER PORT LEVEL AND NEEDS TO BE PUMPED OUT BELOW GROUND LEVEL TO PREVENT FREEZING. FURTHER INVESTIGATION NEEDS TO BE DONE AFTER WINTER. | 02-00-FP-HT-2T
401517 | CR | 20191119 |  | 3 | Secured TMU-P-1B due to excessive shaft wobble | N | N |  | N | YES | <D> **** Detailed Description **** It was reported to the MCR that TMU-P-1B shaft wobble was excessive and the pump needed to be secured. <I> **** Actions Taken **** Started TMU-P-1C and stopped TMU-P-1B | 02-00-TMU-M-P/1B
401518 | CR | 20191119 |  | 4 | MD-V-85 leak-by repairs not performed, continued degradation | N | N |  | N | YES | <D> **** Detailed Description **** MD-V-85 leak-by appears to have taken a step change higher after the late august HP Turb Diff Temp event, when all MD valves opened. Current leak-by is estimated 0.4 MWe. Corrective valve work was deferred from R24 with no new work request initiated. Old valve parts put back in under R24 WO 02118046. Valve needs to be replaced per inspection that was performed. WR is being initiated with this CR for valve replacement, however, WO 02037331 is scoped in for R25 downstream piping replacement. It is recommended that the valve replacement be bundled with the piping replacement. WR can be canceled if scope is added to WO 02037331. <I> **** Actions Taken **** Discussed with thermal performance and AOV program owners and relevant supervisors. <N> **** Equipment Description **** T -476- - -C1/7.9 - | 02-00-MD-V-85
401520 | CR | 20191119 |  | 4 | batteries not holding charge on manlift | N | N |  | N | YES | <D> **** Detailed Description **** it was identified that the batteries in manlift E-EQ-SL3 on the RX 522 woudl not provide power to the lift for very long. The lift was plugged in and was verified to have full charge, but when attempting to move it drained rapidly <I> **** Actions Taken **** moved lift to safe storage location and left it unplugged checked water in the batteries SAT just wont hold a charge | 02-00-E-EQ-SL3
401523 | CR | 20191119 |  | 3 | NEIL 2019 Property Loss Evaluation |  |  |  | N | NO | <D> **** Detailed Description **** NEIL loss control representative (LCR) performing the NEIL 2019 Property Loss evaluation has identified a housekeeping concern related to material condition at el. 507 of the Radwaste building. This is a condition identified during the 2018 NEIL evaluation. The LCR noted that the material condition has improved, but his concern is the amount and location of combustible materials in the demineralizer area on el. 507. As currently staged, individal 'piles' of are located such that a potential fire could spread thru adjacent piles. He has stated this will be documented as a 'should' observation which will carry no penalty points and not require immediate action. However, recommendation is to reduce amounts or separate individual piles with barriers or distance. Recommend assignment to AR-TEFP. <I> **** Actions Taken **** 1) Discussed potential resolutions which would satisfy NEIL guidance. 2) Discussed with manager. 3) Initiated CR.
401524 | CR | 20191119 | CAQ | C | (NRC OPDS 2019) E502-1 and E513-3 Drawing Descrpencies |  |  |  | N | NO | <D> **** Detailed Description **** During review of E502-1 and E513-3 drawings it was identified that the E-TR-S and E-TR-B windings are not shown consitnetly with other drawings. . On E502-1, E-TR-B does not indictae the winding configuration of the secondary winding (compared to E507-3 which shows the winding condifuration.) . On E513-3, E-TR-S is shown without the burried delta winding (in comparision to E502-1 and E507-2). . Update drawings to have alignment between drawings and actual transformer winding configuration.
401525 | CR | 20191119 |  | 3 | (NRC OPDS 2019) Updates/Review of ABN-ELEC-GRID for OPDS |  |  |  | N | NO | <D> **** Detailed Description **** Review of ABN-ELEC-GRID identified multiple tpyographical errors,legacy statements that need to be reviewed/revised: 1) Tpyographical errors in sections 1.3, and 1.4 (XFMR v.s. TRANSFORMER) to match naming of the annunciator . 2) Section 4.4. and Section 4.4 don't discuss Open Phase Alarms or OPDS conbsiderations . 3) Legacy statment for OPDS in section 5 (1.3-1.4) needs to be revised/removed
401526 | CR | 20191119 |  | 3 | (NRC OPDS 2019) Updates/Review of ABN-ELEC-125VDC for OPDS |  |  |  | N | NO | <D> **** Detailed Description **** Review of ABN-ELEC-125VDC identified that the procedure does not consider/include OPDS on the load list for E-DP- S1/7. . Review of the E-DP-S1/7 Load List should be conducted to determine if OPDS needs to be considered/removed from the Load list/Load List of Potential Nonessential Loads for Load Reduction.
401527 | CR | 20191119 |  | 3 | (NRC OPDS 2019) OPDS Procedure Typographical Errors |  |  |  | N | NO | <D> **** Detailed Description **** During review of procedures 4.OPDS.TRB and SOP-ELEC-OPDS -TRS, the following typographical Errors were identified: . In SOP-ELEC-OPDS-TRS, Section 4.2 states E-TR-A instead of E-TR-S . The Title of 4.OPDS-TRB is written as 4.OPDS.TR-B instead of 4.OPDS.TRB.Update to align with Asset Suite reserved name and for procedure alignment with procedures which reference 4.OPDS.TRB.
401528 | CR | 20191119 |  | 3 | PCR needed FCP-3 drop 8-4 |  |  |  | N | NO | <D> **** Detailed Description **** step 2 directs verifying proper fan operation but references the incorrect fans. WMA-FN-53A/B supply 467' SWGR areas. WMA-FN-52A or B supply the 484' cable spreading room. SEE EDMS <N> editorial was completed per SWP-PRO-02. Level 1 copy corrected and updated 4.FCP.3 revision 024/002 corrected the identified issue and was implemented 11/20/2019 . No action is required per this AR.
401529 | CR | 20191120 |  | 4 | RW Elevator Door | N | N |  | N | YES | <D> **** Detailed Description **** RW elevator door occasionally gets stuck in the closed position on RW 441' <I> **** Actions Taken **** Pushed the open button but the door did not open. RW elevator removed from service pending FIN investigation. <N> **** Equipment Description **** RW Building Elevator Door on the 441'.
401530 | CR | 20191120 |  | 3 | OSP-RCIC/IST-Q702 enhancement |  |  |  | N | NO | <D> **** Detailed Description **** OSP-RCIC/IST-Q702, step 7.2.55 has you record RCIC-PI-2 pressure, however there are no steps to open and then close the root isolation valve for the pressure indicator. the root isolation valve is normally closed and is opened to support surveillance testing. Steps to control the root isolation valve is prudent to ensure PCSC. Recommend adding steps to open/close RCIC-PI-2 root isolation valve.
401531 | CR | 20191120 | CAQ | D | M&TE Rejected |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0066004 Mitutoyo Dial Indicator- model 2414S found OOT & Rejeccted- Broken Beyond Repair. EFIN Eval: PMT's were performed after the maintenance using this M&TE. The PMT's were satisfactory for all equipment. There have been no issues identified on the three pieces of equipment where this M&TE was used. DEF #7365A written. No Plant Impact. No Action Required.. <I> **** Actions Taken **** None Trending purposes only
401532 | CR | 20191120 | CAQ | D | M&TE Suspended/ Lost |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0064723 Fluke Module- model 700P05 30psig Can't be located- Out of Calibration. EFIN EVAL: This M&TE was only used for WR #29150355 for a troubleshooting plan. The equipment was placed back in service with no further issues. Suspended/ Lost. No Plant Impact. DEF #7367A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
401533 | CR | 20191120 |  | 3 | PPM 10.20.1, Minor editorials needed |  |  |  | N | YES | <D> **** Detailed Description **** PPM 10.20.1 2 year Mechanical PM. During the DG1 maintenance window in Oct. 2019, some minor editorials were found in the procedure. This AR will track and revise PPM 10.20.1. No affect on any other EDG procedures. <I> **** Actions Taken **** Wrote this AR, red-lined affected pages of PPM 10.20.1 and attached. <N> **** Equipment Description **** DG1 and DG2 rooms | 02-00-DG-ENG-1A1,02-00-DG-ENG-1A2,02-00-DG-ENG-1B1,02-00-DG-ENG-1B2
401534 | CR | 20191120 |  | 4 | Local RMS for TMU-P-1B will not go to 'PTL' | N | N |  | N | YES | <D> **** Detailed Description **** Local control switch for TMU-P-1B will not stay pulled out in EMERGENCY STOP. | 02-00-TMU-RMS-P1B/LOC
401538 | CR | 20191120 |  | 3 | Turbine Lube Oil System Description needs correction |  |  |  | N | NO | <D> **** Detailed Description **** Turbine Lube Oil System Description SD000135, Rev 11, MR 3, Para V.C.2, describes an interlock that prevents turning gear operation if bearing header oil pressure is greater than 4.5 psig or if bearing lift oil pressure is less than 850 psig. This description should be changed to say the interlock prevents turning gear operation until the bearing header oil pressure is greater than 4.5 psig and bearing lift oil pressure is greater than 850 psig. As currently described, it is backwards from what actually occurs. <I> **** Actions Taken **** Investigated Instrument Master Data Sheet for TO-PS-TG and TO-PS-BL and the contacts close at 4.5 Â± 0.3 psig and 850 Â± 45 psig respectively. Recommend Severity 3 in accordance with GBP-CAP-01 to Operations Training to correct the system description.
401539 | CR | 20191120 | CAQ | C | Boundary error on M523-1 |  |  |  | N | NO | <D> **** Detailed Description **** M523-1 designates the pipe between RWCU-V-39 and RWCU-V-40 as Seismic 1, Quality Class 1. The only component in that section of pipe that has a safety function is RWCU-FE-40 and its associated flow transmitter equipment. RWCU-V-37 and 38, which are in this Seismic 1, Quality Class 1 pipe run, are test valves, and have no safety function. The proper designation is therefore for RWCU-FE-40 to be Seismic 1, Quality Class 1, while the rest of the piping should be Seismic 2+, Quality Class 2. The Code Group of C is still appropriate. Recommend assignment to AR-DMC to correct the flow diagram. Note: this SC,QC boundary was correct in Revision 89, but was changed as part of reverting the Code Group designation from D to C in revision 110 by EC 12061. <I> **** Actions Taken **** Researched history of changes to this section of pipe. Discussed this issue with the subject matter expert.
401540 | CR | 20191120 |  | 3 | Modifications are Required to PPM 1.5.4 |  |  |  | N | NO | <D> **** Detailed Description **** Several Modification are required to PPM 1.5.4. The equivalency table attachment 8.1 requires changes to support new M&TE that has been purchased. The small article monitor identified in section 4.1.8 substep k is no longer working. An alternate means of surveying potentially contaminated tools is needed. In section 4.4 substep 4.4.2 incorrectly uses the term Test Uncertainty Ratio (TUR) from the wording in the step what should be Test Accuracy Ratio (TAR) which is acceptable per ANSI Z540-1 . <I> **** Actions Taken **** Initiate CR. Communicated with Supplier Quality regarding the TUR description relating to calibration standards.
401547 | CR | 20191120 |  | 4 | E-TR-M1(2,3) subcomponent EPNs D031 Critical Equipment blank |  |  |  | N | YES | <D> **** Detailed Description **** Numerous E-TR-M1(2,3) subcomponent EPNs in Asset Suite MEL do not have the D031 Critical Equipment field filled out (currently blank instead of C, N, or R). Examples: E-CP-M1(2,3) E-P-MX/PY where X = 1, 2, 3 and Y = 1, 2, 3, 4. EPNs associated with EC PDC 11261 and EC PDC 12272. . This is an administrative issue - Asset Suite MEL should be updated. <I> **** Actions Taken **** This was noted as a delta during the 11/20/19 4th quarter ESP Pilot Session (question posed and answered during training). Had been noted during review of some EPNs associated with TMOD EC 18010. <N> AR-SMS 00401589 initiated to populate equipment criticality fields as described in this CR. | 02-00-E-CP-M1,02-00-E-CP-M2,02-00-E-CP-M3,02-00-E-P-M1/P1,02-00-E-P-M1/P2,02-00-E-P-M1/P3,02-00-E-P-M1/P4,02-00-E-P-M2/P1,02-00-E-P-M2/P2,02-00-E-P-M2/P3,02-00-E-P-M2/P4,02-00-E-P-M3/P1,02-00-E-P-M3/P2,02-00-E-P-M3/P3,02-00-E-P-M3/P4,02-00-E-TR-M1,02-00-E-TR-M2,02-00-E-TR-M3
401549 | CR | 20191120 |  | 3 | Evaluate the applicability of ODCM RFO 6.1.1.1 |  |  |  | N | NO | <D> **** Detailed Description **** The applicability for ODCM RFO 6.1.1.1 is â€œIn accordance with table 6.1.1-1.â€ Footnote D of table 6.1.1-1 states â€œwhen there is flow in the system identified by this function.â€ By defining the applicable mode or other specified condition this way it eliminates the need to perform the specified compensatory measures while there is no flow in the system. This includes required compensatory measure 6.1.1.1.C.2 which is to â€œrestore the channel to Functional status within 30 days.â€ This would allow SW -RIS-604, SW-RIS-605 or TSW-RIS-5 to remain non-functional as long as there was no flow in the system indefinitely. It would also not drive the 6.1.1.1.E.1 required compensatory measure to include the reason for the longer than 30 day out of service time in the Radioactive Effluent Release Report. <I> **** Actions Taken **** I recommend that Licensing and Chemistry evaluate whether or not the current ODCM wording properly supports the requirements for adding information to the RERR. After completing the evaluation I recommend using a licensing position paper to notify Operations on the appropriate way to implement these required compensatory measures until the ODCM and or bases can be updated.
401551 | CR | 20191120 | CAQ | D | Washington State EOC Dialup inoperable | N | Y |  | N | YES | <D> **** Detailed Description **** While performing the monthly test on the dialup phones, Washington State EOC could receive call but could not return the call. All other means of communication to Washington State EOC is available. <I> **** Actions Taken **** Notified EP and verified the phone curcuit on the EN side is good. Also notified Washington State EOC contact of this issue and they are working to resolve on their end. All other means of communication to Washington State EOC is available. Reccomend closing to the WR. <N> **** Equipment Description **** Washington State EOC Dialup Line
401553 | CR | 20191120 |  | 4 | Volume 16's sent to records not included on transmittal form |  |  |  | N | NO | <D> **** Detailed Description **** During the processing of surveillance records it was discovered that two completed Volume 16's had been sent to the Records Department under a transmittal that did not list them as included in the package <I> **** Actions Taken **** Notified the supervisor and wrote this CR. Returned the documents along with a copy of the transmittal to Radiological Services for correction
401554 | CR | 20191120 | CAQ | D | NRC phones not working during monthly testing | N | Y |  | N | YES | <D> **** Detailed Description **** The NRC phones have dial tone but announce the call cannot be completed after dialing. <I> **** Actions Taken **** Notified the MCR, EP, NRC, and Verizon. The Verizon tech indicated they had been makeing changes the day prior. Further testing later today reviled all the ciruits are back working. Recommend closing NCAQ-4 <N> **** Equipment Description **** Main Control room, and EP centers
401555 | CR | 20191120 |  | 3 | need to move ladder storage area 14.1 in RW 437" |  |  |  | N | NO | <D> ladder stored at 14.1 storage area in RW 437" interferes with the cables for ARM-RE-27 detector. This ladder storage rack needs to be relocated. This was identified during NRC walkdown documented on CR 4000987 <I> removed ladder and generated WR to relocate the ladder storage brackets. <N> LADDER STORAGE AREA 14.1 .. CR at INPROG. Approved CR, moved to SRO for OPS Review. WR generated. No further actions required.
401556 | CR | 20191120 | CAQ | D | Two surveillances received in records w/o final signature |  |  |  | N | NO | <D> **** Detailed Description **** During the processing of surveillance records, it was discovered that two surveillances had been sent to the Records Department without final assigned reviewer signature. Document numbers: CSP-INST-H201 & CSP-INST-D201 <I> **** Actions Taken **** Notified the supervisor and wrote this CR. Returned the documents to Radiological Services for correction.
401557 | CR | 20191120 | CAQ | D | A surveillance was sent to Records without final signature |  |  |  | N | NO | <D> **** Detailed Description **** During the processing of surveillance records, it was discovered that one surveillance had been sent to the Records Department without the final assigned reviewer signature. Document number: OSP-SW-C101 <I> **** Actions Taken **** Notified the supervisor and wrote this CR. Returned the documents to Operations for correction.
401558 | CR | 20191120 |  | 3 | CMS-RIT-12A IMDS needs update |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** The Noble Gas detector for CMS-SR-20 was replaced per WO# 02128123. Please update IMDS to reflect new values from calibration sheet provided from vendor. <I> **** Actions Taken **** DIscussed with Supervision and Engineering. Wrote CR to document.
401559 | CR | 20191120 |  | 3 | Tenant Co-Location Agreement Cannot Be Located |  |  |  | N | NO | <D> **** Detailed Description **** A co-location agreement with DOE/MSA to use a portion of the Telecommunications Equipment Center (TEC) at APEL cannot be located. <I> **** Actions Taken **** Verified all other tenant co-location agreements are available. Started process to generate new agreement.
401562 | CR | 20191120 |  | 4 | Heat Trace Panel HT-HTP-PTM/29 Low temp Lights Flashing | N | N |  | N | YES | <D> **** Detailed Description **** When electrical craft in support of I&C on investigating of low temp lights flashing on HT-HTP-PTM/29 they discovered 3 term blocks that have been destroyed due to excessive heat and need to be replaced located on the juction box above the panel for circuit B10-1, also on futher investigation craft also discovered a 120 volt contactor that need to be replace due to a sticky contact (C6-10) for circuit 10 <I> **** Actions Taken **** Craft notified supervisor of findings and create CR & WR for corrections of items needed to be replaced. Craft supervisor notified system engineering and planning supervisor. | 02-00-HT-HTP-PTM/29
401565 | CR | 20191120 | CAQ | C | FP-CP-FSP10 capacitor relocation failed | N | Y |  | N | YES | <D> **** Detailed Description **** WOT# 02139652-07 was planned to relocate the End Of Line (EOL) capacitors (2 each) in FP-CP-FSP10. The first capacitor was relocated and tested on the M2 module (zone 66B) in the panel - no issues. However, after the second capacitor was relocated, the Trouble light would not extinguish on module M3 (zone 66D). The work package was revised to replace the capacitor, with the same results. Discussed with Engineering and decided to restore the capacitor to original configuration to verify the Trouble light would extinguish, which it did. <I> **** Actions Taken **** Zone 66D at FP-CP-FSP10 has been restored to pre-work order status and is back in service. No Trouble or Fire alarms currently exist for this panel. Need to further investigate why this circuit did not function appropriately with the capacitor in the new configuration. <N> This CR documents an issue with an EC during installation. System was restored to original configuration for the issue documented in this CR. FP-CP-FSP10 is Functional for LCS 1.10.2, Essential Sprinkler Suppression (P66). PMT for revised work instructions to restore to pre-EC condition completed SAT. | 02-00-FP-CP-FSP10
401567 | CR | 20191120 |  | 3 | Reword ENG-DES-50 paragraph 3.12.1 for FCRs |  |  |  | N | NO | <D> **** Detailed Description **** Existing PPI PPM ENG-DES-50 paragraph 3.12.1 wording (added via R002 of the SDP Interface Procedure) requires processing of a Field Change Request (FCR) to change modification Engineering Changes (EC) after their approval (even for administrative typographical errors) unless the the changes were planned. This AR CR 401567 is initiated per request of the Design Engineering Manager to reword ENG-DES-50 paragraph 3.12.1 for FCRs and allow processing of EC Revisions without FCRs for more than planned changes. NOTE: Changing ENG-DES-50 paragraph 3.12.1 will also require update of SharePoint SDP Guidance for EC REVISIONS. . This is an administrative process procedure.
401568 | CR | 20191120 | CAQ | D | FP-ENG-1 oil press switch ground pulled off during shipment | N | Y |  | N | YES | <D> **** Detailed Description **** While installing engine after off site repair (02154736-12) noticed that the oil pressure switch ground was pulled out of the lug. Need to replace lug and reattach wire <I> **** Actions Taken **** notified Operations and Maintenance <N> **** Equipment Description **** CWPH | 02-00-FP-ENG-1
401569 | CR | 20191121 | CAQ | D | DG2 South Bearing Oil High | Y | N |  | N | YES | <D> **** Detailed Description **** During OSP-ELEC-M702 the DG2 south bearing oil level was noted to be above the high scribe mark on the sight glass by about 1/16â€. This is high out of spec per the log notes. Additionally, there was no noted frothing in the sight glass and the south bearing temperature was less than then north bearing temperature. Recommend draining a small amount of oil from the bearing. <I> **** Actions Taken **** Notified CRS and SM. | 02-00-DG-ENG-1B2
401570 | CR | 20191121 |  | 4 | S-DOOR-S104 Degraded | N | N |  | N | YES | <D> **** Detailed Description **** S-DOOR-S104 is a non-plant fire door between the RCA enterance and the HP area. The door will not close under its own force. It remains ajar on the latch. <I> **** Actions Taken **** Notified MCR and issued FPSI 19-0043 | 02-00-S-DOOR-S104
401571 | CR | 20191121 | CAQ | D | Security Power Panel 61 Tamper | N | Y |  | N | YES | <D> **** Detailed Description **** Security Power Panel 61 Tamper is not funtioning as designed. Contact Security at extension 2185 for further details. <I> **** Actions Taken **** Security Supervision notiffied, compensatory measures posted, CR/WR generated for Electrical support. | 02-00-SEC-TAS-ES61T
401572 | CR | 20191121 |  | 4 | Lock on TMU Pump House Gate | N | N |  | N | YES | <D> **** Detailed Description **** The Lock on the TMU Pumphouse Gate was found broken when Ops 4 was performing rounds on 11-20-19. gate was temporarily held closed with a red seal while a replacement lock was obtained. <I> **** Actions Taken **** Supervison Notified CR Generated UPDATE: The lock was replaced by the equipment operator responding to the location. <N> **** Equipment Description **** Lock on TMU Pump House Gate
401580 | CR | 20191121 | CAQ | D | Malfunction IDS 20 21 | N | N |  | N | YES | <D> **** Detailed Description **** Malfunction IDS 20 21 Contact Security at x2185 for details <I> **** Actions Taken **** Compensatory Measures Initiated, Security Supervision Notified, Maintenance Notified | 02-00-SEC-IDS-EVAL/20/21
401581 | CR | 20191121 | CAQ | D | M&TE OOT |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0059012 Stephens Analytical Hygrometer- model 600 DDL Dewluxe found OOT & adjusted within specs. EFIN EVAL: M&TE was not responding. No Data could have been taken, thus no erronous data. DEF #7369A written. No Plant Impact. No Action Required. <I> **** Actions Taken **** None Trending purposes only.
401582 | CR | 20191121 |  | 3 | Security Weapon sight needs maintenance |  |  |  | N | YES | <D> **** Detailed Description **** The Aimpoint sight on rifle 320 is not functioning as designed <I> **** Actions Taken **** Rifle removed from service, delivered to the range for repair, CR/WR generated <N> **** Equipment Description **** Building 88
401583 | CR | 20191121 |  | 3 | OCA 89 AutoFocus |  |  |  | N | YES | <D> **** Detailed Description **** OCA 89 AutoFocus, please contact Security for details x2185 <I> **** Actions Taken **** Security Supervision Notified, Security Programs Supervisor Notified <N> **** Equipment Description **** OCA 89 not 90 Resolved issue under WR 29152609.
401584 | CR | 20191121 |  | 3 | Missed Hydrogen Peroxide Addition to Standby Service Water |  |  |  | N | NO | <D> **** Detailed Description **** Hydrogen peroxide delivery and addition were scheduled to take place on 11/21/2019. Order was placed with vendor but did not get fully communicated to the distribution parties, as a result the delivery will be rescheduled to a later date. CR written for trending purposes. <I> **** Actions Taken **** Notified chemistry, notified supervisor, notified scheduling, notified CRS, questioning vendor to find out root cause to avoid repeat event. <N> The hydrogen peroxide delivery was rescheduled for 11/26/19. The shipment of hydrogen peroxide was received on 11/26/19. Both hydrogen peroxide tanks were filled and the balance of the chemical was added to the SSW ponds for system treatment. This CR will be closed with no assignments for trending.
401586 | CR | 20191121 |  | 3 | WCI-4 Level B Criteria is Subject to Interpretation |  |  |  | N | NO | <D> **** Detailed Description **** WCI-4, Online Work Control Process; Attachment 4.3, Graded Approach to Scheduling; Level B Criteria, â€œPotential high dose activitiesâ€ is up for interpretation. There is no clear guidance on what is called high dose and could be based on an individualâ€™s or groupâ€™s perception. <I> **** Actions Taken **** Informed Radiological Supervision <N> The guidance in this procedure is meant to communicate the need to assign schedule grade codes in this case. The assignment of that schedule grade code is the responsibility of the work group that owns the activity with final approval coming from the WWM. These GSA codes are typically aligned upon in our work management forcing function meetings, particularly T-3. The procedure should not be updated with specific limitations on dose, dose rates, contamination levels, etc for assignment of GSA coding as this would be too specific for the intent of the guidance.
401590 | CR | 20191121 |  | 3 | MOT-TURB-1-1 has macros not working properly |  |  |  | N | NO | <D> **** Detailed Description **** While performing annual review of AED PMO MOT-TURB-1-1 under AR 396252-03, it was discovered that programming internal to the document was involuntarily placing information into incorrect fields on other tabs. Changes made on one tab has the effect of inserting the same information into seemingly random fields in another tab resulting in the correct information being overwritten. There were three mid-year updates that were noted for the next revision. It is now recognized that the corrections required for these updates are likely the result of the issues with the file; however, the MOT cannot be revised until this condition is corrected. <I> **** Actions Taken **** Sought out individual in Equipment Reliability that may own the spreadsheet, but the person was out of the office. Sent an email inquiry and included supervisor. <N> Checked the file for MOT-TURB-1-1 and the MOT template file. There were no Macros found in either file, with the exception of a custom Macro/code to print file. The macro for print file was not in use when the issue occured. There was no other code in the file. Showed and communicated this information to CR initiator.
401591 | CR | 20191121 |  | 4 | SA-DY-1 1st stage trap indicator lit | N | N |  | N | YES | <D> **** Detailed Description **** SA-DY-1 1st stage trap indicator is lit. Recommend investigate and repair. <I> **** Actions Taken **** Informed shift supervision, generated AR/WR. | 02-00-SA-DY-1
401592 | CR | 20191121 | CAQ | C | Received P603-A8 4-8, SLC-TANK TEMP HIGH Alarm | Y | N |  | N | NO | <D> **** Detailed Description **** During performance of SOP-SLC-SPARGE/LEVEL to support WO 02136898, annunciator P603-A8 4-8, SLC-TANK TEMP HIGH/LOW alarm was received. The alarm setpoint is 140 F. Per SOP-SLC-SPARGE/LEVEL 135 F should not be exceeded. <I> **** Actions Taken **** Placed SLC-RMS-EHC/2/3 in AUTO.
401595 | CR | 20191121 |  | 4 | (FP) (NEIL 2019) COND-P-4 oil leak | N | N |  | N | YES | <D> **** Detailed Description **** During the 2019 NEIL inspection, the inspectors identified a leak on COND-P-4 that was not noted into the fluid leak management listing. <I> **** Actions Taken **** CR created, supervision notified | 02-00-COND-P-4
401598 | CR | 20191121 |  | 3 | New requirement to PPM 10.25.19 not promulgated |  |  |  | N | NO | <D> **** Detailed Description **** Rev 027 issued 11-21-19 added new requirement to take pictures of all DETERM/RETERMS (page 81, Attachment 9.10 step 2.1.2). Affected personnel were not informed of this new requirement nor were the 100s of affected procedures, instructions, forms and MWOs updated to be in alignment with PPM 10.25.19. Also typo that supervisor can "wave" requirement. <I> **** Actions Taken **** Once informed, supervision is setting up meeting to discuss the new requirement and actions needed. Recommend CR to MNTPROG.
401599 | CR | 20191121 | CAQ | C | FP-ENG-1 Oil Pressure |  |  |  | N | YES | <D> **** Detailed Description **** After rebuilding FP-ENG-1, while running the PPM 15.3.9 for one hour flowing 2000 GPM at 128 PSI (Full FP-P-1 pump rated flow/pressure), FP-ENG-1 oil pressure was observed at 50 PSI. 50 PSI falls within the acceptable range of literature provided by Cummins. Ops procedures that require recording the engine oil pressure on FP-ENG-1 will need to be updated to reflect the new normal operating oil pressure. Assign to FP (AR-TEFP) to work with Ops procedure writers for the change. <I> **** Actions Taken **** Initiated CR. <N> **** Equipment Description **** CWPH | 02-00-FP-ENG-1
401601 | CR | 20191121 |  | 4 | RCC-F-1 filters causing elevated system pH | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** PER SWP-CHE-02 RCC pH for the system has been continuously going above the Closed Cooling Water action levels. The only way to recover from the high pH is to replace the demineralizer which costs roughly $10,000 dollars each time with materials and labor. Chemistry has investigated all the potential causes of the pH problems and has determined that the filters in the RCC-F-1 could be the cause. The system was tested for anions, cations, micro biologicals, and (TOC)total organic carbon (which could all be contributors to the rise or fall of pH). TOC was the only contaminate to be found out of the ordinary for demineralized water.The current filters used in the RCC-F-1 station were rinsed and the rinse water was Need new particulate filters for RCC-F-1. See AR EVAL 401597 PER SWP-CHE-02 RCC pH for the system has been continuously <I> **** Actions Taken **** Informed Chemistry Supervision, System engineer, and chemistry specialist.
401604 | CR | 20191121 |  | 3 | POSSIBLE GAP IN STELLITE MATERIAL EVALUATION PROCESS |  |  |  | N | NO | <D> **** Detailed Description **** THIS IS NOT A PLANT EQUIPMENT ISSUE. THIS CR APPLIES TO NEW REPLACEMENT COMPONENTS THAT ARE IN THE MANUFACTURE STAGE AND NOT INSTALLED IN THE PLANT. There is a possible process gap in PPM 1.11.24 IMPLEMENTATION OF COBALT REDUCTION PROGRAM. The new RRC pump rotating assemblies being procured from Sulzer Pump have stellite clad material on the pump shaft sleeve. The process listed in PPM 1.11.24, section 4.12, does not appear to account for long lead procurement items to perform the cobalt evaluation in time to allow for the use of alternative materials if available. This gap could possibly occur with other long lead items that are not being procured as a design change. Recommend assignment to RP. <I> **** Actions Taken **** This concern was addressed at the 11/21/19 RRC project steering committee meeting with recommendation that a CR should be submitted to capture this. The remaining steps in PPM 1.11.24 will be completed to include submitting for approval the required Waiver For Cobalt Containing Materials form.
401605 | CR | 20191121 |  | 4 | TOA-FL-1A is EOR | N | N |  | N | YES | <D> **** Detailed Description **** The left hand side of TOA-FL-1A is at End of Roll with HVAC alarm sealed in. The right hand roll is near end as well. <I> **** Actions Taken **** Acknowledged alarm. | 02-00-TOA-FL-1A
401606 | CR | 20191121 |  | 3 | CPR-TK-92B "resin Total" in question. | N | N |  | N | YES | <D> **** Detailed Description **** While transferring the resin from CPR-TK-92B the following para meters were noted. Level in the tank was 49% (218 gallons/%). Resin in the tank was listed as 258 cuft3. The tank was recirced for approx. 50 minutes then resin transfer was started. The Resin stream into the cask showed no color or indication of resin and appeared to be all water. Level in CPR-TK-92B was slowly transferred to the cask until the the low level alarm trip of the pump occurred at 13%. The level of resin in the cask was best guessed at 60 cubic feet since it was well below the measuring ruler installed in the cask. This would leave a total of 198 cubic feet in CPR-TK-92B. Its believed the amount of resin in the tank is far less then that based on the amount of resin deposited in the cask for the volume of water transferred. Please evaluate and instruct the logs to be changed as appropriate <I> **** Actions Taken **** Discussed our indications and combined our inputs for the <N> **** Equipment Description **** calculated CPR-TK-92B resin level
401607 | CR | 20191121 | CAQ | C | Discrepancy with operator actions in PPM 5.6.2 | N | Y |  | N | NO | <D> **** Detailed Description **** The purpose of this CR is to identify a discrepancy in PPM 5.6.2 (Station Blackout). Were a complete loss of AC power to occur, PPM 5.6.1 directs Operations to declare either an SBO or ELAP, AND shed load per PPM 5.6.2 attachment 8.4. The issue arises where attachment 8.4 is not specific to an SBO, ESBO, or ELAP. For ELAP, attachment 8.4 was updated to shed E-B1-2 and E-B1-7 to reduce heat generation in the main control room for extended habitability. This becomes an issue if an SBO is declared, because E-B1-2 is credited equipment for coping with the SBO scenario, and E-B1-7 is desirable to maintain the capability to remotely operate circuit breakers required for the DG3 cross tie (ESBO). As 5.6.2 attachment 8.4 is currently written, operators would shed credited coping equipment during an SBO event, or take away the capability to remotely operate circuit breakers required for the ESBO DG3 cross tie. <I> **** Actions Taken **** Discussed issue with operations day shift manager. Recommend revising attachment 8.4 to be scenario specific for determining which equipment to load shed.
401608 | CR | 20191121 |  | 3 | Truck with trailer backed into guardrail |  |  |  | N | NO | <D> **** Detailed Description **** A truck with trailer carrying the 14D-2.0 empty cask was attempting to back into the 437â€™RW truckbay and came into contact with a temporary guardrail. The trucks passenger side bumper and wheel made contact with the temporary guardrail leaving a small dent on the bumper. The temporary guardrail did not appear to be damaged. A spotter positioned behind the trailer attempted to alert the driver the truck was getting close to the temporary guardrail but the driver was unable to stop in time. There was no danger of personnel injury at any time. Spotter was at a safe distance from the moving vehicle. This is not a plant equipment issue. <I> **** Actions Taken **** Put truck and trailer and safe position and informed supervision.
401609 | CR | 20191121 |  | 4 | CL-V-46 Leak | N | N |  | N | YES | <D> **** Detailed Description **** There's a small leak from the threads on the pipe nipple between the hose connection and CL-V-46. This was identified by the delivery personell, who thinks it may eventually degrade into a spray. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** CWPH | 02-00-CL-V-46
401610 | CR | 20191121 |  | 4 | HS-V-W60 Inlet Strainer Elbow Dripping | N | N |  | N | YES | <D> **** Detailed Description **** During system walkdown, it was identified that the inlet strainer elbow HS-V-W60 is dripping at approximately 1 drip every 9 seconds. Currently, there is a drip pan below the leak. <I> **** Actions Taken **** Initiated this AR. <N> **** Equipment Description **** RW 507' | 02-00-HS-V-W60
401612 | CR | 20191121 |  | 4 | Device FP-AN-B80/1 | N | N |  | N | NO | <D> **** Detailed Description **** While performing ppm 15.2.22 during the audible testing portion of the procedure, building 80 B80/1 device was not audible during the alarm. <I> **** Actions Taken **** notified supervisor and documented with this CR
401613 | CR | 20191121 |  | 3 | Outage PMs Require Review & Clean-Up |  |  |  | N | NO | <D> **** Detailed Description **** On 11/21/19, in the 0615 Daily Production Package and Jeopardy Report, it was noted that an Outage PM (WO 02110117, PMID 19631-01) for Condensate Oil Samples (Predictive Maintenance) went late on 11/18/19. Immediate investigation concluded that this specific PM had an AR-SMS performed (379464; initiated on 4/26/18) to defer to R25. This new WO (02141847) has a good late date of post-R25. . See EDMS for PSOâ€™s initial investigation. File â€œOutage PMs Sorted by PMID (late dates before R25) - As of 191121.pdfâ€ lists all PMs that have a late date either in the past or one prior to R25. Of these PMIDs, one (1) has a late date due tomorrow (AR-SMS 401611) and two (2) have no late dates identified. Late dates in the past are highlighted in YELLOW. Late dates that are post-R25 are highlighted in GREEN. <I> **** Actions Taken **** Notified Maintenance & PSO supervision. Performed initial extent of condition review. Reviewed condition / findings with SM, WWM, and PSO. Generated AR-SMS. Generated CR. . Recommend assignment to Maintenance Programs, PM Program to review all Outage PM WOs that are scheduled to go late prior to R25, validate these PMs have current WOs with due dates post-R25, cancel unnecessary WOs, and address subject PMIDs to prevent recurrence for R26 and beyond.
401614 | CR | 20191121 | CAQ | D | Rod accumulator trouble alarm for CRD-HCU-5415. | Y | N |  | N | YES | <D> **** Detailed Description **** ROD ACCUMULATOR TROUBLE, H13-P603.A7.6-7, alarm for CRD -HCU-5415 was due to high water level. OPS 2 has drained accumulator per SOP-CRD-HCU and the alarm is clear. <I> **** Actions Taken **** Informed CRS, wrote this CR and WR. | 02-00-CRD-HCU-5415
401615 | CR | 20191121 | CAQ | C | Radiation Area Posting Removed From Boundary Loaction |  |  |  | N | YES | <D> **** Detailed Description **** Upon performing the weekly walk down of the RX Bldg. 572â€™, HP identified a Radiation Area posting on a stanchion that had been removed from the desired boundary location. The postings normal position is located in the middle of the walk-way in-between the ROA Filter Plenum and the MCC Room. The posting had been moved and placed in front of drywell containment wall next to the MCC Room. According to GEN -RPP-04, section 3.10, only RP personnel should install, remove or alter radiological postings and barriers. <I> **** Actions Taken **** HP placed the boundary posting in the proper orientation and location upon recognition of the finding. HP Supervision and the Shift Manager have been informed. <N> **** Equipment Description **** RX 572'
401616 | CR | 20191122 |  | 4 | CW de-halogenation skid stopped CW B/D | N | N |  | N | YES | <D> **** Detailed Description **** CW B/D stopped - appears to be a result of CW B/D CL2. See EDMS for plot from EDNA points 11/22/19 0328 dm | 02-00-CL-SKID-2
401617 | CR | 20191122 |  | 4 | Security BRE 37 hand rail heaters need maintenance | N | N |  | N | YES | <D> **** Detailed Description **** Security BRE 37 hand rail heaters are inoperable and need maintenance. <I> **** Actions Taken **** CR/WR initiated. Security supervision notified. <N> **** Equipment Description **** Security BRE 37. Contact security for details.
401618 | CR | 20191122 |  | 4 | Circulating Water Chemistry Trouble | N | N |  | N | YES | <D> **** Detailed Description **** Circulating Water Chemistry Trouble alarm came in and OPS4 was dispached to CW HAL/DEHAL Skid to verify all automatic actions. HAL/Dehal chemical inlet isolation valves were found to still be open; automatic actions in 4.840.A4 Drop 9-5 states that they should be closed. <I> **** Actions Taken **** Supervison Notified CR/WR Generated . DECL-MV-01, -02, -03 did not close as described in 4.840.A4 drop 9-5. <N> **** Equipment Description **** DECL-MV-01/02/03
401622 | CR | 20191122 |  | 4 | D-DOOR-D114 knob came off | N | N |  | N | YES | <D> **** Detailed Description **** D-DOOR-D114 knob came off. Knob was pushed back on and appears to be on, but expect it will again come off. Previously door has had the same problem (29018507) and was dissassembled and reassembled. Door is frequently opened. | 02-00-D-DOOR-D114
401623 | CR | 20191122 | CAQ | D | CCH-CR-1B upper oil glass was full (trend CR) | Y | Y |  | N | YES | <D> **** Detailed Description **** CCH-CR-1B upper oil glass was observed to be full when taking the OPS2 readings. the Log direct running the Aux Oil Pump until the level is lowered to 1/8 inch above the bottom of the sight glass and then to document the action with a "trend only CR", this is that CR. also of note the Chiller was secured the prior shift. <I> **** Actions Taken **** wrote cr, recommend "Trend only". | 02-00-CCH-CR-1B
401624 | CR | 20191122 |  | 4 | ROA-HC-2 has a water leak off part return piping | N | N |  | N | YES | <D> **** Detailed Description **** ROA-HC-2 has a water leak off part return piping the leak appears to be from a 1.5 inch to 0.5 inch reducer if I am looking at the prints. If I am looking at the piping, it is between where it comes out of the ventilation and the first valve HCO-V-R8A on a verticle piece of pipe. location of the leak does not allow easy access or viewing from the ladder it appears to be a threaded connection. will need scaffolding due to the height of the valves and piping. <I> **** Actions Taken **** wr | 02-00-ROA-HC-2
401625 | CR | 20191122 |  | 4 | COND-V-156A is leaking by 1 drop/5 sec | N | N |  | N | YES | <D> **** Detailed Description **** COND-V-156A is leaking by at rate of approximately 1 drop every 5 seconds. This is the COND-P-2A discharge drain valve. The leakage is contained to the pump pedestal. I verified the valve is fully shut with no change in leak rate. See EDMS for video. <I> **** Actions Taken **** Informed CRS. wrote AR. | 02-00-COND-V-156A
401626 | CR | 20191123 | CAQ | D | Received Oscillograph Started, H13-P800.C4.4-3, alarm. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** Received Oscillograph Started, H13-P800.C4.4-3, alarm. Plant controllers and equipment response was normal. Startup and Backup voltages are as follows: E-TR-S A: 238 B: 235 C: 238 E-TR-B A: 117 B: 117 C: 118 The following sensors were tripped and are reset: J7 - 500KV Neutral Ground Overcurrent and J12 - SM-8 Under voltage BPA reports the following: a. Cause was Ash Marion #2 500KV Tripped to Lockout at 02:55, Coyote Spring SLATT Tripped to Lockout at 02:59, and Ash Flat #1 tripped to lockout at 03:19 b. Relaying involved a single pole for Ash Marion and Multiphase fault for Coyote Spring and Ash Flat. c. unknown if damaged equipment d. Ash Marion attempted line reclose but failed and locked out. All others were locked out. e. emergent outage needed? - unknown at this time but most likely f. NO 230kv or 115kv involved g. line equipment outage most likely needed h. Does the outage affect the 230kv or 115kv grid - NO i. 02:55, 02:59, 03:19 j. 500 KV k. RAS initiated - YES - Reactive Switching and ATC OFF l. Grid frequency change - unknown <I> **** Actions Taken **** Dispatched OPS-2 Identified Sensors Performed walkdown Contacted BPA Initiated CR
401628 | CR | 20191123 |  | 3 | Evaluation for chock requirement on RW 507 | N | Y |  | N | YES | <D> **** Detailed Description **** Wheel chocks are not required in the RW 507 "Basketball Court," per 10.2.222, Seismic Storage Requirements for Transient Equipment. However, PRM-SR-1 (Stack Monitor Skid) and E-TR -8FB/1 were recently installed in that area . E-TR-8FB/1 is classified as a Critical Digital Asset, and it along with PRM-SR-1 provide Post Accident Monitoring functions. There are STAY CLEAR areas around these two units, and it is possible that equipment can hit them during a seismic event. See attached photos. Please evaulate if "no wheel chocks required" is still appropriate. . <I> **** Actions Taken **** Notified CRS <N> **** Equipment Description **** RW 507
401629 | CR | 20191123 | CAQ | D | HPCS-GEN-DG3 roof leak | Y | N |  | N | YES | <D> **** Detailed Description **** There is a roof leak on the South side of the HPCS-GEN-DG3 room. The leak is coming from one of the roof equipment plugs. With very light rain outside, the plug was leaking at a rate of ~ 3 drops per second. The leakage is not falling onto any of the HPCS-GEN-DG3 equipment. See EDMS for Pics. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** HPCS-GEN-DG3, South of Generator | 02-00-HPCS-GEN-DG3
401630 | CR | 20191123 | CAQ | D | FP-M-P/2B pump vib install | N | N |  | N | NO | <D> **** Detailed Description **** new disk will need to be installed once the pump is installed due to proper oriatation and accessibiility. 02046143 15 <I> **** Actions Taken **** cr <N> **** Equipment Description **** FP-M-P/2B
401631 | CR | 20191123 |  | 4 | Flocculator paddlewheel seal leakage degrading | N | N |  | N | YES | <D> **** Detailed Description **** The leak from the Flocculator paddle wheel seal is severely degrading. This could degrade to the point where we could not maintain level in the flocculator, preventing us from making Potable Water. This issue was written up in July on AR #396774. It does not seem like anything has been done about it yet. See EDMS for video. <I> **** Actions Taken **** Informed MCR. Wrote AR. <N> **** Equipment Description **** Flocculator paddle wheel seal
401632 | CR | 20191124 |  | 4 | RWCU-V-214A Packing Leak | N | N |  | N | YES | <D> **** Detailed Description **** Discovered puddle of water underneath RWCU-V-214A, which is just inside the RW 467' RWCU Holdup Pump Rm gate. The gate is posted LHRA, CA. There was an RWCU-DM-1A backwash/precoat that ended on 11/23/2019 @ 0300. There was not an active drip when observed tonight, but it was wet around the base of the valve and puddled on the floor below. The RWCR Operator peer checked the valve EPN tag for me and I volunteered to initiate this AR/CR. The floor area directly outside the gate was verified to be <1kdpm/pa-LAS. <I> **** Actions Taken **** Informed Operations and initiated this AR/CR. <N> **** Equipment Description **** RWCU-V-214A
401637 | CR | 20191124 |  | 4 | Model work order(s) deficiencies |  |  |  | N | NO | <D> **** Detailed Description **** During a review of PMID 15850-01 DEHSYS186, Oil Analysis and PMID 12673-04 TO-TK-2 Obtain Oil Sample multiple issues/corrections were identified that need to be made to upcoming work orders and model work orders. . SWP-ENV-03 was superseded by GBP-ENV-17. Documents panel and work instructions in both model work orders need to be updated with the correct reference. The MSDSâ€™s are now SDSâ€™s and need to be updated in the documents panel of both work orders so they can be printed. Additionally PMID 15850-01 work instructions include PPM 8.1.4 which is HISTORY and no longer exists. Current upcoming work orders have been returned . Recommend assignment to planning to correct model work orders and work instructions. <I> **** Actions Taken **** Notified planning initiated CR <N> All models have been updated and taken back to Approved with Requisite holds in place.
401638 | CR | 20191124 | CAQ | C | TEA-SR-26 Failed Leak Check | N | Y |  | N | YES | <D> **** Detailed Description **** During the performance of 16.2.1 TEA Low Range Noble Gas Monitor Channel 1 CC/RC the vacuum test failed per step 7.3.12. <I> **** Actions Taken **** Per step 7.3.13 initiating a CR/WR to repair leaks and re -perform leak checks. <N> **** Equipment Description **** TEA-SR-26 RW 525 <R> REP/REGE cancelled as this is ODCM related not TS. No past operability review needed | 02-00-TEA-SR-26
401639 | CR | 20191124 |  | 4 | CAS-C-1C oil level is at Minimum spec | N | N |  | N | YES | <D> **** Detailed Description **** CAS-C-1C oil level is at the Minimum spec of 1/8 th full. Please add oil to 1/2 full (with CAS-C-1C shutdown). Per the Operator logs, CAS-C-1C is operable until oil level is out of sight low. No abnormal oil leakage/usage was noted. The last AR generated to add oil to CAS-C-1C was from 7/4/19. <I> **** Actions Taken **** Informed MCR. Verified oil level is not out of sight low. <N> **** Equipment Description **** TG 441E | 02-00-CAS-C-1C
401640 | CR | 20191124 |  | 4 | COND-CB-CB2B OPEN light socket is broken | N | N |  | N | YES | <D> **** Detailed Description **** COND-CB-CB2B OPEN light socket has broken away from the CB door. This issue has been identified since 12-12-15, ref. WR# 29125725 and WO 02091793. Both the WR and WO are at a Cancelled status with no work being done. There is no indication of the work being tracked by any other open work documents. Please repair this light socket. <I> **** Actions Taken **** Informed MCR. <N> **** Equipment Description **** TG471W | 02-00-COND-CB-CB2B
401641 | CR | 20191124 |  | 3 | esoms LCO tracking summary admin issue |  |  |  | N | YES | <D> **** Detailed Description **** The esoms LCO tracking summary that gets printed with the CRS and SM turnover logs continues to have data that has been closed and should be automatically removed from the report. T19-E-PP-7AF, T19-FOB-E-PP-7A-001, T19-R24-RRC -A/B-001, and T19-R24-SM8-MAINT-001 are still showing as active in the turnover report, however these have been closed for some time and need to be removed to ensure accuracy of the turnover report. <I> **** Actions Taken **** CR written <N> **** Equipment Description **** esoms server
401642 | CR | 20191124 |  | 4 | Constant Tamper Alarm on HOSTCAB1T | N | N |  | N | YES | <D> **** Detailed Description **** CAS has a constant Tamper Alarm on Host Cabinet 1, request electrical maintenance to investigate. Contact x2185 for further information <I> **** Actions Taken **** CR/WR Generated | 02-00-SEC-CAB-HOST/1
401643 | CR | 20191124 | CAQ | D | TG-H2IS-1 channel 4 indicates Failed. | N | N |  | N | YES | <D> **** Detailed Description **** TG-H2IS-1 channel 4 reads "Fail" with audible alarm. All other channels read "0" (which is normal). Channel has the temp mod probe attached to it for the exciter housing. <I> **** Actions Taken **** Attempted to reset with no affect. Use atmosphere detector to verify no H2 leakage at housing. Informed CRS. Added a temp log to verify no H2 leakage twice a shift. | 02-00-TG-H2IS-1
401644 | CR | 20191124 | CAQ | C | Received RHR A OUT OF SERVICE ALARM | Y | Y |  | N | YES | <D> **** Detailed Description **** The MOV NETWORK POWER LOSS/OL BISI in. All valve indications in the MCR for RHR A are normal. Field investigation showed all applicable disconnects are closed. It appears that contacts 1 and 2 are closed on RHR-RLY-80/V17A (the relay appears de-energized) while all other accessible relays appear to be energized and normal. Unable to verify the status of RHR-RLY-80/V73A and RHR-RLY -80/V74A as they are located in TB-R463 which is in the overhead of MCC-7BB room behind a hanging light fixture. | 02-00-RHR-RLY-80/V17A
401645 | CR | 20191125 |  | 3 | SOP-CW-OPS suggested enhancements |  |  |  | N | NO | <D> **** Detailed Description **** The first note in section 5.8 states that CW Blowdown should be stopped prior to halogenation of the CW or TSW systems. Blowdown should not need to be secured if the dehalogenation system is functioning correctly. Also pushing the E-STOP button generates 840.A4.9-5 CW CHEMISTRY TROUBLE alarm. An additional note should be considered to alert operators to the expected alarm.
401655 | CR | 20191125 | CAQ | D | SFS-CP-ISFSI/TMS has yellow alarm on Ambient Temperature | Y | N |  | N | YES | <D> **** Detailed Description **** SFS-CP-ISFSI/TMS has yellow alarm on Ambient Temperature for BLDG 104 Room Temperature. | 02-00-SFS-CP-ISFSI/TMS
401656 | CR | 20191125 | CAQ | D | FP-P-2B initial acceptance inspection could not be performed |  |  |  | N | YES | <D> **** Detailed Description **** The task to perform initial acceptance inspection of new FP-P-1B pump/motor assembly. Reference section D of EC 17870, and section D of EC 17692 could not be performed. QC would not sign for the acceptance inspection due to pump and motor assembly not being released from the warehouse with an acceptance tag. <I> **** Actions Taken **** Notified WWM initiated CR <N> Engineering reviewed test results for the motor performance test and the pump performance test. Based on these test results, engineering waived the witness point for testing the specific pump/motor combination. Pump Serial Number 12300713-1, and motor Serial Number A02 20181526-0001 R0001 are an acceptable combination for installation. The issues discussed in this AR-CR were resolved in OSD&D 16293 to get the motor/pump green tagged, which is cross referenced. | 02-00-FP-P-2B
401660 | CR | 20191125 |  | 4 | MT-ELEV-3, (TG Elevator), is broken. | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-3, (TG Elevator), got stuck on 471TG. People were trapped inside. We could get the outer door opened but not the inner door. The door was finally opened by applying a large amount of force to the door in the Shut Direction. This caused the door to open by its own power. The Outer Door does not appear to be locking up with the inner door properly. | 02-00-MT-ELEV-3
401661 | CR | 20191125 |  | 4 | NRC identified broken knob on D-DOOR-D114 | N | N |  | N | YES | <D> **** Detailed Description **** The NRC identified a broken door knob on D-DOOR-D114 (DG1). D-DOOR-D114 is NOT labeled as a Fire Door or Flood Barrier. D-DOOR-D114 seperates the DG1 switchgear area from the DG1 Engine area. An alternate entry is available if this door were to fail closed. The Door knob was forced back into place and is working at the moment. Unfortunately, a repeat failure is very likely. Significant force is routinely applied to Open this door. Please replace this door knob to prevent future failures. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** DG1 room | 02-00-D-DOOR-D114
401663 | CR | 20191125 | CAQ | C | FLOWSERVE 10CFR PART 21 - DEVIATION FOR ASME III VALVES | N | N |  | N | NO | <D> **** Detailed Description **** During review of AR-OER 399793 (NRC PART 21 - Flowserve VALVE MANUFACTURE ACCEPTANCE CRIT), it was determined that a deviation exists, potentially affecting ASME Section III valves supplied by Flowserve to CGS as Basic Components (that may be installed in the plant or in the warehouse as spares). The issue as documented in the 10CFR Part 21 notification is "Use of Base Material Acceptance Criteria in Lieu of Welding Acceptance Criteria for Valves with Temporary Attachments (i.e. â€“ Lug Removal Areas)." Flowserve evaluated the issue in accordance with the provisions of 10CFR Part 21, and concluded that 1) the examination of Temporary Attachment Removal Areas to NB/NC-2500 acceptance criteria does not result in a risk to safety relating to pressure integrity; and 2) the condition evaluated, while reportable to the NRC (Nuclear Regulatory Commission), is not a significant/substantial safety hazard. The initiator of this CR concurs with the determination by Flowserve that the deviation does not constitute a significant safety hazard, and is therefore not a defect. A REGE assignment (AR 399793-03) has been created to formally determine if CGS Engineering concurs that a defect does not exist. It is noted that Flowserve has stated that "No specific orders or customers are identified as this is systemic to the overall process of valve manufacturing at Flowserve Raleigh." As such, the specific instances (EPN, CID, etc) where the issue has occurred is not known. Any components that were made by Flowserve that had temporary attachments are potentially subject to the deviation. However, since there are no recommendations for additional inspection, and no specific orders have been identified, there are no plans to identify a comprehensive list of locations that are subject to the deviation. It is recommended that this CR be assigned to AR-CPROG for closure following completion of AR-REGE 399793-03. There are no other recommended actions. <I> **** Actions Taken **** AR-OEE 399793-01 assignment completed. AR-REGE 399793-03 submitted. Initiated this CR. Contacted Code Programs SME.
401665 | CR | 20191125 |  | 3 | HCV Walkdown Identified Improvements |  |  |  | N | NO | <D> **** Detailed Description **** During the Hardened Containment Vent walkdown under Work Package 02121192, several possible improvements were identified that should be evaluated for implementation: 1. Valves HCV-V-1 and HCV-V-2 should have equipment number labels that are visible from the floor level. This would aid in equipment identification during the walkdown. 2. The marked area around the bottle rack and remote operating station (E-IR-85) is very worn and does not appear to be correct. The current boundary is marked with a blue and white boundary. This boundary should either be repainted or replaced. 3. A large covered piece of equipment labeled â€œFukushima Emergency Connection Device E-EQ-B08/416/12002â€ (see picture in EDMS folder) is located right up against some of the HCV piping and could damage it during an earthquake. Consider relocating this component.
401666 | CR | 20191125 |  | 4 | CFD Pre-coat Pump Operating Outside of Pump Curve | N | N |  | N | YES | <D> **** Detailed Description **** CFD Pre-coat Pump CF-P-4 is operating outside of its pump curve. This condition was identified in report CGS-004 on 10/22/2013, however it was not entered into the CAP. The report suggested that the low pump head could be causing inadequate septa pre-coating, thus requiring more pre-coat material. It is recommended to troubleshoot by inspecting the impeller for damage or incorrect part, and ensuring the pump motor is operating at the required power level. | 02-00-CF-P-4
401668 | CR | 20191125 | CAQ | B | TEA temporary cart pulley found broken | N | Y |  | N | NO | <C> RISK: MEDIUM CAUSE: UNCERTAIN INVESTIGATION TEMPLATE <D> **** Detailed Description **** The TEA temporary sample cart was found with a broken pulley on 11/25/19 at 0854 during the required 4-hour flow check. Repairs were made and the temporary sample cart was restored at 1300. The temporary cart was off for 4 hours and 6 minutes. ODCM RFO 6.1.2 compensatory measure E.1.2 allows collection of relevant information to provide an estimate of effluent releases in the absence of E.1.1 for auxiliary sampling equipment. If compensatory measure E.1.2 is implemented, then compensatory measure G.1 requires and entry in the annual Radioactive Effluent Release Report for the reason E.1.2 was implemented. This CR is to serve as the driver for documenting the event in the annual Radioactive Effluent Release Report. This should be assigned to Chemistry. <I> **** Actions Taken **** Informed Chemistry Supervision.
401670 | CR | 20191125 |  | 4 | TDAS X413 OOT | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02142756-01, step 7.6.2, TDAS X413 data was found out of tolerance. <I> **** Actions Taken **** Informed Supervision, Operations, and wrote CR/WR per step 7.6.1 2b. <N> **** Equipment Description **** 501RW MCR
401672 | CR | 20191125 |  | 4 | OG-RF-20A seal leakage during compressor evacuation | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of WO 02037195-01 step 4.40 to evacuate the unit the mechanical seal is leaking by and will not hold pressure. Seal needs to be replaced. <I> **** Actions Taken **** Initiated CR and returned work package to planning | 02-00-OG-RF-20A
401674 | CR | 20191125 |  | 3 | Revise PPM 1.10.1 |  |  |  | N | NO | <D> **** Detailed Description **** Table 4.1 of PPM 1.10.1 first asterisk note states â€œThe EP equipment providing the alternate indication (i.e., SDM) shall be made available and functional as soon as reasonably practical but in a period not to exceed 8hours; otherwise, the unplanned outage of the primary EP Equipment (i.e., PRM-RE-1C) is reportable.â€ This phrasing does not clearly reflect the Licensing and EP position that this 8 hour exception for reportability is only applicable when the permanent equipment initially fails Ref Event notification 54409. I suggest revising this note to clearly state when this loss of assessment capability exception can be utilized.
401677 | CR | 20191125 |  | 3 | Did not hang L-MT-HOI-10-001 as scheduled. |  |  |  | N | NO | <D> **** Detailed Description **** L-MT-HOI-10-001 was scheduled to be hung on 11/25 per WO 02124167-04, but was not able to be completed due to a conflict with L-MT-HOI-8-001. This conflict did not show up in esoms because it wasnâ€™t a conflict with tagging position, but a conflict with procedural requirements that only 1 hoist disconnect can be closed at one time on that particular electrical panel. There are many panels where this conflict with plant hoist work. An action needs to be generated to evaluate these hoist disconnects and ensure that PM model work orders are updated to reflect notes that certain PMâ€™s canâ€™t be performed concurrently to prevent the scheduling error in the future.
401678 | CR | 20191125 | CAQ | D | CRD-HCU-2259 had a high water alarm. | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-2259 had a high water alarm. OPS2 cleared the alarm with SOP-CRD-HCU. | 02-00-CRD-HCU-2259
401680 | CR | 20191126 | CAQ | D | FP-V-395 Flange to Piping Leak | N | Y |  | N | YES | <D> **** Detailed Description **** During LHRA door/lock checks, it was noticed that FP-V-395 had a small, steady stream of water coming out of the upper flange to piping gasket area. It is not spraying out, but is flowing down the valve to the floor. The water is pooling up under the stairwell on the north side of the TG 441' Condenser Bay, then running under Door T-104 to make its way to the nearby floor drain. This is in a posted High Radiation Area. The valve is in 15 mrem/hr. <I> **** Actions Taken **** Notified the Shift Manager and initiated this AR/CR. | 02-00-FP-V-395
401681 | CR | 20191126 |  | 4 | CF-LI-42 Reading E3 instead of tank volume | N | N |  | N | YES | <D> **** Detailed Description **** CF-LI-42 is reading "E3" instead of tank volume. Reading the previous night shift was 399 gallons. This issue has happened in the past, most recently AR 368907 WR 29137252 in 2017. The instruction manual, CVI 982-00,1 states E3 indicates " a Loss of Echo condition. The sensor is not able to aquire a target within the range of the sensor." <I> **** Actions Taken **** Notified CRS | 02-00-CF-LI-42
401685 | CR | 20191126 |  | 3 | Update SOP-MT-AOP/TEST to capture required data |  |  |  | N | NO | <D> **** Detailed Description **** Update SOP-MT-AOP/TEST to ensure procedure captures NEIL standards section 2.2.4.3.2.7. Procedure change needed fror R25 to support PMID . Current procedure uses simulated pressure decay. NEIL requires actuating The actuating auto start section is performed via SOP-MT-OIL-OPS section 5.4. However, there is no procedure retention for SOP-MT-OIL-OPS. . Revision will combine both procedures to capture all required NEIL documentation. AR is to revise SOP-MT-AOP/TEST to split into on-line and shutdown sections. Also need to revise/ update SOP-MT-OIL-OPS section 5.4 to just verify AOP/TEST procedure shutdown section is performed. <I> **** Actions Taken **** Attached mark up in EDMS, contacted system engineer for review of recommended procedure changes.
401686 | CR | 20191126 |  | 4 | Missed Fall Protection Training |  |  |  | N | NO | <D> **** Detailed Description **** A member of Org. 54122 missed scheduled fall protection training (SF000054) on 11/25/19. The individual had the training on their calendar, and failed to check their calendar at the start of the work week. <I> **** Actions Taken **** Reinforced expectations for training.
401687 | CR | 20191126 |  | 4 | Door knob broke D-DOOR-d109 | N | N |  | N | YES | <D> **** Detailed Description **** Door knob doesnâ€™t work needs fixed, when turning knob door bolt doesnâ€™t move <I> **** Actions Taken **** Contacted FIN to fix | 02-00-D-DOOR-D109
401691 | CR | 20191126 | CAQ | D | CRD Drive 46-11 indicating +Over on MS-TR-6 | Y | N |  | N | YES | <D> **** Detailed Description **** On tour found on MS-TR-6 HCU 46-11 flashing inbetween 102 degrees and +Over repeatedly. The temperature of 102 aligns with other CRD temperatures. With this indication it is believed the temperature is in band and cause is a failing instrument. <I> **** Actions Taken **** Informed CRS & initiated AR/WR. | 02-00-MS-TR-6
401693 | CR | 20191126 |  | 4 | Wet 20 Flow switch sticking | N | N |  | N | YES | <D> **** Detailed Description **** While performing Wet flow Switch test it was found that the fire alarm would not reset. suspect that FP-FS-20A was stuck in the flow position after flush was completed. Tried a second time with same result. Fire alarm would not reset until we tapped on the flow switch lightly with a hammer. Flow switch needs to be repaired or replaced. | 02-00-FP-FS-20A
401694 | CR | 20191126 |  | 3 | eWP Work Flow Process Fail |  |  |  | N | NO | <D> **** Detailed Description **** Six WO's in eWP, Operations (O) discipline are froze and cannot be taken to WORK COMPLETE. Multiple attempts for resubmisiion have been executed with no success. IS Lead has been notified of the issue. The QAR (legal record) of surveillance activities will not automatically transfer the electronic records until the eWP process has been completed. The following WO's are stuck in eWP with errors: WOT 02082590-03 finished 05/23/2019 WOT 02095630-04 finished 8/16/2019 WOT 02115504-06 finished 9/10/2019 WOT 02118135-01 finished 9/12/2019 WOT 02118745-07 finished 8/19/2019 WOT 02142197-05 closed 11/18/2019 <I> **** Actions Taken **** Notified IS Lead 10/10/2019 and 10/24/2019 of issue. Initiated CR. <N> There are up to 24 packages that are "STUCK" in DataGlance and at this time there is not a "FIX" for them. The listed WO Tasks have been reviewed with the following findings: . 02082590-03: Job-Type= â€˜COâ€™, Set to Finished â€“ QA record will not be generated. This is a Support Task. Stuck in DataGlance without a current fix. AS6 is now at complete . 02095630-04: Job-Type= â€˜COâ€™, Set to Finished â€“ QA record will not be generated. This is a Support Task. Stuck in DataGlance without a current fix. AS6 is now at complete . 02115504-06: Job-Type= â€˜OS, Set to Finished â€“ QA record will not be generated. This is a Support Task. Stuck in DataGlance without a current fix. Task 01 is waiting for Supervisor review prior to completion. . 02118135-01: Job-Type =â€™SVâ€™ â€“ Annotated records in DataGlance have been printed and submitted to Records. . 02118745-07: Job-Type= â€˜SPâ€™, Set to Finished â€“ QA record will not be generated. This is a Support Task. Stuck in DataGlance without a current fix. AS6 is now at complete . 02142197-05: Job-Type= â€˜XXâ€™, Set to Finished â€“ QA record will not be generated. This is a Support Task. Stuck in DataGlance without a current fix. AS6 is now at CLOSED
401695 | CR | 20191126 |  | 3 | (QA) MOTâ€™s contain incorrect information |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) There are multiple examples in which Maintenance Optimization Templates (MOTâ€™s) contain incorrect information. The MOTâ€™s are in the design database and should be maintained accurate. Incorrect MOT information could enable inappropriate PM content and periodicity determinations. Factual Basis: â€¢ MOTâ€™s in error are MOT-BKR-2-4 MOT-CHILL-1-1 MOT-ASD-1-1 MOT-MOTOR-1-1 MOT-TURB-3-1 MOT-XFMR-1-1 and MOT-MOTOR-2-2. The detail on the MOT errors is contained in the EDMS. â€¢ MOTâ€™s provide a detailed description of the Preventative Maintenance (PM) both content and periodicity for selected station equipment and systems. â€¢ PPM 1.5.13, Preventive Maintenance Optimization Living Program step 4.17.1, states â€œIt is the responsibility of the MOT owner to ensure MOTâ€™s are updated and aligned with Asset Suite following the annual review. Insights: â€¢ Annual reviews may require additional rigor to correct MOT inaccuracies. <I> **** Actions Taken **** Notified Systems Engineering Manager and QA Supervisor. This is a deficiency identified during Quality surveillance SR-19-16. Quality Recommends that this CR be assigned to AR-SYSENG.
401697 | CR | 20191126 |  | 3 | Bldg 62 needs cleanup. |  |  |  | N | NO | <D> **** Detailed Description **** Bldg 62 fire brigade station has old SCBAâ€™s and masks piled up in the south east corner of the building. Please find out the owner of this area and equipment and cleanup bldg. 62 fire brigade station. <I> **** Actions Taken **** Discussed with fire training instructor. <N> **** Equipment Description **** Bldg 62
401699 | CR | 20191126 |  | 3 | New model clearance needed for SOP-COLDWEATHER-OPS |  |  |  | N | NO | <D> **** Detailed Description **** Model clearance caution tag needs to be added to ESOMS to support new procedure requirements in SOP-COLDWEATHER-OPS, section 6.1 step 20 for heat lamps at CN-TK-1. <I> **** Actions Taken **** Assign to OPS work control to create new model clearance caution tag. Copy C-CN-PCV-FREEZE-001 from ESOMS CAUTION-25 database. Model work orderws for PMID 15037 (MWO 02149015) and 15036 (MWO 02148850) and all existing work orders have already been updated with HC/LC tasks.
401701 | CR | 20191126 | CAQ | D | FP-V-639 needs to be replaced | N | N |  | N | YES | <D> **** Detailed Description **** While performing 15.1.15 Wet flow switch test FP-V-639 was found extremely tight. Then after flush completed the valve had to be tightened with a wrench to get it to stop leaking. Valve needs to be replaced. | 02-00-FP-V-639
401702 | CR | 20191126 | CAQ | C | (QC)Cat ID# 34448 LOU Required Change |  |  |  | Y | NO | <C> MRT Change: CR 401702 moved from Severity D to Severity C assigned to AR-SECOMP. Document actions taken to mitigate recurrence. <D> **** Detailed Description **** (QC) Limits on Use Requirements for Cat ID 34448 Issue Ticket required an amendment change for the new Motor/Pump FP-P-2B acceptance per EC17692R000A FCR by Quality Control. The Issue Ticket LOU had not been updated to reflect the current Model No/Stage of the Pump/Motor being inspected per WOT #02046143-10. . Maintenance Planning was notified and the LOU requirements for CAT ID 34448 were updated/addressed by Procurement Engineering and accepted by Quality Control. <I> **** Actions Taken **** Notified Maintenance Planning, Procurement Engineering Supervision, and Quality Services. No further action is required, LOU requirements were addressed and Quality Control acceptance documented. . Recommend this CR Closed for Trending.
401704 | CR | 20191126 |  | 3 | MT&E Found out of tolerance | N | N |  | N | NO | <D> **** Detailed Description **** Calcode #44634 Minolta model T-1 Illuminance Meter was found OOT & adjusted. No Plant impact. Please assign to AR-CALSERV <I> **** Actions Taken **** Trending proposes only
401705 | CR | 20191126 |  | 3 | TRH Alarm Caused Unplanned Blow Down Closure | N | N |  | N | YES | <D> **** Detailed Description **** At approximately 10:40 AM 11/26/19 a false high blow down Total Residual Halogens (TRH) caused the blow down valve to close. The closure of the blow down valve on high TRH is a safety feature of the halogenation/dehalogenation system to prevent the discharge to the Columbia River of high TRH as per the conditions contained in the NPDES Permit. The cause of the false high TRH was a flow disruption in the sample line to the Hach TRH monitor which caused a high turbidity burst to the monitor. The monitor picked up the high turbidity in the sample as high TRH. The disruption was caused by a weekly EFSEC cross check sample pull taken at the dehalogenation skid sample rack. The turbidity cleared almost immediately but was enough to trip the blow down valve to close. A picture has been included with this CR in the EDMS doc folder showing the extent of the turbidity excursion and a sample taken minutes after. <I> **** Actions Taken **** : Actions to correct and prevent this occurrence in the future will be to place the Hach unit into hold while taking the weekly samples. This will be added to PPM 12.2.11. In the interim until PPM 12.2.11 is modified, an alternate approved sample point will be used. <N> **** Equipment Description **** BD Hach 17 Monitor
401708 | CR | 20191126 |  | 3 | SOP-SLC-SPARGE/LEVEL enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Add a note or caution prior to step 5.2.6 of SOP-SLC -SPARGE/LEVEL to increase the frequency of tank temperature monitoring when approaching the desired temperature band to ensure not exceeding 135F. This proposed revision is to help address recent Ops OE related to exceeding the max allowed procedural temp limit of 135F to prevent recurrence.
401709 | CR | 20191126 |  | 4 | LORQ Biennial Requal Written Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** One licensed operator failed the biennial written exam administered on 11/26/19. Remediation will be IAW TDI-02 and TDI-08. <I> **** Actions Taken **** De-certified individual in PQD. Notified Operations and Operations Training Management. Recommend Severity Level 4
401710 | CR | 20191126 |  | 4 | REA-FN-16 power cord needs new plug. | N | N |  | N | YES | <D> **** Detailed Description **** REA-FN-16 still has the old style 480 VAC weld receptacle plug on the end of the cord. The plant has changed out the weld receptacles with a new style rendering REA-FN-16 unusable in the event that it is needed. Please investigate and update power cord plug. <I> **** Actions Taken **** Informed fire brigade trainer and wrote this AR/WR. <N> **** Equipment Description **** Rx 471 M/8.0 | 02-00-REA-FN-16
401711 | CR | 20191126 | CAQ | C | Comp pt A543 did not come in during testing | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of ISP-RBM-S402 (0214268101), in table 7.4A, Step 7.4.6j Computer point A543 did not alarm. After reviewing CVI/vendor drawings is does not appear that the computer point should in alarm with the RBM signal by itself. The same issue has occurred on ISP-RBM-S401 (RBM-A). Table 7.4A needs to be revised to remove Computer point A543 and Step 7.4.6j should be N/Aâ€™d in both surveillances. Step 7.4.6j is not a # or $ step, The Computer point A543 is only valid for outputs 7,8, & 9 and not output 6. Outputs 7,8, & 9 had no issues with the A543 point alarming and resetting. Therefore this should not affect the operability of the RBM Drawer. <I> **** Actions Taken **** Talked with Supervisor/ System engineer/ and CRS created CR
401713 | CR | 20191126 |  | 3 | Unable to access DEH processor because of password change |  |  |  | N | NO | <D> **** Detailed Description **** We were unable to access the DEH Monitor Processor because the password had changed and we were unaware of it. One, end users (SMEâ€™s) should know when the password has been changed and know how to find it. This problem was for a nuisance alarmâ€¦but it could be a big issue if we needed to support a plant transient/problem. Two, training should be provided for the end users, supervisors, Shift Managers and CRSâ€™s for how to access the passwords in support of the plant <I> **** Actions Taken **** wrote this CR and informed my Supervisor, manager, CRS, and SM
401714 | CR | 20191126 |  | 3 | Data Diode Management connection not working | N | N |  | N | YES | <D> **** Detailed Description **** EC 13492 - DAPS installed a data diode for mail messaging into the 525 Comm Room. Drawing EWD-103E-009 shows a Rariton Connector between the Diode and the KVM Switch. That is what is installed, but it does not work. It should be an HP Connector. This prevents that KVM from being able to manage this specific Data Diode. The Diode functions correctly and we can manage it via an SSH network connection from a management workstation, but the KVM Management access does not work as designed. This CR should go to Computer Engineering. <I> **** Actions Taken **** Verified configuration as shown on the drawing. Verified that it does not function as installed. <N> AR type EVAL needed for additional configuration change? | 02-00-NET3-DDIODE-OWL/2,02-00-PDIS-KVM-525RW
401715 | CR | 20191126 |  | 3 | OI-54 vs Qual Directory Discrepancy | N | N |  | N | NO | <D> **** Detailed Description **** It was noted that there are discrepancies between OI-54 - Operations Qualification Management and the Qualification Directory - Section No. 4.7. This discrepancy does not affect any of the watchstanders being qualified. It appears that when changes were made to the qual directory, it did not get relayed to change OI-54 to match. <I> **** Actions Taken **** Notified Ops Crew Manager, notified Training.
401716 | CR | 20191126 |  | 3 | WO for SLC chem add needs a separate task for CSP-SLC-C101 | N | N |  | N | NO | <D> **** Detailed Description **** WO#02136898 for the recent SLC tank Boron chemical addition has CSP-SLC-C101 included in task 01 but it should be a separate task that is performed prior to the chemical addition. It was done prior to the chemical addition this time but it did not get all the proper signatures in a timely manner. If it has a separate task it will not get missed in the signature process. Recommend updating the model work order to reflect this. <I> **** Actions Taken **** Notified CRS, Chemistry supervision, and System specialist
401717 | CR | 20191126 |  | 3 | CRO3 iPad will not log into eWP |  |  |  | N | NO | <D> **** Detailed Description **** CRO3 iPad will not log into eWP <I> **** Actions Taken **** closed the program, restarted the iPad, still unable to log in. Used another iPad for scheduled work.
401718 | CR | 20191126 |  | 4 | MCR small caution tag printer does not work |  |  |  | N | YES | <D> **** Detailed Description **** The small caution tag printer will not print tags. <I> **** Actions Taken **** Followed the guide to turn off, unplug, restart and calibrate the printer and it still does not work. <N> **** Equipment Description **** MCR small caution tag printer
401719 | CR | 20191126 |  | 4 | SW-LS-1A1 causing level alarm with normal pond level | N | N |  | N | YES | <D> **** Detailed Description **** SW-LS-1A1 causing level alarm with normal pond level. A spray pond level is 13.4 feet as indicated on SW-LI-1A. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-SW-LS-1A1
401720 | CR | 20191126 | CAQ | B | TEA Temporary Sample Cart Nonfunctional | N | Y |  | N | YES | <C> RISK: MEDIUM CAUSE: UNCERTAIN INVESTIGATION TEMPLATE <D> **** Detailed Description **** The temporary TEA sample cart installed to support PPM 16.2.1 and 16.2.3 was found to be without power. Upon investigation power was discovered to be lost to the receptacle the cart was plugged into. The circuit was reset with permission from the CRS. Power was restored to the sample cart and it tripped the circuit breaker again after the pump ran for less than 10 seconds. The sample cart is a required compensatory measure per ODCM RFO 6.1.2. <I> **** Actions Taken **** Notifed MCR and SM <N> This CR is being addressed in the OPIT being conducted under CR 401668. Per SWP-CAP-01, an assignment under resolving AR-CR 401668 has been created to address the issue documented in this CR. Appropriate cross references have been added. | 02-00-TEA-SR-26
401721 | CR | 20191126 | CAQ | B | Temporary sample rack found not running | N | Y |  | N | YES | <C> RISK; MEDIUM CAUSE: UNCERTAIN, INVESTIGATION TEMPLATE <D> **** Detailed Description **** Temporary sample cart installed as compensatory measure for TEA-SR-26 inoperability found not running. No power at receptacle which is fed from E-CB-LP8EDA/9 reset the tripped breaker, and restarted the temporary sample cart which again tripped the breaker. Additionally nothing else was plugged into any other receptacle powered from E-CB-LP8EDA/9. The sample cart is now tripping the breaker which feeds the receptacle and had a broken belt a few days ago investigate and repair the temporary sample cart. <I> **** Actions Taken **** Contacted supervisor and maintenance to investigate the temporary sample rack. <N> **** Equipment Description **** W525 Temporary Sample Cart This CR is being addressed in the OPIT being conducted under CR 401668. Per SWP-CAP-01, an assignment under resolving AR-CR 401668 has been created to address the issue documented in this CR. Appropriate cross references have been added.
401722 | CR | 20191126 |  | 3 | PPM 13.8.1 Prodecure Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** PPM 13.8.1 Table of Contents directs user to Attachement 7.6 for Compensatory Measures for TEA or WEA on page 30. Attachement 7.6 is located on page 28 of the procedure. <I> **** Actions Taken **** Initiate CR.
401723 | CR | 20191127 | CAQ | D | NRC notification fax did not go through | N | Y |  | N | I DONT KNOW | <D> **** Detailed Description **** When performing the notification at 06:55 EST on November 27, 2019 the faxed form did not go through. It was attemped 2 times. The phone call worked as expected. The NRC individual requested that a copy of the form be sent to "hoo.hoc@NRC.gov" This was accomplished. This is also the alternate method described in PPM 13.14.11. <I> **** Actions Taken **** wrote cr and emailed form <N> **** Equipment Description **** NRC SM Fax machine
401728 | CR | 20191127 |  | 4 | TG-ID-1 | N | N |  | N | YES | <D> **** Detailed Description **** Main generator condition monitor TG-ID-1 is not operating. Request craft investigate and restore to service as necessary. <I> **** Actions Taken **** Notified CRS. Contacted Maintenance to investigate and restart as necessary. | 02-00-TG-ID-1
401729 | CR | 20191127 |  | 4 | PWC-SEW-13 eyewash activation bar is loose. | N | N |  | N | YES | <D> **** Detailed Description **** PWC-SEW-13 eyewash activation bar is loose. It is held in place by a bolt and nut arrangement and the bolt head has a square hole. The eyewash can still be operated. See EDMS for pics. <I> **** Actions Taken **** Notified supervisor and noted on weekly eyewash station checks. <N> **** Equipment Description **** Between SW pump houses. | 02-00-PWC-SEW-13
401730 | CR | 20191127 |  | 4 | Multiple light fixtures not lit | N | N |  | N | YES | <D> **** Detailed Description **** On the TB 501 west side there are three fixtures that are not lit. One between the TOA enclosures, one along the south wall behind the TOA enclosure, and one above the stairwell down to the TB471'. <I> **** Actions Taken **** Notified SM. <N> **** Equipment Description **** TB501 SW lighting fixtures
401731 | CR | 20191127 | CAQ | D | Received Rod Accumulator Trouble Alarm for HCU 18-23 | Y | N |  | N | YES | <D> **** Detailed Description **** od Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD-HCU -1823 was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear | 02-00-CRD-HCU-1823
401732 | CR | 20191127 |  | 3 | CI-10.5 Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** CI-10.5 Measure of Conductivity references incorrect attachment and section numbers. For example 9.3.13 references attachment 15.2 and should be 14.2. Also, 9.3.15 references section 9.1 and should be 9.2. These attachment and section number mistakes are carried throughout the rest of the proceedure. <I> **** Actions Taken **** CR written
401733 | CR | 20191127 |  | 4 | No Lighting (RHR "A" HX Room) Safety-Concern |  |  |  | N | NO | <D> **** Detailed Description **** -HP Technician entered the RHR "A" HX Room on RX 572' to perform a pre-job survey on RHR-V-173A to support plant work next week. Room is Dark and has no lighting, this needs to be addressed prior to any work next week. <I> **** Actions Taken **** Notified Supervision -Initiated CR . This is incompatible with safe work. WO 02122618, RHR-MO-73A EXTERNAL PM is scheduled to be done NEXT WEEK starting with scaffold erection at 07:00 12/2/19. The main task is scheduled for 07:00 12/3. This WO cannot proceed without first correcting the lighting conditions in this area.
401734 | CR | 20191127 |  | 4 | TOA-FL-1B | N | N |  | N | YES | <D> **** Detailed Description **** TOA-FL-1B is at end of roll and needs replaced <I> **** Actions Taken **** informed the MCR initiated CR/WR | 02-00-TOA-FL-1B
401735 | CR | 20191127 | CAQ | C | DSA-PI-12 Low During OSP-ELEC-M703 | Y | N |  | N | YES | <D> **** Detailed Description **** The local air start pressure on the west side of DG3 at DSA-PI-12 was found to be low with a reading of 178# during OSP-ELEC-M703. The minimum specification per SOP-DG3 -START logs is 180#. This reading is routinely taken by OPS2 and has had a stable trend at 182# during routine rounds. The minimum specification during OPS2 rounds is 170#. A determination needs to be made on which minimum value is correct between the OPS2 rounds and SOP-DG3-START. The Technical Specification Operability requirement per TS 3.8.3 is GT 223# at the DG3 receivers (DSA-PI-7 and DSA-PI-8), both of which are currently in specification. <I> **** Actions Taken **** Notified CRS | 02-00-DSA-PI-12
401736 | CR | 20191128 |  | 4 | GY-F-10A2 | N | N |  | N | YES | <D> **** Detailed Description **** Small leak discovered near top of GY-F-10A2. | 02-00-GY-F-10A2
401742 | CR | 20191128 |  | 4 | lighting cover in chemistry breakroom fell | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During the chem tech D-15 in the chemistry breakroom an overhead lighting cover suddenly shattered and fell to the floor next to the chem techs. No techs were injured. <I> **** Actions Taken **** Notificed CRS. Wrote CR to document near miss and degraded condition of Chemistry breakroom. Observed all lighting fixtures in breakroom for degraded condition Initiated actions to have HP, Ops, Maint, and Security walkdown their work areas to look for similar at risk fixtures.
401743 | CR | 20191128 | CAQ | D | EDR-P-18B excessive run time. | N | N |  | N | YES | <D> **** Detailed Description **** EDR-P-18B ran for 7.8 hours on the previous shift. Discovered on day shift 11/28. When discovered the pump was still running. Flagging the CS to "off" stopped the pump and the switch remains in auto. EDR-P-18A has an open/actioned WR for a sticking level switch, and EDR-P -18B has a completed WR which resolved this problem by mechanically agitating a check valve. <I> **** Actions Taken **** Notified supervisor and flagged EDR-P-18B to the off position. . C-EDR-P-18A/18B-001 has been hanging since 6/28/2019 due to EDR-P-18A and EDR-P-18B do not shut off automatically on low level. WO 02154992 at PLAN. <N> **** Equipment Description **** TG441 | 02-00-EDR-P-18B
401744 | CR | 20191128 |  | 4 | HT-HTP-FP/8 44F Power On light not lit | N | N |  | N | YES | <D> **** Detailed Description **** HT-HTP-FP/8 44F Power On light is not lit. This panel is for the fire protection piping out at the Flocculator Building. <I> **** Actions Taken **** Initiated CR. Replaced light bulb. Non-essential FP support system. | 02-00-HT-HTP-FP/8
401745 | CR | 20191128 |  | 4 | DO-LITS-15 shows intermittent fault | N | N |  | N | YES | <D> **** Detailed Description **** DO-LITS-15 (HPCS fuel oil storage tank) intermittently displays a red "FAULT" light. In addition, I observed the displayed reading to change from 129.8 to 133.2" and back again in about 15 seconds. Please investigate. <I> **** Actions Taken **** Notified SMgt, wrote CR. . DO-LITS-15 has not been calibrated or cal checked since 2007. Per PM 23369 it is supposed to have a loop cal every 8 years. The last scheduled calibration under WO was cancelled per AR 382497. <N> **** Equipment Description **** HPCS fuel oil storage tank room. | 02-00-DO-LITS-15
401746 | CR | 20191129 |  | 4 | Security XD-4 | N | N |  | N | YES | <D> **** Detailed Description **** Explosive Detector 4 is not functioning as designed. Please contact Security at extension 2185 for further information. <I> **** Actions Taken **** Security Supervision notified, unit taken out of service. CR/WR generated for I&C support. | 02-00-SEC-XD-4
401750 | CR | 20191129 |  | 3 | No training for new CW PH control (DECL-AIT-03) |  |  |  | N | YES | <D> **** Detailed Description **** We were asked to perform a cleaning task for our CW-PHITS-1 probe. We were very familiar with this, but now that has changed. A new control system was installed without the I&C department being involved. I believe this was all part of the Dehalogenation project? Without involvement in the project, we do not know the ways we could affect the control loop or the plant. We could blindly follow instructions, but that is clearly not part of our path to Excellence. Are there new hazards in the area due to additional chemicals? It seems the mechanical and electrical department would be effected by these changes too? Training the right people would allow us to take ownership and support the plant when needed. Who is expected to perform the routine maintenance on all the additional instrumentation? OE has shown us that ignorance of systems leads to mistakes and injuries. <I> **** Actions Taken **** wrote this CR and TREQ 19-0175 <N> **** Equipment Description **** DECL-AIT-03
401751 | CR | 20191129 |  | 3 | instrument DECL-AIT-03 is not in Portal-J |  |  |  | N | YES | <D> **** Detailed Description **** As part of WO# 02142746-01, our first step is to verify DECL-AIT-03 is actively monitoring CW PH. We can do this though a computer point. The problem is, if it was not working, there is no information in Portal-J about it. It appears the EPN does not exist. This is our primary way to access information about plant equipment. Is this the only component of the new system that has no way for us to access information? Maybe I did it wrong, but I tried to search for any EPN with the prefix of DECL and it came up with nothing. My concern is we have a plant system that we have no access to CVIs, or any other information, in order to perform maintenance on. This will affect the mechanics and electricians too. We cannot provide Excellence in maintenance if we have no training or access to information. <I> **** Actions Taken **** wrote this CR <N> **** Equipment Description **** the entire DECL system
401752 | CR | 20191129 |  | 3 | Knowledge gap on requirements in PPM 1.3.83 |  |  |  | N | NO | <D> **** Detailed Description **** There is a knowledge gap within the Operating Crews on the requirements in PPM 1.3.83 for verification of protected equipment. The procedure clearly states in section 3.1 that protected signs and barriers are to be walked down every shift to verify that the barriers are in place and no unauthorized work is in progress. <I> **** Actions Taken **** A lessons learned has been generated to refresh the knowledge of the Operating crews on the requirements of PPM 1.3.83. On shift CRS and Shift Manager informed.
401753 | CR | 20191129 |  | 4 | (NRC identified) Seismic NCC time not synced | N | Y |  | N | YES | <D> **** Detailed Description **** NRC identified the time on the seismic NCC display screen does not match the control room clock being approximately 5 minutes behind. During investigation of this concern, control room staff identified additional issues for resolution (1) the time on the KVM computer also does not match the control room clock (2) The KVM computer logfile indicates monitoring is not active (3) an error message on the KVM when restart was attempted from the file menu that states the KVM cannot establish communication wih the NCC (4) two labelled purple LAN cables disconnected from the network time server NET4-TCS-4. Check of seismic self-tests indicates no faults. Request I&C and/or Computer Engineering investigate and determine if the seismic monitoring system is working as designed and if the time sync discrepancies can be resolved. <I> **** Actions Taken **** Reviewed these items with the SM. Attempted restart of the KVM from the file menu as directed by the on screen instructions without success. Adjusted system time to within 5 sec of MCR clocktime. This will need to be done periodically. The time does not impact functionality of the unit, only makes data analysis more difficult after an event. The seismic system remainins functional. | 02-00-NET4-TCS-4,02-00-SEIS-COMP-NCC,02-00-SEIS-KVM-1
401754 | CR | 20191129 |  | 3 | Untimely Resolution to CR#00376506 (Safety Concern) |  |  |  | N | NO | <D> **** Detailed Description **** CR#00376506 was initiated on 02/04/2018 due to a safety conern on the NE Elevator. It hasn't been addressed, and is coming up on two years since it was brought up. <I> **** Actions Taken **** Initiated CR
401755 | CR | 20191129 |  | 3 | Update CW-PHITS-1 IMDS |  |  |  | N | NO | <D> **** Detailed Description **** CW-PHITS-1 IMDS says CBD-LCV-1 will Close during calibration. This IMDS has not been updated since the dehalogenation project was installed. WO# 02142746-01 states there will be no action during cleaning/calibration (step 2.8). Please update the IMDS to reflect current system actions. <I> **** Actions Taken **** talked with supervisor and wrote this CR
401756 | CR | 20191129 |  | 3 | align WO task instructions with impact statement | N | N |  | N | YES | <D> **** Detailed Description **** In WO# 02142746-01, the Work Control Review section of the Impact Statement says SAT-V-6 will receive an auto close signal during calibration AND that it will be reset per work order instructions. Section 4.18 of the instructions is for calibration and mentions nothing about SAT-V-6. Please validate which document is valid and correct the instructions as needed.This is a system we have received no training on. <I> **** Actions Taken **** informed supervisor. I wrote this CR and I already wrote TREQ 19-0175 and CRs 00401755, 00401751, and 00401750 addressing other issues. <N> **** Equipment Description **** dehalogenaton system at CW
401757 | CR | 20191129 |  | 4 | HCO-T-W9A heating coil N for RW HVAC has a steam leak | N | N |  | N | YES | <D> **** Detailed Description **** Steam leak on the RW HVAC heating steam coil 'N' | 02-00-HCO-T-W9A
401758 | CR | 20191129 |  | 4 | Light out over SW stairwell on the TB 501'. | N | N |  | N | YES | <D> **** Detailed Description **** The light hanging over the SW stairwell on the TB 501' is out and needs to have its' bulb replaced. <I> **** Actions Taken **** Initiated CR. Non-essential lighting <N> **** Equipment Description **** Above SW stairwell on the TB 501'
401759 | CR | 20191129 |  | 4 | Emergency Use SCBA bottle pressure 2600 psig | N | N |  | N | YES | <D> **** Detailed Description **** A SCBA was discovered with a low bottle pressure (2600 psig) at the TG 441 turnout location. The bottle was replaced with a fully charged bottle. <I> **** Actions Taken **** Replaced bottle - notified HP. <N> **** Equipment Description **** SCBA at the TG 441 turnout station used for the Fire Brigad
401760 | CR | 20191129 |  | 4 | GEM-5 At Security PAAP Out Of Service | N | N |  | N | YES | <D> **** Detailed Description **** GEM-5 HP-EQ-42738 at the Security PAAP is out of service due to Detector #1 fault. The fault indicates "HV Out Of Range" and the main screen also says "Excessive Count Time". <I> **** Actions Taken **** Placed OOS sign on monitor, contacted RP Supervision and initiated WR. <N> **** Equipment Description **** Security PAAP | 02-00-HP-EQ-42738
401761 | CR | 20191129 |  | 4 | CAS-C-1C oil d/p higher than normal | N | N |  | N | YES | <D> **** Detailed Description **** Following an auto start of CAS-C-1C found CAS-DPI-27C reading 12-13#. Normally this reading is leass than 5#. Max spec is 20# by the logs. Log date shows that one week before this reading was 7# and trending up 1# per day. <I> **** Actions Taken **** Informed MCR, initated AR. | 02-00-CAS-C-1C
401762 | CR | 20191129 |  | 3 | SOP-LO-OPS enhancment |  |  |  | N | NO | <D> **** Detailed Description **** SOP-LO-OPS, Section 5.8 should include a note that reads as follows: "TO-TK-2 level is approximately equal to 200 gallons per inch." This note will provide Operators with the needed information to decide how many barrels should be added to TO-LOC-1 to restore TO-TK-2 level. This information can be verified, as it is already a note in SOP-LO-FILL. <I> **** Actions Taken **** Informed MCR. Verified information against SOP-LO-FILL <N> **** Equipment Description **** SOP-LO-FILL
401767 | CR | 20191130 |  | 3 | E-LP-6NA Breaker Designation Card Inside Panel Door Typo |  |  |  | N | YES | <D> **** Detailed Description **** During the performance of D-FP-P-2B-001, it was noted that the breaker designation card inside of E-LP-6NA on E-CB -LP6NA/22 had a typographical error in the description. The card noted the description as, â€œFP-H-P/23.â€ Verification on the most current revision of SOP-ELEC-LP-LU as well as on print EWD-46E-469 proved the correct description to be, â€œFP-H-P/2B.â€ Management and MCR approval was obtained before proceeding with performing the clearance. Informed SSS and currently in process of updating the breaker designation card. <I> **** Actions Taken **** Informed supervision, printed current revision of SOP -ELEC-LP-LU for replacement | 02-00-E-LP-6NA
401768 | CR | 20191130 |  | 3 | EWP unable to authorized or take to working |  |  |  | N | NO | <D> **** Detailed Description **** WO #02105231-08 was at EWP step "Walkdown Complete". Supervisor was unable to take this work order to Authorized or to Workiing. Notified PSRO, PSRO and Shift Manager was unable to get EWP to the proper status. Hard copy is being utilized. <I> **** Actions Taken **** Supervisor notified PSRO, Shift Manager. Hard Copy is being used and tracked in Portal J, CR initiated for tracking purposes. Shift Manager took task to working in Portal J. <N> **** Equipment Description **** Data Glance issue
401769 | CR | 20191130 |  | 4 | Constant Alarm Host 1T | N | N |  | N | YES | <D> **** Detailed Description **** CAS has a Constant Tamper Alarm on Host Cabinet 1, Contact x2185 for further information <I> **** Actions Taken **** Tamper Alarm received, notified supervision, CR/WR generated <N> **** Equipment Description **** Inside CAS, back corner area Per discusion with security this issue does not affect the site security plan. | 02-00-SEC-CAB-HOST/1
401770 | CR | 20191130 |  | 4 | TSW-DPIS-26A OFF-SCALE LOW. | N | N |  | N | YES | <D> **** Detailed Description **** TSW-DPIS-26A IS READING OFF-SCALE LOW. <I> **** Actions Taken **** NOTIFIED SUPERVISOR. <N> **** Equipment Description **** CW PH EAST SIDE | 02-00-TSW-DPIS-26A
401771 | CR | 20191130 | CAQ | D | FP-P-110 OIL LEVEL AT "LOW" MARK | N | Y |  | N | YES | <D> **** Detailed Description **** FP-P-110 NEEDS OIL. OIL LEVEL IS WITHIN SPEC, BUT AT "LOW MARK." <I> **** Actions Taken **** NOTIFIED SUPERVISOR. <N> **** Equipment Description **** FLOCCULATOR BLDG. | 02-00-FP-P-110
401772 | CR | 20191130 |  | 4 | Visitor entry warning sign into DG1 and HPCS DG rooms. | N | N |  | N | NO | <D> **** Detailed Description **** Visitor entry warning sign into DG1 and HPCS DG rooms are in poor condition and are peeling off the wall. <I> **** Actions Taken **** CR written <N> **** Equipment Description **** DG corridor outside DG rooms.
401773 | CR | 20191130 | CAQ | D | FP-M-P/2B De-term | N | Y |  | N | YES | <D> **** Detailed Description **** While de-terming FP-M-P/2B under WO #02105231-08 craft noticed with QC the as found condition was not as what the EWD--62E-032 and CTI EC17692-01 indicated, also cable # BM6N-0011 was only identified on BLACK and BLUE conductor and not on the RED conductor. <I> **** Actions Taken **** Craft stop and notified supervision, Supervisor identified that the conductors was located in Conduit BM6N-11-1 and two of the three conductors was labeled, so the 3rd conductor was also BM6N-0011 and will need to be labeled in the re-install task of WO #02105231. The as found condition was corrected in the CTI of WO #02105231-08 IP-01 CR was initiated and WWM, Control Room and QC Supervisor was notified. | 02-00-FP-M-P/2B
401774 | CR | 20191130 | CAQ | D | Intermittent Accumulator trouble alarm | Y | N |  | N | YES | <D> **** Detailed Description **** H13.P603-A7 drop 6-7 Rod Accumulator Trouble alarm for HCU 30-47 has been intermittently alarming and clearing throughout the shift. Dispatched OPS 2 to investigate, but the alarm did not re-flash while he was on station. Local N2 pressure was 1100 psig. Suspect a transponder card malfunction due to the rapid triggering and clearing of the alarm. <I> **** Actions Taken **** Dispatched operator to investigate with no local issues visually noted. Informed Shift management. | 02-00-CRD-HCU-3047
401775 | CR | 20191130 | CAQ | D | Rod accumulator trouble on CRD-HCU-2203 due to high water | Y | N |  | N | YES | <D> **** Detailed Description **** Rod accumulator trouble on CRD-HCU-2203 due to high water level. Cleared alarm per SOP-CRD-HCU. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-HCU-2203
401815 | CR | 20191201 |  | 4 | MAIN GEN vibration monitoring bad readings 02132133-01 | N | N |  | N | YES | <D> **** Detailed Description **** While performing vibe collection on E-GEN-1 at the Bently Nevada panel in the main control room craft was not able to obtain a reading on TG-MON-RP (Dual Thrust Monitor) Prox A and Prox B. Approptriate values were collected at all other test points during the course of this job. The test equipment is not suspect. <I> **** Actions Taken **** Informed Shift Manager and craft supervisor <N> **** Equipment Description **** MCR | 02-00-E-GEN-1
401816 | CR | 20191201 |  | 4 | Excessive Oil Leakage- Lube Oil Coolers TO-HX-1A / TO-HX-1B | N | N |  | N | YES | <D> **** Detailed Description **** Excessive oil leakage coming from the upper head flanges of TO-HX-1A/1B on the TGB 501' and leaking down into the TGB 471' TO-TK-2 room. <I> **** Actions Taken **** Notified Supervision. Requested laborers setup a catch to funnel oil leakage to collection point. <N> **** Equipment Description **** TGB EAST SIDE 501' | 02-00-TO-HX-1A,02-00-TO-HX-1B
401817 | CR | 20191201 |  | 4 | OG-TIS-601B causing low temp alarm with normal temp | N | N |  | N | YES | <D> **** Detailed Description **** OG-TIS-601B is causing H13-P672.A9.2-2, RECOMBINER B INLET TEMP LOW, alarm with temperature indicating normal at 355 Â°F. The alarm setpoint is 300Â°F. No temperature changes are indicated on OG-TRS-602, all temperatures are normal and stable. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-OG-TIS-601B
401818 | CR | 20191202 |  | 4 | NRC identified R-DOOR-R013 handle is loose | N | N |  | N | YES | <D> **** Detailed Description **** R-DOOR-R013 RHR C east entrance door inside handle is loose. <I> **** Actions Taken **** Informed supervision and intiated wr to correct issue. | 02-00-R-DOOR-R013
401819 | CR | 20191202 | CAQ | D | NRC identified TEA-SR-26 lagging is coming off | N | Y |  | N | YES | <D> **** Detailed Description **** TEA-SR-26 lagging is coming off the heat traced piping on the north side of the rack. Have insulators repair the loose lagging. <I> **** Actions Taken **** Informed supervision | 02-00-TEA-SR-26
401820 | CR | 20191202 |  | 4 | NRC identified MT-ELEV-4 making noise | N | N |  | N | YES | <D> **** Detailed Description **** MT-ELEV-4 at the 441 elevation the doors are making a dragging noise when operating. MT-ELEV-4 is making a scratching noise as it transitions between the 487 and the 501 elevations. <I> **** Actions Taken **** Informed supervision. | 02-00-MT-ELEV-4
401821 | CR | 20191202 |  | 4 | NRC identified light flickering in the radwaste stairwell | N | N |  | N | YES | <D> Fluorescent light flickering on the A-7 stairwell. The light is located above the 471 landing. Recommend relamp fixture or replace with LED. <I> Informed supervision <N> above the w471 A-7 stairwell landing ... CR at INPROG. Approved CR, moved to SRO for OPS Review.
401842 | CR | 20191202 | CAQ | D | SW-RR-1 pt 3 has wrong units displayed | N | Y |  | N | YES | <D> **** Detailed Description **** SW-RR-1 is displaying the wrong units for Point 3, AR-RIS -21 "Mechanical Vacuum Pump Discharge Rad Monitor" is displaying the units in R/hr vs mR/hr. The Analog meter is tracking with the Yokogawa recorder at the expected value for 100% power (~30 mR/hr), so there seems to be no operability issue, just the wrong units are displayed on the recorder itself. This instrument is used below 5% Reactor power during Mechanical Vacuum Pump Operation. Recommend changing the display units during the next calibration cycle for the instrument. <I> **** Actions Taken **** Informed Shift supervision of the discrepency. | 02-00-SW-RR-1
401843 | CR | 20191202 |  | 4 | Safety Concern - Buildings 105 & 106 door lights are Out | N | N |  | N | NO | <D> **** Detailed Description **** The lights above the entrance doors to building 105 (Saluce Building - ISFSI Equipment Storage) and 106 (Dry Creek Building) are out and need to be replaced. This is a safety concern especially during this time of year with diminished daylight and inclement weather. Per Facilities, these LED lights failed during a past power outage. Action: Replace the LED lights above the entrance doors to buildings 105 and 106 with occupied building 106 being the first priority. There is currently a work order task to re-lamp the entrance to building 106 that needs to be worked (WOT 02071021-11). Did not find a work order to re-lamp the entrance door of 105. A work request for building 105 will be generated from this CR. <I> **** Actions Taken **** Initiated CR. Discussed with Supervision and Department Group meeting. <N> **** Equipment Description **** Buildings 105 and 106 entrance door lights.
401845 | CR | 20191202 |  | 3 | Inconsistent calculation of source counts | N | N |  | N | NO | <D> **** Detailed Description **** While reviewing the Ludlum Model 2000 (s/n 0064887) sample counter daily performance check log for November 2019, it was noted that the source count rate (in cpm) was being inconsistently calculated. Specifically, some entries were offset for the background levels (in cpm) and others were not. The background count rate is generally less than 1 cpm; therefore, the change in calculated decision level is negligible. While the impact is low, it is not technically accurate to calculate source count rates without offsetting the values for background levels. <I> **** Actions Taken **** Discussed issue with radiological operations team. <N> TREQ 19-0179, Calculating Count Rates for Ludlum Model 2000, was initiated on 12/03/19. No further action required.
401846 | CR | 20191202 |  | 3 | Abnormal background changes for Model 2000 | N | N |  | N | NO | <D> **** Detailed Description **** While reviewing the Ludlum 2000 (s/n 0064887) sample counter daily performance check log for November 2019, it was noted that background levels are varying from day-to -day in an unexplainable trend. Background count rates have varied from 5 cpm to 20 cpm during the month, but the trend was erratic and not steadily increasing or decreasing. The Model 2000 is located on the RW 467 near abandoned equipment, and background radiation levels do not appear to have changed during this period. <I> **** Actions Taken **** Discussed issue with the radiological operations team. <N> Discussion with CR author indicate that it was intended to be counts, not counts per min (cpm). This is still an unusual variation in the total count. Will be investigating.
401849 | CR | 20191202 |  | 3 | Data on PSR-CAB-1 MMS Monitor not taken for CI-15.2. | N | N |  | N | YES | <D> **** Detailed Description **** During the CI-15.2 Daily monitor Data surveillance. It requires data from PSR-CAB-1 Durability Monitor for PSR -SR-49. Found the monitor screen frozen in place so all Data could not be recorded. <I> **** Actions Taken **** Restarted computer and followed instructions from CI-15.2. The data available would pop up on screen and would then instantly freeze so could not toggle to receive the MMSGnd(pt) data which is needed for CI-15.2. The data that is available on screen shows normal readings for PSR-SR-49. Messages that would pop on screen were "Optimum performance user exit & designate new ECP/Chem File", "Program Error DDE Method invoked with no channel open" & "Chem ECP File greater than 4 megabytes". This is a Windows 98 program. A Work Request to replace computer has already been issued. Contacted Chemistry Specialist and Supervision. This CR is for trending purposes. <N> **** Equipment Description **** NorthEast corner of RX 548'. | 02-00-PSR-CAB-1
401851 | CR | 20191202 |  | 4 | Elevated Platform Safety Gate does not close properly | N | N |  | N | NO | <D> **** Detailed Description **** During a scaffold survey on an elevated platform on the RB 522 SW corner against containment it was noticed that the safety swing gate does not fully close on its own. I has to be pulled close to be in the proper position. <I> **** Actions Taken **** Initiated this CR, notified HP Supervision, OPs supervision and made sure the gate was in the closed position upon exiting the permanent platform. Attached pictures in EDMS. Safety gate has been fixed and verified. No further action required.
401852 | CR | 20191202 | CAQ | D | Handwheel not broken. It didnâ€™t fit | Y | N |  | N | NO | <D> **** Detailed Description **** During performance of WO 02140243-01 it was discovered that the handwheel for RHR-V-159A was not broken it was too big to manipulate in place. The handwheel contacted nearby piping when rotating for closure or opening. The replacement CID 54912263 was the same size. The craftsmen stopped engaged Supervision, Ops and Engineering to see if trimming the handle was allowable. After review Engineering determined that it was allowed, handwheel was trimmed to allow manipulation. <I> **** Actions Taken **** CR generated for documentation, Gold cards issued to the Craftsmen and Engineer A limitation on use was added to CID 54912263 for future reference that Hand wheel may require trimming if interference exists. Reference AR CR 401852, WO 02140243 -01.
401853 | CR | 20191202 |  | 3 | Revise SD000145 to reflect RPV Water Inv Control TS change |  |  |  | N | NO | <D> **** Detailed Description **** SD000145 "Condensate Storage and Transfer" needs to be revised to reflect TS Amendment 251 (RPV Water Inventory Control). Specifically, the title of TS 3.5.2 is changed. Also, the RCIC Instrumentation TS number is changed.
401854 | CR | 20191202 |  | 3 | HPI-12.75 Rad. Posting During TIP need enhancements |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** During HP Continuing Cycle training (19-03) on the TIP System students noted the procedure needs updating. Please evaluate the need to enhance the procedure on the following: Add - Evacuate personnel when posting. Section 3.6 - dose rates should be consistent with previous or expected post TIP run dose rates not normal reactor power level. Add - should a peer check be included? Add - Do we need to tell Security no access? Create - Some students requested an action checklist Remove - note to leave elevator @ 501â€™ on map Add - Section 3.7 how much is considered an elevated dose rate? <I> **** Actions Taken **** Captured students feedback on parking lot. Wrote this CR for procedure enhancements. RP Supervision and Training Supervision informed during observation of training.
401861 | CR | 20191202 |  | 3 | Enhancement to SOP-LO-FILL and OPS |  |  |  | N | NO | <D> **** Detailed Description **** Please change the wording of SOP-LO-OPS, step 5.8.5 AND SOP-LO-FILL, step 5.2.3 e. to BOTH read as follows: "VERIFY the hand truck-mounted electric pump discharge is installed into ANY convenient compartment of TO-LOC-1." See attached EDMS for email chain with System Engineer. Note AR 401762 was also recently generated for a enhancement to SOP-LO-OPS. <I> **** Actions Taken **** Communicated with System Engineer to recieve concurance on proposed changes. <N> **** Equipment Description **** SOP-LO-OPS and SOP-LO-FILL.
401863 | CR | 20191202 | CAQ | D | FP-P-2A Sealing Water Pressure Low Out of Spec | N | Y |  | N | YES | <D> **** Detailed Description **** FP-P-2A sealing water pressure, as read on FP-PI-5A indicated 82 PSIG. Minimum spec is 85 PSIG. Sealing water strainer FP-ST-2A was blown down per logs and pressure on FP-PI-5A was checked again but pressure remained at 82 PSIG. Recommend FP-ST-2A cleaning or replacement. <I> **** Actions Taken **** Informed supervision, wrote AR | 02-00-FP-ST-2A
401864 | CR | 20191203 | CAQ | D | On RHR-MO-64A, Nomax410 insulating barrier had to be trimmed | Y | N |  | N | YES | <D> **** Detailed Description **** While installing torque switch on RHR-MO-64A (02135657) the torque switch could not be installed because the insulating barrier was oversized (NOMEX410) contacted engineering and engineering authorized the trimming of the NOMEX410 for proper installation per email <I> **** Actions Taken **** contacted QC, Ops, Engineering, OCC, and maintenance, wrote this CR to document the trimming of the NOMEX410 for proper fit <N> **** Equipment Description **** RX 446 K0/9.3 | 02-00-RHR-MO-64A
401865 | CR | 20191203 |  | 4 | E-BU-SWA6/4 emergency battery unit has a charger fault | N | N |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was discovered that E -BU-SWA6/4 emergency battery unit has a charger fault. The green ready light on the unit was lit. The red light was blinking three time in succession indicating a charger fault. <I> **** Actions Taken **** Notified CRS and wrote CR | 02-00-E-BU-SWA6/4
401866 | CR | 20191203 |  | 4 | Annunciator Tile Cover is broken on P601 | N | N |  | N | NO | <D> **** Detailed Description **** Annunciator 4.601.A3.6-2 tile cover is broken off. <I> **** Actions Taken **** Taped Annunciator back into place. <N> **** Equipment Description **** MCR
401875 | CR | 20191203 |  | 4 | SAFETY ISSUE. Light out over BLDG 26 rear exit door |  |  |  | N | YES | <D> **** Detailed Description **** External light over the rear (north) exit door at BLDG 26 (PEC) is out. Safety issue, please repair. Door is the exit only door near stairs. <I> **** Actions Taken **** CR generated. <N> **** Equipment Description **** BLGD 26 north exit door light
401880 | CR | 20191203 |  | 4 | Improper After Hours Implementation of procedure |  |  |  | N | NO | <D> **** Detailed Description **** On 11/19/2019, the operating crew performed an editorial revision to 4.FCP.3. The active revision at the time was 024/001, but the revision filed into the Main Control Room binder after hours was listed as revision 024/003. This caused confusion as the Automated Process Workflows (APW) assigned it as revision 024/002. An email was sent to Document Control per SWP-PRO-02 step 5.9.1.c.2), however it was not apparent that an After Hours Implementation occurred. <I> **** Actions Taken **** Coaching was provided to the individual who performed the After Hours Implementation. The revision number to 4.FCP.3 was corrected in APW prior to Document Control filing the revision in other locations on site. This CR is for trending purposes only and no action is required.
401882 | CR | 20191203 |  | 4 | TMU-LCV-2A did not appear to be controlling | N | N |  | N | YES | <D> **** Detailed Description **** MCR noticed CW basin level lowering and noticed TMU-LCV-2A did not appear to be controlling. OPS 4 was sent to investigate and noted significant air past the shaft (operator) seal. Position was noted to be approx 50 degrees. MCR reports that they have opened it up in manual to approx 70 percent signal. Please investigate. <I> **** Actions Taken **** investigated will attach videos later | 02-00-TMU-LCV-2A
401883 | CR | 20191203 |  | 4 | Worker hours not updated in eSOMS |  |  |  | N | NO | <D> **** Detailed Description **** Contrary to SWP-FFD-04, a Non-Licensed Operators work hours were not scheduled and therefore appropriately verifed in eSOMS prior to taking the shift on 12/3/2019 at 0600 (dayshift). This occured due to a recent vacation cancellation and a change of the workers relief schedule. Manpower schedules were up to date, but eSOMS was not accurate. eSOMS has been updated and no fatigue rule violation occured. This CR was created for trending. <I> **** Actions Taken **** eSOMS updated. CR initiated for trending.
401884 | CR | 20191203 |  | 4 | DEH-TI-42 May Need Calibration | N | N |  | N | YES | <D> **** Detailed Description **** The DEH fans are starting at 106Â°F as read on DEH-TI-42. <I> **** Actions Taken **** Informed MCR <N> **** Equipment Description **** 471 | 02-00-DEH-TI-42
401885 | CR | 20191203 |  | 4 | Electronic Information Monitors Not Working |  |  |  | N | NO | <D> **** Detailed Description **** Three electronic information monitors located in the Yakima Building are not working. All three appear to have electrical power to the monitors. It is suspected that the Ethernet feed is not operating. Locations: Yakima 441, main entry. Yakima 441 Lunchroom, Yakima 441 outside the Operations Briefing Room. <I> **** Actions Taken **** No EPN. This is non-plant equpment installed by Information Services. <N> **** Equipment Description **** Yakima Building
401886 | CR | 20191203 |  | 3 | Lambda Electric Power Supply Model RWS15A-24/A is obsolete |  |  |  | N | NO | <D> **** Detailed Description **** CAT ID 0060808055 shows we have 2 on hand and there may be more of these power supplies available for purchase surplus via different distributors. This product may no longer be supported and there is a catalog for Lamda Electric attached to edms of this AR. Need Supply Chain or PE to start considering replacement of RWS15A-24/A for a newer model or purchase more of the obsolete power supplies to have in stock inventory. A note should be made in the CAT 0060808055 that manufacturer made notification of obsolescence for that model RWS15A-24/A. CAT ID 0060808055 is used in the following applications: SW-E/S-40, CW-E/S -4, TMU-LPW-4, SW-E/S-32B, SW-E/S-32BR, TMU-E/S-2A, CBD -E/S-10, SW-E/S-1C, SW-E/S-32A, SW-E/S-1A, FP-E/S-10. This CR is administrative in nature and has no impact to the plant. Notified PE, Supervisor and OPS SM. <I> **** Actions Taken **** Notified PE, EFIN Supervisor and OPS SM
401887 | CR | 20191203 |  | 3 | Gap in Clearance Order Warning Practices |  |  |  | N | NO | <D> **** Detailed Description **** While preparing to perform a flush of the MWR line, it was noted by the work group that they were required to sign onto a clearance order to access a scaffold in close proximity to a de-energized hoist bus bar. This was not known to the HP technicians performing the pre-job survey, and there was no signage posted at the scaffold that required personnel to sign onto a clearance before accessing the scaffold. When discussing the issue with the PSRO, the Maintenance Shop, and Williams Carpenters, it is apparent that the station is not aligned on how clearance notices should be hung to provide warning to general plant workers that may access these affected areas. This scaffold is part of a routinely surveyed area, and general access is allowed with no visible notice that a clearance order is in place or that potentially energized bus bars are present in the overhead. <I> **** Actions Taken **** A caution notice was added to the base of the ladder to inform personnel that an electrocution hazard exists in the overhead and that a clearance order was required to access the scaffold.
401888 | CR | 20191203 |  | 4 | RP exceeded dose estimate in November |  |  |  | N | NO | <D> **** Detailed Description **** RP received 238mrem vs a goal of 176mrem in November. 31mrem was due to emergent work ans 37mrem was Pre-job surveys for upcoming work. Radwaste activities were 11mrem over estimate for this month also. <I> **** Actions Taken **** Wrote CR
401890 | CR | 20191203 |  | 3 | SD000134 for Condensate needs some updates |  |  |  | N | YES | <D> **** Detailed Description **** In the DESIGN BASIS section at the begining of the SD it has incorrect numbers for mass flow rate, pressure and temperature listed. The current FSAR numbers are in section 10.4.7.2. Some of the photos in the SD can use an update due to panel changes that have occurred over time. <I> **** Actions Taken **** Informed instructor. <N> **** Equipment Description **** SD000134 updates
401891 | CR | 20191203 |  | 4 | Received H13.P840.A4 drop 9-5 "CW CHEMISTRY TOUBLE" | N | N |  | N | YES | <D> **** Detailed Description **** At 10:30, the MCr received 4.840.A5 9-5 "CW CHEMISTRY TROUBLE" alarm. CW blow down flow automatically isolated. EDNA point DHBDPH read CW blowdown PH at 0. Took actions per ARP. <I> **** Actions Taken **** Informed Chemistry, Dispatched OPS4 for ARP actions. | 02-00-CW-PHIC-1
401893 | CR | 20191203 |  | 3 | WO 02137241 rescheduled from the 12/2/19 work week |  |  |  | N | YES | <D> **** Detailed Description **** WO 02137241, CABLE 1SM7-0060 TRAIN RADIUS IS LESS THAN THE REQUIREMENT, required re-schedule from the 12/2/19 work week due to issues and alternate solutions identified during implementation. This required rescheduling of the work order to the next safety system window in in 2020. Because the work was not completed, inspections of the cables will be performed to identify any degradation. <I> **** Actions Taken **** Discussed with OCC Rescheduled to 12/2020 Notified management team <N> This work was ultimately completed in the work week. There is no additional action required for this CR based on the work being completed. | 02-00-RHR-M-P/2A
401896 | CR | 20191203 |  | 4 | Williams Plant Services over November monthly dose estimate |  |  |  | N | NO | <D> **** Detailed Description **** Williams Plant Services went over the Departments November monthly dose estimate of 215 MR, the monthly actual was 374 MR. The monthly department dose goal was 193 MR. Zone 13 Fire Detector installation dose was not transferred into the month of November from October. This accounted for an additional 56 MR that was not in the WPS November estimate. The camera cable installation work went over the monthly dose estimate by 69 MR. The dose for this work was under estimated. Our General Foreman contacted ALARA every day when they knew they were not going to meet their dose goal for the day or week. One instance the dose rates were higher in the overhead than anticipated, as a survey was not performed until after the scaffold was installed. It was then identified that the dose rates were 11 MR/HR. This was due to being above the RHR A piping that had lead shielding on the bottom portion of the pipe. No shielding was on the top side of the piping. <I> **** Actions Taken **** Contacted Health Physics and Management.
401897 | CR | 20191203 |  | 4 | OCA 87 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** OCA 87 is not functioning as designed and requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervision notified. Initiate CR/WR <N> **** Equipment Description **** OCA Camera 87
401898 | CR | 20191203 |  | 4 | Broken 110v Duplex Receptacle | N | N |  | N | NO | <D> **** Detailed Description **** A broken 110v duplex receptacle was found in the Yakima Building (B27) 456 elevation, 232C office area. Operations initiated work request 29152974 for repairs and tagged the receptacle as non-functioning. <I> **** Actions Taken **** Facilities & Commercial Engineering was advised. The receptacle was identified as 5BC-26 in CAD File 0272EP001 sheet EP3.
401899 | CR | 20191203 | CAQ | C | Standard Found out of Tolerance | N | N |  | N | NO | <D> Calcode #0064458 Thunder Scientific Model 1200 Humidity Generator SN 0702035 was found out of tolerance and adjusted to manufacturer specifications. <I> For Trending purposes only <N> CR at INPROG. Approved CR, moved to SRO for OPS Review.
401900 | CR | 20191203 |  | 4 | Task not performed per schedule |  |  |  | N | NO | <D> **** Detailed Description **** Operations had a scheduled task on 12/2/19 to lift the danger clearance for RHR-V-4A in support of the RHR-SYS-A maintenance outage. A decision was made to not lift the clearance per the schedule and to lift the clearance with the rest of the system clearance the next day. This decision to not adhere to the schedule was not communicated to the OCC or WWM. CR is for trending purposes. Reference D-RHR-V-4A-001. <I> **** Actions Taken **** Clearance was lifted although not per the schedule. Thumbs down discussion at production meeting and OFM.
401902 | CR | 20191203 |  | 3 | Gaps to Excellence during RHR-P-2A outage |  |  |  | N | NO | <D> **** Detailed Description **** The challenges presented during the RHR-SYS-A outage have shown that we are not meeting the INPO 12-012 Traits of a Healthy Nuclear Safety Culture in our work processes. Example 1: Removing clearance required work scope (WO# 02122835) on day 1, due to crediting past work. The credited work was completed in December 2018, allowing ample time to update the scope for the week. This scope removal challenged the operating crews to shift resources and to determine the required operability test for the system. Trait example: WP.1c. Leaders consider the impact of changes to the work scope and the need to keep personnel apprised of the work status. Example 2: WO#02137241 to repair an inadequate bend radius for RHR-M-P/2A cabling had inadequate contingency actions ,resulting in schedule delays. With high risk work scheduled after the completion of the RHR system outage, delays to this schedule are more impactful. Trait example: WP.1b. The work process appropriately prioritizes work and incorporates contingency plans, compensatory actions, and abort criteria as needed. In all, the most important thing is that the work is performed safely, but these examples show where we have room to improve.
401903 | CR | 20191203 | CAQ | C | Sole plate on FP-P-2B is cracked at hold down bolt holes | N | Y |  | N | YES | <D> **** Detailed Description **** During pump replacement for FP-P-2B under WOT 02046143 task 01 cracking was identified on the holes associated with the pump to sole plate attachment. The sole plate appears to be cast iron and is grouted onto the pump floor. One of the cracks appears to be to the extent of reaching to one of the imbedded anchors. Recommend replacement of the soul plate with carbon steel material. Pump is out of service <I> **** Actions Taken **** Contacted system engineer | 02-00-FP-P-2B
401904 | CR | 20191203 |  | 3 | (QA) CGS CRE/Source Term Reduction Plan not Updated | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) The CGS CRE/Source Term Reduction Plan was not annually updated as required by GEN-RPP-01. If the dose reduction plan is not maintained current, opportunities to fund and implement dose reduction initiatives may not be effectively implemented. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality and Radiation Protection, recommend assignment to Radiation Protection.
401905 | CR | 20191203 | CAQ | C | (QA) Dose Reduction Assessments Missing Required Element | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) Periodic assessments of ALARA program effectiveness do not include a review of groups receiving the highest exposure, contrary to Regulatory Guide 8.10. Radiation Protection performed ALARA program self-assessments that included all of the elements except a review of groups receiving the highest exposures. This increases the risk of delayed or missed implementation of dose reduction initiatives. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality and Radiation Protection, recommend assignment to Radiation Protection.
401906 | CR | 20191203 | CAQ | C | (QA) Source Log Deficiencies | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) RW 487â€™ source locker tracking log had four instances of incorrect locations and six instances of ditto marks for locations. Accurate source tracking and records ensure positive control. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality and Radiation Protection, recommend assignment to Radiation Protection.
401907 | CR | 20191203 | CAQ | C | (QA) Inconsistent application of Alpha smear analysis | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) 3 of 5 sampled contamination surveys did not meet the alpha activity analysis required in Table A of PPM 11.2.13.1. Not applying consistent Alpha smear analysis to ensure an accurate area contamination assessment increases the risk for a failure to identify an Alpha Level 2 or 3 area and appropriate measures to mitigate worker exposure. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality and Radiation Protection, recommend assignment to Radiation Protection.
401908 | CR | 20191203 |  | 3 | (QA) ALARA Briefing Not Documented | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) An ALARA briefing was not documented for High Radiation Area (HRA) Radiation Work Permit (RWP) 30004487 as required by PPM 11.2.2.14. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality and Radiation Protection, recommend assignment to Radiation Protection.
401909 | CR | 20191203 |  | 3 | (QA) High Risk Post Job Reviews Not Performed. | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) A sample of 3 of 3 High Risk Work Plan Post job reviews were not completed as required by PPM 1.3.76. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality and Radiation Protection, recommend assignment to Radiation Protection.
401910 | CR | 20191203 |  | 3 | (QA) JIT Details Not In ALARA Plan | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) RWP 30004487 Mock up Just in Time Training (JIT) details were not added to the ALARA Plan in accordance with PPM 11.2.2.14 . (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality and Radiation Protection, recommend assignment to Radiation Protection.
401911 | CR | 20191203 | CAQ | C | (QA) PMID-RQs Should Be ESSN | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) Preventive Maintenance Identification-Requirement (PMID-RQs) 19681-01 and 22219-01 for respiratory equipment are not categorized as Essential (ESSN) as specified by PPM 1.5.13 as this PMID-RQ fulfills requirements specified in 10 CFR 20.1703. The PM Category "OTHR" is lower priority, and the potential consequences are cancellation or late performance of a regulatory-required PM Work Order Task (WOT). (See EDMS for detailed description) PMIDs are not associated with SSCs, implements 10 CFR 20.1703 respiratory equipment testing and are being performed. <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality and Radiation Protection, recommend assignment to Radiation Protection.
401912 | CR | 20191203 | CAQ | C | (QA) RP Work Documentation Errors | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) 10 of 19 sampled Radiation Protection (RP) Preventive Maintenance (PM) Work Order Tasks (WOTs) contained documentation errors. Examples include missing pre-job brief documentation, improper data corrections, and incorrect next calibration due dates. Legibility and accuracy of the Quality Assurance Records is adversely affected. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality and Radiation Protection, recommend assignment to Radiation Protection.
401913 | CR | 20191203 | CAQ | C | Minimum train radius for 1SM7-0060 | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of WO 02137241 task 01, it was identified that the as found condition of the cables within the termination box at RHR-M-P/2A did not meet the train radius criteria as specified in EC 17511. Further manipulation of the cables identified that the train radius criteria specified in the EC cannot be met within the current termination box due to the length of the field cables (1SM7-0060). The scope of the WOT 02137241-01 was to cut back the cables within the termination box, reinstall stress cones and re-terminate; this was not performed due to time constraints. <I> **** Actions Taken **** Initiated CR. Notified OCC. <N> Remaining actions to restore to proper train radius is being addressed through the referenced work order. No additional action needed. | 02-00-RHR-M-P/2A
401914 | CR | 20191203 |  | 4 | (QA) Supervisor Not Assigned Respiratory Qual Group | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) One Health Physics (HP) Craft Supervisor of respirator users is not currently qualified to the Qualification Group Level contrary to ISPM-17. The supervisor has credit for the required course, but is not assigned to the correct qualification group. Qualification documentation demonstrates compliance with regulatory requirements. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality and Radiation Protection, recommend assignment to Radiation Protection. <N> Supervisor is now green in PQD for PA04. No further action required.
401915 | CR | 20191203 |  | 3 | (QA) Monthly Breathing Tests Not Performed | N | N |  | Y | NO | <D> **** Detailed Description **** (QA) Monthly radioactive contaminants plant breathing air testing was not completed during the May/June 2017 refueling outage, contrary to GEN-RPP-05. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality and Chemistry, recommend assignment to Chemistry.
401916 | CR | 20191203 | CAQ | D | Hole in FP-P-2B pump casing | N | Y |  | N | YES | <D> **** Detailed Description **** A quarter to half dollar size hole was found in the pump casing of FP-P-2B. Monitoring and trending of pump identified issues with the pump developing adequate pressure. The hole found in the 5th stage impaellar is the likely cause of the degradation. Picture will be placed in EDMS folder of parent AR. <I> **** Actions Taken **** Wrote a CR for tracking/trending. FP-P-2B is being repalced with a new pump and motor with WO 02046143. No actions with this CR, CR written just to document as-found condition. FP-P-2B is out of service and the as-found hole does not currently affect functionality of the pump. Recommend close-to-trend. <N> **** Equipment Description **** Grade Level - CWPH | 02-00-FP-P-2B
401917 | CR | 20191203 |  | 3 | WCI-4 needs revision to align EITER priority with PPM 1.3.68 | N | N |  | N | NO | <D> **** Detailed Description **** WCI-4 should be revised to align with the guidance of PPM 1.3.68 regarding prioritization of work on plant equipment important to emergency response (EITER). WCI-4, Online Work Process was revised on July 9, 2019 in a manner that caused its guidance (for determining the priority of maintenance on plant equipment that also serves an emergency preparedness function) to deviate from the guidance in PPM 1.3.68, Work Management Process. PPM 1.3.68 is aligned with current industry best practice standards. The revised text in WCI-4 is not. <I> **** Actions Taken **** Discussed with EP Manager & initiated this CR.
401918 | CR | 20191203 |  | 3 | Vendor services attained outside of contract | N | N |  | N | NO | <D> **** Detailed Description **** A contracted vendor was engaged to provide additional services that was later realized to be outside the scope of the current contract (354212). Payment of the first invoice was made via department credit card. During supervisor review of the credit card allocation statement, credit card payment versus contract payment was questioned and it was determined that there was an internal misunderstanding within the department regarding the payment methodology for the added service. When the situation was discovered, we reached out to contracts to acknowledge the unintended out of process scenario and for direction on how to proceed. The second/final payment is pending as of the initiation of this CR. <I> **** Actions Taken **** When the situation was discovered, we reached out to contracts to acknowledge the unintended out of process scenario and for direction on how to proceed. The second/final payment is pending as of the initiation of this CR. <S> Additional documentation added to EDMS. Original intent was to follow the contracting process. A miscommunication within the department resulted in getting out of process. A department briefing reviewing expectations was completed December 4, 2019.
401919 | CR | 20191203 |  | 3 | Security Computer not sending current data to corp network | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** The IEBS Host has not been sending current IEBS BADGE table export file thru the diodes to the corp network <I> **** Actions Taken **** Comp Engineering with IS support is working on resolution...servers have been restarted, full manual exports done, but issue is not resolved
401920 | CR | 20191203 |  | 3 | PRA model updates to reflect plant changes will be inspected | N | N |  | N | NO | <D> **** Detailed Description **** NRC Change Notice 19-038 describes revisions to multiple documents including NRC Inspection Manual 71111.18. For plants that have implemented 10 CFR 50.69, TS Surveillance Frequency Control Program (SFCP), or TS Risk-Informed Completion Time (RICT) the following Inspection considerations apply: The PRA model is appropriately updated to reflect plant modifications. This inspection will apply to CGS as the station is approved for the SFCP and has plans to implement 50.69 and RICT. SYS-4-34, PSA configuration Control, is the procedure CGS uses to maintain configuration control over the PSA model. Per step 4.1.1 the PSA group is responsible for monitoring Design changes using the Design Attribute Review form or Form 7. However, the responsible engineer for the EC is responsible for identifying other plant departments that may have plant documents that require revision as a result of the change. Design engineers are trained on design basis requirements and are not trained on probabilistic risk models. The process should not rely on engineers who are not knowledgeable of the PRA model to identify if there may be an impact. Recommend that the EC process be revised to require the PSA group to be included on the design attribute review for all ECs or another process is implemented to ensure the PRA group is contacted for all ECs. This will reduce the risk of missing a PRA impact design change which could lead to an NRC violation. Recommend assign to Design Engineering.
401921 | CR | 20191203 |  | 3 | PRA model updates to reflect operating procedure changes | N | N |  | N | NO | <D> **** Detailed Description **** PRA model updates to reflect operating procedure changes relies on the individual revising the procedure to identify the PSA group as an impacted party. SYS-4-34, PSA configuration Control, is the procedure CGS uses to maintain configuration control over the PSA model. Per step 4.1.a the PSA group is responsible for monitoring changes in operating procedures including: system operating procedures, abnormal condition procedures, emergency operating procedures, and severe accident guidelines. The step references Form 23761. The process relies on the individual revising the procedure to identify and include the PSA group as a cross discipline review. Station personnel are not trained on the PRA model inputs and should not be relied upon to identify the PRA group as an impacted party. A new process needs to be developed to ensure all procedure changes that impact the PRA are captured. Recommend assign 3 to AR-RXENG
401922 | CR | 20191203 |  | 4 | BS and SS RV tailpipe temperatures indicate lifting | N | N |  | N | YES | <D> **** Detailed Description **** During monitoring and trending it was found that on 11/23/2019 at 0700 the cycle isolation monitoring temperatures downstream of BS-RV-26A&B and BS-RV-47A&B had a step change of 15-20 degF and began cycling at the elevated temperature. The cycling temperatures are indicative of lifting of one of the 6 relief valves that connect to a common discharge header. See EDMS files for trend plots. Temperatures indicate that lifting is less significant than the Dec 2017 incident (AR 374506) and there is no significant drop in HP turbine first stage pressure that would equate to a MWe loss. <I> **** Actions Taken **** Notified thermal performance, relief valve and AOV program owners and their respective supervisors. Performed a walkdown of MS-PIC-18A&B and BS-PIC-18A&B and no significant issues were observed. <N> **** Equipment Description **** T -484- - -F0/4.8 - | 02-00-BS-RV-26A
401923 | CR | 20191203 | CAQ | C | NRC observation of protection scheme implemenation |  |  |  | N | NO | <D> **** Detailed Description **** Prior to the recent CRD window, the NRC resident noted the protection scheme was not hung accordingly. This was pointed out to the shift manager and resolved immediately. The shift manager did not initiate a condition report as expected at the time, thus this condition report covers both not initiating the condition report in a timely manner and to document the observation by the NRC resident. A night order has been generated by the on-shift shift manager to ensure the operating staff understands the expectations regarding condition report generation in regards to NRC observations. <I> **** Actions Taken **** initiated night order to reinforce expecations. discussed issue with shift managers during tuesday phone call. Operations management will conduct random reviews of protection schemes to ensure adequacy. <N> Recommend CAQ C to AR-OPSCM for follow up to document night order and effectiveness of communication and protection scheme implementation.
401924 | CR | 20191203 |  | 3 | (NRC) Concern Raised During IP 71111.11 | N | N |  | N | NO | <D> **** Detailed Description **** During the Biennial Requalification Inspection IP 71111.11, a concern was raised by the NRC regarding the reporting periodicity of medical amendments to Operator Licenses. CGS will need to address the impact of License Renewals on the reporting frequency of ongoing medical amendments. <I> **** Actions Taken **** Informed the Training and Regulatory Affairs Managers.
401925 | CR | 20191203 |  | 3 | Procedures direct operator to use a superseded SOP | N | N |  | N | NO | <D> **** Detailed Description **** SOP-FLEX-GEN-DG5-PM was been superseded by OSP-FLEX-Q705 on 7/10/19. The following procedures still direct the use of SOP-FLEX-GEN-DG5-PM: SOP-FLEX-GEN-DG5-SHUTDOWN, SOP-FLEX -GEN-DG5-SHUTDOWN-QC, SOP-FLEX-GEN-DG5-START, and SOP -FLEX-GEN-DG5- START-QC <I> **** Actions Taken **** Generated this CR
401926 | CR | 20191203 | CAQ | D | Rod Accumulator Trouble Alarm on CRD-HCU-0647 | Y | N |  | N | YES | <D> **** Detailed Description **** Rod Accumulator Trouble Alarm P603-A7 drop 6-7 for CRD -HCU-0647 was due to high water level. OPS 2 drained water per SOP-CRD-HCU and alarm is clear. trend only | 02-00-CRD-HCU-0647
401928 | CR | 20191203 | CAQ | C | CMS-SR-20 lost power | Y | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During performance of WO# 02143125-01, CMS-SR-20 lost power and shut down. <I> **** Actions Taken **** Informed Operations and Supervision. Verified sample rack in safe condition. Wrote CR/WR. <N> **** Equipment Description **** 548RX
401929 | CR | 20191203 |  | 4 | MT-ELEV-4 door mechanism damaged belt | N | N |  | N | YES | <D> **** Detailed Description **** Found MT-ELEV-4 door stuck open on elevation 441 with door mechanism stuck and attempting to close. The pulley system was spinning with no belt movement and causing belt to smoke excessively. That spot on built is now excessively worn and should be replaced. Door is having sticking probems previously identivied in AR 401820 <I> **** Actions Taken **** Informed MCR, Reset the door, power removed. | 02-00-MT-ELEV-4
401937 | CR | 20191204 | CAQ | C | (QA) SCBA Bottle Hydrotest Certificates Not in Records |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) 3 of 3 sampled groups of Self-Contained Breathing Apparatus (SCBA) hydrotest certificates were not in records location DIC 1564.1, contrary to GEN-RPP-05. This is a repeat of similar hydrotest certificate Records issues identified in 2009, 2016, and 2018. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality and Radiation Protection, recommend assignment to Radiation Protection.
401938 | CR | 20191204 | CAQ | C | (QA) TEDE ALARA Evaluations Errors |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Five of five Total Effective Dose Equivalent (TEDE) ALARA evaluations reviewed contained procedure non -compliance and human performance errors indicating a lack of rigor by personnel completing the forms, and ineffective supervisor oversight. In one case, a less conservative Respiratory Efficiency Factor (REF) was used for the calculation specified by procedure. Other errors included using the incorrect calculation revisions, not addressing engineering controls dose and not authenticating the record with signature, printed names, and dates. The audit team did not identify any instances where the errors above resulted in making the wrong determination for respirator use; however, they demonstrate a lack of rigor increasing the risk of error. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality and Radiation Protection, recommend assignment to Radiation Protection.
401939 | CR | 20191204 | CAQ | C | (QA) 3 Expired SCBA Cylinders Not Removed From Service |  |  |  | Y | NO | <C> As per discussion from the MRT, this CR has been changed from a non-caq 3 to CAQ C/MECSHOP. See email in EDMS. <D> **** Detailed Description **** (QA) Three Self-Contained Breathing Air (SCBA) cylinders with expired hydrostatic test certificates were filled instead of removed from service, contrary to PPM 10.2.62. Hydrostatic tests of the SCBA cylinders every 5 years verify structural integrity and safety throughout the maximum 15-year service life. Subsequently identified and removed from service by PM 3 months later. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality, Maintenance, and Radiation Protection, recommend assignment to Mechanical Maintenance.
401940 | CR | 20191204 |  | 3 | (QA) Two RP Procedures Missing Requirements Tracking |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) GEN-RPP-01 and GEN-RPP-10 contain steps satisfying regulatory requirements without requirements tracking, contrary to SWP-PRO-03. The reference numbers protect future procedure changes from inadvertently deleting steps (or portions of steps) that satisfy regulatory requirements. (See EDMS for detailed description) <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality and Radiation Protection, recommend assignment to Radiation Protection.
401941 | CR | 20191204 |  | 4 | Employee slipped on ice leading to First Aid |  |  |  | N | NO | <D> **** Detailed Description **** Employee was traversing across site when they slipped on an isolated section of pavement that resulted in employee self-administering first aid and returned to work. The employees immediately notified supervisor and sift manager to walk down the surrounding area for additional conditions, area was corrected. <I> **** Actions Taken **** Security Management, Shift Manager, Safety, Occupational Health notified and CR initiated.
401942 | CR | 20191204 |  | 4 | OCA 90 Requires Maintenance | N | N |  | N | YES | <D> **** Detailed Description **** OCA 90 is not functioning as designed and requires maintnenance. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervision notified. Initiated CR/WR <N> **** Equipment Description **** OCA 90 located at the PAAP
401943 | CR | 20191204 | CAQ | D | CPR-V-361 didn't open during resin flush following recirc | N | N |  | N | YES | <D> **** Detailed Description **** CPR-TK-92A was placed in recirc in anticipation of a resin transfer. Performed steps 5.4.1 to 5.4.7. of SOP -RW/CPR-OPS. While CPR-TK-92A was reciculating per step 5.4.8, I was notified by the Laborer a resin transfer will not be taking place today. At that point I switched to SOP -RW/CPR-OPS section 5.6 to secure recirculation. Steps 5.6.1 through 5.6.9(e) were completed. I attempted to open CPR-V-361 per 5.6.9(f) but it did not open. No relay noises were heard and the closed light remained lit. 5.6.9(f) states to hold CPR-V-361 open for approx. 30 seconds; it was held for approx 2 min without indicating open. (Previously, CPR-V-361 was opened on 5.6.9(b) for 3 minutes . There was light indication and a level increase in CPR-TK-92A of about 3%.) Step 5.6.9(g) was already closed due to not opening, and step 5.6.9(h) was performed to close CPR-V-356A and closeout Section 5.6. <I> **** Actions Taken **** Notified CRS | 02-00-CPR-V-361
401944 | CR | 20191204 |  | 3 | (QA) GEN-RPP-05 Cites Obsolete MI-2.4.1 |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) GBP-RPP-05 cites obsolete MI-2.4.1. A procedure citing an obsolete document can lead to a loss of productivity. Factual Basis: â€¢ GEN-RPP-05 "Respiratory Protection Program Description,â€ rev 015, step 3.5.8 points to MI- 2.4.1 "Inspection of SCBA Cylinders and Cylinder Valve Maintenance," for Self -Contained Breathing Apparatus (SCBA) air cylinder inspection and SCBA cylinder valve maintenance. â€¢ MI-2.4.1 went to "HISTORY" status on 9/19/2012 in Asset Suite. Insights: â€¢ Asset Suite does not show what document superseded MI -2.4.1, however PPM 10.2.62, â€œBreathing Air Compressor Operation,â€ appears to perform some of the functions that were performed by MI-2.4.1. <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality and Radiation Protection, recommend assignment to Radiation Protection.
401945 | CR | 20191204 |  | 3 | (QA) Missing WO Hold Code |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) Work Order (WO) 02140205 did not have a â€œHRP-High Risk Work Plan Approvalâ€ hold code as required by PPM 1.3.76. The lack of hold code prevents direct monitoring to ensure high risk plans are approved by T-3 week. (See EDMS for detailed description) NOTE- Work is now complete and a high risk plan was approved and used. <I> **** Actions Taken **** This was identified as a Deficiency during the Radiation Protection and Process Control Audit, AU-RP/RW-19. Informed Quality, Maintenance and Radiation Protection, recommend assignment to Maintenance.
401949 | CR | 20191204 | CAQ | C | 10.27.67 & 10.27.68 Need procedure change |  |  |  | N | NO | <D> **** Detailed Description **** During walkdown it was identified 10.27.67 and 10.27.68 need a procedure change, the current revisions would not be able to be perform as currently written. <I> **** Actions Taken **** Wrote CR & discussed changes with Procedure Writer, Informed Supervison
401950 | CR | 20191204 | CAQ | D | PM Inspection not performed as per procedure | N | N |  | N | NO | <D> **** Detailed Description **** PPM 10.25.187E section 7.13 â€“ Fuse Inspections Note 1 instructs electricians to replace line power fuses and secondary control fuses with new fuses during the MCC starter /bucket inspection. There has been inconsistences following this instructions during some past bucket inspections as reflected in the fuse logs. Currently fuse log page 0595-001 indicates that one fuse was replaced while inspecting FDR-42-7CA2B starter under WO 02091705. Review of work package 02091705 indicates 2 line fuses and one control power fuses were replaced. Based on EWD-35E -001, 3 line fuses should have been replaced. There should be consistency in the information recorded on the fuse logs and work instruction. Procedure adherence is part of the excellence model and should be followed while performing PM activities in-order to avoid reworks. <I> **** Actions Taken **** Spoke with E-shop supervisor E-shop supervisor James Hardman informed me that the electricain had recorded to have picked the 3 line fuses on fuse log sheet page 589 and because there was not enough space on 589, the electrian recordered the 1 control fuse on page 590. Because we have had previous fuse logs not matching information indicated in the work packages, I recommend this CR going to the E-shop group for trending
401952 | CR | 20191204 |  |  | BUILDING 13 INSPECTOR TEST SIGHT GLASS LENS IS BROKEN |  |  |  | N | YES | <D> **** Detailed Description **** While performing15.3.15 Fire System internal inspection it was found that the sight glass below the inspector test valve FP-V-B13/05 is broken and needs to be repaired. | 02-00-FP-V-658
401953 | CR | 20191204 |  | 4 | Building 13 inspector test sight glass is broken | N | N |  | N | NO | <D> **** Detailed Description **** While performing 15.3.15 Fire system internal inspection it was found that the sight glass lens below FP-V-B13/05 (inspector test valve) is broken. <N> **** Equipment Description **** Building 13
401954 | CR | 20191204 | CAQ | D | Green "Power On" Lamps LT-1 on REA-FU-2A/2B not illuminated | N | Y |  | N | NO | <D> **** Detailed Description **** For upcoming work on 15.2.29 for heat Detector water spray CFTs, for REA-FU-2A WOT 02109860, one of the first steps is to check that the power on lamp is illuminated. Currently the unit is powered on as REA-FN-2A is in service however the Green LT-1 lamp is not illuminated. This is common for both REA-FU-2A and 2B units, although REA-FU-2B is not currently in service. <I> **** Actions Taken **** Provided picture for SSS who was going to have an EO address the lamps. <N> **** Equipment Description **** Green LT-1 lamp for Power On indication for REA-FU-2A Heat Detector Water Spray Control Box. REA-FU-2B as well.
401955 | CR | 20191204 |  | 3 | (QA) No effective process for review and optimization of PM |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) No process in place to satisfy the procedural requirement to continuously review and optimize PMs. Potential impact to miss opportunities to increase reliability of equipment, while at the same time gaining efficiencies with how maintenance resources are used. See EDMS for full text. <I> **** Actions Taken **** This was identified as a deficiency during the Equipment Reliability Surveillance, SR-19-16. Informed Maintenance and Engineering
401956 | CR | 20191204 |  | 3 | (QA) Reinstate PMRC or similar forcing function |  |  |  | Y | NO | <D> **** Detailed Description **** (QA) A forcing function is necessary to ensure regular review and optimization of plant PMs. The Preventive Maintenance Review Committee used to serve the function of reviewing and optimizing PMs. It met regularly, comprised of component managers, unit coordinators, engineering, and others. They would collectively look at recent PM performance and challenge each other on periodicities. Shop personnel stated PMRC was useful, but was disbanded within the last four years. No one knew why or exactly when. They said it was useful to find real issues and prevent rework. It forced owners to talk about it. One individual stated a recurring AR to force the review at an individual level, in lieu of the committee would also be beneficial. All those asked expressed their thoughts that the PMRC, or a similar forcing function, would be beneficial. <I> **** Actions Taken **** This was identified as a recommendation during the Equipment Reliability Surveillance SR-19-16. Maintenance and Engineering informed.
401959 | CR | 20191204 |  | 3 | NRC Feedback - Improvement to TDI-23 Scenario Guide Developm |  |  |  | N | NO | <D> **** Detailed Description **** It was noted by the NRC during the 71111.11 inspection on 12/3/2019 that one scenario guide listed some expected alarms (annunciators) while another scenario guide did not. NRC inspectors recommended listing important alarms that are applicable to the scenario in the scenario guides. They specifically stated there is no direct regulatory requirement for this, but that it can really help both inspectors and instructors when performing evaluations. Recommend adding a new statement in section 4.4 of TDI-23 that reads something like the statement in EDMS doc. Recommend assignment to operations training and Training Supervisor for resolution. <N> (name removed from AR Description field in CR).
401962 | CR | 20191204 |  | 4 | TOA-HV-1A steam leak | N | N |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was discovered that TOA-HV-1A has a steam leak on the heating coils. Water is leaking and pooling onto the floor around the unit. <I> **** Actions Taken **** Notified CRS and wrote CR | 02-00-TOA-HV-1A
401965 | CR | 20191204 | CAQ | C | EWD-36E-032 drawing is incorrect |  |  |  | N | NO | <D> **** Detailed Description **** At D9 in drawing EWD-36E-032 â€œA1 POWER FILTER ASSEMBLYâ€ there is only one fuse on the Hot. The drawing shows a fuse on L1 and L2. <I> **** Actions Taken **** Notified System Engineer
401966 | CR | 20191204 |  | 4 | Electronic Information Monitor Not Working |  |  |  | N | NO | <D> **** Detailed Description **** An electronic information monitor located in the Yakima Building second floor is not working. The unit does not appear to have electrical power and/or the Ethernet feed is not operating. The location is Yakima Building (B27), elevation 456, outside room 217 (PGMâ€™s office). <I> **** Actions Taken **** Initiated CR and WR. No EPN. This is non-plant equipment installed by Information Services. <N> **** Equipment Description **** Yakima Building Elevation 456 outside room 217
401967 | CR | 20191204 |  | 4 | Late eSOMS entry for work hours |  |  |  | N | NO | <D> **** Detailed Description **** An individual from org 52622 was scheduled to work from 0600-1600, which was reflected in eSOMS. Prior to 1600, the individual was asked by their supervisor to hold over an additional two hours. These two additional hours were never entered into eSOMS. eSOMS has been updated and no fatigue rule violation occurred. <I> **** Actions Taken **** Notified supervision. eSOMS updated. CR initiated.
401969 | CR | 20191204 | CAQ | D | CMS-SR-20 | Y | N |  | N | YES | <D> **** Detailed Description **** Check voltages within the rack and it appeared at the RM -2000 cabinet a neutral was lost. We checked the fuse inside the Power filter assembly and it was good. Closed CMS-DISC-SR20/SW1 and rack power came back on. We suspect that disconnect is out of alignment. Discussed with supervisor and CRS about electricians investigating the disconnect. <I> **** Actions Taken **** Notified System Engineer Notified CRS Notified Supervisor | 02-00-CMS-DISC-SR20/SW1
401970 | CR | 20191204 |  | 3 | Evaluate tagging out DEH-AC-IR for proper cleaning | N | N |  | N | NO | <D> **** Detailed Description **** During performance of WO 02150282-01 DEH-AC-IR/TRIP replace filters/clean coils, it was noticed that the coils for both the evaporator and condenser of the unit were extremely dirty. Although they were able to be cleaned with air, it needs to be evaluated to do a proper cleaning of the coils with water. This will require the unit to be tagged out. This could be done during an outage prior to startup or during a DEH maintenance window. The unit functions as it should but without properly cleaning the coils over a long period will have a negative impact on unit efficiency. <I> **** Actions Taken **** Engineering evaluate the Maintenance recommendation
401972 | CR | 20191204 |  | 4 | TPE Failure PQD code HP001907 |  |  |  | N | NO | <D> **** Detailed Description **** TPE failure while performing a task to Don and Remove Powered Air Purifying Respirator (PAPER). Failure based on not meeting all task standards under Required Performance Components per GEN-TQS-03 attachment 9.1. Precautions and Limitations were not fully discussed. Trend. <I> **** Actions Taken **** Performed actions IAW GEN-TQS-03 section 5.4.24.
401973 | CR | 20191204 |  | 4 | Images Delayed for Implemented Procedure Revisions |  |  |  | N | NO | <D> **** Detailed Description **** The Automated Procedure Process was not able to immediately process some images for procedure revisions implemented 12-04-2019. This resulted in a delay for some users to access these images from Asset Suite and EN Docs. The cause was identified and resolved and the images are now available. This issue was caused by a user replacing the Procedure Native file in a revision document set with a file that was created outside of the automated process. The foreign document contained metadata for a different document number than the document number that was being revised. SWP-PRO-02 and GBP-PRO-03 specify to edit the native file that populates the document set when a revision is created in the automated process. The reason behind this specification is to ensure the integrity of the underlying metadata is maintained. <I> **** Actions Taken **** Verified the cause and resolved the issue for the affected document images. Wrote CR for information and trending.
401975 | CR | 20191204 |  | 4 | Less than adequate housekeeping standards 422' RHR Pump Room |  |  |  | N | NO | <D> **** Detailed Description **** During a tour of the Reactor Building, it was observed that there was inadequate housekeeping (tools by contaminated boundary, tools and harnesses laying on floor) standards in the posted contaminated area entry to 422â€™ B RHR Pump Room. This information was provided to Operations and Radiation Protection. <I> **** Actions Taken **** The HP lead technician dispatched HP staff to address and the area has been cleaned up.
401977 | CR | 20191204 |  | 4 | Bldg 106 ISPM-6 Violation for Use of Extension Cord |  |  |  | N | NO | <D> **** Detailed Description **** During electrical inspection in Bldg 106, it was discovered that the media stand for the RWP log-in station and the media stand for the eSoms kiosk were powered from one common extension cord from which a power strip from each of the media stands was plugged into (daisy chained). This is not in compliance with ISPM-6. Immediate action: extension cord was removed and both media stands were powered down while an acceptable long-term solution is pursued. Notified facilities Fire Marshall. No further action required â€“ recommend trend.
401979 | CR | 20191204 |  | 4 | 16.1.7 Computer points found OOT | N | N |  | N | NO | <D> **** Detailed Description **** During the performance of 02135807-01 16.1.7 the TDAS x213 and Process computer point L106 were found out of tolerance. Per the surveillance instructions we contacted a computer technician and the points were calibrated back into tolerance. All as left values were in tolerance. <I> **** Actions Taken **** Calibrated computer points into tolerance, wrote CR for tracking.
401980 | CR | 20191204 |  | 4 | SEC-XD-6 Failed Operability test | N | N |  | N | YES | <D> **** Detailed Description **** SEC-XD-6 failed an operability test. Request I&C to investigate. <I> **** Actions Taken **** Unit will remain out of service; CR/WR generated | 02-00-SEC-XD-6
401981 | CR | 20191204 |  | 3 | COND-P-1B Seal Water Indicating Low | N | N |  | N | YES | <D> **** Detailed Description **** The seal water pressure for COND-P-1B as indicated on COND-PI-3BG has fallen from 60 psig on 7/3/2019 to 20 psig on 12/4/2019. Vendor drawing calls for 15-20 psi above suction pressure (see xref, note 7). Excessive seal water leakoff was identified at the start of the cycle (see xref). <I> **** Actions Taken **** Notified BOP Supervisor and Components Supervisor <N> **** Equipment Description **** T -441- - -D6/14.1- | 02-00-COND-P-1B
401982 | CR | 20191204 |  | 4 | TDAS was unable to be updated | N | N |  | N | NO | <D> **** Detailed Description **** During the performace of 02138407-01, 16.1.7 the TDAS X213 and L106 was found out of tolerance. They were calibrated back into tolerance and the PPC was updated. The TDAS computer was unable to be logged into and be updated with the new values. <I> **** Actions Taken **** Contacted supervisor, called engineering, wrote CR for tracking, and WR to update values. <N> **** Equipment Description **** MCR
401983 | CR | 20191204 |  | 4 | LED light on the OPS4 truck bumper fell off on pass. side | N | N |  | N | YES | <D> **** Detailed Description **** The bumper mounted LED light came loose from the mount. Suspect the vibration of the truck when driving to and from TMU loosened the screw that was holding the light to the mount. Noticed the light hanging off when returning from TMU. It was attached when I inspected the truck on rounds. <I> **** Actions Taken **** Ziptied the light to the towing bracket to prevent the cord from being stressed <N> **** Equipment Description **** Bumper mounted LED light on the OPS 4 truck.
401984 | CR | 20191205 |  | 3 | CW-SKID-2 switch CL-RMS-BP/1 is in bypass due recent issues | N | N |  | N | YES | <D> **** Detailed Description **** CW-SKID-2 switch CL-RMS-BP/1 is in bypass due recent issues with CW-SKID-2 tripping off and securing CW Blowdown. A caution clearnce has been placed on the bypass switch. 401891 was written to document the unexpected trip of the skid with WR 29152978 against CW-PHIC-1. 401705 was written about a TRH alarm securing the Skid with no WR against it. As it stand there does not appear to be a closure mechanism to return the dehaogenation skid back to service at this time. <I> **** Actions Taken **** Request that the cause of the unexpected trips of CL -SKID-2 be determined and a corrective action be put in place to allow reliable operation | 02-00-CL-SKID-2
401985 | CR | 20191205 |  | 4 | sightglass leak on TMU-M-1A | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** while electricians were performing weekly vibes on TMU pumps they noticed that there is evidence of bearing oil leaking from the upper bearing sightglass. There may potentially be multiple sources of bearing oil leak as the attached pictures will show the oil sheen on the East side of the motor is higher than the upper sightglass. The oil leak has been documented in the past (CR# 398107) <I> **** Actions Taken **** Notified CRS and Write CR <N> **** Equipment Description **** TMU Pumphouse TMU-M-1A
401992 | CR | 20191205 |  | 3 | TSP-DG1/LOCA-B501 procedure correction |  |  |  | N | NO | <D> **** Detailed Description **** TSP-DG1/LOCA-B501 Standby Diesel Generator DG 1 LOCA Test attachment 10.1 comkputer point X256-03 incorrectly titled SM-7 CKT BKR 8-1 POSITION. It should say "7-1 position". There is no 8-1 breaker. <I> **** Actions Taken **** Verified same point used in TSP-DG1/LOP-B501 is correctly titled.
401993 | CR | 20191205 |  | 4 | Near Miss - Employee Slipped on Ice |  |  |  | N | NO | <D> **** Detailed Description **** While walking on pavement outside building 9, an employee slipped on some ice. He was lucky there was another employee walking with him and helped him catch his balance. The area appeared to have adequate gravel and the employee had good traction shoes on, but the area was more slippery than anticipated. No injury occurred. This is a good example to walk carefully in icy conditions. <I> **** Actions Taken **** employee notified his supervisor.
401999 | CR | 20191205 |  | 4 | 21A Video Monitor | N | N |  | N | YES | <D> **** Detailed Description **** The video monitor at 21A requires maintenance. Contact 2185 for more details. <I> **** Actions Taken **** Security Supervision notifed. Initiate CR/WR. <N> **** Equipment Description **** BRE 21A Video monitoring system
402000 | CR | 20191205 |  | 3 | ABN-HAZMAT and spill kits |  |  |  | N | NO | <D> **** Detailed Description **** During fire brigade training and reiview of ABN-HAZMAT, the procedure requries certainn actions to occur, but the materical to accomplish the task is not readily available in the spill kit. Example danger tape and signs. Recommend reviwing spill procedures and improving the spill response kits accordinly to preclude challenging the fire brigade during events.
402005 | CR | 20191205 |  | 4 | Poisonous bugs in bld 35 |  |  |  | N | NO | <D> **** Detailed Description **** Two Scorpionâ€™s and a Black widow spider were killed in the Klickitat building 35. on week of 12/2/19. Suggest facilities spray building for bugs. <I> **** Actions Taken **** Notified Manager and wrote CR <N> **** Equipment Description **** Klickitat building 35
402006 | CR | 20191205 | CAQ | C | 10.20.18 procedure correction - DG3 12 year maintenance |  |  |  | N | NO | <C> MRT Change: CR 402006 moved from NON-CAQ Severity 3 to CAQ Severity C. Procedure on safety related system that was incorrect. <D> **** Detailed Description **** 10.20.18 step 7.57.28.i says to open isolation valves DLO -V-706A1, A2, B1 or B2. These valves are for DG1 and DG2. 10.20.18 is for DG3. This step should say " IF present Then, OPEN instrument isolation valve for DLO-PS-24."
402008 | CR | 20191205 |  | 4 | Point 271 on TG-TR-144 has failed downscale. | N | N |  | N | YES | <C> MRT Change: CR 402008 moved from CAQ Severity D/Trend Repair to NON-CAQ Severity 4/Trend Repair. <D> **** Detailed Description **** Point 271 is at -50Â° F on TG-TR-144. TG-TE-33 (pg 1, slot 3, pt 26) as displayed on DEH-MON-RO in the Main Control Room is reading normal at 143Â° F. | 02-00-TG-TE-33
402009 | CR | 20191205 |  | 3 | Inaccurate poster in Roosevelt Room (B64-R172) |  |  |  | N | NO | <D> **** Detailed Description **** The poster located directly behind the podium in the Roosevelt Room had an inaccurate Energy Services and Development Vision statement. Apparently the poster was not changed when the FY19-20-21 Strategic Plan and Excellence Model Handbook 5.0 were both approved and published. <I> **** Actions Taken **** Notified the Public Affairs Assistant Manager and removed the poster that contained the inaccurate information. See EDMS for additional information.
402010 | CR | 20191205 |  | 4 | Service building heater leak in pipe above HHW-V-57 | N | N |  | N | YES | <D> **** Detailed Description **** There is a slow drip coming from the pipe joint that is above HHW-V-57 on the service building heater.There is also sodium nitrite salt build up around that area due to the corrosion inhibitor in the leak. <I> **** Actions Taken **** Notified CRS, Chemistry Supervision and chemistry specialist <N> **** Equipment Description **** GSB basement service building heater. The valve listed is not the actual leak it is in the pipe joint above it. | 02-00-HHW-V-57
402011 | CR | 20191205 |  | 4 | WHCO-P-1B has packing leak leaking onto floor. | N | N |  | N | YES | <D> **** Detailed Description **** WHCO-P-1B has a packing leak that is running out onto the floor. This was written up as WR 29140233 which was cancelled to WO 02105482 which was cancelled when the planner walked it down in August when heating steam is shutdown for warm weather operation and therefore found no leakage. Please investigate and repair the packing. Also the run light bulb for WHCO-P-1B is broken off inside the socket and needs removal. This is a push and twist style lamp. Please remove old base from socket and replace the lamp. See picture in EDMS and WR attributes. <I> **** Actions Taken **** Informed laborers to install a catch for the leak. Wrote this AR/WR. <N> **** Equipment Description **** W437 L9/12.2 | 02-00-WHCO-P-1B
402012 | CR | 20191205 | CAQ | C | Electrical Safety Hazard Exists in E-CP-H13/604 | N | Y |  | N | YES | <D> **** Detailed Description **** On 10/24/19, while troubleshooting OG-RIS-601A, field measurements revealed there is a floating ground on the power circuit feeding the component. Shortly after replacement of the OG-RIS-601A rate meter at E-CP-H13/P604, field measurements reveal there is expected power coming into the device from Live to Neutral of 120 VAC, but when taking measurements to ground, it gave the craft 0VAC. Which means the Ground loop is open. Drawing EWD-36E-005 reveals device is supposed to be grounded at the panel common instrument bus bar. Drawing EWD-46E-203B shows Hot (or Live) and Neutral 120 VAC comes from E-PP-US, Circuit 4, Div A via E-CB-USPP/4. Drawing 02H13-05,61,1 shows the circuit provides power via outlet J1-AL-P11. See edms for previous email notifications.A review of AR 004005500 never initiated a WR to address this Electrical Safety Hazard condition that exists. WR needs to be coded IS. This condition does not impact OG-RIS-601A since the device is getting power to perform all of its design functions. This condition pertains to Electrical Safety to personnel in the event the circuit experiences a High Current to Ground Fault and there is no grounding protection, the personnel would become path to ground if making contact on the circuit at time of fault. AR 004005500 also states the condition as a â€œfloating neutralâ€ this is technically incorrect. <I> **** Actions Taken **** Notified EFIN Engineering Supervisor <N> **** Equipment Description **** RW 501 CR Purpose of CR is to have WR coded IS to address the safety issue. | 02-00-E-CP-H13/P604
402013 | CR | 20191205 |  | 4 | WHCO-CU-1 sight glass leaking. | N | N |  | N | YES | <D> **** Detailed Description **** WHCO-CU-1 sight glass lower gland is leaking. Tightened lower gland nut two flats and slowed the leak, but did not want to crack the glass. The gland seals are probably hard as this is at 200 F during coldweather operation. Please investigate and correct. See pictures in EDMS and WR attributes. <I> **** Actions Taken **** Tightened lower gland nut and wrote AR/WR. <N> **** Equipment Description **** W437 L9/12.2 | 02-00-WHCO-CU-1
402014 | CR | 20191205 |  | 4 | MT-CRA-3 West bridge function issues | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of FP-P-2B Replace Pump EC 17870 MT-CRA-3 (CWPH crane) West Bridge function is not working properly. When bridged West the crane cuts out intermittently. Crane remote batteries have been replaced several times but issue still occurs. Recommend FIN electrical investigate. <I> **** Actions Taken **** Notified MCR, WWM, and FIN team. Initiated CR. | 02-00-MT-CRA-3
402015 | CR | 20191205 |  | 4 | PIC calibration intervals result in duplication of work |  |  |  | N | NO | <D> **** Detailed Description **** Currently, the pocket ion chambers (PIC or DRD) at the station are calibrated at a six month interval. These PICs are spread throughout various locations across all plant areas, including Site One in emergency response kits. Within the kits, there are also dosimeters of legal record (DLR or OSL), which are changed out based on read period (twice per year, in January and July). In theory, these intervals should line up so that PICs and DLRs are swapped at the same time, but the PIC calibration due date is six months from the date of calibration, meaning it has five or less months of actual use in the field. This requires PICs to be swapped out approximately one month before the DLRs are changed. This duplication of work could be eliminated if the PICs were calibrated on an annual interval instead of a semi-annual interval. This would allow the PICs to be changed with the DLRs twice per year without exceeding the calibration due date of the PICs. <I> **** Actions Taken **** E-kit PICs were swapped out as required. <N> Cross referenced AR 357111, LDCN-16-044 (FSAR) Sect 12.5.2 CHG Inst. & DRD Cal/Test Freq. This AR is tracking the revision to the FSAR to incorporate changes to frequencies suggested in this CR. No further action required.
402017 | CR | 20191205 |  | 3 | OPDS implementation |  |  |  | N | NO | <D> **** Detailed Description **** the ability to disable the OPDS trip during periods when SDC is in service or when DG's are paralleled in 100%. if the operators can respond in a timely manner to preclude an event, then we should be able to disable OPDS on a risk informed basis.
402018 | CR | 20191205 |  | 3 | ABN-ELEC-INV procedure correction |  |  |  | N | NO | <D> **** Detailed Description **** In ABN-ELEC-INV step 2.3.2, it says in regards to a loss of E-PP-7AA: "RCC flow to Containment loads is isolated due to closure of RCC-V-5 and RCC-V-40 (loss of RC-1)." RCC -V-40 closes on loss of E-PP-8AA not PP-7AA. Recommend validating this and replacing RCC-V-40 with RCC-V-21. <I> **** Actions Taken **** CR created <N> **** Equipment Description **** Procedure
402021 | CR | 20191205 |  | 3 | Service Building Heater leaks causing out of spec chemistry | N | N |  | N | YES | <C> Changed at the request of K. Gillard and A. Pierson <D> **** Detailed Description **** The out of spec. corrosion inhibitor for the service building heater (SHHW) is being caused by the multiple leaks on the Heater system. HCO-V-S69 ~86 Liters a day leak, HCO-V-S5D / HCO-ST-S5 Blowdown valve leak by ~10 liters / day, and Piping above HHW-V-57 has a slow leak ~2 liters / day are draining the system at roughly 25 gallons a day. A full chemical addition for corrosion inhibitor will be put down the drain in about 2 weeks. We are just putting chemicals down the sewer system. The SBH needs to run all winter long, so these leaks need to be fixed as soon so corrosion inhibitor can be added and prevent more degradation (or failure). Normally chemistry does one full add at startup of the system and it sustains through the entire winter. Chemistry has done two chemical additions since 11/1/19 and with a third one now required. See cross EDMS doc for pdf of leak pictures and information <I> **** Actions Taken **** Notified CRS, Chemistry Supervision, Chemistry System specialist. <N> **** Equipment Description **** GSB basement Service building heater HHW-V-57 is actually downstream from the leak. The leak is up at the where the valve pipe connects to larger piping. | 02-00-HCO-V-S5D,02-00-HCO-V-S69,02-00-HHW-V-57
402022 | CR | 20191205 |  | 4 | HCO-V-S5D / HCO-ST-S5 Blowdown valve leak by ~10 liters/day | N | N |  | N | YES | <D> **** Detailed Description **** The Service building heater HCO-V-S5D / HCO-ST-S5 Blowdown valve leak by ~10 liters / day. It has been documented as leaking since 1/10/18.AR# 375653 HCO-V-S5D leaks by seat has been closed, WR#29140637 was originated on 01/10/2018 and Completed, and WO#02123118 was closed on 7/22/19 for this valve leak by. HCO-V-S5D is still leaking with a hose on it to a drain the hose has become a permanent fixture. <I> **** Actions Taken **** Notified CRS, Chemistry Supervision, Chemistry system specialist. <N> **** Equipment Description **** GSB basement Service building heater | 02-00-HCO-V-S5D
402023 | CR | 20191205 |  | 3 | Bottled Gas Storage Method |  |  |  | N | NO | <D> **** Detailed Description **** Fire Marshall identified issues with method for securing Bottled gas in B-73 Warehouse gas storage area. This issue was previously idntified and documented under CR 386265. Work Request 29145796 was created as a result of CR 386265. The work request is currently in working status. <I> **** Actions Taken **** Facilities and Warehouse Personnel have taken interim actions to ensure safe storage. Additional chains and clips were applied where possible. All chains werre verified as tight. Spoke to facilities Manager and immediate actions have been taken. Bottles are stored safely in the interim until permanent actions are established. See Photo for reference.
402025 | CR | 20191205 |  | 3 | Work delayed due to verbal commitment from RP not met. |  |  |  | N | NO | <D> **** Detailed Description **** At the SSAC Meeting held on 11/12/19, the dose estimate for WO 02126633, â€˜EC 17755 - MODIFY ZONE 20 FIRE DETECTIONâ€™, was challenged. During that meeting it was noted that a box of septa were stored on the floor of RW 437â€™ very near a scaffold location. The box of septa is located inside of a High Rad Area, with the source being the box of septa. RP personnel committed to having the high dose box of septa relocated so that scaffold crew would not be subjected to the elevated dose rates. Efforts had been made to get the box relocated, but it had not been accomplished before the scheduled scaffold install. Both HP and Laborer resources are required. No documented action came out of the SSAC meeting and no Work Request nor Work Order task were created to facilitate getting the high dose box relocated. <I> **** Actions Taken **** Documented this CR, informed RP Supervision and we are currently working to resolve the issue. Close to trend.
402026 | CR | 20191205 |  | 3 | BS-V-56 (Trap Station #25) cycling every 4-5min | N | N |  | N | YES | <D> **** Detailed Description **** BS-V-56, the bypass valve for trap station #25 (from HP turb 4th stage extraction to MSR 1B 1st stage reheat), is cycling open every 4-5 minutes. This is not a normal condition at 100% power and indicates a failure of BS-LS-56. Recommend a temp mod evaluation to maintain BS-V-56 closed and permanent repair via replacement of BS-LS-56 in R25. <I> **** Actions Taken **** Notified Ops. <N> **** Equipment Description **** T -485- - -E1/7.3 - | 02-00-BS-LS-56,02-00-BS-V-56
402027 | CR | 20191205 |  | 3 | System Engineering SharePoint Migration |  |  |  | N | NO | <D> **** Detailed Description **** On 1/14/20, the System Engineering S:\ Drive will become read only. There are several procedures that point to specific locations in the Systems Engineering S:\ Drive. Those procedures will need to be reviewed and updated as required. <I> **** Actions Taken **** Discussed with Systems Supervisors.
402028 | CR | 20191205 |  | 3 | Request Engineering evaluate procedure steps |  |  |  | N | NO | <D> **** Detailed Description **** OSP-ELEC-M701 has steps for the STA to establish a real time plot for DG-1 voltage and frequency and SM-7 voltage. This real time data is not asked for again in the procedure nor attached to the procedure for further review. The historical data can be retrieved using eDna trend at any time for trending purposes and no immediate operability decisions are made using the plot. It appears this administrative burden of establishing unused plots should be removed from the surveillance. Evaluate OSP-ELEC-M702 and OSP-ELEC-M703 as well. <N> This is a procedure enhancement. Operability determinations are not impacted by this. The surveillance can be successfully completed without these real time plots.
402029 | CR | 20191205 |  | 3 | SOP-COMPUTER-OPS / OSP-ELEC-M701 | N | N |  | N | NO | <D> **** Detailed Description **** The instructions for establishing real time plots in SOP -COMPUTER-OPS no longer work. When establishing the plot required for OSP-ELEC-M701 the program could not access the data for the required points. Additionally OSP-ELEC-M701 step 3.11 requires establishing a plot for three points but the real time plot surveillance file only is set up for two of the points. <I> **** Actions Taken **** initiated CR
402031 | CR | 20191205 |  | 3 | MS-V-137A cycling every ~65 minutes | N | N |  | N | YES | <D> **** Detailed Description **** This is the cause of previous CR 401922 elevated temperatures downstream of BS RVs supplying SS EVAPs. MS-V-137A, the bypass valve for trap station #14 (MS supply to SS-EV-1A). The cycling of MS-RV-137A began on 11/23/19 at 0700. Degradation of MS-LS-137A is likely caused by the nearby MS-V-183A S4 pipe cap leak (WR 29151710). Recommend a temp mod evaluation to maintain MS-V-137A closed and permanent repair via replacement of MS-LS-137A in R25. <I> **** Actions Taken **** Notified Ops. Notified Supervisor and AOV program owner. <N> **** Equipment Description **** T -477- - -E8/5.1 - | 02-00-MS-LS-137A,02-00-MS-V-137A
402032 | CR | 20191205 |  | 3 | CMS-RIT-12A IMDS Update |  |  |  | N | YES | <D> **** Detailed Description **** The Particulate Detector for CMS-SR-20 was replaced per WO 0210958. CMS-RIT-12A IMDS needs to be updated to reflect new values from the calibration sheet provided by the vendor. This work was completed on in november, but no CR was written at that time to update the IMDS. Reccomend evaluation to determine if step is necessary to write CRs to ensure IMDS updates occur. Reccomend adding this work to the IMDS update currntly happening (AR 401558) <I> **** Actions Taken **** CR Written <N> Document change only. No impact on operability of the instrument. | 02-00-CMS-RIT-12A,02-00-CMS-SR-20
402033 | CR | 20191205 |  | 4 | Flooding in CWPH Rm B107 and CWPH Floor | N | N |  | N | YES | <D> **** Detailed Description **** During the halogenation 12-5-19 water came up out of the sump drain in room B107 of the CWPH for 12-15 mins. resulting in the room flooding with over 4 inches of water. The water ran underneath the doors out of B107 including door to the main CWPH area and covered an area from the rollup door to the fire pumps and as well as adjacent rooms. This has been documented multiple times with no resolution. <I> **** Actions Taken **** CR Written and Supervisor notified <N> **** Equipment Description **** CWPH vault sump and pump
402035 | CR | 20191205 |  | 3 | LORQ Exam Impacts |  |  |  | N | NO | <D> **** Detailed Description **** LORQ Annual Exams administrated in 2019 and 2018 severely impact crew manning and available resources. Based on historical data, failures on the annual exam should be expected. Amplifying the loss of manning due to exam failures, the Annual Exam cycle is historically scheduled during a high volume vacation period (November â€“ December). Recommend contingency/compensatory actions be developed and implemented prior to the 2020 LORQ Annual Exam cycle, such as maintaining an off-crew qualifications and proficiency for the duration of the exam cycle. <I> **** Actions Taken **** Initiated CR for lessons learned
402036 | CR | 20191205 | CAQ | D | LORQ Annual Operating Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** One licensed operator failed the Annual Operating Exam administered the week of 12/2/19. Remediation will be IAW TDI-02 and TDI-08. <I> **** Actions Taken **** De-certified individual in PQD. Notified Operations and Operations Training Management. Recommend Severity Level 4.
402037 | CR | 20191205 | CAQ | D | LORQ Biennial Requal Written Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** One licensed operator failed the biennial written exam administered on 12/5/19. Remediation will be IAW TDI-02 and TDI-08. <I> **** Actions Taken **** De-certified individual in PQD. Notified Operations and Operations Training Management. Recommend Severity Level 4.
402038 | CR | 20191205 |  | 3 | WO: 02155413-04 TMU-LCV-2A Test Equipment Issues. | N | N |  | N | NO | <D> **** Detailed Description **** During Valve Diagnostic Testing of TMU-LCV-2A, multiple issues with the Votes Infinity test equipment occurred. The votes Infinity software could not perform an automatic drop-test on a double-acting cylinder, however the option appears for single acting cylinder once selected in valve properties. This option should appear for both single and double acting cylinders. This appears to be a software issue. Next issue discovered was with the I/P (current to pressure transducer) not being able to change its mA input. The DAU (Data Acquisition Unit) had the I/P current locked in at a value of -122mA, and could not be changed. This issue has happened on previous valve testing. This is likely an issue with the DAU unit. Additionally access to Test equipment in the clean tool crib is an issue. Only one DAU unit is available, the rest are in the plant, and none could pass the SAM to be taken out. <I> **** Actions Taken **** Supervision notified of issues with Diagnostic Testing which led to significant delays to valve testing.
402039 | CR | 20191205 |  | 3 | ECCS fill verification procedure enhancements |  |  |  | N | NO | <D> **** Detailed Description **** ECCS fill verification surveillance procedures contain conditional steps with teh qualifier "AND is not following a maintenance outage". This statement is not clear enough as to what the intent is. Engineering describes the intent as maintenance outage in which work on the fluid side of the system has occurred. Modify the steps to provide this additional clarity to prevent inappropriate N/A of steps. Affected procedures are OSP-RHR-M101, OSP-RHR-M102, OSP -RHR-M103, OSP-HPCS-M101. <I> **** Actions Taken **** Wrote this CR.
402040 | CR | 20191205 |  | 3 | Software project upgrade documentation found incomplete |  |  |  | N | NO | <D> **** Detailed Description **** During the project kick off meeting, the previous software upgrade AR ITSR was reviewed for lessons learned and the documentation that is required appears to be incomplete. Writing this CR to create actions to correct the deficiency and get in alignment with PPI ENG PJM-6-1 Project Close Out and Lessons Learned. This has been communicated to IS Leadership.
402041 | CR | 20191205 |  | 3 | Hours Missing in Report Sent to Industrial Safety |  |  |  | N | NO | <D> **** Detailed Description **** Since 9/1/19, NCHR hours have not been imported into PeopleSoft Financials Projects module. The hours worked information that is submitted to Industrial Safety for the Industrial Safety PI is pulled from the PeopleSoft Financials Projects module. Consequently, the hours worked data submitted to Industrial Safety since 9/1/19 has been under stated. <I> **** Actions Taken **** I have notified manager, Regulatory and Industrial Safety. I have contacted Human Resources and Finance to determine if something was changed in the interface between PeopleSoft HR and PeopleSoft Financials that would account for the NCHR hours not being imported.
402042 | CR | 20191205 | CAQ | D | failed emergency lighting fixtures in Radwaste building | N | N |  | N | YES | <D> **** Detailed Description **** During the performance of quarterly inspection of Emergency egress lighting per WO# 02131849-01, five fixtures were found with LED status faults. Fire System Impairment Permit #19-0302 was posted at the respective locations with a portable lantern. A Work Request will be generated to troubleshoot and repair. The following fixtures are needing troubleshoot/repair, W487/10, W525/4, W487/3, W467/13 and W467/8. The EBU locations can be verified by using attachment 9.18 of 10.25.175 (pg.35) <I> **** Actions Taken **** posted FSIP staged lanterns and generate WR <N> **** Equipment Description **** E-BU-W467/8 various locations in RW building.
402043 | CR | 20191205 | CAQ | C | RHR-fill verification venting times | Y | Y |  | N | NO | <D> **** Detailed Description **** RHR-fill verification venting times. While performing OSP -RHR-M101 there several points during the venting of the system that the vent times(air before steady stream of water) were noted. This is mainly due to the fact that they are performed in contaminated areas with the stop watch in a plastic bag and difficult to operate at best AND more to the point there are runs of pipe and in one case 50' of red hose prior to seeing a solid stream that significantly adds to the time. Need to evaluate or account for the pipe lengths and hose length for timimg purposes.The time for 522' rx from RHR-V-923 was 4.5 sec.,time for 501' rx tip mezzanine for RHR-V-922 was 1.5 seconds. <I> **** Actions Taken **** Contacted SM and initiated this CR
402045 | CR | 20191205 | CAQ | C | OPEN MOC Switch Contact Indicates Closed with DMM | Y | Y |  | N | YES | <D> **** Detailed Description **** During performance of WOT 0210776101, E-CB-DG1/7, DETAILED INPECTION OF MOC SWITCH, normally open contact S13-S13T indicated closed with a digital multimeter. It was visually verified to be open. Craft contacted Engineering, who determined this was an expected condition for the equipment configuration. This work has been done previously during a DG1 outage with the diesel and associated circuitry tagged out. <I> **** Actions Taken **** Craft contacted OCC and Engineering for resolution. | 02-00-E-POS-52S/DG1/7
402046 | CR | 20191206 |  | 4 | Received 4.840.A1 drop 7-4 RFW PUMP A/B SEAL TANK LEVEL HIGH | N | N |  | N | YES | <D> **** Detailed Description **** Received 4.840.A1 drop 7-4 RFW PUMP A/B SEAL TANK LEVEL HIGH. Equipment operator repots that MD-LIC-1 is mid scale with an 8 psi output. Dispatched OPS 3 to investigate locally. Suspect this is related to WO 02145574 | 02-00-MD-LS-6
402052 | CR | 20191206 | CAQ | D | Accumulator Trouble alarm CRD-HCU-5019 due to low pressure | Y | N |  | N | YES | <D> **** Detailed Description **** Accumulator Trouble alarm CRD-HCU-5019 due to low pressure. OPS2 cleared the alarm per SOP-CRD-HCU. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-HCU-5019
402053 | CR | 20191206 | CAQ | D | MULTIPLE OFFGAS POST TREATMENT ALARMS | N | Y |  | N | YES | <D> **** Detailed Description **** Recieved intermittent P602.A5.1-3 "OFF GAS POST-TREATMENT RADIATION HIGH-HIGH-HIGH" P602.A5.3-2 "OFF GAS POST -TREATMENT RADIATION HIGH-HIGH" and P602.A5.6-3 "OFF GAS POST-TREATMENT RADIATION MONITORS DOWNSCALE" alarms. OG -RIS-601B display appears to be scrolling through displays as if the select button is stuck engaged. The OPER light is extinguished. No offgas isolations have occured. <I> **** Actions Taken **** Attempted to manuever through the displays per the ARP's with no percievable response on OG-RIS-601B display. | 02-00-OG-RIS-601B
402054 | CR | 20191206 | CAQ | D | E-RLY-83/TRB found in the down(Emergency closed) position | Y | N |  | N | YES | <D> **** Detailed Description **** While responding to a fire alarm (4.FCP.2 Drop 6-1 SYS 60 deluge backup xfmr TR-B trouble) from the main control room, it was discovered that E-RLY-83/TRB was found in the down(Emergency closed) position. The normal position for this relay is in the UP position (Normal Closed). The outside temperature was 32 degrees F and the cooling fans were not running at the time. Locally at the transformer (E-TR-B), the 83E Emergency Power alarm lamp was not illuminated. The 83E Emergency Power alarm lamp has been written up for not illuminating durring testing under WO 02062447-01 and AR 388101 WR 29146254 were submitted previously. <I> **** Actions Taken **** Informed CRS and wrote CR | 02-00-E-RLY-83/TRB
402055 | CR | 20191206 |  | 4 | E-BU-TMU-375/2 | N | N |  | N | YES | <D> **** Detailed Description **** W/O # 02146655-01, while performing ppm 10.25.156 E-BU -TMU-375/2 was found after its discharge with a battery voltage less than required. Returned unit to its as found condition. <I> **** Actions Taken **** notified supervision, documented with a CR and WR <N> **** Equipment Description **** EBU located at the TMU
402056 | CR | 20191206 | CAQ | D | OG-RR-601 Channel B indicating pegged Hi. | N | Y |  | N | YES | <C> Duplicate of 402053 <D> **** Detailed Description **** OG-RR-601 Channel B indicating pegged Hi. OG-RR-601 channel B is reading 9.9E01. This is driving the OG Post Treat Hi-Hi alarm to be in on H13.P602-A5.3-2. Neither the OG Post Treat Hi nor Hi-Hi-Hi alarms are in. Those alarms are driven from OG-RIS-601B and not OG-RR-601. This occurred following inspections of WR 29153050. <I> **** Actions Taken **** Notified CRS. Initiated CR and WR <N> **** Equipment Description **** MCR | 02-00-OG-RR-601
402057 | CR | 20191206 |  | 3 | PPM 15.2.23 Thermal Detection CFT |  |  |  | N | NO | <D> **** Detailed Description **** While perform PPM 15.2.23 under WO #02105561-01, procedure did not identify all the drops on FCP-2 in the control room when craft performed lamp test at FSP-2 on step 7.1.4. Craft had identify 3 of the 4 zones associated with FSP-2 zones 57,58 and 59 but failed to identify zone 60. So when the craft performed the lamp test, a trouble indication was received on all 4 zones. <I> **** Actions Taken **** Craft stop work, notified Control Rooom and Supervision, CR was iniated for procedure enhancement to identify the zones that will be effected during the lamp test of a FSP to FCP-2. <N> **** Equipment Description **** All FSP's associated with PPM 15.2.23
402058 | CR | 20191206 | CAQ | C | Lose Connections Found on OG-RIS-601B | N | Y |  | N | YES | <D> **** Detailed Description **** During investigation of OG-RIS-601B as part of WR 29153050, multiple lose connections were found in both front and the back panels, needing up to a full turn. P4 connector was found bent on back of RM-2300 (see pictures in EDMS). <I> **** Actions Taken **** Notified CRS Wrote CR | 02-00-OG-RIS-601B
402059 | CR | 20191206 |  | 3 | Minimize Free Releasing Material from RCA |  |  |  | N | NO | <D> **** Detailed Description **** The Big Box (Clean Box) is free released from the RCA 50+ times a year to be transported over to the PSF for Instrument Calibrations that are inside the Box. The box is used for the transport of Free Released M&TE. Suggestion would be to store the Big Box (Clean Box) outside the RCA and when freshly calibrated M&TE returns to the plant from the PSF there should be transport carts inside the RCA that are used to transport the material back to the Tool Crib so that the Big Box (Clean Box) never enters the RCA which means it would never need to be surveyed for free release in the future. There have been several instances where HP Technicians have found Radioactive Specks on the wheels of the Big Box (Clean Box) while surveying for release from the RCA . Doing it this way would ELIMINATE the risk associated with Free Releasing this Cart so Frequently. (Weekly) -See EDMS Doc-- <I> **** Actions Taken **** -Initiated CR -Notified Supervision via e-mail.
402060 | CR | 20191206 | CAQ | D | IDS 20 needs ice removal | N | Y |  | N | YES | <D> **** Detailed Description **** IDS 20 stuck in constant alarm due to ice. Need assistance. call security for details. <I> **** Actions Taken **** recieved constant alarm, performed walk up, notified supervision, CR/WR generated <N> **** Equipment Description **** south/west of the protected area | 02-00-SEC-IDS-E/S/20/21
402061 | CR | 20191207 |  | 4 | E-CB-N2/6 red closed light out on cubicle on SH-6. | N | N |  | N | YES | <D> **** Detailed Description **** E-CB-N2/6 red closed light out on cubicle on SH-6. Checked bulb and it is good. E-CB-N2/6 red light on H13-P800 in Main Control Room is on. Nut and bolt used to short terminals together on socket is missing. See photo. | 02-00-E-CB-N2/6
402064 | CR | 20191207 | CAQ | D | Check connections on OG-RIS-601A |  |  |  | N | YES | <D> **** Detailed Description **** See CR# 402053 and WR# 29153050, with what was found on the investigation of OG-RIS-601B the Shift Manager has requested to complete an extent of condition check on OG -RIS-601A. <I> **** Actions Taken **** Informed Shift Manager and initiated CR/WR There is no new equipment issue identified in this CR. | 02-00-OG-RIS-601A
402065 | CR | 20191207 |  | 3 | PC 10D3V12 can't be used with acrobat files |  |  |  | N | NO | <D> **** Detailed Description **** this PC in CORC area locks out any attempt to open an Adobe file. See EDMS for error screen reached during opening of Email attachment. Prints and procedures net the same result.
402066 | CR | 20191207 |  | 3 | OSP-CCH/IST-M701 procedure clarification needed |  |  |  | N | YES | <D> **** Detailed Description **** During the task preview of OSP-CCH/IST-M701 it was unclear when step 7.1.13 would be performed. There is no PMID that allows tracking for the annual step and looking through 2019 OSPâ€™s it was not performed during any OSP-CCH/IST -M701. Also, the PMID 721-10 for vibration readings WO 02119304-01 stated in the MASTER 5 to take vibration readings on the â€œchiller and motor (chilled water pump and motor)â€. Step 7.1.56 has an every 2 years for 3 bulleted items â€“ Vibrations on the CCH-P-1A motor and pump bearings; vibrations on the chiller; voltage and current readings on heaters #1 and #2. â€“ There is no specific task in WO 02119304 to take vibrations on the actual chiller. Also, the heater checks are stated to be every 2 years, in step 3.4 it states it is a 3 year PMID. <I> **** Actions Taken **** Coordinated with the electricians to perform voltage and current checks on heater element #3 for step 7.1.13. (4.16 amps; 121 Volts AC). Verified the Chiller and CCH-P-1A pump and motor vibrations were taken during chiller run. | 02-00-CCH-CR-1A,02-00-CCH-H-CR1A/1
402067 | CR | 20191207 | CAQ | D | Roof Leak HPCS Diesel | Y | N |  | N | YES | <D> **** Detailed Description **** Roof Leak in the HPCS Diesel. Rain water seeping through roof hatch seal and creating a puddle on the HPCS Room Floor. <I> **** Actions Taken **** Laborers Notified Supervision Notified CR/WR Generated <N> **** Equipment Description **** HPCS Diesel Roof Hatch Leak
402068 | CR | 20191207 | CAQ | D | Received P851.S.1 Rad board 24 trouble TEA-FN-93 noisy | N | Y |  | N | YES | <D> **** Detailed Description **** Rad board 24 trouble was caused by TEA-RIS-13 OPER lights extinguished. Cause was displayed as TRBL 1/TEMP RANGE. HT-HTP-PTM/28 had no indication of low temperature. TEA -FN-93 sounded abnormally loud per shift chemistry tech. After approximately 25 minutes the OPER light illuminated concurrently with TRBL 1/TEMP RANGE extinguishing. TEA -TIC-SR26 loop 1 was at set point of 145 F. <I> **** Actions Taken **** Informed CRS and followed ARP. | 02-00-TEA-FN-93
402069 | CR | 20191207 |  | 4 | RW 467' Water leak found to be contaminated. | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** During the week RW 467' Weekly survey, water was discovered on the floor in front of the A RWCU Hold up Pump Room on the floor near the stepoff pad. The rag used to clean up the floor was 2000-3000cpm/PA. The floor was deconned and a bucket placed under the drip that appears to be coming from a 1" pipe that is penetrating through the ceiling. Posted the area in front of the A Holdup pump room CA. <I> **** Actions Taken **** Deconned the floor, placed the bucket under the drip, posted the area in front of the A Holdup pump room CA, notified OPs, initiated this CR. Adde3d posting change to RP Turnover.
402070 | CR | 20191207 | CAQ | D | Accumulator trouble alarm CRD-HCU-1411 due to high water | Y | N |  | N | YES | <D> **** Detailed Description **** Accumulator trouble alarm CRD-HCU-1411 due to high water level. OPS2 cleared the alarm per SOP-CRD-HCU. <I> **** Actions Taken **** Informed CRS/ SM, wrote this CR and WR. | 02-00-CRD-HCU-1411
402071 | CR | 20191208 |  | 3 | 15.1.2 needs procedural fix |  |  |  | N | NO | <D> **** Detailed Description **** fire door operability surveillance 15.1.2 procedural steps 6.1 refers to attachment 8.1 and 8.2. those attachments dont exist. current attachments are 9.1 and 9.2 <I> **** Actions Taken **** cr initiated. <N> **** Equipment Description **** all tier 1 doc stations.
402074 | CR | 20191208 |  | 4 | E-TR-N1 power transfer test | N | N |  | N | YES | <D> **** Detailed Description **** during performance of WO# 01172150 the power transfer alarm failed to come in locally and the MCR did not receive a trouble alarm. after the transfer switch was depressed, an audible thunk was heard exactly the same as on the previous test on TR-N2, and another when releasing the button per the procedure. <I> **** Actions Taken **** informed MCR initiated CR/WR | 02-00-E-TR-N1
402075 | CR | 20191208 | CAQ | D | Water dripping from RWCU-DM-1A area to RW 467' |  |  |  | N | YES | <C> CR reopened to cross reference additional WP 02155730 marked completion required box, then taken back to complete <D> **** Detailed Description **** Water is dripping from the RW 487' RWCU-DM-1A room to the RW 467 RWCU pump room area. Rate of water dropping is about 1 drip every 20 seconds. Currently dripping from two different penetrations. A Â½ inch pipe penetration CVI 317 -00,2305; and a 2 inch pipe penetration CVI 317-00,2306. Pictures attached <I> **** Actions Taken **** HP placed buckets to contain the water dripping from the pipes and roped off the area. Removed RWCU-DM-1A from service and Isolated the Demin. Added issue to PCL, held management phone call to discuss issue, completed OI-34. | 02-00-RWCU-DM-1A
402077 | CR | 20191208 |  | 3 | ODMI for RWCU flowrate should be revised |  |  |  | N | NO | <D> **** Detailed Description **** On 12/8/2019, RWCU-DEMIN-1A was removed from service due to suspected leakage. The procedure, SOP-RWCU-DEMIN, step 5.1.1 requires entering a substitute value of 0.0800 mlbm/hr for demin flowrate when a demin is removed from service. However, the existing ODMI associated with AR 391959 for RWCU system flowrate exceeding HX design capacity is silent on whether this value should be used. Prior to isolation of the demin today, both RWCU flowrates had a consdervative substitute value of 0.09 mlbm/hr based on an email chain (see EDMS for email chain). Due to procedural compliance and lacking guidance, RWCU demin A flow was substituted with the procedurally directed less conservative value. Request guidance be incorporated into the ODMI on whether step 5.1.1 should be followed or the more conservative value left in sustitution for the core thermal power calculation. <I> **** Actions Taken **** Discussed with CRS and SM. Substituted 0.08 mlbm/hr value as directed by procedure.
402078 | CR | 20191208 |  | 3 | (NRC Question) RSD and ARSD Panel Switch Blue Dots |  |  |  | N | NO | <D> **** Detailed Description **** The NRC resident inspector observed that at the RSD and ARSD panel there are valve and pump control switches with blue dots and some that do not (blue dots are small blue stickers). Per ABN-CR-EVAC the colored dots on the control switches indicate the normal position for a control room evacuation and that switch alignment verifications can be made via the colored dots or by the procedure alignments within the procedure. A walkdown identified that the following RSD panel control switches do not have colored dots. RCIC-V-13, RCIC-V-46, RCIC-V-45, RCIC-P-2, RCIC-P-4, RHR-V-4B, RHR-V-68B, SW-V -70B, and SW-P-1B. A walkdown of the ARSD panel identified that the control switches for SW-P-1A and WMA-FN-53A do not have colored dots but that a penciled in dot on the control switches had been made. Request an assessment of whether the referenced switches should have blue dots and if so then blue dots be added. If there is a basis behind why the switches do not have blue dots then recommend a revision to ABN-CR-EVAC to provide clarification as to why some switches do not need blue dots. Alternatively all of the blue dots could be removed from all of the switches as the switch alignments are provided by the procedure. <I> Informed licensing to provide a response to the NRC resident inspector.
402079 | CR | 20191208 |  | 4 | CAS-C-1B pressure trending low | N | N |  | N | YES | <D> **** Detailed Description **** The unloader for CAS compressor 1B may be set to low. CAS header pressure has been trending lower than normal (104 -105 psig vs ~110 psig) on CAS-PI-1, when only on CAS-C-1B. Additionally, the standby air compressor auto started 3 times in the last day due to backwashes of demineralizers with B as the main compressor . A standby compressor auto-start while backwashing a demineralizer is an expected, but infrequent, occurance. <I> **** Actions Taken **** Followed ARP 4.840.a5 8-6 | 02-00-CAS-C-1B
402080 | CR | 20191209 |  | 4 | RX Bldg NE Elevator Chain/Cable Noise on Descent | N | N |  | N | YES | <D> **** Detailed Description **** RX BLDG NE ELEVATOR - PERIODIC LOUD BANGING NOISE FROM CABLE AND/OR CHAIN HITTING THE SIDE/BOTTOM OF THE ELEVATOR APPROXIMATELY 10 - 25FT FROM THE 441' ELEVATION ON DESCENT. <I> **** Actions Taken **** REMOVED RX BLDG NE ELEVATOR FROM SERVICE. INFORMED SUPERVISION. <N> **** Equipment Description **** RX BLDG NE ELEVATOR - 441' ELEVATION | 02-00-MT-ELEV-1
402081 | CR | 20191209 |  | 4 | STANDING WATER IN CW PH | N | N |  | N | NO | <D> **** Detailed Description **** STANDING WATER ON THE FLOOR IN THE CW PUMPHOUSE NEAR FP-P -2A/2B. APPEARS TO BE COMING FROM THE ROLL-UP DOOR. FLOOR DRAIN DOES NOT APPEAR TO BE DRAINING. <I> **** Actions Taken **** INFORMED SUPERVISION. <N> **** Equipment Description **** CW PUMPHOUSE
402085 | CR | 20191209 | CAQ | D | TEA Temp Sample Cart Degrading Flow | N | Y |  | N | YES | <D> **** Detailed Description **** TEA Temporary Sample cart is losing its ability to maintain flow in the recommended flow rate range. <I> **** Actions Taken **** Informed the CRS, wrote a CR. <N> **** Equipment Description **** TB 525 TEA Temporary Sample Cart
402087 | CR | 20191209 |  | 3 | Recommend Enhancement to EC 17439 and 17469 RRC Pump Motors |  |  |  | N | NO | <D> **** Detailed Description **** THIS IS NOT AN EQUIPMENT ISSUE. Recommend Enhancement to EC 17439 and 17469 RRC Pump Motor External Oil Reservoirs. The configuration of the new external oil reservoirs (lubricators) installed on RRC-P-1B motor in R24 outage is less than ideal in that it inadvertently increases maintenance exposure to radiological safety and industrial safety risks. The lubricator inhibits the ability to add oil to the motor bearing reservoir via the normal fill port, resulting in needing to add oil through the new lubricator. This method is time consuming and requires multiple trips in/out of the drywell to accomplish, resulting in additional dose, where in the past it was relatively quick with only one drywell entry needed. This configuration also applies to RRC-P-1A motor which will be installed in R25 outage. This CR is being submitted after discussions with design and maintenance staff on this matter. <I> **** Actions Taken **** Informed Design Engineering and Maintenance of CR submission to help drive resolution. Forwarded information to Rad Planning and Industrial Safety for awareness. <N> As per discussion with the system engineer, RE, RX Maintenance, and Maintenance, this AR is re-assigned to the system engineer to incorporate the concerns identified in this AR-CR into the technical evaluation that is being prepared for AR EVAL 401976.
402088 | CR | 20191209 |  | 3 | Simulator funding not included for GE NUMAC replacements |  |  |  | N | NO | <D> **** Detailed Description **** Two GE NUMAC devices located in the main control room have been replaced. These changes effect physical fidelity of the simulator and result in a noticeable difference between the plant and simulator. 10 CFR 55.46 and ANS-3.5 -2009 require the simulator to match the plant including in physical appearance. The look and feel of the simulated devices is required by regulation to match the plant. Simulator changes and funding for the simulator were not considered during the planning process for these replacements. See full detailed description and photos in EDMS doc. This CR is to request funding from the organization that installed the upgraded NUMACs to make the needed simulator changes. Do NOT assign this CR to anyone in training or the simulator group. See full description in EDMS doc for recommendations on who to assign the CR to.
402090 | CR | 20191209 |  | 3 | 15.3.15 needs revised |  |  |  | N | NO | <D> **** Detailed Description **** While performing 15.3.15 (Fire protection sprinkler system internal inspection) it was found that section 7.1 does not have proper instructions to inspect and restore dry pipe systems. There should be a seperate section and attachment for the dry pipe systems with specific steps to isolate and restore dry pipe systems specifically. A second option may be to remove dry pipe systems all together and revise 15.1.23 sections 7.3 and 7.4 to include the internal inspecton since it is performed every year and the faceplate needs to be removed to reset. Contact origiator or Fire protection engineering department.
402092 | CR | 20191209 | CAQ | D | IDS 20&21 Malfuntion | N | N |  | N | YES | <D> **** Detailed Description **** IDS 20 & 21 Malfunction. <I> **** Actions Taken **** Compensatory measure posted. A walk down of the zone initially provide an evironmental cause( heavy rain), but as the rain subsided, it continued to give malfunction alarms. | 02-00-SEC-IDS-E/S/20/21
402093 | CR | 20191209 |  | 3 | PPM 10.25.141C REQUIRES REVISION. |  |  |  | N | NO | <D> **** Detailed Description **** WHILE REVIEWING PPM 10.25.141C IT WAS NOTED THAT THERE WERE SEVERAL REFERENCES TO ISPM-7 IN THE REFERENCE SECTION AS WELL AS THE PRECAUTIONS AND LIMITATIONS SECTION. ISPM-7 WAS SUPERCEDED IN MARCH OF 2018. . IN PPM 10.25.141C, IN THE REFERENCES, REMOVE REFERENCE 2.8. . IN THE PRECAUTIONS AND LIMITATIONS SECTION REFERENCE 4.12, CHANGE ISPM-7 TO ISPM-20. ON REFERENCE 4.13, CHANGE ISPM-7 TO ISPM-20. <I> **** Actions Taken **** DISCUSSED THIS ISSUE WITH SUPERVISION AND INITIATED THIS CR.
402094 | CR | 20191209 |  | 3 | PDIS-MON-STA/B failed | N | N |  | N | YES | <D> **** Detailed Description **** PDIS-MON-STA/B, one of 2 monitors for STA level 3 workstation, failed. Monitor shows black screen but is powered on. It shows the desktop briefly when powered off then on, but then goes back to a black screen. PDIS-MON-STA/A is functioning normally as is the workstation itself (PDIS-COMP-STA). Need to replace monitor with spare, Computer Engineering will provide. . Recommend assign to Computer Engineering to document SWP -CSW-24 compliance testing. <I> **** Actions Taken **** Investigated after notification from SM. Generated CR and WR to replace with spare monitor. | 02-00-PDIS-MON-STA/B
402096 | CR | 20191209 |  | 3 | Piping on RCC-P-1B in poor condition | N | N |  | N | YES | <D> **** Detailed Description **** While replacing RCC-P-1B per work order 02031003-01 It was noted that the vent and drain piping appears to be at minimum wall thickness. This is the threated end of the piping upstream of RCC-V-141 and RCC-V-147. It appears to be only the threaded ends that connect to the pump that need replaced. <I> **** Actions Taken **** Contacted supervisor | 02-00-RCC-P-1B
402099 | CR | 20191209 |  | 3 | PMID 17156 and 17075 is missing the PM for January and Febru |  |  |  | N | NO | <D> **** Detailed Description **** During T-7 review it was noticed ISP-ARM-M402 and ISP -CMS/PRM-M402 were not on the schedule. Look at the individual PMID and both were missing work orders for January and February. Work orders are there for Nov, Dec, then start again for March thru June <I> **** Actions Taken **** Contacted PM coordinator Wrote CR
402100 | CR | 20191209 |  | 4 | TMU-AO-2A- Loose connection between piston and stem. | N | N |  | N | YES | <D> **** Detailed Description **** While performing overhaul on the subject air operator the following discrepancies were noted. The piston/actuator stem connection was loose which caused the piston to become misaligned in the cylinder which then caused piston and cylinder scoring to occur. The lower stem bushing O-ring was dry and cracked, the set screw that retains the vertical position of the valve stem clevis was broken allowing the valve stem clevis to slide down the valve stem approximately Â¼â€. This in-turn caused the actuator stem to become misaligned causing binding to the air actuator. The actuator was rebuilt to include new elastomers and a new piston. There was no cylinder on site at the time, so the existing cylinder was polished and reused. The set screw was replaced on the valve stem clevis and proper alignment to the actuator was re-established. A new cylinder (CID 13194) is now available on site and should be replaced at the next possible convenience. <I> **** Actions Taken **** OCC and AOV Program Manager notified. <N> **** Equipment Description **** A -408- | 02-00-TMU-AO-2A
402101 | CR | 20191209 |  | 4 | Undeclared Prohibited Item |  |  |  | N | NO | <D> **** Detailed Description **** Contractor for a commercial tenant brought a prohibited item to the Security Checkpoint. Prior to arrival, contractor was informed of the prohibited items and consequences of bringing such items. <I> **** Actions Taken **** Security denied access. Notified points-of-contact for contractor and commercial tenant.
402103 | CR | 20191209 |  | 4 | Incorrect Configuration Found, Violating ISPM 6, 3.7.4.b | N | N |  | N | NO | <D> **** Detailed Description **** Conference Computer change-out required. While doing work to change out the conference computer in Kootenai/207 it was found that the old computer was plugged directly into the wall instead of a UL Listed Surge Protector or UL Listed Relocatable Power Tap per ISPM 6, 3.7.4.b: "Computerized electrical equipment should only be plugged directly into surge protectors or relocatable power taps." <I> **** Actions Taken **** Worked with a user in that department to locate a UL Listed Surge Protector I could use for the deployment and conducted the deployment and plugged the PC into the Surge Protector.
402105 | CR | 20191209 |  | 3 | Backup Exec software version reached End-of-Support |  |  |  | N | YES | <D> **** Detailed Description **** Backup Exec 15 reached End of Support Life from the vendor in Nov. 2019. This is software used for automatic backups for Windows computers on the Level 3 and 4 plant networks. End of Support Life means that the vendor will not provide any technical support for this version regardless of whether or not there is a valid support contract. This support refusal situation has already been encountered. Current contract covers 11/2019 - 11/2020. This software should be upgraded to the latest supported version to maintain vendor technical support. . There is no change in production device functionality due to End-of-Support status. This does not impact Operations. This is not a reportable condition. . Recommend to Computer Engineering. <I> **** Actions Taken **** Generated CR | 02-00-NET3-SOFT-BKUPEX/APPDB,02-00-NET3-SOFT-BKUPEX/SVR,02-00-NET3-SOFT-BKUPEX/WIN,02-00-NET4-SOFT-BKUPEX/APPDB,02-00-NET4-SOFT-BKUPEX/SVR,02-00-NET4-SOFT-BKUPEX/WIN
402106 | CR | 20191209 |  | 3 | SOP-ELEC-115KV-OPS has nomenclature error. |  |  |  | N | NO | <D> **** Detailed Description **** The first note on page 12 of SOP-ELEC-115KV-OPS lists E-DISC-7AA3B as the Normal 480V supply and E-DISC-8AA-3F as the Alternate 480V supply. Per Portal J, EWD-46E-280, CVI DWG 41-00,91 and plant labelling E-DISC-7AA3B is the Alternate and E-DISC-8AA3F is the Normal supply. Please verify and correct this note. Also, the first bullet in the note has the hyphen in the wrong place for the drawing number, calling it EWD-46E2-80 instead of EWD-46E-280. <I> **** Actions Taken **** Informed supervisor and wrote this AR/PCR.
402108 | CR | 20191209 |  | 3 | Backup Exec BDR not functional on ACUMEN Win10 workstations |  |  |  | N | YES | <D> **** Detailed Description **** During development of Backup and Disaster Recovery Instructions (BDRI) for EC 17398 (ACUMEN), it was discovered that the creation of the recover disk was not capable of loading the network driver necessary for the Dell Optiplex 7060 machines. This disk is necessary for performing full bare-metal restoration of these workstations. Restoration from backup to a machine that still boots into Windows is functional. This prevents completion of the BDR forms for the four Windows 10 machines installed for the ACUMEN project. WO 02140090-20 is also impacted because the BDRs can't be completed as instructed in the WO. . This does not impact Operations This is not a reportable condition. . Recommend to Computer Engineering for resolution. <I> **** Actions Taken **** Generated CR. Discussed with EC 17398 RE. | 02-00-PDIS-COMP-IC,02-00-PDIS-COMP-LAB/3,02-00-PPC-COMP-ACUMEN/WS,02-00-TDAS-COMP-ACUMEN/WS
402110 | CR | 20191209 |  | 3 | PPM12.5.35B needs enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Chemistry has a method to collect ODCM required samples from TEA in the event that the back-up temporary sample cart fails. This involves a WR with instructions for setting up sampling equipment on the Radwaste roof. With the frequency the temporary TEA sample cart has been breaking, it would be helpful to include this backup backup method in PPM 12.5.35B. <I> **** Actions Taken **** Informed Chemistry Specialist. Wrote CR.
402111 | CR | 20191209 | CAQ | D | RCIC-DPS-14, RCIC TURBINE OIL FILTER HIGH DP during OSP | Y | N |  | N | YES | <D> **** Detailed Description **** During performance of OSP-RCIC/IST-Q701 4.601.A4 drop 6-6 RCIC TURBINE OIL FILTER D/P HIGH alarm was received. Local indication while running on RCIC-PI-6 was 16 PSIG and RCIC-PI-7 was 14 PSIG. Which is a DP of 2 PSID, lower than the setpoint. Pictures attached. RCIC-V-761 and RCIC-V-762 were verified open per SOP-RCIC-LU. When the RCIC pump was secured, the alarm cleared. Alarm is supposed to come in at ~ 6PSID per the IMDS for RCIC-DPS-14. | 02-00-RCIC-DPS-14
402112 | CR | 20191209 |  | 3 | VAMP area radiation monitor procedure |  |  |  | N | NO | <D> **** Detailed Description **** It was discovered that procedure HPI-12.16, Operation of the Victoreen Vamp Area Monitor, does not include source check instructions while recently changing Vamp area radiation monitors at the TSC\OSC. Instructions for performing source checks on the Vamp area monitors are only addressed in work instructions. Suggest adding procedural guidance on source checks within the procedure. <I> **** Actions Taken **** Generated CR
402114 | CR | 20191209 |  | 3 | Ice Melt probable cause of Argos contamination alarms |  |  |  | N | NO | <D> **** Detailed Description **** Personnel reporting for work ont he evening of 12/9/2019 were unable to enter the MCR due to Argos alarms indicating contamination on the bottom of their shoes. Additionally personnel exiting the PAAP at the end of dayshift were unable to leave site due to setting off the GEM5 alarms. This required HP support to decontaminate 6 personnel to permit watch relief in the MCR, as well as send resources to the PAAP to allow personnel to go home. It was raining at the time these personnel transited from the parking area to the MCR and from the GSB to the PAAP. It appears that whatever ice-melt product was purchased and applied to the walking surfaces outside is the cause of the alarms and delays in watch relief and personnel leaving site. Request the station evaluate the product being used taking into account the need for personnel to pass through detectors and potential contaminates causing these false alarms. <I> **** Actions Taken **** Discussed with SM and HP.
402115 | CR | 20191209 |  | 4 | SMA-FL-51 - END OF ROLL | N | N |  | N | YES | <D> **** Detailed Description **** GSB 456' SMA-FL-51 - END OF ROLL <I> **** Actions Taken **** INFORMED SUPERVISION <N> **** Equipment Description **** S -456- - -E5/3.0 - | 02-00-SMA-FL-51
402116 | CR | 20191209 |  | 3 | R-DOOR-R612, electrical cord routed under it | N | N |  | N | YES | <D> **** Detailed Description **** R-DOOR-R612 has an electrical cord routed under it with no impairment posted. No active impairment could be found. This is a non-essential 3 hr fire door. <I> **** Actions Taken **** Wrote impairment and posted. Placed on hourly fire tour. BIP 19-0518. Cord is routed under door into the RHR-HX-1A room. RHR-HX -1A thermal performance monitoring was performed earlier on day shift. This cord could be supporting test equipment in the room. <N> **** Equipment Description **** R-DOOR-R612 | 02-00-R-DOOR-R612
402123 | CR | 20191210 |  | 4 | DEH AC Alarm Check | N | N |  | N | YES | <D> **** Detailed Description **** The DEH AC Unit on the Turbine Building 501' has two alarms in. "Fail Modes" and "High Control" alarms are currently in. <I> **** Actions Taken **** Supervision Notified CR/WR Generated <N> **** Equipment Description **** CTurbine 501' DEH AC unit
402125 | CR | 20191210 |  | 3 | Electrical connection hazard during RW shipping activity |  |  |  | N | NO | <D> **** Detailed Description **** While connecting a string of lights to a three-way splitter inside of the outdoor radiologically controlled area next to the spray ponds, smoke was observed when the light string was connected to the splitter. The laborer immediately disconnected the light string. Both the three-way splitter and the light string were removed from service. The most likely cause for the issue was water intrusion through a broken light bulb during recent rainy weather. A functional light string and cord were used to replace them. The lights used underneath trailers appear to be indoor-type light strands and should be fully replaced with suitable lighting that is rated for use outdoors. <I> **** Actions Taken **** Removed faulty items from service and briefed the laborers on the potential safety issue.
402126 | CR | 20191210 |  | 4 | MCR CORC capabilities lost |  |  |  | N | NO | <D> **** Detailed Description **** MCR computers were replaced without Adobe Pro. This removes our capability to write Cert Packages for emergent clearances. Recommend restoring Adobe Pro to the MCR. <I> **** Actions Taken **** Shift Manager notified of reduced capabilities. Adobe Pro loaded onto the MCR CRO2 computer. <N> Adobe Pro DC has been installed on CRP3DV2/CRO2 Station. Sign in and tested with two different operators verified functional.
402131 | CR | 20191210 |  | 3 | Procedure Change to ABN-FSG-003 |  |  |  | N | NO | <D> **** Detailed Description **** Revise step 4.2.6 to be before steps 4.2.4 and 4.2.5 so DG-4 is started before loading DG-4 by placing loads on the diesel (section 4.3 requires revision also). ABN-FSG-004 for FLEX-GEN-DG5 needs to be revised in this same manner also (section 4.3 and 4.4). ABN-ELEC-DG4-CROSSTIE/MC-7A and ABN-ELEC-DG4-CROSSTIE/MC-8A were reviewed and the diesel is started before loading it. <I> **** Actions Taken **** Discussed with FLEX program owner (email attached).
402132 | CR | 20191210 |  | 3 | Printers Wasting Paper upon Security scans |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** This morning 14 sheets of paper/jobs were printed with random jumble on it.According to the copier's job log, they have no person as origin nor print job name. These printouts are a waste of company resources (printer paper) since it occurs sitewide.See EDMS for a sample of this jumble print outs. <I> **** Actions Taken **** IS Solutions Center referred me to the Pacific Office Automation representative. This representative informed me that this occurs due to a network cycber security scan. They also told me that he gets called from many other employees about their copiers "going crazy" like this. They have informed CyberSecurity to eliminate these random prints and they responded with "We're on it." I have decided to initiate this CR to eliminate the paper waste.
402133 | CR | 20191210 |  | 4 | Circ Water floor drains plugged | N | N |  | N | YES | <D> **** Detailed Description **** Floor drains in Circ water chemistry sample room are plugged causing water to backup into the building. Winter season will provide more water to drains increasing the likelyhood of more flooding and water intrusion into the electrical room. <I> **** Actions Taken **** Informed SSS, MCR, and Initiated CR. Spoke with FIN Team, but it was not a high enough priority. <N> **** Equipment Description **** Circ Water Pumphouse Bldg. storm drains
402134 | CR | 20191210 | CAQ | C | FP-ID-16/14 Existing wiring does not match electrical print |  |  |  | N | YES | <D> **** Detailed Description **** During FP detector replacement work, per WO# 02126631-01, the wiring at detector FP-ID-16/14 does not appear to match drawing 217-00,84,50. The drawing shows detector 16/14 in between 16/13 and 16/15 (normal configuration) however, detector 16/12 through 16/16 appear to be different, based on existing wire labels and conduit routing. This did not affect circuit and detector function, as previous periodic testing has proven in the past. This appears to be a drawing configuration issue only. <I> **** Actions Taken **** Notified Supervision, wrote CR. Utilizing the generated WR, need to further investigate the Zone 16 circuit to determine the actual wiring configuration of the detectors in this area. Discussed with Engineering; will get as-found wiring detail to them for evaluation. | 02-00-FP-ID-16/14
402135 | CR | 20191210 |  | 3 | Scaffold issues SAT-TK-2 | N | N |  | N | YES | <D> **** Detailed Description **** There were several found on the scaffold surrounding SAT -TK-2. Netting is torn and degraded, scaffold information tag is faded with no legible instructions. <I> **** Actions Taken **** Informed Maintenance and MCR | 02-00-SAT-TK-2
402137 | CR | 20191210 |  | 4 | Labeling discepancies on E-MC-7CB |  |  |  | N | YES | <D> **** Detailed Description **** Some of the labels on E-MC-7CB have not been updated to the current EPN's which are found in Portal J. The discrepancy is due to the change from labeling disconnects starting with "E" to the current labeling in which we label them per system. Recommend relabeling MC-7CB to avoid issues identifying the proper components during work. <I> **** Actions Taken **** Informed CRS <N> **** Equipment Description **** R572 | 02-00-E-MC-7CB
402139 | CR | 20191210 |  | 4 | Flooding In RM B107 - CWPH | N | N |  | N | YES | <D> **** Detailed Description **** While working out at the CWPH 12/9/19, the floor drain in RM B107 was backing up and flowing out the door into the main CWPH area. Floor had standing water from the roll up door to the fire pump area. Heavy rains supplemented with a little water from the cooling tower drift was causing the vault sump to work hard to keep up with the water entering the vault. <I> **** Actions Taken **** Informed Supervision and posted no fishing signs. Reoccurring issue. See AR 402033. <N> **** Equipment Description **** CWPH vault sump and pump
402140 | CR | 20191210 |  | 4 | ERB-W467/9 | N | N |  | N | YES | <D> **** Detailed Description **** W/O # 02131879-01, while performing ppm 10.25.64 fixture ERB-W467/9 did not have at least one light lit after the circuit was opened. LP-6BA-19 is the lighting circuit, scaffold will be needed to access this fixture. <I> **** Actions Taken **** notified supervision, intiated this CR and generated a WR. This is non-essential lighting. <N> **** Equipment Description **** Rad Waste valve galley A
402141 | CR | 20191210 |  | 3 | COND-HX-3A shell pressure has trended down 6 psi since R23 | N | N |  | N | YES | <D> **** Detailed Description **** COND-HX-3A shell pressure has trended down 6 psi since R23. Both the eDNA data from BS-PT-3A and MCR walkdown data from BS-PI-3AG indicate the same drop in shell pressure since June 2017. Heater level control valve demand has been consistent at ~65-66% over this same period. Recommend action to system engineering to evaluate cause and take necessary actions. <I> **** Actions Taken **** Reviewed HD LCV position and COND-HX-3 in/out temps as well as drain cooler approach temps. <N> **** Equipment Description **** T -508- - -F5/8.5 - | 02-00-COND-HX-3A
402142 | CR | 20191210 |  | 4 | ERB-W487 multiple light fixtures | N | N |  | N | YES | <D> **** Detailed Description **** W/O # 02131882, while performing ppm 10.25.64 several light fixtures failed the criteria for this procedure. Fixture #5 was not lit to begin with, fixtures 2,3,4 did not have thier quartz lights come on after the circuit was opened then closed back in. Fixture ERB-W487/2 needs to be replaced, there is an exisiting CR 388704 <I> **** Actions Taken **** notified supervision, intiated this CR and generated a WR This is non-essential lighting. <N> **** Equipment Description **** Rad waste 487 and the cable spreading room
402143 | CR | 20191210 | CAQ | C | DEP missed opportunities during LOR Scenario Evaluation |  |  |  | N | NO | <D> **** Detailed Description **** During an LOR scenario evaluation, the Notification for the declared emergencies were improperly perform, resulting in missed DEP Opportunities. Individualâ€™s qualification for LOAJ has been suspended. <I> **** Actions Taken **** Individual"s LOAJ qualification has been suspended
402144 | CR | 20191210 |  | 4 | Yellow PMDD found in Scanning Station Unattended |  |  |  | N | NO | <D> **** Detailed Description **** A Yellow USB, used for testing, was found scanning without the proper 'Work In Progress' signage displayed. This is outside the scope of what is allowed for yellow PMDD within SWP-CSW-15. This is NOT reportable under 10 CFR 73.77. <I> **** Actions Taken **** - Provided immediate coaching to individual that was performing the work. - Validated information on media with individual performing work. - Virus scan performed on yellow USB, scan was clean. - Yellow USB secured within designated storage location. - Contacted Supervisor and CSPM <N> **** Equipment Description **** Engineering Computer Lab
402145 | CR | 20191210 |  | 4 | ERB-TG441 Fixtures | N | N |  | N | YES | <D> **** Detailed Description **** W/O# 02146979-01, while performing ppm 10.25.64 fixtures 14,16,17 did not have their quartz lights come on after the circuit was opened then closed back in. <I> **** Actions Taken **** notified supervision, intiated this CR and generated a WR This is non-essential lighting. <N> **** Equipment Description **** TG 441
402146 | CR | 20191210 |  | 4 | As Found times out of tolerance range | N | N |  | Y | YES | <D> **** Detailed Description **** As Found time for E-RLY-5051/5/53/C was out of tolerance range. As-Found Check 1 time was 1.06 second with a range tolerance of 0.95 to 1.05 Check point 2 As Found time was 4.35 with tolerance range of 3.80 to 4.20 seconds. Relay functioned per its design. <I> **** Actions Taken **** Adjusted relay back into tolerance Check point 1 As-Left is 0.97 seconds Check point 2 As-Left is 3.98 seconds Relay installed back to service. <N> **** Equipment Description **** E-SH-5 | 02-00-E-RLY-5051/5/53/C
402147 | CR | 20191210 |  | 4 | Emergency Light Error Indicator | N | N |  | N | NO | <D> **** Detailed Description **** Reactor Building 522' elevation Northwest stairwell emergency light (SWS 3/6 LP-3DA-D-12) has a charger fault indication. <I> **** Actions Taken **** Generated CR. Non-essential lighting. <N> **** Equipment Description **** RB 522' NW Stairwell SWS 3/6 LP-3DA-D-12
402148 | CR | 20191210 |  | 4 | Standard found out of tolerance |  |  |  | N | NO | <D> **** Detailed Description **** Calcode # 0054068 AKO Model TSD011/002 Torque Cell was found OOT and adjusted. Reverse Traces have been done. No equipment was affected to ENSL or SLIC due to the standard being OOT. Report Located in G:\Standard OOT Data Reports\Torque Cells\20LbIn Cell and is labeled as Reverse Trace.
402149 | CR | 20191210 |  | 4 | WebEOC Fusion link to INPO briefly unavailable today. |  |  |  | N | NO | <D> **** Detailed Description **** The WebEOC Fusion link that connects Columbiaâ€™s vendor -hosted WebEOC software system to INPOâ€™s WebEOC system became disconnected on the vendorâ€™s server today. The issue was reported to the vendor, Juvare, whose staff analyzed the issue & restored the systemâ€™s Fusion connection to INPO at about 1510 PST today. WebEOC would be used in an emergency to convey selected event information to INPO in accordance with INPO IER 13-10. Columbia does not use WebEOC to satisfy any regulatory requirement or commitment. As such, its short period of degraded capability today was not a loss of any credited emergency response function. Recommend Cat â€œDâ€œ to support trending reliability of cloud-based solutions. <I> **** Actions Taken **** Contacted IS call center at ext. 8400. Then contacted the vendorâ€™s 24/7 customer support line. Troubleshooting by the vendor eventually determined that a Windows service (that the Windows-based WebEOC software relies upon) had stopped running. The vendor re-booted the Windows service and restored the WebEOC Fusion connection to INPO. WebEOC was checked to verify indications that the Fusion link had been restored. WebEOC was re-checked several more times since it was restored.
402150 | CR | 20191210 |  | 3 | MD-V-86 did not stroke during monthly cycle. | N | N |  | N | YES | <D> **** Detailed Description **** Ref WO 02143752. MD-V-86 did not stroke open on the first attempt during monthly cycle of MD valves. On the second attempt MD-V-86 stroked open and closed normal. Suspect solenoid MS-SPV-86 may be sticking when deenergized. The intent of this AR is for trending. <I> **** Actions Taken **** Finished WO 02143752. | 02-00-MD-V-86
402151 | CR | 20191210 |  | 4 | Exterior lights near PAAP building doors are out | N | N |  | N | YES | <D> **** Detailed Description **** The light fixtures on the exterior of the PAAP located near the revolving entrance doors have been out for a few weeks. Request facilities relamp or investigate the light loss to restore illumination at the entrance to normal levels. <N> **** Equipment Description **** Lights on PAAP building exterior near the revolving doors.
402152 | CR | 20191210 | CAQ | D | RCIC-DT-1 oil level below low level mark | Y | N |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was observed that RCIC-DT-1 oil level was below the low oil level mark for both the inboard and outboard bearings. The oil level for both bearings was about 1/16 inch below the "LOW (Standby Only)" mark. No oil leak was observed for RCIC-DT-1. <I> **** Actions Taken **** Notified CRS and wrote CR Oil added per WR. Approx 80 ml of oil added. Level in both the inboard and outboard drive turbine bearings sight glasses restored to above the low mark. | 02-00-RCIC-DT-1
402153 | CR | 20191210 |  | 4 | E-BU-SWA6/4 emergency battery unit has a charger fault | N | N |  | N | YES | <D> **** Detailed Description **** While performing operator rounds it was discovered that E -BU-SWA6/4 emergency battery unit has a charger fault. The green ready light on the unit was lit. The red light was blinking three times in succession indicating a charger fault. The same issue was noted in a CR about a week ago for the same emergency battery unit, but the work request was canceled due to the red light not flashing when electricians went out to inspect the emergency battery unit. AR 401865 WR 29152964 <I> **** Actions Taken **** Notified CRS and wrote CR E-BU-SWA6/4 is a non-essential emergency lighting unit. FPSI 19-0311 issued and posted. Staged portable lantern. | 02-00-E-BU-SWA6/4
402154 | CR | 20191211 | CAQ | C | White dust in suction side of TEA-FN-93 | N | Y |  | N | YES | <D> **** Detailed Description **** during replacement of TEA-FN-93, 02155727, noticed a white dust on the inlet of TEA-FN-93, installed new pump and staged old pump on RW 525 <I> **** Actions Taken **** informed maintenance, ops and engineering <N> **** Equipment Description **** Rad Wst 525 K1/11.1 | 02-00-TEA-FN-93
402155 | CR | 20191211 |  | 3 | Drawing and EPN inconsistencies for RCWU valves |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** RWCU Vessel outlet valves are inconsistent in their EPN on drawings and labeling. Specifically, RWCU-FCV-266A and RWCU-FCV-266B. EWD-4E-037A refers to the valves as a Valve (V). Whereas M523-3 refers to the valves as RWCU-FCV-266 A(B). Additionally, the RWCU panel in the Rad Waste Control room is inconsistent. The front display that has open and closed light indication labels both valves as FCVâ€™s. Inside the panel, they are labeled RWCU-FCV-266A and RWCU-V-266B. This has created a lot of confusion in placing tags and needs clarification, consistency, and relabeling. <I> **** Actions Taken **** Notified CRS and initiated CR
402157 | CR | 20191211 |  | 4 | M&TE OOT |  |  |  | N | NO | <D> **** Detailed Description **** Calcode #0062494 Dresser Sensor - model HQS-1 25" found OOT & adjusted within specs. Not used in the OOT range of 25". No Plant Impact. DEF # 7371A written. No Action Required <I> **** Actions Taken **** NONE TRENDING PURPOSES ONLY
402158 | CR | 20191211 |  | 4 | BWROG SAG Training in NANTeL |  |  |  | N | NO | <D> **** Detailed Description **** This AR is written to encourage the development of a plan and schedule for implementation of the BWROG Severe Accident Management Guideline (SAMG) Computer Based Training (CBT). The BWR SAMG CBT is under development and will be available for use September 1st, 2020 through INPOâ€™s NANTeL. This training incorporates the technical content of EPG/SAG Rev 4 SAMG which will be implemented by CGS by R25. The training targets NEI 94-01 ERO Functions of 1. Decision Makers, 2. Evaluators and 3. Implementers. Supporting documents attached in EDMS and contact the EOP Coordinator for additional information. <N> TREQ 19-0185 initiated to further evaluate this training
402159 | CR | 20191211 |  | 3 | Recommend writing a procedure for Transferring TR-B aux pwr |  |  |  | N | NO | <D> **** Detailed Description **** TR-B aux power is controlled with kirk keys. It can be powered from E-MC-7AA or E-MC-8AA. Upon loss of power ABN -Transformer directs the power restored from the alternate source but does not say how to transfer it. SOP-ELEC-SM7 -MAINT and SOP-ELEC-SM8-MAINT have steps that say how to do it. We have been using work request instructions to this point to transfer power. . Yesterday we had a near miss when the FIN ooperator requested from the PSRO to transfer power per his work request. Transferring aux power stops the cooling fans and INOP's TR-B. . I request that work instructions are written in the appropirate SOP to transfer TR-B aux power. Include declaring it INOP and doing an offsite power alignment. <I> **** Actions Taken **** Wrote CR. Discussed with WC Manager and Shift Manager . See EDMS for Operability data <N> Consider a separate assignment for Engineering to do an analysis that allows TR-B to remian operable while transferring aux power.
402163 | CR | 20191211 |  | 3 | Add Heise PTE-1 voltage and current measurements in1.5.4 |  |  |  | N | NO | <D> **** Detailed Description **** Add Heise PTE-1 voltage and current measurements in 1.5.4 We can utilize this function to measure mA and voltage loops. Could save dose due to less equipment having to hook up before performing a loop calibration. <I> **** Actions Taken **** disscused in FIN shop
402170 | CR | 20191211 |  | 3 | Facilities B5B scheduled eq outages not scheduled |  |  |  | N | NO | <D> **** Detailed Description **** Facilities Work Order affecting LCS required equipment not in the on line work planning process were not on the schedule and not reviewed for impact by Ops Work Control. This resulted in the on shift Op[s Crew having to perform an impact review, generate the correct LCS Inop sheet, enter the LCS RFO and perform the required actions on the fly. Email chain in EDMS for more detail. PMs related to B5B/FLEX need to be reviewed to ensure they are set up to be included in the on line power block planning and scheduling process. <I> **** Actions Taken **** Completed required actions, initated CR.
402172 | CR | 20191211 |  | 3 | Compressor Jacket water appeared cloudy | N | N |  | N | YES | <D> **** Detailed Description **** The CJW closed loop samples taken on 12/11/19 appeared to be cloudy. Chemistry suspected possible oil contamination as the compressor oil is a clear silcon based oil and appears cloudy in water. Chemistry sampled the jacket sample for TOC and found it to be relatively high for demineralized water and Nalco. Another closed loop system will be sampled for TOC as a comparison to the CJW next week when the DG-2 is sampled. Since there is no real base line for TOC in the cooling jackets that have Nalco in them we need to check the CJW against a comparable system. This AR is for trending and also to inform FIN that there may be oil leaking into the CJW. <I> **** Actions Taken **** Notified MCR, Chemistry Supervision and chemistry system specialist. Used the sample point valve as the equipment ID but it is the entire jacket water that is being referenced. <N> **** Equipment Description **** TG-441' East end just outside the Aux boiler room Where the compressors are. | 02-00-CJW-V-132
402173 | CR | 20191211 |  | 3 | RWCU Heat Exchanger Project |  |  |  | N | NO | <C> MRT Change: CR 402173 moved from Severity 3 to Severity 2 to perform an OPIT. <D> **** Detailed Description **** Project was designated as a preliminary budget on the Columbia Long Range Plan when it should have been designated as â€œbudgetaryâ€ per the plantâ€™s four-year budget cycle for projects. Late identification of project scope and costs have increased instability to the Stationâ€™s Long Range Plan. Approval of the additional scope requires either expending all capital contingency or deferring 13 projects to offset the additional costs. cycle for projects. Late identification of project scope and costs have increased instability to the Stationâ€™s Long Range Plan. Approval of the additional scope requires either expending all capital contingency or deferring 13 projects to offset the additional costs. <I> **** Actions Taken **** Discussed with the project manager from CPM and the manager from Asset Management's. Recommend to non-caq 3 to Asset Management
402176 | CR | 20191211 | CAQ | C | 16.3.3 & 16.3.1 need updated |  |  |  | N | NO | <D> **** Detailed Description **** There was a test key switch installed in WEA-CP-25 in order to make performance of 16.3.3 & 16.3.1 safer. However, 16.3.3 & 16.3.1 have not been updated to reflect the use of Key 246 for WEA-RMS-CP25/TEST. <I> **** Actions Taken **** Wrote CR, Informed procedure writer, and provided marked up copy of procedures. <N> A revision task has been created within the Maintenance revision data base. A link to this task assignment has been created within the EDMS of this AR. No further actions are required for this issue.
402177 | CR | 20191211 |  | 4 | FDR-PS-16 Pressure Switch Stuck Closed. | N | N |  | N | YES | <D> **** Detailed Description **** WO 02135602: During Calibration of FDR-PS-16 Switch contacts were stuck in the closed position. The pressure switch was isolated and vented into a pump, monitored by a 0-100PSI Heise gauge. while pressure indication read 0 PSI, switch contacts read .0035VAC. The switch was Pressurized to 40 PSI with no change in voltage (.0035VAC) . This switch failure was also verified by operations by starting up the Diminilizer with the switch isolated. This switch while isolated still allowed the process to start normally. If it was working correctly it would have never allowed valves 116 and 104 inlet/outlet valves to open. The switch is wired NO with an increasing trip setpoint of 36.5+-3psig. Needs Replaced <I> **** Actions Taken **** Supervision and operations notfied of switch failure. CR written and WR iniciated to fix the pressureswitch. <N> **** Equipment Description **** 467 Radwaste, E-IR-58 | 02-00-FDR-PS-16
402179 | CR | 20191211 |  | 3 | Main exciter bearing vibrations increasing and oscillating | N | N |  | N | YES | <D> **** Detailed Description **** Review of main exciter bearing 11 vibration trends show the exciter bearing vibrations are increasing and are varying between 2.5 to 5 mils . The changes in vibrations appear to be related to changes in generator hydrogen gas temperature and seal oil temperature, the vibrations increase with decreasing temperatures. Siemens was consulted and indicate the bearing 11 vibration profile was indicative of a gland seal ring rub, the generator bearings 9 and 10 show a similar vibration profile but the changes are much smaller in magnitude. The exciter bearing has a history of varying over time due to changes in temperature, the variations are typically small in magnitude. Following R24 bearing 11 vibrations have significantly increased and variations in vibration magnitudes are much larger. Review of operating parameters shows hydrogen gas temperature is being controlled about 6 to 8 degrees lower following the outage. Review of work activities shows TSW-TIC-9 was replaced and is now controlling at a lower temperature. TSW-TIC-9 temperature setpoint should be increased to control H2 gas temperature at approximately 100F to 105F followed by a monitoring period to assess the impact of the change and evaluate additional generator system temperature changes. This condition does not impact the overall function of the main exciter as vibrations are below the OEM recommended 7 mils for alarm and 14 mils for trip. <I> **** Actions Taken **** Discussed with Supervisor, recommend increasing generator H2 gas temperatures. <N> See EDMS for eDNA plots showing exciter vibrations and Hydrogen temperatures from prior to R24 and after R24 | 02-00-E-EXC-1
402181 | CR | 20191211 |  | 4 | EN Qual Cert Entered Into PQD Without Approval |  |  |  | N | NO | <D> **** Detailed Description **** Two students were given credit through ETAR for ME000650 (Basic Rigging Certificate) following completion of the course but prior to receiving final approval from the rigging coordinator. The students were given credit for the certificate on November 18th and maintained the incorrect status through December 9th when they received the rigging coordinators approval. No rigging work has been performed by the students. <I> **** Actions Taken **** The students certificate has been removed by reentering ME000650 in ETAR. <N> No work was performed while individuals held this qualification. Individual in Cal Lab entered the data, noticed the line for Rigging Coordinator approval, but assumed it was okay to enter. Issue was caught when Rigging Coordinator was signing paperwork and noticed that the individuals were already green in PQD viewer. Individual who entered the qualificaiton was coached, and the correct process was then followed, and individuals are now qualified. No further action needed.
402185 | CR | 20191211 | CAQ | D | RHR-A discharge pressure high | Y | Y |  | N | YES | <D> **** Detailed Description **** The RHR-A discharge pressure indication in EDNA (point X155) is high and increasing since the last RHR-A pump run for heat exchanger thermal performance (12/9/2019). The current pressurization rate is approximately 3 psig/hour and the current discharge pressure is 394 psig in EDNA. If the pressure continues to increase at this rate, the alarm setpoint of 455 psig may be met in about a day or so. The recommendation is to verify the EDNA reading is correct and if so, vent the system to reduce the pressure and potentially stop the pressurizations (in the past venting has helped slow pressurization rate and/or stop the pressurization). The RHR discharge pressure increase has been previously documented in CR 398119. The corrective actions to prevent pressurizations are scheduled to be completed in R25 (WO 02081140 RHR-V-50A Repair leakby). <I> **** Actions Taken **** Notified SM | 02-00-RHR-V-50A,02-00-RHR-V-53A
402187 | CR | 20191211 |  | 4 | CW Blowdown auto isolation | N | N |  | N | YES | <D> **** Detailed Description **** CW Blowdown isolated due to CW Chemistry Trouble Alarm. CW-LCV-1 auto-closed as required. <I> **** Actions Taken **** Placed CW-LCV-1 control switch in closed position. Notified Chemistry. <N> **** Equipment Description **** CW pumphouse. | 02-00-CBD-LCV-1
402188 | CR | 20191211 | CAQ | C | CDA Log generation and transmission to SIEM | N | Y |  | N | NO | <D> **** Detailed Description **** Review of a sample of CDA configuration identified some capable CDAs not generating and transmitting logs to McAfee SIEM. Recommend an extent of condition to identify those CDAs that are capable of logging but are not currently and implement a plan to address scope. Not reportable under 10CFR 73.77. <I> **** Actions Taken **** Consulted with Cyber supervisor and began reviewing CDA configuration in relation to log management.
402189 | CR | 20191211 |  | 4 | TG-TE-SCSRH on the Main Turbine RH Steam Chest is failed HI | N | N |  | N | YES | <D> **** Detailed Description **** The temperature element for Left side Steam Chest shallow temperature element is failed high and requires replacement/repair. This signal is one of two parameters used to determine temperature gradient across the wall of the steam chest (reference Attachment 3 of PPI PPM 4.820 .B1). This is a repeat occurrence of the condition. See â€œCross Referenceâ€ tab. <I> **** Actions Taken **** Discussed with RO researched prior CRs/WOs | 02-00-TG-TE-SCSRH
402190 | CR | 20191211 |  | 3 | DEH monitor displays erroneous values for steam chest deltaT | N | N |  | N | YES | <D> **** Detailed Description **** The Main Turbine Steam Chest differential temperature screen does not show the correct temperatures in value box or on the lower graph. Left Side steam chest has values of 535degF Deep and 513degF Shallow for a difference of 22 degF. The display shows 0 (zero) for this value. Right Side steam chest has values of 539degF Deep and a 795degF (failed high) Shallow for a difference of -256 degF. The display shows 271degF for this value. See photo in EDMS. <I> **** Actions Taken **** Discussed with DEH-ELEC engineer | 02-00-DEH-MON-RO
402191 | CR | 20191211 |  | 3 | Discrepancy in ARP and OMM for Steam Chest differential Temp | N | N |  | N | NO | <D> **** Detailed Description **** The Steam Chest differential temperature for Deep and Shallow listed in Attachment 3 of PPI PPM 4.820.B1 has a limit of 150degF. The OEM value provided in CVI OMM 01 -00,113,1,1 is 125degF in the list on Page 401/725, and 150degF in the spreadsheet on Page 623/725. <I> **** Actions Taken **** Requested OEM confirm proper value and provide updated documentation to reconcile OMM.
402192 | CR | 20191211 |  | 4 | NLORQ Biennial Requal Written Exam Failure |  |  |  | N | NO | <D> **** Detailed Description **** One non-licensed operator failed the biennial written exam administered on 12/11/19. Remediation will be IAW TDI-02 and TDI-10. <I> **** Actions Taken **** De-certified individual in PQD. Notified Operations and Operations Training Management. Recommend Severity Level 4.
402193 | CR | 20191211 |  | 4 | Found by NRC- large puddle found inside B600 entrance. | N | N |  | N | YES | <D> **** Detailed Description **** NRC noticed a large puddle inside B600 entrance directly in front of the personnel door during a walkdown. Determined that rain water leaked in from underneath and around the door. <I> **** Actions Taken **** Investigated puddle and informed supervisor of what I found. Initiated this CR. <N> **** Equipment Description **** Building 600
402194 | CR | 20191211 |  | 3 | Values in CVI OMM for Main Turbine Diff Exp are incorrect |  |  |  | N | YES | <D> **** Detailed Description **** Values for Differential Expansion located in Tab 5 of CVI OMM 01-00,113,1,1 (Turbine Controls Settings) are not current according to the turbine OEM. This appears to be a documentation issue with the OMM that resides in Passport. Settings in the Turbine Supervisory System for TG-MON-DE2 are correct and match what the OEM says is current. This is true for TG-MON-RP as well. However, settings for TG-MON-DE1 do not match either the OMM or the values provided by the OEM. The IMDS for this instrument needs to be updated and settings in the Turbine Supervisory System validated. <I> **** Actions Taken **** Contacted OEM and requested current documentation for Turbine Control Setting to replace the existing Tab 5 of the OMM. Discussed with I/C engineering Autogenerated WR for TG-MON-DE2 settings following IMDS change. | 02-00-TG-MON-DE1,02-00-TG-MON-DE2
402196 | CR | 20191212 |  | 4 | Unable to initiate CW blowdown after auto-isolation | N | N |  | N | YES | <D> **** Detailed Description **** CW Blowdown was unable to be established IAw SOP-CW-OPS and PPM 12.2.9. Earlier in the day CW BD had isolated as documented in AR 402187. After attempting to establish CW BD had field operator reverify line up. There were not trip signals indicated by Annunciator 4.840.A4 9-5 being clear. OPS4 checked locally for any alrms in at the dehalogenation skid. Unable to determine a cause that would pervent succesful performance of CWBD. CL-RMS-BP/1 was left in AUTO whilst attempting to establish CW BD. <I> **** Actions Taken **** Please correct this issue and allow for reliable CW BD. Attached Picture to EDMS. Issue appears to be the E-STOP False indication. | 02-00-CBD-LCV-1,02-00-CL-SKID-2
402197 | CR | 20191212 |  | 4 | SMA-FL-1 End of Roll | N | N |  | N | YES | <D> **** Detailed Description **** SMA-FL-1 end or roll. Rolls are quite clean, appears rolls are advancing unnecessarily. Please replace rolls and investigate the advancing mechanism. <I> **** Actions Taken **** Notified CRS | 02-00-SMA-FL-1
402198 | CR | 20191212 |  | 3 | Error in Maintenance Rule Tracking Log Entry |  |  |  | N | NO | <D> **** Detailed Description **** An incorrect equipment ID (RHR-P-2A) was used in a control room log maintenancr rule entry on 12/9/19. The correct equipment ID should have been RHR-SYS-A. this created an error in the eSoms Operabilitly and Availabilty Report. A late control room log entry was made on 12/13/19 night shift to document the error and correct the Operability and Availability Report. <I> **** Actions Taken **** Emailed Maintenance Rule Coordinator. Recommend to trending.
402200 | CR | 20191212 |  | 4 | SCW-TK-1 level rising | N | N |  | N | YES | <D> **** Detailed Description **** Water was added to SCW-TK-1 last shift. This shift level was out of sight high in the round sightglass with an approximate level of 14.5" Level was lowered to approximately 12.5" per SOP-SCW-OPS. Seven hours later, tank level appeared to have increased about 1". SCW conductivity as read on CITS-2 was 0.068 uS. SCW-V-431 was re-checked closed after being told the valve can be deceptive as it is hard to operate. SCW-V-431 did move slightly when re-checked closed. Level will be monitored over next shift to verify level is no longer increasing. <I> **** Actions Taken **** Notified supervisors | 02-00-SCW-TK-1
402201 | CR | 20191212 |  | 3 | ABN-ELEC-GRID needs updated |  |  |  | N | NO | <D> **** Detailed Description **** Currently section 5.0, item 1.3-1.4 states that the OPDS system will be monitor phase until December 2017. The OPDS system for the 115 and 230 KV systems will be armed in December 2019 and were not armed in 2017. The purpose of this CR is to update this section or clarify the section
402203 | CR | 20191212 |  | 4 | Building 12 Safety Inspection Discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** During this quarterâ€™s Building 12 Safety Inspection I found two discrepancies. One mice droppings in a closet space in the interior bathroom. Then in the room accessed without keys on the north side, items stored on a shelf that does not leave the required 24â€ gap per Inspection form 24570. <I> **** Actions Taken **** Photos taken, CR initiated, supervision informed. See EDMS for photos <N> **** Equipment Description **** Building 12
402204 | CR | 20191212 | CAQ | D | Received RPIS or DMM INOP and ROD DRIVE CONTROL SYS INOP ala | Y | Y |  | N | YES | <D> **** Detailed Description **** Received RPIS or DMM INOP, H13-P603.A7,1-7, alarm accompanied by ROD DRIVE CONTROL SYS INOP, H13-P603.A7, 2 -8. Rod 18-03 is selected. Reset per ARP and both alarms are reset. | 02-00-CRD-RDCC-1
402206 | CR | 20191212 |  | 4 | Monthly Chemical Storage area inspection discrepancies |  |  |  | N | NO | <D> **** Detailed Description **** The monthly inspection of Mechanical Maintenance chemical storage areas discovered the following discrepancies: Expired Chemicals found in Hot tool crib and RV test area. <I> **** Actions Taken **** Notified appropriate personnel to resolve. All discrepancies resolved, no further action required.
402210 | CR | 20191212 | CAQ | D | OG Analyzer Left N2 bottle low | N | Y |  | N | YES | <D> **** Detailed Description **** the Left OG N2 bottle is reading about 450 psig. right side bottle is reading 1950 psig. Left side regulator is supposed to be set to 60-70 psig and the right side regulator set to 10 psig higher so that the right side bottle should empty first. the RIght side bottle was replaced on 10-20-19. suspect either the regulator needs to be adjusted or the valve lineup needed to be verified sto be checked <I> **** Actions Taken **** wrote CR and WR to verify valve lineup check regulator settings and replace left side bottle <N> **** Equipment Description **** Left OG Analyzer N2 bottle T-441' SW side
402211 | CR | 20191212 |  | 4 | Fire Door S104 Doesnâ€™t Close From 1/3 Open (NRC Identified) | N | N |  | N | YES | <D> **** Detailed Description **** When allowing door S104 to close from one-third open, the door latch hangs up preventing the door from fully closing. NRC identified. <I> **** Actions Taken **** NRC informed SSS | 02-00-S-DOOR-S104
402212 | CR | 20191212 |  | 3 | EC-17259 inadequate PPM markups result in rework |  |  |  | N | NO | <D> **** Detailed Description **** CR-402176 states that PPMs 16.3.3 and 16.3.1 need updating as EC-17259 installed a test key switch. The markups in EC-17259 and AR-348089 did not indicate that the new test switch had a key. <I> **** Actions Taken **** Recommend trending for Rework. <N> Contrary to what is indicated in this AR CR, modification packages (e.g., EC DEC 17259 R0) do not include mark-ups of impacted procedures (e.g., PPM 16.3.1 and PPM 16.3.3). For EC DEC 17259 R0, mark-ups of impacted procedures PPM 16.3.1 and PPM 16.3.3 were provided by the AE as a courtesy separate from the DECP. EC DEC 17259 R0 very clearly states that a "new Two-Position Maintained Keyed Switch (Test Switch) is installed and mounted on WEA-CP-25". . Discussion with the CR initiator and AR-MODS supervisor indicate that all material needed for revising PPM 16.3.1 & 16.3.3 has been obtained by maintenance procedure writers. No further action needed and this CR can be closed.
402213 | CR | 20191212 |  | 3 | eSOMS equipment manager errors |  |  |  | N | NO | <D> **** Detailed Description **** CORC personnel are no longer able to copy EPN's to create new EPN's using eSOMS equipment manager. This is a required function for creating clearances where often new EPN's must be created for various reasons to hang tags on temporary or new components. Request IS update eSOMS permissions for RO's to allow copying and creation of EPN's.
402214 | CR | 20191212 |  | 3 | EC-14954 inadequate new PPM information results in rework |  |  |  | N | NO | <D> **** Detailed Description **** CR-401949 states that PPMs 10.27.67 and 10.27.68 need revision in order to be performed. The vendor literature supplied to create the procedures in EC-14954 and AR -224656-94 did not address the installed conditions, such as the test terminals for SW-PIC-15A, B would be inaccessible. <I> **** Actions Taken **** Recommend trending for Rework.
402215 | CR | 20191212 | CAQ | C | E503-2A drawing error |  |  |  | N | NO | <D> **** Detailed Description **** Zone K-15 of drawing depicts feeder breaker to E-MC-1B EPN as "E-CB-11/B". This EPN does not exist. Correct EPN is E-CB-11/1B. Zone C-15 has similar error for feeder breaker to E-MC-3C. Actual EPN should read E-CB-31/3C.
402216 | CR | 20191212 |  | 4 | STATE FM-B64 Fire Door Unauthorized Modifications Found | N | N |  | N | NO | <D> **** Detailed Description **** State Fire Marshal inspection found several fire doors in Willamette Building 64 where a mirror film has been applied to the fire rated window for three offices. . This is an unauthorized modification to the fire door. Plastic film material must be removed. Includes offices: 171A, 171B and 171C. Work Request written to remove this material from the glass. <N> **** Equipment Description **** Willamette Building 64
402217 | CR | 20191212 |  | 3 | Automated signatures bypassed in automated workflow process |  |  |  | N | NO | <D> **** Detailed Description **** On a new procedure SWP-ESD-03 initially it was unknown if they needed POC review when starting the automated procedure process in Automated Process Workflows (APW). Once the determination was made for POC review the appropriate approvals were not added back to the automated workflow process so the approval signatures were bypassed. the procedure. <I> **** Actions Taken **** This was noticed before the procedure was posted and the appropriate group was contacted to provide guidance on how to correct the signature approvals so the signers could sign and approve. The resolution provided was to obtain hard copy signatures from the signers needed on form 23761 Major Revision Reviews and approvals. Once the signatures are obtained then the form will be posted in EDMS and forwarded to the appropriate group so they can proceed with their process to finalize. The form 23761 was sent to the signers so they were aware of the hard copy signature needed. Recommend assign to AR-CALSERV. CR is for trending purposes.
402218 | CR | 20191212 |  | 3 | STATE FM-B64-Fire Door Unauthorized Modification | N | N |  | N | YES | <D> **** Detailed Description **** State Fire Marshal inspection found several fire doors in Willamette Building 64 where a mirror film has been applied to the fire rated glass windows. This is an unauthorized modification to the fire door. The plastic film material must be removed. Assign this CR to AR-FACIL to have this issue discussed in a management led briefing. This is a repeat violation from the 2018 State FM inspection. This violates the Fire Code and is included in ISPM-10, Section 3.2.2.f (Rev 10, Minor Rev 3). This film was applied after Facilities was required to remove film from fire doors in Building 34 (CR 387858) in 2018. <I> **** Actions Taken **** Work Request written to remove the material from the fire rated glass for offices 171A, 171B and 171C. <N> **** Equipment Description **** B64 Fire Doors 171A, 171C and 171C
402220 | CR | 20191212 | CAQ | D | Vac increase at TEA-SR-26 after return to service | N | Y |  | N | YES | <D> **** Detailed Description **** After TEA-SR-26 was returned to service following replacement of TEA-FN-93, a stepwise increase of vacuum has been observed on TEA-PTD-1. Vacuum was observed at 13.5' Hg on 12/11 (up from 11' Hg prior to TEA-FN-93 replacement) and observed at 12.7' Hg on 12/12. Vacuum measurements are made daily during performance of CI -15.2. The guidance in CI-15.2 , page 8, states that a vacuum level greater than 14' Hg will damage detector. <I> **** Actions Taken **** Spoke to supervisor, contacted engineering, verified TEA -SR-26 valve alignment correct. | 02-00-TEA-SR-26
402221 | CR | 20191212 |  | 3 | STATE FM-Failed Emergency Egress Lights and Exit Signs | N | N |  | N | YES | <D> **** Detailed Description **** State Fire Marshal performs random tests the battery backup of emergency egress lights and exit signs during inspections. Several units were found with the battery not functioning. All of these lights are normally tested monthly with an additional annual battery. Suspect that some are not on the model work order list. Recommend assignment to AR-FACIL to have each emergency light and each exit sign marked with a specific EPN to ensure that the craft can verify the procedure is completed in full and every unit is tested as required.. <I> **** Actions Taken **** WR written to have each identified unit fixed. <N> **** Equipment Description **** B26 Multiple exit signs B32 two exit signs B27 two emergency egress lights
402222 | CR | 20191212 |  | 3 | Hal/Dehal Skid Trip on False High TRH | N | N |  | N | YES | <D> **** Detailed Description **** The afternoon of Wednesday 12/11/19 the halogenation/dehalogenation skid Total Residual Halogenation (TRH) monitor indicated an above 0.08 ppm limit TRH. This caused the CW blow down valve CBD-LCV-1 to close. This functioned per design. The monitor was checked and flushed and the level dropped to normal and all alarms cleared. Not long after, the TRH monitor saw another crud burst and another over limit TRH. This set all the alarms back on. When OPS went to restore blow down the active alarms in the skid would not allow the blow down valve to open. solids from winter runoff which is contributing to the overall crud build up in the system. Results of the cleaning are shown in the attached pictures included in the EDMS doc folder for this CR. <I> **** Actions Taken **** The TRH monitor was cleaned and inspected Monday 12/9/19, two days before this incident. River make up to the CW system is showing high suspended. All the tubing and the spectrophotometer cell were cleaned again. Crud deposits were found in the tubing due to the increase in incoming suspended solids. Sample flow rates were increased to help prevent buildup of the crud. Recognizing the trouble caused by the incoming high suspended solids, Suez is looking at potential sampling changes to help prevent this. <N> **** Equipment Description **** Halogenation/Dehalogenation Skid
402223 | CR | 20191212 |  | 3 | N1 Spare Transformer Heater Found Off | N | N |  | N | YES | <D> **** Detailed Description **** The N1 Spare transformerâ€™s heater was found off. The GFCI circuit supplying the power was found tripped. Further inspection found damage to the insulation in the portion that resides in the oil containment berm (see EDMS for pictures). This heater power cable is suspended in air above the bottom of berm and the GFCI circuit reset/heater restored. Recommend replacement of the cabinet heater power feed cable. Note: The N1 spare transformer is located outside by the warehouse complex. The N1 Spare transformer cabinet heater is fed from 24LDS4-080 and located on Pedestal P5A & B. <I> **** Actions Taken **** Verified cable was not laying in the bottom of the berm, reset GFCI , contacted System Engineer and Supervision. <N> **** Equipment Description **** South of the Warehouse Complex. | 02-00-E-TR-N1-SPARE
402224 | CR | 20191212 |  | 3 | Recommend enhancement to SOP-RCIC-INJECTION-QC |  |  |  | N | NO | <D> **** Detailed Description **** Recommend adding Resetting RCIC Turbine Mechanical Overspeed Trip section to SOP-RCIC-INJECTION-QC. Recommend adding steps 7.1.1 through 7.1.7 of ABN-RCIC-ISOL/TRIP to what would be new section 2.4 of SOP-RCIC-INJECTION-QC. Also add steps 2.3.1 and 2.3.2 from SOP-RCIC-INJECTION-QC to the end of this new section to allow initiation of RCIC injection.
402226 | CR | 20191212 | CAQ | C | Received error on LEFM CPU 2 | N | Y |  | N | YES | <D> **** Detailed Description **** During performance of WO#02140538-01 REBOOT THE LEFM CPU'S, the STA noted that there was a â€œStale Dataâ€ error found on CPU 2 on the operatorsâ€™ P15 screen. After unlocking the CPU, an error message was discovered that said â€œScriptWorX 2006 Runtime has encountered a problem and needs to close.â€ (see photos attached in EDMS). I informed the STA who directed me to contact Engineering for resolution. System engineer recommended continuing on with Work Order instructions as written to reboot LEFM computers. Once this was complete, the error condition no longer existed. LEFM remained in Check Plus mode through the entire evolution. No actions necessary. <I> **** Actions Taken **** Informed operations, supervisor, and system engineer. Rebooted LEFM CPUs per work order instructions. Wrote this CR. | 02-00-RFW-CPU-FE4
402227 | CR | 20191212 |  | 3 | ESDI-3.8 Needs Revision |  |  |  | N | NO | <D> **** Detailed Description **** ESDI 3.8 requires revision to reflect organizational and programmatic changes within ESD
402230 | CR | 20191212 |  | 3 | First Aid Injury due to Minor Burn |  |  |  | N | NO | <D> **** Detailed Description **** An individual recieved a minor burn to their wrist while making coffee in an office enviornment. The individual was in the process of running hot water from a water cooler into a filter device which was on top of a coffee cup that the person was holding. When the individual moved away from the cooler after filling the device, the device dislodged and spilled the hot water and coffee grounds on their wrist. The individual immediately reported to Occupational Health and the Supervisor was informed. The burn was treated at Occupational Health and the individual returned to work. This should be classified as a first aid injury. <I> **** Actions Taken **** Occupational Health, Supervisor, Manager, and Industrial Safety notified. Individual was coached to always aim to use a risk free approach even when performing what seems to be a mundane activity in an office. <N> Plant Tracking Log entry has been made. Notification required by ISPM-1 have been made including SM, Occ Health, Ind Safety, CNO, CEO.
402232 | CR | 20191212 |  | 3 | Evaluation of PMT for SM-1, 2, and 3 crosstie bkrs |  |  |  | N | NO | <D> **** Detailed Description **** WO 02129061 called for performance of a detailed inspection of E-CB-1/2. The PMT task called for cycling the breaker under load. Turns out this PMT was not needed based on work performed, however this CR is written to evaluate if cycling this breaker is prudent under load since the switch is local to the cubicle and is not normally performed. These breakers are only closed during station blackout and ABN crosstie procedures and they are opened and closed under no load conditions. This would also apply to E-CB -3/2 and E-CB-2/1/3. Evaluate if work that does required cycling these breakers should only be performed during bus outages. <I> **** Actions Taken **** CR written
402233 | CR | 20191212 |  | 4 | Simulator |  |  |  | N | NO | <D> **** Detailed Description **** The CGS Simulator computers stopped communicating with the simulator equipment on 12/12/2019. This was discovered at 1700. Efforts to correct the problem have failed at this time . We will continue to pursue the issue on Monday, December 16. No training impact. <I> **** Actions Taken **** Notified OTM
402234 | CR | 20191212 |  | 4 | urinal valve in building 17 restroom sticking | N | N |  | N | YES | <D> **** Detailed Description **** While using the urinal and flushed the urinal, the valve stuck open and started over flowing, got to unrinal valve to reseat and put signage on the uruinal not to use <I> **** Actions Taken **** informed maintenance and operations <N> **** Equipment Description **** First urinal you come to as you enter building 17 bathroom
402235 | CR | 20191213 |  | 4 | BRE 21A CCTV Control Box | N | N |  | N | YES | <D> **** Detailed Description **** BRE 21A CCTV Control Box is not functioning as intended. Contact Security Supervison at 2185 for details. <I> **** Actions Taken **** Generated CR/WR. <N> **** Equipment Description **** BRE 21A, BRE at Security Checkpoint Equipment was restored and returned to service, no further action required.
402239 | CR | 20191213 |  | 3 | Incorrect Sealfast Adapters discovered inside COND-DM-1D | N | N |  | N | YES | <D> **** Detailed Description **** During disassembly of COND-DM-1D during WO 02152130, two different sized Sealfast adapters were discovered. The design calls for 1.25 inch high adapters (CID 58408644, CVI DWG 895-00,3). Both 1.25 inch and 1 inch adapters were found installed inside the CFD. The manufacturer, Graver, does not supply a 1 inch adapter. The 1 inch adapter will not affect the performance of the CFD or IFD modification. This is a configuration management issue. <I> **** Actions Taken **** Discussed with Project Manager and Manufacturer. <N> **** Equipment Description **** W -487- - -N1/12.2- | 02-00-COND-DM-1D
402240 | CR | 20191213 |  | 4 | TSW-V-232B slow leakage from threaded connections | N | N |  | N | YES | <D> **** Detailed Description **** There is slow (minor weap) leakage from the 1" and 2" small bore threaded connections associated with TSW-V-232B (R548' overhead just off the sourtheast reactor building elevator). See the photos attached to the EDMS of this AR CR 402240. Leakage noted due to tell-tale build-up of mineral deposits. | 02-00-TSW-V-232B
402241 | CR | 20191213 | CAQ | C | R548' TSW corrosion coupon branchline drawing discrepancies |  |  |  | N | YES | <D> **** Detailed Description **** Drawing discripancies exist for the R548' overhead TSW corrosion coupon small bore branchlines. A 12" TSW supply to RCC-HX-1A: CVI 215-00,3166 indicates the branchline is a 1" thread-o-let (TOL) with a 1" NPT plug. This 1" plugged branchline is not currently depicted on AED MEC M508-1. Please update AED MEC M508-1. B 12" TSW supply to RCC-HX-1B: CVI 215-00,3167 indicates the branchline is a 2" threaded couplet with a short 2" pipe nipple with a 2" ball valve (TSW-V-232B). This 2" configuration agrees with what is depicted on AED MEC M508-1 (2"TSW(17)-1). However, the field configuration appears that the branchline is smaller diameter (e.g., 1") and necks up to a larger (e.g., 2") ball valve with miscellaneous downstream pipe fittings. Please update CVI 215-00,3167 and AED MEC M508-1. C 12" TSW supply to RCC-HX-1C: CVI 215-00,3168 indicates the branchline is a 1" threaded couplet with a short 2" pipe nipple with a 2" ball valve (TSW-V-232C). The transition fitting between the 1" threaded couplet and the 2" pipe nipple is missing from the CVI drawing. AED MEC M508-1 indicates this branchline is entirely 2" diameter (2"TSW(17)-1). In the field, this branchline appears essentially identical to the B branchline configuration but also has some additional low voltage electrical cable tie-wrapped to it. Please update CVI 215-00,3168 and AED MEC M508-1. See the photo attached to the EDMS of this AR CR 402241. Recommend non-CAQ resolution by Mechanical Design & Drafting. This condition is a drawing issue only and has no impact upon the continued qualification, function, or operation of the subject branchlines or of any other station SSC. | 02-00-TSW-V-232B,02-00-TSW-V-232C
402243 | CR | 20191213 |  | 3 | E-RLY-27/6 As found Pickup out tolerance | N | N |  | N | I DONT KNOW | <D> While performing as found testing of E-RLY-27/6 UTC#370237 per WO 02143927-03 following relay replacement, the As Found Pickup test was found out of tolerance. The relay is supposed to pick up between 79.54-84.46 VAC. The As Found Pickup was 84.81VAC. The As Found Time Checks were in tolerance. The relay functioned and operated per design. This CR is for trending purposes only. <I> Notified CR and Supervision . Found this CR at INPROG at 06:27 12/14/19. Moved to APPROVED. <N> E-SH-6
402244 | CR | 20191213 |  | 3 | DES-4-1 Attachment 8.4 direction for CMR preparation |  |  |  | N | NO | <D> **** Detailed Description **** As currently written, the DES-4-1 Attachment 8.4 direction for "PREPARATION of CMRs" does not work correctly. Specifically, step 8 (DES-4-1 pg 36) to advance the CMR to status 'H/APPR' will not work in Asset Suite until after step 10 (DES-4-1 pg 36) is performed by the Verifier (who clicks the 'Reviewed?' checkbox on the Affected Documents List (ADL) in Asset Suite). Please correct the DES-4-1 Attachment 8.4 direction for CMR preparation. Additionally, the Procedure Sponsor for DES-4-1 indicated in Asset Suite needs to be corrected as it currently indicates an individual who no longer works for Energy Northwest. Recommend resolution by Design Engineering.
402245 | CR | 20191213 |  | 4 | Pressure Regulator for SOP-CW-CHEM Does Not Work | N | N |  | N | YES | <D> **** Detailed Description **** The pressure regulator that is connected to CAS-V-608 per SOP-CW-CHEM when operations performs a chemical offload will not rotate and will not allow air pressure downstream. AR# 400057 (written 10/09/2019) stated the pressure regulator was having problems providing consistent pressure. WR# 29152021 states a new pressure regulator was installed 10/29/2019. This is not a permanently installed piece of plant equipment, it is installed by procedure to regulate pressure sent to the delivery trailer then removed when the evolution is complete. Please prioritize regulator repair or replacement with a working unit as operations uses this regularly for chemical offloads. <I> **** Actions Taken **** Informed supervision, wrote AR <N> **** Equipment Description **** CWPH Acid Pump Room, Regulator hanging on cable connected to CAS-V-608. Connects downstream of CAS-V-608
402246 | CR | 20191213 | CAQ | D | Small packing leak on FP-V-40. | N | Y |  | N | YES | <D> **** Detailed Description **** There is a small, approximately one drop per minute packing leak on FP-V-40 in the east stairwell TB 441'. <I> **** Actions Taken **** Initiated CR. | 02-00-FP-V-40
402247 | CR | 20191213 |  | 3 | PPM 1.3.83 (Protected Equipment) Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** PPM 1.3.83 (Protected Equipment) currently has a requirment to perform SHIFTLY verifications of ALL hanging protected equipment signs. This requirement is not in alignment with the Operations Dept. business needs. I reccommend the following be added, as a note, to Section 3.1 of PPM 1.3.83: Note: Protected Equipment Postings in areas with limited access (Keys/Special permissions required for entry) are exempt from shiftly verification. (Examples of areas of limited access would be TMU Pumphouse, HRAs, C -Zones, etc.). <N> **** Equipment Description **** PPM 1.3.83
402248 | CR | 20191213 |  | 3 | Holes tapped with incorrect pitch tap on COND-DM-1D | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** While working on WO 02152130-01 COND-DM-1D septa replacement and IFD mod the vessel bolt holes were tapped using a 1 Â¼ -7 starter tap. The tap that should have been used was 1 Â¼ -8, this was identified when the team started to use the 1 Â¼ -7 die nut on the bolts and it would not start. A total of ~28 holes (see EDMS for Picture between arrows S to E) were tapped using the incorrect tap. Bolts were ran into the holes with no noticeable slop. A stack up close to the vessel lid thickness was used and torqued to the 550ftlbs required, again with no noticeable issues. Need engineering assistance for evaluation <I> **** Actions Taken **** CR generated for documentation, notified PM SM and Engineering. <N> E-mail from engineering â€œFrom my discussions with Mechanical Supervisor, the bolt holes were slightly tapered from the top of the hole to the bottom of the hole. Our discussion determined that approximately Â¾â€ at the top of the holes was not affected by the tapping performed (virtually no material was removed in the top Â¾â€ of the holes). Based on this information, there would be (3/4) (8) = 6 threads effective. Based on the Shigley Machine Design book excerpt, â€œthree full threads are all that are required to develop the full bolt strength.â€ Additionally, the holes have shown that full torque can be developed. Therefore, the maintenance activity performed to tap the holes is acceptable and full bolt strength will be developed when the maintenance is completed. This email can be attached to the WO task that is performing this maintenance activity to capture the Engineering review that this activity is evaluated as a Maintenance Activity. There is no benefit to generating an AR EVAL to evaluate this as a Maintenance activity since this will be captured and documented in the work order task.â€ . Engineering determined that the thread engagement are acceptable as is and the vessel head can be reinstalled with no issues. Copy of e-mail attached to EDMS
402249 | CR | 20191213 |  | 4 | Foot Injury |  |  |  | N | NO | <D> **** Detailed Description **** A NSO reported to his supervision that he was experiencing pain in his left foot the day after conducting his annual Physical Agility Testing. The NSO was seen by Occupational Health who referred him to be examined offsite. Contact Security for further information. <I> **** Actions Taken **** Security Management, Shift Manager, Occupational Health, and Industrial Safety were all notified. NSO taken to Occ health for evaluation and referred offsite. Security Supervision accompanied NSO to offsite examination. CR generated. No further MCR actions required.
402250 | CR | 20191213 | CAQ | D | Rod 30-43 accumulator trouble alarm. | Y | N |  | N | YES | <D> **** Detailed Description **** CRD-HCU-3043 accumulator trouble due to high water level. <I> **** Actions Taken **** Followed ARP | 02-00-CRD-HCU-3043
402254 | CR | 20191214 | CAQ | C | FP-B0-1B electrolyte found low | N | Y |  | N | NO | <D> **** Detailed Description **** FP engineer to evaluate per 15.2.1 step 7.2.4. While performing WO 02143729-01 electrolyte level on FP -B0-1B was found low on all 12 sells, contacted CRS, Supervisor and FP Engineer. See WO 02143729-01 for more details. <N> **** Equipment Description **** FP-B0-1B
402255 | CR | 20191214 | CAQ | D | Blue scram light on full core display slow to illuminate | Y | N |  | N | YES | <D> **** Detailed Description **** Blue scram light on full core display slow to illuminate. Locally verified that inlet and out let scram valves were open. This switch took about 10 seconds to show open. The POS shifted to open position as expected and no deficiencies were note. <I> **** Actions Taken **** Visually inspected the switches and valves locally. Informed MCR of local findings. | 02-00-CRD-POS-1262247
402256 | CR | 20191214 | CAQ | D | Blue scram light on full core display slow to illuminate | Y | N |  | N | YES | <D> **** Detailed Description **** Blue scram light on full core display slow to illuminate Locally verified that inlet and out let scram valves were open. This switch took about 3-4 seconds to show open. The POS shifted to open position as expected and no deficiencies were note. Did not determine which switch was not making up correctly <I> **** Actions Taken **** Identified during TSP-CRD-C101 Informed MCR of local findings. | 02-00-CRD-POS-1261423,02-00-CRD-POS-1271423
402257 | CR | 20191214 | CAQ | D | Water added to FP-B0-110B | N | Y |  | N | NO | <D> **** Detailed Description **** FP engineer to evaluate per 15.2.1 step 7.4.4. While performing WO 02143729-01 electrolyte level on FP -B0-110B was found low on 7 of 12 cells. Contacted CRS, Supervisor and FP Engineer. See WO 02143729-01 for more details. <I> **** Actions Taken **** Contacted CRS, Supervisor and FP Engineer. added water per procedure 15.2.1 <N> **** Equipment Description **** FP-B0-110B Building 33
402258 | CR | 20191214 |  | 4 | MS-V-142A Oily Lagging | N | N |  | N | YES | <D> **** Detailed Description **** There is oil under the lagging upstream of MS-V-142A. This piping was heated while RFT-DT-1A was out of service causing small wisps of oily smoke to be noticed. Recommend lagging removal and oil clean up. This line is only used while the RFT is shutdown to drain the HP Stop Valve (MS -V-172A) <I> **** Actions Taken **** Notified CRS and SM | 02-00-MS-V-142A
402259 | CR | 20191214 |  | 3 | Update Scram Timing Database | N | N |  | N | NO | <D> **** Detailed Description **** While performing TSP-CRD-C101 it was identified that the scram timing database has two pressure corrected rods, 26 -15 and 30-11 . These rods weren't tested during the Scram Timing Surveillance on 12/14/19 and does not impact the validity of the Scram Timing Surveillance results. This indicates that the database has not been updated or synchronized with the other computer properly. This appears to be a database only problem, and does not impact performance on 12/14/19. These rods have been verified at pressure prior to exceeding 40% for this cycle already, and the database should not indicate that these rods are pressure corrected. <I> **** Actions Taken **** Notified and Discussed issue with CRS. Wrote Condition Report. Recommend assigning to Reactor Engineering to verify/update the AST database as appropriate.
402260 | CR | 20191214 | CAQ | D | Blue scram light on full core display slow to illuminate | Y | N |  | N | YES | <D> **** Detailed Description **** Blue scram light on full core display slow to illuminate. Locally verified that inlet and out let scram valves were open. This switch took about 10 seconds to show open. The POS shifted to open position as expected and no deficiencies were note. <I> **** Actions Taken **** Identified during TSP-CRD-C101 Informed MCR of local findings | 02-00-CRD-POS-1263803,02-00-CRD-POS-1273803
402261 | CR | 20191214 | CAQ | D | Blue scram light on full core display slow to illuminate | Y | N |  | N | YES | <D> **** Detailed Description **** Blue scram light on full core display slow to illuminate Locally verified that inlet and out let scram valves were open. This switch took about ~2 sec to show open. The POS shifted to open position as expected and no deficiencies were note. Did not determine which switch was not making up correctly <I> **** Actions Taken **** Identified during TSP-CRD-C101 Informed MCR of local findings.Visually inspected the switches and valves locally | 02-00-CRD-POS-1263023,02-00-CRD-POS-1273023
402262 | CR | 20191214 | CAQ | D | Blue scram light on full core display slow to illuminate | Y | N |  | N | YES | <D> **** Detailed Description **** Blue scram light on full core display slow to illuminate Locally verified that inlet and out let scram valves were open. This switch took about 7 seconds to show open. The POS shifted to open position as expected and no deficiencies were note. Did not determine which switch was not making up correctly <I> **** Actions Taken **** Visually inspected the switches and valves locally. Informed MCR of local findings. Identified during TSP-CRD -C101 | 02-00-CRD-POS-1263815,02-00-CRD-POS-1273815
402263 | CR | 20191214 |  | 4 | FLM walkdown at 65% power. | N | N |  | N | YES | <D> **** Detailed Description **** During the FLM walkdown at 65%, one new leak was found. HD-V-3C27 has an S4 packing leak. No packing adjustment was attempted, as I was running up on my max dose allowed. | 02-00-HD-V-3C27
402264 | CR | 20191214 |  | 4 | MS-V-172A and BS-V-60A IN TEST light not lit. | N | N |  | N | YES | <D> **** Detailed Description **** During SOP-RFT-START section 5.5, MS-V-172A failed to stroke closed and the IN TEST light did not illuminate. BS-V-60A did start to close, red light out, the IN TEST light never illuminated. Verified Light bulb good. | 02-00-BS-V-60A,02-00-MS-V-172A
402265 | CR | 20191214 | CAQ | D | HCU accumulator trouble alarms | Y | N |  | N | YES | <D> **** Detailed Description **** Recieved high water level alarms on the following HCU's: 38-55, 42-03, and 38-03. Alarms cleared using SOP-CRD-HCU. | 02-00-CRD-HCU-3803,02-00-CRD-HCU-3855,02-00-CRD-HCU-4203
402266 | CR | 20191214 |  | 4 | BRE 33 Door Handle |  |  |  | N | YES | <D> **** Detailed Description **** BRE 33 Door Handle is loose. The handle functions as designed, but there is a degraded spring in the inner portion, which will not allow the handle to return to a horizonal position. <I> **** Actions Taken **** Security Supervision notified. CR/WR generated. <N> **** Equipment Description **** BRE 33
402267 | CR | 20191214 |  | 3 | HV-V-31A need replaced next outage | N | N |  | N | YES | <D> **** Detailed Description **** TEAM was Unable to stop the leak through injection, packing follower and packing gland are steam cut in multiple spots. This valve should be cut out and replaced of base metal repaired and machined. | 02-00-HV-V-31A
402268 | CR | 20191214 |  | 3 | Recommend reinjection of RFW-HX-6A clamp next down power. | N | N |  | N | YES | <D> **** Detailed Description **** TEAM (VENDOR) recommends to perform a reinjection during the next down power of the clamp installed under WO 02154822-01. Current RFW-HX-6A is not leaking. | 02-00-RFW-HX-6A
402269 | CR | 20191214 | CAQ | C | Unable to reach valve to take measurement for Furmanite/TEAM |  |  |  | N | YES | <D> **** Detailed Description **** Craft was unable to reach MD-V-71 with extension ladder, this will take a scaffold to do this work and the dose rates a high at 65% power approx.. 800mr/hr. This will need to be scheduled for next down power but, recommend doing this work next outage. | 02-00-MD-V-71
402270 | CR | 20191214 |  | 3 | PPC computer on RO-2 desk not working | N | N |  | N | YES | <D> **** Detailed Description **** The Plant computer on the RO-2 desk is not working, the screen displays the following message. Windows could not start because the following file is missing or corrupt: system32\DRIVERS\pci.sys You can attempt to repair this file by starting Windows Setup using the original Setup CD-ROM. Select â€˜râ€™ at the first screen to start repair. <I> **** Actions Taken **** generated WR to facilitate repair. This is a problem only with the terminal on the RO2 desk. Other terminals are working properly, so PPC is properly functioning. PPC is functional along with LEFM and Core Thermal Powr calculations. There is no DNC. <N> **** Equipment Description **** MCR RO-2 plant computer.
402271 | CR | 20191214 |  | 3 | SOP-RFT-SHUTDOWN procedure enhancements |  |  |  | N | NO | <D> **** Detailed Description **** SOP-RFT-SHUTDOWN Step 5.5.7 for checking shut COND-V-610A should be conditional same as 5.5.6 for COND-V-147A. Verify COND-V-610A CLOSED if completely isolating RFT-DT -1A. Step 5.6.7 for B RFT also needs revised.for COND-V -610B.
402272 | CR | 20191214 |  | 4 | CW blowdown isolated | N | N |  | N | YES | <D> **** Detailed Description **** CW blowdown isolated after receiving CW Chemistry Trouble Alarm (4.840.A4.9-5) due to high Chlorine concentration spike. <I> **** Actions Taken **** Placed CBD-LCV-1 to close after CW blowdown flow indicated 0gpm. Dispatched an Operator to verify automatic actions. Notified Chemistry | 02-00-CL-SKID-2
402273 | CR | 20191214 | CAQ | D | MS-V-164A required 3 strokes to indicate proper OSP-MS-S701 | N | Y |  | N | YES | <D> **** Detailed Description **** MS-V-164A required 3 strokes to indicate properly during OSP-MS-S701. Valve stroked closed properly (green light) then went gray with no indication at all. <I> **** Actions Taken **** Informed OCC | 02-00-MS-V-164A
402274 | CR | 20191214 | CAQ | D | MS-V-166B required 2 strokes to indicate proper OSP-MS-S701 | N | Y |  | N | YES | <D> **** Detailed Description **** MS-V-166B required 2 strokes to indicate properly during OSP-MS-S701. Valve indicated closed properly, but then went gray with no indication. <I> **** Actions Taken **** OCC informed | 02-00-MS-V-166B
402275 | CR | 20191214 |  | 3 | PPM 15.1.2 Procedure Enhancement |  |  |  | N | NO | <D> **** Detailed Description **** Most recent revision of PPM 15.1.2 inadvertently changed the 'Materials, Tools, and Test Equipment' section to step number 4.12 vice 5.0. This is incorrect because Section 4 is the P&L's. This error changed all subsequent step numbers and resulted in the procedure step numbers not matching with the steps in the attachment headings. Recommend revising step numbers. <I> **** Actions Taken **** Wrote AR.
402276 | CR | 20191214 |  | 3 | Conflicing procedure guidance for RFT turning gear ops |  |  |  | N | NO | <D> **** Detailed Description **** SOP-RFT-SHUTDOWN, SOP-RFT-START and SOP-RFT-OPS all have conflicting procedure guidance in P&Ls and procedure steps for turning gear ops relative to when a turning gear can be secured early. <I> **** Actions Taken **** Added procedure mark ups for all 3 to eliminate or clarify procedures in EDMS
402277 | CR | 20191215 |  | 3 | HD-LIC-1A controlling higher than expected | N | N |  | N | YES | <D> **** Detailed Description **** HD-LIC-1A is controlling level in FWH-1A at approximately 94% output signal, HD-LIC-1B and 1C are controlling level with approximately 55-60% output. Heater was taken offline at CRS direction the water level in the heater took an abnormally long amount of time to drain with HD-LIC-1A at 100% output (full open). HD-LIC-1A was replaced during R -24 WO 02094545, recommend troubleshooting HD-LCV-1A or HD -E/P-1A. It appears as if HD-LCV-1A is not opening enough or has some obstruction to prevent the same flow as HD -LCV-1B and HD-LCV-1C. <I> **** Actions Taken **** Removed FWH-1A from service per CRS direction. <N> At times while controlling in automatic, HD-LIC-1A was positioned as high as 99% open. Concern was controller being maxed out potentially causing an uncontrollable rise in level and subsequent trip of 1A feedwater heater. Removed from service pending investigation. See PNL 4.4 of SOP -FWH-SHUTDOWN for potential transient caused by a trip of feedwater heater 1A. When HD-LIC-1A was removed from service it took approximately 2 minutes for level to drop off-scale with the control valve full-open (see video). | 02-00-HD-E/P-1A,02-00-HD-LCV-1A
402278 | CR | 20191215 |  | 4 | Restoring blowdown following high chlorine concentration | N | N |  | N | I DONT KNOW | <D> **** Detailed Description **** After receiving a CW Chemistry Trouble Alarm for high chlorine concentrations, CW blowdown isolated. This occurred at 12-14-19 1926. The chlorine concentrations per PPM 12.2.9 did not reach acceptable levels until 12-15-19 0400. <I> **** Actions Taken **** Informed on-call chemistry supervisor, system specialist and vendor. And performed a partial surveillance of PPM 12.2.9 to restore blowdown.
402286 | CR | 20191215 |  | 3 | MCR computers not working | N | N |  | N | YES | <D> **** Detailed Description **** Computers 5N9RMG1 and D89RMG1 in the MCR are not working. Both are used for TDAS/PPC monitoring in the MCR. <I> **** Actions Taken **** Contacted IS and was reffered to Compupter Engineering. . There are still 7 computers in the main control room with TDAS/PPC capability. <N> **** Equipment Description **** MCR computers
402287 | CR | 20191215 |  | 4 | CAS-DPI-30B appears to have been damaged. | N | N |  | N | YES | <D> **** Detailed Description **** CAS-DPI-30B appears to have been damaged. the guage is missing a face piece the trim atound the guage is broken and seperating. see picture attached. Please find a suitable replacement. <I> **** Actions Taken **** wrote WR CR | 02-00-CAS-DPI-30B
402288 | CR | 20191215 | CAQ | C | Shipping software issue discovered |  |  |  | N | NO | <D> **** Detailed Description **** While preparing to ship radwaste liners 19-093-HP and 19 -096-HP a discrepancy was discovered in the paperwork for shipment 19-114 manifest number 02658. The two liners were being prepared for shipment on a single flatbed to the burial site. Total Package Activity of 808 mCi on NRC Form 540 Block 16 did not match the Container Total Activity 822 mCi on NRC Form 541 Block 15. The discrepancy was unable to be immediately resolved in the field and a decision was made to postpone the shipment. The radwaste liners did not leave the protected area and are currently stored in a secure location near the spray ponds. The difference in the total shipment activity was traced to the shipping software used to generate the shipping manifest. The data entries were validated as correct for the shipment. The shipping software did not provide the correct activity totals on the printed manifest. The activity totals were correct in other reports generated by the software. <I> **** Actions Taken **** Notified Management of the discrepancy and cancelled shipment. Informed software vendor of a potential software issue and made arrangements to provide copy of database for analysis. Informed waste disposal site the shipment was cancelled. Created test scenarios to verify the software was functioning as intended. Three separate scenarios were created but unable to replicate the discrepancy. Conducted a review of two previous multi-container shipments with no identified discrepancies. Recommend the following compensatory action: â€¢ For multi-package shipments ensure NRC Form 540 sum of individual package activities match the total activity on NRC Form 541
402289 | CR | 20191215 | CAQ | C | EWD's do not appear to agree with plant | N | N |  | N | NO | <D> **** Detailed Description **** EWD-74E-059 for HV-V-23A and HV-V-23B and EWD-74E-007 for HV-V-15C show Push Buttons that are not consistent with the plant. The push buttons appear to be swapped between the drawings and appears to be the same in all the drawings for the 23's and 15's. Recommend reviewing the EWD-74E series further for accuracy and making appropriate corrections. <I> **** Actions Taken **** Compared several drawings
402290 | CR | 20191215 | CAQ | D | FP-V-52 Packing Leak | N | Y |  | N | YES | <D> **** Detailed Description **** FP-V-52 has a ~3 drop per minute packing leak. <I> **** Actions Taken **** Wrote CR, Informed CRS | 02-00-FP-V-52
402291 | CR | 20191215 |  | 3 | SOP-AS-SHUTDOWN procedure enhancement. |  |  |  | N | NO | <D> **** Detailed Description **** SOP-AS-SHUTDOWN step 5.2.10 does not have a sign off line and could be missed. <I> **** Actions Taken **** cr
402292 | CR | 20191215 |  | 4 | MS-V-141B has a minor packing leak | N | N |  | N | YES | <D> **** Detailed Description **** MS-V-141B has a minor packing leak. its just inside the high rad area about head height. <I> **** Actions Taken **** cr wr | 02-00-MS-V-141B
402293 | CR | 20191215 | CAQ | D | NRC Resident Concern; 2-DO-FLX-3A1 leaks | Y | N |  | N | YES | <D> **** Detailed Description **** DG1 engine 1A1 flex hose 2-DO-FLX-3A1 leaks at the connection where the flex hose connects to the hard pipe. Picture will be attached to show the connection. Leak is less than one drop every 5 minutes. <I> **** Actions Taken **** Cleaned area, verified no other flex hoses leaked. MCR staff informed, CR & WR written. | 02-00-DO-FLX-3A1
402294 | CR | 20191215 | CAQ | D | NRC Resident Concern: Leak from DO-FLX-4B2 | Y | N |  | N | YES | <D> **** Detailed Description **** DG2 engine 1B2 flex hose 2-DO-FLX-4B2 leaks at the connection from hard pipe to flex hose. Picture attached to point the leakage location. Leak is less than one drop every 5 minutes. <I> **** Actions Taken **** Cleaned area, verified no other flex hoses leak. MCR staff informed. CR & WR written. | 02-00-DO-FLX-4B2
402295 | CR | 20191216 |  |  | GSB 441' Soap Dispenser in Men's Bathroom is Broken |  |  |  |  | YES | <C> CR initiated anonymously, reviewed for Safety Conscious Work Environment (SCWE) content. Moved to CR-SRO for OPS review. <D> **** ANONYMOUS CR - Detailed Description **** The soap dispenser in the Men's Bathroom located in the Yakima Bldg 441' is Broken. There is a small piece of plastic laying on the counter just below the dispenser. <I> **** Actions Taken **** Initiated this AR / CR. Could not initiate a work request due to this being anonymous? <N> **** Equipment Description **** GSB Yakima Bldg 441' Mens Bathroom Soap Dispenser
402296 | CR | 20191216 |  | 3 | ALARA Suggestion - Reduce RW 467' Fan Room Dose Rates |  |  |  | N | NO | <D> **** Detailed Description **** The RW 467' Fan Room continues to be a storage location for items that cause the fan room to have elevated dose rates. Some of these items may be staged for decon, but they normally remain in place for months and sometimes years. The fan room does not have any system that causes dose, so it should be <1 mrem/hr. Some of the items in the room include: RWCU-RST-70A (*60 mrem/hr on contact/8 mrem/hr @ 30cm), Dragon Valve High Pressure Hoses (*20 mrem/hr on contact/4 mrem/hr @ 30cm), SDIV Material Knaack Box (*45 mrem/hr on contact/15 mrem/hr @ 30cm), EDR-P-11 (*25 mrem/hr on contact/6 mrem/hr @ 30cm), Misc Hoses (*8 mrem/hr on contact/2 mrem/hr @ 30cm). This causes the general area to be 1-3 mrem/hr for new resin stacking and lead blanket storage and retrieval, and are resurveyed monthly by RP. Needed items could be stored in the empty Centrifuge "A" Rm connected to the decon facility. <I> **** Actions Taken **** Initiated this AR/CR.
402303 | CR | 20191216 |  |  | Isolation of PCIVs not tracked correctly | Y | Y |  | N | NO | <D> **** Detailed Description **** In September Operations exited TSAS 3.6.1.3 while some PSR valves remained inoperable. The penetration flow paths remain isolated by C-PSR-PCIV-002. Reference T17-C-PSR -PCIV-001 -001
402304 | CR | 20191216 |  |  | M&TE REJECTED |  |  |  | N | I DONT KNOW | <D> **** Detailed Description **** Calcode #0063051 Omega Hygrothermograph- model CT485B Found OOT and Rejected. EFIN Eval : The one item on the usage card is for non-plant equipment. The low humidity fail has no impact on the plant.Tthe M&TE passed all temperature ranges and higher humidity ranges. DEF #7370A Written. No Plant Impact. No Action Required <I> **** Actions Taken **** NONE TRENDING PURPOSES ONLY
402305 | CR | 20191216 |  |  | Evaluate sections in SOP-ELEC-DIV1-TEMPPOWER for any Mode |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate sections in SOP-ELEC-DIV1-TEMPPOWER for TP installation in any Mode. This will support R25 pre-outage work to minimize electrical resources in R25. See AR 396821 . Section 5.29 RW Decon Shower Hot Water Heater (WPWH HX-1) Temporary Power. The purpose of this Section is to provide temporary power to RW Decon Shower Hot Water Heater (WPWH HX-1) during a Division 1 outage. The disconnect WPWH-DISC-7E3E in the RW 487 Bldg. will be back fed from a spare breaker in E-MC-6B RW467. . Section 5.33 RW 507 Welding Receptacles Temporary Power Installation. The purpose of this section is to provide temporary power to Rad Waste 507 welding receptacles during E-SL-73 outage.
402306 | CR | 20191216 |  |  | DEH historical logging stopped error | Y | Y |  | N | YES | <D> **** Detailed Description **** DEH historical logging stopped error popped up on DEH-MON -02. It shows that the historical logging stopped at 7:00 am on 12/16/19. <I> **** Actions Taken **** Wrote CR Informed CRS | 02-00-DEH-MON-2
402311 | CR | 20191216 |  |  | Procedure change request |  |  |  | N | NO | <D> **** Detailed Description **** Identify step 7.12 of OSP-CONT-M101 as SRO/CRS step. This is an administrative check and has an associated WO task to update the LCO sheets.
402315 | CR | 20191216 |  |  | M&TE REJECTED |  |  |  | N | NO | <D> **** Detailed Description **** Calcode # 45220 Fluke DMM - Model 45 As founds passed Calibration. Now Rejected broken beyond economical repair. No Plant Impact. DEF # 7372A written. No Action Required. <I> **** Actions Taken **** None Trending purposes only
402316 | CR | 20191216 |  |  | TGRI is not mentioned for allowing RO's to perform tag hangs |  |  |  | N | NO | <D> **** Detailed Description **** A SM requested assistance in maintaining boundary tag hanger quals for an RO. The RO needed the refresher course TG000056 which is for the qual group TGEO. Step 2.1.4 of PPM 1.3.64 states. â€œAn SRO can perform RO functions (TGSO or TGRO) in eSOMS and an RO can perform EO functions (TGRO or TGEO) in eSOMS as long as they meet qualification requirements for that function.â€ With the split of TGRO into TGRI (Clearance Processing) and TGRO (Clearance Preparation), per PPM 1.3.64 , an RO would have to qualified TGRO before hanging tags. Usually, TGEO is removed from the RO qualification when becoming an RO. Recommendation is to add TGRI to Step 2.1.4 of PPM 1.3.64.
402318 | CR | 20191216 |  |  | CVI ISO 317-00,532 shows incorrect EPN. |  |  |  | N | NO | <D> **** Detailed Description **** CVI ISO 317-00,532 shows BD-V-12 which is not even in the Passport system. The correct EPN would be BD-V-14 as it is missing from the drawing and belongs in that manifold. See M513 for confirmation. Please update CVI ISO 317-00,532. <I> **** Actions Taken **** Wrote this AR. This AR/CR is a duplicate of AR/CR 400487 which is already assigned to AR-DESDFTM. Reccomend trend AR 402318 to AR 400487.
402319 | CR | 20191216 |  |  | Unguarded shafts on RCC pumps |  |  |  | N | YES | <D> **** Detailed Description **** Safety concern- The shafts on the RCC pumps (548 RxB) have unprotected sections of shaft which represent a signinficant safety risk to personnel working in the area. It is extremely hard for people in the area adjacent to the pumps to tell which pumps are running in the area. The pumps are near the entrance to the RWCU Hx room where personnel spend a good amount of time- especially during outage. In addtion, the pumps and shafts are at a height such that someone in the area could easily lose focus and rest their hand on the spinning shaft. Request guards be installed over these shafts. This item has been evaluated before, but it needs a fresh look with the R25 and the major project in the RWCU Hx room on the horizon. <I> **** Actions Taken **** Wrote CR, dsicussed with my supervisor. <N> AR-EVAL 402353 and WR 29153190 initiated and cross referenced. | 02-00-RCC-P-1A
402325 | CR | 20191216 |  |  | Inadequate Closure of AR-CR 380246 |  |  |  | N | NO | <D> **** Detailed Description **** This is solely a documentation issue and does not affect operation of plant equipment. AR-CR 380246 documents that OG-SPV-16A and OG-SPV-16B are labeled as OG-LSPV-16A and OG-LSPV-16B in the field which matches EWD-40E-059. The designator "LSPV" in asset suite description says "SOL. PILOT VALVE TMU-LEVEL" which implies that the designator is only intended for TMU. AR-CR 380246 recommended that the labeling and EWD-40E-059 be updated to clearly identify the subject off gas solenoid pilot valves as OG-SPV-16A and OG-SPV-16B. . AR-ASGN 380246-01 did not follow this recommendation; no documents were updated, it can be presumed that new equipment labels were not created, and Asset Suite was updated to set OG-SPV-16A and OG-SPV-16B to NONEQUIP status. Based on discussion with design and drafting, 1) EWD-40E-059 should be updated to reflect OG-SPV-16A and OG-SPV-16B rather than LSPV (this would be consistent with M535-1 and M975). 2) Asset Suite should be updated to return OG-SPV-16A and 16B to Active status and set OG -LSPV-16A and OG-LSPV-16B to NONEQUIP status; the appropriate D078 documentation should also be transfered from the NONEQUIP to the ACTIVE EPNs, as appropriate. 3) New labels should be created for OG-SPV-16A and OG-SPV-16B. Recommend assigning to AR-DESDFTE. <I> **** Actions Taken **** Discussed with Design and Drafting. Reviewed Asset Suite and drawing info associated with OG-SPV-16A and OG-SPV-16B. Wrote CR. . Performed walkdown and verified that EPN labels in the field still say "LSPV"; see pictures in AR EDMS.
402331 | CR | 20191216 |  |  | STATE FM-Unsecured Compressed Gas Bottles Found |  |  |  | N | NO | <D> **** Detailed Description **** 2019 State Fire Marshal inspection found several examples of unsecured or ineffective securing of compressed gas bottles at facility buildings at Columbia. The following areas were noted: B26-Pop machine mixing area, one tank CO2 B32-Nitrogen unsecured in East side bottle storage rack B73-Multilple examples of ineffective securing of cylinders B80-Fire extinguisher rebuild station with multiple fire extinguishers unsecured and not nested. B191-SPA50 dry chemical bottles on a pallet with shrink wrap but not properly secured. B13-protected area-poorly secured nitrogen cylinder <I> **** Actions Taken **** B26, B32 and B13 bottles were immediately secured. The cylinder owners were contacted to make permanent corrections. B73 warehouse area cylinders were corrected and an active work request was identified to fix the legacy problem. B191 cylinders were identified as obsolete and disposal is being arranged. B80-fire extinguisher rebuild owned by the mechanics shop, will be contacted to make corrections. . See cross referenced CR's for multiple instances of this issue going back several years.
402332 | CR | 20191216 |  |  | E-VM-SH6/B As-Found was of tolerance | N | N |  | N | YES | <D> **** Detailed Description **** E-VM-SH6/B As-Found was of tolerance. Meter has a 2% tolerance range & was found to be out @ 3.3% & 2.2% for two of the calibrartion points. <I> **** Actions Taken **** Adjusted meter per PPM 10.25.81 As-Left is 1.1% Meter is run to failure. Suggest replace meter. <N> **** Equipment Description **** E-CP-H13/P800 BOARD C | 02-00-E-VM-SH6/B
402333 | CR | 20191216 |  |  | Evaluate NSO Job Analysis against current conditions |  |  |  | N | NO | <D> **** Detailed Description **** Evaluate the NSO job analysis in the position description form 12723 to align with current job related duties. <I> **** Actions Taken **** Initiated CR, notified Security Management
402337 | CR | 20191216 |  |  | Install Permanent Scaffold Ladder MC-8BB (Safety Concern) |  |  |  | N | NO | <D> **** Detailed Description **** Performing OSP-SW-M102 requires checking SW-V-112 locked open. Permanent scaffolding in the MC-8BB room blocks the line of sight from the floor but there is no ladder to access this scaffold with . Please install a permanent scaffold ladder to access SW-V-112. This is a safety concern as the only way to visually check SW-V-112 would be to free climb or bring a temporary ladder into the MC-8BB room with the risk of bumping SR buckets or worse falling from the less secure ladder. <I> **** Actions Taken **** Discussed with MCR. <N> **** Equipment Description **** Scaffold in MC-8BB room on RB 572.
402340 | CR | 20191216 |  |  | Eval for Justification of Crit R designation for DSA-V-4A |  |  |  | N | NO | <D> **** Detailed Description **** While it was ultimately determined from the Root Cause Evaluation (RCE 399463) performed that DSA-V-4A did not fail to perform any of its Mrule defined functions and/or safety functions, this CR is being generated to evaluate further whether DSA-V-4A requires justification for classifying the SSC as Crit R component. While DSA-V-4A did not fail its S/R or MRule function, the improper system alignment along with DSA-V-4A being degraded were contributing causes to CR 399463. <I> **** Actions Taken **** Discussed with MRule Coordinator and supervisor
402342 | CR | 20191216 |  |  | GBP-IS-03 and ITPRC LRP Processes not in alignment |  |  |  | N | NO | <D> **** Detailed Description **** GBP-IS-03 and ITPRC LRP Processes not in alignment with GBP-AM-11. This delta is documented with Snapshot Assessment #399985. <I> **** Actions Taken **** Assignment were made to facilitate the procedure update on AR#399985 (02 & 03).
402344 | CR | 20191216 |  |  | RRA-TS-XXX calibration implementation issue |  |  |  | N | NO | <D> **** Detailed Description **** During preparation of WO 02109020 it was not recognized during the walk down that test equipment would not have a power source in several of the MCC rooms (ie. requiring an extension cord through the door). During execution, good questioning attitude was used, system engineering concurrence was sought out and received to determ/reterm the temperature switches to allow for the calibration outside of the MCC room. These MCC doors are HELB barriers and cannot be propped open or impaired in Modes 1, 2, and 3. Action requested for planning to update the model work order for future occurrences to include this information. <I> **** Actions Taken **** Informed Mgmt, WWM, Planning, FP, and Ops
402345 | CR | 20191216 |  |  | PPM 10.27.65 was not revised for ISCR-369397 |  |  |  | N | NO | <D> **** Detailed Description **** I&C Tech noted that PPM 10.27.65 was not revised for ISCR -369397 that will be implemented this week. The change was due to installing a new keep alive source in TSC-RIS-1B that will affect the High and Hi-Hi alarm setpoints. ISCR-369397 was closed in 2018 with no assignment to revise the affected procedure. <I> **** Actions Taken **** PPM 10.27.65 is currently in approval routing to bring it into alignment with TSC-RIS IMDS setpoints and should be issued in time for maintenance.
402346 | CR | 20191216 |  |  | (NRC) CR Initiation for Alarm Receipt |  |  |  | N | NO | <D> **** Detailed Description **** NRC resident questioned why CR was not written for a control room alarm. During the RX downpower, at 09:43 12/14/19 the control room received P .800 .C5 .9-1 "DIESEL GENERATOR 2 STORAGE TANK LEVEL LOW" alarm. OPS2 reported oil level at 134.5" locally; the setpoint is 134.5". OPS2 transferred FO from FO-TK-1 to DO-TK-1B per SOP-FO -OPS to clear the alarm. Final level 134.7". The alarm receipt and actions taken were logged in the control room log. Per SWP-CAP-01, if an issue is plant equipment related, an AR-CR should be initiated as soon as possible, but no later than the end of the shift the issue is identified. <I> **** Actions Taken **** No further actions.
402347 | CR | 20191216 |  |  | LPRM 4049A Shows Rejected in ACUMEN |  |  |  | N | YES | <D> **** Detailed Description **** LPRM 4049A shows rejected (highlighted in red) on the 12/16/19 at 1700 ACUMEN case. Plot of LPRM is stable and symmetrical LPRM values are consistent with 4049A's value of 60. <I> **** Actions Taken **** Informed CRS. | 02-00-LPRM-DET-40/49A
402348 | CR | 20191217 |  |  | FPc-RV-21 lifting on pump start | [5 empty] | <D> **** Detailed Description **** After shifting from FPC-DM-1B to FPC-DM-1A to support I&C instrument calibrations, RWCR reported indications of FPC -RV-21A lifting on the re-start of FPC-P-1B. Confirmed the indications via EDR-TK-2 and SST levels. After reviewing FPC temperature trends crew supervision made the decision to transfer FPC to one pump operation. After securing the FPC-P-1B the relief valve indicates cloesed via previous indications. CR initiated for trending. <I> **** Actions Taken **** Secured FPC-P-1B per SOP-FPC-OPS | 02-00-FPC-RV-21A
402349 | CR | 20191217 |  |  | FPC-V-12B slow to close. | [5 empty] | <D> **** Detailed Description **** During backwash of FPC-DM-1B, FPC-V-12B took approximately 20 minutes to close ( should have taken less than 2 minutes) SOP-FPC-DEMIN step 5.8.12.n <I> **** Actions Taken **** MCR staff informed. CR & WR written. | 02-00-FPC-V-12B
402352 | CR | 20191217 |  |  | PM 02143745 cannot be performed due to FP-P-2b oos | [5 empty] | <D> **** Detailed Description **** Per PPM 1.5.13 step 4.4 and 4.8, initated CR to document surveillance PM WO 02143745/PMRQ 16622-01 (PPM 15.1.6) will go past late date due to FP-P-2B OOS for extended maintenance. Performance of surveillance tracked in ESOMS tracking log LCS L19-FP-P-2B-001 per procedure. PM coordinator notified. No additional actions required.
402356 | CR | 20191217 |  |  | Div 2 24 Volt charger surveillances title show wrong div. | [5 empty] | <D> **** Detailed Description **** While reviewing the T20 schedule it was discovered that ESP-C02A-B101 and ESP-C02B-B101 surveillance procedures identify the wrong division in the title. It is recommended to update the procedure title to the correct division and review.
402357 | CR | 20191217 |  |  | Spare transformer condition/debris | [5 empty] | <D> **** Detailed Description **** While performing the PMs for the spare transformers it was noticed that birds had been building nests and leaving other gifts in the low voltage terminal boxes. The purpose of this CR is to build covers (plexiglass or wood) for the low voltage terminal boxes to ensure that there will no longer be issues with bird foreign material building up in the terminal boxes. This CR only impacts E-TR-N1-SPARE, E-TR-B-SPARE and E-TR -N2-SPARE | 02-00-E-TR-B-SPARE,02-00-E-TR-N1-SPARE,02-00-E-TR-N2-SPARE

## Sheet1
ORIGINATION_DATE
20180815 | 2018-08-15 | 2019-12-17 | 489
20180816
20180817
20180818
20180819
20180820
20180821
20180822
20180823
20180824
20180825
20180826
20180827
20180828
20180829
20180830
20180831
20180901
20180902
20180903
20180904
20180905
20180906
20180907
20180908
20180909
20180910
20180911
20180912
20180913
20180914
20180915
20180916
20180917
20180918
20180919
20180920
20180921
20180922
20180923
20180924
20180925
20180926
20180927
20180928
20180929
20180930
20181001
20181002
20181003
20181004
20181005
20181006
20181007
20181008
20181009
20181010
20181011
20181012
20181013
20181014
20181015
20181016
20181017
20181018
20181019
20181020
20181021
20181022
20181023
20181024
20181025
20181026
20181027
20181028
20181029
20181030
20181031
20181101
20181102
20181103
20181104
20181105
20181106
20181107
20181108
20181109
20181110
20181111
20181112
20181113
20181114
20181115
20181116
20181117
20181118
20181119
20181120
20181121
20181122
20181123
20181124
20181125
20181126
20181127
20181128
20181129
20181130
20181201
20181202
20181203
20181204
20181205
20181206
20181207
20181208
20181209
20181210
20181211
20181212
20181213
20181214
20181215
20181216
20181217
20181218
20181219
20181220
20181221
20181222
20181223
20181224
20181225
20181226
20181227
20181228
20181229
20181230
20181231
20190101
20190102
20190103
20190104
20190105
20190106
20190107
20190108
20190109
20190110
20190111
20190112
20190113
20190114
20190115
20190116
20190117
20190118
20190119
20190120
20190121
20190122
20190123
20190124
20190125
20190126
20190127
20190128
20190129
20190130
20190131
20190201
20190202
20190203
20190204
20190205
20190206
20190207
20190208
20190209
20190210
20190211
20190212
20190213
20190214
20190215
20190216
20190217
20190218
20190219
20190220
20190221
20190222
20190223
20190224
20190225
20190226
20190227
20190228
20190301
20190302
20190303
20190304
20190305
20190306
20190307
20190308
20190309
20190310
20190311
20190312
20190313
20190314
20190315
20190316
20190317
20190318
20190319
20190320
20190321
20190322
20190323
20190324
20190325
20190326
20190327
20190328
20190329
20190330
20190331
20190401
20190402
20190403
20190404
20190405
20190406
20190407
20190408
20190409
20190410
20190411
20190412
20190413
20190414
20190415
20190416
20190417
20190418
20190419
20190420
20190421
20190422
20190423
20190424
20190425
20190426
20190427
20190428
20190429
20190430
20190501
20190502
20190503
20190504
20190505
20190506
20190507
20190508
20190509
20190510
20190511
20190512
20190513
20190514
20190515
20190516
20190517
20190518
20190519
20190520
20190521
20190522
20190523
20190524
20190525
20190526
20190527
20190528
20190529
20190530
20190531
20190601
20190602
20190603
20190604
20190605
20190606
20190607
20190608
20190609
20190610
20190611
20190612
20190613
20190614
20190615
20190616
20190617
20190618
20190619
20190620
20190621
20190622
20190623
20190624
20190625
20190626
20190627
20190628
20190629
20190630
20190701
20190702
20190703
20190704
20190705
20190706
20190707
20190708
20190709
20190710
20190711
20190712
20190713
20190714
20190715
20190716
20190717
20190718
20190719
20190720
20190721
20190722
20190723
20190724
20190725
20190726
20190727
20190728
20190729
20190730
20190731
20190801
20190802
20190803
20190804
20190805
20190806
20190807
20190808
20190809
20190810
20190811
20190812
20190813
20190814
20190815
20190816
20190817
20190818
20190819
20190820
20190821
20190822
20190823
20190824
20190825
20190826
20190827
20190828
20190829
20190830
20190831
20190901
20190902
20190903
20190904
20190905
20190906
20190907
20190908
20190909
20190910
20190911
20190912
20190913
20190914
20190915
20190916
20190917
20190918
20190919
20190920
20190921
20190922
20190923
20190924
20190925
20190926
20190927
20190928
20190929
20190930
20191001
20191002
20191003
20191004
20191005
20191006
20191007
20191008
20191009
20191010
20191011
20191012
20191013
20191014
20191015
20191016
20191017
20191018
20191019
20191020
20191021
20191022
20191023
20191024
20191025
20191026
20191027
20191028
20191029
20191030
20191031
20191101
20191102
20191103
20191104
20191105
20191106
20191107
20191108
20191109
20191110
20191111
20191112
20191113
20191114
20191115
20191116
20191117
20191118
20191119
20191120
20191121
20191122
20191123
20191124
20191125
20191126
20191127
20191128
20191129
20191130
20191201
20191202
20191203
20191204
20191205
20191206
20191207
20191208
20191209
20191210
20191211
20191212
20191213
20191214
20191215
20191216
20191217